## Sheet 1
Water Consumption
Plant Name | Type | Cooling | Location | (gal/kWh) | Notes | Source
Cooling Water
Geysers - Calpine | Dry Steam | Water | CA | 1.1257 | Municipal waste water piped in for reservoir make-up | Calpine 2012
Coso Hay Ranch/China Lake | Flash | Water | CA | 0.73465 | Groundwater, Make-up injection for lost from cooling; average annual consumption | BLM and U.S. Navy 2008
Salt Wells - Vulcan | Flash | Water | NV | 3.7881 | Estimated water consumption, could be geofluid or fresh make-up water | BLM 2011a
Dixie Valley | Flash | Water | NV | 2.1729 | Re-injection program started in 2002 | NDWR 2012
Modeled System | Flash | Water |  | 2.7 | System modeled in GETEM, assumes all lost geofluid replaced through reinjection | Clark et al. 2012
Blue Mountain | Undecided | Water | NV | 2.4244 | Estimated, would be groundwater if Binary or Condensate if Flash plant | BLM 2007
East Mesa | 4 Binary, 2 Flash | Water | CA | 4.8575 | Exact generation unclear. Source mentions 73 MW in one location and 50 MW in another. Cooling water is taken from surface water from local irrigation district | Environmental Management Associates 2006
Tuscorora | Binary | Water | NV | 3.7895 | From freshwater wells, Wet cooling towers with 3.2X concentration factor | DOE 2011
Patua | Binary | Water | NV | 4.5 | Groundwater for wet cooled system, no significant water required for air cooled system | BLM 2010a
Salt Wells - Vulcan | Binary | Water | NV | 4.5457 | For wet cooling | BLM 2011a
Oregon Institute of Technology | Binary | Water | OR | 1.5 | Estimated evaporative loss, make-up from fresh groundwater well | MHA 2008
San Emidio | Binary | Water | NV | 2.763 | Based on new permits for consumptive use in 2010 coinciding with revamping and expanding the plant which opened in 2012 with net generation of 8.6 MW | NDWR 2012
Salt Wells - Ormat | Binary | Hybrid | NV | 1.1 | Range of 2500-3500 gpm when operating wet cooling, 1.1 gal/kwh assuming 3 months, 1.5 assuming 4 months | BLM 2011a
Coyote Canyon | Flash | Hybrid | NV | 0.32469 | Exact plant configuration not determined, water consumption assuming a flash system with hybrid cooling | BLM 2010b
McGinnis | Binary | Hybrid | NV | 1.7218 | Hybrid Cooling, 50% fresh water, 50% geofluid, only fresh water included | BLM 2011b
Soda Lake | Binary | Hybrid | NV | 0.56999 | cool working fluid in cooling towers, for dust suppression, for drilling equipment maintenance, etc. | NDWR 2012
Theoretical Plant | Binary | Hybrid | - | 0.74 | Model results showing water consumption for hybrid system that increases summer output by ~15% | Kozubal and Kutscher 2003
Water for Other Uses
Dixie Valley | Flash | Water | NV | 0.23995 | Max consumption for drilling and plant operations | NDWR 2012
Steamboat Complex | 6 binary, 1 flash | Air | NV | 0.06779 | Fresh surface water consumption for enhanced cooling and other industrial uses. Much of water being used for hybrid cooling tests at some of the binary plants | NDWR 2012
Jersey Valley | Binary | Air | NV | 0.0010747 | Facility operations, mostly washing and bathrooms | DOE 2011
Coyote Canyon | Flash or Binary | Hybrid or Air |  | 0.029517 | Maximum non cooling water consumption (dust control, maintenance, domestic water) | BLM 2010b
Cooper Creek EGS - Geodynamics | Binary (EGS) | Air | Australia | 0.12232 | Estimated ongoing water requirements for plant, sourced from local groundwater | Geodynamics 2011
Telephone Flat | Flash | Water | CA | 0.005787 | Does not include loss of geofluid. Fresh water consumption for other plant uses. | Kagel et al. 2005
Salton Sea (all plants) | Flash | Water | CA | 0.056316 | Total fresh groundwater use for whole complex (from source appendix A) | CEC 2008

## References
BLM (Bureau of Land Management), 2007, Environmental Assessment: Blue Mountain Geothermal Development Project, Humboldt County, Nevada, Pershing County, Nevada, NV‑020-08-01, U.S. Department of the Interior, Winnemucca Field Office, Winnemucca, Nev., Dec. Available at http://www.blm.gov/nv/st/en/fo/wfo/blm_information/nepa0/minerals/
geothermal/blue_mtn_.html.
BLM, 2010a, Patua Geothermal Development Project (Vulvan Power Company) Environmental Assessment, U.S. Department of the Interior, Stillwater Field Office, Carson City Nev. Available at http://www.blm.gov/nv/st/en/fo/carson_city_field/blm_information/nepa/patua_vulcan_
geothermal.html.
BLM, 2010b, Coyote Canyon Geothermal Utilization Environmental Assessment, U.S. Department of the Interior, Stillwater Field Office, Carson City, Nev. Available at http://www.blm.gov/nv/st/en/fo/carson_city_field/blm_information/nepa/tgp_coyote_canyon.html.
BLM, 2011a, Final Environmental Impact Statement, Salt Wells Energy Projects, U.S. Department of the Interior, Stillwater Field Office, Carson City, Nev., July. Available at http://www.blm.gov/nv/st/en/fo/carson_city_field/blm_information/nepa/salt_wells_energy.html.
BLM, 2011b, McGinness Hills Geothermal Development Project Environmental Assessment, U.S. Department of the Interior, Mount Lewis Field Office, Battle Mountain, Nev. Available at www.blm.gov/pgdata/etc/medialib/blm/nv/field_offices/battle_mountain_field/blm_information/nepa/mcginness_hills_ea.Par.11536.File.dat/MH_Geothermal_Development_Project_Revised_EA_V3.pdf.
BLM and U.S. Navy, 2008, Coso Hay Ranch Water Extraction and Delivery System Environmental Assessment, U.S. Department of the Interior, Ridgecrest Field Office. Available at www.blm.gov/pgdata/etc/medialib/blm/ca/pdf/ridgecrest/ea.Par.1465.File.dat/
HayRanchEA.pdf.
Calpine (Calpine Corporation), 2012, Renewable Energy, Available at http://www.geysers.
com/renewable.htm.
CEC (California Energy Commission), 2008, 2007 Environmental Performance Report on California’s Electrical Generation System, CEC-700-2007-016-SF, Jan. Available at http://www.energy.ca.gov/2007publications/CEC-700-2007-016/CEC-700-2007-016-SF.PDF.
Clark, C.E., et al., 2012, Water Resource Assessment of Geothermal Resources and Water Use in Geopressured Geothermal Systems, ANL/EVS/R-11/10–Rev. 1, prepared for U.S. Department of Energy, Office of Energy Efficiency and Renewable Energy (EERE), Geothermal Technologies Program, Argonne National Laboratory, Argonne, Ill.
DOE (U.S. Department of Energy), 2011, Final Environmental Assessment: Ormat Northern Nevada Geothermal Power Plant Projects, DOE/EA-1849, Aug. Available at http://energy.gov/nepa/downloads/ea-1849-final-environmental-assessment.
Environmental Management Associates, 2006, Environmental Assessment for Ormesa Geothermal Projects Continuing Geothermal Lease Operations East Mesa Known Geothermal Resource Area Imperial County, California, prepared for U.S. Department of the Interior, Bureau of Land Management.
Geodynamics (Geodynamics Limited), 2011, Environmental Impact Report─Cooper Creek Water Extraction. Available at www.pir.sa.gov.au/__data/assets/pdf_file/0016/156040/
GDY_Water_Extraction_SEO_Jun_2011.pdf.
Kagel, A., et al., 2005, A Guide to Geothermal Energy and the Environment, Geothermal Energy Association, Washington, D.C.
Kozubal, E., and C. Kutscher, 2003, “Analysis of a Water-Cooled Condenser in Series with an Air-Cooled Condenser for a Proposed I-MW Geothermal Power Plant,” Geothermal Resources Council Transactions 27.
MHA (MHA Environmental Consulting), 2008, Oregon Institute of Technology Deep Geothermal Well and Power Plant Project Final Environmental Assessment, prepared for U.S. Department of Energy. Available at .http://www.eere.energy.gov/golden/
ReadingRoom/NEPA/1621/OITFinalEA.pdf.
NDWR (State of Nevada Division of Water Resources), 2012, Nevada Water Permit Search. Available at http://water.nv.gov/data/permit/index.cfm. Accessed Sept. 25, 2012.