## TEA Summary
GETEM Input |  | Business-as-Usual | Discovery Through Mining: BLM Land | Discovery Through Mining: Private Land
RESOURCE EXPLORATION AND DEVELOPMENT | Exploration Duration | 4 yrs | 0.75–1 yrs | 0.75–1 yrs
INPUTS | Exploration Costs with Early Drilling | $18M | $1.1–$8.8M | $1.1–$7.6M
($/project)
| Drilling Costs | $12.6M | $14.8M | $14.8M
| Royalty | 1.75% |  | 0%
| Leasing Costs $/acre | 20 | 1 | 0
| Transmission Costs | $750k-$1M/mile | 0 | 0
| Period to Project On-Line | 8.25 yrs | 4.7–5.2 yrs | 4.2–4.75 yrs
| CAPEX $/kW | $8.6k | $5.4k–5.6k | $5.3k–5.6k
RESULTS | LCOE $/MWh | 87 | $65-67 | $62-65
| Total capital cost | $116M | $101–$107M | $99–$106M
GETEM input parameter adjustments and estimated costs for BAU and modeled scenarios of geothermal development through mineral exploration.
To model cost and schedule reductions in GETEM, the study selected a representative and reasonable hypothetical resource based on known hydrothermal systems in Nevada as well as temperatures at depths identified by mining activity (e.g., 330°F at the Meikle mine). Higher temperatures might be found deeper but this would require confirmation through geochemical analyses or additional measured temperatures. The modeled resource assumes a 330°F temperature at a depth of ~2,000 feet, with pumped wells averaging ~1,750 gpm supplied to a 20-MWe air-cooled binary power plant. These resource characteristics as well as the water-limited and arid setting of Nevada are typically best matched to air-cooled binary power plants.
20-MWe Diesel Plant |  | 2014–2018 Low | 2014–2018 High
FUEL | Annual fuel usage (gallons/year) | 10680677 | 10680677
| Cost ($/gallon) | 1.683 | 2.985
RESULTS | Fuel Cost $/MWh | 93 | 166
| LCOE $/MWh | 109 | 185
| Annual Fuel cost | $18M | $32M
Cost estimates for a 20-MWe diesel power plant.
The fuel total does not include delivery fuel consumption or degradation of capacity factor.
Bleiwas, D.I. 2011. Estimates of Electricity Requirements for the Recovery of Mineral Commodities, with Examples Applied to Sub-Saharan Africa. USGS Open-file Report 2011-1253, 100 p.
These prices do not include a premium for site transportation or road conditions.
U.S. Energy Information Administration. 2020. “Refiner Petroleum Product Prices by Sales Type.” https://www.eia.gov/dnav/pet/PET_PRI_REFOTH_A_EPD2_PTG_DPGAL_A.htm

## BAU Scenario
OVERNIGHT CAPITAL COST & PERFORMANCE SUMMARY |  | GETEM Assumptions
Power Sales | kW | 20000
Period to Bring Project On-Line | yr | 8.25
Year Project Comes On-Line | yr | 2026
Project Life | yr | 30
Net Capacity Factor |  | 0.95
Total Capital Cost (w/o Contingency) |  | 103421152.9706
TOTAL CAPITAL COST (with Contingency) |  | 115614080.6696
Exploration
Exploration Drilling Costs (full-sized) |  | 11379347.5657
Exploration Stimulation Costs |  | 0
Small Diameter Exploration Drilling |  | 4795350.0802
Non-Drilling Exploration Costs |  | 899542.6829
Permitting & Leasing Costs |  | 393573.9601
Other Indirect Costs |  | 424954.8883
TOTAL EXPLORATION COST (w/o Contingency) |  | 17892769.1772
Drilling
Well Count
Number Production Wells Required |  | 4.9597
Number Injection Wells Required |  | 3.2123
Number of Wells Drilled to Complete Field |  | 6.8054
# Undeveloped Sites Drilled |  | 0
Total Wells Drilled at Other Sites |  | 0
# Wells Stimulated |  | 0
Well Cost
Production Well Cost |  | 1580464.9397
Injection Well Cost |  | 1580464.9397
Stimulation Cost per Well |  | 0
Drilling Costs
Failed Wells Supplement Injection |  | Yes
Production Capacity Drilled before PPA |  | 0.6
Permitting Costs |  | 1083709.2732
Production Well Costs |  | 4075388.3835
Injection Well Costs |  | 6680232.3618
Stimulation Costs |  | 0
Non-Drilling Costs |  | 793315.1633
TOTAL DRILLING COST (w/o contingency) |  | 12632645.1818
Field Gathering System & GF Pumping
Total Production Flow | kg/s | 545.571
Flow per well | kg/s | 110
Production Pumping | kW | 2806.4592
Total Injection Flow | kg/s | 545.571
Injection Pumping | kW | 2140.9404
Wells Used for Injection |  | 4.8456
Surface Equipment Costs |  | 5044971.7133
Total Production Pump Costs |  | 1829010.8673
Total Injection Pump Costs |  | 1139857.1238
Indirect Costs |  | 1092796.3233
TOTAL FIELD GATHERING SYSTEM COST (w/o contingency) |  | 9106636.0277
Power Plant Costs
Transmission Line | miles | 0
Estimated Generator Nameplate | kW | 29394.8509
Power Plant Net Output | kW | 24947.3996
Geothermal Pumping Power | kW | 4947.3996
Transmission Cost |  | 0
Power Plant Cost (per net KW) | $/kW | 2556.944
Power Plant Cost |  | 63789102.5838
TOTAL POWER PLANT & TRANSMISSION COST (w/o contingency) |  | 63789102.5838
O&M COST SUMMARY
Facility Staff |  | 11.3895
Labor Cost | per yr | 1128011.9862
Plant Maintenance | per yr | 1148203.8465
Field Maintenance | per yr | 325227.666
Geothermal Pump Maintenance/Replacement | per yr | 612853.3618
Make-up Water Cost | per yr | 0
Taxes & Insurance | per yr | 742640.0862
TOTAL ANNUAL O&M COST |  | 3956936.9467
RESERVOIR
Decline Rate | %/yr | 0.005
Temperature Decline at Replacement | C | 22.45
# Well Field/Reservoir Replacements |  | 0
Year of 1st Replacement |  | NA
Temperature at End of Project | C | 141.9532
Sales @ End of Project Life | MW | 10.6502
CAPEX ($/kW) | Binary | 8562.9637
Levelized Cost of Energy ($/MWh) | Binary | 87.1781

## BLM Land Scenarios
OVERNIGHT CAPITAL COST & PERFORMANCE SUMMARY |  | GETEM Assumptions w/ Exploration Drilling | GETEM Assumptions w/ No Exploration Drilling
Power Sales | kW | 20000 | 20000
Period to Bring Project On-Line | yr | 8.1667 | 4.6667
Year Project Comes On-Line | yr | 2026 | 2022
Project Life | yr | 30 | 30
Net Capacity Factor |  | 0.95 | 0.95
Total Capital Cost (w/o Contingency) |  | 95523770.723 | 88733402.233
TOTAL CAPITAL COST (with Contingency) |  | 107220862.2068 | 100116035.574
Exploration
Exploration Drilling Costs (full-sized) |  | 4741394.819 | 0
Exploration Stimulation Costs |  | 0 | 0
Small Diameter Exploration Drilling |  | 1500000 | 0
Non-Drilling Exploration Costs |  | 1100000 | 1100000
Permitting & Leasing Costs |  | 303776.659 | 15000
Other Indirect Costs |  | 177064.5368 | 0
TOTAL EXPLORATION COST (w/o Contingency) |  | 7822236.0148 | 1115000
Drilling
Well Count
Number Production Wells Required |  | 4.9904 | 4.9904
Number Injection Wells Required |  | 3.1412 | 3.21
Number of Wells Drilled to Complete Field |  | 8.0679 | 8
# Undeveloped Sites Drilled |  | 0 | 0
Total Wells Drilled at Other Sites |  | 0 | 0
# Wells Stimulated |  | 0 | 0
Well Cost
Production Well Cost |  | 1580464.9397 | 1580464.9397
Injection Well Cost |  | 1580464.9397 | 1580464.9397
Stimulation Cost per Well |  | 0 | 0
Drilling Costs
Failed Wells Supplement Injection |  | Yes | Yes
Production Capacity Drilled before PPA |  | 0.6 | 0.6
Permitting Costs |  | 1083709.2732 | 1083709.2732
Production Well Costs |  | 6163813.2647 | 6163813.2647
Injection Well Costs |  | 6637952.7466 | 6685366.6948
Stimulation Costs |  | 0 | 0
Non-Drilling Costs |  | 901007.0195 | 903502.4904
TOTAL DRILLING COST (w/o contingency) |  | 14786482.304 | 14836391.7232
Field Gathering System & GF Pumping
Total Production Flow | kg/s | 548.9436 | 548.9436
Flow per well | kg/s | 110 | 110
Production Pumping | kW | 2823.8079 | 2823.8079
Total Injection Flow | kg/s | 548.9436 | 548.9436
Injection Pumping | kW | 2156.0757 | 2156.0757
Wells Used for Injection |  | 5.0775 | 5.79
Surface Equipment Costs |  | 5180079.2019 | 5063002.3349
Total Production Pump Costs |  | 1840317.3083 | 1840317.3083
Total Injection Pump Costs |  | 1144604.5569 | 1144604.5569
Indirect Costs |  | 1113409.2364 | 1097444.2091
TOTAL FIELD GATHERING SYSTEM COST (w/o contingency) |  | 9278410.3034 | 9145368.4092
Power Plant Costs
Transmission Line | miles | 0 | 0
Estimated Generator Nameplate | kW | 29420.7976 | 29420.7976
Power Plant Net Output | kW | 24979.8836 | 24979.8836
Geothermal Pumping Power | kW | 4979.8836 | 4979.8836
Transmission Cost |  | 0 | 0
Power Plant Cost (per net KW) | $/kW | 2547.5156 | 2547.5156
Power Plant Cost |  | 63636642.1006 | 63636642.1006
TOTAL POWER PLANT & TRANSMISSION COST (w/o contingency) |  | 63636642.1006 | 63636642.1006
O&M COST SUMMARY
Facility Staff |  | 11.3981 | 11.3981
Labor Cost | per yr | 1128878.6428 | 1128878.6428
Plant Maintenance | per yr | 1145459.5578 | 1145459.5578
Field Maintenance | per yr | 333550.786 | 326400.1269
Geothermal Pump Maintenance/Replacement | per yr | 616641.8523 | 616641.8523
Make-up Water Cost | per yr | 0 | 0
Taxes & Insurance | per yr | 738629.4371 | 722471.5355
TOTAL ANNUAL O&M COST |  | 3963160.276 | 3939851.7153
RESERVOIR
Decline Rate | %/yr | 0.005 | 0.005
Temperature Decline at Replacement | C | 22.45 | 22.45
# Well Field/Reservoir Replacements |  | 0 | 0
Year of 1st Replacement |  | NA | NA
Temperature at End of Project | C | 141.9532 | 141.9532
Sales @ End of Project Life | MW | 10.638 | 10.638
CAPEX ($/kW) | Binary | 5646.6166 | 5371.9221
Levelized Cost of Energy ($/MWh) | Binary | 67.3951 | 65.0768

## Private Land Scenarios
OVERNIGHT CAPITAL COST & PERFORMANCE SUMMARY |  | GETEM Assumptions w/ Exploration Drilling | GETEM Assumptions w/ No Exploration Drilling
Power Sales | kW | 20000 | 20000
Period to Bring Project On-Line | yr | 4.75 | 4.1667
Year Project Comes On-Line | yr | 2022 | 2022
Project Life | yr | 30 | 30
Net Capacity Factor |  | 0.95 | 0.95
Total Capital Cost (w/o Contingency) |  | 94318950.9095 | 88082389.1744
TOTAL CAPITAL COST (with Contingency) |  | 105835319.4213 | 99374482.6488
Exploration
Exploration Drilling Costs (full-sized) |  | 4741394.819 | 0
Exploration Stimulation Costs |  | 0 | 0
Small Diameter Exploration Drilling |  | 1500000 | 0
Non-Drilling Exploration Costs |  | 1100000 | 1100000
Permitting & Leasing Costs |  | 65000 | 15000
Other Indirect Costs |  | 177064.5368 | 0
TOTAL EXPLORATION COST (w/o Contingency) |  | 7583459.3558 | 1115000
Drilling
Well Count
Number Production Wells Required |  | 5.7143 | 5.7143
Number Injection Wells Required |  | 3.5711 | 3.3926
Number of Wells Drilled to Complete Field |  | 8.46 | 8.46
# Undeveloped Sites Drilled |  | 0 | 0
Total Wells Drilled at Other Sites |  | 0 | 0
# Wells Stimulated |  | 0 | 0
Well Cost
Production Well Cost |  | 1580464.9397 | 1580464.9397
Injection Well Cost |  | 1580464.9397 | 1580464.9397
Stimulation Cost per Well |  | 0 | 0
Drilling Costs
Failed Wells Supplement Injection |  | Yes | Yes
Production Capacity Drilled before PPA |  | 0.6 | 0.6
Permitting Costs |  | 1083709.2732 | 1083709.2732
Production Well Costs |  | 6163813.2647 | 6163813.2647
Injection Well Costs |  | 6637952.7466 | 6637952.7466
Stimulation Costs |  | 0 | 0
Non-Drilling Costs |  | 901007.0195 | 901007.0195
TOTAL DRILLING COST (w/o contingency) |  | 14786482.304 | 14786482.304
Field Gathering System & GF Pumping
Total Production Flow | kg/s | 628.5784 | 628.5784
Flow per well | kg/s | 110 | 110
Production Pumping | kW | 3233.4555 | 3233.4555
Total Injection Flow | kg/s | 628.5784 | 628.5784
Injection Pumping | kW | 2516.3688 | 2516.3688
Wells Used for Injection |  | 5.8718 | 6.2685
Surface Equipment Costs |  | 5961227.2442 | 6165297.1504
Total Production Pump Costs |  | 2107290.6603 | 2107290.6603
Total Injection Pump Costs |  | 1253864.3312 | 1253864.3312
Indirect Costs |  | 1271233.9412 | 1299061.6557
TOTAL FIELD GATHERING SYSTEM COST (w/o contingency) |  | 10593616.1768 | 10825513.7975
Power Plant Costs
Transmission Line | miles | 0 | 0
Estimated Generator Nameplate | kW | 30075.032 | 30075.032
Power Plant Net Output | kW | 25749.8243 | 25749.8243
Geothermal Pumping Power | kW | 5749.8243 | 5749.8243
Transmission Cost |  | 0 | 0
Power Plant Cost (per net KW) | $/kW | 2382.75 | 2382.75
Power Plant Cost |  | 61355393.0728 | 61355393.0728
TOTAL POWER PLANT & TRANSMISSION COST (w/o contingency) |  | 61355393.0728 | 61355393.0728
O&M COST SUMMARY
Facility Staff |  | 11.6024 | 11.6024
Labor Cost | per yr | 1149289.1119 | 1149289.1119
Plant Maintenance | per yr | 1104397.0753 | 1104397.0753
Field Maintenance | per yr | 382899.563 | 395363.4627
Geothermal Pump Maintenance/Replacement | per yr | 706097.5899 | 706097.5899
Make-up Water Cost | per yr | 0 | 0
Taxes & Insurance | per yr | 746932.4067 | 753393.9352
TOTAL ANNUAL O&M COST |  | 4089615.7469 | 4108541.175
RESERVOIR
Decline Rate | %/yr | 0.005 | 0.005
Temperature Decline at Replacement | C | 22.45 | 22.45
# Well Field/Reservoir Replacements |  | 0 | 0
Year of 1st Replacement |  | NA | NA
Temperature at End of Project | C | 141.9532 | 141.9532
Sales @ End of Project Life | MW | 10.3494 | 10.3494
CAPEX ($/kW) | Binary | 5636.0384 | 5292.0398
Levelized Cost of Energy ($/MWh) | Binary | 64.6765 | 62.3093