## EERE-GTO
Plant Type
|  | Characteristic n | Flash | Binary
Flexibility Characteristics | Resource Characteristics | 1 | Some resources (Iceland, Imperial Valley, CA, etc.) have high NCG concentrations that may be used to generate liquid fuel (e.g. methanol in Iceland)
|  | 2 | Some resources have high concentrations of brine metals/REE that may be recoverable (e.g. lithium, zinc, silica, manganese)
|  | 3 | *Depending on the resource and power plant type, some of the potential flexibility options for geothermal carry the risk of variable/potentially unpredictable resource depletion/temperature & pressure decreases or increases
|  | 4 | Variable well flow rates are limited by the wellbore size, well productivity, and minimum required rate to maintain unassisted flow | Variable well flow rates are limited by wellbore size, well productivity, pump limitations, and predicted longterm reservoir performance
| Plant Characteristics | Characteristic 1 | Ramp rate = ~2-5% of nominal power if not a black start; increases O&M costs | Ramp rate = 15% of nominal power/minute (Flexible operation mode = 30% of nominal power/minute using motive fluid bypass valve); requires no fuel consumption on standby & minimal O&M increase
|  | Characteristic 2 |  | Turndown = 0% of nominal power with no affect on operating costs
|  | Characteristic 3 |  | Baseload
|  | Characteristic 4 |  | Spinning reserve
|  | Characteristic 5 |  | Supplemental reserve
|  | Characteristic 6 |  | Dispatchable/Real power regulation through AGC and inertia supply (inertia constant ~1.75-5sec)
|  | Characteristic 7 |  | Load following
|  | Characteristic 8 |  | Automatic voltage regulation
|  | Characteristic 9 |  | Automatic adjustment of reactive power
|  | Characteristic 10 |  | Under/over voltage ride-through; NERC “PRC-024-1” standard compliant - “Generator Performance during Frequency and Voltage Excursions”; can remain on-line during grid disruption
|  | Characteristic 11 |  | Under/over frequency ride-through (up to ±5% nominal frequency) using Governor Automatic Droop Response
|  | Characteristic 12 | Transmission capacity requirements similar to traditional energy resources due to >80% capacity factors (i.e. lower than variable resources)
|  | Characteristic 13 | Lower integration costs than variable energy sources
|  | Characteristic 14 | Standby wells can be throttled or shut-in to reduce output and used sporadically on-demand assuming either pumps can be turned on or wells will self flow; this may only be feasible in a reservoir with declining pressure that can't tolerate full production levels for extended time periods (e.g. at the Geysers in the 1990s); this caused increased O&M costs related to thermal cycling damage, corrosion, pipeline damage, and increased NCGs. | Variable frequency drive (VFD) pumps and injection booster pumps; VFDs can provide adjustable well specific flow rates but equivalent injection must be maintained which may require pumps on the injection line; cost limitations: are the additional expenses justified if not in full time use
|  | Characteristic 15 |  | Seasonal net output depending on ambient temperature fluctuations; geothermal plants typically produce more power in the coldest months which complements reduced solar output
|  | Characteristic 16 |  | Cooling fans/towers emit waste heat that may be recoverable for cascade use
|  | Characteristic 17 |  | Depending on brine chemistry and required injection temperatures, some additional heat may be available from the injectate for direct use or specific chemical processes.
|  | Characteristic 18 |  | Potential for combined heat and power
|  | Characteristic 19 |  | Potential to be coupled with thermal/energy storage; additional R&D required
| Miscellaneous | Characteristic 1 | Financing and PPA restrictions/rigidity do not currently encourage flexibility (e.g. energy-only PPAs at fixed energy prices with low or even no escalation rates prevent reserve market participation)
|  | Characteristic 2 | Assuming PPA flexibility, ancillary service prices must predictably and consistently exceed energy prices
|  | Characteristic 3 | Cost of multiple cycling daily with respect to pumps, wellheads, and casings is not well known. Will add cost in terms of equipment lifetimes and O&M.