## US GDH data
ABOUT | ABOUT | ABOUT | ABOUT | ABOUT | ECONOMIC | ECONOMIC | ECONOMIC |  | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL | TECHNICAL |  | TECHNICAL | CONTACT | CONTACT | COST | COST | COST | COST | COST | LOCATION | LOCATION | LOCATION | STATUS | STATUS | STATUS | STATUS | ABOUT
State | Site | General Location | Year Closed | Year Opened | Original system cost | 2020 Updated capital cost | Annual O&M cost | Source(s) | Minerals | Temp (F) | Temp (C) | Flow (GPM) | Flow (L/min) | Depth (ft) | Capacity (10^6 Btu/hr) | Capacity (10^9 Btu/yr) | Capacity (MWt) | Energy Use (X10^9 Btu/yr) | Energy Use (GWh/yr) | Energy Use (X10^12 TJ/yr) | Load Factor | Notes | Source(s) | Contact | Source | Employment | Installation Cost | Source for Installation Cost | Operation Cost | Source for Operation Cost | Latitude | Longitude | Source | Status of Project | Status Updated | If closed or inactive - why? | Source for project status | Notes
CA | San Bernardino District Heating | San Bernardino (37 bldgs.), CA |  | 1984 | 6000000 | 13800000 | 161280 | Mattson and Neupane, 2017 |  | 138 | 58.8889 | 3700 | 14023 |  | 43.8 | 383.688 | 12.8333 | 75 | 21.9748 | 79.05 | 0.19547 |  |  | Kristen Jensen | OIT Geo-heat Center Database CD-2004 | [5 empty] | 34.0921 | -117.2896 | Google Maps pg 4 https://www.ci.san-bernardino.ca.us/civicax/filebank/blobdload.aspx?blobid=4209 | open | 2016 |  | https://www.ci.san-bernardino.ca.us/water/divisions/water_utility/water_quality/geothermal/default.asp
CA | Susanville District Heating | Susanville, CA |  | 1982 | 2400000 | 3329822 | 67200 | Mattson and Neupane, 2017 |  | 170 | 76.6667 | 1300 | 4927 |  | 19 | 166.44 | 5.5669 | 11.5 | 3.3695 | 12.121 | 0.069094 |  |  | Daniel Gibbs | OIT Geo-heat Center Database CD-2004 | [5 empty] | 40.4166 | -120.6537 | Google Maps, coordinates for city center | open | 2016 |  | second link confirms heating system still operating http://www.energy.ca.gov/geothermal/direct_use_projects/SUSANVILLE_CITY.PDF http://www.lassennews.com/story/2016/04/05/news/chapman-walks-out-of-wednesdays-pool-meeting/1001.html
CA | Canby/I'SOT District Heating System | Canby, CA |  | 2003 | 1400000 | 1568000 | 10496 | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 185 | 85 |  | 62 |  |  |  | 0.38 |  | 1.2 |  | 0.47 |  |  | Dale Merrick | OIT Geo-heat Center Database CD-2004
CA | Modoc joint unified school district (Alturas) | Modoc County, CA |  | 2017 | 4963448 | 4963448 | 31558 | Operator interviews 7&8-2020 |  | 180 | 82 | 500 | 1892 |  | 1.5 | 13.14 | 0.44 | [6 empty] | Darryl Anderson | Heats schools and hospital
CO | Pagosa Springs District Heating | Pagosa Springs, CO |  | 1982 | 1364000 | 3458000 | 35000 | Operator interview 6-2020, Mattson and Neupane, 2017 | 115 | 140 | 60 | 450 | 1705.5 |  | 17.5 | 153.3 | 5.1275 | 16.4 | 4.8052 | 17.2856 | 0.10698 |  |  | Martin Schmidt, Gene Tautges | OIT Geo-heat Center Database CD-2004 | [5 empty] | 37.2657 | -107.0143 | Google Maps, help from city map http://www.pagosasprings.co.gov/vertical/Sites/%7B175F1D4C-10BE-47AA-AF3E-C1BCDE2446A6%7D/uploads/%7BB8D0B650-704E-421C-AE26-52332EAEEB5A%7D.GIF | open | 2016 |  | http://www.pagosasprings.co.gov/index.asp?Type=B_BASIC&SEC=%7BE4D74380-5C86-4626-972B-C735CE3280D9%7D
ID | Boise City District Heating | Boise, ID |  | 1983 | 7128000 |  | 379000 | Site visit & interview 6-2020, Mattson and Neupane, 2017 |  | 174 | 78.8889 | 2100 | 7959 |  | 70.3 | 615.828 | 20.6 |  | 42.3 |  | 0 |  | Technical data updated based on numbers from Jon Gunnerson, previous flow rate 4000 GPM | Jon Gunnerson | http://publicworks.cityofboise.org/contact-us/geothermal-program/ | [5 empty] | 43.615 | -116.2023 | Google Maps, pg. 231 http://geology.isu.edu/Geothermal/References/GRC/Neely_etal_2006_GRC_Trans.pdf | open | 2016 |  | http://publicworks.cityofboise.org/services/geothermal/
ID | College of Southern Idaho | Twin Falls, ID |  | 1980 |  |  | 190400 | Mattson and Neupane, 2017 |  | 100 | 37.7778 |  | NA |  |  |  | 6.34 |  | 14 | 14 |  |  |  | Jon Caton | OIT Geo-heat Center Database CD-2004 | [5 empty] | 42.5816 | -114.4744 | Google Maps | open | 2016 |  | http://sustainability.csi.edu/map/index.asp
ID | Fort Boise Veteran's Hospital | Boise, ID |  | 1988 | 7500000 | 14775000 |  | Mattson and Neupane, 2017 |  | 162 | 72.2222 | 300 | 1137 |  | 6 | 52.56 | 1.758 | 12.1 | 3.5453 | 12.7534 | 0.23021 |  |  | Doug Lamb | OIT Geo-heat Center Database CD-2004 | [5 empty] | 43.621 | -116.1898 | Google Maps | open | 2016 |  | https://www.energystar.gov/index.cfm?fuseaction=%20labeled_buildings.showProfile&profile_id=2010
ID | Idaho Capitol Mall | Boise, ID |  | 1982 | 1800000 | 4446000 | 23500 | Operator interview 6-2020, Mattson and Neupane, 2017 |  | 169 | 76.1111 | 750 | 2842.5 |  | 11.3 | 98.988 | 3.3109 | 63.8 | 18.6932 | 67.2452 | 0.64452 |  |  | Ric Johnston | OIT Geo-heat Center Database CD-2004 | [5 empty] | 43.6178 | -116.1996 | Google Maps | open | 2016 |  | http://www.nrel.gov/docs/fy04osti/36158.pdf
ID | Kanaka Rapids Ranch | Buhl, ID |  | 1989 |  |  | 29120 | Operator Interview 6-2020, Mattson and Neupane, 2017 |  | 99 | 37.2222 |  | NA |  |  |  | 1.1 |  | 2.4 |  |  |  |  | Allen Lansbury, Val Clemens | contact info from realtor | [5 empty] | 42.6644 | -114.8032 | Google Maps | open | 2016 |  | https://energy.idaho.gov/renewableenergy/geothermal_heating.htm
ID | Ketchum District Heating | Ketchum, ID |  | 1929 | [5 empty] | 158 | 70 | 1027 | 3892.33 |  | 3 | 26.28 | 0.87899 | 6.6 | 1.9338 | 6.9564 | 0.25114 |  |  | Sherry Newland | Boyd, 2015 | [5 empty] | 43.6833 | -114.4106 | Google Maps, help from Appendix 1 in linked doc http://geology.isu.edu/Geothermal/References/Consultants/ODay_2008_Guyer_Hot_Spring.pdf | open | 2016 | most of the system was abandoned as fluoride contamination from a pipe failure occurred in the 80's, an unknown number of residences still use the undamaged portion | http://geology.isu.edu/Geothermal/References/Consultants/ODay_2008_Guyer_Hot_Spring.pdf
ID | Warm Springs Water District | Boise, ID |  | 1892 |  |  | 313600 | Site visit & interview 6-2020, Mattson and Neupane, 2017 |  | 176 | 80 | 1600 | 6064 |  | 12.3 | 107.748 | 3.6039 | 30 | 8.7899 | 31.62 | 0.27843 |  |  | Del Eytchison | OIT Geo-heat Center Database CD-2004 | [5 empty] | 43.607 | -116.1826 | Google Maps, help from http://bwswd.com/wp-content/uploads/2015/09/BWSWD_Map_2015.jpg | open | 2016 |  | http://bwswd.com/about-the-district/
NM | Gila Hot Springs Ranch | Gila Hot Springs, NM |  | 1987 |  |  | 7000 | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 165 | 73.8889 |  | 284 |  |  |  | 0.3 |  | 0.9 | 0.9 | 0.3 |  |  | Allen Campbell | OIT Geo-heat Center Database CD-2004 | [5 empty] | 33.1959 | -108.207 | Google Maps | open | 2015 |  | http://www.gilahotspringsranch.com/index.htm
NM | New Mexico State University* | Las Cruces, NM | 2003 | 1982 | [5 empty] | 142 | 61.1111 | 417 | 1580.43 |  | 7.5 | 65.7 | 2.1975 | 45.9 | 13.4486 | 48.3786 | 0.69863 |  |  |  | GEA, Benjamin Matek | [5 empty] | 32.2812 | -106.7513 | Google Maps | closed | 2016 | initial engineering design decisions | http://www.ourenergypolicy.org/wp-content/uploads/2011/11/2008_12_Elsevier_EnergyPolicy_Hildigunnur_Tester_BarriersEnablersGeopthermalDistrictHeatingSystemDevelopmentUS.pdf
NV | Elko County School District | Elko, NV |  | 1986 | 1500000 | 3270000 | 84000 | Mattson and Neupane, 2017 |  | 190 | 87.7778 | 950 | 3600.5 |  | 14.5 | 127.02 | 4.2485 | 15.7 | 4.6001 | 16.5478 | 0.1236 |  |  | Casey Kelly | OIT Geo-heat Center Database CD-2004 | [5 empty] | 40.8394 | -115.762 | Google Maps, help from pg. 1 http://www.energy.wsu.edu/Documents/3GeoHeat%20Bulletin_July04.pdf | open | 2016 |  | pg. 4: https://geothermal.org/PDFs/Final_Nevada.pdf
NV | Elko District Heat | Elko, NV |  | 1982 | 827000 | 2964000 | 75000 | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 175 | 79.4444 | 650 | 2463.5 | 869 | 13 | 113.88 | 3.809 | 22.2 | 6.5045 | 23.3988 | 0.19494 |  |  | Mike Lattin | OIT Geo-heat Center Database CD-2004 | [5 empty] | 40.8316 | -115.7634 | Google Maps, help from pg. 1 http://www.energy.wsu.edu/Documents/1GeoHeat%20Bulletin_July04.pdf | open | 2016 |  | pg. 4: https://geothermal.org/PDFs/Final_Nevada.pdf
NV | Manzanita Estates | Reno, NV |  | 1986 | 1400000 | 3360000 |  | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 212 | 100 | 600 | 2274 |  |  |  | 3.6 |  | 21.2 |  | 0.67 |  |  | Steve McKay | OIT Geo-heat Center Database CD-2004 | [5 empty] | 39.4742 | -119.837 | Google Maps | open | 2016 |  | http://nvgeothermal.com/ | heats 100 homes together with "Warren Estates" system, updated flow rate from 710 to 600 based on phone call with Steve McKay
NV | Warren Estates | Reno, NV |  | 1983 |  | tied to Manzanita |  | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 209 | 98.3333 | 600 | 2274 |  | 3.6 | 31.536 | 1.0548 | 7.9 | 2.3147 | 8.3266 | 0.25051 |  |  | Steve McKay | OIT Geo-heat Center Database CD-2004 | [5 empty] | 39.4886 | -119.8246 | Google Maps | open | 2016 |  | http://nvgeothermal.com/ http://citeseerx.ist.psu.edu/viewdoc/download?doi=10.1.1.544.2685&rep=rep1&type=pdf | heats 100 homes together with "Manzanita Estates" system, updated flow rate from 1000 to 600 based on phone call with Steve McKay
OR | City of Klamath Falls DH | Klamath Falls, OR |  | 1984 | 2801000 | 5394000 | 100800 | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 210 | 98.8889 | 1000 | 3790 |  | 16 | 140.16 | 4.688 | 35 | 10.2549 | 36.89 | 0.24971 |  |  | Scott Souders | Operator interview 7-2020 | City Engineer |  |  |  |  | 42.2254 | -121.7798 | Google Maps, help from map pg. 1: http://www.oit.edu/docs/default-source/geoheat-center-documents/publications/space-district-heating/tp125.pdf?sfvrsn=3 | open | 2016 |  | http://dspace.mit.edu/bitstream/handle/1721.1/42932/251518357-MIT.pdf;sequence=2
OR | Lakeview Prison | Lakeview, OR |  | 2005 | 1300000 | 1456000 | 47040 | Mattson and Neupane, 2017 | [6 empty] | 40 | 350.4 | 11.7199 | [6 empty] | Darryl Anderson
OR | Lakeview District Hospitals and Lakeview schools | Lakeview, OR |  | 2014 | 3837250 | 3837250 | 48521 | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 190 | 87.7778 |  | 946.3529 |  |  |  | 1.6 |  | 4.4 | 16.35 |  |  |  | Brian Brown | Boyd, 2015 | [5 empty] | 42.1813 | -120.3522 | Google Maps | open | 2016 |  | http://www.ourenergypolicy.org/wp-content/uploads/2011/11/2008_12_Elsevier_EnergyPolicy_Hildigunnur_Tester_BarriersEnablersGeopthermalDistrictHeatingSystemDevelopmentUS.pdf | Coordinates listed are for hospital, map of whole system was not found
OR | Oregon Institute of Technology | Klamath Falls, OR |  | 1964 |  |  | 22590 | Operator interview 7-2020, Mattson and Neupane, 2017 |  | 192 | 88.8889 | 745 | 2823.55 |  | 21.2 | 185.712 | 6.2115 | 46.6 | 13.6537 | 49.1164 | 0.25093 |  |  | Thom Darrah | OIT Geo-heat Center Database CD-2004 | [5 empty] | 42.2562 | -121.786 | Google Maps | open | 2016 |  | http://www.oit.edu/sustainability/clean-energy
SD | Midland District Heat | Midland, SD |  | 1969 |  |  | 2016 | Mattson and Neupane, 2017 |  | 152 | 66.6667 | 85 | 322.15 |  | 0.3 | 2.628 | 0.087899 | 0.8 | 0.2344 | 0.8432 | 0.30441 |  |  |  | OIT Geo-heat Center Database CD-2004 | [5 empty] | 44.0708 | -101.1603 | Google Maps, help from pg. 2 http://www.oit.edu/docs/default-source/geoheat-center-documents/quarterly-bulletin/vol-18/18-4/18-4-art5.pdf?sfvrsn=4 | open | 2016 |  | http://www.ourenergypolicy.org/wp-content/uploads/2011/11/2008_12_Elsevier_EnergyPolicy_Hildigunnur_Tester_BarriersEnablersGeopthermalDistrictHeatingSystemDevelopmentUS.pdf
SD | Philip District Heating | Philip, SD |  | 1980 | 1218884 |  | 20080 | Mattson and Neupane, 2017 |  | 155 | 68.3333 | 300 | 1137 |  | 8.4 | 73.584 | 2.4612 | 17.8 | 5.2154 | 18.7612 | 0.2419 |  |  |  | OIT Geo-heat Center Database CD-2004 | [5 empty] | 44.0394 | -101.6654 | Google Maps, help from pg. 1 http://www.oit.edu/docs/default-source/geoheat-center-documents/quarterly-bulletin/vol-24/24-2/24-2-art6.pdf?sfvrsn=4 | open | 2016 |  | http://www.ourenergypolicy.org/wp-content/uploads/2011/11/2008_12_Elsevier_EnergyPolicy_Hildigunnur_Tester_BarriersEnablersGeopthermalDistrictHeatingSystemDevelopmentUS.pdf

## Funding sources (WIP)
ABOUT | ABOUT | ABOUT | ECONOMIC | ECONOMIC | FEDERAL FUNDING SOURCE |  |  |  |  | STATE FUNDING SOURCE
State | Site | Year Opened | Original system cost | 2020 Updated capital cost | USDA loan | USDOE loan | USDOE grant | HUD grant | Other federal grants | State Grant | State Business Energy Tax Credit Program | State Loan | Total grant amount | Notes
CA | San Bernardino District Heating | 1984 | 6000000 | 13800000 |  |  | 60000 |  |  | 1959895 |  |  | 2019895 | One grant from DOE for site characteristics study, two grants from California Energy Commission - $60,000 and $400,000 - for economic study and installation, respectively, and final $2.75 million grant from the CEC
CA | Susanville District Heating | 1982 | 2400000 | 3329822 |  |  | 2039499 | 820000 |  | 1028110 |  | 59000 | 3887609 | State grants came from California Energy Commission
CA | Canby/I'SOT District Heating System | 2003 | 1400000 | 1568000 |  |  | 204000 |  | 307000 | 304500 |  |  | 815500 | Source: https://www.energy.gov/sites/prod/files/2014/02/f7/canby_cascaded_peer2013.pdf
CA | Modoc joint unified school district (Alturas) | 2017 | 4963448 | 4963448 | [5 empty] | 4786295 |  |  | 4786295 | Source: Anderson Engineering (email) "Modoc unified school district covered the rest of the cost - $992,689"
CO | Pagosa Springs District Heating | 1982 | 1364000 | 3458000 |  | 1213000 |  |  | 274620 |  |  |  | 274620 | Sources listed in Rachel Rubin's documentation
ID | Boise City District Heating | 1983 | 7128000 |  |  |  | 4470000 |  | 355000 |  |  |  | 4825000 | Source: email communication with Doug Lamb
ID | College of Southern Idaho | 1980
ID | Fort Boise Veteran's Hospital | 1988 | 7500000 | 14775000 |  |  |  |  | 7500000 |  |  |  | 7500000 | Doug Lamb email: "Federally funded by the Department of Veteran's Affairs"
ID | Idaho Capitol Mall | 1982 | 1800000 | 4446000
ID | Kanaka Rapids Ranch | 1989
ID | Ketchum District Heating | 1929
ID | Warm Springs Water District | 1892
NM | Gila Hot Springs Ranch | 1987
NM | New Mexico State University* | 1982 | [7 empty] | x |  |  |  | Design and construction($?) funded by the New Mexico State Legislature
NV | Elko County School District | 1986 | 1500000 | 3270000 | [9 empty] | Source: GHG Bulletin August 1997
NV | Elko District Heat | 1982 | 827000 | 2964000 |  |  | 250000 | [5 empty] | 250000 | Sources listed in Rachel Rubin's documentation
NV | Manzanita Estates | 1986 | 1400000 | 3360000 |  |  | 827000 | [5 empty] | 827000
NV | Warren Estates | 1983 |  | tied to Manzanita | [9 empty] | Lund, 1979 states that the federal government funded 80% of the approx. $2 million costs and that the rest would come from "city, county, and state funds"
OR | City of Klamath Falls DH | 1984 | 2801000 | 5394000
OR | Lakeview Prison | 2005 | 1300000 | 1456000 |  |  | 1600000 | 300000 |  | 400000 |  |  | 2300000 | Sources listed in Rachel Rubin's documentation
OR | Lakeview District Hospitals and Lakeview schools | 2014 | 3837250 | 3837250 | 2665000 | [5 empty] | 900000 |  |  | https://www.rd.usda.gov/newsroom/news-release/clean-geothermal-heating-lakeview-oregon-community-buildings-keeping-energy
OR | Oregon Institute of Technology | 1964 | [5 empty] | 200000 |  |  |  |  | 200000 | Source: https://urbanecologycmu.wordpress.com/2016/11/01/geothermal-energy-oregon-institute-of-technology/
SD | Midland District Heat | 1969 |  |  |  |  | 4500000 |  | 3000000 | 2400000 |  | 6000000 | 9900000 | Sources listed in Rachel Rubin's documentation
SD | Philip District Heating | 1980 | 1218884 |  |  |  | 938540 | [5 empty] | 938540 | Source: Geothermal District Heating System, Philip, South Dakota, GHC Bulletin June 2003, Vol 24, No. 2