## Minneapolis
| Property | Soil |  |  |  |  | Property | Soil
| Thermal conductivity [W/m K] | 1.72 |  | W/M-K | 0.57779 | BTU/HR-FT-R | Thermal conductivity [Btu/Hr-ft-R] | 0.99379
| Specific heat [J/kg K] | 1900
| Density [kg/m3] | 1300
| Volumeric specific heat [MJ/K-M3] | 2.47
| Thermal diffusivity [m2/hr] | 0.0025069 |  | m2/hr | 10.7639 | ft2/hr | Thermal diffusivity [ft2/hr] | 0.026984
VBGHE design and performance
| Borehole number | 2
| Borehole depth | 280 | ft | 85 | m
| Annual Max. LFT | 70 | F
| Annual Min. LFT | 29.5 | F
Time | Thermal load | Fluid flow | Outlet temperature | Far field ground temperature | Load
| Btu/hr | GPM | F | F | W
2020-01-01 | -12624.5 | 6.6648 | 42.0259 | 48.4627 | -3699.8757
2020-01-02 01:00 | -12181.4 | 6.6648 | 41.01 | 48.4627 | -3570.0159
2020-01-03 02:00 | -12445.7 | 6.6648 | 40.1945 | 48.4627 | -3647.4746
2020-01-04 03:00 | -12463.4 | 6.6648 | 39.7713 | 48.4627 | -3652.662
2020-01-05 04:00 | -12458.8 | 6.6648 | 39.3582 | 48.4627 | -3651.3138
2020-01-06 05:00 | -12552.4 | 6.6648 | 38.9024 | 48.4627 | -3678.7453
2020-01-07 06:00 | -12507 | 6.6648 | 38.7152 | 48.4627 | -3665.4399
2020-01-08 07:00 | -12135.4 | 6.6648 | 38.6962 | 48.4627 | -3556.5347
2020-01-09 08:00 | -11500.5 | 6.6648 | 38.8538 | 48.4627 | -3370.4638
2020-01-10 09:00 | -11674 | 6.6648 | 38.6445 | 48.4627 | -3421.3117
2020-01-11 10:00 | -11448.2 | 6.6648 | 38.586 | 48.4627 | -3355.1362
2020-01-12 11:00 | -11196.4 | 6.6648 | 38.5565 | 48.4627 | -3281.3409
2020-01-13 12:00 | -10665.8 | 6.6648 | 38.792 | 48.4627 | -3125.8374
2020-01-14 13:00 | -10408.2 | 6.6648 | 38.9148 | 48.4627 | -3050.3423
2020-01-15 14:00 | -10013.9 | 6.6648 | 39.0963 | 48.4627 | -2934.7844
2020-01-16 15:00 | -9830.98 | 6.6648 | 39.1879 | 48.4627 | -2881.1758
2020-01-17 16:00 | -9486.08 | 6.6648 | 39.3538 | 48.4627 | -2780.0956
2020-01-18 17:00 | -7828.98 | 6.6648 | 40.2038 | 48.4627 | -2294.4475
2020-01-19 18:00 | -7668.56 | 6.6648 | 40.4251 | 48.4627 | -2247.4331
2020-01-20 19:00 | -8212.78 | 6.6648 | 40.2173 | 48.4627 | -2406.9282
2020-01-21 20:00 | -8549.93 | 6.6648 | 40.002 | 48.4627 | -2505.7371
2020-01-22 21:00 | -8544.27 | 6.6648 | 39.9456 | 48.4627 | -2504.0784
2020-01-23 22:00 | -9031.4 | 6.6648 | 39.6581 | 48.4627 | -2646.8421
2020-01-24 23:00 | -9103.02 | 6.6648 | 39.5133 | 48.4627 | -2667.8318
2020-01-26 | -10550.3 | 6.6648 | 38.7232 | 48.4627 | -3091.9877
2020-01-27 01:00 | -10767.6 | 6.6648 | 38.4373 | 48.4627 | -3155.6721
2020-01-28 02:00 | -10815.7 | 6.6648 | 38.2828 | 48.4627 | -3169.7688
2020-01-29 03:00 | -11273.9 | 6.6648 | 37.957 | 48.4627 | -3304.0539
2020-01-30 04:00 | -11185.8 | 6.6648 | 37.8775 | 48.4627 | -3278.2344
2020-01-31 05:00 | -10882.2 | 6.6648 | 37.9259 | 48.4627 | -3189.258
2020-02-01 06:00 | -10307 | 6.6648 | 38.1733 | 48.4627 | -3020.6835
2020-02-02 07:00 | -10163.1 | 6.6648 | 38.2488 | 48.4627 | -2978.5106
2020-02-03 08:00 | -10247.2 | 6.6648 | 38.191 | 48.4627 | -3003.1579
2020-02-04 09:00 | -9554.65 | 6.6648 | 38.5101 | 48.4627 | -2800.1915
2020-02-05 10:00 | -8623.37 | 6.6648 | 39.0217 | 48.4627 | -2527.2603
2020-02-06 11:00 | -8725.85 | 6.6648 | 39.0647 | 48.4627 | -2557.2942
2020-02-07 12:00 | -7598.14 | 6.6648 | 39.6703 | 48.4627 | -2226.795
2020-02-08 13:00 | -8453.99 | 6.6648 | 39.3537 | 48.4627 | -2477.6199
2020-02-09 14:00 | -8330.29 | 6.6648 | 39.4081 | 48.4627 | -2441.367
2020-02-10 15:00 | -8306.83 | 6.6648 | 39.4234 | 48.4627 | -2434.4916
2020-02-11 16:00 | -7456.4 | 6.6648 | 39.8622 | 48.4627 | -2185.2551
2020-02-12 17:00 | -6957.7 | 6.6648 | 40.1938 | 48.4627 | -2039.1006
2020-02-13 18:00 | -7163.12 | 6.6648 | 40.1553 | 48.4627 | -2099.3032
2020-02-14 19:00 | -7627.47 | 6.6648 | 39.9374 | 48.4627 | -2235.3908
2020-02-15 20:00 | -8424.73 | 6.6648 | 39.4996 | 48.4627 | -2469.0446
2020-02-16 21:00 | -9216.66 | 6.6648 | 39.0037 | 48.4627 | -2701.1364
2020-02-17 22:00 | -10384.8 | 6.6648 | 38.2617 | 48.4627 | -3043.4844
2020-02-18 23:00 | -11818.1 | 6.6648 | 37.3129 | 48.4627 | -3463.5432
2020-02-20 | -12118.9 | 6.6648 | 36.8948 | 48.4627 | -3551.699
2020-02-21 01:00 | -12362.6 | 6.6648 | 36.5804 | 48.4627 | -3623.1204
2020-02-22 02:00 | -12517.9 | 6.6648 | 36.348 | 48.4627 | -3668.6343
2020-02-23 03:00 | -12801.8 | 6.6648 | 36.0665 | 48.4627 | -3751.8372
2020-02-24 04:00 | -12995.4 | 6.6648 | 35.8273 | 48.4627 | -3808.5758
2020-02-25 05:00 | -13104.4 | 6.6648 | 35.6463 | 48.4627 | -3840.5205
2020-02-26 06:00 | -12971.3 | 6.6648 | 35.5981 | 48.4627 | -3801.5128
2020-02-27 07:00 | -12876.5 | 6.6648 | 35.5596 | 48.4627 | -3773.7296
2020-02-28 08:00 | -12935.4 | 6.6648 | 35.4568 | 48.4627 | -3790.9915
2020-02-29 09:00 | -12559.2 | 6.6648 | 35.5726 | 48.4627 | -3680.7382
2020-03-01 10:00 | -11271.8 | 6.6648 | 36.2022 | 48.4627 | -3303.4385
2020-03-02 11:00 | -10024.8 | 6.6648 | 36.9382 | 48.4627 | -2937.9789
2020-03-03 12:00 | -8819.38 | 6.6648 | 37.7072 | 48.4627 | -2584.7051
2020-03-04 13:00 | -8745.77 | 6.6648 | 37.9352 | 48.4627 | -2563.1322
2020-03-05 14:00 | -8550.11 | 6.6648 | 38.1523 | 48.4627 | -2505.7899
2020-03-06 15:00 | -9219.66 | 6.6648 | 37.9091 | 48.4627 | -2702.0156
2020-03-07 16:00 | -10106.3 | 6.6648 | 37.4544 | 48.4627 | -2961.8642
2020-03-08 17:00 | -10471.6 | 6.6648 | 37.1763 | 48.4627 | -3068.923
2020-03-09 18:00 | -10699.8 | 6.6648 | 36.9657 | 48.4627 | -3135.8018
2020-03-10 19:00 | -11202.9 | 6.6648 | 36.63 | 48.4627 | -3283.2459
2020-03-11 20:00 | -11571 | 6.6648 | 36.3329 | 48.4627 | -3391.1254
2020-03-12 21:00 | -12166.1 | 6.6648 | 35.9206 | 48.4627 | -3565.5319
2020-03-13 22:00 | -12600.9 | 6.6648 | 35.5686 | 48.4627 | -3692.9592
2020-03-14 23:00 | -12996.5 | 6.6648 | 35.2293 | 48.4627 | -3808.8982
2020-03-16 | -13235 | 6.6648 | 34.9622 | 48.4627 | -3878.7956
2020-03-17 01:00 | -13356.7 | 6.6648 | 34.7679 | 48.4627 | -3914.4624
2020-03-18 02:00 | -13548.6 | 6.6648 | 34.5506 | 48.4627 | -3970.7027
2020-03-19 03:00 | -13727.5 | 6.6648 | 34.349 | 48.4627 | -4023.1331
2020-03-20 04:00 | -13947.1 | 6.6648 | 34.1348 | 48.4627 | -4087.4915
2020-03-21 05:00 | -14118.9 | 6.6648 | 33.9416 | 48.4627 | -4137.8411
2020-03-22 06:00 | -13916.1 | 6.6648 | 33.9445 | 48.4627 | -4078.4063
2020-03-23 07:00 | -13854.4 | 6.6648 | 33.914 | 48.4627 | -4060.3238
2020-03-24 08:00 | -13842.2 | 6.6648 | 33.8662 | 48.4627 | -4056.7484
2020-03-25 09:00 | -13743.4 | 6.6648 | 33.8613 | 48.4627 | -4027.7929
2020-03-26 10:00 | -13553.3 | 6.6648 | 33.9114 | 48.4627 | -3972.0801
2020-03-27 11:00 | -13215.1 | 6.6648 | 34.0533 | 48.4627 | -3872.9635
2020-03-28 12:00 | -12934.8 | 6.6648 | 34.1831 | 48.4627 | -3790.8157
2020-03-29 13:00 | -12697.6 | 6.6648 | 34.2981 | 48.4627 | -3721.2992
2020-03-30 14:00 | -12292.2 | 6.6648 | 34.5031 | 48.4627 | -3602.4882
2020-03-31 15:00 | -12462.4 | 6.6648 | 34.4388 | 48.4627 | -3652.3689
2020-04-01 16:00 | -12554.1 | 6.6648 | 34.3748 | 48.4627 | -3679.2435
2020-04-02 17:00 | -12388.8 | 6.6648 | 34.4272 | 48.4627 | -3630.7989
2020-04-03 18:00 | -12507.1 | 6.6648 | 34.3539 | 48.4627 | -3665.4692
2020-04-04 19:00 | -12711 | 6.6648 | 34.2185 | 48.4627 | -3725.2264
2020-04-05 20:00 | -13099.7 | 6.6648 | 33.965 | 48.4627 | -3839.1431
2020-04-06 21:00 | -13609.7 | 6.6648 | 33.6246 | 48.4627 | -3988.6093
2020-04-07 22:00 | -13865.8 | 6.6648 | 33.3915 | 48.4627 | -4063.6648
2020-04-08 23:00 | -14169.3 | 6.6648 | 33.1392 | 48.4627 | -4152.6119
2020-04-10 | -14613.9 | 6.6648 | 32.8214 | 48.4627 | -4282.9113
2020-04-11 01:00 | -14839.8 | 6.6648 | 32.5923 | 48.4627 | -4349.1161
2020-04-12 02:00 | -15091.3 | 6.6648 | 32.3587 | 48.4627 | -4422.8234
2020-04-13 03:00 | -15379.3 | 6.6648 | 32.1126 | 48.4627 | -4507.2279
2020-04-14 04:00 | -15552.1 | 6.6648 | 31.9195 | 48.4627 | -4557.8706
2020-04-15 05:00 | -15638.2 | 6.6648 | 31.7771 | 48.4627 | -4583.104
2020-04-16 06:00 | -15519.3 | 6.6648 | 31.7536 | 48.4627 | -4548.2579
2020-04-17 07:00 | -15422.8 | 6.6648 | 31.7436 | 48.4627 | -4519.9765
2020-04-18 08:00 | -15532.8 | 6.6648 | 31.6406 | 48.4627 | -4552.2143
2020-04-19 09:00 | -14961.4 | 6.6648 | 31.8783 | 48.4627 | -4384.7535
2020-04-20 10:00 | -14025.7 | 6.6648 | 32.3661 | 48.4627 | -4110.5269
2020-04-21 11:00 | -13455.3 | 6.6648 | 32.738 | 48.4627 | -3943.3592
2020-04-22 12:00 | -12940.4 | 6.6648 | 33.0807 | 48.4627 | -3792.4569
2020-04-23 13:00 | -12748.4 | 6.6648 | 33.26 | 48.4627 | -3736.1872
2020-04-24 14:00 | -13074.3 | 6.6648 | 33.1569 | 48.4627 | -3831.6991
2020-04-25 15:00 | -13490.4 | 6.6648 | 32.9478 | 48.4627 | -3953.646
2020-04-26 16:00 | -13856.3 | 6.6648 | 32.7196 | 48.4627 | -4060.8807
2020-04-27 17:00 | -14133.9 | 6.6648 | 32.5156 | 48.4627 | -4142.2372
2020-04-28 18:00 | -14118.8 | 6.6648 | 32.452 | 48.4627 | -4137.8118
2020-04-29 19:00 | -14173.4 | 6.6648 | 32.3739 | 48.4627 | -4153.8135
2020-04-30 20:00 | -14424 | 6.6648 | 32.2044 | 48.4627 | -4227.2571
2020-05-01 21:00 | -14838.1 | 6.6648 | 31.9325 | 48.4627 | -4348.6178
2020-05-02 22:00 | -15236.7 | 6.6648 | 31.6393 | 48.4627 | -4465.436
2020-05-03 23:00 | -15533.5 | 6.6648 | 31.3842 | 48.4627 | -4552.4195
2020-05-05 | -15768.9 | 6.6648 | 31.1578 | 48.4627 | -4621.4084
2020-05-06 01:00 | -15915.7 | 6.6648 | 30.9768 | 48.4627 | -4664.4312
2020-05-07 02:00 | -15942.8 | 6.6648 | 30.8688 | 48.4627 | -4672.3735
2020-05-08 03:00 | -15880.4 | 6.6648 | 30.8291 | 48.4627 | -4654.0858
2020-05-09 04:00 | -15940.2 | 6.6648 | 30.7482 | 48.4627 | -4671.6115
2020-05-10 05:00 | -15884.9 | 6.6648 | 30.726 | 48.4627 | -4655.4046
2020-05-11 06:00 | -15772 | 6.6648 | 30.7427 | 48.4627 | -4622.3169
2020-05-12 07:00 | -15506.7 | 6.6648 | 30.8508 | 48.4627 | -4544.5652
2020-05-13 08:00 | -15155.4 | 6.6648 | 31.0273 | 48.4627 | -4441.6093
2020-05-14 09:00 | -14606.6 | 6.6648 | 31.326 | 48.4627 | -4280.7719
2020-05-15 10:00 | -14064.2 | 6.6648 | 31.6543 | 48.4627 | -4121.8101
2020-05-16 11:00 | -14061.6 | 6.6648 | 31.7249 | 48.4627 | -4121.0482
2020-05-17 12:00 | -13494.6 | 6.6648 | 32.0448 | 48.4627 | -3954.8769
2020-05-18 13:00 | -13305.1 | 6.6648 | 32.2111 | 48.4627 | -3899.3399
2020-05-19 14:00 | -13677.3 | 6.6648 | 32.0768 | 48.4627 | -4008.4209
2020-05-20 15:00 | -13395 | 6.6648 | 32.2116 | 48.4627 | -3925.687
2020-05-21 16:00 | -13293 | 6.6648 | 32.2867 | 48.4627 | -3895.7937
2020-05-22 17:00 | -12910.3 | 6.6648 | 32.5132 | 48.4627 | -3783.6354
2020-05-23 18:00 | -12687.2 | 6.6648 | 32.6751 | 48.4627 | -3718.2513
2020-05-24 19:00 | -13083.8 | 6.6648 | 32.517 | 48.4627 | -3834.4833
2020-05-25 20:00 | -13156.2 | 6.6648 | 32.4719 | 48.4627 | -3855.7016
2020-05-26 21:00 | -13192.6 | 6.6648 | 32.4445 | 48.4627 | -3866.3694
2020-05-27 22:00 | -13368.4 | 6.6648 | 32.3518 | 48.4627 | -3917.8913
2020-05-28 23:00 | -13487.4 | 6.6648 | 32.2708 | 48.4627 | -3952.7667
2020-05-30 | -14036.8 | 6.6648 | 31.9586 | 48.4627 | -4113.78
2020-05-31 01:00 | -14428 | 6.6648 | 31.6874 | 48.4627 | -4228.4294
2020-06-01 02:00 | -14450.8 | 6.6648 | 31.5984 | 48.4627 | -4235.1114
2020-06-02 03:00 | -14572.4 | 6.6648 | 31.4862 | 48.4627 | -4270.7489
2020-06-03 04:00 | -14647.5 | 6.6648 | 31.3992 | 48.4627 | -4292.7585
2020-06-04 05:00 | -14625.1 | 6.6648 | 31.3596 | 48.4627 | -4286.1937
2020-06-05 06:00 | -14536.2 | 6.6648 | 31.3694 | 48.4627 | -4260.1397
2020-06-06 07:00 | -14331.9 | 6.6648 | 31.457 | 48.4627 | -4200.2653
2020-06-07 08:00 | -13836.8 | 6.6648 | 31.7107 | 48.4627 | -4055.1658
2020-06-08 09:00 | -13256 | 6.6648 | 32.0464 | 48.4627 | -3884.9501
2020-06-09 10:00 | -12410.6 | 6.6648 | 32.5473 | 48.4627 | -3637.1878
2020-06-10 11:00 | -10958.3 | 6.6648 | 33.4061 | 48.4627 | -3211.5607
2020-06-11 12:00 | -9907.34 | 6.6648 | 34.1531 | 48.4627 | -2903.5547
2020-06-12 13:00 | -9406.23 | 6.6648 | 34.6348 | 48.4627 | -2756.6939
2020-06-13 14:00 | -9343.04 | 6.6648 | 34.8551 | 48.4627 | -2738.1747
2020-06-14 15:00 | -9135.36 | 6.6648 | 35.1003 | 48.4627 | -2677.3097
2020-06-15 16:00 | -10830.9 | 6.6648 | 34.3634 | 48.4627 | -3174.2235
2020-06-16 17:00 | -10158.6 | 6.6648 | 34.6359 | 48.4627 | -2977.1918
2020-06-17 18:00 | -10780.6 | 6.6648 | 34.3605 | 48.4627 | -3159.482
2020-06-18 19:00 | -11123.5 | 6.6648 | 34.1714 | 48.4627 | -3259.976
2020-06-19 20:00 | -11590.2 | 6.6648 | 33.8905 | 48.4627 | -3396.7523
2020-06-20 21:00 | -11797.5 | 6.6648 | 33.7192 | 48.4627 | -3457.5059
2020-06-21 22:00 | -11946.2 | 6.6648 | 33.606 | 48.4627 | -3501.0856
2020-06-22 23:00 | -12137.4 | 6.6648 | 33.4574 | 48.4627 | -3557.1208
2020-06-24 | -12584.2 | 6.6648 | 33.1743 | 48.4627 | -3688.065
2020-06-25 01:00 | -12908.7 | 6.6648 | 32.9241 | 48.4627 | -3783.1665
2020-06-26 02:00 | -13074.7 | 6.6648 | 32.7543 | 48.4627 | -3831.8163
2020-06-27 03:00 | -13292.6 | 6.6648 | 32.5685 | 48.4627 | -3895.6765
2020-06-28 04:00 | -13266.8 | 6.6648 | 32.5183 | 48.4627 | -3888.1153
2020-06-29 05:00 | -13317.6 | 6.6648 | 32.4427 | 48.4627 | -3903.0033
2020-06-30 06:00 | -13011.9 | 6.6648 | 32.5614 | 48.4627 | -3813.4115
2020-07-01 07:00 | -12733.5 | 6.6648 | 32.7054 | 48.4627 | -3731.8205
2020-07-02 08:00 | -12701.5 | 6.6648 | 32.7424 | 48.4627 | -3722.4422
2020-07-03 09:00 | -12673.7 | 6.6648 | 32.7623 | 48.4627 | -3714.2948
2020-07-04 10:00 | -12660 | 6.6648 | 32.7656 | 48.4627 | -3710.2797
2020-07-05 11:00 | -12019.7 | 6.6648 | 33.0866 | 48.4627 | -3522.6263
2020-07-06 12:00 | -10771.3 | 6.6648 | 33.7767 | 48.4627 | -3156.7564
2020-07-07 13:00 | -11227.3 | 6.6648 | 33.6859 | 48.4627 | -3290.3968
2020-07-08 14:00 | -11551.4 | 6.6648 | 33.5431 | 48.4627 | -3385.3812
2020-07-09 15:00 | -10926.3 | 6.6648 | 33.8465 | 48.4627 | -3202.1824
2020-07-10 16:00 | -10695.1 | 6.6648 | 34.0444 | 48.4627 | -3134.4244
2020-07-11 17:00 | -10951.9 | 6.6648 | 33.98 | 48.4627 | -3209.6851
2020-07-12 18:00 | -10820.8 | 6.6648 | 34.0427 | 48.4627 | -3171.2634
2020-07-13 19:00 | -11049.9 | 6.6648 | 33.9467 | 48.4627 | -3238.406
2020-07-14 20:00 | -11307.7 | 6.6648 | 33.8211 | 48.4627 | -3313.9597
2020-07-15 21:00 | -12056.9 | 6.6648 | 33.4122 | 48.4627 | -3533.5286
2020-07-16 22:00 | -12251.6 | 6.6648 | 33.2286 | 48.4627 | -3590.5895
2020-07-17 23:00 | -12508.4 | 6.6648 | 33.0329 | 48.4627 | -3665.8502
2020-07-19 | -12754 | 6.6648 | 32.8413 | 48.4627 | -3737.8284
2020-07-20 01:00 | -12750.2 | 6.6648 | 32.7788 | 48.4627 | -3736.7148
2020-07-21 02:00 | -12744 | 6.6648 | 32.7432 | 48.4627 | -3734.8977
2020-07-22 03:00 | -12794 | 6.6648 | 32.6938 | 48.4627 | -3749.5513
2020-07-23 04:00 | -12649.6 | 6.6648 | 32.7405 | 48.4627 | -3707.2318
2020-07-24 05:00 | -12555.8 | 6.6648 | 32.7845 | 48.4627 | -3679.7417
2020-07-25 06:00 | -12359.2 | 6.6648 | 32.8872 | 48.4627 | -3622.124
2020-07-26 07:00 | -12146.2 | 6.6648 | 33.0106 | 48.4627 | -3559.6998
2020-07-27 08:00 | -12189.3 | 6.6648 | 33.0134 | 48.4627 | -3572.3312
2020-07-28 09:00 | -11784.9 | 6.6648 | 33.2331 | 48.4627 | -3453.8133
2020-07-29 10:00 | -11113.5 | 6.6648 | 33.6238 | 48.4627 | -3257.0453
2020-07-30 11:00 | -9925.44 | 6.6648 | 34.3272 | 48.4627 | -2908.8593
2020-07-31 12:00 | -8531.5 | 6.6648 | 35.2037 | 48.4627 | -2500.3358
2020-08-01 13:00 | -8654.26 | 6.6648 | 35.3708 | 48.4627 | -2536.3132
2020-08-02 14:00 | -8086.1 | 6.6648 | 35.7934 | 48.4627 | -2369.802
2020-08-03 15:00 | -8292.9 | 6.6648 | 35.8374 | 48.4627 | -2430.4091
2020-08-04 16:00 | -8520.02 | 6.6648 | 35.82 | 48.4627 | -2496.9714
2020-08-05 17:00 | -9076.9 | 6.6648 | 35.5846 | 48.4627 | -2660.1768
2020-08-06 18:00 | -9033.18 | 6.6648 | 35.5923 | 48.4627 | -2647.3637
2020-08-07 19:00 | -9516.96 | 6.6648 | 35.3655 | 48.4627 | -2789.1457
2020-08-08 20:00 | -9796.45 | 6.6648 | 35.2005 | 48.4627 | -2871.0561
2020-08-09 21:00 | -10736 | 6.6648 | 34.6924 | 48.4627 | -3146.411
2020-08-10 22:00 | -11056.2 | 6.6648 | 34.4314 | 48.4627 | -3240.2524
2020-08-11 23:00 | -11747.4 | 6.6648 | 33.9962 | 48.4627 | -3442.8231
2020-08-13 | -11942 | 6.6648 | 33.7739 | 48.4627 | -3499.8547
2020-08-14 01:00 | -11968 | 6.6648 | 33.6636 | 48.4627 | -3507.4746
2020-08-15 02:00 | -11881.5 | 6.6648 | 33.6368 | 48.4627 | -3482.1239
2020-08-16 03:00 | -11944.9 | 6.6648 | 33.5656 | 48.4627 | -3500.7046
2020-08-17 04:00 | -11783.6 | 6.6648 | 33.6068 | 48.4627 | -3453.4323
2020-08-18 05:00 | -11418 | 6.6648 | 33.7854 | 48.4627 | -3346.2855
2020-08-19 06:00 | -10912.6 | 6.6648 | 34.0704 | 48.4627 | -3198.1674
2020-08-20 07:00 | -10868.8 | 6.6648 | 34.1494 | 48.4627 | -3185.3308
2020-08-21 08:00 | -9690.2 | 6.6648 | 34.7852 | 48.4627 | -2839.9173
2020-08-22 09:00 | -9288.66 | 6.6648 | 35.1317 | 48.4627 | -2722.2375
2020-08-23 10:00 | -8116.52 | 6.6648 | 35.858 | 48.4627 | -2378.7172
2020-08-24 11:00 | -7341.8 | 6.6648 | 36.4443 | 48.4627 | -2151.6692
2020-08-25 12:00 | -6835.55 | 6.6648 | 36.8944 | 48.4627 | -2003.302
2020-08-26 13:00 | -6268.42 | 6.6648 | 37.3655 | 48.4627 | -1837.0926
2020-08-27 14:00 | -6309.16 | 6.6648 | 37.5201 | 48.4627 | -1849.0323
2020-08-28 15:00 | -6750.48 | 6.6648 | 37.4229 | 48.4627 | -1978.3704
2020-08-29 16:00 | -7181.8 | 6.6648 | 37.2541 | 48.4627 | -2104.7778
2020-08-30 17:00 | -7498.65 | 6.6648 | 37.1071 | 48.4627 | -2197.6374
2020-08-31 18:00 | -7746.87 | 6.6648 | 36.9797 | 48.4627 | -2270.3835
2020-09-01 19:00 | -8455.93 | 6.6648 | 36.6091 | 48.4627 | -2478.1885
2020-09-02 20:00 | -8607.76 | 6.6648 | 36.4646 | 48.4627 | -2522.6854
2020-09-03 21:00 | -9590.97 | 6.6648 | 35.9249 | 48.4627 | -2810.8358
2020-09-04 22:00 | -9742.38 | 6.6648 | 35.7368 | 48.4627 | -2855.2097
2020-09-05 23:00 | -10574 | 6.6648 | 35.2335 | 48.4627 | -3098.9335
2020-09-07 | -10688 | 6.6648 | 35.0473 | 48.4627 | -3132.3436
2020-09-08 01:00 | -10717.2 | 6.6648 | 34.94 | 48.4627 | -3140.9013
2020-09-09 02:00 | -10836.1 | 6.6648 | 34.8118 | 48.4627 | -3175.7474
2020-09-10 03:00 | -10727.4 | 6.6648 | 34.8128 | 48.4627 | -3143.8906
2020-09-11 04:00 | -10655.4 | 6.6648 | 34.8169 | 48.4627 | -3122.7895
2020-09-12 05:00 | -10489.7 | 6.6648 | 34.8891 | 48.4627 | -3074.2276
2020-09-13 06:00 | -10071.6 | 6.6648 | 35.1029 | 48.4627 | -2951.6946
2020-09-14 07:00 | -10011.9 | 6.6648 | 35.1712 | 48.4627 | -2934.1982
2020-09-15 08:00 | -9067.77 | 6.6648 | 35.675 | 48.4627 | -2657.5011
2020-09-16 09:00 | -8805.21 | 6.6648 | 35.9136 | 48.4627 | -2580.5523
2020-09-17 10:00 | -7198.48 | 6.6648 | 36.8178 | 48.4627 | -2109.6662
2020-09-18 11:00 | -5977.48 | 6.6648 | 37.6451 | 48.4627 | -1751.8265
2020-09-19 12:00 | -5178.86 | 6.6648 | 38.2905 | 48.4627 | -1517.774
2020-09-20 13:00 | -4662.01 | 6.6648 | 38.7766 | 48.4627 | -1366.3003
2020-09-21 14:00 | -4664.22 | 6.6648 | 38.9697 | 48.4627 | -1366.9479
2020-09-22 15:00 | -5205.54 | 6.6648 | 38.8432 | 48.4627 | -1525.5932
2020-09-23 16:00 | -5699.7 | 6.6648 | 38.6522 | 48.4627 | -1670.4172
2020-09-24 17:00 | -6268.09 | 6.6648 | 38.3776 | 48.4627 | -1836.9958
2020-09-25 18:00 | -6613.85 | 6.6648 | 38.1795 | 48.4627 | -1938.3281
2020-09-26 19:00 | -7161.31 | 6.6648 | 37.8755 | 48.4627 | -2098.7728
2020-09-27 20:00 | -7992.1 | 6.6648 | 37.3947 | 48.4627 | -2342.2533
2020-09-28 21:00 | -8957.11 | 6.6648 | 36.8071 | 48.4627 | -2625.0698
2020-09-29 22:00 | -9405.81 | 6.6648 | 36.4324 | 48.4627 | -2756.5708
2020-09-30 23:00 | -10097.6 | 6.6648 | 35.954 | 48.4627 | -2959.3144
2020-10-02 | -10313.8 | 6.6648 | 35.6935 | 48.4627 | -3022.6764
2020-10-03 01:00 | -10875.4 | 6.6648 | 35.2801 | 48.4627 | -3187.2651
2020-10-04 02:00 | -11229.5 | 6.6648 | 34.9571 | 48.4627 | -3291.0416
2020-10-05 03:00 | -11149.5 | 6.6648 | 34.8709 | 48.4627 | -3267.5959
2020-10-06 04:00 | -11279.9 | 6.6648 | 34.7246 | 48.4627 | -3305.8124
2020-10-07 05:00 | -11333.8 | 6.6648 | 34.6245 | 48.4627 | -3321.6089
2020-10-08 06:00 | -11223.2 | 6.6648 | 34.6102 | 48.4627 | -3289.1952
2020-10-09 07:00 | -11271.8 | 6.6648 | 34.5439 | 48.4627 | -3303.4385
2020-10-10 08:00 | -10426.7 | 6.6648 | 34.9342 | 48.4627 | -3055.7641
2020-10-11 09:00 | -9952.21 | 6.6648 | 35.2229 | 48.4627 | -2916.7048
2020-10-12 10:00 | -8431.83 | 6.6648 | 36.0568 | 48.4627 | -2471.1254
2020-10-13 11:00 | -7715.23 | 6.6648 | 36.5879 | 48.4627 | -2261.1107
2020-10-14 12:00 | -8621.98 | 6.6648 | 36.2772 | 48.4627 | -2526.8529
2020-10-15 13:00 | -8727.39 | 6.6648 | 36.2213 | 48.4627 | -2557.7455
2020-10-16 14:00 | -8701.6 | 6.6648 | 36.2319 | 48.4627 | -2550.1872
2020-10-17 15:00 | -8843.92 | 6.6648 | 36.18 | 48.4627 | -2591.8971
2020-10-18 16:00 | -8153.41 | 6.6648 | 36.521 | 48.4627 | -2389.5286
2020-10-19 17:00 | -8248.5 | 6.6648 | 36.5256 | 48.4627 | -2417.3967
2020-10-20 18:00 | -7977.36 | 6.6648 | 36.6983 | 48.4627 | -2337.9334
2020-10-21 19:00 | -7917.5 | 6.6648 | 36.783 | 48.4627 | -2320.3902
2020-10-22 20:00 | -8129.1 | 6.6648 | 36.7224 | 48.4627 | -2382.404
2020-10-23 21:00 | -8986.13 | 6.6648 | 36.3065 | 48.4627 | -2633.5747
2020-10-24 22:00 | -9240.7 | 6.6648 | 36.0998 | 48.4627 | -2708.1818
2020-10-25 23:00 | -9914.73 | 6.6648 | 35.6949 | 48.4627 | -2905.7205
2020-10-27 | -10428.8 | 6.6648 | 35.3409 | 48.4627 | -3056.3796
2020-10-28 01:00 | -10443.2 | 6.6648 | 35.2288 | 48.4627 | -3060.5998
2020-10-29 02:00 | -10973.9 | 6.6648 | 34.8942 | 48.4627 | -3216.1326
2020-10-30 03:00 | -11754.1 | 6.6648 | 34.4064 | 48.4627 | -3444.7867
2020-10-31 04:00 | -11988.7 | 6.6648 | 34.142 | 48.4627 | -3513.5411
2020-11-01 05:00 | -12215.5 | 6.6648 | 33.9162 | 48.4627 | -3580.0097
2020-11-02 06:00 | -12335.7 | 6.6648 | 33.7537 | 48.4627 | -3615.2368
2020-11-03 07:00 | -12185.7 | 6.6648 | 33.7355 | 48.4627 | -3571.2761
2020-11-04 08:00 | -11853.3 | 6.6648 | 33.8424 | 48.4627 | -3473.8593
2020-11-05 09:00 | -11125.4 | 6.6648 | 34.2014 | 48.4627 | -3260.5329
2020-11-06 10:00 | -9823.56 | 6.6648 | 34.9025 | 48.4627 | -2879.0012
2020-11-07 11:00 | -8734.2 | 6.6648 | 35.587 | 48.4627 | -2559.7413
2020-11-08 12:00 | -7226.78 | 6.6648 | 36.5269 | 48.4627 | -2117.9601
2020-11-09 13:00 | -7086.72 | 6.6648 | 36.8347 | 48.4627 | -2076.9126
2020-11-10 14:00 | -6721.39 | 6.6648 | 37.1799 | 48.4627 | -1969.845
2020-11-11 15:00 | -6920.88 | 6.6648 | 37.2257 | 48.4627 | -2028.3097
2020-11-12 16:00 | -8351.78 | 6.6648 | 36.5822 | 48.4627 | -2447.6651
2020-11-13 17:00 | -8018.32 | 6.6648 | 36.685 | 48.4627 | -2349.9376
2020-11-14 18:00 | -8553.54 | 6.6648 | 36.4172 | 48.4627 | -2506.7951
2020-11-15 19:00 | -9242.83 | 6.6648 | 36.0363 | 48.4627 | -2708.8061
2020-11-16 20:00 | -9907.74 | 6.6648 | 35.6076 | 48.4627 | -2903.672
2020-11-17 21:00 | -10282.9 | 6.6648 | 35.3072 | 48.4627 | -3013.6205
2020-11-18 22:00 | -10277.6 | 6.6648 | 35.2248 | 48.4627 | -3012.0672
2020-11-19 23:00 | -10412 | 6.6648 | 35.0945 | 48.4627 | -3051.456
2020-11-21 | -11555.3 | 6.6648 | 34.4414 | 48.4627 | -3386.5241
2020-11-22 01:00 | -11449.3 | 6.6648 | 34.3313 | 48.4627 | -3355.4586
2020-11-23 02:00 | -10909 | 6.6648 | 34.5181 | 48.4627 | -3197.1123
2020-11-24 03:00 | -11177.1 | 6.6648 | 34.3787 | 48.4627 | -3275.6847
2020-11-25 04:00 | -10737.4 | 6.6648 | 34.5626 | 48.4627 | -3146.8213
2020-11-26 05:00 | -10656.3 | 6.6648 | 34.6048 | 48.4627 | -3123.0532
2020-11-27 06:00 | -10600.6 | 6.6648 | 34.6527 | 48.4627 | -3106.7292
2020-11-28 07:00 | -10454.5 | 6.6648 | 34.7413 | 48.4627 | -3063.9115
2020-11-29 08:00 | -10733 | 6.6648 | 34.6146 | 48.4627 | -3145.5318
2020-11-30 09:00 | -11505.7 | 6.6648 | 34.2014 | 48.4627 | -3371.9878
2020-12-01 10:00 | -11775.4 | 6.6648 | 33.9598 | 48.4627 | -3451.0291
2020-12-02 11:00 | -9700.94 | 6.6648 | 34.9277 | 48.4627 | -2843.0649
2020-12-03 12:00 | -8729.86 | 6.6648 | 35.5702 | 48.4627 | -2558.4694
2020-12-04 13:00 | -8747.76 | 6.6648 | 35.7164 | 48.4627 | -2563.7154
2020-12-05 14:00 | -8234.25 | 6.6648 | 36.0396 | 48.4627 | -2413.2205
2020-12-06 15:00 | -8604.5 | 6.6648 | 35.9541 | 48.4627 | -2521.73
2020-12-07 16:00 | -9844.54 | 6.6648 | 35.3705 | 48.4627 | -2885.1499
2020-12-08 17:00 | -9075.53 | 6.6648 | 35.6599 | 48.4627 | -2659.7753
2020-12-09 18:00 | -9618.86 | 6.6648 | 35.4007 | 48.4627 | -2819.0096
2020-12-10 19:00 | -9997.49 | 6.6648 | 35.1722 | 48.4627 | -2929.9751
2020-12-11 20:00 | -10567 | 6.6648 | 34.8093 | 48.4627 | -3096.882
2020-12-12 21:00 | -10973 | 6.6648 | 34.5192 | 48.4627 | -3215.8689
2020-12-13 22:00 | -11168.7 | 6.6648 | 34.3533 | 48.4627 | -3273.2229
2020-12-14 23:00 | -11373 | 6.6648 | 34.168 | 48.4627 | -3333.0973
2020-12-16 | -12083.5 | 6.6648 | 33.7278 | 48.4627 | -3541.3243
2020-12-17 01:00 | -12413.2 | 6.6648 | 33.4284 | 48.4627 | -3637.9498
2020-12-18 02:00 | -12530.8 | 6.6648 | 33.247 | 48.4627 | -3672.415
2020-12-19 03:00 | -12648.3 | 6.6648 | 33.0981 | 48.4627 | -3706.8508
2020-12-20 04:00 | -12724.1 | 6.6648 | 32.9841 | 48.4627 | -3729.0656
2020-12-21 05:00 | -12970.8 | 6.6648 | 32.7796 | 48.4627 | -3801.3662
2020-12-22 06:00 | -13176.3 | 6.6648 | 32.593 | 48.4627 | -3861.5923
2020-12-23 07:00 | -12636.4 | 6.6648 | 32.7893 | 48.4627 | -3703.3633
2020-12-24 08:00 | -12160.3 | 6.6648 | 33.0288 | 48.4627 | -3563.8321
2020-12-25 09:00 | -12083.3 | 6.6648 | 33.0988 | 48.4627 | -3541.2657
2020-12-26 10:00 | -12081.1 | 6.6648 | 33.1031 | 48.4627 | -3540.6209
2020-12-27 11:00 | -11448.4 | 6.6648 | 33.4096 | 48.4627 | -3355.1948
2020-12-28 12:00 | -11752.5 | 6.6648 | 33.2973 | 48.4627 | -3444.3178
2020-12-29 13:00 | -11369.4 | 6.6648 | 33.4726 | 48.4627 | -3332.0422
2020-12-30 14:00 | -9723.36 | 6.6648 | 34.3256 | 48.4627 | -2849.6355
2020-12-31 15:00 | -9157.2 | 6.6648 | 34.7788 | 48.4627 | -2683.7104
2021-01-01 16:00 | -9521.37 | 6.6648 | 34.7415 | 48.4627 | -2790.4381
2021-01-02 17:00 | -8943.8 | 6.6648 | 35.0741 | 48.4627 | -2621.169
2021-01-03 18:00 | -9445.86 | 6.6648 | 34.923 | 48.4627 | -2768.3083
2021-01-04 19:00 | -9887.55 | 6.6648 | 34.73 | 48.4627 | -2897.7549
2021-01-05 20:00 | -10064 | 6.6648 | 34.6099 | 48.4627 | -2949.4672
2021-01-06 21:00 | -10325.9 | 6.6648 | 34.4532 | 48.4627 | -3026.2226
2021-01-07 22:00 | -10697.4 | 6.6648 | 34.2396 | 48.4627 | -3135.0985
2021-01-08 23:00 | -10760.9 | 6.6648 | 34.1497 | 48.4627 | -3153.7085
2021-01-10 | -11759 | 6.6648 | 33.6124 | 48.4627 | -3446.2227
2021-01-11 01:00 | -11854.6 | 6.6648 | 33.453 | 48.4627 | -3474.2403
2021-01-12 02:00 | -11905 | 6.6648 | 33.3437 | 48.4627 | -3489.0111
2021-01-13 03:00 | -11889.7 | 6.6648 | 33.2927 | 48.4627 | -3484.5271
2021-01-14 04:00 | -11855.7 | 6.6648 | 33.2661 | 48.4627 | -3474.5627
2021-01-15 05:00 | -11816.5 | 6.6648 | 33.2433 | 48.4627 | -3463.0743
2021-01-16 06:00 | -11686 | 6.6648 | 33.2905 | 48.4627 | -3424.8285
2021-01-17 07:00 | -11797 | 6.6648 | 33.2269 | 48.4627 | -3457.3594
2021-01-18 08:00 | -11681.9 | 6.6648 | 33.2616 | 48.4627 | -3423.6269
2021-01-19 09:00 | -10947.9 | 6.6648 | 33.6304 | 48.4627 | -3208.5128
2021-01-20 10:00 | -9904.4 | 6.6648 | 34.2332 | 48.4627 | -2902.6931
2021-01-21 11:00 | -10178.1 | 6.6648 | 34.2192 | 48.4627 | -2982.9067
2021-01-22 12:00 | -9167.79 | 6.6648 | 34.7795 | 48.4627 | -2686.814
2021-01-23 13:00 | -8034.45 | 6.6648 | 35.4907 | 48.4627 | -2354.6649
2021-01-24 14:00 | -8132.92 | 6.6648 | 35.6379 | 48.4627 | -2383.5236
2021-01-25 15:00 | -8955.15 | 6.6648 | 35.3179 | 48.4627 | -2624.4954
2021-01-26 16:00 | -8301.94 | 6.6648 | 35.6339 | 48.4627 | -2433.0584
2021-01-27 17:00 | -8393.51 | 6.6648 | 35.671 | 48.4627 | -2459.895
2021-01-28 18:00 | -8255.4 | 6.6648 | 35.7947 | 48.4627 | -2419.4189
2021-01-29 19:00 | -8613.61 | 6.6648 | 35.6505 | 48.4627 | -2524.3999
2021-01-30 20:00 | -8885.18 | 6.6648 | 35.5144 | 48.4627 | -2603.9892
2021-01-31 21:00 | -9563.59 | 6.6648 | 35.1649 | 48.4627 | -2802.8116
2021-02-01 22:00 | -9762.03 | 6.6648 | 34.9971 | 48.4627 | -2860.9686
2021-02-02 23:00 | -10221.3 | 6.6648 | 34.7163 | 48.4627 | -2995.5673
2021-02-04 | -10553.4 | 6.6648 | 34.4789 | 48.4627 | -3092.8962
2021-02-05 01:00 | -10541.1 | 6.6648 | 34.4068 | 48.4627 | -3089.2915
2021-02-06 02:00 | -10395.4 | 6.6648 | 34.4364 | 48.4627 | -3046.591
2021-02-07 03:00 | -10384.4 | 6.6648 | 34.438 | 48.4627 | -3043.3672
2021-02-08 04:00 | -10027.8 | 6.6648 | 34.6095 | 48.4627 | -2938.8581
2021-02-09 05:00 | -9715.15 | 6.6648 | 34.7988 | 48.4627 | -2847.2294
2021-02-10 06:00 | -9351 | 6.6648 | 35.0346 | 48.4627 | -2740.5076
2021-02-11 07:00 | -9532.96 | 6.6648 | 35.0062 | 48.4627 | -2793.8348
2021-02-12 08:00 | -9631.45 | 6.6648 | 34.9772 | 48.4627 | -2822.6994
2021-02-13 09:00 | -10245.8 | 6.6648 | 34.6738 | 48.4627 | -3002.7476
2021-02-14 10:00 | -9887.94 | 6.6648 | 34.806 | 48.4627 | -2897.8692
2021-02-15 11:00 | -9602.67 | 6.6648 | 34.9621 | 48.4627 | -2814.2648
2021-02-16 12:00 | -9379.62 | 6.6648 | 35.1056 | 48.4627 | -2748.8953
2021-02-17 13:00 | -7731.83 | 6.6648 | 35.978 | 48.4627 | -2265.9757
2021-02-18 14:00 | -6829.65 | 6.6648 | 36.6118 | 48.4627 | -2001.5728
2021-02-19 15:00 | -6951.03 | 6.6648 | 36.7485 | 48.4627 | -2037.1458
2021-02-20 16:00 | -7411.28 | 6.6648 | 36.6121 | 48.4627 | -2172.0318
2021-02-21 17:00 | -8919.03 | 6.6648 | 35.8678 | 48.4627 | -2613.9097
2021-02-22 18:00 | -9007.99 | 6.6648 | 35.7163 | 48.4627 | -2639.9813
2021-02-23 19:00 | -9769.78 | 6.6648 | 35.2643 | 48.4627 | -2863.2399
2021-02-24 20:00 | -11048.8 | 6.6648 | 34.5 | 48.4627 | -3238.0836
2021-02-25 21:00 | -12034.6 | 6.6648 | 33.803 | 48.4627 | -3526.9931
2021-02-26 22:00 | -12645.2 | 6.6648 | 33.2762 | 48.4627 | -3705.9423
2021-02-27 23:00 | -13415.8 | 6.6648 | 32.7065 | 48.4627 | -3931.7829
2021-03-01 | -13856.9 | 6.6648 | 32.2834 | 48.4627 | -4061.0565
2021-03-02 01:00 | -14212.8 | 6.6648 | 31.9073 | 48.4627 | -4165.3605
2021-03-03 02:00 | -14527.3 | 6.6648 | 31.5673 | 48.4627 | -4257.5314
2021-03-04 03:00 | -14765.6 | 6.6648 | 31.2786 | 48.4627 | -4327.3702
2021-03-05 04:00 | -14945.7 | 6.6648 | 31.03 | 48.4627 | -4380.1523
2021-03-06 05:00 | -15037.6 | 6.6648 | 30.8503 | 48.4627 | -4407.0855
2021-03-07 06:00 | -15022.8 | 6.6648 | 30.7359 | 48.4627 | -4402.7481
2021-03-08 07:00 | -15216.3 | 6.6648 | 30.5371 | 48.4627 | -4459.4573
2021-03-09 08:00 | -15262 | 6.6648 | 30.4117 | 48.4627 | -4472.8507
2021-03-10 09:00 | -14685.2 | 6.6648 | 30.6251 | 48.4627 | -4303.8073
2021-03-11 10:00 | -13919.4 | 6.6648 | 31.006 | 48.4627 | -4079.3735
2021-03-12 11:00 | -13129.2 | 6.6648 | 31.4575 | 48.4627 | -3847.7887
2021-03-13 12:00 | -12397 | 6.6648 | 31.9097 | 48.4627 | -3633.2021
2021-03-14 13:00 | -11991.3 | 6.6648 | 32.2108 | 48.4627 | -3514.3031
2021-03-15 14:00 | -11918.7 | 6.6648 | 32.3288 | 48.4627 | -3493.0262
2021-03-16 15:00 | -12109 | 6.6648 | 32.2781 | 48.4627 | -3548.7976
2021-03-17 16:00 | -12448.5 | 6.6648 | 32.1087 | 48.4627 | -3648.2952
2021-03-18 17:00 | -12928.1 | 6.6648 | 31.8325 | 48.4627 | -3788.8521
2021-03-19 18:00 | -13224.8 | 6.6648 | 31.61 | 48.4627 | -3875.8063
2021-03-20 19:00 | -13268.2 | 6.6648 | 31.517 | 48.4627 | -3888.5256
2021-03-21 20:00 | -13591.5 | 6.6648 | 31.3062 | 48.4627 | -3983.2754
2021-03-22 21:00 | -14156 | 6.6648 | 30.9521 | 48.4627 | -4148.7141
2021-03-23 22:00 | -14609 | 6.6648 | 30.6157 | 48.4627 | -4281.4753
2021-03-24 23:00 | -14998.1 | 6.6648 | 30.3053 | 48.4627 | -4395.5092
2021-03-26 | -15317.8 | 6.6648 | 30.0273 | 48.4627 | -4489.204
2021-03-27 01:00 | 0 | 0 | 37.805 | 48.4627 | 0
2021-03-28 02:00 | -12942.7 | 6.6648 | 32.5911 | 48.4627 | -3793.1309
2021-03-29 03:00 | -14523 | 6.6648 | 31.2934 | 48.4627 | -4256.2711
2021-03-30 04:00 | -14548.7 | 6.6648 | 30.8173 | 48.4627 | -4263.8031
2021-03-31 05:00 | -15090.8 | 6.6648 | 30.4746 | 48.4627 | -4422.6769
2021-04-01 06:00 | -15440.8 | 6.6648 | 30.2224 | 48.4627 | -4525.2518
2021-04-02 07:00 | 0 | 0 | 37.8482 | 48.4627 | 0
2021-04-03 08:00 | -12054.2 | 6.6648 | 33.0781 | 48.4627 | -3532.7373
2021-04-04 09:00 | -14207.2 | 6.6648 | 31.6247 | 48.4627 | -4163.7193
2021-04-05 10:00 | -14698.9 | 6.6648 | 30.9108 | 48.4627 | -4307.8224
2021-04-06 11:00 | -15481.1 | 6.6648 | 30.3982 | 48.4627 | -4537.0625
2021-04-07 12:00 | -14275.3 | 6.6648 | 30.9116 | 48.4627 | -4183.6774
2021-04-08 13:00 | -13785.2 | 6.6648 | 30.8418 | 48.4627 | -4040.0433
2021-04-09 14:00 | -12776.7 | 6.6648 | 31.3551 | 48.4627 | -3744.4811
2021-04-10 15:00 | -12326.8 | 6.6648 | 31.6803 | 48.4627 | -3612.6285
2021-04-11 16:00 | -12525.4 | 6.6648 | 31.6716 | 48.4627 | -3670.8324
2021-04-12 17:00 | -12777 | 6.6648 | 31.5926 | 48.4627 | -3744.5691
2021-04-13 18:00 | -12536.7 | 6.6648 | 31.7242 | 48.4627 | -3674.1441
2021-04-14 19:00 | -12593.3 | 6.6648 | 31.6113 | 48.4627 | -3690.7319
2021-04-15 20:00 | -12937.5 | 6.6648 | 31.427 | 48.4627 | -3791.607
2021-04-16 21:00 | -13314.1 | 6.6648 | 31.2029 | 48.4627 | -3901.9775
2021-04-17 22:00 | -13656.2 | 6.6648 | 30.9858 | 48.4627 | -4002.2371
2021-04-18 23:00 | -13905.9 | 6.6648 | 30.8208 | 48.4627 | -4075.417
2021-04-20 | -14237 | 6.6648 | 30.6025 | 48.4627 | -4172.4528
2021-04-21 01:00 | -14458.1 | 6.6648 | 30.3616 | 48.4627 | -4237.2508
2021-04-22 02:00 | -14488.5 | 6.6648 | 30.2689 | 48.4627 | -4246.1602
2021-04-23 03:00 | -14459.3 | 6.6648 | 30.2317 | 48.4627 | -4237.6025
2021-04-24 04:00 | -14453.6 | 6.6648 | 30.1999 | 48.4627 | -4235.932
2021-04-25 05:00 | -14538.9 | 6.6648 | 30.1299 | 48.4627 | -4260.931
2021-04-26 06:00 | -14560.5 | 6.6648 | 30.0876 | 48.4627 | -4267.2613
2021-04-27 07:00 | 0 | 0 | 37.5025 | 48.4627 | 0
2021-04-28 08:00 | -11838.5 | 6.6648 | 32.8133 | 48.4627 | -3469.5219
2021-04-29 09:00 | -14135.7 | 6.6648 | 31.2816 | 48.4627 | -4142.7647
2021-04-30 10:00 | -14178.1 | 6.6648 | 30.798 | 48.4627 | -4155.1909
2021-05-01 11:00 | -12629.2 | 6.6648 | 31.5327 | 48.4627 | -3701.2532
2021-05-02 12:00 | -11759.7 | 6.6648 | 32.1292 | 48.4627 | -3446.4279
2021-05-03 13:00 | -11916 | 6.6648 | 31.9768 | 48.4627 | -3492.2349
2021-05-04 14:00 | -12138.9 | 6.6648 | 31.8877 | 48.4627 | -3557.5604
2021-05-05 15:00 | -12218.6 | 6.6648 | 31.8719 | 48.4627 | -3580.9182
2021-05-06 16:00 | -12216.4 | 6.6648 | 31.905 | 48.4627 | -3580.2734
2021-05-07 17:00 | -11480.8 | 6.6648 | 32.3025 | 48.4627 | -3364.6903
2021-05-08 18:00 | -11577.7 | 6.6648 | 32.3331 | 48.4627 | -3393.0889
2021-05-09 19:00 | -11690.2 | 6.6648 | 32.1974 | 48.4627 | -3426.0594
2021-05-10 20:00 | -11814.8 | 6.6648 | 32.1333 | 48.4627 | -3462.5761
2021-05-11 21:00 | -11965.5 | 6.6648 | 32.0746 | 48.4627 | -3506.7419
2021-05-12 22:00 | -12088.2 | 6.6648 | 32.0263 | 48.4627 | -3542.7017
2021-05-13 23:00 | -12000.1 | 6.6648 | 32.0617 | 48.4627 | -3516.8821
2021-05-15 | -12333.7 | 6.6648 | 31.8953 | 48.4627 | -3614.6507
2021-05-16 01:00 | -12720.6 | 6.6648 | 31.6393 | 48.4627 | -3728.0399
2021-05-17 02:00 | -12768.9 | 6.6648 | 31.5614 | 48.4627 | -3742.1952
2021-05-18 03:00 | -12771.1 | 6.6648 | 31.5345 | 48.4627 | -3742.8399
2021-05-19 04:00 | -12569.7 | 6.6648 | 31.6259 | 48.4627 | -3683.8154
2021-05-20 05:00 | -12467.8 | 6.6648 | 31.6817 | 48.4627 | -3653.9515
2021-05-21 06:00 | -12363.6 | 6.6648 | 31.7469 | 48.4627 | -3623.4135
2021-05-22 07:00 | -11912.9 | 6.6648 | 31.9076 | 48.4627 | -3491.3263
2021-05-23 08:00 | -11174.5 | 6.6648 | 32.3301 | 48.4627 | -3274.9227
2021-05-24 09:00 | -10343.3 | 6.6648 | 32.8676 | 48.4627 | -3031.322
2021-05-25 10:00 | -10188.6 | 6.6648 | 33.095 | 48.4627 | -2985.9839
2021-05-26 11:00 | -11165.6 | 6.6648 | 32.6937 | 48.4627 | -3272.3143
2021-05-27 12:00 | -10502 | 6.6648 | 33.0038 | 48.4627 | -3077.8324
2021-05-28 13:00 | -10130.7 | 6.6648 | 33.2628 | 48.4627 | -2969.0151
2021-05-29 14:00 | -10453.7 | 6.6648 | 33.1838 | 48.4627 | -3063.677
2021-05-30 15:00 | -11629.3 | 6.6648 | 32.5875 | 48.4627 | -3408.2114
2021-05-31 16:00 | -12284.7 | 6.6648 | 32.1415 | 48.4627 | -3600.2902
2021-06-01 17:00 | -12577.9 | 6.6648 | 31.8887 | 48.4627 | -3686.2186
2021-06-02 18:00 | -12874.2 | 6.6648 | 31.6509 | 48.4627 | -3773.0556
2021-06-03 19:00 | -13706.9 | 6.6648 | 31.1275 | 48.4627 | -4017.0958
2021-06-04 20:00 | -14054.2 | 6.6648 | 30.7914 | 48.4627 | -4118.8794
2021-06-05 21:00 | -14500.9 | 6.6648 | 30.428 | 48.4627 | -4249.7943
2021-06-06 22:00 | -15187.2 | 6.6648 | 29.9424 | 48.4627 | -4450.929
2021-06-07 23:00 | 0 | 0 | 37.6121 | 48.4627 | 0
2021-06-09 | -12887.4 | 6.6648 | 32.3651 | 48.4627 | -3776.9241
2021-06-10 01:00 | -14690 | 6.6648 | 30.9546 | 48.4627 | -4305.214
2021-06-11 02:00 | -14594.9 | 6.6648 | 30.4985 | 48.4627 | -4277.343
2021-06-12 03:00 | -14835.3 | 6.6648 | 30.2974 | 48.4627 | -4347.7972
2021-06-13 04:00 | -14690 | 6.6648 | 30.3271 | 48.4627 | -4305.214
2021-06-14 05:00 | -14739.5 | 6.6648 | 30.0322 | 48.4627 | -4319.721
2021-06-15 06:00 | 0 | 0 | 37.5671 | 48.4627 | 0
2021-06-16 07:00 | -12310.6 | 6.6648 | 32.6255 | 48.4627 | -3607.8807
2021-06-17 08:00 | -14316.9 | 6.6648 | 31.1974 | 48.4627 | -4195.8692
2021-06-18 09:00 | -14116.7 | 6.6648 | 30.844 | 48.4627 | -4137.1964
2021-06-19 10:00 | -13946.3 | 6.6648 | 30.8932 | 48.4627 | -4087.2571
2021-06-20 11:00 | -14848.5 | 6.6648 | 30.3222 | 48.4627 | -4351.6658
2021-06-21 12:00 | 0 | 0 | 37.621 | 48.4627 | 0
2021-06-22 13:00 | -11545.5 | 6.6648 | 33.0428 | 48.4627 | -3383.652
2021-06-23 14:00 | -15074.1 | 6.6648 | 30.9028 | 48.4627 | -4417.7826
2021-06-24 15:00 | -13259.4 | 6.6648 | 31.2576 | 48.4627 | -3885.9465
2021-06-25 16:00 | -13435.2 | 6.6648 | 31.2165 | 48.4627 | -3937.4684
2021-06-26 17:00 | -13333.4 | 6.6648 | 31.3218 | 48.4627 | -3907.6338
2021-06-27 18:00 | -13452.5 | 6.6648 | 30.9236 | 48.4627 | -3942.5386
2021-06-28 19:00 | -13493.1 | 6.6648 | 30.848 | 48.4627 | -3954.4373
2021-06-29 20:00 | -13558.1 | 6.6648 | 30.8353 | 48.4627 | -3973.4869
2021-06-30 21:00 | -13790.2 | 6.6648 | 30.706 | 48.4627 | -4041.5087
2021-07-01 22:00 | -14122.9 | 6.6648 | 30.5099 | 48.4627 | -4139.0134
2021-07-02 23:00 | -14483.9 | 6.6648 | 30.2208 | 48.4627 | -4244.8121
2021-07-04 | -14743.2 | 6.6648 | 29.9019 | 48.4627 | -4320.8054
2021-07-05 01:00 | 0 | 0 | 37.4027 | 48.4627 | 0
2021-07-06 02:00 | -12192.9 | 6.6648 | 32.5483 | 48.4627 | -3573.3862
2021-07-07 03:00 | -14200.7 | 6.6648 | 31.1245 | 48.4627 | -4161.8143
2021-07-08 04:00 | -14986.1 | 6.6648 | 30.2637 | 48.4627 | -4391.9924
2021-07-09 05:00 | -15457.2 | 6.6648 | 29.8821 | 48.4627 | -4530.0581
2021-07-10 06:00 | 0 | 0 | 37.6949 | 48.4627 | 0
2021-07-11 07:00 | -12028.9 | 6.6648 | 32.7066 | 48.4627 | -3525.3226
2021-07-12 08:00 | -14091.1 | 6.6648 | 31.2593 | 48.4627 | -4129.6938
2021-07-13 09:00 | -15484.3 | 6.6648 | 30.0851 | 48.4627 | -4538.0004
2021-07-14 10:00 | 0 | 0 | 37.8732 | 48.4627 | 0
2021-07-15 11:00 | -12153.9 | 6.6648 | 33.086 | 48.4627 | -3561.9565
2021-07-16 12:00 | -14254.9 | 6.6648 | 31.3571 | 48.4627 | -4177.6988
2021-07-17 13:00 | -15361.6 | 6.6648 | 30.1576 | 48.4627 | -4502.0405
2021-07-18 14:00 | 0 | 0 | 37.8757 | 48.4627 | 0
2021-07-19 15:00 | -11760 | 6.6648 | 33.2774 | 48.4627 | -3446.5158
2021-07-20 16:00 | -14433 | 6.6648 | 31.3499 | 48.4627 | -4229.8948
2021-07-21 17:00 | -14178.1 | 6.6648 | 30.9566 | 48.4627 | -4155.1909
2021-07-22 18:00 | -13350.2 | 6.6648 | 31.2056 | 48.4627 | -3912.5574
2021-07-23 19:00 | -13298.7 | 6.6648 | 31.313 | 48.4627 | -3897.4642
2021-07-24 20:00 | -13482.1 | 6.6648 | 31.0274 | 48.4627 | -3951.2135
2021-07-25 21:00 | -13675.4 | 6.6648 | 30.902 | 48.4627 | -4007.8641
2021-07-26 22:00 | -13924.6 | 6.6648 | 30.6549 | 48.4627 | -4080.8974
2021-07-27 23:00 | -14166 | 6.6648 | 30.4657 | 48.4627 | -4151.6448
2021-07-29 | -14392.8 | 6.6648 | 30.3073 | 48.4627 | -4218.1133
2021-07-30 01:00 | -14460.9 | 6.6648 | 30.1763 | 48.4627 | -4238.0714
2021-07-31 02:00 | -14640.5 | 6.6648 | 29.9237 | 48.4627 | -4290.707
2021-08-01 03:00 | 0 | 0 | 37.4085 | 48.4627 | 0
2021-08-02 04:00 | -12209.8 | 6.6648 | 32.5472 | 48.4627 | -3578.3392
2021-08-03 05:00 | -14065.2 | 6.6648 | 31.2179 | 48.4627 | -4122.1032
2021-08-04 06:00 | -14934.7 | 6.6648 | 30.2451 | 48.4627 | -4376.9285
2021-08-05 07:00 | -15397.9 | 6.6648 | 29.8385 | 48.4627 | -4512.679
2021-08-06 08:00 | 0 | 0 | 37.6766 | 48.4627 | 0
2021-08-07 09:00 | -11986 | 6.6648 | 32.7387 | 48.4627 | -3512.7498
2021-08-08 10:00 | -13163.6 | 6.6648 | 31.7009 | 48.4627 | -3857.8703
2021-08-09 11:00 | -13222.4 | 6.6648 | 31.3085 | 48.4627 | -3875.1029
2021-08-10 12:00 | -11520.6 | 6.6648 | 32.1595 | 48.4627 | -3376.3546
2021-08-11 13:00 | -12036 | 6.6648 | 32.1088 | 48.4627 | -3527.4034
2021-08-12 14:00 | -11140 | 6.6648 | 32.3525 | 48.4627 | -3264.8117
2021-08-13 15:00 | -11233.4 | 6.6648 | 32.2796 | 48.4627 | -3292.1846
2021-08-14 16:00 | -11831.5 | 6.6648 | 32.0413 | 48.4627 | -3467.4704
2021-08-15 17:00 | -11979.1 | 6.6648 | 31.9703 | 48.4627 | -3510.7277
2021-08-16 18:00 | -12056.1 | 6.6648 | 31.9253 | 48.4627 | -3533.2941
2021-08-17 19:00 | -12249 | 6.6648 | 31.8466 | 48.4627 | -3589.8275
2021-08-18 20:00 | -12525.7 | 6.6648 | 31.5723 | 48.4627 | -3670.9203
2021-08-19 21:00 | -12909.2 | 6.6648 | 31.3269 | 48.4627 | -3783.3131
2021-08-20 22:00 | -13214.2 | 6.6648 | 31.1213 | 48.4627 | -3872.6997
2021-08-21 23:00 | -13580.6 | 6.6648 | 30.8815 | 48.4627 | -3980.081
2021-08-23 | -13783.5 | 6.6648 | 30.7009 | 48.4627 | -4039.5451
2021-08-24 01:00 | -13876.1 | 6.6648 | 30.5582 | 48.4627 | -4066.6835
2021-08-25 02:00 | -13931.1 | 6.6648 | 30.4665 | 48.4627 | -4082.8024
2021-08-26 03:00 | -13910.5 | 6.6648 | 30.3684 | 48.4627 | -4076.7651
2021-08-27 04:00 | -13821.1 | 6.6648 | 30.3741 | 48.4627 | -4050.5646
2021-08-28 05:00 | -13722.7 | 6.6648 | 30.4095 | 48.4627 | -4021.7264
2021-08-29 06:00 | -13618.8 | 6.6648 | 30.4287 | 48.4627 | -3991.2763
2021-08-30 07:00 | -13488.8 | 6.6648 | 30.4948 | 48.4627 | -3953.177
2021-08-31 08:00 | -13401 | 6.6648 | 30.4888 | 48.4627 | -3927.4454
2021-09-01 09:00 | -13622.2 | 6.6648 | 30.3781 | 48.4627 | -3992.2727
2021-09-02 10:00 | -12930.2 | 6.6648 | 30.6824 | 48.4627 | -3789.4675
2021-09-03 11:00 | -11385.9 | 6.6648 | 31.5318 | 48.4627 | -3336.8779
2021-09-04 12:00 | -10872.4 | 6.6648 | 31.9768 | 48.4627 | -3186.3859
2021-09-05 13:00 | -11824.9 | 6.6648 | 31.6356 | 48.4627 | -3465.5361
2021-09-06 14:00 | -11106.3 | 6.6648 | 31.961 | 48.4627 | -3254.9352
2021-09-07 15:00 | -10456 | 6.6648 | 32.3823 | 48.4627 | -3064.3511
2021-09-08 16:00 | -10771.6 | 6.6648 | 32.3612 | 48.4627 | -3156.8443
2021-09-09 17:00 | -11102.1 | 6.6648 | 32.2295 | 48.4627 | -3253.7043
2021-09-10 18:00 | -11403.7 | 6.6648 | 32.0666 | 48.4627 | -3342.0946
2021-09-11 19:00 | -11639.5 | 6.6648 | 31.9457 | 48.4627 | -3411.2007
2021-09-12 20:00 | -11746.7 | 6.6648 | 31.8786 | 48.4627 | -3442.6179
2021-09-13 21:00 | -12121.4 | 6.6648 | 31.675 | 48.4627 | -3552.4317
2021-09-14 22:00 | -12375.5 | 6.6648 | 31.5082 | 48.4627 | -3626.901
2021-09-15 23:00 | -12667.5 | 6.6648 | 31.295 | 48.4627 | -3712.4778
2021-09-17 | -12948.8 | 6.6648 | 31.0934 | 48.4627 | -3794.9187
2021-09-18 01:00 | -12915.5 | 6.6648 | 31.0588 | 48.4627 | -3785.1594
2021-09-19 02:00 | -12891.4 | 6.6648 | 31.0391 | 48.4627 | -3778.0964
2021-09-20 03:00 | -12861.3 | 6.6648 | 31.0016 | 48.4627 | -3769.275
2021-09-21 04:00 | -12729.1 | 6.6648 | 31.0493 | 48.4627 | -3730.531
2021-09-22 05:00 | -12497.3 | 6.6648 | 31.1708 | 48.4627 | -3662.5971
2021-09-23 06:00 | -12405.1 | 6.6648 | 31.2305 | 48.4627 | -3635.5759
2021-09-24 07:00 | -12250.3 | 6.6648 | 31.3328 | 48.4627 | -3590.2085
2021-09-25 08:00 | -12177 | 6.6648 | 31.3693 | 48.4627 | -3568.7264
2021-09-26 09:00 | -11413.5 | 6.6648 | 31.7873 | 48.4627 | -3344.9667
2021-09-27 10:00 | -11824.7 | 6.6648 | 31.6692 | 48.4627 | -3465.4775
2021-09-28 11:00 | -9435.27 | 6.6648 | 32.9086 | 48.4627 | -2765.2047
2021-09-29 12:00 | -8346.93 | 6.6648 | 33.6964 | 48.4627 | -2446.2437
2021-09-30 13:00 | -9279.88 | 6.6648 | 33.4769 | 48.4627 | -2719.6644
2021-10-01 14:00 | -8993.37 | 6.6648 | 33.6804 | 48.4627 | -2635.6966
2021-10-02 15:00 | -8757.11 | 6.6648 | 33.8827 | 48.4627 | -2566.4556
2021-10-03 16:00 | -9267.65 | 6.6648 | 33.7448 | 48.4627 | -2716.0801
2021-10-04 17:00 | -9851.7 | 6.6648 | 33.4619 | 48.4627 | -2887.2483
2021-10-05 18:00 | -9723.02 | 6.6648 | 33.4833 | 48.4627 | -2849.5359
2021-10-06 19:00 | -10211.2 | 6.6648 | 33.256 | 48.4627 | -2992.6073
2021-10-07 20:00 | -10690 | 6.6648 | 32.9891 | 48.4627 | -3132.9297
2021-10-08 21:00 | -11551.6 | 6.6648 | 32.4878 | 48.4627 | -3385.4398
2021-10-09 22:00 | -11768.6 | 6.6648 | 32.2775 | 48.4627 | -3449.0362
2021-10-10 23:00 | -12240.8 | 6.6648 | 31.956 | 48.4627 | -3587.4244
2021-10-12 | -12677.1 | 6.6648 | 31.6267 | 48.4627 | -3715.2913
2021-10-13 01:00 | -12949.8 | 6.6648 | 31.3561 | 48.4627 | -3795.2117
2021-10-14 02:00 | -13260.4 | 6.6648 | 31.0938 | 48.4627 | -3886.2396
2021-10-15 03:00 | -13647.7 | 6.6648 | 30.7978 | 48.4627 | -3999.746
2021-10-16 04:00 | -13930.1 | 6.6648 | 30.5446 | 48.4627 | -4082.5093
2021-10-17 05:00 | -14089.7 | 6.6648 | 30.3629 | 48.4627 | -4129.2835
2021-10-18 06:00 | -14295.4 | 6.6648 | 30.1531 | 48.4627 | -4189.5682
2021-10-19 07:00 | -14441.4 | 6.6648 | 29.979 | 48.4627 | -4232.3566
2021-10-20 08:00 | 0 | 0 | 37.338 | 48.4627 | 0
2021-10-21 09:00 | -12096.5 | 6.6648 | 32.4777 | 48.4627 | -3545.1342
2021-10-22 10:00 | -13792 | 6.6648 | 31.1807 | 48.4627 | -4042.0362
2021-10-23 11:00 | -13661.7 | 6.6648 | 30.7929 | 48.4627 | -4003.849
2021-10-24 12:00 | -12315.7 | 6.6648 | 31.4242 | 48.4627 | -3609.3754
2021-10-25 13:00 | -12607.8 | 6.6648 | 31.3953 | 48.4627 | -3694.9814
2021-10-26 14:00 | -11956.1 | 6.6648 | 31.5068 | 48.4627 | -3503.987
2021-10-27 15:00 | -11520 | 6.6648 | 31.7643 | 48.4627 | -3376.1787
2021-10-28 16:00 | -12046.1 | 6.6648 | 31.5848 | 48.4627 | -3530.3634
2021-10-29 17:00 | -12336 | 6.6648 | 31.4403 | 48.4627 | -3615.3247
2021-10-30 18:00 | -12382 | 6.6648 | 31.3831 | 48.4627 | -3628.806
2021-10-31 19:00 | -12943 | 6.6648 | 31.0902 | 48.4627 | -3793.2189
2021-11-01 20:00 | -13402 | 6.6648 | 30.6752 | 48.4627 | -3927.7385
2021-11-02 21:00 | -13582.3 | 6.6648 | 30.4799 | 48.4627 | -3980.5792
2021-11-03 22:00 | -13759.8 | 6.6648 | 30.3267 | 48.4627 | -4032.5993
2021-11-04 23:00 | -13920.6 | 6.6648 | 30.1901 | 48.4627 | -4079.7251
2021-11-06 | -14483 | 6.6648 | 29.8344 | 48.4627 | -4244.5483
2021-11-07 01:00 | 0 | 0 | 37.2016 | 48.4627 | 0
2021-11-08 02:00 | -12323.6 | 6.6648 | 32.2208 | 48.4627 | -3611.6906
2021-11-09 03:00 | -14465 | 6.6648 | 30.6724 | 48.4627 | -4239.273
2021-11-10 04:00 | -14591.4 | 6.6648 | 30.1073 | 48.4627 | -4276.3172
2021-11-11 05:00 | -14718.9 | 6.6648 | 29.9381 | 48.4627 | -4313.6838
2021-11-12 06:00 | 0 | 0 | 37.478 | 48.4627 | 0
2021-11-13 07:00 | -12056.2 | 6.6648 | 32.4474 | 48.4627 | -3533.3234
2021-11-14 08:00 | -14449.7 | 6.6648 | 30.7391 | 48.4627 | -4234.789
2021-11-15 09:00 | -14527.3 | 6.6648 | 30.2021 | 48.4627 | -4257.5314
2021-11-16 10:00 | -14928.7 | 6.6648 | 29.909 | 48.4627 | -4375.1701
2021-11-17 11:00 | 0 | 0 | 37.5369 | 48.4627 | 0
2021-11-18 12:00 | -11786.9 | 6.6648 | 32.6504 | 48.4627 | -3454.3994
2021-11-19 13:00 | -13938.9 | 6.6648 | 31.0421 | 48.4627 | -4085.0883
2021-11-20 14:00 | -14162.7 | 6.6648 | 30.4524 | 48.4627 | -4150.6776
2021-11-21 15:00 | -15147.2 | 6.6648 | 29.8523 | 48.4627 | -4439.2061
2021-11-22 16:00 | 0 | 0 | 37.5425 | 48.4627 | 0
2021-11-23 17:00 | -12068.9 | 6.6648 | 32.517 | 48.4627 | -3537.0454
2021-11-24 18:00 | -14518.3 | 6.6648 | 30.7262 | 48.4627 | -4254.8937
2021-11-25 19:00 | -14586.6 | 6.6648 | 30.1657 | 48.4627 | -4274.9105
2021-11-26 20:00 | -14789.5 | 6.6648 | 29.9652 | 48.4627 | -4334.3746
2021-11-27 21:00 | 0 | 0 | 37.5549 | 48.4627 | 0
2021-11-28 22:00 | -12487.1 | 6.6648 | 32.3225 | 48.4627 | -3659.6078
2021-11-29 23:00 | -14670.3 | 6.6648 | 30.6361 | 48.4627 | -4299.4405
2021-12-01 | -15067.7 | 6.6648 | 29.9298 | 48.4627 | -4415.907
2021-12-02 01:00 | 0 | 0 | 37.5241 | 48.4627 | 0
2021-12-03 02:00 | -12580.8 | 6.6648 | 32.4903 | 48.4627 | -3687.0685
2021-12-04 03:00 | -14703.6 | 6.6648 | 30.7664 | 48.4627 | -4309.1998
2021-12-05 04:00 | -14833.9 | 6.6648 | 30.0723 | 48.4627 | -4347.3869
2021-12-06 05:00 | 0 | 0 | 37.6209 | 48.4627 | 0
2021-12-07 06:00 | -12326.5 | 6.6648 | 32.6685 | 48.4627 | -3612.5405
2021-12-08 07:00 | -14709.7 | 6.6648 | 30.8176 | 48.4627 | -4310.9875
2021-12-09 08:00 | -14461 | 6.6648 | 30.4 | 48.4627 | -4238.1007
2021-12-10 09:00 | -15062.6 | 6.6648 | 29.9204 | 48.4627 | -4414.4123
2021-12-11 10:00 | 0 | 0 | 37.6103 | 48.4627 | 0
2021-12-12 11:00 | -12101.9 | 6.6648 | 32.5266 | 48.4627 | -3546.7168
2021-12-13 12:00 | -13914.6 | 6.6648 | 31.1936 | 48.4627 | -4077.9667
2021-12-14 13:00 | -14273.5 | 6.6648 | 30.4687 | 48.4627 | -4183.1499
2021-12-15 14:00 | -14444.5 | 6.6648 | 30.2833 | 48.4627 | -4233.2651
2021-12-16 15:00 | -14432.7 | 6.6648 | 30.2664 | 48.4627 | -4229.8068
2021-12-17 16:00 | 0 | 0 | 37.3924 | 48.4627 | 0
2021-12-18 17:00 | -12444.1 | 6.6648 | 32.2309 | 48.4627 | -3647.0057
2021-12-19 18:00 | -14503.9 | 6.6648 | 30.7358 | 48.4627 | -4250.6735
2021-12-20 19:00 | -14785.9 | 6.6648 | 30.1238 | 48.4627 | -4333.3195
2021-12-21 20:00 | -14988.3 | 6.6648 | 29.9284 | 48.4627 | -4392.6371
2021-12-22 21:00 | 0 | 0 | 37.5518 | 48.4627 | 0
2021-12-23 22:00 | -12567.4 | 6.6648 | 32.1672 | 48.4627 | -3683.1414
2021-12-24 23:00 | -15087.8 | 6.6648 | 30.4098 | 48.4627 | -4421.7977
2021-12-26 | 0 | 0 | 37.6687 | 48.4627 | 0
2021-12-27 01:00 | -12699.1 | 6.6648 | 32.4466 | 48.4627 | -3721.7388
2021-12-28 02:00 | -15017 | 6.6648 | 30.8404 | 48.4627 | -4401.0483
2021-12-29 03:00 | -15146.5 | 6.6648 | 30.0344 | 48.4627 | -4439.001
2021-12-30 04:00 | 0 | 0 | 37.5984 | 48.4627 | 0
2021-12-31 05:00 | -12624.7 | 6.6648 | 32.4963 | 48.4627 | -3699.9343
2022-01-01 06:00 | -14879 | 6.6648 | 30.6524 | 48.4627 | -4360.6045
2022-01-02 07:00 | -15159.6 | 6.6648 | 29.9838 | 48.4627 | -4442.8402
2022-01-03 08:00 | 0 | 0 | 37.7052 | 48.4627 | 0
2022-01-04 09:00 | -12340.6 | 6.6648 | 32.7064 | 48.4627 | -3616.6728
2022-01-05 10:00 | -14462.5 | 6.6648 | 30.9312 | 48.4627 | -4238.5403
2022-01-06 11:00 | -14608.3 | 6.6648 | 30.327 | 48.4627 | -4281.2701
2022-01-07 12:00 | -14404.6 | 6.6648 | 30.2257 | 48.4627 | -4221.5715
2022-01-08 13:00 | -14410 | 6.6648 | 30.2186 | 48.4627 | -4223.1541
2022-01-09 14:00 | 0 | 0 | 37.4062 | 48.4627 | 0
2022-01-10 15:00 | -12320.8 | 6.6648 | 32.4473 | 48.4627 | -3610.87
2022-01-11 16:00 | -14184.2 | 6.6648 | 30.8878 | 48.4627 | -4156.9787
2022-01-12 17:00 | -14785.6 | 6.6648 | 30.1142 | 48.4627 | -4333.2316
2022-01-13 18:00 | -14697.7 | 6.6648 | 30.0527 | 48.4627 | -4307.4707
2022-01-14 19:00 | -14928 | 6.6648 | 29.9139 | 48.4627 | -4374.9649
2022-01-15 20:00 | 0 | 0 | 37.2191 | 48.4627 | 0
2022-01-16 21:00 | -12753.9 | 6.6648 | 31.9546 | 48.4627 | -3737.7991
2022-01-17 22:00 | -14809.1 | 6.6648 | 30.4586 | 48.4627 | -4340.1188
2022-01-18 23:00 | -15112.2 | 6.6648 | 29.8324 | 48.4627 | -4428.9486
2022-01-20 | 0 | 0 | 37.469 | 48.4627 | 0
2022-01-21 01:00 | -12679.1 | 6.6648 | 32.3601 | 48.4627 | -3715.8774
2022-01-22 02:00 | -14759.6 | 6.6648 | 30.5246 | 48.4627 | -4325.6118
2022-01-23 03:00 | -15029.7 | 6.6648 | 29.867 | 48.4627 | -4404.7703
2022-01-24 04:00 | 0 | 0 | 37.4662 | 48.4627 | 0
2022-01-25 05:00 | -12415.7 | 6.6648 | 32.5035 | 48.4627 | -3638.6825
2022-01-26 06:00 | -14434.6 | 6.6648 | 30.8393 | 48.4627 | -4230.3637
2022-01-27 07:00 | -14835.3 | 6.6648 | 30.1565 | 48.4627 | -4347.7972
2022-01-28 08:00 | 0 | 0 | 37.5194 | 48.4627 | 0
2022-01-29 09:00 | -12618.8 | 6.6648 | 32.4469 | 48.4627 | -3698.2052
2022-01-30 10:00 | -14377.6 | 6.6648 | 30.8633 | 48.4627 | -4213.6586
2022-01-31 11:00 | -14610.5 | 6.6648 | 30.2707 | 48.4627 | -4281.9149
2022-02-01 12:00 | -14636.3 | 6.6648 | 30.0649 | 48.4627 | -4289.4761
2022-02-02 13:00 | -14741.1 | 6.6648 | 29.9822 | 48.4627 | -4320.1899
2022-02-03 14:00 | 0 | 0 | 37.255 | 48.4627 | 0
2022-02-04 15:00 | -12079.6 | 6.6648 | 32.4333 | 48.4627 | -3540.1813
2022-02-05 16:00 | -13841.9 | 6.6648 | 31.0198 | 48.4627 | -4056.6604
2022-02-06 17:00 | -14397.4 | 6.6648 | 30.3064 | 48.4627 | -4219.4614
2022-02-07 18:00 | -14264.2 | 6.6648 | 30.2905 | 48.4627 | -4180.4244
2022-02-08 19:00 | -14509.9 | 6.6648 | 30.1688 | 48.4627 | -4252.4319
2022-02-09 20:00 | 0 | 0 | 37.2113 | 48.4627 | 0
2022-02-10 21:00 | -12426.1 | 6.6648 | 32.141 | 48.4627 | -3641.7304
2022-02-11 22:00 | -14331.1 | 6.6648 | 30.75 | 48.4627 | -4200.0308
2022-02-12 23:00 | -14718.4 | 6.6648 | 30.1115 | 48.4627 | -4313.5372
2022-02-14 | 0 | 0 | 37.5185 | 48.4627 | 0
2022-02-15 01:00 | -12339.3 | 6.6648 | 32.5739 | 48.4627 | -3616.2919
2022-02-16 02:00 | -14370.4 | 6.6648 | 30.7923 | 48.4627 | -4211.5485
2022-02-17 03:00 | -14523.2 | 6.6648 | 30.2071 | 48.4627 | -4256.3298
2022-02-18 04:00 | -14510.6 | 6.6648 | 30.0485 | 48.4627 | -4252.6371
2022-02-19 05:00 | -14550.5 | 6.6648 | 30.0104 | 48.4627 | -4264.3306
2022-02-20 06:00 | 0 | 0 | 37.2477 | 48.4627 | 0
2022-02-21 07:00 | -12115.5 | 6.6648 | 32.4035 | 48.4627 | -3550.7025
2022-02-22 08:00 | -13940.8 | 6.6648 | 30.8855 | 48.4627 | -4085.6452
2022-02-23 09:00 | -13942.7 | 6.6648 | 30.4403 | 48.4627 | -4086.202
2022-02-24 10:00 | -13849.7 | 6.6648 | 30.4542 | 48.4627 | -4058.9464
2022-02-25 11:00 | -14341.4 | 6.6648 | 30.211 | 48.4627 | -4203.0494
2022-02-26 12:00 | 0 | 0 | 37.2092 | 48.4627 | 0
2022-02-27 13:00 | -11617.1 | 6.6648 | 32.573 | 48.4627 | -3404.6359
2022-02-28 14:00 | -13817.6 | 6.6648 | 31.0223 | 48.4627 | -4049.5388
2022-03-01 15:00 | -12333.7 | 6.6648 | 31.3395 | 48.4627 | -3614.6507
2022-03-02 16:00 | -12694.3 | 6.6648 | 31.2373 | 48.4627 | -3720.3321
2022-03-03 17:00 | -12950.6 | 6.6648 | 31.1652 | 48.4627 | -3795.4462
2022-03-04 18:00 | -13422 | 6.6648 | 30.5819 | 48.4627 | -3933.5999
2022-03-05 19:00 | -13726.8 | 6.6648 | 30.3484 | 48.4627 | -4022.928
2022-03-06 20:00 | -14065.4 | 6.6648 | 30.0549 | 48.4627 | -4122.1618
2022-03-07 21:00 | 0 | 0 | 37.2128 | 48.4627 | 0
2022-03-08 22:00 | -12209.7 | 6.6648 | 32.2795 | 48.4627 | -3578.3098
2022-03-09 23:00 | -14458.6 | 6.6648 | 30.7116 | 48.4627 | -4237.3974
2022-03-11 | -14637.7 | 6.6648 | 29.9309 | 48.4627 | -4289.8864
2022-03-12 01:00 | 0 | 0 | 37.3354 | 48.4627 | 0
2022-03-13 02:00 | -12071.9 | 6.6648 | 32.5379 | 48.4627 | -3537.9246
2022-03-14 03:00 | -13963.5 | 6.6648 | 30.9564 | 48.4627 | -4092.2979
2022-03-15 04:00 | -14101.5 | 6.6648 | 30.3859 | 48.4627 | -4132.7417
2022-03-16 05:00 | -14894 | 6.6648 | 29.8969 | 48.4627 | -4365.0005
2022-03-17 06:00 | 0 | 0 | 37.43 | 48.4627 | 0
2022-03-18 07:00 | -11786.4 | 6.6648 | 32.5433 | 48.4627 | -3454.2529
2022-03-19 08:00 | -14005.7 | 6.6648 | 31.0065 | 48.4627 | -4104.6655
2022-03-20 09:00 | -14331.9 | 6.6648 | 30.27 | 48.4627 | -4200.2653
2022-03-21 10:00 | -13269.2 | 6.6648 | 30.6987 | 48.4627 | -3888.8186
2022-03-22 11:00 | -13078.2 | 6.6648 | 30.9016 | 48.4627 | -3832.8421
2022-03-23 12:00 | -12572.7 | 6.6648 | 30.9464 | 48.4627 | -3684.6946
2022-03-24 13:00 | -12339.3 | 6.6648 | 30.9891 | 48.4627 | -3616.2919
2022-03-25 14:00 | -12253.1 | 6.6648 | 31.0663 | 48.4627 | -3591.0291
2022-03-26 15:00 | -12192.8 | 6.6648 | 31.1553 | 48.4627 | -3573.3569
2022-03-27 16:00 | -11740.3 | 6.6648 | 31.4172 | 48.4627 | -3440.7423
2022-03-28 17:00 | -11341.7 | 6.6648 | 31.711 | 48.4627 | -3323.9242
2022-03-29 18:00 | -11503.8 | 6.6648 | 31.6086 | 48.4627 | -3371.431
2022-03-30 19:00 | -11471.5 | 6.6648 | 31.6563 | 48.4627 | -3361.9648
2022-03-31 20:00 | -11687.6 | 6.6648 | 31.5656 | 48.4627 | -3425.2974
2022-04-01 21:00 | -12094.9 | 6.6648 | 31.3116 | 48.4627 | -3544.6653
2022-04-02 22:00 | -12538.3 | 6.6648 | 31.0572 | 48.4627 | -3674.613
2022-04-03 23:00 | -12884.6 | 6.6648 | 30.8358 | 48.4627 | -3776.1035
2022-04-05 | -13186.8 | 6.6648 | 30.5854 | 48.4627 | -3864.6696
2022-04-06 01:00 | -13392.7 | 6.6648 | 30.356 | 48.4627 | -3925.0129
2022-04-07 02:00 | -13579.2 | 6.6648 | 30.1967 | 48.4627 | -3979.6707
2022-04-08 03:00 | -13597.7 | 6.6648 | 30.1362 | 48.4627 | -3985.0925
2022-04-09 04:00 | -13657.3 | 6.6648 | 30.0546 | 48.4627 | -4002.5595
2022-04-10 05:00 | -13721.8 | 6.6648 | 29.9883 | 48.4627 | -4021.4626
2022-04-11 06:00 | 0 | 0 | 36.9406 | 48.4627 | 0
2022-04-12 07:00 | -11671.7 | 6.6648 | 32.2471 | 48.4627 | -3420.6376
2022-04-13 08:00 | -14438.7 | 6.6648 | 30.4293 | 48.4627 | -4231.5653
2022-04-14 09:00 | 0 | 0 | 37.3464 | 48.4627 | 0
2022-04-15 10:00 | -11531.5 | 6.6648 | 32.7293 | 48.4627 | -3379.549
2022-04-16 11:00 | -14425.2 | 6.6648 | 30.9008 | 48.4627 | -4227.6088
2022-04-17 12:00 | -11714.2 | 6.6648 | 31.5213 | 48.4627 | -3433.0931
2022-04-18 13:00 | -10707.3 | 6.6648 | 32.1702 | 48.4627 | -3137.9999
2022-04-19 14:00 | -10736.9 | 6.6648 | 32.3751 | 48.4627 | -3146.6748
2022-04-20 15:00 | -10476.5 | 6.6648 | 32.3879 | 48.4627 | -3070.3591
2022-04-21 16:00 | -10671.2 | 6.6648 | 32.3598 | 48.4627 | -3127.42
2022-04-22 17:00 | -9212.23 | 6.6648 | 33.1998 | 48.4627 | -2699.8381
2022-04-23 18:00 | -9697.59 | 6.6648 | 33.0335 | 48.4627 | -2842.0831
2022-04-24 19:00 | -9909.24 | 6.6648 | 32.981 | 48.4627 | -2904.1116
2022-04-25 20:00 | -10093.9 | 6.6648 | 32.9158 | 48.4627 | -2958.2301
2022-04-26 21:00 | -10106.8 | 6.6648 | 32.8055 | 48.4627 | -2962.0107
2022-04-27 22:00 | -10242.5 | 6.6648 | 32.7709 | 48.4627 | -3001.7804
2022-04-28 23:00 | -10435.2 | 6.6648 | 32.7052 | 48.4627 | -3058.2552
2022-04-30 | -11601.7 | 6.6648 | 32.0974 | 48.4627 | -3400.1226
2022-05-01 01:00 | -11748.8 | 6.6648 | 31.8826 | 48.4627 | -3443.2334
2022-05-02 02:00 | -11823.8 | 6.6648 | 31.7804 | 48.4627 | -3465.2137
2022-05-03 03:00 | -11923.1 | 6.6648 | 31.6963 | 48.4627 | -3494.3157
2022-05-04 04:00 | -11990.3 | 6.6648 | 31.6148 | 48.4627 | -3514.0101
2022-05-05 05:00 | -12177.4 | 6.6648 | 31.4769 | 48.4627 | -3568.8436
2022-05-06 06:00 | -12581.1 | 6.6648 | 31.1522 | 48.4627 | -3687.1564
2022-05-07 07:00 | -12566.1 | 6.6648 | 31.0848 | 48.4627 | -3682.7604
2022-05-08 08:00 | -12374.3 | 6.6648 | 31.1318 | 48.4627 | -3626.5493
2022-05-09 09:00 | -12392.9 | 6.6648 | 31.062 | 48.4627 | -3632.0005
2022-05-10 10:00 | -12108.7 | 6.6648 | 31.1876 | 48.4627 | -3548.7097
2022-05-11 11:00 | -11186 | 6.6648 | 31.6835 | 48.4627 | -3278.293
2022-05-12 12:00 | -10482.5 | 6.6648 | 32.1505 | 48.4627 | -3072.1175
2022-05-13 13:00 | -10344 | 6.6648 | 32.3466 | 48.4627 | -3031.5271
2022-05-14 14:00 | -10512.7 | 6.6648 | 32.3269 | 48.4627 | -3080.9682
2022-05-15 15:00 | -10730.8 | 6.6648 | 32.2532 | 48.4627 | -3144.887
2022-05-16 16:00 | -11541 | 6.6648 | 31.8547 | 48.4627 | -3382.3332
2022-05-17 17:00 | -11093.9 | 6.6648 | 32.0153 | 48.4627 | -3251.3011
2022-05-18 18:00 | -11846.5 | 6.6648 | 31.6384 | 48.4627 | -3471.8664
2022-05-19 19:00 | -12214.6 | 6.6648 | 31.3824 | 48.4627 | -3579.7459
2022-05-20 20:00 | -12694.5 | 6.6648 | 31.0411 | 48.4627 | -3720.3907
2022-05-21 21:00 | -13112.9 | 6.6648 | 30.7349 | 48.4627 | -3843.0116
2022-05-22 22:00 | -13450.8 | 6.6648 | 30.4724 | 48.4627 | -3942.0403
2022-05-23 23:00 | -13814.7 | 6.6648 | 30.1796 | 48.4627 | -4048.6889
2022-05-25 | -14453.1 | 6.6648 | 29.7302 | 48.4627 | -4235.7855
2022-05-26 01:00 | 0 | 0 | 37.0323 | 48.4627 | 0
2022-05-27 02:00 | -12124.6 | 6.6648 | 32.1242 | 48.4627 | -3553.3695
2022-05-28 03:00 | -14248.6 | 6.6648 | 30.6001 | 48.4627 | -4175.8524
2022-05-29 04:00 | -14561.5 | 6.6648 | 29.9418 | 48.4627 | -4267.5544
2022-05-30 05:00 | 0 | 0 | 37.3183 | 48.4627 | 0
2022-05-31 06:00 | -11909.2 | 6.6648 | 32.5302 | 48.4627 | -3490.242
2022-06-01 07:00 | -14006.7 | 6.6648 | 30.8351 | 48.4627 | -4104.9586
2022-06-02 08:00 | -14284.4 | 6.6648 | 30.2002 | 48.4627 | -4186.3444
2022-06-03 09:00 | -15066 | 6.6648 | 29.6752 | 48.4627 | -4415.4087
2022-06-04 10:00 | 0 | 0 | 37.3369 | 48.4627 | 0
2022-06-05 11:00 | -11265.8 | 6.6648 | 32.7192 | 48.4627 | -3301.6801
2022-06-06 12:00 | -13351 | 6.6648 | 31.304 | 48.4627 | -3912.7919
2022-06-07 13:00 | -11350 | 6.6648 | 31.7916 | 48.4627 | -3326.3566
2022-06-08 14:00 | -11181.2 | 6.6648 | 32.0171 | 48.4627 | -3276.8862
2022-06-09 15:00 | -11420.2 | 6.6648 | 32.0429 | 48.4627 | -3346.9302
2022-06-10 16:00 | -11638.4 | 6.6648 | 31.75 | 48.4627 | -3410.8783
2022-06-11 17:00 | -12224.8 | 6.6648 | 31.3183 | 48.4627 | -3582.7352
2022-06-12 18:00 | -12773.5 | 6.6648 | 30.9994 | 48.4627 | -3743.5433
2022-06-13 19:00 | -13183.4 | 6.6648 | 30.7139 | 48.4627 | -3863.6731
2022-06-14 20:00 | -13593.5 | 6.6648 | 30.4275 | 48.4627 | -3983.8616
2022-06-15 21:00 | -13940 | 6.6648 | 30.154 | 48.4627 | -4085.4107
2022-06-16 22:00 | 0 | 0 | 37.1359 | 48.4627 | 0
2022-06-17 23:00 | -12313.2 | 6.6648 | 32.1068 | 48.4627 | -3608.6427
2022-06-19 | -14401.5 | 6.6648 | 30.5903 | 48.4627 | -4220.663
2022-06-20 01:00 | -14746.4 | 6.6648 | 29.8262 | 48.4627 | -4321.7432
2022-06-21 02:00 | 0 | 0 | 37.2809 | 48.4627 | 0
2022-06-22 03:00 | -12218.9 | 6.6648 | 32.3848 | 48.4627 | -3581.0061
2022-06-23 04:00 | -14296.5 | 6.6648 | 30.6842 | 48.4627 | -4189.8906
2022-06-24 05:00 | -14471.7 | 6.6648 | 30.0237 | 48.4627 | -4241.2366
2022-06-25 06:00 | 0 | 0 | 37.3701 | 48.4627 | 0
2022-06-26 07:00 | -12249.8 | 6.6648 | 32.4707 | 48.4627 | -3590.062
2022-06-27 08:00 | -13695.4 | 6.6648 | 31.1007 | 48.4627 | -4013.7255
2022-06-28 09:00 | -13819.1 | 6.6648 | 30.612 | 48.4627 | -4049.9784
2022-06-29 10:00 | -14018.5 | 6.6648 | 30.2882 | 48.4627 | -4108.4168
2022-06-30 11:00 | -13845.9 | 6.6648 | 30.332 | 48.4627 | -4057.8327
2022-07-01 12:00 | -12392.3 | 6.6648 | 30.8536 | 48.4627 | -3631.8246
2022-07-02 13:00 | -12047.1 | 6.6648 | 31.1438 | 48.4627 | -3530.6565
2022-07-03 14:00 | -11478.2 | 6.6648 | 31.418 | 48.4627 | -3363.9284
2022-07-04 15:00 | -11591.7 | 6.6648 | 31.451 | 48.4627 | -3397.1919
2022-07-05 16:00 | -11818.3 | 6.6648 | 31.3957 | 48.4627 | -3463.6018
2022-07-06 17:00 | -12338.8 | 6.6648 | 31.163 | 48.4627 | -3616.1453
2022-07-07 18:00 | -12698.9 | 6.6648 | 30.8351 | 48.4627 | -3721.6802
2022-07-08 19:00 | -13024.8 | 6.6648 | 30.6143 | 48.4627 | -3817.1921
2022-07-09 20:00 | -13365.6 | 6.6648 | 30.3869 | 48.4627 | -3917.0707
2022-07-10 21:00 | -13820.2 | 6.6648 | 30.0873 | 48.4627 | -4050.3008
2022-07-11 22:00 | 0 | 0 | 37.0763 | 48.4627 | 0
2022-07-12 23:00 | -12440.6 | 6.6648 | 31.9869 | 48.4627 | -3645.98
2022-07-14 | -14320.7 | 6.6648 | 30.5524 | 48.4627 | -4196.9829
2022-07-15 01:00 | -14513.4 | 6.6648 | 29.9415 | 48.4627 | -4253.4577
2022-07-16 02:00 | 0 | 0 | 37.2515 | 48.4627 | 0
2022-07-17 03:00 | -11965.1 | 6.6648 | 32.4702 | 48.4627 | -3506.6247
2022-07-18 04:00 | -14077.9 | 6.6648 | 30.7705 | 48.4627 | -4125.8252
2022-07-19 05:00 | -14224.5 | 6.6648 | 30.1794 | 48.4627 | -4168.7894
2022-07-20 06:00 | -14136.7 | 6.6648 | 30.0682 | 48.4627 | -4143.0578
2022-07-21 07:00 | -14910.5 | 6.6648 | 29.6557 | 48.4627 | -4369.8362
2022-07-22 08:00 | 0 | 0 | 37.0192 | 48.4627 | 0
2022-07-23 09:00 | -12063 | 6.6648 | 32.1796 | 48.4627 | -3535.3163
2022-07-24 10:00 | -13442.5 | 6.6648 | 30.9637 | 48.4627 | -3939.6079
2022-07-25 11:00 | -14382.5 | 6.6648 | 30.0855 | 48.4627 | -4215.0947
2022-07-26 12:00 | 0 | 0 | 37.3737 | 48.4627 | 0
2022-07-27 13:00 | -11909.1 | 6.6648 | 32.6268 | 48.4627 | -3490.2127
2022-07-28 14:00 | -14245.7 | 6.6648 | 30.6945 | 48.4627 | -4175.0025
2022-07-29 15:00 | -14428.8 | 6.6648 | 30.0628 | 48.4627 | -4228.6639
2022-07-30 16:00 | 0 | 0 | 37.3857 | 48.4627 | 0
2022-07-31 17:00 | -11700.6 | 6.6648 | 32.7595 | 48.4627 | -3429.1074
2022-08-01 18:00 | -14994 | 6.6648 | 30.4867 | 48.4627 | -4394.3076
2022-08-02 19:00 | 0 | 0 | 37.6222 | 48.4627 | 0
2022-08-03 20:00 | -11840 | 6.6648 | 32.7681 | 48.4627 | -3469.9615
2022-08-04 21:00 | -15279.2 | 6.6648 | 30.6458 | 48.4627 | -4477.8915
2022-08-05 22:00 | 0 | 0 | 37.6187 | 48.4627 | 0
2022-08-06 23:00 | -12137.4 | 6.6648 | 32.7043 | 48.4627 | -3557.1208
2022-08-08 | -14568.9 | 6.6648 | 30.9868 | 48.4627 | -4269.7231
2022-08-09 01:00 | -15030.8 | 6.6648 | 30.0063 | 48.4627 | -4405.0926
2022-08-10 02:00 | 0 | 0 | 37.5039 | 48.4627 | 0
2022-08-11 03:00 | -11982.2 | 6.6648 | 32.7836 | 48.4627 | -3511.6362
2022-08-12 04:00 | -14166.3 | 6.6648 | 30.9574 | 48.4627 | -4151.7327
2022-08-13 05:00 | -15210.6 | 6.6648 | 29.9113 | 48.4627 | -4457.7868
2022-08-14 06:00 | 0 | 0 | 37.568 | 48.4627 | 0
2022-08-15 07:00 | -11852.2 | 6.6648 | 32.8025 | 48.4627 | -3473.5369
2022-08-16 08:00 | -14063.2 | 6.6648 | 31.018 | 48.4627 | -4121.5171
2022-08-17 09:00 | -13463.7 | 6.6648 | 30.8423 | 48.4627 | -3945.821
2022-08-18 10:00 | -11945.9 | 6.6648 | 31.5078 | 48.4627 | -3500.9977
2022-08-19 11:00 | -10163.8 | 6.6648 | 32.6131 | 48.4627 | -2978.7157
2022-08-20 12:00 | -9079.31 | 6.6648 | 33.1647 | 48.4627 | -2660.8831
2022-08-21 13:00 | -8780.67 | 6.6648 | 33.5538 | 48.4627 | -2573.3604
2022-08-22 14:00 | -8516.54 | 6.6648 | 33.7727 | 48.4627 | -2495.9515
2022-08-23 15:00 | -8459.81 | 6.6648 | 33.9704 | 48.4627 | -2479.3256
2022-08-24 16:00 | -8364.08 | 6.6648 | 34.1124 | 48.4627 | -2451.2699
2022-08-25 17:00 | -9365.7 | 6.6648 | 33.72 | 48.4627 | -2744.8157
2022-08-26 18:00 | -9628.82 | 6.6648 | 33.4733 | 48.4627 | -2821.9286
2022-08-27 19:00 | -10259.4 | 6.6648 | 33.0816 | 48.4627 | -3006.7333
2022-08-28 20:00 | -9998.72 | 6.6648 | 33.1784 | 48.4627 | -2930.3356
2022-08-29 21:00 | -10732.3 | 6.6648 | 32.8404 | 48.4627 | -3145.3266
2022-08-30 22:00 | -10492.5 | 6.6648 | 32.8294 | 48.4627 | -3075.0482
2022-08-31 23:00 | -11079.7 | 6.6648 | 32.5205 | 48.4627 | -3247.1395
2022-09-02 | -10969.4 | 6.6648 | 32.5211 | 48.4627 | -3214.8138
2022-09-03 01:00 | -10975.2 | 6.6648 | 32.4946 | 48.4627 | -3216.5136
2022-09-04 02:00 | -11371.3 | 6.6648 | 32.1921 | 48.4627 | -3332.5991
2022-09-05 03:00 | -11116.4 | 6.6648 | 32.2658 | 48.4627 | -3257.8952
2022-09-06 04:00 | -11040.7 | 6.6648 | 32.3025 | 48.4627 | -3235.7098
2022-09-07 05:00 | -10804.9 | 6.6648 | 32.4359 | 48.4627 | -3166.6036
2022-09-08 06:00 | -10584.6 | 6.6648 | 32.5184 | 48.4627 | -3102.04
2022-09-09 07:00 | -10294.5 | 6.6648 | 32.7106 | 48.4627 | -3017.0201
2022-09-10 08:00 | -9005.74 | 6.6648 | 33.4103 | 48.4627 | -2639.3219
2022-09-11 09:00 | -8040.08 | 6.6648 | 34.084 | 48.4627 | -2356.3148
2022-09-12 10:00 | -6231.18 | 6.6648 | 35.1998 | 48.4627 | -1826.1786
2022-09-13 11:00 | -5186.56 | 6.6648 | 36.0369 | 48.4627 | -1520.0307
2022-09-14 12:00 | -3984.81 | 6.6648 | 36.9137 | 48.4627 | -1167.8325
2022-09-15 13:00 | -3392.11 | 6.6648 | 37.5313 | 48.4627 | -994.1293
2022-09-16 14:00 | -3278.23 | 6.6648 | 37.8736 | 48.4627 | -960.7544
2022-09-17 15:00 | -3460.6 | 6.6648 | 38.0034 | 48.4627 | -1014.2017
2022-09-18 16:00 | -3421.29 | 6.6648 | 38.1499 | 48.4627 | -1002.6811
2022-09-19 17:00 | -4899.13 | 6.6648 | 37.5394 | 48.4627 | -1435.7933
2022-09-20 18:00 | -5284.17 | 6.6648 | 37.3314 | 48.4627 | -1548.6374
2022-09-21 19:00 | -6072.97 | 6.6648 | 36.8997 | 48.4627 | -1779.8118
2022-09-22 20:00 | -6808.79 | 6.6648 | 36.4806 | 48.4627 | -1995.4594
2022-09-23 21:00 | -7872.07 | 6.6648 | 35.8616 | 48.4627 | -2307.076
2022-09-24 22:00 | -8258.59 | 6.6648 | 35.4779 | 48.4627 | -2420.3538
2022-09-25 23:00 | -9421.45 | 6.6648 | 34.7773 | 48.4627 | -2761.1544
2022-09-27 | -10150.5 | 6.6648 | 34.2283 | 48.4627 | -2974.8179
2022-09-28 01:00 | -10262.3 | 6.6648 | 33.9838 | 48.4627 | -3007.5832
2022-09-29 02:00 | -10462.4 | 6.6648 | 33.7157 | 48.4627 | -3066.2268
2022-09-30 03:00 | -10455.1 | 6.6648 | 33.6126 | 48.4627 | -3064.0873
2022-10-01 04:00 | -10850.8 | 6.6648 | 33.3246 | 48.4627 | -3180.0556
2022-10-02 05:00 | -11530.1 | 6.6648 | 32.8903 | 48.4627 | -3379.1387
2022-10-03 06:00 | -11448 | 6.6648 | 32.7563 | 48.4627 | -3355.0776
2022-10-04 07:00 | -10416.8 | 6.6648 | 33.2082 | 48.4627 | -3052.8627
2022-10-05 08:00 | -8809.81 | 6.6648 | 34.084 | 48.4627 | -2581.9004
2022-10-06 09:00 | -7931.85 | 6.6648 | 34.7037 | 48.4627 | -2324.5958
2022-10-07 10:00 | -6875.32 | 6.6648 | 35.4048 | 48.4627 | -2014.9574
2022-10-08 11:00 | -5465.46 | 6.6648 | 36.3265 | 48.4627 | -1601.7682
2022-10-09 12:00 | -4544.5 | 6.6648 | 37.0662 | 48.4627 | -1331.8615
2022-10-10 13:00 | -4072.69 | 6.6648 | 37.5629 | 48.4627 | -1193.5876
2022-10-11 14:00 | -3941.31 | 6.6648 | 37.8326 | 48.4627 | -1155.0839
2022-10-12 15:00 | -4004.35 | 6.6648 | 37.9598 | 48.4627 | -1173.5591
2022-10-13 16:00 | -4680.14 | 6.6648 | 37.7364 | 48.4627 | -1371.6136
2022-10-14 17:00 | -4209.8 | 6.6648 | 38.0226 | 48.4627 | -1233.7706
2022-10-15 18:00 | -5128.79 | 6.6648 | 37.6614 | 48.4627 | -1503.1
2022-10-16 19:00 | -5776.1 | 6.6648 | 37.3342 | 48.4627 | -1692.8078
2022-10-17 20:00 | -6412.78 | 6.6648 | 36.9626 | 48.4627 | -1879.4003
2022-10-18 21:00 | -6719.82 | 6.6648 | 36.7467 | 48.4627 | -1969.3848
2022-10-19 22:00 | -7128.55 | 6.6648 | 36.4805 | 48.4627 | -2089.1718
2022-10-20 23:00 | -7484.25 | 6.6648 | 36.2291 | 48.4627 | -2193.4172
2022-10-22 | -8932.67 | 6.6648 | 35.4198 | 48.4627 | -2617.9072
2022-10-23 01:00 | -9252.18 | 6.6648 | 35.0765 | 48.4627 | -2711.5463
2022-10-24 02:00 | -9341.44 | 6.6648 | 34.8857 | 48.4627 | -2737.7058
2022-10-25 03:00 | -9554.84 | 6.6648 | 34.6889 | 48.4627 | -2800.2472
2022-10-26 04:00 | -9826.07 | 6.6648 | 34.4685 | 48.4627 | -2879.7368
2022-10-27 05:00 | -9861.28 | 6.6648 | 34.3576 | 48.4627 | -2890.0559
2022-10-28 06:00 | -10276.1 | 6.6648 | 34.0886 | 48.4627 | -3011.6276
2022-10-29 07:00 | -9320.84 | 6.6648 | 34.5016 | 48.4627 | -2731.6686
2022-10-30 08:00 | -7840.76 | 6.6648 | 35.2811 | 48.4627 | -2297.8999
2022-10-31 09:00 | -6900.66 | 6.6648 | 35.9054 | 48.4627 | -2022.3838
2022-11-01 10:00 | -5823.26 | 6.6648 | 36.6139 | 48.4627 | -1706.629
2022-11-02 11:00 | -4451.55 | 6.6648 | 37.5005 | 48.4627 | -1304.6205
2022-11-03 12:00 | -3329.19 | 6.6648 | 38.3223 | 48.4627 | -975.6893
2022-11-04 13:00 | -2979.97 | 6.6648 | 38.7714 | 48.4627 | -873.343
2022-11-05 14:00 | -3808.28 | 6.6648 | 38.5516 | 48.4627 | -1116.0967
2022-11-06 15:00 | -4242.16 | 6.6648 | 38.3968 | 48.4627 | -1243.2544
2022-11-07 16:00 | -4163.62 | 6.6648 | 38.4594 | 48.4627 | -1220.2366
2022-11-08 17:00 | -3642.77 | 6.6648 | 38.7844 | 48.4627 | -1067.5905
2022-11-09 18:00 | -4720.61 | 6.6648 | 38.3446 | 48.4627 | -1383.4742
2022-11-10 19:00 | -4982.58 | 6.6648 | 38.1677 | 48.4627 | -1460.2501
2022-11-11 20:00 | -5602.57 | 6.6648 | 37.8314 | 48.4627 | -1641.9512
2022-11-12 21:00 | -5795.94 | 6.6648 | 37.696 | 48.4627 | -1698.6223
2022-11-13 22:00 | -6323.14 | 6.6648 | 37.3799 | 48.4627 | -1853.1294
2022-11-14 23:00 | -6685.01 | 6.6648 | 37.1162 | 48.4627 | -1959.183
2022-11-16 | -7760.27 | 6.6648 | 36.4974 | 48.4627 | -2274.3106
2022-11-17 01:00 | -8085.78 | 6.6648 | 36.1869 | 48.4627 | -2369.7082
2022-11-18 02:00 | -8199.98 | 6.6648 | 36.0088 | 48.4627 | -2403.1769
2022-11-19 03:00 | -8201.88 | 6.6648 | 35.937 | 48.4627 | -2403.7337
2022-11-20 04:00 | -8059.69 | 6.6648 | 35.9639 | 48.4627 | -2362.062
2022-11-21 05:00 | -8034 | 6.6648 | 35.9526 | 48.4627 | -2354.533
2022-11-22 06:00 | -7612.2 | 6.6648 | 36.1533 | 48.4627 | -2230.9156
2022-11-23 07:00 | -7786.34 | 6.6648 | 36.0997 | 48.4627 | -2281.951
2022-11-24 08:00 | -7835.14 | 6.6648 | 36.0706 | 48.4627 | -2296.2529
2022-11-25 09:00 | -8263.24 | 6.6648 | 35.8377 | 48.4627 | -2421.7166
2022-11-26 10:00 | -8247.06 | 6.6648 | 35.7901 | 48.4627 | -2416.9747
2022-11-27 11:00 | -8261.18 | 6.6648 | 35.7394 | 48.4627 | -2421.1129
2022-11-28 12:00 | -8102.37 | 6.6648 | 35.7792 | 48.4627 | -2374.5702
2022-11-29 13:00 | -8120.7 | 6.6648 | 35.7471 | 48.4627 | -2379.9422
2022-11-30 14:00 | -8084.1 | 6.6648 | 35.7395 | 48.4627 | -2369.2158
2022-12-01 15:00 | -8128.35 | 6.6648 | 35.6998 | 48.4627 | -2382.1842
2022-12-02 16:00 | -7310.94 | 6.6648 | 36.0962 | 48.4627 | -2142.625
2022-12-03 17:00 | -7353.59 | 6.6648 | 36.1321 | 48.4627 | -2155.1245
2022-12-04 18:00 | -7150.42 | 6.6648 | 36.2573 | 48.4627 | -2095.5812
2022-12-05 19:00 | -7558.96 | 6.6648 | 36.0763 | 48.4627 | -2215.3125
2022-12-06 20:00 | -7792.19 | 6.6648 | 35.9407 | 48.4627 | -2283.6655
2022-12-07 21:00 | -8799.29 | 6.6648 | 35.4044 | 48.4627 | -2578.8173
2022-12-08 22:00 | -8770.52 | 6.6648 | 35.3078 | 48.4627 | -2570.3857
2022-12-09 23:00 | -9760.76 | 6.6648 | 34.7439 | 48.4627 | -2860.5964
2022-12-11 | -10165.4 | 6.6648 | 34.4079 | 48.4627 | -2979.1847
2022-12-12 01:00 | -10204.3 | 6.6648 | 34.2582 | 48.4627 | -2990.5851
2022-12-13 02:00 | -10178.8 | 6.6648 | 34.1933 | 48.4627 | -2983.1118
2022-12-14 03:00 | -10162.4 | 6.6648 | 34.1567 | 48.4627 | -2978.3054
2022-12-15 04:00 | -10304.4 | 6.6648 | 34.0332 | 48.4627 | -3019.9215
2022-12-16 05:00 | -9992.4 | 6.6648 | 34.136 | 48.4627 | -2928.4834
2022-12-17 06:00 | -9664.88 | 6.6648 | 34.29 | 48.4627 | -2832.4967
2022-12-18 07:00 | -9820.99 | 6.6648 | 34.2252 | 48.4627 | -2878.248
2022-12-19 08:00 | -9745.84 | 6.6648 | 34.2398 | 48.4627 | -2856.2238
2022-12-20 09:00 | -9888.22 | 6.6648 | 34.156 | 48.4627 | -2897.9512
2022-12-21 10:00 | -8362.55 | 6.6648 | 34.9048 | 48.4627 | -2450.8215
2022-12-22 11:00 | -7383.53 | 6.6648 | 35.5299 | 48.4627 | -2163.899
2022-12-23 12:00 | -7524.1 | 6.6648 | 35.6154 | 48.4627 | -2205.096
2022-12-24 13:00 | -5806.01 | 6.6648 | 36.5613 | 48.4627 | -1701.5736
2022-12-25 14:00 | -5753.55 | 6.6648 | 36.8058 | 48.4627 | -1686.1991
2022-12-26 15:00 | -5941.76 | 6.6648 | 36.868 | 48.4627 | -1741.358
2022-12-27 16:00 | -5949.33 | 6.6648 | 36.9283 | 48.4627 | -1743.5765
2022-12-28 17:00 | -6681.78 | 6.6648 | 36.609 | 48.4627 | -1958.2364
2022-12-29 18:00 | -7060.13 | 6.6648 | 36.4054 | 48.4627 | -2069.1199
2022-12-30 19:00 | -7671.76 | 6.6648 | 36.052 | 48.4627 | -2248.3709
2022-12-31 20:00 | -8288.13 | 6.6648 | 35.671 | 48.4627 | -2429.0111
2023-01-01 21:00 | -9375.28 | 6.6648 | 35.0286 | 48.4627 | -2747.6233
2023-01-02 22:00 | -9829.67 | 6.6648 | 34.6279 | 48.4627 | -2880.7919
2023-01-03 23:00 | -10450.3 | 6.6648 | 34.1745 | 48.4627 | -3062.6806
2023-01-05 | -11104.8 | 6.6648 | 33.7008 | 48.4627 | -3254.4956
2023-01-06 01:00 | -11519.3 | 6.6648 | 33.3127 | 48.4627 | -3375.9736
2023-01-07 02:00 | -11745.8 | 6.6648 | 33.0308 | 48.4627 | -3442.3542
2023-01-08 03:00 | -11868.1 | 6.6648 | 32.84 | 48.4627 | -3478.1968
2023-01-09 04:00 | -11899.9 | 6.6648 | 32.7129 | 48.4627 | -3487.5164
2023-01-10 05:00 | -11835.3 | 6.6648 | 32.655 | 48.4627 | -3468.584
2023-01-11 06:00 | -11803.2 | 6.6648 | 32.5986 | 48.4627 | -3459.1765
2023-01-12 07:00 | -11882.2 | 6.6648 | 32.5049 | 48.4627 | -3482.3291
2023-01-13 08:00 | -11899.2 | 6.6648 | 32.4396 | 48.4627 | -3487.3113
2023-01-14 09:00 | -11370 | 6.6648 | 32.6679 | 48.4627 | -3332.2181
2023-01-15 10:00 | -10894.6 | 6.6648 | 32.9178 | 48.4627 | -3192.8921
2023-01-16 11:00 | -10066.4 | 6.6648 | 33.3758 | 48.4627 | -2950.1706
2023-01-17 12:00 | -8470.96 | 6.6648 | 34.2825 | 48.4627 | -2482.5933
2023-01-18 13:00 | -7891.54 | 6.6648 | 34.7738 | 48.4627 | -2312.7821
2023-01-19 14:00 | -7826.49 | 6.6648 | 34.9722 | 48.4627 | -2293.7178
2023-01-20 15:00 | -7823.37 | 6.6648 | 35.0748 | 48.4627 | -2292.8034
2023-01-21 16:00 | -7892.83 | 6.6648 | 35.1117 | 48.4627 | -2313.1601
2023-01-22 17:00 | -8849.02 | 6.6648 | 34.6773 | 48.4627 | -2593.3918
2023-01-23 18:00 | -9528.12 | 6.6648 | 34.2687 | 48.4627 | -2792.4163
2023-01-24 19:00 | -10272.3 | 6.6648 | 33.7963 | 48.4627 | -3010.514
2023-01-25 20:00 | -10869 | 6.6648 | 33.3804 | 48.4627 | -3185.3895
2023-01-26 21:00 | -11601.7 | 6.6648 | 32.8791 | 48.4627 | -3400.1226
2023-01-27 22:00 | -12034.7 | 6.6648 | 32.4997 | 48.4627 | -3527.0224
2023-01-28 23:00 | -12550.8 | 6.6648 | 32.1011 | 48.4627 | -3678.2764
2023-01-30 | -12972.9 | 6.6648 | 31.7356 | 48.4627 | -3801.9817
2023-01-31 01:00 | -13207.8 | 6.6648 | 31.4698 | 48.4627 | -3870.8241
2023-02-01 02:00 | -13426.1 | 6.6648 | 31.2233 | 48.4627 | -3934.8015
2023-02-02 03:00 | -13509.8 | 6.6648 | 31.0638 | 48.4627 | -3959.3315
2023-02-03 04:00 | -13549.9 | 6.6648 | 30.9392 | 48.4627 | -3971.0837
2023-02-04 05:00 | -13598.1 | 6.6648 | 30.8343 | 48.4627 | -3985.2097
2023-02-05 06:00 | -13504.3 | 6.6648 | 30.8141 | 48.4627 | -3957.7197
2023-02-06 07:00 | -13322.8 | 6.6648 | 30.8621 | 48.4627 | -3904.5273
2023-02-07 08:00 | -12816.1 | 6.6648 | 31.0889 | 48.4627 | -3756.0281
2023-02-08 09:00 | -11696.1 | 6.6648 | 31.6869 | 48.4627 | -3427.7885
2023-02-09 10:00 | -9995.88 | 6.6648 | 32.6691 | 48.4627 | -2929.5032
2023-02-10 11:00 | -8833.14 | 6.6648 | 33.4816 | 48.4627 | -2588.7378
2023-02-11 12:00 | -7810.32 | 6.6648 | 34.2251 | 48.4627 | -2288.9788
2023-02-12 13:00 | -7460.56 | 6.6648 | 34.63 | 48.4627 | -2186.4743
2023-02-13 14:00 | -7325.93 | 6.6648 | 34.8788 | 48.4627 | -2147.0181
2023-02-14 15:00 | -7918.26 | 6.6648 | 34.7149 | 48.4627 | -2320.6129
2023-02-15 16:00 | -7759.62 | 6.6648 | 34.8287 | 48.4627 | -2274.1201
2023-02-16 17:00 | -8984.22 | 6.6648 | 34.2631 | 48.4627 | -2633.015
2023-02-17 18:00 | -9270.32 | 6.6648 | 34.0531 | 48.4627 | -2716.8626
2023-02-18 19:00 | -10125.7 | 6.6648 | 33.5602 | 48.4627 | -2967.5497
2023-02-19 20:00 | -10216.4 | 6.6648 | 33.4144 | 48.4627 | -2994.1313
2023-02-20 21:00 | -11789.3 | 6.6648 | 32.5544 | 48.4627 | -3455.1028
2023-02-21 22:00 | -11920.6 | 6.6648 | 32.2803 | 48.4627 | -3493.583
2023-02-22 23:00 | -12246.7 | 6.6648 | 31.9844 | 48.4627 | -3589.1535
2023-02-24 | -12759.1 | 6.6648 | 31.6019 | 48.4627 | -3739.3231
2023-02-25 01:00 | -13110.2 | 6.6648 | 31.2846 | 48.4627 | -3842.2203
2023-02-26 02:00 | -13303.5 | 6.6648 | 31.0382 | 48.4627 | -3898.871
2023-02-27 03:00 | -13435.7 | 6.6648 | 30.8694 | 48.4627 | -3937.615
2023-02-28 04:00 | -13510.8 | 6.6648 | 30.732 | 48.4627 | -3959.6246
2023-03-01 05:00 | -13638.2 | 6.6648 | 30.5898 | 48.4627 | -3996.9619
2023-03-02 06:00 | -13564.6 | 6.6648 | 30.5476 | 48.4627 | -3975.3918
2023-03-03 07:00 | -13268.6 | 6.6648 | 30.6537 | 48.4627 | -3888.6428
2023-03-04 08:00 | -12930.2 | 6.6648 | 30.8111 | 48.4627 | -3789.4675
2023-03-05 09:00 | -12533.6 | 6.6648 | 31.0307 | 48.4627 | -3673.2356
2023-03-06 10:00 | -12248.7 | 6.6648 | 31.2048 | 48.4627 | -3589.7396
2023-03-07 11:00 | -11567.1 | 6.6648 | 31.5836 | 48.4627 | -3389.9824
2023-03-08 12:00 | -10623.3 | 6.6648 | 32.1388 | 48.4627 | -3113.3819
2023-03-09 13:00 | -9142.69 | 6.6648 | 33.0234 | 48.4627 | -2679.4579
2023-03-10 14:00 | -9094.03 | 6.6648 | 33.2532 | 48.4627 | -2665.1971
2023-03-11 15:00 | -9297.35 | 6.6648 | 33.2713 | 48.4627 | -2724.7843
2023-03-12 16:00 | -8833.73 | 6.6648 | 33.5699 | 48.4627 | -2588.9107
2023-03-13 17:00 | -8737.3 | 6.6648 | 33.7292 | 48.4627 | -2560.6499
2023-03-14 18:00 | -8370.45 | 6.6648 | 34.0086 | 48.4627 | -2453.1367
2023-03-15 19:00 | -8801.78 | 6.6648 | 33.8788 | 48.4627 | -2579.5471
2023-03-16 20:00 | -9259.19 | 6.6648 | 33.6691 | 48.4627 | -2713.6007
2023-03-17 21:00 | -10121.7 | 6.6648 | 33.2273 | 48.4627 | -2966.3774
2023-03-18 22:00 | -10303.9 | 6.6648 | 33.0679 | 48.4627 | -3019.775
2023-03-19 23:00 | -11265.7 | 6.6648 | 32.5365 | 48.4627 | -3301.6508
2023-03-21 | -11546.5 | 6.6648 | 32.2729 | 48.4627 | -3383.9451
2023-03-22 01:00 | -11416.6 | 6.6648 | 32.2388 | 48.4627 | -3345.8752
2023-03-23 02:00 | -11453.2 | 6.6648 | 32.1774 | 48.4627 | -3356.6016
2023-03-24 03:00 | -11402.2 | 6.6648 | 32.175 | 48.4627 | -3341.655
2023-03-25 04:00 | -11441.7 | 6.6648 | 32.1292 | 48.4627 | -3353.2313
2023-03-26 05:00 | -11327.7 | 6.6648 | 32.1723 | 48.4627 | -3319.8212
2023-03-27 06:00 | -11274.8 | 6.6648 | 32.1929 | 48.4627 | -3304.3177
2023-03-28 07:00 | -10532.2 | 6.6648 | 32.5728 | 48.4627 | -3086.6831
2023-03-29 08:00 | -10062.8 | 6.6648 | 32.8834 | 48.4627 | -2949.1156
2023-03-30 09:00 | -9750.03 | 6.6648 | 33.129 | 48.4627 | -2857.4517
2023-03-31 10:00 | -8949.34 | 6.6648 | 33.6128 | 48.4627 | -2622.7926
2023-04-01 11:00 | -7831.04 | 6.6648 | 34.3154 | 48.4627 | -2295.0513
2023-04-02 12:00 | -7098.25 | 6.6648 | 34.8786 | 48.4627 | -2080.2917
2023-04-03 13:00 | -6591.29 | 6.6648 | 35.3125 | 48.4627 | -1931.7164
2023-04-04 14:00 | -6652.47 | 6.6648 | 35.4398 | 48.4627 | -1949.6465
2023-04-05 15:00 | -5886.47 | 6.6648 | 35.9418 | 48.4627 | -1725.1541
2023-04-06 16:00 | -6488.68 | 6.6648 | 35.7941 | 48.4627 | -1901.6444
2023-04-07 17:00 | -5940.28 | 6.6648 | 36.1299 | 48.4627 | -1740.9242
2023-04-08 18:00 | -6489.63 | 6.6648 | 35.9516 | 48.4627 | -1901.9228
2023-04-09 19:00 | -7293.47 | 6.6648 | 35.5708 | 48.4627 | -2137.5051
2023-04-10 20:00 | -8248.81 | 6.6648 | 35.042 | 48.4627 | -2417.4876
2023-04-11 21:00 | -8961.04 | 6.6648 | 34.5795 | 48.4627 | -2626.2216
2023-04-12 22:00 | -9309.86 | 6.6648 | 34.3004 | 48.4627 | -2728.4506
2023-04-13 23:00 | -9800.22 | 6.6648 | 33.956 | 48.4627 | -2872.161
2023-04-15 | -11162.2 | 6.6648 | 33.1535 | 48.4627 | -3271.3179
2023-04-16 01:00 | -11684.4 | 6.6648 | 32.6772 | 48.4627 | -3424.3596
2023-04-17 02:00 | -11767.4 | 6.6648 | 32.4675 | 48.4627 | -3448.6845
2023-04-18 03:00 | -11879.7 | 6.6648 | 32.297 | 48.4627 | -3481.5964
2023-04-19 04:00 | -12015.5 | 6.6648 | 32.1308 | 48.4627 | -3521.3954
2023-04-20 05:00 | -12146.3 | 6.6648 | 31.964 | 48.4627 | -3559.7291
2023-04-21 06:00 | -12216.2 | 6.6648 | 31.8466 | 48.4627 | -3580.2148
2023-04-22 07:00 | -11451.1 | 6.6648 | 32.1754 | 48.4627 | -3355.9861
2023-04-23 08:00 | -10604 | 6.6648 | 32.6365 | 48.4627 | -3107.7256
2023-04-24 09:00 | -10591.1 | 6.6648 | 32.7267 | 48.4627 | -3103.945
2023-04-25 10:00 | -10221.4 | 6.6648 | 32.9458 | 48.4627 | -2995.5966
2023-04-26 11:00 | -9410.93 | 6.6648 | 33.4057 | 48.4627 | -2758.0713
2023-04-27 12:00 | -9252.12 | 6.6648 | 33.6026 | 48.4627 | -2711.5287
2023-04-28 13:00 | -8730.35 | 6.6648 | 33.9412 | 48.4627 | -2558.613
2023-04-29 14:00 | -9212.34 | 6.6648 | 33.7768 | 48.4627 | -2699.8703
2023-04-30 15:00 | -9165.13 | 6.6648 | 33.8076 | 48.4627 | -2686.0345
2023-05-01 16:00 | -8463.59 | 6.6648 | 34.1834 | 48.4627 | -2480.4334
2023-05-02 17:00 | -7608.62 | 6.6648 | 34.7039 | 48.4627 | -2229.8664
2023-05-03 18:00 | -8304.76 | 6.6648 | 34.4839 | 48.4627 | -2433.8849
2023-05-04 19:00 | -8896.45 | 6.6648 | 34.185 | 48.4627 | -2607.2921
2023-05-05 20:00 | -9715.61 | 6.6648 | 33.7255 | 48.4627 | -2847.3642
2023-05-06 21:00 | -10335.5 | 6.6648 | 33.3333 | 48.4627 | -3029.036
2023-05-07 22:00 | -10843.5 | 6.6648 | 32.9714 | 48.4627 | -3177.9161
2023-05-08 23:00 | -11246.4 | 6.6648 | 32.6454 | 48.4627 | -3295.9945
2023-05-10 | -12127.9 | 6.6648 | 32.0872 | 48.4627 | -3554.3366
2023-05-11 01:00 | -12507.1 | 6.6648 | 31.7357 | 48.4627 | -3665.4692
2023-05-12 02:00 | -12695.5 | 6.6648 | 31.5107 | 48.4627 | -3720.6838
2023-05-13 03:00 | -12928.4 | 6.6648 | 31.2925 | 48.4627 | -3788.94
2023-05-14 04:00 | -13007.1 | 6.6648 | 31.1512 | 48.4627 | -3812.0047
2023-05-15 05:00 | -13194.4 | 6.6648 | 30.9609 | 48.4627 | -3866.8969
2023-05-16 06:00 | -13387.9 | 6.6648 | 30.7744 | 48.4627 | -3923.6062
2023-05-17 07:00 | -13037.2 | 6.6648 | 30.8679 | 48.4627 | -3820.8262
2023-05-18 08:00 | -12236 | 6.6648 | 31.2477 | 48.4627 | -3586.0176
2023-05-19 09:00 | -12176.7 | 6.6648 | 31.3186 | 48.4627 | -3568.6385
2023-05-20 10:00 | -12228.9 | 6.6648 | 31.2966 | 48.4627 | -3583.9368
2023-05-21 11:00 | -10977.2 | 6.6648 | 31.9183 | 48.4627 | -3217.0997
2023-05-22 12:00 | -10333.3 | 6.6648 | 32.3599 | 48.4627 | -3028.3913
2023-05-23 13:00 | -10128 | 6.6648 | 32.5806 | 48.4627 | -2968.2238
2023-05-24 14:00 | -9876.85 | 6.6648 | 32.7773 | 48.4627 | -2894.619
2023-05-25 15:00 | -10048.5 | 6.6648 | 32.7571 | 48.4627 | -2944.9246
2023-05-26 16:00 | -10214 | 6.6648 | 32.7065 | 48.4627 | -2993.4279
2023-05-27 17:00 | -9092.13 | 6.6648 | 33.2793 | 48.4627 | -2664.6403
2023-05-28 18:00 | -9394.67 | 6.6648 | 33.2402 | 48.4627 | -2753.306
2023-05-29 19:00 | -9897.7 | 6.6648 | 33.0223 | 48.4627 | -2900.7295
2023-05-30 20:00 | -10182.1 | 6.6648 | 32.8464 | 48.4627 | -2984.0789
2023-05-31 21:00 | -10248.5 | 6.6648 | 32.7913 | 48.4627 | -3003.5389
2023-06-01 22:00 | -11354.1 | 6.6648 | 32.2262 | 48.4627 | -3327.5582
2023-06-02 23:00 | -11129.6 | 6.6648 | 32.2177 | 48.4627 | -3261.7638
2023-06-04 | -11850.4 | 6.6648 | 31.8029 | 48.4627 | -3473.0094
2023-06-05 01:00 | -11917.1 | 6.6648 | 31.677 | 48.4627 | -3492.5572
2023-06-06 02:00 | -11978.9 | 6.6648 | 31.5785 | 48.4627 | -3510.669
2023-06-07 03:00 | -12239.7 | 6.6648 | 31.3959 | 48.4627 | -3587.102
2023-06-08 04:00 | -12324.3 | 6.6648 | 31.302 | 48.4627 | -3611.8958
2023-06-09 05:00 | -12162 | 6.6648 | 31.3283 | 48.4627 | -3564.3304
2023-06-10 06:00 | -11918.9 | 6.6648 | 31.438 | 48.4627 | -3493.0848
2023-06-11 07:00 | -11787.1 | 6.6648 | 31.51 | 48.4627 | -3454.458
2023-06-12 08:00 | -10893.9 | 6.6648 | 31.9724 | 48.4627 | -3192.6869
2023-06-13 09:00 | -10434.9 | 6.6648 | 32.2942 | 48.4627 | -3058.1673
2023-06-14 10:00 | -9167.18 | 6.6648 | 33.0454 | 48.4627 | -2686.6353
2023-06-15 11:00 | -7761.41 | 6.6648 | 33.9416 | 48.4627 | -2274.6447
2023-06-16 12:00 | -7130.03 | 6.6648 | 34.5094 | 48.4627 | -2089.6055
2023-06-17 13:00 | -6407.17 | 6.6648 | 35.0908 | 48.4627 | -1877.7562
2023-06-18 14:00 | -5953.42 | 6.6648 | 35.5302 | 48.4627 | -1744.7752
2023-06-19 15:00 | -6036.11 | 6.6648 | 35.6893 | 48.4627 | -1769.0092
2023-06-20 16:00 | -5953.77 | 6.6648 | 35.8666 | 48.4627 | -1744.8777
2023-06-21 17:00 | -7327.86 | 6.6648 | 35.2677 | 48.4627 | -2147.5838
2023-06-22 18:00 | -7738.97 | 6.6648 | 35.0139 | 48.4627 | -2268.0682
2023-06-23 19:00 | -8298.52 | 6.6648 | 34.6899 | 48.4627 | -2432.0561
2023-06-24 20:00 | -9483.38 | 6.6648 | 34.0294 | 48.4627 | -2779.3043
2023-06-25 21:00 | -10693.1 | 6.6648 | 33.2716 | 48.4627 | -3133.8383
2023-06-26 22:00 | -11303.9 | 6.6648 | 32.7548 | 48.4627 | -3312.8461
2023-06-27 23:00 | -11925 | 6.6648 | 32.267 | 48.4627 | -3494.8725
2023-06-29 | -12240.4 | 6.6648 | 31.937 | 48.4627 | -3587.3071
2023-06-30 01:00 | -12420.3 | 6.6648 | 31.6875 | 48.4627 | -3640.0306
2023-07-01 02:00 | -12449.3 | 6.6648 | 31.5462 | 48.4627 | -3648.5297
2023-07-02 03:00 | -12440.6 | 6.6648 | 31.4597 | 48.4627 | -3645.98
2023-07-03 04:00 | -12361.1 | 6.6648 | 31.4264 | 48.4627 | -3622.6808
2023-07-04 05:00 | -12196.9 | 6.6648 | 31.4623 | 48.4627 | -3574.5585
2023-07-05 06:00 | -12019.6 | 6.6648 | 31.5288 | 48.4627 | -3522.597
2023-07-06 07:00 | -11713.3 | 6.6648 | 31.6748 | 48.4627 | -3432.8294
2023-07-07 08:00 | -10792.5 | 6.6648 | 32.1624 | 48.4627 | -3162.9695
2023-07-08 09:00 | -9931.16 | 6.6648 | 32.7024 | 48.4627 | -2910.5357
2023-07-09 10:00 | -8958.82 | 6.6648 | 33.3311 | 48.4627 | -2625.571
2023-07-10 11:00 | -8070.63 | 6.6648 | 33.9504 | 48.4627 | -2365.2682
2023-07-11 12:00 | -6513.12 | 6.6648 | 34.9316 | 48.4627 | -1908.807
2023-07-12 13:00 | -5581.15 | 6.6648 | 35.6756 | 48.4627 | -1635.6736
2023-07-13 14:00 | -4409.3 | 6.6648 | 36.5299 | 48.4627 | -1292.2383
2023-07-14 15:00 | -3973.57 | 6.6648 | 37.0314 | 48.4627 | -1164.5384
2023-07-15 16:00 | -3128.72 | 6.6648 | 37.6976 | 48.4627 | -916.9373
2023-07-16 17:00 | -4056.1 | 6.6648 | 37.4814 | 48.4627 | -1188.7256
2023-07-17 18:00 | -4646.55 | 6.6648 | 37.2768 | 48.4627 | -1361.7694
2023-07-18 19:00 | -5671.53 | 6.6648 | 36.796 | 48.4627 | -1662.1614
2023-07-19 20:00 | -5892.69 | 6.6648 | 36.6522 | 48.4627 | -1726.977
2023-07-20 21:00 | -7064.69 | 6.6648 | 36.0495 | 48.4627 | -2070.4563
2023-07-21 22:00 | -7711.31 | 6.6648 | 35.6136 | 48.4627 | -2259.9619
2023-07-22 23:00 | -8925.67 | 6.6648 | 34.8908 | 48.4627 | -2615.8557
2023-07-24 | -9335.25 | 6.6648 | 34.5172 | 48.4627 | -2735.8917
2023-07-25 01:00 | -9778.5 | 6.6648 | 34.1636 | 48.4627 | -2865.7955
2023-07-26 02:00 | -10313.9 | 6.6648 | 33.7563 | 48.4627 | -3022.7057
2023-07-27 03:00 | -9694.65 | 6.6648 | 33.9365 | 48.4627 | -2841.2214
2023-07-28 04:00 | -9890.28 | 6.6648 | 33.7985 | 48.4627 | -2898.5549
2023-07-29 05:00 | -9998.57 | 6.6648 | 33.699 | 48.4627 | -2930.2916
2023-07-30 06:00 | -9879.61 | 6.6648 | 33.7051 | 48.4627 | -2895.4279
2023-07-31 07:00 | -9137.91 | 6.6648 | 34.0687 | 48.4627 | -2678.0571
2023-08-01 08:00 | -7979.23 | 6.6648 | 34.7221 | 48.4627 | -2338.4815
2023-08-02 09:00 | -7426.2 | 6.6648 | 35.1402 | 48.4627 | -2176.4044
2023-08-03 10:00 | -6536.1 | 6.6648 | 35.7198 | 48.4627 | -1915.5418
2023-08-04 11:00 | -5433.7 | 6.6648 | 36.4483 | 48.4627 | -1592.4603
2023-08-05 12:00 | -4957.12 | 6.6648 | 36.9066 | 48.4627 | -1452.7885
2023-08-06 13:00 | -4450.09 | 6.6648 | 37.3449 | 48.4627 | -1304.1926
2023-08-07 14:00 | -5451.13 | 6.6648 | 36.995 | 48.4627 | -1597.5685
2023-08-08 15:00 | -6114.39 | 6.6648 | 36.6706 | 48.4627 | -1791.9508
2023-08-09 16:00 | -5696.13 | 6.6648 | 36.8458 | 48.4627 | -1669.3709
2023-08-10 17:00 | -5944.42 | 6.6648 | 36.763 | 48.4627 | -1742.1375
2023-08-11 18:00 | -5896.46 | 6.6648 | 36.8018 | 48.4627 | -1728.0818
2023-08-12 19:00 | -6398.79 | 6.6648 | 36.5559 | 48.4627 | -1875.3002
2023-08-13 20:00 | -6736.46 | 6.6648 | 36.3601 | 48.4627 | -1974.2615
2023-08-14 21:00 | -7696.21 | 6.6648 | 35.8467 | 48.4627 | -2255.5365
2023-08-15 22:00 | -8102.86 | 6.6648 | 35.5346 | 48.4627 | -2374.7139
2023-08-16 23:00 | -8977.78 | 6.6648 | 34.9939 | 48.4627 | -2631.1276
2023-08-18 | -9383.17 | 6.6648 | 34.648 | 48.4627 | -2749.9357
2023-08-19 01:00 | -9601.88 | 6.6648 | 34.4115 | 48.4627 | -2814.0332
2023-08-20 02:00 | -9763.03 | 6.6648 | 34.234 | 48.4627 | -2861.2616
2023-08-21 03:00 | -9764.99 | 6.6648 | 34.1633 | 48.4627 | -2861.8361
2023-08-22 04:00 | -9529.55 | 6.6648 | 34.231 | 48.4627 | -2792.8354
2023-08-23 05:00 | -9222.85 | 6.6648 | 34.3796 | 48.4627 | -2702.9505
2023-08-24 06:00 | -8678.62 | 6.6648 | 34.6743 | 48.4627 | -2543.4524
2023-08-25 07:00 | -8484.39 | 6.6648 | 34.8302 | 48.4627 | -2486.5293
2023-08-26 08:00 | -8655.01 | 6.6648 | 34.782 | 48.4627 | -2536.533
2023-08-27 09:00 | -8959.97 | 6.6648 | 34.6324 | 48.4627 | -2625.908
2023-08-28 10:00 | -8957.1 | 6.6648 | 34.606 | 48.4627 | -2625.0669
2023-08-29 11:00 | -8502.54 | 6.6648 | 34.823 | 48.4627 | -2491.8485
2023-08-30 12:00 | -8319.08 | 6.6648 | 34.9363 | 48.4627 | -2438.0817
2023-08-31 13:00 | -8620.15 | 6.6648 | 34.7988 | 48.4627 | -2526.3166
2023-09-01 14:00 | -8643.76 | 6.6648 | 34.7611 | 48.4627 | -2533.236
2023-09-02 15:00 | -8544.99 | 6.6648 | 34.7992 | 48.4627 | -2504.2894
2023-09-03 16:00 | -7854.25 | 6.6648 | 35.15 | 48.4627 | -2301.8535
2023-09-04 17:00 | -7329.78 | 6.6648 | 35.4761 | 48.4627 | -2148.1465
2023-09-05 18:00 | -7183.54 | 6.6648 | 35.6238 | 48.4627 | -2105.2878
2023-09-06 19:00 | -7429.65 | 6.6648 | 35.5505 | 48.4627 | -2177.4155
2023-09-07 20:00 | -7531.18 | 6.6648 | 35.5146 | 48.4627 | -2207.171
2023-09-08 21:00 | -8096.7 | 6.6648 | 35.2467 | 48.4627 | -2372.9085
2023-09-09 22:00 | -8155.88 | 6.6648 | 35.1812 | 48.4627 | -2390.2525
2023-09-10 23:00 | -8822.38 | 6.6648 | 34.8217 | 48.4627 | -2585.5843
2023-09-12 | -9157.79 | 6.6648 | 34.5821 | 48.4627 | -2683.8833
2023-09-13 01:00 | -9241.85 | 6.6648 | 34.4744 | 48.4627 | -2708.5189
2023-09-14 02:00 | -9143.94 | 6.6648 | 34.4838 | 48.4627 | -2679.8243
2023-09-15 03:00 | -9083.39 | 6.6648 | 34.5064 | 48.4627 | -2662.0788
2023-09-16 04:00 | -9096.13 | 6.6648 | 34.491 | 48.4627 | -2665.8126
2023-09-17 05:00 | -9044.89 | 6.6648 | 34.508 | 48.4627 | -2650.7956
2023-09-18 06:00 | -9033.64 | 6.6648 | 34.5043 | 48.4627 | -2647.4985
2023-09-19 07:00 | -8047.44 | 6.6648 | 35.0052 | 48.4627 | -2358.4719
2023-09-20 08:00 | -7363.02 | 6.6648 | 35.445 | 48.4627 | -2157.8881
2023-09-21 09:00 | -8744.68 | 6.6648 | 34.8551 | 48.4627 | -2562.8127
2023-09-22 10:00 | -9122.67 | 6.6648 | 34.5836 | 48.4627 | -2673.5907
2023-09-23 11:00 | -9193.98 | 6.6648 | 34.473 | 48.4627 | -2694.4896
2023-09-24 12:00 | -8967.16 | 6.6648 | 34.558 | 48.4627 | -2628.0152
2023-09-25 13:00 | -8937.11 | 6.6648 | 34.5605 | 48.4627 | -2619.2084
2023-09-26 14:00 | -9436.66 | 6.6648 | 34.2741 | 48.4627 | -2765.612
2023-09-27 15:00 | -9631.48 | 6.6648 | 34.1119 | 48.4627 | -2822.7081
2023-09-28 16:00 | -9879.4 | 6.6648 | 33.926 | 48.4627 | -2895.3663
2023-09-29 17:00 | -8812.96 | 6.6648 | 34.4111 | 48.4627 | -2582.8236
2023-09-30 18:00 | -9433.71 | 6.6648 | 34.1482 | 48.4627 | -2764.7475
2023-10-01 19:00 | -9828.86 | 6.6648 | 33.8941 | 48.4627 | -2880.5545
2023-10-02 20:00 | -10179.6 | 6.6648 | 33.6283 | 48.4627 | -2983.3463
2023-10-03 21:00 | -10368.9 | 6.6648 | 33.4631 | 48.4627 | -3038.8246
2023-10-04 22:00 | -10537.8 | 6.6648 | 33.3206 | 48.4627 | -3088.3243
2023-10-05 23:00 | -10650.5 | 6.6648 | 33.198 | 48.4627 | -3121.3534
2023-10-07 | -11566.2 | 6.6648 | 32.6741 | 48.4627 | -3389.7186
2023-10-08 01:00 | -11758 | 6.6648 | 32.4456 | 48.4627 | -3445.9296
2023-10-09 02:00 | -11819 | 6.6648 | 32.3179 | 48.4627 | -3463.807
2023-10-10 03:00 | -11910.4 | 6.6648 | 32.2019 | 48.4627 | -3490.5937
2023-10-11 04:00 | -11952 | 6.6648 | 32.1156 | 48.4627 | -3502.7854
2023-10-12 05:00 | -11914.4 | 6.6648 | 32.0635 | 48.4627 | -3491.766
2023-10-13 06:00 | -12017 | 6.6648 | 31.966 | 48.4627 | -3521.835
2023-10-14 07:00 | -11561.1 | 6.6648 | 32.1462 | 48.4627 | -3388.2239
2023-10-15 08:00 | -10860.6 | 6.6648 | 32.5001 | 48.4627 | -3182.9277
2023-10-16 09:00 | -10394.1 | 6.6648 | 32.7963 | 48.4627 | -3046.21
2023-10-17 10:00 | -10495.9 | 6.6648 | 32.8074 | 48.4627 | -3076.0446
2023-10-18 11:00 | -10380.9 | 6.6648 | 32.88 | 48.4627 | -3042.3415
2023-10-19 12:00 | -9495.42 | 6.6648 | 33.3585 | 48.4627 | -2782.8329
2023-10-20 13:00 | -10019.2 | 6.6648 | 33.1926 | 48.4627 | -2936.3377
2023-10-21 14:00 | -9118.84 | 6.6648 | 33.6545 | 48.4627 | -2672.4682
2023-10-22 15:00 | -10012.4 | 6.6648 | 33.2809 | 48.4627 | -2934.3448
2023-10-23 16:00 | -10021.9 | 6.6648 | 33.2428 | 48.4627 | -2937.129
2023-10-24 17:00 | -9008.63 | 6.6648 | 33.7411 | 48.4627 | -2640.1688
2023-10-25 18:00 | -9292.26 | 6.6648 | 33.6885 | 48.4627 | -2723.2926
2023-10-26 19:00 | -9494.54 | 6.6648 | 33.6131 | 48.4627 | -2782.575
2023-10-27 20:00 | -10035.9 | 6.6648 | 33.3124 | 48.4627 | -2941.232
2023-10-28 21:00 | -10204.2 | 6.6648 | 33.1769 | 48.4627 | -2990.5558
2023-10-29 22:00 | -10482 | 6.6648 | 33.0013 | 48.4627 | -3071.971
2023-10-30 23:00 | -10514.7 | 6.6648 | 32.9305 | 48.4627 | -3081.5544
2023-11-01 | -11669.6 | 6.6648 | 32.2986 | 48.4627 | -3420.0222
2023-11-02 01:00 | -11865.6 | 6.6648 | 32.0602 | 48.4627 | -3477.4641
2023-11-03 02:00 | -11923.3 | 6.6648 | 31.9268 | 48.4627 | -3494.3743
2023-11-04 03:00 | -11988.9 | 6.6648 | 31.8304 | 48.4627 | -3513.5998
2023-11-05 04:00 | -12018.9 | 6.6648 | 31.7583 | 48.4627 | -3522.3919
2023-11-06 05:00 | -11967 | 6.6648 | 31.7219 | 48.4627 | -3507.1815
2023-11-07 06:00 | -11868.8 | 6.6648 | 31.7391 | 48.4627 | -3478.4019
2023-11-08 07:00 | -11261.9 | 6.6648 | 32.0264 | 48.4627 | -3300.5371
2023-11-09 08:00 | -10110.3 | 6.6648 | 32.6488 | 48.4627 | -2963.0364
2023-11-10 09:00 | -9213.19 | 6.6648 | 33.2295 | 48.4627 | -2700.1195
2023-11-11 10:00 | -7637.26 | 6.6648 | 34.1875 | 48.4627 | -2238.26
2023-11-12 11:00 | -6646.31 | 6.6648 | 34.9295 | 48.4627 | -1947.8412
2023-11-13 12:00 | -5925.67 | 6.6648 | 35.545 | 48.4627 | -1736.6424
2023-11-14 13:00 | -5092.76 | 6.6648 | 36.2017 | 48.4627 | -1492.5406
2023-11-15 14:00 | -5410.05 | 6.6648 | 36.2775 | 48.4627 | -1585.5291
2023-11-16 15:00 | -6831.09 | 6.6648 | 35.695 | 48.4627 | -2001.9949
2023-11-17 16:00 | -6487.66 | 6.6648 | 35.842 | 48.4627 | -1901.3455
2023-11-18 17:00 | -7006.5 | 6.6648 | 35.6256 | 48.4627 | -2053.4025
2023-11-19 18:00 | -7408.33 | 6.6648 | 35.4287 | 48.4627 | -2171.1672
2023-11-20 19:00 | -7919.8 | 6.6648 | 35.133 | 48.4627 | -2321.0643
2023-11-21 20:00 | -8206.35 | 6.6648 | 34.9309 | 48.4627 | -2405.0438
2023-11-22 21:00 | -9348.43 | 6.6648 | 34.3114 | 48.4627 | -2739.7544
2023-11-23 22:00 | -9867.07 | 6.6648 | 33.9057 | 48.4627 | -2891.7528
2023-11-24 23:00 | -10886.1 | 6.6648 | 33.2486 | 48.4627 | -3190.401
2023-11-26 | -10990.5 | 6.6648 | 33.0148 | 48.4627 | -3220.9976
2023-11-27 01:00 | -11183.9 | 6.6648 | 32.7871 | 48.4627 | -3277.6775
2023-11-28 02:00 | -11409.2 | 6.6648 | 32.5611 | 48.4627 | -3343.7065
2023-11-29 03:00 | -11608.5 | 6.6648 | 32.3678 | 48.4627 | -3402.1155
2023-11-30 04:00 | -11593.3 | 6.6648 | 32.2848 | 48.4627 | -3397.6608
2023-12-01 05:00 | -11488.6 | 6.6648 | 32.2843 | 48.4627 | -3366.9763
2023-12-02 06:00 | -11087.6 | 6.6648 | 32.4557 | 48.4627 | -3249.4548
2023-12-03 07:00 | -11013.2 | 6.6648 | 32.4979 | 48.4627 | -3227.6503
2023-12-04 08:00 | -10946.4 | 6.6648 | 32.5228 | 48.4627 | -3208.0732
2023-12-05 09:00 | -10288.7 | 6.6648 | 32.8532 | 48.4627 | -3015.3203
2023-12-06 10:00 | -9478.45 | 6.6648 | 33.3211 | 48.4627 | -2777.8595
2023-12-07 11:00 | -9173.62 | 6.6648 | 33.5827 | 48.4627 | -2688.5226
2023-12-08 12:00 | -7706.96 | 6.6648 | 34.4064 | 48.4627 | -2258.687
2023-12-09 13:00 | -7622.23 | 6.6648 | 34.6322 | 48.4627 | -2233.8551
2023-12-10 14:00 | -6900.09 | 6.6648 | 35.1239 | 48.4627 | -2022.2168
2023-12-11 15:00 | -6976.15 | 6.6648 | 35.237 | 48.4627 | -2044.5077
2023-12-12 16:00 | -6930.37 | 6.6648 | 35.3572 | 48.4627 | -2031.091
2023-12-13 17:00 | -7524.73 | 6.6648 | 35.1324 | 48.4627 | -2205.2807
2023-12-14 18:00 | -7856.57 | 6.6648 | 34.9582 | 48.4627 | -2302.5334
2023-12-15 19:00 | -8595.06 | 6.6648 | 34.5674 | 48.4627 | -2518.9634
2023-12-16 20:00 | -9234.85 | 6.6648 | 34.1725 | 48.4627 | -2706.4674
2023-12-17 21:00 | -10145.7 | 6.6648 | 33.6155 | 48.4627 | -2973.4112
2023-12-18 22:00 | -10759.1 | 6.6648 | 33.1587 | 48.4627 | -3153.1809
2023-12-19 23:00 | -11585.6 | 6.6648 | 32.5992 | 48.4627 | -3395.4042
2023-12-21 | -11783.5 | 6.6648 | 32.3255 | 48.4627 | -3453.403
2023-12-22 01:00 | -11879.8 | 6.6648 | 32.1483 | 48.4627 | -3481.6257
2023-12-23 02:00 | -12010.5 | 6.6648 | 31.9783 | 48.4627 | -3519.9301
2023-12-24 03:00 | -12201.8 | 6.6648 | 31.7895 | 48.4627 | -3575.9946
2023-12-25 04:00 | -12268.1 | 6.6648 | 31.6636 | 48.4627 | -3595.4252
2023-12-26 05:00 | -12210.2 | 6.6648 | 31.6243 | 48.4627 | -3578.4564
2023-12-27 06:00 | -12135.1 | 6.6648 | 31.6114 | 48.4627 | -3556.4467
2023-12-28 07:00 | -11516.3 | 6.6648 | 31.8904 | 48.4627 | -3375.0944
2023-12-29 08:00 | -9800.57 | 6.6648 | 32.7936 | 48.4627 | -2872.2635
2023-12-30 09:00 | -8706.74 | 6.6648 | 33.5287 | 48.4627 | -2551.6936
2023-12-31 10:00 | -7310.71 | 6.6648 | 34.4391 | 48.4627 | -2142.5576
2024-01-01 11:00 | -6020.26 | 6.6648 | 35.3443 | 48.4627 | -1764.364
2024-01-02 12:00 | -5398.05 | 6.6648 | 35.9408 | 48.4627 | -1582.0123
2024-01-03 13:00 | -5195.94 | 6.6648 | 36.2836 | 48.4627 | -1522.7797
2024-01-04 14:00 | -5231.01 | 6.6648 | 36.4382 | 48.4627 | -1533.0577
2024-01-05 15:00 | -5941.88 | 6.6648 | 36.2068 | 48.4627 | -1741.3931
2024-01-06 16:00 | -6074.85 | 6.6648 | 36.1742 | 48.4627 | -1780.3628
2024-01-07 17:00 | -6846.89 | 6.6648 | 35.8134 | 48.4627 | -2006.6254
2024-01-08 18:00 | -7757.64 | 6.6648 | 35.3199 | 48.4627 | -2273.5399
2024-01-09 19:00 | -8776.91 | 6.6648 | 34.7122 | 48.4627 | -2572.2584
2024-01-10 20:00 | -9414.92 | 6.6648 | 34.2461 | 48.4627 | -2759.2407
2024-01-11 21:00 | -10361.2 | 6.6648 | 33.6333 | 48.4627 | -3036.568
2024-01-12 22:00 | -10507.7 | 6.6648 | 33.3809 | 48.4627 | -3079.5029
2024-01-13 23:00 | -11210.2 | 6.6648 | 32.8945 | 48.4627 | -3285.3853
2024-01-15 | -11319.6 | 6.6648 | 32.6838 | 48.4627 | -3317.4473
2024-01-16 01:00 | -11270.4 | 6.6648 | 32.5921 | 48.4627 | -3303.0282
2024-01-17 02:00 | -11177.6 | 6.6648 | 32.5634 | 48.4627 | -3275.8312
2024-01-18 03:00 | -10994.6 | 6.6648 | 32.614 | 48.4627 | -3222.1992
2024-01-19 04:00 | -10803.9 | 6.6648 | 32.6855 | 48.4627 | -3166.3105
2024-01-20 05:00 | -10603.1 | 6.6648 | 32.7885 | 48.4627 | -3107.4619
2024-01-21 06:00 | -10057.5 | 6.6648 | 33.0823 | 48.4627 | -2947.5623
2024-01-22 07:00 | -9463.09 | 6.6648 | 33.4485 | 48.4627 | -2773.3579
2024-01-23 08:00 | -8051.33 | 6.6648 | 34.2625 | 48.4627 | -2359.6119
2024-01-24 09:00 | -6981.32 | 6.6648 | 34.9983 | 48.4627 | -2046.0229
2024-01-25 10:00 | -5102.46 | 6.6648 | 36.1697 | 48.4627 | -1495.3834
2024-01-26 11:00 | -3766.3 | 6.6648 | 37.1621 | 48.4627 | -1103.7936
2024-01-27 12:00 | -2515.28 | 6.6648 | 38.1236 | 48.4627 | -737.1558
2024-01-28 13:00 | -1723.72 | 6.6648 | 38.8602 | 48.4627 | -505.1725
2024-01-29 14:00 | -1621.35 | 6.2585 | 39.1575 | 48.4627 | -475.1708
2024-01-30 15:00 | -1942.18 | 6.6648 | 39.2785 | 48.4627 | -569.1968
2024-01-31 16:00 | -1651.69 | 6.3505 | 39.5266 | 48.4627 | -484.0626
2024-02-01 17:00 | -2403.17 | 6.6648 | 39.3476 | 48.4627 | -704.2996
2024-02-02 18:00 | -2935.18 | 6.6648 | 39.1416 | 48.4627 | -860.2163
2024-02-03 19:00 | -3774.56 | 6.6648 | 38.7387 | 48.4627 | -1106.2143
2024-02-04 20:00 | -4391.84 | 6.6648 | 38.3983 | 48.4627 | -1287.1212
2024-02-05 21:00 | -5617.22 | 6.6648 | 37.7353 | 48.4627 | -1646.2447
2024-02-06 22:00 | -6311.43 | 6.6648 | 37.2526 | 48.4627 | -1849.6975
2024-02-07 23:00 | -7328.34 | 6.6648 | 36.609 | 48.4627 | -2147.7244
2024-02-09 | -7551.58 | 6.6648 | 36.3306 | 48.4627 | -2213.1496
2024-02-10 01:00 | -7658.42 | 6.6648 | 36.1552 | 48.4627 | -2244.4613
2024-02-11 02:00 | -8056.95 | 6.6648 | 35.8653 | 48.4627 | -2361.259
2024-02-12 03:00 | -8153.68 | 6.6648 | 35.7227 | 48.4627 | -2389.6077
2024-02-13 04:00 | -8171.94 | 6.6648 | 35.6385 | 48.4627 | -2394.9592
2024-02-14 05:00 | -8431.24 | 6.6648 | 35.4629 | 48.4627 | -2470.9525
2024-02-15 06:00 | -8164.57 | 6.6648 | 35.5411 | 48.4627 | -2392.7993
2024-02-16 07:00 | -7630.98 | 6.6648 | 35.7983 | 48.4627 | -2236.4195
2024-02-17 08:00 | -7141.51 | 6.6648 | 36.0815 | 48.4627 | -2092.97
2024-02-18 09:00 | -6454.12 | 6.6648 | 36.4893 | 48.4627 | -1891.5159
2024-02-19 10:00 | -5520.53 | 6.6648 | 37.0487 | 48.4627 | -1617.9076
2024-02-20 11:00 | -4292.13 | 6.6648 | 37.8143 | 48.4627 | -1257.8991
2024-02-21 12:00 | -3294.21 | 6.6648 | 38.5169 | 48.4627 | -965.4376
2024-02-22 13:00 | -3693.34 | 6.6648 | 38.5172 | 48.4627 | -1082.4111
2024-02-23 14:00 | -3462.56 | 6.6648 | 38.7245 | 48.4627 | -1014.7762
2024-02-24 15:00 | -3982.23 | 6.6648 | 38.5571 | 48.4627 | -1167.0764
2024-02-25 16:00 | -4333.94 | 6.6648 | 38.4063 | 48.4627 | -1270.1524
2024-02-26 17:00 | -5633.92 | 6.6648 | 37.741 | 48.4627 | -1651.139
2024-02-27 18:00 | -6285.19 | 6.6648 | 37.2923 | 48.4627 | -1842.0074
2024-02-28 19:00 | -7410.01 | 6.6648 | 36.6079 | 48.4627 | -2171.6596
2024-02-29 20:00 | -7970.26 | 6.6648 | 36.1564 | 48.4627 | -2335.8526
2024-03-01 21:00 | -9476.01 | 6.6648 | 35.2377 | 48.4627 | -2777.1444
2024-03-02 22:00 | -9821.48 | 6.6648 | 34.8177 | 48.4627 | -2878.3917
2024-03-03 23:00 | -11117.5 | 6.6648 | 33.972 | 48.4627 | -3258.2176
2024-03-05 | -11823 | 6.6648 | 33.35 | 48.4627 | -3464.9793
2024-03-06 01:00 | -11966 | 6.6648 | 33.0359 | 48.4627 | -3506.8884
2024-03-07 02:00 | -12157.5 | 6.6648 | 32.7547 | 48.4627 | -3563.0115
2024-03-08 03:00 | -12501.2 | 6.6648 | 32.4286 | 48.4627 | -3663.7401
2024-03-09 04:00 | -12699.3 | 6.6648 | 32.1606 | 48.4627 | -3721.7974
2024-03-10 05:00 | -12754.1 | 6.6648 | 31.9999 | 48.4627 | -3737.8577
2024-03-11 06:00 | -12849.2 | 6.6648 | 31.8444 | 48.4627 | -3765.7288
2024-03-12 07:00 | -12469.3 | 6.6648 | 31.9393 | 48.4627 | -3654.3911
2024-03-13 08:00 | -11650.3 | 6.6648 | 32.3054 | 48.4627 | -3414.3659
2024-03-14 09:00 | -11268.6 | 6.6648 | 32.5285 | 48.4627 | -3302.5007
2024-03-15 10:00 | -9923.26 | 6.6648 | 33.238 | 48.4627 | -2908.2204
2024-03-16 11:00 | -8572.73 | 6.6648 | 34.0526 | 48.4627 | -2512.4192
2024-03-17 12:00 | -7353.8 | 6.6648 | 34.8626 | 48.4627 | -2155.186
2024-03-18 13:00 | -6818.49 | 6.6648 | 35.3474 | 48.4627 | -1998.3022
2024-03-19 14:00 | -6468.27 | 6.6648 | 35.6901 | 48.4627 | -1895.6628
2024-03-20 15:00 | -6435.21 | 6.6648 | 35.8537 | 48.4627 | -1885.9739
2024-03-21 16:00 | -7228.17 | 6.6648 | 35.5499 | 48.4627 | -2118.3675
2024-03-22 17:00 | -6718.82 | 6.6648 | 35.8103 | 48.4627 | -1969.0918
2024-03-23 18:00 | -7655.66 | 6.6648 | 35.3979 | 48.4627 | -2243.6525
2024-03-24 19:00 | -8208.45 | 6.6648 | 35.0827 | 48.4627 | -2405.6592
2024-03-25 20:00 | -8523.3 | 6.6648 | 34.8512 | 48.4627 | -2497.9327
2024-03-26 21:00 | -8930.12 | 6.6648 | 34.5958 | 48.4627 | -2617.1598
2024-03-27 22:00 | -9226.71 | 6.6648 | 34.3889 | 48.4627 | -2704.0818
2024-03-28 23:00 | -9288.84 | 6.6648 | 34.287 | 48.4627 | -2722.2903
2024-03-30 | -10795.4 | 6.6648 | 33.4676 | 48.4627 | -3163.8194
2024-03-31 01:00 | -10939 | 6.6648 | 33.2109 | 48.4627 | -3205.9044
2024-04-01 02:00 | -11049.5 | 6.6648 | 33.0296 | 48.4627 | -3238.2888
2024-04-02 03:00 | -11056.2 | 6.6648 | 32.9424 | 48.4627 | -3240.2524
2024-04-03 04:00 | -11142.6 | 6.6648 | 32.8322 | 48.4627 | -3265.5737
2024-04-04 05:00 | -11304.6 | 6.6648 | 32.6765 | 48.4627 | -3313.0512
2024-04-05 06:00 | -11396.9 | 6.6648 | 32.5766 | 48.4627 | -3340.1017
2024-04-06 07:00 | -10208.6 | 6.6648 | 33.1384 | 48.4627 | -2991.8453
2024-04-07 08:00 | -8680.71 | 6.6648 | 33.998 | 48.4627 | -2544.065
2024-04-08 09:00 | -7508.11 | 6.6648 | 34.7806 | 48.4627 | -2200.4098
2024-04-09 10:00 | -6072.32 | 6.6648 | 35.7135 | 48.4627 | -1779.6213
2024-04-10 11:00 | -4519.66 | 6.6648 | 36.7542 | 48.4627 | -1324.5816
2024-04-11 12:00 | -4030.97 | 6.6648 | 37.32 | 48.4627 | -1181.3607
2024-04-12 13:00 | -3870.26 | 6.6648 | 37.6463 | 48.4627 | -1134.2612
2024-04-13 14:00 | -4089.96 | 6.6648 | 37.708 | 48.4627 | -1198.649
2024-04-14 15:00 | -4926.07 | 6.6648 | 37.3985 | 48.4627 | -1443.6886
2024-04-15 16:00 | -5945.7 | 6.6648 | 36.8991 | 48.4627 | -1742.5127
2024-04-16 17:00 | -5410.2 | 6.6648 | 37.1112 | 48.4627 | -1585.5731
2024-04-17 18:00 | -6887.8 | 6.6648 | 36.4084 | 48.4627 | -2018.6149
2024-04-18 19:00 | -7970.41 | 6.6648 | 35.7572 | 48.4627 | -2335.8966
2024-04-19 20:00 | -8654.41 | 6.6648 | 35.2435 | 48.4627 | -2536.3572
2024-04-20 21:00 | -9271.61 | 6.6648 | 34.7892 | 48.4627 | -2717.2407
2024-04-21 22:00 | -9613.77 | 6.6648 | 34.4773 | 48.4627 | -2817.5179
2024-04-22 23:00 | -9861.15 | 6.6648 | 34.2054 | 48.4627 | -2890.0178
2024-04-24 | -11044.4 | 6.6648 | 33.4846 | 48.4627 | -3236.7941
2024-04-25 01:00 | -11182.8 | 6.6648 | 33.2163 | 48.4627 | -3277.3552
2024-04-26 02:00 | -11459.3 | 6.6648 | 32.9365 | 48.4627 | -3358.3893
2024-04-27 03:00 | -11498 | 6.6648 | 32.8039 | 48.4627 | -3369.7312
2024-04-28 04:00 | -11379.7 | 6.6648 | 32.7782 | 48.4627 | -3335.0609
2024-04-29 05:00 | -11364.6 | 6.6648 | 32.7202 | 48.4627 | -3330.6355
2024-04-30 06:00 | -10916.7 | 6.6648 | 32.9118 | 48.4627 | -3199.3689
2024-05-01 07:00 | -10880.9 | 6.6648 | 32.9392 | 48.4627 | -3188.877
2024-05-02 08:00 | -10504.7 | 6.6648 | 33.1257 | 48.4627 | -3078.6237
2024-05-03 09:00 | -9379.78 | 6.6648 | 33.7211 | 48.4627 | -2748.9422
2024-05-04 10:00 | -7995.38 | 6.6648 | 34.5364 | 48.4627 | -2343.2146
2024-05-05 11:00 | -7233.08 | 6.6648 | 35.1016 | 48.4627 | -2119.8065
2024-05-06 12:00 | -6432.63 | 6.6648 | 35.6697 | 48.4627 | -1885.2178
2024-05-07 13:00 | -6175.49 | 6.6648 | 35.972 | 48.4627 | -1809.8575
2024-05-08 14:00 | -5943.09 | 6.6648 | 36.2309 | 48.4627 | -1741.7477
2024-05-09 15:00 | -6152.21 | 6.6648 | 36.2419 | 48.4627 | -1803.0348
2024-05-10 16:00 | -6068.59 | 6.6648 | 36.3482 | 48.4627 | -1778.5282
2024-05-11 17:00 | -6952.45 | 6.6648 | 35.9548 | 48.4627 | -2037.562
2024-05-12 18:00 | -7473.08 | 6.6648 | 35.6533 | 48.4627 | -2190.1436
2024-05-13 19:00 | -8144.3 | 6.6648 | 35.26 | 48.4627 | -2386.8587
2024-05-14 20:00 | -8754.49 | 6.6648 | 34.8725 | 48.4627 | -2565.6878
2024-05-15 21:00 | -9894.47 | 6.6648 | 34.1907 | 48.4627 | -2899.7829
2024-05-16 22:00 | -10200 | 6.6648 | 33.8568 | 48.4627 | -2989.3249
2024-05-17 23:00 | -11255.6 | 6.6648 | 33.1816 | 48.4627 | -3298.6907
2024-05-19 | -11563.7 | 6.6648 | 32.8336 | 48.4627 | -3388.9859
2024-05-20 01:00 | -11934 | 6.6648 | 32.4866 | 48.4627 | -3497.5101
2024-05-21 02:00 | -12046 | 6.6648 | 32.2858 | 48.4627 | -3530.3341
2024-05-22 03:00 | -12149.8 | 6.6648 | 32.1228 | 48.4627 | -3560.7549
2024-05-23 04:00 | -12131.7 | 6.6648 | 32.0302 | 48.4627 | -3555.4503
2024-05-24 05:00 | -12109.4 | 6.6648 | 31.9741 | 48.4627 | -3548.9148
2024-05-25 06:00 | -11841 | 6.6648 | 32.0543 | 48.4627 | -3470.2545
2024-05-26 07:00 | -11312.5 | 6.6648 | 32.3037 | 48.4627 | -3315.3665
2024-05-27 08:00 | -10452.5 | 6.6648 | 32.7658 | 48.4627 | -3063.3254
2024-05-28 09:00 | -9783.54 | 6.6648 | 33.1893 | 48.4627 | -2867.2725
2024-05-29 10:00 | -8277.84 | 6.6648 | 34.0527 | 48.4627 | -2425.9954
2024-05-30 11:00 | -7056.88 | 6.6648 | 34.8669 | 48.4627 | -2068.1674
2024-05-31 12:00 | -5934.61 | 6.6648 | 35.6632 | 48.4627 | -1739.2625
2024-06-01 13:00 | -5620.26 | 6.6648 | 36.061 | 48.4627 | -1647.1356
2024-06-02 14:00 | -5316.83 | 6.6648 | 36.3935 | 48.4627 | -1558.2091
2024-06-03 15:00 | -5108.68 | 6.6648 | 36.6603 | 48.4627 | -1497.2063
2024-06-04 16:00 | -5486.98 | 6.6648 | 36.604 | 48.4627 | -1608.0751
2024-06-05 17:00 | -6081.63 | 6.6648 | 36.3672 | 48.4627 | -1782.3498
2024-06-06 18:00 | -6784.51 | 6.6648 | 36.0122 | 48.4627 | -1988.3436
2024-06-07 19:00 | -7667.95 | 6.6648 | 35.5261 | 48.4627 | -2247.2543
2024-06-08 20:00 | -8126.49 | 6.6648 | 35.2066 | 48.4627 | -2381.6391
2024-06-09 21:00 | -9207.74 | 6.6648 | 34.576 | 48.4627 | -2698.5222
2024-06-10 22:00 | -9624.32 | 6.6648 | 34.2158 | 48.4627 | -2820.6098
2024-06-11 23:00 | -10646.8 | 6.6648 | 33.5666 | 48.4627 | -3120.2691
2024-06-13 | -11090.8 | 6.6648 | 33.1604 | 48.4627 | -3250.3926
2024-06-14 01:00 | -11273.8 | 6.6648 | 32.914 | 48.4627 | -3304.0246
2024-06-15 02:00 | -11495 | 6.6648 | 32.6805 | 48.4627 | -3368.8519
2024-06-16 03:00 | -11658.4 | 6.6648 | 32.4903 | 48.4627 | -3416.7398
2024-06-17 04:00 | -11598.4 | 6.6648 | 32.4225 | 48.4627 | -3399.1555
2024-06-18 05:00 | -11355.3 | 6.6648 | 32.4893 | 48.4627 | -3327.9099
2024-06-19 06:00 | -11072.5 | 6.6648 | 32.6117 | 48.4627 | -3245.0294
2024-06-20 07:00 | -10960.7 | 6.6648 | 32.6716 | 48.4627 | -3212.2641
2024-06-21 08:00 | -10694.1 | 6.6648 | 32.8064 | 48.4627 | -3134.1313
2024-06-22 09:00 | -10939.1 | 6.6648 | 32.697 | 48.4627 | -3205.9337
2024-06-23 10:00 | -10303.1 | 6.6648 | 32.9947 | 48.4627 | -3019.5405
2024-06-24 11:00 | -9572.33 | 6.6648 | 33.4055 | 48.4627 | -2805.373
2024-06-25 12:00 | -9457.37 | 6.6648 | 33.5438 | 48.4627 | -2771.6815
2024-06-26 13:00 | -9285.75 | 6.6648 | 33.6707 | 48.4627 | -2721.3847
2024-06-27 14:00 | -9363.7 | 6.6648 | 33.6585 | 48.4627 | -2744.2296
2024-06-28 15:00 | -9191.93 | 6.6648 | 33.7615 | 48.4627 | -2693.8888
2024-06-29 16:00 | -8409.59 | 6.6648 | 34.1854 | 48.4627 | -2464.6075
2024-06-30 17:00 | -8056.02 | 6.6648 | 34.4514 | 48.4627 | -2360.9864
2024-07-01 18:00 | -7807.79 | 6.6648 | 34.6622 | 48.4627 | -2288.2374
2024-07-02 19:00 | -8236.65 | 6.6648 | 34.5186 | 48.4627 | -2413.9238
2024-07-03 20:00 | -8256.44 | 6.6648 | 34.5258 | 48.4627 | -2419.7237
2024-07-04 21:00 | -8888.07 | 6.6648 | 34.2362 | 48.4627 | -2604.8362
2024-07-05 22:00 | -9453.08 | 6.6648 | 33.9142 | 48.4627 | -2770.4243
2024-07-06 23:00 | -10002.1 | 6.6648 | 33.5663 | 48.4627 | -2931.3261
2024-07-08 | -10085.4 | 6.6648 | 33.4392 | 48.4627 | -2955.739
2024-07-09 01:00 | -10255.6 | 6.6648 | 33.3061 | 48.4627 | -3005.6197
2024-07-10 02:00 | -10074.3 | 6.6648 | 33.3559 | 48.4627 | -2952.4859
2024-07-11 03:00 | -10016 | 6.6648 | 33.3802 | 48.4627 | -2935.3998
2024-07-12 04:00 | -9825.37 | 6.6648 | 33.4775 | 48.4627 | -2879.5317
2024-07-13 05:00 | -9740.48 | 6.6648 | 33.5398 | 48.4627 | -2854.6529
2024-07-14 06:00 | -9104.46 | 6.6648 | 33.8795 | 48.4627 | -2668.2538
2024-07-15 07:00 | -9052.61 | 6.6648 | 33.9778 | 48.4627 | -2653.0581
2024-07-16 08:00 | -8828.32 | 6.6648 | 34.1322 | 48.4627 | -2587.3252
2024-07-17 09:00 | -8733.37 | 6.6648 | 34.2266 | 48.4627 | -2559.4981
2024-07-18 10:00 | -8270.95 | 6.6648 | 34.5014 | 48.4627 | -2423.9762
2024-07-19 11:00 | -7819.06 | 6.6648 | 34.8022 | 48.4627 | -2291.5403
2024-07-20 12:00 | -7293.51 | 6.6648 | 35.15 | 48.4627 | -2137.5168
2024-07-21 13:00 | -7209.99 | 6.6648 | 35.2918 | 48.4627 | -2113.0395
2024-07-22 14:00 | -7399.4 | 6.6648 | 35.2634 | 48.4627 | -2168.5501
2024-07-23 15:00 | -7594 | 6.6648 | 35.1952 | 48.4627 | -2225.5817
2024-07-24 16:00 | -6962.93 | 6.6648 | 35.5264 | 48.4627 | -2040.6333
2024-07-25 17:00 | -6812.72 | 6.6648 | 35.6785 | 48.4627 | -1996.6111
2024-07-26 18:00 | -6698.77 | 6.6648 | 35.794 | 48.4627 | -1963.2157
2024-07-27 19:00 | -7097.83 | 6.6648 | 35.6399 | 48.4627 | -2080.1686
2024-07-28 20:00 | -7405.52 | 6.6648 | 35.4881 | 48.4627 | -2170.3437
2024-07-29 21:00 | -7823.94 | 6.6648 | 35.2716 | 48.4627 | -2292.9705
2024-07-30 22:00 | -8043.24 | 6.6648 | 35.1279 | 48.4627 | -2357.241
2024-07-31 23:00 | -8773.88 | 6.6648 | 34.7245 | 48.4627 | -2571.3704
2024-08-02 | -9168.74 | 6.6648 | 34.4363 | 48.4627 | -2687.0924
2024-08-03 01:00 | -9417.78 | 6.6648 | 34.2251 | 48.4627 | -2760.0789
2024-08-04 02:00 | -9345.88 | 6.6648 | 34.1965 | 48.4627 | -2739.0071
2024-08-05 03:00 | -9354.28 | 6.6648 | 34.163 | 48.4627 | -2741.4688
2024-08-06 04:00 | -9123.33 | 6.6648 | 34.2518 | 48.4627 | -2673.7841
2024-08-07 05:00 | -9035.79 | 6.6648 | 34.2967 | 48.4627 | -2648.1286
2024-08-08 06:00 | -8408.62 | 6.6648 | 34.6206 | 48.4627 | -2464.3233
2024-08-09 07:00 | -8358.58 | 6.6648 | 34.7083 | 48.4627 | -2449.658
2024-08-10 08:00 | -8179.89 | 6.6648 | 34.8367 | 48.4627 | -2397.2891
2024-08-11 09:00 | -8229.65 | 6.6648 | 34.8501 | 48.4627 | -2411.8723
2024-08-12 10:00 | -7983.28 | 6.6648 | 34.9919 | 48.4627 | -2339.6684
2024-08-13 11:00 | -7492.98 | 6.6648 | 35.2818 | 48.4627 | -2195.9757
2024-08-14 12:00 | -7204.65 | 6.6648 | 35.4967 | 48.4627 | -2111.4745
2024-08-15 13:00 | -6720.91 | 6.6648 | 35.813 | 48.4627 | -1969.7043
2024-08-16 14:00 | -6429.78 | 6.6648 | 36.0512 | 48.4627 | -1884.3825
2024-08-17 15:00 | -6512.97 | 6.6648 | 36.1007 | 48.4627 | -1908.7631
2024-08-18 16:00 | -5632.19 | 6.6648 | 36.601 | 48.4627 | -1650.6319
2024-08-19 17:00 | -5639.89 | 6.6648 | 36.7213 | 48.4627 | -1652.8886
2024-08-20 18:00 | -5566.24 | 6.6648 | 36.8381 | 48.4627 | -1631.3039
2024-08-21 19:00 | -6111.04 | 6.6648 | 36.62 | 48.4627 | -1790.969
2024-08-22 20:00 | -6232.82 | 6.6648 | 36.5576 | 48.4627 | -1826.6592
2024-08-23 21:00 | -7459.72 | 6.6648 | 35.9453 | 48.4627 | -2186.2281
2024-08-24 22:00 | -7819.42 | 6.6648 | 35.6581 | 48.4627 | -2291.6458
2024-08-25 23:00 | -8484.43 | 6.6648 | 35.2369 | 48.4627 | -2486.541
2024-08-27 | -9432.4 | 6.6648 | 34.6486 | 48.4627 | -2764.3636
2024-08-28 01:00 | -9613.12 | 6.6648 | 34.4028 | 48.4627 | -2817.3274
2024-08-29 02:00 | -9861.88 | 6.6648 | 34.1582 | 48.4627 | -2890.2317
2024-08-30 03:00 | -9705.96 | 6.6648 | 34.1497 | 48.4627 | -2844.5361
2024-08-31 04:00 | -9909.24 | 6.6648 | 33.9852 | 48.4627 | -2904.1116
2024-09-01 05:00 | -9938.18 | 6.6648 | 33.8998 | 48.4627 | -2912.593
2024-09-02 06:00 | -9906.33 | 6.6648 | 33.8564 | 48.4627 | -2903.2587
2024-09-03 07:00 | -9367.55 | 6.6648 | 34.0903 | 48.4627 | -2745.3579
2024-09-04 08:00 | -8498.91 | 6.6648 | 34.5492 | 48.4627 | -2490.7846
2024-09-05 09:00 | -8592.89 | 6.6648 | 34.5835 | 48.4627 | -2518.3275
2024-09-06 10:00 | -7760.34 | 6.6648 | 35.0354 | 48.4627 | -2274.3311
2024-09-07 11:00 | -6141.23 | 6.6648 | 35.9563 | 48.4627 | -1799.8168
2024-09-08 12:00 | -6004.75 | 6.6648 | 36.248 | 48.4627 | -1759.8185
2024-09-09 13:00 | -6483.22 | 6.6648 | 36.1405 | 48.4627 | -1900.0442
2024-09-10 14:00 | -6562.11 | 6.6648 | 36.1313 | 48.4627 | -1923.1646
2024-09-11 15:00 | -6612.04 | 6.6648 | 36.1469 | 48.4627 | -1937.7976
2024-09-12 16:00 | -6857.48 | 6.6648 | 36.0563 | 48.4627 | -2009.729
2024-09-13 17:00 | -5574.45 | 6.6648 | 36.7029 | 48.4627 | -1633.71
2024-09-14 18:00 | -6059.48 | 6.6648 | 36.5809 | 48.4627 | -1775.8583
2024-09-15 19:00 | -6416.07 | 6.6648 | 36.4373 | 48.4627 | -1880.3645
2024-09-16 20:00 | -6912.22 | 6.6648 | 36.1716 | 48.4627 | -2025.7717
2024-09-17 21:00 | -7156.24 | 6.6648 | 36.0223 | 48.4627 | -2097.2869
2024-09-18 22:00 | -7128.87 | 6.6648 | 36.0154 | 48.4627 | -2089.2656
2024-09-19 23:00 | -7175.48 | 6.6648 | 35.9694 | 48.4627 | -2102.9256
2024-09-21 | -8593.66 | 6.6648 | 35.2336 | 48.4627 | -2518.5531
2024-09-22 01:00 | -8886.26 | 6.6648 | 34.9456 | 48.4627 | -2604.3057
2024-09-23 02:00 | -9015.27 | 6.6648 | 34.7814 | 48.4627 | -2642.1148
2024-09-24 03:00 | -8748.58 | 6.6648 | 34.8604 | 48.4627 | -2563.9557
2024-09-25 04:00 | -8744.47 | 6.6648 | 34.8462 | 48.4627 | -2562.7512
2024-09-26 05:00 | -8612.38 | 6.6648 | 34.8798 | 48.4627 | -2524.0394
2024-09-27 06:00 | -8539.87 | 6.6648 | 34.9147 | 48.4627 | -2502.7888
2024-09-28 07:00 | -7709.75 | 6.6648 | 35.3446 | 48.4627 | -2259.5047
2024-09-29 08:00 | -6940.59 | 6.6648 | 35.819 | 48.4627 | -2034.0861
2024-09-30 09:00 | -7259.48 | 6.6648 | 35.7753 | 48.4627 | -2127.5436
2024-10-01 10:00 | -7117.53 | 6.6648 | 35.8778 | 48.4627 | -2085.9421
2024-10-02 11:00 | -6596.37 | 6.6648 | 36.1723 | 48.4627 | -1933.2052
2024-10-03 12:00 | -6158.31 | 6.6648 | 36.4843 | 48.4627 | -1804.8225
2024-10-04 13:00 | -5879.36 | 6.6648 | 36.7238 | 48.4627 | -1723.0703
2024-10-05 14:00 | -5542.96 | 6.6648 | 36.9776 | 48.4627 | -1624.4812
2024-10-06 15:00 | -5648.27 | 6.6648 | 37.0194 | 48.4627 | -1655.3445
2024-10-07 16:00 | -5300.13 | 6.6648 | 37.2563 | 48.4627 | -1553.3148
2024-10-08 17:00 | -3976.48 | 6.6648 | 38.0085 | 48.4627 | -1165.3912
2024-10-09 18:00 | -4283.47 | 6.6648 | 38.0401 | 48.4627 | -1255.3611
2024-10-10 19:00 | -4598.06 | 6.6648 | 37.9644 | 48.4627 | -1347.5584
2024-10-11 20:00 | -4803.04 | 6.6648 | 37.8861 | 48.4627 | -1407.6321
2024-10-12 21:00 | -4875.27 | 6.6648 | 37.8851 | 48.4627 | -1428.8006
2024-10-13 22:00 | -4976.88 | 6.6648 | 37.8709 | 48.4627 | -1458.5795
2024-10-14 23:00 | -5061.8 | 6.6648 | 37.8412 | 48.4627 | -1483.4671
2024-10-16 | -5911.8 | 6.6648 | 37.4283 | 48.4627 | -1732.5776
2024-10-17 01:00 | -5964.87 | 6.6648 | 37.3496 | 48.4627 | -1748.1308
2024-10-18 02:00 | -5998.3 | 6.6648 | 37.3128 | 48.4627 | -1757.9282
2024-10-19 03:00 | -5882.9 | 6.6648 | 37.374 | 48.4627 | -1724.1078
2024-10-20 04:00 | -5633.76 | 6.6648 | 37.5171 | 48.4627 | -1651.0921
2024-10-21 05:00 | -5411.42 | 6.6648 | 37.6574 | 48.4627 | -1585.9306
2024-10-22 06:00 | -4932.5 | 6.6648 | 37.9511 | 48.4627 | -1445.5731
2024-10-23 07:00 | -4789.87 | 6.6648 | 38.1042 | 48.4627 | -1403.7723
2024-10-24 08:00 | -4150.78 | 6.6648 | 38.4962 | 48.4627 | -1216.4735
2024-10-25 09:00 | -3691.94 | 6.6648 | 38.841 | 48.4627 | -1082.0008
2024-10-26 10:00 | -2787.81 | 6.6648 | 39.4216 | 48.4627 | -817.0265
2024-10-27 11:00 | -1170.33 | 4.4431 | 40.1107 | 48.4627 | -342.9899
2024-10-28 12:00 | -1032.68 | 4.143 | 40.4279 | 48.4627 | -302.6486
2024-10-29 13:00 | -216.524 | 1.0666 | 40.7766 | 48.4627 | -63.4569
2024-10-30 14:00 | 1236.21 | 1 | 41.2639 | 48.4627 | 362.2974
2024-10-31 15:00 | 96.8299 | 1 | 41.9651 | 48.4627 | 28.378
2024-11-01 16:00 | 2591.56 | 1 | 41.2218 | 48.4627 | 759.5113
2024-11-02 17:00 | 0 | 0 | 42.4271 | 48.4627 | 0
2024-11-03 18:00 | -738.934 | 2.9153 | 41.5554 | 48.4627 | -216.5602
2024-11-04 19:00 | -1499.58 | 6.0206 | 41.5281 | 48.4627 | -439.4835
2024-11-05 20:00 | -1905.46 | 6.6648 | 41.3502 | 48.4627 | -558.4352
2024-11-06 21:00 | -3223.55 | 6.6648 | 40.6508 | 48.4627 | -944.7292
2024-11-07 22:00 | -3767.45 | 6.6648 | 40.2044 | 48.4627 | -1104.1306
2024-11-08 23:00 | -4911.15 | 6.6648 | 39.4928 | 48.4627 | -1439.316
2024-11-10 | -5253.41 | 6.6648 | 39.1508 | 48.4627 | -1539.6225
2024-11-11 01:00 | -5608.47 | 6.6648 | 38.8361 | 48.4627 | -1643.6803
2024-11-12 02:00 | -5983.89 | 6.6648 | 38.5135 | 48.4627 | -1753.705
2024-11-13 03:00 | -6148.04 | 6.6648 | 38.3147 | 48.4627 | -1801.8127
2024-11-14 04:00 | -6718.83 | 6.6648 | 37.9033 | 48.4627 | -1969.0947
2024-11-15 05:00 | -6305.42 | 6.6648 | 37.9933 | 48.4627 | -1847.9362
2024-11-16 06:00 | -5802.77 | 6.6648 | 38.2062 | 48.4627 | -1700.624
2024-11-17 07:00 | -5865.41 | 6.6648 | 38.1862 | 48.4627 | -1718.982
2024-11-18 08:00 | -5069.62 | 6.6648 | 38.5723 | 48.4627 | -1485.759
2024-11-19 09:00 | -3615.93 | 6.6648 | 39.3746 | 48.4627 | -1059.7245
2024-11-20 10:00 | -2693.49 | 6.6648 | 40.0254 | 48.4627 | -789.384
2024-11-21 11:00 | -2212.92 | 6.6648 | 40.4554 | 48.4627 | -648.5428
2024-11-22 12:00 | -1784.9 | 6.6648 | 40.8241 | 48.4627 | -523.1026
2024-11-23 13:00 | -1655.96 | 6.202 | 40.976 | 48.4627 | -485.314
2024-11-24 14:00 | -2814.22 | 6.6648 | 40.5639 | 48.4627 | -824.7665
2024-11-25 15:00 | -3351.06 | 6.6648 | 40.2589 | 48.4627 | -982.0987
2024-11-26 16:00 | -2773.13 | 6.6648 | 40.492 | 48.4627 | -812.7242
2024-11-27 17:00 | -2612.85 | 6.6648 | 40.6164 | 48.4627 | -765.7507
2024-11-28 18:00 | -2661.03 | 6.6648 | 40.6325 | 48.4627 | -779.8709
2024-11-29 19:00 | -2941.07 | 6.6648 | 40.508 | 48.4627 | -861.9425
2024-11-30 20:00 | -3297.03 | 6.6648 | 40.3304 | 48.4627 | -966.2641
2024-12-01 21:00 | -4076.43 | 6.6648 | 39.9188 | 48.4627 | -1194.6837
2024-12-02 22:00 | -4245.48 | 6.6648 | 39.7496 | 48.4627 | -1244.2274
2024-12-03 23:00 | -5150.35 | 6.6648 | 39.2285 | 48.4627 | -1509.4186
2024-12-05 | -5351.95 | 6.6648 | 39.0053 | 48.4627 | -1568.5017
2024-12-06 01:00 | -5664.79 | 6.6648 | 38.7524 | 48.4627 | -1660.1861
2024-12-07 02:00 | -5549.07 | 6.6648 | 38.7355 | 48.4627 | -1626.2719
2024-12-08 03:00 | -5382.94 | 6.6648 | 38.7913 | 48.4627 | -1577.584
2024-12-09 04:00 | -5341.79 | 6.6648 | 38.8025 | 48.4627 | -1565.5241
2024-12-10 05:00 | -5241.59 | 6.6648 | 38.8497 | 48.4627 | -1536.1584
2024-12-11 06:00 | -4739.45 | 6.6648 | 39.1068 | 48.4627 | -1388.9957
2024-12-12 07:00 | -4677.57 | 6.6648 | 39.1896 | 48.4627 | -1370.8604
2024-12-13 08:00 | -4033.98 | 6.6648 | 39.5469 | 48.4627 | -1182.2428
2024-12-14 09:00 | -4189.78 | 6.6648 | 39.5407 | 48.4627 | -1227.9033
2024-12-15 10:00 | -3481.26 | 6.6648 | 39.9253 | 48.4627 | -1020.2566
2024-12-16 11:00 | -2863.34 | 6.6648 | 40.3215 | 48.4627 | -839.1621
2024-12-17 12:00 | -2550.03 | 6.6648 | 40.5879 | 48.4627 | -747.34
2024-12-18 13:00 | -2519.85 | 6.6648 | 40.6973 | 48.4627 | -738.4951
2024-12-19 14:00 | -3141.51 | 6.6648 | 40.4393 | 48.4627 | -920.6857
2024-12-20 15:00 | -3288.28 | 6.6648 | 40.3595 | 48.4627 | -963.6997
2024-12-21 16:00 | -3158.57 | 6.6648 | 40.4122 | 48.4627 | -925.6855
2024-12-22 17:00 | -3286.43 | 6.6648 | 40.3605 | 48.4627 | -963.1576
2024-12-23 18:00 | -3512.64 | 6.6648 | 40.2378 | 48.4627 | -1029.4532
2024-12-24 19:00 | -4197.84 | 6.6648 | 39.8634 | 48.4627 | -1230.2655
2024-12-25 20:00 | -4603.53 | 6.6648 | 39.5846 | 48.4627 | -1349.1615
2024-12-26 21:00 | -5621.12 | 6.6648 | 38.9977 | 48.4627 | -1647.3877
2024-12-27 22:00 | -6059.67 | 6.6648 | 38.6339 | 48.4627 | -1775.914
2024-12-28 23:00 | -6994.25 | 6.6648 | 38.0292 | 48.4627 | -2049.8123
2024-12-30 | -7244.26 | 6.6648 | 37.7296 | 48.4627 | -2123.083
2024-12-31 01:00 | -7598.38 | 6.6648 | 37.4152 | 48.4627 | -2226.8654
2025-01-01 02:00 | -7675.08 | 6.6648 | 37.2533 | 48.4627 | -2249.3439
2025-01-02 03:00 | -7894.72 | 6.6648 | 37.0491 | 48.4627 | -2313.714
2025-01-03 04:00 | -8026.21 | 6.6648 | 36.8872 | 48.4627 | -2352.25
2025-01-04 05:00 | -7950.9 | 6.6648 | 36.844 | 48.4627 | -2330.1788
2025-01-05 06:00 | -7442.44 | 6.6648 | 37.0435 | 48.4627 | -2181.1639
2025-01-06 07:00 | -7297.29 | 6.6648 | 37.1178 | 48.4627 | -2138.6246
2025-01-07 08:00 | -7013.57 | 6.6648 | 37.2533 | 48.4627 | -2055.4745
2025-01-08 09:00 | -7232.78 | 6.6648 | 37.1508 | 48.4627 | -2119.7186
2025-01-09 10:00 | -5978.27 | 6.6648 | 37.7651 | 48.4627 | -1752.058
2025-01-10 11:00 | -6194.46 | 6.6648 | 37.7551 | 48.4627 | -1815.417
2025-01-11 12:00 | -7251 | 6.6648 | 37.2376 | 48.4627 | -2125.0583
2025-01-12 13:00 | -7837.97 | 6.6648 | 36.8329 | 48.4627 | -2297.0823
2025-01-13 14:00 | -7976.9 | 6.6648 | 36.6493 | 48.4627 | -2337.7986
2025-01-14 15:00 | -7771.91 | 6.6648 | 36.6858 | 48.4627 | -2277.722
2025-01-15 16:00 | -7235.09 | 6.6648 | 36.911 | 48.4627 | -2120.3956
2025-01-16 17:00 | -7051.68 | 6.6648 | 37.0051 | 48.4627 | -2066.6434
2025-01-17 18:00 | -7044.73 | 6.6648 | 37.014 | 48.4627 | -2064.6066
2025-01-18 19:00 | -7411.63 | 6.6648 | 36.824 | 48.4627 | -2172.1343
2025-01-19 20:00 | -7553.32 | 6.6648 | 36.7107 | 48.4627 | -2213.6596
2025-01-20 21:00 | -8388.23 | 6.6648 | 36.2486 | 48.4627 | -2458.3475
2025-01-21 22:00 | -8359.78 | 6.6648 | 36.1441 | 48.4627 | -2450.0097
2025-01-22 23:00 | -9168.37 | 6.6648 | 35.6574 | 48.4627 | -2686.984
2025-01-24 | -9407.11 | 6.6648 | 35.4124 | 48.4627 | -2756.9518
2025-01-25 01:00 | -9438.63 | 6.6648 | 35.2964 | 48.4627 | -2766.1894
2025-01-26 02:00 | -9619.81 | 6.6648 | 35.1341 | 48.4627 | -2819.288
2025-01-27 03:00 | -9588.65 | 6.6648 | 35.0822 | 48.4627 | -2810.1559
2025-01-28 04:00 | -9337.66 | 6.6648 | 35.15 | 48.4627 | -2736.598
2025-01-29 05:00 | -9330.19 | 6.6648 | 35.1319 | 48.4627 | -2734.4088
2025-01-30 06:00 | -8830.07 | 6.6648 | 35.3557 | 48.4627 | -2587.8381
2025-01-31 07:00 | -8653.16 | 6.6648 | 35.4595 | 48.4627 | -2535.9909
2025-02-01 08:00 | -8351.11 | 6.6648 | 35.6242 | 48.4627 | -2447.4687
2025-02-02 09:00 | -8576.98 | 6.6648 | 35.5353 | 48.4627 | -2513.6647
2025-02-03 10:00 | -8509.74 | 6.6648 | 35.5445 | 48.4627 | -2493.9586
2025-02-04 11:00 | -8058.55 | 6.6648 | 35.7631 | 48.4627 | -2361.7279
2025-02-05 12:00 | -7464.78 | 6.6648 | 36.0991 | 48.4627 | -2187.7111
2025-02-06 13:00 | -7643.29 | 6.6648 | 36.0766 | 48.4627 | -2240.0272
2025-02-07 14:00 | -7725.46 | 6.6648 | 36.0466 | 48.4627 | -2264.1088
2025-02-08 15:00 | -7846 | 6.6648 | 35.986 | 48.4627 | -2299.4356
2025-02-09 16:00 | -7153.47 | 6.6648 | 36.3292 | 48.4627 | -2096.4751
2025-02-10 17:00 | -7181.2 | 6.6648 | 36.3743 | 48.4627 | -2104.602
2025-02-11 18:00 | -7281.14 | 6.6648 | 36.3411 | 48.4627 | -2133.8915
2025-02-12 19:00 | -7672.6 | 6.6648 | 36.1385 | 48.4627 | -2248.6171
2025-02-13 20:00 | -8036.9 | 6.6648 | 35.9168 | 48.4627 | -2355.3829
2025-02-14 21:00 | -8932.01 | 6.6648 | 35.417 | 48.4627 | -2617.7137
2025-02-15 22:00 | -9136.67 | 6.6648 | 35.1963 | 48.4627 | -2677.6937
2025-02-16 23:00 | -9803.99 | 6.6648 | 34.7686 | 48.4627 | -2873.2658
2025-02-18 | -10212.9 | 6.6648 | 34.4362 | 48.4627 | -2993.1055
2025-02-19 01:00 | -10742.4 | 6.6648 | 34.0436 | 48.4627 | -3148.2867
2025-02-20 02:00 | -10627.7 | 6.6648 | 33.9703 | 48.4627 | -3114.6714
2025-02-21 03:00 | -10515.8 | 6.6648 | 33.9561 | 48.4627 | -3081.8768
2025-02-22 04:00 | -10444.8 | 6.6648 | 33.9375 | 48.4627 | -3061.0687
2025-02-23 05:00 | -10709.7 | 6.6648 | 33.7564 | 48.4627 | -3138.7032
2025-02-24 06:00 | -10681.3 | 6.6648 | 33.6969 | 48.4627 | -3130.38
2025-02-25 07:00 | -9943.15 | 6.6648 | 34.025 | 48.4627 | -2914.0496
2025-02-26 08:00 | -9043.63 | 6.6648 | 34.5131 | 48.4627 | -2650.4263
2025-02-27 09:00 | -9798.29 | 6.6648 | 34.2151 | 48.4627 | -2871.5953
2025-02-28 10:00 | -9676.12 | 6.6648 | 34.2308 | 48.4627 | -2835.7908
2025-03-01 11:00 | -9352.68 | 6.6648 | 34.3791 | 48.4627 | -2740.9999
2025-03-02 12:00 | -8799.9 | 6.6648 | 34.6926 | 48.4627 | -2578.9961
2025-03-03 13:00 | -8966.9 | 6.6648 | 34.6687 | 48.4627 | -2627.939
2025-03-04 14:00 | -9001.67 | 6.6648 | 34.6504 | 48.4627 | -2638.1291
2025-03-05 15:00 | -9143.59 | 6.6648 | 34.5794 | 48.4627 | -2679.7217
2025-03-06 16:00 | -8926.14 | 6.6648 | 34.6764 | 48.4627 | -2615.9934
2025-03-07 17:00 | -7439.18 | 6.6648 | 35.4497 | 48.4627 | -2180.2084
2025-03-08 18:00 | -8000.55 | 6.6648 | 35.3064 | 48.4627 | -2344.7297
2025-03-09 19:00 | -8121.22 | 6.6648 | 35.2649 | 48.4627 | -2380.0946
2025-03-10 20:00 | -8433.91 | 6.6648 | 35.0956 | 48.4627 | -2471.735
2025-03-11 21:00 | -8486.81 | 6.6648 | 35.0631 | 48.4627 | -2487.2385
2025-03-12 22:00 | -8457.04 | 6.6648 | 35.0806 | 48.4627 | -2478.5138
2025-03-13 23:00 | -8824.18 | 6.6648 | 34.8867 | 48.4627 | -2586.1119
2025-03-15 | -10470.5 | 6.6648 | 34.0078 | 48.4627 | -3068.6006
2025-03-16 01:00 | -10976.8 | 6.6648 | 33.569 | 48.4627 | -3216.9825
2025-03-17 02:00 | -11329.8 | 6.6648 | 33.2403 | 48.4627 | -3320.4366
2025-03-18 03:00 | -11447.7 | 6.6648 | 33.063 | 48.4627 | -3354.9897
2025-03-19 04:00 | -11680 | 6.6648 | 32.8398 | 48.4627 | -3423.0701
2025-03-20 05:00 | -11779.4 | 6.6648 | 32.6702 | 48.4627 | -3452.2014
2025-03-21 06:00 | -11787.2 | 6.6648 | 32.5806 | 48.4627 | -3454.4873
2025-03-22 07:00 | -10950.9 | 6.6648 | 32.94 | 48.4627 | -3209.392
2025-03-23 08:00 | -10251.7 | 6.6648 | 33.3189 | 48.4627 | -3004.4767
2025-03-24 09:00 | -10873.3 | 6.6648 | 33.0589 | 48.4627 | -3186.6497
2025-03-25 10:00 | -9854.47 | 6.6648 | 33.5298 | 48.4627 | -2888.0601
2025-03-26 11:00 | -8463.44 | 6.6648 | 34.3057 | 48.4627 | -2480.3894
2025-03-27 12:00 | -8937.24 | 6.6648 | 34.2419 | 48.4627 | -2619.2465
2025-03-28 13:00 | -9442.87 | 6.6648 | 34.022 | 48.4627 | -2767.432
2025-03-29 14:00 | -10221.3 | 6.6648 | 33.5895 | 48.4627 | -2995.5673
2025-03-30 15:00 | -10482.2 | 6.6648 | 33.3879 | 48.4627 | -3072.0296
2025-03-31 16:00 | -10527.8 | 6.6648 | 33.3015 | 48.4627 | -3085.3936
2025-04-01 17:00 | -9699.84 | 6.6648 | 33.662 | 48.4627 | -2842.7425
2025-04-02 18:00 | -10365.8 | 6.6648 | 33.3598 | 48.4627 | -3037.9161
2025-04-03 19:00 | -10758.2 | 6.6648 | 33.0961 | 48.4627 | -3152.9172
2025-04-04 20:00 | -11256.2 | 6.6648 | 32.7588 | 48.4627 | -3298.8666
2025-04-05 21:00 | -11392.1 | 6.6648 | 32.6039 | 48.4627 | -3338.6949
2025-04-06 22:00 | -11543.9 | 6.6648 | 32.4517 | 48.4627 | -3383.1831
2025-04-07 23:00 | -11562.2 | 6.6648 | 32.3504 | 48.4627 | -3388.5463
2025-04-09 | -12226.2 | 6.6648 | 31.9486 | 48.4627 | -3583.1455
2025-04-10 01:00 | -12677.7 | 6.6648 | 31.6073 | 48.4627 | -3715.4671
2025-04-11 02:00 | -12716.9 | 6.6648 | 31.478 | 48.4627 | -3726.9555
2025-04-12 03:00 | -12684 | 6.6648 | 31.4231 | 48.4627 | -3717.3135
2025-04-13 04:00 | -12635.5 | 6.6648 | 31.3964 | 48.4627 | -3703.0995
2025-04-14 05:00 | -12646.1 | 6.6648 | 31.3381 | 48.4627 | -3706.2061
2025-04-15 06:00 | -12440 | 6.6648 | 31.4032 | 48.4627 | -3645.8041
2025-04-16 07:00 | -11669.8 | 6.6648 | 31.7843 | 48.4627 | -3420.0808
2025-04-17 08:00 | -10321.1 | 6.6648 | 32.5313 | 48.4627 | -3024.8158
2025-04-18 09:00 | -9445.48 | 6.6648 | 33.1362 | 48.4627 | -2768.1969
2025-04-19 10:00 | -7645.86 | 6.6648 | 34.2213 | 48.4627 | -2240.7804
2025-04-20 11:00 | -6292.66 | 6.6648 | 35.1756 | 48.4627 | -1844.1966
2025-04-21 12:00 | -5214.76 | 6.6648 | 36.0278 | 48.4627 | -1528.2953
2025-04-22 13:00 | -4474.51 | 6.6648 | 36.7061 | 48.4627 | -1311.3494
2025-04-23 14:00 | -4348.09 | 6.6648 | 37.0464 | 48.4627 | -1274.2994
2025-04-24 15:00 | -4702.33 | 6.6648 | 37.0828 | 48.4627 | -1378.1169
2025-04-25 16:00 | -4534.32 | 6.6648 | 37.2974 | 48.4627 | -1328.878
2025-04-26 17:00 | -5329.86 | 6.6648 | 37.0181 | 48.4627 | -1562.0278
2025-04-27 18:00 | -6326.87 | 6.6648 | 36.5437 | 48.4627 | -1854.2226
2025-04-28 19:00 | -7323.34 | 6.6648 | 35.9838 | 48.4627 | -2146.2591
2025-04-29 20:00 | -7756.68 | 6.6648 | 35.6641 | 48.4627 | -2273.2585
2025-04-30 21:00 | -9413.08 | 6.6648 | 34.7415 | 48.4627 | -2758.7014
2025-05-01 22:00 | -10105.7 | 6.6648 | 34.1729 | 48.4627 | -2961.6883
2025-05-02 23:00 | -10725.5 | 6.6648 | 33.6569 | 48.4627 | -3143.3338
2025-05-04 | -10616.7 | 6.6648 | 33.5355 | 48.4627 | -3111.4476
2025-05-05 01:00 | -11370.3 | 6.6648 | 33.0411 | 48.4627 | -3332.306
2025-05-06 02:00 | -11015.3 | 6.6648 | 33.0582 | 48.4627 | -3228.2658
2025-05-07 03:00 | -11618 | 6.6648 | 32.679 | 48.4627 | -3404.8997
2025-05-08 04:00 | -11306.1 | 6.6648 | 32.7222 | 48.4627 | -3313.4908
2025-05-09 05:00 | -10861.1 | 6.6648 | 32.8999 | 48.4627 | -3183.0742
2025-05-10 06:00 | -10371.1 | 6.6648 | 33.1518 | 48.4627 | -3039.4694
2025-05-11 07:00 | -9347.41 | 6.6648 | 33.7152 | 48.4627 | -2739.4555
2025-05-12 08:00 | -7836.45 | 6.6648 | 34.5898 | 48.4627 | -2296.6368
2025-05-13 09:00 | -6810.93 | 6.6648 | 35.3281 | 48.4627 | -1996.0865
2025-05-14 10:00 | -5055.9 | 6.6648 | 36.4424 | 48.4627 | -1481.738
2025-05-15 11:00 | -4004.74 | 6.6648 | 37.2764 | 48.4627 | -1173.6734
2025-05-16 12:00 | -2928.88 | 6.6648 | 38.1147 | 48.4627 | -858.37
2025-05-17 13:00 | -2393 | 6.6648 | 38.6828 | 48.4627 | -701.3191
2025-05-18 14:00 | -2545.05 | 6.6648 | 38.8548 | 48.4627 | -745.8805
2025-05-19 15:00 | -3112.76 | 6.6648 | 38.7423 | 48.4627 | -912.2599
2025-05-20 16:00 | -2571.8 | 6.6648 | 39.0997 | 48.4627 | -753.7202
2025-05-21 17:00 | -2908.5 | 6.6648 | 39.071 | 48.4627 | -852.3972
2025-05-22 18:00 | -3436.58 | 6.6648 | 38.888 | 48.4627 | -1007.1622
2025-05-23 19:00 | -4302.36 | 6.6648 | 38.4699 | 48.4627 | -1260.8972
2025-05-24 20:00 | -4794.34 | 6.6648 | 38.181 | 48.4627 | -1405.0824
2025-05-25 21:00 | -5757.57 | 6.6648 | 37.6612 | 48.4627 | -1687.3772
2025-05-26 22:00 | -6165.18 | 6.6648 | 37.3524 | 48.4627 | -1806.8359
2025-05-27 23:00 | -7322.26 | 6.6648 | 36.6728 | 48.4627 | -2145.9426
2025-05-29 | -7825.39 | 6.6648 | 36.2551 | 48.4627 | -2293.3954
2025-05-30 01:00 | -8035.57 | 6.6648 | 36.0104 | 48.4627 | -2354.9931
2025-05-31 02:00 | -8345.25 | 6.6648 | 35.7517 | 48.4627 | -2445.7513
2025-06-01 03:00 | -8251.23 | 6.6648 | 35.7129 | 48.4627 | -2418.1968
2025-06-02 04:00 | -8084.97 | 6.6648 | 35.7398 | 48.4627 | -2369.4708
2025-06-03 05:00 | -7912.93 | 6.6648 | 35.8097 | 48.4627 | -2319.0509
2025-06-04 06:00 | -7381.93 | 6.6648 | 36.0811 | 48.4627 | -2163.4301
2025-06-05 07:00 | -6894.89 | 6.6648 | 36.3752 | 48.4627 | -2020.6928
2025-06-06 08:00 | -6116.24 | 6.6648 | 36.8389 | 48.4627 | -1792.493
2025-06-07 09:00 | -4592.91 | 6.6648 | 37.727 | 48.4627 | -1346.049
2025-06-08 10:00 | -2891.34 | 6.6648 | 38.8 | 48.4627 | -847.3681
2025-06-09 11:00 | -1572.01 | 6.0677 | 39.6813 | 48.4627 | -460.7107
2025-06-10 12:00 | -748.155 | 2.8631 | 39.9689 | 48.4627 | -219.2626
2025-06-11 13:00 | -290.506 | 1.5146 | 40.4767 | 48.4627 | -85.1389
2025-06-12 14:00 | -122.735 | 1.045 | 40.971 | 48.4627 | -35.9701
2025-06-13 15:00 | -232.56 | 1.5103 | 41.043 | 48.4627 | -68.1566
2025-06-14 16:00 | -253.242 | 1.5305 | 41.1393 | 48.4627 | -74.2179
2025-06-15 17:00 | -905.347 | 3.9798 | 41.0412 | 48.4627 | -265.331
2025-06-16 18:00 | -1541.86 | 6.1092 | 40.9966 | 48.4627 | -451.8746
2025-06-17 19:00 | -2499.38 | 6.6648 | 40.5787 | 48.4627 | -732.496
2025-06-18 20:00 | -3253.39 | 6.6648 | 40.1352 | 48.4627 | -953.4745
2025-06-19 21:00 | -4108.54 | 6.6648 | 39.6182 | 48.4627 | -1204.0942
2025-06-20 22:00 | -4866.87 | 6.6648 | 39.1104 | 48.4627 | -1426.3388
2025-06-21 23:00 | -5973.62 | 6.6648 | 38.4105 | 48.4627 | -1750.6952
2025-06-23 | -6579.04 | 6.6648 | 37.917 | 48.4627 | -1928.1263
2025-06-24 01:00 | -6874.33 | 6.6648 | 37.6019 | 48.4627 | -2014.6672
2025-06-25 02:00 | -7082.86 | 6.6648 | 37.3662 | 48.4627 | -2075.7814
2025-06-26 03:00 | -7200.18 | 6.6648 | 37.1996 | 48.4627 | -2110.1645
2025-06-27 04:00 | -7433.91 | 6.6648 | 36.9892 | 48.4627 | -2178.664
2025-06-28 05:00 | -7786.58 | 6.6648 | 36.7266 | 48.4627 | -2282.0213
2025-06-29 06:00 | -7629.1 | 6.6648 | 36.7143 | 48.4627 | -2235.8685
2025-06-30 07:00 | -7879.52 | 6.6648 | 36.5369 | 48.4627 | -2309.2594
2025-07-01 08:00 | -7706.38 | 6.6648 | 36.5555 | 48.4627 | -2258.517
2025-07-02 09:00 | -7575.98 | 6.6648 | 36.5773 | 48.4627 | -2220.3006
2025-07-03 10:00 | -6204.46 | 6.6648 | 37.2438 | 48.4627 | -1818.3477
2025-07-04 11:00 | -5536.37 | 6.6648 | 37.6812 | 48.4627 | -1622.5499
2025-07-05 12:00 | -4242.43 | 6.6648 | 38.4409 | 48.4627 | -1243.3335
2025-07-06 13:00 | -4566.24 | 6.6648 | 38.4433 | 48.4627 | -1338.2328
2025-07-07 14:00 | -4514.87 | 6.6648 | 38.5352 | 48.4627 | -1323.1778
2025-07-08 15:00 | -5106.02 | 6.6648 | 38.286 | 48.4627 | -1496.4267
2025-07-09 16:00 | -5659.89 | 6.6648 | 37.9818 | 48.4627 | -1658.75
2025-07-10 17:00 | -6806.66 | 6.6648 | 37.3374 | 48.4627 | -1994.8351
2025-07-11 18:00 | -7285.02 | 6.6648 | 36.9408 | 48.4627 | -2135.0286
2025-07-12 19:00 | -8697.18 | 6.6648 | 36.0944 | 48.4627 | -2548.8918
2025-07-13 20:00 | -9772.98 | 6.6648 | 35.33 | 48.4627 | -2864.1777
2025-07-14 21:00 | -11071.8 | 6.6648 | 34.4297 | 48.4627 | -3244.8243
2025-07-15 22:00 | -11899.4 | 6.6648 | 33.7233 | 48.4627 | -3487.3699
2025-07-16 23:00 | -12147.2 | 6.6648 | 33.3314 | 48.4627 | -3559.9929
2025-07-18 | -12503.5 | 6.6648 | 32.9307 | 48.4627 | -3664.4141
2025-07-19 01:00 | -12791.8 | 6.6648 | 32.5883 | 48.4627 | -3748.9065
2025-07-20 02:00 | -12929.3 | 6.6648 | 32.3348 | 48.4627 | -3789.2038
2025-07-21 03:00 | -13039.6 | 6.6648 | 32.1295 | 48.4627 | -3821.5295
2025-07-22 04:00 | -13040.3 | 6.6648 | 32.0012 | 48.4627 | -3821.7347
2025-07-23 05:00 | -12988.2 | 6.6648 | 31.923 | 48.4627 | -3806.4657
2025-07-24 06:00 | -12864.7 | 6.6648 | 31.8971 | 48.4627 | -3770.2714
2025-07-25 07:00 | -12420.1 | 6.6648 | 32.0624 | 48.4627 | -3639.972
2025-07-26 08:00 | -10907.2 | 6.6648 | 32.8232 | 48.4627 | -3196.5848
2025-07-27 09:00 | -10140 | 6.6648 | 33.3379 | 48.4627 | -2971.7406
2025-07-28 10:00 | -8940.82 | 6.6648 | 34.0714 | 48.4627 | -2620.2957
2025-07-29 11:00 | -8240.1 | 6.6648 | 34.5897 | 48.4627 | -2414.9349
2025-07-30 12:00 | -7551.27 | 6.6648 | 35.0947 | 48.4627 | -2213.0588
2025-07-31 13:00 | -7126.24 | 6.6648 | 35.4685 | 48.4627 | -2088.4948
2025-08-01 14:00 | -7107.62 | 6.6648 | 35.6058 | 48.4627 | -2083.0378
2025-08-02 15:00 | -7528.46 | 6.6648 | 35.4762 | 48.4627 | -2206.3738
2025-08-03 16:00 | -7159.64 | 6.6648 | 35.6801 | 48.4627 | -2098.2834
2025-08-04 17:00 | -8014.56 | 6.6648 | 35.3056 | 48.4627 | -2348.8357
2025-08-05 18:00 | -8662.37 | 6.6648 | 34.9389 | 48.4627 | -2538.69
2025-08-06 19:00 | -9279.81 | 6.6648 | 34.5484 | 48.4627 | -2719.6438
2025-08-07 20:00 | -9754.04 | 6.6648 | 34.212 | 48.4627 | -2858.6269
2025-08-08 21:00 | -10720 | 6.6648 | 33.6278 | 48.4627 | -3141.7219
2025-08-09 22:00 | -11349.7 | 6.6648 | 33.1419 | 48.4627 | -3326.2687
2025-08-10 23:00 | -12055.5 | 6.6648 | 32.6211 | 48.4627 | -3533.1183
2025-08-12 | -12279.2 | 6.6648 | 32.3357 | 48.4627 | -3598.6783
2025-08-13 01:00 | -12434.3 | 6.6648 | 32.1179 | 48.4627 | -3644.1336
2025-08-14 02:00 | -12433.2 | 6.6648 | 32.001 | 48.4627 | -3643.8112
2025-08-15 03:00 | -12428.9 | 6.6648 | 31.919 | 48.4627 | -3642.551
2025-08-16 04:00 | -12531.5 | 6.6648 | 31.7935 | 48.4627 | -3672.6201
2025-08-17 05:00 | -12545.9 | 6.6648 | 31.7213 | 48.4627 | -3676.8403
2025-08-18 06:00 | -12442.5 | 6.6648 | 31.72 | 48.4627 | -3646.5368
2025-08-19 07:00 | -11352.8 | 6.6648 | 32.2448 | 48.4627 | -3327.1772
2025-08-20 08:00 | -9813.93 | 6.6648 | 33.1025 | 48.4627 | -2876.179
2025-08-21 09:00 | -9355.65 | 6.6648 | 33.5122 | 48.4627 | -2741.8704
2025-08-22 10:00 | -8402.62 | 6.6648 | 34.1268 | 48.4627 | -2462.5648
2025-08-23 11:00 | -7307.82 | 6.6648 | 34.8494 | 48.4627 | -2141.7106
2025-08-24 12:00 | -6518.5 | 6.6648 | 35.4651 | 48.4627 | -1910.3838
2025-08-25 13:00 | -6227.05 | 6.6648 | 35.816 | 48.4627 | -1824.9682
2025-08-26 14:00 | -6154.65 | 6.6648 | 35.9984 | 48.4627 | -1803.7499
2025-08-27 15:00 | -5991.01 | 6.6648 | 36.199 | 48.4627 | -1755.7917
2025-08-28 16:00 | -6595.51 | 6.6648 | 35.9963 | 48.4627 | -1932.9532
2025-08-29 17:00 | -5990.81 | 6.6648 | 36.3326 | 48.4627 | -1755.7331
2025-08-30 18:00 | -7015.04 | 6.6648 | 35.9067 | 48.4627 | -2055.9053
2025-08-31 19:00 | -7752.35 | 6.6648 | 35.5084 | 48.4627 | -2271.9895
2025-09-01 20:00 | -8405.32 | 6.6648 | 35.0992 | 48.4627 | -2463.3561
2025-09-02 21:00 | -8832.36 | 6.6648 | 34.7988 | 48.4627 | -2588.5092
2025-09-03 22:00 | -9235 | 6.6648 | 34.521 | 48.4627 | -2706.5113
2025-09-04 23:00 | -9390.19 | 6.6648 | 34.3505 | 48.4627 | -2751.993
2025-09-06 | -10724.7 | 6.6648 | 33.5997 | 48.4627 | -3143.0993
2025-09-07 01:00 | -11229 | 6.6648 | 33.1661 | 48.4627 | -3290.895
2025-09-08 02:00 | -11527.7 | 6.6648 | 32.8612 | 48.4627 | -3378.4354
2025-09-09 03:00 | -11688 | 6.6648 | 32.6579 | 48.4627 | -3425.4147
2025-09-10 04:00 | -11753.7 | 6.6648 | 32.5242 | 48.4627 | -3444.6694
2025-09-11 05:00 | -11830.8 | 6.6648 | 32.3898 | 48.4627 | -3467.2652
2025-09-12 06:00 | -11632.5 | 6.6648 | 32.4251 | 48.4627 | -3409.1492
2025-09-13 07:00 | -10148.5 | 6.6648 | 33.1543 | 48.4627 | -2974.2318
2025-09-14 08:00 | -8735.66 | 6.6648 | 33.9889 | 48.4627 | -2560.1692
2025-09-15 09:00 | -8167.43 | 6.6648 | 34.4642 | 48.4627 | -2393.6374
2025-09-16 10:00 | -6872.71 | 6.6648 | 35.2659 | 48.4627 | -2014.1925
2025-09-17 11:00 | -5796.58 | 6.6648 | 36.0195 | 48.4627 | -1698.8099
2025-09-18 12:00 | -5228.38 | 6.6648 | 36.5524 | 48.4627 | -1532.2869
2025-09-19 13:00 | -4883.6 | 6.6648 | 36.9274 | 48.4627 | -1431.2419
2025-09-20 14:00 | -4973.19 | 6.6648 | 37.0427 | 48.4627 | -1457.4981
2025-09-21 15:00 | -4867.09 | 6.6648 | 37.2134 | 48.4627 | -1426.4033
2025-09-22 16:00 | -5507.17 | 6.6648 | 36.9888 | 48.4627 | -1613.9922
2025-09-23 17:00 | -4882.06 | 6.6648 | 37.3282 | 48.4627 | -1430.7905
2025-09-24 18:00 | -6061.03 | 6.6648 | 36.8262 | 48.4627 | -1776.3125
2025-09-25 19:00 | -7082.23 | 6.6648 | 36.2655 | 48.4627 | -2075.5967
2025-09-26 20:00 | -7795.28 | 6.6648 | 35.7892 | 48.4627 | -2284.5711
2025-09-27 21:00 | -8374.11 | 6.6648 | 35.3812 | 48.4627 | -2454.2094
2025-09-28 22:00 | -8737.95 | 6.6648 | 35.0846 | 48.4627 | -2560.8404
2025-09-29 23:00 | -9228.72 | 6.6648 | 34.7132 | 48.4627 | -2704.6708
2025-10-01 | -10561.8 | 6.6648 | 33.9126 | 48.4627 | -3095.358
2025-10-02 01:00 | -10990.3 | 6.6648 | 33.4887 | 48.4627 | -3220.939
2025-10-03 02:00 | -11184.3 | 6.6648 | 33.223 | 48.4627 | -3277.7948
2025-10-04 03:00 | -11442.7 | 6.6648 | 32.9677 | 48.4627 | -3353.5243
2025-10-05 04:00 | -11626.2 | 6.6648 | 32.7558 | 48.4627 | -3407.3029
2025-10-06 05:00 | -11841.5 | 6.6648 | 32.5287 | 48.4627 | -3470.4011
2025-10-07 06:00 | -11064.3 | 6.6648 | 32.8353 | 48.4627 | -3242.6262
2025-10-08 07:00 | -10199.4 | 6.6648 | 33.2861 | 48.4627 | -2989.1491
2025-10-09 08:00 | -8699.41 | 6.6648 | 34.1223 | 48.4627 | -2549.5454
2025-10-10 09:00 | -7560.87 | 6.6648 | 34.8689 | 48.4627 | -2215.8723
2025-10-11 10:00 | -6142.97 | 6.6648 | 35.7828 | 48.4627 | -1800.3268
2025-10-12 11:00 | -4717.1 | 6.6648 | 36.7545 | 48.4627 | -1382.4455
2025-10-13 12:00 | -3609.19 | 6.6648 | 37.6093 | 48.4627 | -1057.7492
2025-10-14 13:00 | -3781.8 | 6.6648 | 37.8123 | 48.4627 | -1108.3362
2025-10-15 14:00 | -2981.91 | 6.6648 | 38.3923 | 48.4627 | -873.9116
2025-10-16 15:00 | -3574.16 | 6.6648 | 38.303 | 48.4627 | -1047.4829
2025-10-17 16:00 | -3543.45 | 6.6648 | 38.4279 | 48.4627 | -1038.4827
2025-10-18 17:00 | -4373.14 | 6.6648 | 38.0962 | 48.4627 | -1281.6408
2025-10-19 18:00 | -5149.93 | 6.6648 | 37.7062 | 48.4627 | -1509.2955
2025-10-20 19:00 | -6104.39 | 6.6648 | 37.1853 | 48.4627 | -1789.0201
2025-10-21 20:00 | -6705.22 | 6.6648 | 36.7838 | 48.4627 | -1965.106
2025-10-22 21:00 | -8027.96 | 6.6648 | 36.0171 | 48.4627 | -2352.7628
2025-10-23 22:00 | -8486 | 6.6648 | 35.6011 | 48.4627 | -2487.0011
2025-10-24 23:00 | -9481.29 | 6.6648 | 34.9384 | 48.4627 | -2778.6918
2025-10-26 | -10232.9 | 6.6648 | 34.3664 | 48.4627 | -2998.967
2025-10-27 01:00 | -10260 | 6.6648 | 34.1647 | 48.4627 | -3006.9092
2025-10-28 02:00 | -10587.7 | 6.6648 | 33.8677 | 48.4627 | -3102.9486
2025-10-29 03:00 | -10425.8 | 6.6648 | 33.8368 | 48.4627 | -3055.5004
2025-10-30 04:00 | -10720.5 | 6.6648 | 33.6105 | 48.4627 | -3141.8684
2025-10-31 05:00 | -10428.3 | 6.6648 | 33.6789 | 48.4627 | -3056.233
2025-11-01 06:00 | -10019.6 | 6.6648 | 33.8635 | 48.4627 | -2936.4549
2025-11-02 07:00 | -9045.49 | 6.6648 | 34.3729 | 48.4627 | -2650.9714
2025-11-03 08:00 | -8041.41 | 6.6648 | 34.969 | 48.4627 | -2356.7046
2025-11-04 09:00 | -7748.97 | 6.6648 | 35.2497 | 48.4627 | -2270.9989
2025-11-05 10:00 | -5669.87 | 6.6648 | 36.4063 | 48.4627 | -1661.6749
2025-11-06 11:00 | -3980.27 | 6.6648 | 37.5246 | 48.4627 | -1166.502
2025-11-07 12:00 | -3074.93 | 6.6648 | 38.3054 | 48.4627 | -901.173
2025-11-08 13:00 | -2688.57 | 6.6648 | 38.7729 | 48.4627 | -787.9421
2025-11-09 14:00 | -2387.76 | 6.6648 | 39.1389 | 48.4627 | -699.7834
2025-11-10 15:00 | -2210.86 | 6.6648 | 39.4297 | 48.4627 | -647.9391
2025-11-11 16:00 | -2117.65 | 6.6648 | 39.6423 | 48.4627 | -620.622
2025-11-12 17:00 | -2138.07 | 6.6648 | 39.7645 | 48.4627 | -626.6065
2025-11-13 18:00 | -3002.65 | 6.6648 | 39.4343 | 48.4627 | -879.9898
2025-11-14 19:00 | -3804.08 | 6.6648 | 39.0427 | 48.4627 | -1114.8658
2025-11-15 20:00 | -4430.83 | 6.6648 | 38.6889 | 48.4627 | -1298.5481
2025-11-16 21:00 | -5747.15 | 6.6648 | 37.9783 | 48.4627 | -1684.3234
2025-11-17 22:00 | -6270.5 | 6.6648 | 37.5735 | 48.4627 | -1837.7021
2025-11-18 23:00 | -7186.9 | 6.6648 | 36.9785 | 48.4627 | -2106.2725
2025-11-20 | -7265.16 | 6.6648 | 36.7885 | 48.4627 | -2129.2082
2025-11-21 01:00 | -7424.38 | 6.6648 | 36.6114 | 48.4627 | -2175.871
2025-11-22 02:00 | -7639.15 | 6.6648 | 36.4259 | 48.4627 | -2238.8139
2025-11-23 03:00 | -7712.31 | 6.6648 | 36.3204 | 48.4627 | -2260.2549
2025-11-24 04:00 | -7741.13 | 6.6648 | 36.2526 | 48.4627 | -2268.7013
2025-11-25 05:00 | -7562.44 | 6.6648 | 36.3107 | 48.4627 | -2216.3324
2025-11-26 06:00 | -7075.53 | 6.6648 | 36.5512 | 48.4627 | -2073.6331
2025-11-27 07:00 | -6605.49 | 6.6648 | 36.8267 | 48.4627 | -1935.878
2025-11-28 08:00 | -5850.98 | 6.6648 | 37.2685 | 48.4627 | -1714.753
2025-11-29 09:00 | -5137.35 | 6.6648 | 37.7398 | 48.4627 | -1505.6087
2025-11-30 10:00 | -3390.98 | 6.6648 | 38.7568 | 48.4627 | -993.7981
2025-12-01 11:00 | -1997.06 | 6.6648 | 39.7099 | 48.4627 | -585.2805
2025-12-02 12:00 | -1284.74 | 4.8591 | 40.1029 | 48.4627 | -376.5201
2025-12-03 13:00 | -1101.6 | 4.3576 | 40.3775 | 48.4627 | -322.8471
2025-12-04 14:00 | -1231.24 | 4.9074 | 40.5597 | 48.4627 | -360.8408
2025-12-05 15:00 | -2001.85 | 6.6648 | 40.5205 | 48.4627 | -586.6843
2025-12-06 16:00 | -2517.12 | 6.6648 | 40.2824 | 48.4627 | -737.6951
2025-12-07 17:00 | -2433.72 | 6.6648 | 40.3114 | 48.4627 | -713.2529
2025-12-08 18:00 | -2706.37 | 6.6648 | 40.1979 | 48.4627 | -793.1588
2025-12-09 19:00 | -3143.7 | 6.6648 | 39.9828 | 48.4627 | -921.3275
2025-12-10 20:00 | -3624.11 | 6.6648 | 39.7125 | 48.4627 | -1062.1218
2025-12-11 21:00 | -4615.18 | 6.6648 | 39.1749 | 48.4627 | -1352.5757
2025-12-12 22:00 | -5484.58 | 6.6648 | 38.6301 | 48.4627 | -1607.3717
2025-12-13 23:00 | -6537.36 | 6.6648 | 37.9522 | 48.4627 | -1915.9111
2025-12-15 | -6940.49 | 6.6648 | 37.5648 | 48.4627 | -2034.0568
2025-12-16 01:00 | -7096.22 | 6.6648 | 37.3364 | 48.4627 | -2079.6968
2025-12-17 02:00 | -7405.25 | 6.6648 | 37.068 | 48.4627 | -2170.2645
2025-12-18 03:00 | -7585.75 | 6.6648 | 36.8729 | 48.4627 | -2223.1639
2025-12-19 04:00 | -7535.83 | 6.6648 | 36.8145 | 48.4627 | -2208.5338
2025-12-20 05:00 | -7631.4 | 6.6648 | 36.717 | 48.4627 | -2236.5426
2025-12-21 06:00 | -7117.67 | 6.6648 | 36.9297 | 48.4627 | -2085.9832
2025-12-22 07:00 | -6332.46 | 6.6648 | 37.3354 | 48.4627 | -1855.8608
2025-12-23 08:00 | -4991.28 | 6.6648 | 38.0849 | 48.4627 | -1462.7998
2025-12-24 09:00 | -4550.94 | 6.6648 | 38.4668 | 48.4627 | -1333.7489
2025-12-25 10:00 | -2233.17 | 6.6648 | 39.7687 | 48.4627 | -654.4775
2025-12-26 11:00 | -1162.54 | 4.3791 | 40.2976 | 48.4627 | -340.7068
2025-12-27 12:00 | -1336.6 | 5.3038 | 40.625 | 48.4627 | -391.7188
2025-12-28 13:00 | -2038.4 | 6.6648 | 40.5924 | 48.4627 | -597.3961
2025-12-29 14:00 | -2312.38 | 6.6648 | 40.4952 | 48.4627 | -677.6917
2025-12-30 15:00 | -2432.98 | 6.6648 | 40.4795 | 48.4627 | -713.0361
2025-12-31 16:00 | -1739.9 | 6.5743 | 40.8476 | 48.4627 | -509.9144
2026-01-01 17:00 | -1841.33 | 6.6648 | 40.897 | 48.4627 | -539.6406
2026-01-02 18:00 | -1991.27 | 6.6648 | 40.8773 | 48.4627 | -583.5836
2026-01-03 19:00 | -2728.49 | 6.6648 | 40.5405 | 48.4627 | -799.6415
2026-01-04 20:00 | -3292 | 6.6648 | 40.2264 | 48.4627 | -964.79
2026-01-05 21:00 | -4423.33 | 6.6648 | 39.6072 | 48.4627 | -1296.3501
2026-01-06 22:00 | -5321.75 | 6.6648 | 39.0117 | 48.4627 | -1559.651
2026-01-07 23:00 | -6520.78 | 6.6648 | 38.2346 | 48.4627 | -1911.052
2026-01-09 | -6984.44 | 6.6648 | 37.787 | 48.4627 | -2046.9373
2026-01-10 01:00 | -7323.22 | 6.6648 | 37.4488 | 48.4627 | -2146.2239
2026-01-11 02:00 | -7923.75 | 6.6648 | 37.0054 | 48.4627 | -2322.2219
2026-01-12 03:00 | -8220.26 | 6.6648 | 36.704 | 48.4627 | -2409.1204
2026-01-13 04:00 | -8111.32 | 6.6648 | 36.6235 | 48.4627 | -2377.1932
2026-01-14 05:00 | -7793.26 | 6.6648 | 36.709 | 48.4627 | -2283.979
2026-01-15 06:00 | -7436.4 | 6.6648 | 36.8534 | 48.4627 | -2179.3937
2026-01-16 07:00 | -6554.06 | 6.6648 | 37.2926 | 48.4627 | -1920.8054
2026-01-17 08:00 | -4941.66 | 6.6648 | 38.175 | 48.4627 | -1448.2576
2026-01-18 09:00 | -3847.89 | 6.6648 | 38.9148 | 48.4627 | -1127.7052
2026-01-19 10:00 | -1912.34 | 6.6648 | 40.0931 | 48.4627 | -560.4515
2026-01-20 11:00 | -745.85 | 2.7595 | 40.4381 | 48.4627 | -218.5871
2026-01-21 12:00 | 1471.59 | 1 | 41.1517 | 48.4627 | 431.2805
2026-01-22 13:00 | 2777.29 | 1 | 41.1138 | 48.4627 | 813.9434
2026-01-23 14:00 | 2757.09 | 1 | 41.515 | 48.4627 | 808.0233
2026-01-24 15:00 | 2724.26 | 1 | 41.7989 | 48.4627 | 798.4018
2026-01-25 16:00 | 2778.08 | 1 | 41.9847 | 48.4627 | 814.1749
2026-01-26 17:00 | -181.951 | 1.4132 | 42.6832 | 48.4627 | -53.3246
2026-01-27 18:00 | -1057.92 | 4.4861 | 42.1838 | 48.4627 | -310.0457
2026-01-28 19:00 | -2239.82 | 6.6648 | 41.7184 | 48.4627 | -656.4264
2026-01-29 20:00 | -3137.28 | 6.6648 | 41.1196 | 48.4627 | -919.446
2026-01-30 21:00 | -4755.07 | 6.6648 | 40.1351 | 48.4627 | -1393.5735
2026-01-31 22:00 | -5232.31 | 6.6648 | 39.6287 | 48.4627 | -1533.4387
2026-02-01 23:00 | -6525.98 | 6.6648 | 38.7942 | 48.4627 | -1912.5759
2026-02-03 | -7425.81 | 6.6648 | 38.0921 | 48.4627 | -2176.2901
2026-02-04 01:00 | -7704.25 | 6.6648 | 37.6945 | 48.4627 | -2257.8928
2026-02-05 02:00 | -8097.22 | 6.6648 | 37.2985 | 48.4627 | -2373.0609
2026-02-06 03:00 | -8401.27 | 6.6648 | 36.9711 | 48.4627 | -2462.1692
2026-02-07 04:00 | -8517.36 | 6.6648 | 36.7401 | 48.4627 | -2496.1918
2026-02-08 05:00 | -8580.12 | 6.6648 | 36.5912 | 48.4627 | -2514.5849
2026-02-09 06:00 | -8385.18 | 6.6648 | 36.5991 | 48.4627 | -2457.4537
2026-02-10 07:00 | -6886.25 | 6.6648 | 37.3072 | 48.4627 | -2018.1607
2026-02-11 08:00 | -6142.43 | 6.6648 | 37.773 | 48.4627 | -1800.1685
2026-02-12 09:00 | -6321.18 | 6.6648 | 37.7851 | 48.4627 | -1852.555
2026-02-13 10:00 | -5813.9 | 6.6648 | 38.0523 | 48.4627 | -1703.8859
2026-02-14 11:00 | -4670.67 | 6.6648 | 38.6863 | 48.4627 | -1368.8383
2026-02-15 12:00 | -4494.81 | 6.6648 | 38.9161 | 48.4627 | -1317.2988
2026-02-16 13:00 | -4002.61 | 6.6648 | 39.2384 | 48.4627 | -1173.0492
2026-02-17 14:00 | -4391.11 | 6.6648 | 39.1152 | 48.4627 | -1286.9073
2026-02-18 15:00 | -3642.52 | 6.6648 | 39.5157 | 48.4627 | -1067.5172
2026-02-19 16:00 | -3841.25 | 6.6648 | 39.5006 | 48.4627 | -1125.7592
2026-02-20 17:00 | -2432.3 | 6.6648 | 40.2601 | 48.4627 | -712.8368
2026-02-21 18:00 | -3028.58 | 6.6648 | 40.1248 | 48.4627 | -887.5892
2026-02-22 19:00 | -3463.25 | 6.6648 | 39.9479 | 48.4627 | -1014.9784
2026-02-23 20:00 | -4055.49 | 6.6648 | 39.6436 | 48.4627 | -1188.5468
2026-02-24 21:00 | -4597.49 | 6.6648 | 39.3395 | 48.4627 | -1347.3913
2026-02-25 22:00 | -5121.89 | 6.6648 | 39.0297 | 48.4627 | -1501.0778
2026-02-26 23:00 | -5719.97 | 6.6648 | 38.6445 | 48.4627 | -1676.3577
2026-02-28 | -7535.96 | 6.6648 | 37.6258 | 48.4627 | -2208.5719
2026-03-01 01:00 | -8209.08 | 6.6648 | 37.0536 | 48.4627 | -2405.8439
2026-03-02 02:00 | -8893.2 | 6.6648 | 36.5154 | 48.4627 | -2606.3396
2026-03-03 03:00 | -9531.43 | 6.6648 | 36.0102 | 48.4627 | -2793.3864
2026-03-04 04:00 | -10027.8 | 6.6648 | 35.5698 | 48.4627 | -2938.8581
2026-03-05 05:00 | -10188.2 | 6.6648 | 35.2935 | 48.4627 | -2985.8667
2026-03-06 06:00 | -9392.97 | 6.6648 | 35.5605 | 48.4627 | -2752.8078
2026-03-07 07:00 | -8922.37 | 6.6648 | 35.7649 | 48.4627 | -2614.8885
2026-03-08 08:00 | -9732.82 | 6.6648 | 35.3371 | 48.4627 | -2852.408
2026-03-09 09:00 | -9896.29 | 6.6648 | 35.1331 | 48.4627 | -2900.3163
2026-03-10 10:00 | -9738.29 | 6.6648 | 35.1045 | 48.4627 | -2854.0111
2026-03-11 11:00 | -9849.83 | 6.6648 | 34.9786 | 48.4627 | -2886.7002
2026-03-12 12:00 | -9827.54 | 6.6648 | 34.9027 | 48.4627 | -2880.1677
2026-03-13 13:00 | -10024 | 6.6648 | 34.7104 | 48.4627 | -2937.7444
2026-03-14 14:00 | -9903.72 | 6.6648 | 34.6834 | 48.4627 | -2902.4938
2026-03-15 15:00 | -9597.2 | 6.6648 | 34.7774 | 48.4627 | -2812.6617
2026-03-16 16:00 | -7698.88 | 6.6648 | 35.7209 | 48.4627 | -2256.319
2026-03-17 17:00 | -8191.14 | 6.6648 | 35.6148 | 48.4627 | -2400.5862
2026-03-18 18:00 | -8420.32 | 6.6648 | 35.5053 | 48.4627 | -2467.7522
2026-03-19 19:00 | -8690.18 | 6.6648 | 35.3306 | 48.4627 | -2546.8404
2026-03-20 20:00 | -8663.49 | 6.6648 | 35.3127 | 48.4627 | -2539.0183
2026-03-21 21:00 | -8846.24 | 6.6648 | 35.2106 | 48.4627 | -2592.577
2026-03-22 22:00 | -8925.77 | 6.6648 | 35.1207 | 48.4627 | -2615.885
2026-03-23 23:00 | -9913.25 | 6.6648 | 34.5799 | 48.4627 | -2905.2868
2026-03-25 | -9940.09 | 6.6648 | 34.4552 | 48.4627 | -2913.1528
2026-03-26 01:00 | -9989.16 | 6.6648 | 34.3696 | 48.4627 | -2927.5338
2026-03-27 02:00 | -10014.5 | 6.6648 | 34.32 | 48.4627 | -2934.9602
2026-03-28 03:00 | -9621.62 | 6.6648 | 34.4893 | 48.4627 | -2819.8185
2026-03-29 04:00 | -9488.7 | 6.6648 | 34.5548 | 48.4627 | -2780.8635
2026-03-30 05:00 | -9088.56 | 6.6648 | 34.7757 | 48.4627 | -2663.594
2026-03-31 06:00 | -8895.39 | 6.6648 | 34.9122 | 48.4627 | -2606.9815
2026-04-01 07:00 | -8791.76 | 6.6648 | 34.9986 | 48.4627 | -2576.6105
2026-04-02 08:00 | -9620.23 | 6.6648 | 34.5989 | 48.4627 | -2819.4111
2026-04-03 09:00 | -9203.6 | 6.6648 | 34.7411 | 48.4627 | -2697.3089
2026-04-04 10:00 | -9098.65 | 6.6648 | 34.7914 | 48.4627 | -2666.5511
2026-04-05 11:00 | -8367.84 | 6.6648 | 35.1727 | 48.4627 | -2452.3718
2026-04-06 12:00 | -7868.97 | 6.6648 | 35.4899 | 48.4627 | -2306.1675
2026-04-07 13:00 | -7900.18 | 6.6648 | 35.5507 | 48.4627 | -2315.3142
2026-04-08 14:00 | -8150.08 | 6.6648 | 35.4715 | 48.4627 | -2388.5527
2026-04-09 15:00 | -7316.98 | 6.6648 | 35.8989 | 48.4627 | -2144.3952
2026-04-10 16:00 | -6901.32 | 6.6648 | 36.1949 | 48.4627 | -2022.5772
2026-04-11 17:00 | -7037.85 | 6.6648 | 36.2045 | 48.4627 | -2062.5902
2026-04-12 18:00 | -7542.81 | 6.6648 | 35.9674 | 48.4627 | -2210.5794
2026-04-13 19:00 | -8220.75 | 6.6648 | 35.59 | 48.4627 | -2409.264
2026-04-14 20:00 | -9197.8 | 6.6648 | 35.0293 | 48.4627 | -2695.6091
2026-04-15 21:00 | -9799.92 | 6.6648 | 34.5898 | 48.4627 | -2872.073
2026-04-16 22:00 | -11050.3 | 6.6648 | 33.811 | 48.4627 | -3238.5232
2026-04-17 23:00 | -11456.8 | 6.6648 | 33.3899 | 48.4627 | -3357.6566
2026-04-19 | -11545.8 | 6.6648 | 33.1713 | 48.4627 | -3383.74
2026-04-20 01:00 | -11612.7 | 6.6648 | 33.0167 | 48.4627 | -3403.3464
2026-04-21 02:00 | -11840.4 | 6.6648 | 32.8077 | 48.4627 | -3470.0787
2026-04-22 03:00 | -11575.3 | 6.6648 | 32.8375 | 48.4627 | -3392.3856
2026-04-23 04:00 | -11606.8 | 6.6648 | 32.7708 | 48.4627 | -3401.6173
2026-04-24 05:00 | -11052.4 | 6.6648 | 33.0019 | 48.4627 | -3239.1387
2026-04-25 06:00 | -10845.4 | 6.6648 | 33.1082 | 48.4627 | -3178.473
2026-04-26 07:00 | -10433.8 | 6.6648 | 33.3209 | 48.4627 | -3057.8449
2026-04-27 08:00 | -10356 | 6.6648 | 33.395 | 48.4627 | -3035.044
2026-04-28 09:00 | -9491.17 | 6.6648 | 33.8558 | 48.4627 | -2781.5873
2026-04-29 10:00 | -8699.72 | 6.6648 | 34.3596 | 48.4627 | -2549.6362
2026-04-30 11:00 | -8260.77 | 6.6648 | 34.7102 | 48.4627 | -2420.9927
2026-05-01 12:00 | -8700 | 6.6648 | 34.5918 | 48.4627 | -2549.7183
2026-05-02 13:00 | -6739.79 | 6.6648 | 35.615 | 48.4627 | -1975.2375
2026-05-03 14:00 | -6130.31 | 6.6648 | 36.1488 | 48.4627 | -1796.6165
2026-05-04 15:00 | -5207.47 | 6.6648 | 36.8119 | 48.4627 | -1526.1588
2026-05-05 16:00 | -5372.14 | 6.6648 | 36.9168 | 48.4627 | -1574.4188
2026-05-06 17:00 | -5797.48 | 6.6648 | 36.8126 | 48.4627 | -1699.0737
2026-05-07 18:00 | -6801.34 | 6.6648 | 36.364 | 48.4627 | -1993.276
2026-05-08 19:00 | -7608.41 | 6.6648 | 35.908 | 48.4627 | -2229.8049
2026-05-09 20:00 | -8630.05 | 6.6648 | 35.3089 | 48.4627 | -2529.218
2026-05-10 21:00 | -9078.85 | 6.6648 | 34.9425 | 48.4627 | -2660.7483
2026-05-11 22:00 | -10117.6 | 6.6648 | 34.2947 | 48.4627 | -2965.1759
2026-05-12 23:00 | -10196.5 | 6.6648 | 34.0885 | 48.4627 | -2988.2992
2026-05-14 | -10281.3 | 6.6648 | 33.9482 | 48.4627 | -3013.1516
2026-05-15 01:00 | -10548.1 | 6.6648 | 33.7335 | 48.4627 | -3091.343
2026-05-16 02:00 | -10565.9 | 6.6648 | 33.6389 | 48.4627 | -3096.5596
2026-05-17 03:00 | -10462.7 | 6.6648 | 33.6142 | 48.4627 | -3066.3147
2026-05-18 04:00 | -10475.7 | 6.6648 | 33.5697 | 48.4627 | -3070.1246
2026-05-19 05:00 | -9835.3 | 6.6648 | 33.8554 | 48.4627 | -2882.4419
2026-05-20 06:00 | -9577.39 | 6.6648 | 34.0149 | 48.4627 | -2806.8559
2026-05-21 07:00 | -9127.78 | 6.6648 | 34.2783 | 48.4627 | -2675.0883
2026-05-22 08:00 | -9128.39 | 6.6648 | 34.3363 | 48.4627 | -2675.267
2026-05-23 09:00 | -8948.38 | 6.6648 | 34.4593 | 48.4627 | -2622.5113
2026-05-24 10:00 | -8197.81 | 6.6648 | 34.885 | 48.4627 | -2402.5409
2026-05-25 11:00 | -6424.97 | 6.6648 | 35.8859 | 48.4627 | -1882.9728
2026-05-26 12:00 | -6053.07 | 6.6648 | 36.3043 | 48.4627 | -1773.9797
2026-05-27 13:00 | -5792.88 | 6.6648 | 36.5955 | 48.4627 | -1697.7255
2026-05-28 14:00 | -5472.35 | 6.6648 | 36.8816 | 48.4627 | -1603.7875
2026-05-29 15:00 | -4026.26 | 6.6648 | 37.7457 | 48.4627 | -1179.9803
2026-05-30 16:00 | -4133.96 | 6.6648 | 37.9259 | 48.4627 | -1211.5441
2026-05-31 17:00 | -4586.94 | 6.6648 | 37.8179 | 48.4627 | -1344.2994
2026-06-01 18:00 | -6100.17 | 6.6648 | 37.0903 | 48.4627 | -1787.7833
2026-06-02 19:00 | -6907.02 | 6.6648 | 36.5931 | 48.4627 | -2024.2477
2026-06-03 20:00 | -7921.55 | 6.6648 | 35.9848 | 48.4627 | -2321.5771
2026-06-04 21:00 | -8439.13 | 6.6648 | 35.5813 | 48.4627 | -2473.2649
2026-06-05 22:00 | -9886.61 | 6.6648 | 34.7156 | 48.4627 | -2897.4794
2026-06-06 23:00 | -9912.5 | 6.6648 | 34.4759 | 48.4627 | -2905.067
2026-06-08 | -10225.2 | 6.6648 | 34.1845 | 48.4627 | -2996.7103
2026-06-09 01:00 | -10363.7 | 6.6648 | 34.0019 | 48.4627 | -3037.3006
2026-06-10 02:00 | -10702.8 | 6.6648 | 33.7317 | 48.4627 | -3136.681
2026-06-11 03:00 | -10956.5 | 6.6648 | 33.4792 | 48.4627 | -3211.0332
2026-06-12 04:00 | -10739.8 | 6.6648 | 33.4874 | 48.4627 | -3147.5247
2026-06-13 05:00 | -10371.8 | 6.6648 | 33.6156 | 48.4627 | -3039.6745
2026-06-14 06:00 | -10117.2 | 6.6648 | 33.7364 | 48.4627 | -2965.0586
2026-06-15 07:00 | -8626.29 | 6.6648 | 34.499 | 48.4627 | -2528.116
2026-06-16 08:00 | -7855.98 | 6.6648 | 35.0331 | 48.4627 | -2302.3605
2026-06-17 09:00 | -6679.2 | 6.6648 | 35.7881 | 48.4627 | -1957.4803
2026-06-18 10:00 | -5376.67 | 6.6648 | 36.6565 | 48.4627 | -1575.7464
2026-06-19 11:00 | -4094.44 | 6.6648 | 37.5593 | 48.4627 | -1199.9619
2026-06-20 12:00 | -3283.85 | 6.6648 | 38.2607 | 48.4627 | -962.4014
2026-06-21 13:00 | -3491.7 | 6.6648 | 38.408 | 48.4627 | -1023.3163
2026-06-22 14:00 | -3066.41 | 6.6648 | 38.7802 | 48.4627 | -898.6761
2026-06-23 15:00 | -2479.15 | 6.6648 | 39.2415 | 48.4627 | -726.5671
2026-06-24 16:00 | -2880.32 | 6.6648 | 39.2196 | 48.4627 | -844.1385
2026-06-25 17:00 | -3598.44 | 6.6648 | 38.941 | 48.4627 | -1054.5987
2026-06-26 18:00 | -4889.69 | 6.6648 | 38.2945 | 48.4627 | -1433.0267
2026-06-27 19:00 | -5691.67 | 6.6648 | 37.8068 | 48.4627 | -1668.0638
2026-06-28 20:00 | -6657.27 | 6.6648 | 37.2197 | 48.4627 | -1951.0532
2026-06-29 21:00 | -7735.36 | 6.6648 | 36.5298 | 48.4627 | -2267.0102
2026-06-30 22:00 | -8535.13 | 6.6648 | 35.9396 | 48.4627 | -2501.3997
2026-07-01 23:00 | -8898.38 | 6.6648 | 35.5657 | 48.4627 | -2607.8577
2026-07-03 | -9301.85 | 6.6648 | 35.2109 | 48.4627 | -2726.1031
2026-07-04 01:00 | -9623.47 | 6.6648 | 34.9097 | 48.4627 | -2820.3607
2026-07-05 02:00 | -9701.29 | 6.6648 | 34.7415 | 48.4627 | -2843.1674
2026-07-06 03:00 | -9692.43 | 6.6648 | 34.6469 | 48.4627 | -2840.5708
2026-07-07 04:00 | -9770.77 | 6.6648 | 34.5351 | 48.4627 | -2863.53
2026-07-08 05:00 | -9422.47 | 6.6648 | 34.6445 | 48.4627 | -2761.4534
2026-07-09 06:00 | -9249.74 | 6.6648 | 34.7159 | 48.4627 | -2710.8312
2026-07-10 07:00 | -8266.76 | 6.6648 | 35.212 | 48.4627 | -2422.7482
2026-07-11 08:00 | -7899.17 | 6.6648 | 35.4804 | 48.4627 | -2315.0182
2026-07-12 09:00 | -6768.05 | 6.6648 | 36.133 | 48.4627 | -1983.5197
2026-07-13 10:00 | -6245.88 | 6.6648 | 36.5449 | 48.4627 | -1830.4867
2026-07-14 11:00 | -4892.56 | 6.6648 | 37.364 | 48.4627 | -1433.8678
2026-07-15 12:00 | -4151.87 | 6.6648 | 37.9482 | 48.4627 | -1216.793
2026-07-16 13:00 | -4132.69 | 6.6648 | 38.1551 | 48.4627 | -1211.1719
2026-07-17 14:00 | -3517.85 | 6.6648 | 38.5971 | 48.4627 | -1030.9801
2026-07-18 15:00 | -2903.21 | 6.6648 | 39.0556 | 48.4627 | -850.8469
2026-07-19 16:00 | -2834.24 | 6.6648 | 39.2632 | 48.4627 | -830.6337
2026-07-20 17:00 | -3384.46 | 6.6648 | 39.1005 | 48.4627 | -991.8873
2026-07-21 18:00 | -4204.79 | 6.6648 | 38.7233 | 48.4627 | -1232.3023
2026-07-22 19:00 | -4728.97 | 6.6648 | 38.4355 | 48.4627 | -1385.9243
2026-07-23 20:00 | -5621.06 | 6.6648 | 37.9497 | 48.4627 | -1647.3701
2026-07-24 21:00 | -5999.41 | 6.6648 | 37.6672 | 48.4627 | -1758.2535
2026-07-25 22:00 | -6616.97 | 6.6648 | 37.2782 | 48.4627 | -1939.2425
2026-07-26 23:00 | -7241.75 | 6.6648 | 36.863 | 48.4627 | -2122.3474
2026-07-28 | -7347.59 | 6.6648 | 36.6966 | 48.4627 | -2153.3661
2026-07-29 01:00 | -7375.69 | 6.6648 | 36.6105 | 48.4627 | -2161.6014
2026-07-30 02:00 | -7441.24 | 6.6648 | 36.5341 | 48.4627 | -2180.8122
2026-07-31 03:00 | -7413.24 | 6.6648 | 36.5045 | 48.4627 | -2172.6062
2026-08-01 04:00 | -7357.54 | 6.6648 | 36.5048 | 48.4627 | -2156.2821
2026-08-02 05:00 | -7046.6 | 6.6648 | 36.6536 | 48.4627 | -2065.1546
2026-08-03 06:00 | -5941.95 | 6.6648 | 37.2425 | 48.4627 | -1741.4136
2026-08-04 07:00 | -5280.81 | 6.6648 | 37.6965 | 48.4627 | -1547.6526
2026-08-05 08:00 | -5975.91 | 6.6648 | 37.4728 | 48.4627 | -1751.3663
2026-08-06 09:00 | -5887.86 | 6.6648 | 37.5202 | 48.4627 | -1725.5614
2026-08-07 10:00 | -5756.35 | 6.6648 | 37.6081 | 48.4627 | -1687.0197
2026-08-08 11:00 | -5416.28 | 6.6648 | 37.8196 | 48.4627 | -1587.355
2026-08-09 12:00 | -4610.64 | 6.6648 | 38.2721 | 48.4627 | -1351.2452
2026-08-10 13:00 | -4443.68 | 6.6648 | 38.4473 | 48.4627 | -1302.3141
2026-08-11 14:00 | -4015.01 | 6.6648 | 38.7387 | 48.4627 | -1176.6833
2026-08-12 15:00 | -3754.22 | 6.6648 | 38.9537 | 48.4627 | -1100.2533
2026-08-13 16:00 | -2243.11 | 6.6648 | 39.8092 | 48.4627 | -657.3906
2026-08-14 17:00 | -2749.71 | 6.6648 | 39.7594 | 48.4627 | -805.8605
2026-08-15 18:00 | -3190.7 | 6.6648 | 39.6105 | 48.4627 | -935.1019
2026-08-16 19:00 | -3466.59 | 6.6648 | 39.4837 | 48.4627 | -1015.9572
2026-08-17 20:00 | -4031.88 | 6.6648 | 39.2186 | 48.4627 | -1181.6274
2026-08-18 21:00 | -4088.36 | 6.6648 | 39.1803 | 48.4627 | -1198.18
2026-08-19 22:00 | -4387.94 | 6.6648 | 39.0225 | 48.4627 | -1285.9783
2026-08-20 23:00 | -5970.06 | 6.6648 | 38.2058 | 48.4627 | -1749.6519
2026-08-22 | -6272.21 | 6.6648 | 37.9028 | 48.4627 | -1838.2033
2026-08-23 01:00 | -6503.65 | 6.6648 | 37.6837 | 48.4627 | -1906.0317
2026-08-24 02:00 | -6533.38 | 6.6648 | 37.6029 | 48.4627 | -1914.7447
2026-08-25 03:00 | -6727.19 | 6.6648 | 37.451 | 48.4627 | -1971.5448
2026-08-26 04:00 | -6803.76 | 6.6648 | 37.3394 | 48.4627 | -1993.9852
2026-08-27 05:00 | -7163.41 | 6.6648 | 37.1116 | 48.4627 | -2099.3882
2026-08-28 06:00 | -6216.01 | 6.6648 | 37.5274 | 48.4627 | -1821.7327
2026-08-29 07:00 | -5594.77 | 6.6648 | 37.8875 | 48.4627 | -1639.6652
2026-08-30 08:00 | -6523.95 | 6.6648 | 37.492 | 48.4627 | -1911.981
2026-08-31 09:00 | -6398.06 | 6.6648 | 37.4948 | 48.4627 | -1875.0863
2026-09-01 10:00 | -6127.31 | 6.6648 | 37.6088 | 48.4627 | -1795.7373
2026-09-02 11:00 | -5088.25 | 6.6648 | 38.1723 | 48.4627 | -1491.2189
2026-09-03 12:00 | -4312.25 | 6.6648 | 38.6706 | 48.4627 | -1263.7957
2026-09-04 13:00 | -3539.34 | 6.6648 | 39.1842 | 48.4627 | -1037.2782
2026-09-05 14:00 | -2995.72 | 6.6648 | 39.6112 | 48.4627 | -877.9589
2026-09-06 15:00 | -2742.21 | 6.6648 | 39.8879 | 48.4627 | -803.6624
2026-09-07 16:00 | -1271.9 | 4.8058 | 40.5072 | 48.4627 | -372.7571
2026-09-08 17:00 | -1968.5 | 6.6648 | 40.6338 | 48.4627 | -576.9104
2026-09-09 18:00 | -3153.25 | 6.6648 | 40.1102 | 48.4627 | -924.1264
2026-09-10 19:00 | -4242.01 | 6.6648 | 39.4968 | 48.4627 | -1243.2104
2026-09-11 20:00 | -4836.04 | 6.6648 | 39.0986 | 48.4627 | -1417.3034
2026-09-12 21:00 | -5505.34 | 6.6648 | 38.6743 | 48.4627 | -1613.4559
2026-09-13 22:00 | -5998.07 | 6.6648 | 38.3037 | 48.4627 | -1757.8608
2026-09-14 23:00 | -7461.13 | 6.6648 | 37.4417 | 48.4627 | -2186.6414
2026-09-16 | -8060.31 | 6.6648 | 36.9287 | 48.4627 | -2362.2437
2026-09-17 01:00 | -8388.01 | 6.6648 | 36.5815 | 48.4627 | -2458.2831
2026-09-18 02:00 | -8693.57 | 6.6648 | 36.2805 | 48.4627 | -2547.8339
2026-09-19 03:00 | -8611.71 | 6.6648 | 36.1862 | 48.4627 | -2523.8431
2026-09-20 04:00 | -8732.31 | 6.6648 | 36.0136 | 48.4627 | -2559.1874
2026-09-21 05:00 | -8382.43 | 6.6648 | 36.1043 | 48.4627 | -2456.6477
2026-09-22 06:00 | -7952.58 | 6.6648 | 36.2864 | 48.4627 | -2330.6711
2026-09-23 07:00 | -6708.95 | 6.6648 | 36.9244 | 48.4627 | -1966.1992
2026-09-24 08:00 | -5857.18 | 6.6648 | 37.4724 | 48.4627 | -1716.57
2026-09-25 09:00 | -3872.09 | 6.6648 | 38.6233 | 48.4627 | -1134.7976
2026-09-26 10:00 | -2596.33 | 6.6648 | 39.5431 | 48.4627 | -760.9092
2026-09-27 11:00 | -991.937 | 3.7331 | 40.2533 | 48.4627 | -290.708
2026-09-28 12:00 | -560.173 | 2.4181 | 40.7069 | 48.4627 | -164.1705
2026-09-29 13:00 | -106.14 | 0.86596 | 41.3409 | 48.4627 | -31.1066
2026-09-30 14:00 | 88.0989 | 1 | 41.9637 | 48.4627 | 25.8192
2026-10-01 15:00 | 2688.48 | 1 | 41.2682 | 48.4627 | 787.9157
2026-10-02 16:00 | 0 | 0 | 42.5787 | 48.4627 | 0
2026-10-03 17:00 | -354.104 | 1.7148 | 41.8734 | 48.4627 | -103.7776
2026-10-04 18:00 | -1289.35 | 5.3516 | 41.7629 | 48.4627 | -377.8712
2026-10-05 19:00 | -2122.76 | 6.6648 | 41.4828 | 48.4627 | -622.1195
2026-10-06 20:00 | -3292.57 | 6.6648 | 40.829 | 48.4627 | -964.957
2026-10-07 21:00 | -3970.13 | 6.6648 | 40.3136 | 48.4627 | -1163.5302
2026-10-08 22:00 | -4918.21 | 6.6648 | 39.6989 | 48.4627 | -1441.3851
2026-10-09 23:00 | -5336 | 6.6648 | 39.3209 | 48.4627 | -1563.8272
2026-10-11 | -5401.8 | 6.6648 | 39.153 | 48.4627 | -1583.1113
2026-10-12 01:00 | -5378.41 | 6.6648 | 39.0763 | 48.4627 | -1576.2564
2026-10-13 02:00 | -5536.51 | 6.6648 | 38.9419 | 48.4627 | -1622.5909
2026-10-14 03:00 | -5358.46 | 6.6648 | 38.954 | 48.4627 | -1570.4096
2026-10-15 04:00 | -5411.73 | 6.6648 | 38.9096 | 48.4627 | -1586.0215
2026-10-16 05:00 | -5232.42 | 6.6648 | 38.983 | 48.4627 | -1533.4709
2026-10-17 06:00 | -5215.31 | 6.6648 | 38.9943 | 48.4627 | -1528.4565
2026-10-18 07:00 | -5041.83 | 6.6648 | 39.0797 | 48.4627 | -1477.6145
2026-10-19 08:00 | -5556.31 | 6.6648 | 38.836 | 48.4627 | -1628.3937
2026-10-20 09:00 | -5569.66 | 6.6648 | 38.7826 | 48.4627 | -1632.3062
2026-10-21 10:00 | -5258.64 | 6.6648 | 38.9118 | 48.4627 | -1541.1553
2026-10-22 11:00 | -4227.12 | 6.6648 | 39.4433 | 48.4627 | -1238.8466
2026-10-23 12:00 | -2123.14 | 6.6648 | 40.6069 | 48.4627 | -622.2309
2026-10-24 13:00 | -1048.1 | 3.8876 | 41.011 | 48.4627 | -307.1678
2026-10-25 14:00 | 0 | 0 | 42.1684 | 48.4627 | 0
2026-10-26 15:00 | 2577.56 | 1 | 41.5247 | 48.4627 | 755.4083
2026-10-27 16:00 | -163.155 | 1.3292 | 42.4033 | 48.4627 | -47.816
2026-10-28 17:00 | -943.445 | 4.0796 | 42.0412 | 48.4627 | -276.4964
2026-10-29 18:00 | -2284.23 | 6.6648 | 41.6143 | 48.4627 | -669.4417
2026-10-30 19:00 | -3083.03 | 6.6648 | 41.1136 | 48.4627 | -903.5469
2026-10-31 20:00 | -4220.96 | 6.6648 | 40.4298 | 48.4627 | -1237.0413
2026-11-01 21:00 | -4644.51 | 6.6648 | 40.0272 | 48.4627 | -1361.1715
2026-11-02 22:00 | -5498.27 | 6.6648 | 39.4775 | 48.4627 | -1611.3839
2026-11-03 23:00 | -5438.08 | 6.6648 | 39.3664 | 48.4627 | -1593.7439
2026-11-05 | -5577.09 | 6.6648 | 39.2123 | 48.4627 | -1634.4837
2026-11-06 01:00 | -5309.19 | 6.6648 | 39.2758 | 48.4627 | -1555.97
2026-11-07 02:00 | -5885.56 | 6.6648 | 38.9497 | 48.4627 | -1724.8874
2026-11-08 03:00 | -5981.32 | 6.6648 | 38.7898 | 48.4627 | -1752.9519
2026-11-09 04:00 | -5828.01 | 6.6648 | 38.802 | 48.4627 | -1708.0211
2026-11-10 05:00 | -5527.17 | 6.6648 | 38.9264 | 48.4627 | -1619.8536
2026-11-11 06:00 | -5235.2 | 6.6648 | 39.082 | 48.4627 | -1534.2857
2026-11-12 07:00 | -4986.78 | 6.6648 | 39.2262 | 48.4627 | -1461.481
2026-11-13 08:00 | -5710.44 | 6.6648 | 38.8981 | 48.4627 | -1673.5648
2026-11-14 09:00 | -5204.78 | 6.6648 | 39.1093 | 48.4627 | -1525.3704
2026-11-15 10:00 | -5594.16 | 6.6648 | 38.9366 | 48.4627 | -1639.4865
2026-11-16 11:00 | -5493.74 | 6.6648 | 38.9585 | 48.4627 | -1610.0563
2026-11-17 12:00 | -5565.1 | 6.6648 | 38.8922 | 48.4627 | -1630.9698
2026-11-18 13:00 | -5766.5 | 6.6648 | 38.7451 | 48.4627 | -1689.9943
2026-11-19 14:00 | -5439.31 | 6.6648 | 38.8596 | 48.4627 | -1594.1044
2026-11-20 15:00 | -4606.5 | 6.6648 | 39.251 | 48.4627 | -1350.0319
2026-11-21 16:00 | -4365.95 | 6.6648 | 39.4337 | 48.4627 | -1279.5336
2026-11-22 17:00 | -4168.26 | 6.6648 | 39.5762 | 48.4627 | -1221.5964
2026-11-23 18:00 | -4484.19 | 6.6648 | 39.453 | 48.4627 | -1314.1864
2026-11-24 19:00 | -4729.08 | 6.6648 | 39.328 | 48.4627 | -1385.9565
2026-11-25 20:00 | -5531.48 | 6.6648 | 38.9111 | 48.4627 | -1621.1168
2026-11-26 21:00 | -5771.4 | 6.6648 | 38.7063 | 48.4627 | -1691.4304
2026-11-27 22:00 | -6294.25 | 6.6648 | 38.3774 | 48.4627 | -1844.6626
2026-11-28 23:00 | -6744.31 | 6.6648 | 38.0627 | 48.4627 | -1976.5621
2026-11-30 | -6706.47 | 6.6648 | 37.9878 | 48.4627 | -1965.4723
2026-12-01 01:00 | -6872.93 | 6.6648 | 37.8488 | 48.4627 | -2014.2569
2026-12-02 02:00 | -6830.44 | 6.6648 | 37.8223 | 48.4627 | -2001.8044
2026-12-03 03:00 | -6655.29 | 6.6648 | 37.8716 | 48.4627 | -1950.473
2026-12-04 04:00 | -6482.85 | 6.6648 | 37.9455 | 48.4627 | -1899.9358
2026-12-05 05:00 | -6148.85 | 6.6648 | 38.1148 | 48.4627 | -1802.05
2026-12-06 06:00 | -5575.42 | 6.6648 | 38.4276 | 48.4627 | -1633.9943
2026-12-07 07:00 | -4579 | 6.6648 | 38.9971 | 48.4627 | -1341.9724
2026-12-08 08:00 | -3926.3 | 6.6648 | 39.4667 | 48.4627 | -1150.6849
2026-12-09 09:00 | -1870.46 | 6.6648 | 40.6588 | 48.4627 | -548.1777
2026-12-10 10:00 | -922.743 | 3.4054 | 40.9842 | 48.4627 | -270.4293
2026-12-11 11:00 | 2049.66 | 1 | 41.489 | 48.4627 | 600.696
2026-12-12 12:00 | 3041.31 | 1 | 41.6169 | 48.4627 | 891.32
2026-12-13 13:00 | 3050.92 | 1 | 56.7939 | 48.4627 | 894.1364
2026-12-14 14:00 | 3039.3 | 1 | 53.9111 | 48.4627 | 890.7309
2026-12-15 15:00 | 4015.12 | 1.3042 | 53.9555 | 48.4627 | 1176.7155
2026-12-16 16:00 | 3998.43 | 1.3164 | 54.1007 | 48.4627 | 1171.8242
2026-12-17 17:00 | 3134.57 | 1.0306 | 54.3114 | 48.4627 | 918.6518
2026-12-18 18:00 | 2979.59 | 1 | 43.0637 | 48.4627 | 873.2316
2026-12-19 19:00 | -204.687 | 1.4639 | 43.6973 | 48.4627 | -59.9878
2026-12-20 20:00 | -1574.35 | 6.307 | 43.1327 | 48.4627 | -461.3964
2026-12-21 21:00 | -2459.06 | 6.6648 | 42.5041 | 48.4627 | -720.6793
2026-12-22 22:00 | -3743.6 | 6.6648 | 41.6703 | 48.4627 | -1097.1409
2026-12-23 23:00 | -4125.54 | 6.6648 | 41.2339 | 48.4627 | -1209.0764
2026-12-25 | -4808.02 | 6.6648 | 40.6766 | 48.4627 | -1409.0916
2026-12-26 01:00 | -5102.99 | 6.6648 | 40.3495 | 48.4627 | -1495.5387
2026-12-27 02:00 | -5443.32 | 6.6648 | 40.0311 | 48.4627 | -1595.2796
2026-12-28 03:00 | -5419.84 | 6.6648 | 39.9003 | 48.4627 | -1588.3983
2026-12-29 04:00 | -5471.52 | 6.6648 | 39.7751 | 48.4627 | -1603.5442
2026-12-30 05:00 | -5142.89 | 6.6648 | 39.8572 | 48.4627 | -1507.2323
2026-12-31 06:00 | -4825.65 | 6.6648 | 39.9754 | 48.4627 | -1414.2584
2027-01-01 07:00 | -3836.51 | 6.6648 | 40.4802 | 48.4627 | -1124.3701
2027-01-02 08:00 | -3066.61 | 6.6648 | 40.9631 | 48.4627 | -898.7347
2027-01-03 09:00 | -1525.36 | 5.6886 | 41.727 | 48.4627 | -447.0389
2027-01-04 10:00 | 0 | 0 | 42.8508 | 48.4627 | 0
2027-01-05 11:00 | 2579.69 | 1 | 42.2347 | 48.4627 | 756.0325
2027-01-06 12:00 | 3029.76 | 1 | 58.7757 | 48.4627 | 887.935
2027-01-07 13:00 | 2773.34 | 1 | 42.8689 | 48.4627 | 812.7857
2027-01-08 14:00 | -456.124 | 2.4059 | 43.3559 | 48.4627 | -133.6767
2027-01-09 15:00 | -344.152 | 1.7121 | 43.1469 | 48.4627 | -100.861
2027-01-10 16:00 | -419.353 | 2.0683 | 43.0974 | 48.4627 | -122.9002
2027-01-11 17:00 | -748.905 | 3.2288 | 42.9818 | 48.4627 | -219.4824
2027-01-12 18:00 | -1242.82 | 4.9108 | 42.8551 | 48.4627 | -364.2346
2027-01-13 19:00 | -1769.16 | 6.6648 | 42.7363 | 48.4627 | -518.4896
2027-01-14 20:00 | -2881.06 | 6.6648 | 42.1242 | 48.4627 | -844.3553
2027-01-15 21:00 | -3260.48 | 6.6648 | 41.8011 | 48.4627 | -955.5524
2027-01-16 22:00 | -4137.83 | 6.6648 | 41.242 | 48.4627 | -1212.6783
2027-01-17 23:00 | -4765.2 | 6.6648 | 40.7546 | 48.4627 | -1396.5423
2027-01-19 | -4910.43 | 6.6648 | 40.5044 | 48.4627 | -1439.105
2027-01-20 01:00 | -4993.34 | 6.6648 | 40.3316 | 48.4627 | -1463.4035
2027-01-21 02:00 | -5071.72 | 6.6648 | 40.2206 | 48.4627 | -1486.3744
2027-01-22 03:00 | -5078.77 | 6.6648 | 40.15 | 48.4627 | -1488.4406
2027-01-23 04:00 | -5331.21 | 6.6648 | 39.9736 | 48.4627 | -1562.4234
2027-01-24 05:00 | -5168.12 | 6.6648 | 39.9972 | 48.4627 | -1514.6265
2027-01-25 06:00 | -4097.35 | 6.6648 | 40.5146 | 48.4627 | -1200.8147
2027-01-26 07:00 | -3342.29 | 6.6648 | 40.9743 | 48.4627 | -979.5285
2027-01-27 08:00 | -3875.35 | 6.6648 | 40.8085 | 48.4627 | -1135.753
2027-01-28 09:00 | -2640.62 | 6.6648 | 41.4265 | 48.4627 | -773.8893
2027-01-29 10:00 | -1084.56 | 3.9812 | 41.9604 | 48.4627 | -317.8532
2027-01-30 11:00 | 0 | 1 | 43.1 | 48.4627 | 0
2027-01-31 12:00 | 2995.8 | 1 | 42.2824 | 48.4627 | 877.9823
2027-02-01 13:00 | 2938.06 | 1 | 54.1239 | 48.4627 | 861.0604
2027-02-02 14:00 | 3510.46 | 1.1787 | 54.0576 | 48.4627 | 1028.8143
2027-02-03 15:00 | 3495.25 | 1.1412 | 54.572 | 48.4627 | 1024.3567
2027-02-04 16:00 | 5415.01 | 1.7688 | 54.7473 | 48.4627 | 1586.9828
2027-02-05 17:00 | 3402.12 | 1.1314 | 54.9094 | 48.4627 | 997.0629
2027-02-06 18:00 | 3078.14 | 1 | 43.6913 | 48.4627 | 902.1138
2027-02-07 19:00 | 2946.97 | 1 | 43.766 | 48.4627 | 863.6717
2027-02-08 20:00 | -27.2384 | 0.83099 | 44.7366 | 48.4627 | -7.9828
2027-02-09 21:00 | -501.381 | 2.431 | 43.9418 | 48.4627 | -146.9403
2027-02-10 22:00 | -888.549 | 3.6588 | 43.6538 | 48.4627 | -260.408
2027-02-11 23:00 | -2391.42 | 6.6648 | 43.1801 | 48.4627 | -700.856
2027-02-13 | -3142.14 | 6.6648 | 42.5797 | 48.4627 | -920.8703
2027-02-14 01:00 | -3768.83 | 6.6648 | 42.0428 | 48.4627 | -1104.535
2027-02-15 02:00 | -3918.46 | 6.6648 | 41.8008 | 48.4627 | -1148.3873
2027-02-16 03:00 | -4159.27 | 6.6648 | 41.5498 | 48.4627 | -1218.9617
2027-02-17 04:00 | -3883.9 | 6.6648 | 41.5516 | 48.4627 | -1138.2587
2027-02-18 05:00 | -3884.39 | 6.6648 | 41.4924 | 48.4627 | -1138.4023
2027-02-19 06:00 | -2755.03 | 6.6648 | 42.0129 | 48.4627 | -807.4196
2027-02-20 07:00 | -1915.31 | 6.6648 | 42.495 | 48.4627 | -561.322
2027-02-21 08:00 | -1923.28 | 6.6648 | 42.6088 | 48.4627 | -563.6577
2027-02-22 09:00 | -695.226 | 2.4806 | 42.6889 | 48.4627 | -203.7506
2027-02-23 10:00 | 2046.22 | 1 | 54.4382 | 48.4627 | 599.6879
2027-02-24 11:00 | 3308.33 | 1.142 | 53.9551 | 48.4627 | 969.5758
2027-02-25 12:00 | 5293.25 | 1.6955 | 55.034 | 48.4627 | 1551.2984
2027-02-26 13:00 | 6352.57 | 2.1154 | 55.0117 | 48.4627 | 1861.7545
2027-02-27 14:00 | 7432.55 | 2.4389 | 55.5432 | 48.4627 | 2178.2654
2027-02-28 15:00 | 7649.87 | 2.6324 | 55.44 | 48.4627 | 2241.9556
2027-03-01 16:00 | 9635.88 | 3.2277 | 55.9785 | 48.4627 | 2823.9977
2027-03-02 17:00 | 8430.38 | 2.6922 | 56.8935 | 48.4627 | 2470.7005
2027-03-03 18:00 | 6426.07 | 2.0351 | 57.1624 | 48.4627 | 1883.2952
2027-03-04 19:00 | 5299.82 | 1.6315 | 57.4324 | 48.4627 | 1553.2239
2027-03-05 20:00 | 4186.76 | 1.3092 | 57.2228 | 48.4627 | 1227.0182
2027-03-06 21:00 | 3119.58 | 1.0033 | 56.8617 | 48.4627 | 914.2586
2027-03-07 22:00 | 3130.63 | 1 | 61.0327 | 48.4627 | 917.4971
2027-03-08 23:00 | 0 | 0 | 46.1411 | 48.4627 | 0
2027-03-10 | -283.305 | 1.5334 | 45.1976 | 48.4627 | -83.0285
2027-03-11 01:00 | -496.755 | 2.3096 | 44.8914 | 48.4627 | -145.5845
2027-03-12 02:00 | -710.558 | 2.984 | 44.6879 | 48.4627 | -208.244
2027-03-13 03:00 | -797.081 | 3.2191 | 44.5416 | 48.4627 | -233.6014
2027-03-14 04:00 | -914.31 | 3.6167 | 44.3985 | 48.4627 | -267.9578
2027-03-15 05:00 | -665.231 | 2.6823 | 44.3464 | 48.4627 | -194.96
2027-03-16 06:00 | -447.812 | 2.0183 | 44.4114 | 48.4627 | -131.2407
2027-03-17 07:00 | 199.842 | 1 | 45.0943 | 48.4627 | 58.5679
2027-03-18 08:00 | 116.671 | 1 | 45.1804 | 48.4627 | 34.1929
2027-03-19 09:00 | 3091.25 | 1 | 44.1844 | 48.4627 | 905.9559
2027-03-20 10:00 | 3707.09 | 1.1737 | 56.2517 | 48.4627 | 1086.4408
2027-03-21 11:00 | 5054.56 | 1.6108 | 56.3722 | 48.4627 | 1481.3453
2027-03-22 12:00 | 5088.31 | 1.6047 | 56.7342 | 48.4627 | 1491.2365
2027-03-23 13:00 | 5270.87 | 1.6743 | 56.8275 | 48.4627 | 1544.7395
2027-03-24 14:00 | 5114.86 | 1.6387 | 56.889 | 48.4627 | 1499.0175
2027-03-25 15:00 | 6229.1 | 2.0713 | 56.5805 | 48.4627 | 1825.569
2027-03-26 16:00 | 7560.52 | 2.5482 | 56.6099 | 48.4627 | 2215.7697
2027-03-27 17:00 | 7257.76 | 2.3293 | 57.3557 | 48.4627 | 2127.0395
2027-03-28 18:00 | 6031.89 | 1.8599 | 57.9252 | 48.4627 | 1767.7725
2027-03-29 19:00 | 5103.04 | 1.5292 | 58.2422 | 48.4627 | 1495.5534
2027-03-30 20:00 | 3070.4 | 1 | 60.8288 | 48.4627 | 899.8454
2027-03-31 21:00 | 2741.35 | 1 | 45.8107 | 48.4627 | 803.4104
2027-04-01 22:00 | -447.667 | 2.2593 | 45.9423 | 48.4627 | -131.1982
2027-04-02 23:00 | -1304.52 | 5.0512 | 45.3652 | 48.4627 | -382.3171
2027-04-04 | -1818.1 | 6.5876 | 45.0093 | 48.4627 | -532.8325
2027-04-05 01:00 | -2385.48 | 6.6648 | 44.5145 | 48.4627 | -699.1152
2027-04-06 02:00 | -2807.32 | 6.6648 | 44.1055 | 48.4627 | -822.7443
2027-04-07 03:00 | -3314.63 | 6.6648 | 43.6444 | 48.4627 | -971.4222
2027-04-08 04:00 | -3515.32 | 6.6648 | 43.3621 | 48.4627 | -1030.2386
2027-04-09 05:00 | -3375.32 | 6.6648 | 43.2799 | 48.4627 | -989.2086
2027-04-10 06:00 | -3145.24 | 6.6648 | 43.2924 | 48.4627 | -921.7789
2027-04-11 07:00 | -2636.27 | 6.6648 | 43.4795 | 48.4627 | -772.6145
2027-04-12 08:00 | -2254.78 | 6.6648 | 43.6615 | 48.4627 | -660.8108
2027-04-13 09:00 | -1313 | 4.6828 | 43.8496 | 48.4627 | -384.8023
2027-04-14 10:00 | -251.512 | 1.0864 | 44.0897 | 48.4627 | -73.7109
2027-04-15 11:00 | 2750.11 | 1 | 44.0647 | 48.4627 | 805.9777
2027-04-16 12:00 | 2960.44 | 1 | 59.2083 | 48.4627 | 867.6193
2027-04-17 13:00 | 2857.63 | 1 | 56.4373 | 48.4627 | 837.4887
2027-04-18 14:00 | 3669.16 | 1.2336 | 55.7478 | 48.4627 | 1075.3246
2027-04-19 15:00 | 4775.67 | 1.6384 | 55.7266 | 48.4627 | 1399.6107
2027-04-20 16:00 | 5192.69 | 1.6839 | 56.5313 | 48.4627 | 1521.8272
2027-04-21 17:00 | 4371.61 | 1.4931 | 56.1671 | 48.4627 | 1281.1924
2027-04-22 18:00 | 2872.13 | 1 | 59.3856 | 48.4627 | 841.7382
2027-04-23 19:00 | 2884.67 | 1 | 45.2414 | 48.4627 | 845.4133
2027-04-24 20:00 | -538.062 | 2.5949 | 45.5311 | 48.4627 | -157.6904
2027-04-25 21:00 | -1236.42 | 4.7961 | 45.045 | 48.4627 | -362.3589
2027-04-26 22:00 | -2419.33 | 6.6648 | 44.4424 | 48.4627 | -709.0356
2027-04-27 23:00 | -2841.13 | 6.6648 | 43.9778 | 48.4627 | -832.653
2027-04-29 | -3274.79 | 6.6648 | 43.5569 | 48.4627 | -959.7462
2027-04-30 01:00 | -3525.83 | 6.6648 | 43.2363 | 48.4627 | -1033.3188
2027-05-01 02:00 | -4042.24 | 6.6648 | 42.8353 | 48.4627 | -1184.6636
2027-05-02 03:00 | -3643.95 | 6.6648 | 42.8752 | 48.4627 | -1067.9363
2027-05-03 04:00 | -3730.87 | 6.6648 | 42.7515 | 48.4627 | -1093.4101
2027-05-04 05:00 | -3156.87 | 6.6648 | 42.9647 | 48.4627 | -925.1873
2027-05-05 06:00 | -2712.78 | 6.6648 | 43.1785 | 48.4627 | -795.0373
2027-05-06 07:00 | -1701.48 | 6.1468 | 43.6299 | 48.4627 | -498.6546
2027-05-07 08:00 | -980.56 | 3.5345 | 43.7386 | 48.4627 | -287.3738
2027-05-08 09:00 | 2175.12 | 1 | 44.059 | 48.4627 | 637.4647
2027-05-09 10:00 | 3949.3 | 1.3436 | 55.1629 | 48.4627 | 1157.4256
2027-05-10 11:00 | 5996.22 | 2.0012 | 55.6957 | 48.4627 | 1757.3186
2027-05-11 12:00 | 7452.75 | 2.4579 | 56.2356 | 48.4627 | 2184.1854
2027-05-12 13:00 | 7908.51 | 2.6724 | 56.4106 | 48.4627 | 2317.7555
2027-05-13 14:00 | 8399.46 | 2.7196 | 57.1934 | 48.4627 | 2461.6387
2027-05-14 15:00 | 8295.4 | 2.8224 | 56.9639 | 48.4627 | 2431.1418
2027-05-15 16:00 | 7713.95 | 2.4399 | 57.9216 | 48.4627 | 2260.7356
2027-05-16 17:00 | 6032.89 | 1.9123 | 58.0056 | 48.4627 | 1768.0655
2027-05-17 18:00 | 3174.78 | 1.0353 | 57.6633 | 48.4627 | 930.4362
2027-05-18 19:00 | 2716.66 | 1 | 46.0988 | 48.4627 | 796.1745
2027-05-19 20:00 | -1022.45 | 4.2785 | 46.0812 | 48.4627 | -299.6505
2027-05-20 21:00 | -2039.18 | 6.6648 | 45.4203 | 48.4627 | -597.6247
2027-05-21 22:00 | -3653.68 | 6.6648 | 44.2347 | 48.4627 | -1070.7879
2027-05-22 23:00 | -4291.23 | 6.6648 | 43.5368 | 48.4627 | -1257.6354
2027-05-24 | -4955.21 | 6.6648 | 42.8924 | 48.4627 | -1452.2287
2027-05-25 01:00 | -5608.28 | 6.6648 | 42.2605 | 48.4627 | -1643.6246
2027-05-26 02:00 | -5976.71 | 6.6648 | 41.8129 | 48.4627 | -1751.6008
2027-05-27 03:00 | -6060.05 | 6.6648 | 41.5348 | 48.4627 | -1776.0253
2027-05-28 04:00 | -6159.2 | 6.6648 | 41.3032 | 48.4627 | -1805.0833
2027-05-29 05:00 | -6004.05 | 6.6648 | 41.2255 | 48.4627 | -1759.6134
2027-05-30 06:00 | -5779.33 | 6.6648 | 41.2352 | 48.4627 | -1693.7544
2027-05-31 07:00 | -5501.44 | 6.6648 | 41.2984 | 48.4627 | -1612.3129
2027-06-01 08:00 | -6039.05 | 6.6648 | 40.9927 | 48.4627 | -1769.8708
2027-06-02 09:00 | -5913.26 | 6.6648 | 40.9486 | 48.4627 | -1733.0054
2027-06-03 10:00 | -4303.01 | 6.6648 | 41.6924 | 48.4627 | -1261.0877
2027-06-04 11:00 | -2941.98 | 6.6648 | 42.4617 | 48.4627 | -862.2092
2027-06-05 12:00 | -1720.25 | 6.2757 | 43.1627 | 48.4627 | -504.1555
2027-06-06 13:00 | -1442.17 | 5.2298 | 43.3114 | 48.4627 | -422.6583
2027-06-07 14:00 | -1073.92 | 4.0039 | 43.442 | 48.4627 | -314.7349
2027-06-08 15:00 | -963.157 | 3.7437 | 43.5752 | 48.4627 | -282.2735
2027-06-09 16:00 | -755.734 | 3.0203 | 43.658 | 48.4627 | -221.4838
2027-06-10 17:00 | -954.408 | 3.8231 | 43.7125 | 48.4627 | -279.7094
2027-06-11 18:00 | -1961.46 | 6.6648 | 43.5791 | 48.4627 | -574.8472
2027-06-12 19:00 | -3004.35 | 6.6648 | 42.9659 | 48.4627 | -880.4881
2027-06-13 20:00 | -4591.53 | 6.6648 | 42.0408 | 48.4627 | -1345.6446
2027-06-14 21:00 | -5243.49 | 6.6648 | 41.5076 | 48.4627 | -1536.7152
2027-06-15 22:00 | -6492.04 | 6.6648 | 40.6896 | 48.4627 | -1902.6291
2027-06-16 23:00 | -6921.85 | 6.6648 | 40.2309 | 48.4627 | -2028.594
2027-06-18 | -7376.12 | 6.6648 | 39.7955 | 48.4627 | -2161.7274
2027-06-19 01:00 | -7556.87 | 6.6648 | 39.5213 | 48.4627 | -2214.7
2027-06-20 02:00 | -7761.84 | 6.6648 | 39.2724 | 48.4627 | -2274.7708
2027-06-21 03:00 | -7818.06 | 6.6648 | 39.1073 | 48.4627 | -2291.2472
2027-06-22 04:00 | -7768.86 | 6.6648 | 39.0229 | 48.4627 | -2276.8281
2027-06-23 05:00 | -7527.69 | 6.6648 | 39.0552 | 48.4627 | -2206.1482
2027-06-24 06:00 | -7138.04 | 6.6648 | 39.1998 | 48.4627 | -2091.953
2027-06-25 07:00 | -6472.67 | 6.6648 | 39.5189 | 48.4627 | -1896.9523
2027-06-26 08:00 | -5997.45 | 6.6648 | 39.8015 | 48.4627 | -1757.6791
2027-06-27 09:00 | -4605.37 | 6.6648 | 40.5569 | 48.4627 | -1349.7007
2027-06-28 10:00 | -2973.1 | 6.6648 | 41.533 | 48.4627 | -871.3296
2027-06-29 11:00 | -1939.98 | 6.6648 | 42.2804 | 48.4627 | -568.552
2027-06-30 12:00 | -1245.27 | 4.5188 | 42.5414 | 48.4627 | -364.9526
2027-07-01 13:00 | -981.35 | 3.7928 | 42.7813 | 48.4627 | -287.6053
2027-07-02 14:00 | -415.205 | 1.8032 | 43.024 | 48.4627 | -121.6846
2027-07-03 15:00 | -262.013 | 1.4835 | 43.3563 | 48.4627 | -76.7884
2027-07-04 16:00 | -619.501 | 2.8103 | 43.3149 | 48.4627 | -181.5578
2027-07-05 17:00 | -972.23 | 3.94 | 43.2644 | 48.4627 | -284.9325
2027-07-06 18:00 | -2060.61 | 6.6648 | 43.0656 | 48.4627 | -603.9052
2027-07-07 19:00 | -2804.71 | 6.6648 | 42.6135 | 48.4627 | -821.9794
2027-07-08 20:00 | -3998.59 | 6.6648 | 41.9159 | 48.4627 | -1171.871
2027-07-09 21:00 | -4685.57 | 6.6648 | 41.4084 | 48.4627 | -1373.205
2027-07-10 22:00 | -6140.09 | 6.6648 | 40.5141 | 48.4627 | -1799.4827
2027-07-11 23:00 | -6959.16 | 6.6648 | 39.8592 | 48.4627 | -2039.5285
2027-07-13 | -7271.1 | 6.6648 | 39.4758 | 48.4627 | -2130.9491
2027-07-14 01:00 | -7437.25 | 6.6648 | 39.2188 | 48.4627 | -2179.6428
2027-07-15 02:00 | -8092.71 | 6.6648 | 38.7455 | 48.4627 | -2371.7392
2027-07-16 03:00 | -8454.92 | 6.6648 | 38.3827 | 48.4627 | -2477.8925
2027-07-17 04:00 | -8503.6 | 6.6648 | 38.2025 | 48.4627 | -2492.1592
2027-07-18 05:00 | -8655.84 | 6.6648 | 38.0104 | 48.4627 | -2536.7763
2027-07-19 06:00 | -8002.23 | 6.6648 | 38.2379 | 48.4627 | -2345.2221
2027-07-20 07:00 | -7696.66 | 6.6648 | 38.3632 | 48.4627 | -2255.6684
2027-07-21 08:00 | -8341.63 | 6.6648 | 38.028 | 48.4627 | -2444.6904
2027-07-22 09:00 | -8713.9 | 6.6648 | 37.7425 | 48.4627 | -2553.792
2027-07-23 10:00 | -8552.88 | 6.6648 | 37.7128 | 48.4627 | -2506.6017
2027-07-24 11:00 | -8437.68 | 6.6648 | 37.7044 | 48.4627 | -2472.8399
2027-07-25 12:00 | -8606.06 | 6.6648 | 37.5505 | 48.4627 | -2522.1872
2027-07-26 13:00 | -8551.27 | 6.6648 | 37.4801 | 48.4627 | -2506.1298
2027-07-27 14:00 | -8544.83 | 6.6648 | 37.4082 | 48.4627 | -2504.2425
2027-07-28 15:00 | -8078.29 | 6.6648 | 37.5812 | 48.4627 | -2367.5131
2027-07-29 16:00 | -6238.18 | 6.6648 | 38.4999 | 48.4627 | -1828.2301
2027-07-30 17:00 | -6615.67 | 6.6648 | 38.4492 | 48.4627 | -1938.8615
2027-07-31 18:00 | -6850.75 | 6.6648 | 38.3517 | 48.4627 | -2007.7566
2027-08-01 19:00 | -7251.66 | 6.6648 | 38.1189 | 48.4627 | -2125.2518
2027-08-02 20:00 | -7441.94 | 6.6648 | 37.9908 | 48.4627 | -2181.0173
2027-08-03 21:00 | -7603.04 | 6.6648 | 37.8823 | 48.4627 | -2228.2311
2027-08-04 22:00 | -7647.62 | 6.6648 | 37.8142 | 48.4627 | -2241.2962
2027-08-05 23:00 | -8954.5 | 6.6648 | 37.1178 | 48.4627 | -2624.3049
2027-08-07 | -9237 | 6.6648 | 36.8292 | 48.4627 | -2707.0975
2027-08-08 01:00 | -9429.14 | 6.6648 | 36.6224 | 48.4627 | -2763.4081
2027-08-09 02:00 | -9498.9 | 6.6648 | 36.5102 | 48.4627 | -2783.8528
2027-08-10 03:00 | -9656.81 | 6.6648 | 36.361 | 48.4627 | -2830.1316
2027-08-11 04:00 | -9756.82 | 6.6648 | 36.2193 | 48.4627 | -2859.4417
2027-08-12 05:00 | -9604.02 | 6.6648 | 36.2294 | 48.4627 | -2814.6604
2027-08-13 06:00 | -8427.58 | 6.6648 | 36.7893 | 48.4627 | -2469.8799
2027-08-14 07:00 | -7836.37 | 6.6648 | 37.1642 | 48.4627 | -2296.6133
2027-08-15 08:00 | -7947.19 | 6.6648 | 37.1889 | 48.4627 | -2329.0915
2027-08-16 09:00 | -6383.97 | 6.6648 | 38.0034 | 48.4627 | -1870.9569
2027-08-17 10:00 | -6293.63 | 6.6648 | 38.2042 | 48.4627 | -1844.4809
2027-08-18 11:00 | -5869.85 | 6.6648 | 38.5243 | 48.4627 | -1720.2832
2027-08-19 12:00 | -5765.89 | 6.6648 | 38.6594 | 48.4627 | -1689.8156
2027-08-20 13:00 | -4683.27 | 6.6648 | 39.2757 | 48.4627 | -1372.5309
2027-08-21 14:00 | -4053.6 | 6.6648 | 39.7527 | 48.4627 | -1187.9929
2027-08-22 15:00 | -3570.8 | 6.6648 | 40.1427 | 48.4627 | -1046.4982
2027-08-23 16:00 | -2185.43 | 6.6648 | 40.9803 | 48.4627 | -640.4863
2027-08-24 17:00 | -2987.32 | 6.6648 | 40.7995 | 48.4627 | -875.4971
2027-08-25 18:00 | -3980.39 | 6.6648 | 40.369 | 48.4627 | -1166.5372
2027-08-26 19:00 | -4884.67 | 6.6648 | 39.8661 | 48.4627 | -1431.5555
2027-08-27 20:00 | -5631.72 | 6.6648 | 39.4143 | 48.4627 | -1650.4942
2027-08-28 21:00 | -6176.74 | 6.6648 | 39.0366 | 48.4627 | -1810.2238
2027-08-29 22:00 | -6561.08 | 6.6648 | 38.7222 | 48.4627 | -1922.8627
2027-08-30 23:00 | -7771.11 | 6.6648 | 38.0065 | 48.4627 | -2277.4875
2027-09-01 | -8159.62 | 6.6648 | 37.6388 | 48.4627 | -2391.3486
2027-09-02 01:00 | -8189.91 | 6.6648 | 37.4842 | 48.4627 | -2400.2257
2027-09-03 02:00 | -8320.42 | 6.6648 | 37.3306 | 48.4627 | -2438.4744
2027-09-04 03:00 | -8190.55 | 6.6648 | 37.3146 | 48.4627 | -2400.4133
2027-09-05 04:00 | -8131.87 | 6.6648 | 37.2769 | 48.4627 | -2383.2158
2027-09-06 05:00 | -7684.67 | 6.6648 | 37.4674 | 48.4627 | -2252.1545
2027-09-07 06:00 | -7254.65 | 6.6648 | 37.6945 | 48.4627 | -2126.128
2027-09-08 07:00 | -6369.02 | 6.6648 | 38.1815 | 48.4627 | -1866.5755
2027-09-09 08:00 | -5557.41 | 6.6648 | 38.6997 | 48.4627 | -1628.7161
2027-09-10 09:00 | -3931.62 | 6.6648 | 39.6623 | 48.4627 | -1152.2441
2027-09-11 10:00 | -2393.99 | 6.6648 | 40.6819 | 48.4627 | -701.6092
2027-09-12 11:00 | -1223.06 | 4.5445 | 41.2841 | 48.4627 | -358.4435
2027-09-13 12:00 | -467.88 | 1.9379 | 41.6788 | 48.4627 | -137.1221
2027-09-14 13:00 | 0 | 1 | 42.7717 | 48.4627 | 0
2027-09-15 14:00 | 2653.86 | 1 | 42.1092 | 48.4627 | 777.7696
2027-09-16 15:00 | 3073.86 | 1 | 42.3988 | 48.4627 | 900.8594
2027-09-17 16:00 | 3088.15 | 1 | 42.7116 | 48.4627 | 905.0474
2027-09-18 17:00 | 3111.19 | 1 | 42.9228 | 48.4627 | 911.7998
2027-09-19 18:00 | 0 | 0 | 44.1839 | 48.4627 | 0
2027-09-20 19:00 | -798.183 | 3.4549 | 43.286 | 48.4627 | -233.9243
2027-09-21 20:00 | -2041.81 | 6.6648 | 42.9226 | 48.4627 | -598.3954
2027-09-22 21:00 | -2810.01 | 6.6648 | 42.3934 | 48.4627 | -823.5326
2027-09-23 22:00 | -3943.82 | 6.6648 | 41.6629 | 48.4627 | -1155.8195
2027-09-24 23:00 | -4295.05 | 6.6648 | 41.2818 | 48.4627 | -1258.7549
2027-09-26 | -4516.74 | 6.6648 | 41.0454 | 48.4627 | -1323.7258
2027-09-27 01:00 | -4522.86 | 6.6648 | 40.9491 | 48.4627 | -1325.5194
2027-09-28 02:00 | -4446.95 | 6.6648 | 40.9119 | 48.4627 | -1303.2724
2027-09-29 03:00 | -3958.04 | 6.6648 | 41.1079 | 48.4627 | -1159.987
2027-09-30 04:00 | -3589.37 | 6.6648 | 41.306 | 48.4627 | -1051.9405
2027-10-01 05:00 | -3444.39 | 6.6648 | 41.4074 | 48.4627 | -1009.4511
2027-10-02 06:00 | -3724.86 | 6.6648 | 41.3024 | 48.4627 | -1091.6487
2027-10-03 07:00 | -3786.31 | 6.6648 | 41.2674 | 48.4627 | -1109.6579
2027-10-04 08:00 | -4383.55 | 6.6648 | 40.9665 | 48.4627 | -1284.6917
2027-10-05 09:00 | -4968.77 | 6.6648 | 40.6076 | 48.4627 | -1456.2027
2027-10-06 10:00 | -5193.87 | 6.6648 | 40.395 | 48.4627 | -1522.173
2027-10-07 11:00 | -4555.04 | 6.6648 | 40.6332 | 48.4627 | -1334.9504
2027-10-08 12:00 | -3412.15 | 6.6648 | 41.2174 | 48.4627 | -1000.0025
2027-10-09 13:00 | -4546.3 | 6.6648 | 40.7277 | 48.4627 | -1332.389
2027-10-10 14:00 | -4717.3 | 6.6648 | 40.5507 | 48.4627 | -1382.5042
2027-10-11 15:00 | -3021.61 | 6.6648 | 41.3307 | 48.4627 | -885.5465
2027-10-12 16:00 | -2854.73 | 6.6648 | 41.5293 | 48.4627 | -836.6388
2027-10-13 17:00 | -3307.98 | 6.6648 | 41.3533 | 48.4627 | -969.4732
2027-10-14 18:00 | -4227.67 | 6.6648 | 40.8465 | 48.4627 | -1239.0078
2027-10-15 19:00 | -4689.56 | 6.6648 | 40.5229 | 48.4627 | -1374.3744
2027-10-16 20:00 | -5906.24 | 6.6648 | 39.8341 | 48.4627 | -1730.9481
2027-10-17 21:00 | -6246.35 | 6.6648 | 39.4967 | 48.4627 | -1830.6245
2027-10-18 22:00 | -7283.2 | 6.6648 | 38.8394 | 48.4627 | -2134.4952
2027-10-19 23:00 | -7579.47 | 6.6648 | 38.5096 | 48.4627 | -2221.3234
2027-10-21 | -7954.84 | 6.6648 | 38.1698 | 48.4627 | -2331.3335
2027-10-22 01:00 | -8213.54 | 6.6648 | 37.9077 | 48.4627 | -2407.151
2027-10-23 02:00 | -8325.35 | 6.6648 | 37.7403 | 48.4627 | -2439.9192
2027-10-24 03:00 | -8976.61 | 6.6648 | 37.2955 | 48.4627 | -2630.7847
2027-10-25 04:00 | -9005.75 | 6.6648 | 37.1297 | 48.4627 | -2639.3248
2027-10-26 05:00 | -8552.17 | 6.6648 | 37.2455 | 48.4627 | -2506.3936
2027-10-27 06:00 | -8515.2 | 6.6648 | 37.2236 | 48.4627 | -2495.5588
2027-10-28 07:00 | -7757.26 | 6.6648 | 37.5613 | 48.4627 | -2273.4285
2027-10-29 08:00 | -7210.23 | 6.6648 | 37.8656 | 48.4627 | -2113.1098
2027-10-30 09:00 | -5950.54 | 6.6648 | 38.5679 | 48.4627 | -1743.9311
2027-10-31 10:00 | -4856.75 | 6.6648 | 39.2736 | 48.4627 | -1423.3729
2027-11-01 11:00 | -4200.12 | 6.6648 | 39.7854 | 48.4627 | -1230.9337
2027-11-02 12:00 | -3648.14 | 6.6648 | 40.2281 | 48.4627 | -1069.1643
2027-11-03 13:00 | -3247.81 | 6.6648 | 40.5867 | 48.4627 | -951.8392
2027-11-04 14:00 | -3238.38 | 6.6648 | 40.7331 | 48.4627 | -949.0755
2027-11-05 15:00 | -2233.68 | 6.6648 | 41.3334 | 48.4627 | -654.627
2027-11-06 16:00 | -2635.9 | 6.6648 | 41.2847 | 48.4627 | -772.506
2027-11-07 17:00 | -3356.47 | 6.6648 | 40.9811 | 48.4627 | -983.6843
2027-11-08 18:00 | -4212.27 | 6.6648 | 40.5314 | 48.4627 | -1234.4945
2027-11-09 19:00 | -5125.09 | 6.6648 | 39.9992 | 48.4627 | -1502.0156
2027-11-10 20:00 | -6391.76 | 6.6648 | 39.2543 | 48.4627 | -1873.2399
2027-11-11 21:00 | -7104.39 | 6.6648 | 38.7027 | 48.4627 | -2082.0912
2027-11-12 22:00 | -8153.59 | 6.6648 | 37.9886 | 48.4627 | -2389.5813
2027-11-13 23:00 | -8390.57 | 6.6648 | 37.6564 | 48.4627 | -2459.0333
2027-11-15 | -8604.85 | 6.6648 | 37.386 | 48.4627 | -2521.8326
2027-11-16 01:00 | -8642.57 | 6.6648 | 37.2337 | 48.4627 | -2532.8872
2027-11-17 02:00 | -8616.73 | 6.6648 | 37.1463 | 48.4627 | -2525.3143
2027-11-18 03:00 | -8555.37 | 6.6648 | 37.0916 | 48.4627 | -2507.3314
2027-11-19 04:00 | -8525.56 | 6.6648 | 37.0467 | 48.4627 | -2498.595
2027-11-20 05:00 | -8120.96 | 6.6648 | 37.2005 | 48.4627 | -2380.0184
2027-11-21 06:00 | -7425.95 | 6.6648 | 37.5498 | 48.4627 | -2176.3311
2027-11-22 07:00 | -5968.23 | 6.6648 | 38.344 | 48.4627 | -1749.1156
2027-11-23 08:00 | -5417.7 | 6.6648 | 38.7876 | 48.4627 | -1587.7711
2027-11-24 09:00 | -3929.56 | 6.6648 | 39.6842 | 48.4627 | -1151.6404
2027-11-25 10:00 | -2692.81 | 6.6648 | 40.5424 | 48.4627 | -789.1847
2027-11-26 11:00 | -1401.29 | 5.2388 | 41.2688 | 48.4627 | -410.6776
2027-11-27 12:00 | -1460.64 | 5.5812 | 41.5749 | 48.4627 | -428.0713
2027-11-28 13:00 | -1785.4 | 6.6648 | 41.7273 | 48.4627 | -523.2491
2027-11-29 14:00 | -1711.05 | 6.3247 | 41.8197 | 48.4627 | -501.4593
2027-11-30 15:00 | -766.324 | 2.815 | 41.9025 | 48.4627 | -224.5874
2027-12-01 16:00 | -602.58 | 2.6353 | 42.2187 | 48.4627 | -176.5988
2027-12-02 17:00 | -1095.7 | 4.4796 | 42.2904 | 48.4627 | -321.118
2027-12-03 18:00 | -1910.67 | 6.6648 | 42.199 | 48.4627 | -559.9621
2027-12-04 19:00 | -2925.05 | 6.6648 | 41.6684 | 48.4627 | -857.2475
2027-12-05 20:00 | -4094.21 | 6.6648 | 41.0093 | 48.4627 | -1199.8945
2027-12-06 21:00 | -4740.59 | 6.6648 | 40.5405 | 48.4627 | -1389.3298
2027-12-07 22:00 | -5928.23 | 6.6648 | 39.7998 | 48.4627 | -1737.3927
2027-12-08 23:00 | -6392.69 | 6.6648 | 39.367 | 48.4627 | -1873.5125
2027-12-10 | -6487.48 | 6.6648 | 39.1587 | 48.4627 | -1901.2927
2027-12-11 01:00 | -6763.05 | 6.6648 | 38.9176 | 48.4627 | -1982.0543
2027-12-12 02:00 | -6755.77 | 6.6648 | 38.8282 | 48.4627 | -1979.9207
2027-12-13 03:00 | -6583.2 | 6.6648 | 38.8416 | 48.4627 | -1929.3455
2027-12-14 04:00 | -6494.17 | 6.6648 | 38.854 | 48.4627 | -1903.2534
2027-12-15 05:00 | -6022.73 | 6.6648 | 39.0716 | 48.4627 | -1765.0879
2027-12-16 06:00 | -5909.19 | 6.6648 | 39.1496 | 48.4627 | -1731.8126
2027-12-17 07:00 | -6031.8 | 6.6648 | 39.1003 | 48.4627 | -1767.7461
2027-12-18 08:00 | -7024.88 | 6.6648 | 38.5832 | 48.4627 | -2058.7891
2027-12-19 09:00 | -7255.58 | 6.6648 | 38.3513 | 48.4627 | -2126.4006
2027-12-20 10:00 | -7227.18 | 6.6648 | 38.2719 | 48.4627 | -2118.0774
2027-12-21 11:00 | -7374.55 | 6.6648 | 38.1269 | 48.4627 | -2161.2673
2027-12-22 12:00 | -7226.8 | 6.6648 | 38.1191 | 48.4627 | -2117.966
2027-12-23 13:00 | -7552.91 | 6.6648 | 37.8933 | 48.4627 | -2213.5394
2027-12-24 14:00 | -7623.97 | 6.6648 | 37.7758 | 48.4627 | -2234.365
2027-12-25 15:00 | -6926.85 | 6.6648 | 38.0501 | 48.4627 | -2030.0593
2027-12-26 16:00 | -6772.39 | 6.6648 | 38.1257 | 48.4627 | -1984.7916
2027-12-27 17:00 | -6877.24 | 6.6648 | 38.0588 | 48.4627 | -2015.5201
2027-12-28 18:00 | -7022.78 | 6.6648 | 37.9427 | 48.4627 | -2058.1736
2027-12-29 19:00 | -7611.17 | 6.6648 | 37.6001 | 48.4627 | -2230.6137
2027-12-30 20:00 | -8278.26 | 6.6648 | 37.1864 | 48.4627 | -2426.1185
2027-12-31 21:00 | -8494.64 | 6.6648 | 36.9611 | 48.4627 | -2489.5332
2028-01-01 22:00 | -9120.57 | 6.6648 | 36.5535 | 48.4627 | -2672.9752
2028-01-02 23:00 | -9300.29 | 6.6648 | 36.3436 | 48.4627 | -2725.6459
2028-01-04 | -9471.24 | 6.6648 | 36.1547 | 48.4627 | -2775.7464
2028-01-05 01:00 | -9460.7 | 6.6648 | 36.0784 | 48.4627 | -2772.6575
2028-01-06 02:00 | -9514.21 | 6.6648 | 35.9935 | 48.4627 | -2788.3397
2028-01-07 03:00 | -9611.55 | 6.6648 | 35.881 | 48.4627 | -2816.8672
2028-01-08 04:00 | -9591.47 | 6.6648 | 35.8292 | 48.4627 | -2810.9824
2028-01-09 05:00 | -9327.13 | 6.6648 | 35.9106 | 48.4627 | -2733.512
2028-01-10 06:00 | -8442.72 | 6.6648 | 36.3396 | 48.4627 | -2474.317
2028-01-11 07:00 | -8028.37 | 6.6648 | 36.6056 | 48.4627 | -2352.883
2028-01-12 08:00 | -8323.19 | 6.6648 | 36.5146 | 48.4627 | -2439.2862
2028-01-13 09:00 | -8001.05 | 6.6648 | 36.6719 | 48.4627 | -2344.8763
2028-01-14 10:00 | -7266.78 | 6.6648 | 37.0755 | 48.4627 | -2129.683
2028-01-15 11:00 | -7172.55 | 6.6648 | 37.211 | 48.4627 | -2102.0669
2028-01-16 12:00 | -6924.13 | 6.6648 | 37.3805 | 48.4627 | -2029.2622
2028-01-17 13:00 | -6835.65 | 6.6648 | 37.4668 | 48.4627 | -2003.3313
2028-01-18 14:00 | -6498.74 | 6.6648 | 37.6816 | 48.4627 | -1904.5927
2028-01-19 15:00 | -6199.18 | 6.6648 | 37.8893 | 48.4627 | -1816.8003
2028-01-20 16:00 | -4228.37 | 6.6648 | 38.9518 | 48.4627 | -1239.2129
2028-01-21 17:00 | -4541.42 | 6.6648 | 39.0188 | 48.4627 | -1330.9588
2028-01-22 18:00 | -4908.67 | 6.6648 | 38.9311 | 48.4627 | -1438.5892
2028-01-23 19:00 | -5588.73 | 6.6648 | 38.6131 | 48.4627 | -1637.8951
2028-01-24 20:00 | -5774.68 | 6.6648 | 38.5075 | 48.4627 | -1692.3916
2028-01-25 21:00 | -5967.69 | 6.6648 | 38.4131 | 48.4627 | -1748.9573
2028-01-26 22:00 | -6135.15 | 6.6648 | 38.3061 | 48.4627 | -1798.035
2028-01-27 23:00 | -7480.48 | 6.6648 | 37.5999 | 48.4627 | -2192.3123
2028-01-29 | -7726.94 | 6.6648 | 37.3392 | 48.4627 | -2264.5426
2028-01-30 01:00 | -7962.36 | 6.6648 | 37.1311 | 48.4627 | -2333.5374
2028-01-31 02:00 | -7936.69 | 6.6648 | 37.0782 | 48.4627 | -2326.0142
2028-02-01 03:00 | -8214.75 | 6.6648 | 36.89 | 48.4627 | -2407.5056
2028-02-02 04:00 | -7990.22 | 6.6648 | 36.9226 | 48.4627 | -2341.7023
2028-02-03 05:00 | -7907.67 | 6.6648 | 36.938 | 48.4627 | -2317.5093
2028-02-04 06:00 | -6833.97 | 6.6648 | 37.4684 | 48.4627 | -2002.8389
2028-02-05 07:00 | -5442.82 | 6.6648 | 38.2654 | 48.4627 | -1595.1331
2028-02-06 08:00 | -5098.67 | 6.6648 | 38.6211 | 48.4627 | -1494.2727
2028-02-07 09:00 | -3862.84 | 6.6648 | 39.3858 | 48.4627 | -1132.0867
2028-02-08 10:00 | -2573.18 | 6.6648 | 40.2435 | 48.4627 | -754.1246
2028-02-09 11:00 | -1595.03 | 6.012 | 40.9279 | 48.4627 | -467.4571
2028-02-10 12:00 | -1089.01 | 4.1041 | 41.1964 | 48.4627 | -319.1573
2028-02-11 13:00 | -1662.83 | 6.5069 | 41.4572 | 48.4627 | -487.3274
2028-02-12 14:00 | -2020.66 | 6.6648 | 41.4149 | 48.4627 | -592.197
2028-02-13 15:00 | -1973.74 | 6.6648 | 41.5125 | 48.4627 | -578.4461
2028-02-14 16:00 | -752.968 | 2.736 | 41.6567 | 48.4627 | -220.6731
2028-02-15 17:00 | -1074.27 | 4.4113 | 41.9526 | 48.4627 | -314.8375
2028-02-16 18:00 | -1772.36 | 6.6648 | 41.9687 | 48.4627 | -519.4274
2028-02-17 19:00 | -2744.29 | 6.6648 | 41.4824 | 48.4627 | -804.272
2028-02-18 20:00 | -3357.93 | 6.6648 | 41.1264 | 48.4627 | -984.1121
2028-02-19 21:00 | -3900.08 | 6.6648 | 40.7944 | 48.4627 | -1143.0006
2028-02-20 22:00 | -4247.3 | 6.6648 | 40.531 | 48.4627 | -1244.7608
2028-02-21 23:00 | -5644.98 | 6.6648 | 39.7388 | 48.4627 | -1654.3803
2028-02-23 | -6002.85 | 6.6648 | 39.3761 | 48.4627 | -1759.2617
2028-02-24 01:00 | -5998.29 | 6.6648 | 39.2508 | 48.4627 | -1757.9253
2028-02-25 02:00 | -6267.12 | 6.6648 | 39.0491 | 48.4627 | -1836.7116
2028-02-26 03:00 | -6444.09 | 6.6648 | 38.8862 | 48.4627 | -1888.5764
2028-02-27 04:00 | -6537.19 | 6.6648 | 38.7545 | 48.4627 | -1915.8613
2028-02-28 05:00 | -6079.69 | 6.6648 | 38.9326 | 48.4627 | -1781.7813
2028-02-29 06:00 | -5377.5 | 6.6648 | 39.2933 | 48.4627 | -1575.9897
2028-03-01 07:00 | -3930.63 | 6.6648 | 40.0862 | 48.4627 | -1151.9539
2028-03-02 08:00 | -3418.34 | 6.6648 | 40.5116 | 48.4627 | -1001.8166
2028-03-03 09:00 | -2247.8 | 6.6648 | 41.2452 | 48.4627 | -658.7652
2028-03-04 10:00 | -1400.31 | 5.1822 | 41.6619 | 48.4627 | -410.3904
2028-03-05 11:00 | -1510.19 | 5.7463 | 41.8977 | 48.4627 | -442.593
2028-03-06 12:00 | -1526.57 | 5.7261 | 42.0092 | 48.4627 | -447.3935
2028-03-07 13:00 | -1739.35 | 6.5219 | 42.094 | 48.4627 | -509.7532
2028-03-08 14:00 | -925.972 | 3.3731 | 42.1275 | 48.4627 | -271.3756
2028-03-09 15:00 | 0 | 1 | 43.1919 | 48.4627 | 0
2028-03-10 16:00 | 2671.05 | 1 | 42.4514 | 48.4627 | 782.8075
2028-03-11 17:00 | 2036.22 | 1 | 43.0428 | 48.4627 | 596.7572
2028-03-12 18:00 | -572.069 | 2.8238 | 43.2277 | 48.4627 | -167.6569
2028-03-13 19:00 | -1497.28 | 5.8928 | 42.9384 | 48.4627 | -438.8095
2028-03-14 20:00 | -3096.86 | 6.6648 | 42.127 | 48.4627 | -907.6001
2028-03-15 21:00 | -3893.23 | 6.6648 | 41.5478 | 48.4627 | -1140.9931
2028-03-16 22:00 | -5185.19 | 6.6648 | 40.6787 | 48.4627 | -1519.6292
2028-03-17 23:00 | -5808.21 | 6.6648 | 40.1168 | 48.4627 | -1702.2183
2028-03-19 | -6022.58 | 6.6648 | 39.8197 | 48.4627 | -1765.044
2028-03-20 01:00 | -6547.77 | 6.6648 | 39.4186 | 48.4627 | -1918.962
2028-03-21 02:00 | -6934.53 | 6.6648 | 39.0812 | 48.4627 | -2032.3101
2028-03-22 03:00 | -7175.25 | 6.6648 | 38.8137 | 48.4627 | -2102.8582
2028-03-23 04:00 | -7408.06 | 6.6648 | 38.554 | 48.4627 | -2171.0881
2028-03-24 05:00 | -7051.72 | 6.6648 | 38.605 | 48.4627 | -2066.6551
2028-03-25 06:00 | -6694.28 | 6.6648 | 38.7268 | 48.4627 | -1961.8998
2028-03-26 07:00 | -5780.77 | 6.6648 | 39.1656 | 48.4627 | -1694.1764
2028-03-27 08:00 | -5164.9 | 6.6648 | 39.5352 | 48.4627 | -1513.6828
2028-03-28 09:00 | -3900.69 | 6.6648 | 40.2523 | 48.4627 | -1143.1794
2028-03-29 10:00 | -2170.78 | 6.6648 | 41.2895 | 48.4627 | -636.1928
2028-03-30 11:00 | -977.793 | 3.5803 | 41.7206 | 48.4627 | -286.5628
2028-03-31 12:00 | -481.257 | 2.0955 | 42.13 | 48.4627 | -141.0425
2028-04-01 13:00 | 120.229 | 1 | 43.0816 | 48.4627 | 35.2356
2028-04-02 14:00 | 2679.9 | 1 | 42.4181 | 48.4627 | 785.4012
2028-04-03 15:00 | 2791.67 | 1 | 42.7794 | 48.4627 | 818.1577
2028-04-04 16:00 | 2768.11 | 1 | 43.0383 | 48.4627 | 811.253
2028-04-05 17:00 | 2726.37 | 1 | 43.2153 | 48.4627 | 799.0202
2028-04-06 18:00 | -473.759 | 2.4428 | 43.6445 | 48.4627 | -138.8451
2028-04-07 19:00 | -1364.58 | 5.4165 | 43.2882 | 48.4627 | -399.9189
2028-04-08 20:00 | -2941.63 | 6.6648 | 42.4911 | 48.4627 | -862.1067
2028-04-09 21:00 | -4038.95 | 6.6648 | 41.7313 | 48.4627 | -1183.6994
2028-04-10 22:00 | -5021.34 | 6.6648 | 41.0019 | 48.4627 | -1471.6095
2028-04-11 23:00 | -5663.87 | 6.6648 | 40.4304 | 48.4627 | -1659.9164
2028-04-13 | -5897.61 | 6.6648 | 40.1214 | 48.4627 | -1728.4189
2028-04-14 01:00 | -7092.34 | 6.6648 | 39.3617 | 48.4627 | -2078.5597
2028-04-15 02:00 | -6911.5 | 6.6648 | 39.2188 | 48.4627 | -2025.5607
2028-04-16 03:00 | -6747.5 | 6.6648 | 39.1592 | 48.4627 | -1977.497
2028-04-17 04:00 | -6848 | 6.6648 | 39.0193 | 48.4627 | -2006.9507
2028-04-18 05:00 | -6022.06 | 6.6648 | 39.3401 | 48.4627 | -1764.8916
2028-04-19 06:00 | -5104.5 | 6.6648 | 39.8155 | 48.4627 | -1495.9813
2028-04-20 07:00 | -3854.13 | 6.6648 | 40.5388 | 48.4627 | -1129.534
2028-04-21 08:00 | -2691.11 | 6.6648 | 41.2881 | 48.4627 | -788.6865
2028-04-22 09:00 | -1031.1 | 3.7834 | 41.9273 | 48.4627 | -302.1856
2028-04-23 10:00 | 1935.45 | 1 | 42.4741 | 48.4627 | 567.2244
2028-04-24 11:00 | 2792.82 | 1 | 42.6407 | 48.4627 | 818.4947
2028-04-25 12:00 | 3019.71 | 1.082 | 53.4461 | 48.4627 | 884.9896
2028-04-26 13:00 | 3210.74 | 1.1552 | 53.6376 | 48.4627 | 940.975
2028-04-27 14:00 | 3899.78 | 1.3961 | 53.9056 | 48.4627 | 1142.9127
2028-04-28 15:00 | 4810.14 | 1.7151 | 54.186 | 48.4627 | 1409.7129
2028-04-29 16:00 | 4749.93 | 1.6808 | 54.5035 | 48.4627 | 1392.0671
2028-04-30 17:00 | 3854.97 | 1.3879 | 54.5073 | 48.4627 | 1129.7802
2028-05-01 18:00 | 2737.34 | 1 | 59.7611 | 48.4627 | 802.2352
2028-05-02 19:00 | 181.387 | 1 | 45.1002 | 48.4627 | 53.1593
2028-05-03 20:00 | -844.571 | 3.7271 | 44.1901 | 48.4627 | -247.5193
2028-05-04 21:00 | -1859.15 | 6.6648 | 43.8203 | 48.4627 | -544.8631
2028-05-05 22:00 | -3265.69 | 6.6648 | 42.9012 | 48.4627 | -957.0793
2028-05-06 23:00 | -3908.34 | 6.6648 | 42.3127 | 48.4627 | -1145.4214
2028-05-08 | -4933.76 | 6.6648 | 41.5663 | 48.4627 | -1445.9423
2028-05-09 01:00 | -4925.3 | 6.6648 | 41.3542 | 48.4627 | -1443.4629
2028-05-10 02:00 | -5259.28 | 6.6648 | 41.0379 | 48.4627 | -1541.3428
2028-05-11 03:00 | -5201.16 | 6.6648 | 40.9233 | 48.4627 | -1524.3095
2028-05-12 04:00 | -5129.01 | 6.6648 | 40.8596 | 48.4627 | -1503.1644
2028-05-13 05:00 | -4789.45 | 6.6648 | 40.9586 | 48.4627 | -1403.6492
2028-05-14 06:00 | -3771.1 | 6.6648 | 41.4526 | 48.4627 | -1105.2003
2028-05-15 07:00 | -2219.01 | 6.6648 | 42.3151 | 48.4627 | -650.3276
2028-05-16 08:00 | -1254.35 | 4.5517 | 42.6892 | 48.4627 | -367.6137
2028-05-17 09:00 | 0 | 0 | 43.8078 | 48.4627 | 0
2028-05-18 10:00 | 2844.04 | 1 | 43.0583 | 48.4627 | 833.5058
2028-05-19 11:00 | 2888.77 | 1.0355 | 53.9257 | 48.4627 | 846.6149
2028-05-20 12:00 | 3811.59 | 1.3228 | 54.4596 | 48.4627 | 1117.0668
2028-05-21 13:00 | 4517.49 | 1.5398 | 54.8874 | 48.4627 | 1323.9456
2028-05-22 14:00 | 4782.24 | 1.6448 | 55.0594 | 48.4627 | 1401.5362
2028-05-23 15:00 | 5241.24 | 1.7901 | 55.3383 | 48.4627 | 1536.0558
2028-05-24 16:00 | 4635.3 | 1.609 | 55.3601 | 48.4627 | 1358.4723
2028-05-25 17:00 | 3754.88 | 1.2941 | 55.5283 | 48.4627 | 1100.4467
2028-05-26 18:00 | 2865.31 | 1 | 44.7388 | 48.4627 | 839.7395
2028-05-27 19:00 | 2804.46 | 1 | 44.7318 | 48.4627 | 821.9061
2028-05-28 20:00 | -504.29 | 2.5032 | 45.0191 | 48.4627 | -147.7928
2028-05-29 21:00 | -1110.5 | 4.3927 | 44.5516 | 48.4627 | -325.4554
2028-05-30 22:00 | -2141.98 | 6.6648 | 44.0985 | 48.4627 | -627.7524
2028-05-31 23:00 | -2724.81 | 6.6648 | 43.6052 | 48.4627 | -798.563
2028-06-02 | -2964.44 | 6.6648 | 43.2986 | 48.4627 | -868.7916
2028-06-03 01:00 | -3319.39 | 6.6648 | 42.9561 | 48.4627 | -972.8172
2028-06-04 02:00 | -3727.06 | 6.6648 | 42.6296 | 48.4627 | -1092.2935
2028-06-05 03:00 | -3846.5 | 6.6648 | 42.436 | 48.4627 | -1127.2979
2028-06-06 04:00 | -3800.89 | 6.6648 | 42.362 | 48.4627 | -1113.9309
2028-06-07 05:00 | -3389.16 | 6.6648 | 42.5069 | 48.4627 | -993.2647
2028-06-08 06:00 | -2659.96 | 6.6648 | 42.8585 | 48.4627 | -779.5573
2028-06-09 07:00 | -1823.87 | 6.6318 | 43.3087 | 48.4627 | -534.5235
2028-06-10 08:00 | -1684.81 | 6.07 | 43.3971 | 48.4627 | -493.7691
2028-06-11 09:00 | -829.716 | 3.0118 | 43.457 | 48.4627 | -243.1658
2028-06-12 10:00 | -378.377 | 1.748 | 43.757 | 48.4627 | -110.8914
2028-06-13 11:00 | 2446.66 | 1 | 43.7604 | 48.4627 | 717.0453
2028-06-14 12:00 | 2838.64 | 1 | 43.9496 | 48.4627 | 831.9233
2028-06-15 13:00 | 2796.4 | 1 | 44.1855 | 48.4627 | 819.5439
2028-06-16 14:00 | 2909.97 | 1 | 44.2763 | 48.4627 | 852.828
2028-06-17 15:00 | 2892.1 | 1 | 55.8534 | 48.4627 | 847.5908
2028-06-18 16:00 | 2850.79 | 1 | 56.4431 | 48.4627 | 835.4841
2028-06-19 17:00 | 2746.46 | 1 | 44.5952 | 48.4627 | 804.908
2028-06-20 18:00 | 2037.32 | 1 | 44.8848 | 48.4627 | 597.0796
2028-06-21 19:00 | -341.826 | 1.9443 | 44.9603 | 48.4627 | -100.1793
2028-06-22 20:00 | -1445.13 | 5.6601 | 44.4851 | 48.4627 | -423.5258
2028-06-23 21:00 | -2169.82 | 6.6648 | 44.0461 | 48.4627 | -635.9115
2028-06-24 22:00 | -3483.29 | 6.6648 | 43.2151 | 48.4627 | -1020.8515
2028-06-25 23:00 | -4387.11 | 6.6648 | 42.5036 | 48.4627 | -1285.735
2028-06-27 | -4743.83 | 6.6648 | 42.0654 | 48.4627 | -1390.2793
2028-06-28 01:00 | -5102.44 | 6.6648 | 41.702 | 48.4627 | -1495.3776
2028-06-29 02:00 | -5408.3 | 6.6648 | 41.3871 | 48.4627 | -1585.0163
2028-06-30 03:00 | -5812.48 | 6.6648 | 41.028 | 48.4627 | -1703.4697
2028-07-01 04:00 | -6189.8 | 6.6648 | 40.6857 | 48.4627 | -1814.0513
2028-07-02 05:00 | -6140.44 | 6.6648 | 40.5607 | 48.4627 | -1799.5853
2028-07-03 06:00 | -5236.47 | 6.6648 | 40.9081 | 48.4627 | -1534.6579
2028-07-04 07:00 | -4159.04 | 6.6648 | 41.4584 | 48.4627 | -1218.8943
2028-07-05 08:00 | -4080.23 | 6.6648 | 41.578 | 48.4627 | -1195.7974
2028-07-06 09:00 | -3197.66 | 6.6648 | 42.0533 | 48.4627 | -937.1416
2028-07-07 10:00 | -2160.82 | 6.6648 | 42.6714 | 48.4627 | -633.2738
2028-07-08 11:00 | -1306.18 | 4.72 | 42.9782 | 48.4627 | -382.8036
2028-07-09 12:00 | -751.707 | 2.9067 | 43.1887 | 48.4627 | -220.3036
2028-07-10 13:00 | -169.391 | 1.0139 | 43.6265 | 48.4627 | -49.6436
2028-07-11 14:00 | 2511.96 | 1 | 43.4771 | 48.4627 | 736.1828
2028-07-12 15:00 | 2767.01 | 1 | 43.7405 | 48.4627 | 810.9306
2028-07-13 16:00 | 2799.68 | 1 | 56.1058 | 48.4627 | 820.5052
2028-07-14 17:00 | 2740.44 | 1 | 44.1375 | 48.4627 | 803.1437
2028-07-15 18:00 | 0 | 0 | 45.2102 | 48.4627 | 0
2028-07-16 19:00 | -819.121 | 3.2582 | 44.2155 | 48.4627 | -240.0607
2028-07-17 20:00 | -1357.71 | 5.2314 | 44.0506 | 48.4627 | -397.9055
2028-07-18 21:00 | -2074.83 | 6.6648 | 43.7796 | 48.4627 | -608.0726
2028-07-19 22:00 | -2577.81 | 6.6648 | 43.3997 | 48.4627 | -755.4815
2028-07-20 23:00 | -4350.2 | 6.6648 | 42.3656 | 48.4627 | -1274.9178
2028-07-22 | -5096.81 | 6.6648 | 41.7604 | 48.4627 | -1493.7276
2028-07-23 01:00 | -5526.51 | 6.6648 | 41.3405 | 48.4627 | -1619.6602
2028-07-24 02:00 | -5897.01 | 6.6648 | 40.9717 | 48.4627 | -1728.243
2028-07-25 03:00 | -6151.04 | 6.6648 | 40.6734 | 48.4627 | -1802.6919
2028-07-26 04:00 | -6256.07 | 6.6648 | 40.4614 | 48.4627 | -1833.4731
2028-07-27 05:00 | -6119.4 | 6.6648 | 40.4094 | 48.4627 | -1793.4191
2028-07-28 06:00 | -4809.23 | 6.6648 | 41.0086 | 48.4627 | -1409.4462
2028-07-29 07:00 | -3797.22 | 6.6648 | 41.5871 | 48.4627 | -1112.8553
2028-07-30 08:00 | -3582.36 | 6.6648 | 41.8097 | 48.4627 | -1049.8861
2028-07-31 09:00 | -2520.79 | 6.6648 | 42.4135 | 48.4627 | -738.7706
2028-08-01 10:00 | -1210.33 | 4.3844 | 42.8892 | 48.4627 | -354.7127
2028-08-02 11:00 | -317.228 | 1.3707 | 43.2506 | 48.4627 | -92.9703
2028-08-03 12:00 | 674.975 | 1 | 44.0082 | 48.4627 | 197.8156
2028-08-04 13:00 | 0 | 0 | 44.4504 | 48.4627 | 0
2028-08-05 14:00 | 1717.65 | 1 | 43.9367 | 48.4627 | 503.3935
2028-08-06 15:00 | 2761.82 | 1 | 43.8058 | 48.4627 | 809.4095
2028-08-07 16:00 | 2794.95 | 1 | 58.2583 | 48.4627 | 819.119
2028-08-08 17:00 | 2742.89 | 1 | 44.2153 | 48.4627 | 803.8617
2028-08-09 18:00 | 0 | 0 | 45.2691 | 48.4627 | 0
2028-08-10 19:00 | -588.918 | 2.8393 | 44.4239 | 48.4627 | -172.5948
2028-08-11 20:00 | -1152.27 | 4.5305 | 44.1563 | 48.4627 | -337.697
2028-08-12 21:00 | -1534.99 | 5.7241 | 44.0175 | 48.4627 | -449.8612
2028-08-13 22:00 | -1935.78 | 6.6648 | 43.8455 | 48.4627 | -567.3211
2028-08-14 23:00 | -3474.36 | 6.6648 | 42.9592 | 48.4627 | -1018.2344
2028-08-16 | -4002.21 | 6.6648 | 42.504 | 48.4627 | -1172.932
2028-08-17 01:00 | -4297.43 | 6.6648 | 42.2056 | 48.4627 | -1259.4524
2028-08-18 02:00 | -4452.29 | 6.6648 | 42.0076 | 48.4627 | -1304.8374
2028-08-19 03:00 | -4336.35 | 6.6648 | 41.9574 | 48.4627 | -1270.8587
2028-08-20 04:00 | -4316.84 | 6.6648 | 41.8905 | 48.4627 | -1265.1409
2028-08-21 05:00 | -3689.52 | 6.6648 | 42.1584 | 48.4627 | -1081.2916
2028-08-22 06:00 | -3359.38 | 6.6648 | 42.3553 | 48.4627 | -984.5371
2028-08-23 07:00 | -3003.21 | 6.6648 | 42.5723 | 48.4627 | -880.154
2028-08-24 08:00 | -2994.57 | 6.6648 | 42.6231 | 48.4627 | -877.6218
2028-08-25 09:00 | -2462.14 | 6.6648 | 42.912 | 48.4627 | -721.582
2028-08-26 10:00 | -1684.96 | 6.1084 | 43.2815 | 48.4627 | -493.813
2028-08-27 11:00 | -1046.61 | 3.7989 | 43.3841 | 48.4627 | -306.7311
2028-08-28 12:00 | -1216.65 | 4.6922 | 43.5524 | 48.4627 | -356.5649
2028-08-29 13:00 | -1705.65 | 6.3707 | 43.5732 | 48.4627 | -499.8767
2028-08-30 14:00 | -1814.52 | 6.5678 | 43.5248 | 48.4627 | -531.7833
2028-08-31 15:00 | -1119.89 | 4.0028 | 43.4907 | 48.4627 | -328.2074
2028-09-01 16:00 | -865.682 | 3.3881 | 43.623 | 48.4627 | -253.7064
2028-09-02 17:00 | -853.459 | 3.4158 | 43.6775 | 48.4627 | -250.1241
2028-09-03 18:00 | -1301.85 | 5.0397 | 43.677 | 48.4627 | -381.5346
2028-09-04 19:00 | -1746.16 | 6.4714 | 43.6255 | 48.4627 | -511.749
2028-09-05 20:00 | -3013.8 | 6.6648 | 42.9767 | 48.4627 | -883.2576
2028-09-06 21:00 | -3531.01 | 6.6648 | 42.5765 | 48.4627 | -1034.8369
2028-09-07 22:00 | -4652.39 | 6.6648 | 41.8732 | 48.4627 | -1363.4809
2028-09-08 23:00 | -5229.25 | 6.6648 | 41.3959 | 48.4627 | -1532.5419
2028-09-10 | -5159.73 | 6.6648 | 41.2635 | 48.4627 | -1512.1676
2028-09-11 01:00 | -5344.15 | 6.6648 | 41.0737 | 48.4627 | -1566.2158
2028-09-12 02:00 | -5319.49 | 6.6648 | 41.0068 | 48.4627 | -1558.9886
2028-09-13 03:00 | -5135.44 | 6.6648 | 41.033 | 48.4627 | -1505.0489
2028-09-14 04:00 | -4987.41 | 6.6648 | 41.079 | 48.4627 | -1461.6656
2028-09-15 05:00 | -4460.91 | 6.6648 | 41.3302 | 48.4627 | -1307.3637
2028-09-16 06:00 | -4002.05 | 6.6648 | 41.5847 | 48.4627 | -1172.8851
2028-09-17 07:00 | -3538.46 | 6.6648 | 41.863 | 48.4627 | -1037.0203
2028-09-18 08:00 | -4022.51 | 6.6648 | 41.6808 | 48.4627 | -1178.8813
2028-09-19 09:00 | -3490.34 | 6.6648 | 41.9337 | 48.4627 | -1022.9177
2028-09-20 10:00 | -2668.77 | 6.6648 | 42.3948 | 48.4627 | -782.1393
2028-09-21 11:00 | -2503.36 | 6.6648 | 42.5806 | 48.4627 | -733.6624
2028-09-22 12:00 | -2387.32 | 6.6648 | 42.7007 | 48.4627 | -699.6544
2028-09-23 13:00 | -2183.07 | 6.6648 | 42.8473 | 48.4627 | -639.7947
2028-09-24 14:00 | -2339.92 | 6.6648 | 42.8249 | 48.4627 | -685.7629
2028-09-25 15:00 | -1789.72 | 6.5106 | 43.0988 | 48.4627 | -524.5152
2028-09-26 16:00 | -1794.63 | 6.5162 | 43.1502 | 48.4627 | -525.9541
2028-09-27 17:00 | -1805.63 | 6.5537 | 43.1778 | 48.4627 | -529.1779
2028-09-28 18:00 | -2362.51 | 6.6648 | 42.9274 | 48.4627 | -692.3833
2028-09-29 19:00 | -2961.99 | 6.6648 | 42.5846 | 48.4627 | -868.0736
2028-09-30 20:00 | -3935.08 | 6.6648 | 42.0306 | 48.4627 | -1153.2581
2028-10-01 21:00 | -4355.13 | 6.6648 | 41.6919 | 48.4627 | -1276.3626
2028-10-02 22:00 | -5264.33 | 6.6648 | 41.1175 | 48.4627 | -1542.8228
2028-10-03 23:00 | -5570.13 | 6.6648 | 40.8088 | 48.4627 | -1632.444
2028-10-05 | -5726.16 | 6.6648 | 40.6039 | 48.4627 | -1678.1718
2028-10-06 01:00 | -5780.68 | 6.6648 | 40.4807 | 48.4627 | -1694.1501
2028-10-07 02:00 | -5819.8 | 6.6648 | 40.3913 | 48.4627 | -1705.615
2028-10-08 03:00 | -5734.45 | 6.6648 | 40.3701 | 48.4627 | -1680.6014
2028-10-09 04:00 | -5632.14 | 6.6648 | 40.3837 | 48.4627 | -1650.6173
2028-10-10 05:00 | -5150.38 | 6.6648 | 40.5998 | 48.4627 | -1509.4274
2028-10-11 06:00 | -4930.14 | 6.6648 | 40.7267 | 48.4627 | -1444.8814
2028-10-12 07:00 | -4493.05 | 6.6648 | 40.9649 | 48.4627 | -1316.783
2028-10-13 08:00 | -4671.27 | 6.6648 | 40.9206 | 48.4627 | -1369.0141
2028-10-14 09:00 | -4188.82 | 6.6648 | 41.1696 | 48.4627 | -1227.622
2028-10-15 10:00 | -3647.57 | 6.6648 | 41.4911 | 48.4627 | -1068.9972
2028-10-16 11:00 | -3157.79 | 6.6648 | 41.8148 | 48.4627 | -925.4569
2028-10-17 12:00 | -2646.54 | 6.6648 | 42.1593 | 48.4627 | -775.6243
2028-10-18 13:00 | -2308.83 | 6.6648 | 42.4249 | 48.4627 | -676.6513
2028-10-19 14:00 | -1931.29 | 6.6648 | 42.7103 | 48.4627 | -566.0052
2028-10-20 15:00 | -1122.25 | 4.043 | 42.8414 | 48.4627 | -328.899
2028-10-21 16:00 | -437.663 | 1.8517 | 43.1161 | 48.4627 | -128.2664
2028-10-22 17:00 | -266.396 | 1.4916 | 43.4616 | 48.4627 | -78.073
2028-10-23 18:00 | -553.293 | 2.5653 | 43.4522 | 48.4627 | -162.1542
2028-10-24 19:00 | -1186.19 | 4.741 | 43.3956 | 48.4627 | -347.638
2028-10-25 20:00 | -2519.57 | 6.6648 | 42.9717 | 48.4627 | -738.4131
2028-10-26 21:00 | -3327.83 | 6.6648 | 42.4586 | 48.4627 | -975.2907
2028-10-27 22:00 | -4615.97 | 6.6648 | 41.6824 | 48.4627 | -1352.8073
2028-10-28 23:00 | -5131.15 | 6.6648 | 41.2377 | 48.4627 | -1503.7916
2028-10-30 | -5476.69 | 6.6648 | 40.9039 | 48.4627 | -1605.0594
2028-10-31 01:00 | -5846.76 | 6.6648 | 40.5857 | 48.4627 | -1713.5162
2028-11-01 02:00 | -5650.56 | 6.6648 | 40.5655 | 48.4627 | -1656.0157
2028-11-02 03:00 | -5736.28 | 6.6648 | 40.451 | 48.4627 | -1681.1377
2028-11-03 04:00 | -5762.83 | 6.6648 | 40.3741 | 48.4627 | -1688.9188
2028-11-04 05:00 | -4754.7 | 6.6648 | 40.825 | 48.4627 | -1393.465
2028-11-05 06:00 | -3843.77 | 6.6648 | 41.3324 | 48.4627 | -1126.4978
2028-11-06 07:00 | -2635.69 | 6.6648 | 42.047 | 48.4627 | -772.4445
2028-11-07 08:00 | -1806.65 | 6.641 | 42.6299 | 48.4627 | -529.4768
2028-11-08 09:00 | -610.614 | 2.1691 | 42.7717 | 48.4627 | -178.9533
2028-11-09 10:00 | 2280.6 | 1 | 43.1867 | 48.4627 | 668.3779
2028-11-10 11:00 | 3073.31 | 1 | 60.9606 | 48.4627 | 900.6983
2028-11-11 12:00 | 3029.94 | 1 | 55.474 | 48.4627 | 887.9878
2028-11-12 13:00 | 3791.84 | 1.2081 | 55.5841 | 48.4627 | 1111.2786
2028-11-13 14:00 | 3975.52 | 1.3168 | 55.4376 | 48.4627 | 1165.1099
2028-11-14 15:00 | 5715.01 | 1.8295 | 56.0113 | 48.4627 | 1674.9041
2028-11-15 16:00 | 6079.11 | 1.9803 | 56.1416 | 48.4627 | 1781.6113
2028-11-16 17:00 | 5887.21 | 2.0224 | 55.8597 | 48.4627 | 1725.3709
2028-11-17 18:00 | 4512.1 | 1.4748 | 56.5432 | 48.4627 | 1322.366
2028-11-18 19:00 | 3266.02 | 1.0908 | 56.3487 | 48.4627 | 957.176
2028-11-19 20:00 | 2996.31 | 1 | 45.1536 | 48.4627 | 878.1318
2028-11-20 21:00 | 1925.27 | 1 | 45.5141 | 48.4627 | 564.2409
2028-11-21 22:00 | -627.051 | 2.9292 | 45.3482 | 48.4627 | -183.7705
2028-11-22 23:00 | -1011.79 | 3.9687 | 44.9169 | 48.4627 | -296.5264
2028-11-24 | -1302.47 | 4.8961 | 44.7049 | 48.4627 | -381.7163
2028-11-25 01:00 | -1500.59 | 5.506 | 44.5745 | 48.4627 | -439.7795
2028-11-26 02:00 | -1610.23 | 5.8373 | 44.4593 | 48.4627 | -471.9118
2028-11-27 03:00 | -1571.01 | 5.6642 | 44.358 | 48.4627 | -460.4176
2028-11-28 04:00 | -1522.14 | 5.5122 | 44.3176 | 48.4627 | -446.0952
2028-11-29 05:00 | -1056.44 | 3.8553 | 44.2872 | 48.4627 | -309.612
2028-11-30 06:00 | -654.914 | 2.6154 | 44.3835 | 48.4627 | -191.9363
2028-12-01 07:00 | -225.128 | 1.2337 | 44.6559 | 48.4627 | -65.9785
2028-12-02 08:00 | 36.6897 | 1 | 45.3205 | 48.4627 | 10.7527
2028-12-03 09:00 | 2305.26 | 1 | 44.602 | 48.4627 | 675.605
2028-12-04 10:00 | 3541.7 | 1.1682 | 55.947 | 48.4627 | 1037.9698
2028-12-05 11:00 | 4719.21 | 1.6569 | 55.5575 | 48.4627 | 1383.0639
2028-12-06 12:00 | 5688.05 | 1.8437 | 56.635 | 48.4627 | 1667.0029
2028-12-07 13:00 | 5897.75 | 1.9258 | 56.8381 | 48.4627 | 1728.4599
2028-12-08 14:00 | 6206.23 | 2.0298 | 57.0515 | 48.4627 | 1818.8665
2028-12-09 15:00 | 7124.24 | 2.3699 | 57.0562 | 48.4627 | 2087.9086
2028-12-10 16:00 | 7190.62 | 2.3434 | 57.4972 | 48.4627 | 2107.3627
2028-12-11 17:00 | 6279.5 | 2.072 | 57.5395 | 48.4627 | 1840.3398
2028-12-12 18:00 | 4463.64 | 1.4404 | 57.8177 | 48.4627 | 1308.1638
2028-12-13 19:00 | 3008.43 | 1 | 62.4191 | 48.4627 | 881.6838
2028-12-14 20:00 | 0 | 0 | 47.0938 | 48.4627 | 0
2028-12-15 21:00 | -765.127 | 3.0612 | 45.884 | 48.4627 | -224.2366
2028-12-16 22:00 | -1692.43 | 6.3191 | 45.5508 | 48.4627 | -496.0023
2028-12-17 23:00 | -2552.59 | 6.6648 | 44.9097 | 48.4627 | -748.0903
2028-12-19 | -2975.9 | 6.6648 | 44.4395 | 48.4627 | -872.1502
2028-12-20 01:00 | -3188.67 | 6.6648 | 44.1168 | 48.4627 | -934.5069
2028-12-21 02:00 | -3650.19 | 6.6648 | 43.7318 | 48.4627 | -1069.7651
2028-12-22 03:00 | -4060.98 | 6.6648 | 43.3512 | 48.4627 | -1190.1558
2028-12-23 04:00 | -4380.65 | 6.6648 | 43.015 | 48.4627 | -1283.8418
2028-12-24 05:00 | -4130.07 | 6.6648 | 42.9828 | 48.4627 | -1210.404
2028-12-25 06:00 | -2781.18 | 6.6648 | 43.5756 | 48.4627 | -815.0834
2028-12-26 07:00 | -1777.09 | 6.3814 | 44.0919 | 48.4627 | -520.8137
2028-12-27 08:00 | -1746.29 | 6.2467 | 44.1999 | 48.4627 | -511.7871
2028-12-28 09:00 | -1468.65 | 5.2538 | 44.2399 | 48.4627 | -430.4188
2028-12-29 10:00 | -859.895 | 3.181 | 44.3123 | 48.4627 | -252.0103
2028-12-30 11:00 | -705.569 | 2.8725 | 44.4801 | 48.4627 | -206.7819
2028-12-31 12:00 | -1100.46 | 4.3177 | 44.4937 | 48.4627 | -322.513
2029-01-01 13:00 | -1446.16 | 5.3934 | 44.4163 | 48.4627 | -423.8277
2029-01-02 14:00 | -1600.99 | 5.8284 | 44.3414 | 48.4627 | -469.2039
2029-01-03 15:00 | -1809.58 | 6.5375 | 44.2808 | 48.4627 | -530.3355
2029-01-04 16:00 | -675.609 | 2.3712 | 44.1839 | 48.4627 | -198.0015
2029-01-05 17:00 | -1101.7 | 4.3894 | 44.3558 | 48.4627 | -322.8764
2029-01-06 18:00 | -1630.67 | 6.0645 | 44.2757 | 48.4627 | -477.9022
2029-01-07 19:00 | -2150.7 | 6.6648 | 44.0192 | 48.4627 | -630.308
2029-01-08 20:00 | -2509.66 | 6.6648 | 43.7603 | 48.4627 | -735.5087
2029-01-09 21:00 | -2825.2 | 6.6648 | 43.53 | 48.4627 | -827.9844
2029-01-10 22:00 | -3421.54 | 6.6648 | 43.1406 | 48.4627 | -1002.7544
2029-01-11 23:00 | -5012.55 | 6.6648 | 42.2182 | 48.4627 | -1469.0334
2029-01-13 | -5500.21 | 6.6648 | 41.748 | 48.4627 | -1611.9524
2029-01-14 01:00 | -5916.67 | 6.6648 | 41.3592 | 48.4627 | -1734.0048
2029-01-15 02:00 | -5997.18 | 6.6648 | 41.1696 | 48.4627 | -1757.6
2029-01-16 03:00 | -6078.33 | 6.6648 | 41.0095 | 48.4627 | -1781.3827
2029-01-17 04:00 | -6208.77 | 6.6648 | 40.8315 | 48.4627 | -1819.6109
2029-01-18 05:00 | -6007.87 | 6.6648 | 40.842 | 48.4627 | -1760.7329
2029-01-19 06:00 | -4932.85 | 6.6648 | 41.3311 | 48.4627 | -1445.6756
2029-01-20 07:00 | -3922.12 | 6.6648 | 41.893 | 48.4627 | -1149.4599
2029-01-21 08:00 | -3843.34 | 6.6648 | 42.0336 | 48.4627 | -1126.3718
2029-01-22 09:00 | -2798.77 | 6.6648 | 42.6034 | 48.4627 | -820.2385
2029-01-23 10:00 | -1751.68 | 6.3808 | 43.2097 | 48.4627 | -513.3667
2029-01-24 11:00 | -911.37 | 3.2735 | 43.3712 | 48.4627 | -267.0962
2029-01-25 12:00 | -455.015 | 1.9923 | 43.7159 | 48.4627 | -133.3517
2029-01-26 13:00 | 0 | 1 | 44.64 | 48.4627 | 0
2029-01-27 14:00 | 2664.6 | 1 | 43.8816 | 48.4627 | 780.9172
2029-01-28 15:00 | 2775.55 | 1 | 44.2065 | 48.4627 | 813.4334
2029-01-29 16:00 | 2822.39 | 1.0075 | 54.9043 | 48.4627 | 827.1609
2029-01-30 17:00 | 2761.47 | 1 | 59.9543 | 48.4627 | 809.307
2029-01-31 18:00 | 2694.5 | 1 | 44.7499 | 48.4627 | 789.68
2029-02-01 19:00 | -305.48 | 1.7952 | 45.2177 | 48.4627 | -89.5274
2029-02-02 20:00 | -934.91 | 3.8333 | 44.7654 | 48.4627 | -273.9951
2029-02-03 21:00 | -1441.86 | 5.4254 | 44.5448 | 48.4627 | -422.5675
2029-02-04 22:00 | -1970.4 | 6.6648 | 44.3437 | 48.4627 | -577.4672
2029-02-05 23:00 | -3436.83 | 6.6648 | 43.4849 | 48.4627 | -1007.2354
2029-02-07 | -3992.83 | 6.6648 | 42.9805 | 48.4627 | -1170.183
2029-02-08 01:00 | -4422.68 | 6.6648 | 42.6068 | 48.4627 | -1296.1596
2029-02-09 02:00 | -4723.93 | 6.6648 | 42.3051 | 48.4627 | -1384.4472
2029-02-10 03:00 | -5083.56 | 6.6648 | 41.984 | 48.4627 | -1489.8444
2029-02-11 04:00 | -4844.8 | 6.6648 | 41.9651 | 48.4627 | -1419.8707
2029-02-12 05:00 | -4099.54 | 6.6648 | 42.2722 | 48.4627 | -1201.4566
2029-02-13 06:00 | -3682.24 | 6.6648 | 42.485 | 48.4627 | -1079.158
2029-02-14 07:00 | -3061.54 | 6.6648 | 42.8292 | 48.4627 | -897.2488
2029-02-15 08:00 | -2530.69 | 6.6648 | 43.1617 | 48.4627 | -741.672
2029-02-16 09:00 | -1347.37 | 4.8387 | 43.586 | 48.4627 | -394.8752
2029-02-17 10:00 | -322.982 | 1.3258 | 43.8543 | 48.4627 | -94.6567
2029-02-18 11:00 | 2761 | 1 | 43.9268 | 48.4627 | 809.1692
2029-02-19 12:00 | 2897.79 | 1 | 60.3928 | 48.4627 | 849.2584
2029-02-20 13:00 | 2912.52 | 1 | 60.6235 | 48.4627 | 853.5754
2029-02-21 14:00 | 2996.91 | 1 | 59.7743 | 48.4627 | 878.3076
2029-02-22 15:00 | 3635.18 | 1.2426 | 55.7585 | 48.4627 | 1065.3661
2029-02-23 16:00 | 4012 | 1.3296 | 56.2696 | 48.4627 | 1175.8011
2029-02-24 17:00 | 3464.48 | 1.1944 | 56.0183 | 48.4627 | 1015.3389
2029-02-25 18:00 | 2879.83 | 1 | 45.273 | 48.4627 | 843.9949
2029-02-26 19:00 | 1024.89 | 1 | 45.9356 | 48.4627 | 300.3656
2029-02-27 20:00 | -1011.48 | 4.2617 | 45.3574 | 48.4627 | -296.4355
2029-02-28 21:00 | -1681.52 | 6.1941 | 44.9953 | 48.4627 | -492.8049
2029-03-01 22:00 | -3057.39 | 6.6648 | 44.1678 | 48.4627 | -896.0326
2029-03-02 23:00 | -3629.69 | 6.6648 | 43.6209 | 48.4627 | -1063.7571
2029-03-04 | -4017.04 | 6.6648 | 43.197 | 48.4627 | -1177.2782
2029-03-05 01:00 | -4313.55 | 6.6648 | 42.8719 | 48.4627 | -1264.1767
2029-03-06 02:00 | -4413.34 | 6.6648 | 42.682 | 48.4627 | -1293.4223
2029-03-07 03:00 | -4442.66 | 6.6648 | 42.5473 | 48.4627 | -1302.0151
2029-03-08 04:00 | -4332.12 | 6.6648 | 42.511 | 48.4627 | -1269.619
2029-03-09 05:00 | -3680.31 | 6.6648 | 42.7746 | 48.4627 | -1078.5924
2029-03-10 06:00 | -3360.05 | 6.6648 | 42.9358 | 48.4627 | -984.7334
2029-03-11 07:00 | -2635.7 | 6.6648 | 43.3191 | 48.4627 | -772.4474
2029-03-12 08:00 | -2532.25 | 6.6648 | 43.4433 | 48.4627 | -742.1292
2029-03-13 09:00 | -1435.22 | 5.1415 | 43.8248 | 48.4627 | -420.6215
2029-03-14 10:00 | -440.04 | 1.704 | 44.0205 | 48.4627 | -128.963
2029-03-15 11:00 | 10.8625 | 1 | 45.0492 | 48.4627 | 3.1835
2029-03-16 12:00 | 2673.2 | 1 | 44.2673 | 48.4627 | 783.4376
2029-03-17 13:00 | 3153.79 | 1 | 61.973 | 48.4627 | 924.2846
2029-03-18 14:00 | 3118.64 | 1 | 61.7541 | 48.4627 | 913.9832
2029-03-19 15:00 | 3992.3 | 1.2765 | 56.4787 | 48.4627 | 1170.0276
2029-03-20 16:00 | 4527.7 | 1.4621 | 56.588 | 48.4627 | 1326.9379
2029-03-21 17:00 | 4398.74 | 1.4294 | 56.7307 | 48.4627 | 1289.1434
2029-03-22 18:00 | 3031.12 | 1 | 57.3189 | 48.4627 | 888.3336
2029-03-23 19:00 | 3049.85 | 1 | 45.3571 | 48.4627 | 893.8228
2029-03-24 20:00 | -443.505 | 2.243 | 45.7773 | 48.4627 | -129.9785
2029-03-25 21:00 | -1015.59 | 4.0364 | 45.314 | 48.4627 | -297.64
2029-03-26 22:00 | -2004.68 | 6.6648 | 44.9443 | 48.4627 | -587.5137
2029-03-27 23:00 | -2781.03 | 6.6648 | 44.3629 | 48.4627 | -815.0394
2029-03-29 | -3180.24 | 6.6648 | 43.9553 | 48.4627 | -932.0363
2029-03-30 01:00 | -3523.96 | 6.6648 | 43.5911 | 48.4627 | -1032.7707
2029-03-31 02:00 | -3712.04 | 6.6648 | 43.3666 | 48.4627 | -1087.8915
2029-04-01 03:00 | -3647.86 | 6.6648 | 43.2796 | 48.4627 | -1069.0822
2029-04-02 04:00 | -3600.17 | 6.6648 | 43.2179 | 48.4627 | -1055.1057
2029-04-03 05:00 | -2612.65 | 6.6648 | 43.6506 | 48.4627 | -765.6921
2029-04-04 06:00 | -2191.28 | 6.6648 | 43.9018 | 48.4627 | -642.2008
2029-04-05 07:00 | -1378.99 | 4.9015 | 44.0977 | 48.4627 | -404.1421
2029-04-06 08:00 | -933.589 | 3.4907 | 44.2482 | 48.4627 | -273.6079
2029-04-07 09:00 | 385.738 | 1 | 45.1255 | 48.4627 | 113.0486
2029-04-08 10:00 | 2580.91 | 1 | 58.7229 | 48.4627 | 756.3901
2029-04-09 11:00 | 3357.57 | 1.1202 | 55.9054 | 48.4627 | 984.0066
2029-04-10 12:00 | 4776.83 | 1.5185 | 56.6746 | 48.4627 | 1399.9507
2029-04-11 13:00 | 4905.89 | 1.614 | 56.6156 | 48.4627 | 1437.7744
2029-04-12 14:00 | 5017.28 | 1.6029 | 57.1552 | 48.4627 | 1470.4196
2029-04-13 15:00 | 6181.7 | 2.0522 | 56.9295 | 48.4627 | 1811.6774
2029-04-14 16:00 | 6622.51 | 2.1486 | 57.4075 | 48.4627 | 1940.8661
2029-04-15 17:00 | 6442.04 | 2.0841 | 57.6527 | 48.4627 | 1887.9756
2029-04-16 18:00 | 4742.12 | 1.4967 | 58.0507 | 48.4627 | 1389.7782
2029-04-17 19:00 | 3047.54 | 1 | 58.6168 | 48.4627 | 893.1458
2029-04-18 20:00 | 2762.16 | 1 | 46.2296 | 48.4627 | 809.5092
2029-04-19 21:00 | -223.647 | 1.4995 | 46.6108 | 48.4627 | -65.5445
2029-04-20 22:00 | -1204.8 | 4.7372 | 45.9394 | 48.4627 | -353.092
2029-04-21 23:00 | -2082.51 | 6.6648 | 45.4628 | 48.4627 | -610.3234
2029-04-23 | -2480.21 | 6.6648 | 45.027 | 48.4627 | -726.8778
2029-04-24 01:00 | -2584.07 | 6.6648 | 44.7909 | 48.4627 | -757.3162
2029-04-25 02:00 | -2840.36 | 6.6648 | 44.5098 | 48.4627 | -832.4273
2029-04-26 03:00 | -3039.82 | 6.6648 | 44.2855 | 48.4627 | -890.8833
2029-04-27 04:00 | -3138.29 | 6.6648 | 44.1183 | 48.4627 | -919.742
2029-04-28 05:00 | -2363.18 | 6.6648 | 44.4106 | 48.4627 | -692.5797
2029-04-29 06:00 | -1675.21 | 5.9336 | 44.6546 | 48.4627 | -490.9556
2029-04-30 07:00 | -737.111 | 2.6441 | 44.7115 | 48.4627 | -216.0259
2029-05-01 08:00 | -138.832 | 0.92033 | 45.2413 | 48.4627 | -40.6876
2029-05-02 09:00 | 2222.91 | 1 | 56.119 | 48.4627 | 651.4706
2029-05-03 10:00 | 3739.05 | 1.2902 | 55.9749 | 48.4627 | 1095.8074
2029-05-04 11:00 | 5388.47 | 1.7876 | 56.6895 | 48.4627 | 1579.2047
2029-05-05 12:00 | 5676.06 | 1.8666 | 57.1214 | 48.4627 | 1663.489
2029-05-06 13:00 | 5570.54 | 1.7861 | 57.636 | 48.4627 | 1632.5641
2029-05-07 14:00 | 5713.07 | 1.8825 | 57.528 | 48.4627 | 1674.3355
2029-05-08 15:00 | 7104.93 | 2.3619 | 57.5806 | 48.4627 | 2082.2494
2029-05-09 16:00 | 7360.79 | 2.4138 | 57.9695 | 48.4627 | 2157.2346
2029-05-10 17:00 | 7166.44 | 2.3999 | 57.9381 | 48.4627 | 2100.2762
2029-05-11 18:00 | 5621.02 | 1.7969 | 58.5413 | 48.4627 | 1647.3583
2029-05-12 19:00 | 3608.75 | 1.1696 | 58.3746 | 48.4627 | 1057.6202
2029-05-13 20:00 | 2963.6 | 1 | 46.7713 | 48.4627 | 868.5454
2029-05-14 21:00 | -129.207 | 1.1449 | 47.2834 | 48.4627 | -37.8668
2029-05-15 22:00 | -1068.4 | 4.2611 | 46.4588 | 48.4627 | -313.1171
2029-05-16 23:00 | -1705.45 | 6.1761 | 46.0628 | 48.4627 | -499.8181
2029-05-18 | -2001.36 | 6.6648 | 45.7487 | 48.4627 | -586.5407
2029-05-19 01:00 | -2408.46 | 6.6648 | 45.3648 | 48.4627 | -705.8499
2029-05-20 02:00 | -2801.28 | 6.6648 | 44.987 | 48.4627 | -820.9741
2029-05-21 03:00 | -2731.19 | 6.6648 | 44.8703 | 48.4627 | -800.4328
2029-05-22 04:00 | -2593.17 | 6.6648 | 44.8345 | 48.4627 | -759.9831
2029-05-23 05:00 | -1903.17 | 6.6648 | 45.1054 | 48.4627 | -557.7641
2029-05-24 06:00 | -1310.94 | 4.5725 | 45.093 | 48.4627 | -384.1986
2029-05-25 07:00 | -304.474 | 1.2697 | 45.2857 | 48.4627 | -89.2325
2029-05-26 08:00 | 1860.68 | 1 | 45.566 | 48.4627 | 545.3115
2029-05-27 09:00 | 2905.36 | 1 | 58.5774 | 48.4627 | 851.477
2029-05-28 10:00 | 4840.32 | 1.5826 | 57.052 | 48.4627 | 1418.5578
2029-05-29 11:00 | 6316.72 | 2.121 | 57.1025 | 48.4627 | 1851.2479
2029-05-30 12:00 | 7041.25 | 2.3439 | 57.5377 | 48.4627 | 2063.5867
2029-05-31 13:00 | 7402.91 | 2.4191 | 58.0252 | 48.4627 | 2169.5788
2029-06-01 14:00 | 7689.56 | 2.523 | 58.2175 | 48.4627 | 2253.5876
2029-06-02 15:00 | 8801.72 | 2.9126 | 58.3315 | 48.4627 | 2579.5295
2029-06-03 16:00 | 8883.82 | 2.9091 | 58.6949 | 48.4627 | 2603.5906
2029-06-04 17:00 | 8506.43 | 2.7896 | 58.8647 | 48.4627 | 2492.9885
2029-06-05 18:00 | 6740.95 | 2.1418 | 59.3109 | 48.4627 | 1975.5774
2029-06-06 19:00 | 4877.18 | 1.5244 | 59.4423 | 48.4627 | 1429.3604
2029-06-07 20:00 | 3071 | 1 | 64.3512 | 48.4627 | 900.0213
2029-06-08 21:00 | 3053.18 | 1 | 47.1842 | 48.4627 | 894.7987
2029-06-09 22:00 | -357.729 | 1.9126 | 47.4804 | 48.4627 | -104.84
2029-06-10 23:00 | -1055.54 | 4.1187 | 46.8389 | 48.4627 | -309.3482
2029-06-12 | -1582.68 | 5.7254 | 46.4603 | 48.4627 | -463.8377
2029-06-13 01:00 | -1965.31 | 6.6648 | 46.1778 | 48.4627 | -575.9755
2029-06-14 02:00 | -2187.68 | 6.6648 | 45.8749 | 48.4627 | -641.1457
2029-06-15 03:00 | -2246.4 | 6.6648 | 45.6534 | 48.4627 | -658.3549
2029-06-16 04:00 | -2567.84 | 6.6648 | 45.3654 | 48.4627 | -752.5596
2029-06-17 05:00 | -2370.39 | 6.6648 | 45.3269 | 48.4627 | -694.6927
2029-06-18 06:00 | -1422.95 | 4.9591 | 45.4724 | 48.4627 | -417.0255
2029-06-19 07:00 | -398.536 | 1.5463 | 45.59 | 48.4627 | -116.7994
2029-06-20 08:00 | 20.3442 | 1 | 46.5437 | 48.4627 | 5.9623
2029-06-21 09:00 | 2193.89 | 1 | 58.5548 | 48.4627 | 642.9657
2029-06-22 10:00 | 3537.56 | 1.2926 | 56.0954 | 48.4627 | 1036.7565
2029-06-23 11:00 | 5255.67 | 1.7632 | 57.1884 | 48.4627 | 1540.2848
2029-06-24 12:00 | 5765.3 | 2.0355 | 56.9886 | 48.4627 | 1689.6426
2029-06-25 13:00 | 6450.69 | 2.1422 | 57.8301 | 48.4627 | 1890.5106
2029-06-26 14:00 | 6704.96 | 2.3248 | 57.6323 | 48.4627 | 1965.0298
2029-06-27 15:00 | 6830.45 | 2.4039 | 57.6634 | 48.4627 | 2001.8073
2029-06-28 16:00 | 8660.61 | 3.0348 | 57.8419 | 48.4627 | 2538.1742
2029-06-29 17:00 | 7608.97 | 2.6619 | 58.1391 | 48.4627 | 2229.969
2029-06-30 18:00 | 6450.27 | 2.1161 | 58.8798 | 48.4627 | 1890.3875
2029-07-01 19:00 | 4824.49 | 1.5499 | 59.0737 | 48.4627 | 1413.9184
2029-07-02 20:00 | 3408.11 | 1.1041 | 58.884 | 48.4627 | 998.8184
2029-07-03 21:00 | 3084.72 | 1 | 63.7804 | 48.4627 | 904.0422
2029-07-04 22:00 | 3060.43 | 1 | 47.1158 | 48.4627 | 896.9235
2029-07-05 23:00 | -921.024 | 3.831 | 47.2894 | 48.4627 | -269.9255
2029-07-07 | -1579.75 | 5.7234 | 46.7443 | 48.4627 | -462.979
2029-07-08 01:00 | -2104.18 | 6.6648 | 46.3068 | 48.4627 | -616.6743
2029-07-09 02:00 | -2675.26 | 6.6648 | 45.8095 | 48.4627 | -784.0413
2029-07-10 03:00 | -3005.52 | 6.6648 | 45.4207 | 48.4627 | -880.831
2029-07-11 04:00 | -3325.47 | 6.6648 | 45.0275 | 48.4627 | -974.5991
2029-07-12 05:00 | -3291.36 | 6.6648 | 44.8808 | 48.4627 | -964.6024
2029-07-13 06:00 | -2509.43 | 6.6648 | 45.1532 | 48.4627 | -735.4413
2029-07-14 07:00 | -1839.84 | 6.4557 | 45.4349 | 48.4627 | -539.2039
2029-07-15 08:00 | -2309.73 | 6.6648 | 45.2444 | 48.4627 | -676.915
2029-07-16 09:00 | -2149.82 | 6.6648 | 45.2463 | 48.4627 | -630.05
2029-07-17 10:00 | -1783.73 | 6.2503 | 45.3043 | 48.4627 | -522.7597
2029-07-18 11:00 | -731.333 | 2.5639 | 45.2959 | 48.4627 | -214.3325
2029-07-19 12:00 | 364.456 | 1 | 46.2057 | 48.4627 | 106.8115
2029-07-20 13:00 | 2694.94 | 1 | 45.5202 | 48.4627 | 789.8089
2029-07-21 14:00 | 3026.62 | 1 | 45.6849 | 48.4627 | 887.0148
2029-07-22 15:00 | 3001.36 | 1 | 62.9289 | 48.4627 | 879.6118
2029-07-23 16:00 | 4393.19 | 1.4492 | 57.2424 | 48.4627 | 1287.5169
2029-07-24 17:00 | 2934.61 | 1.0272 | 56.885 | 48.4627 | 860.0493
2029-07-25 18:00 | 2844.42 | 1 | 46.2487 | 48.4627 | 833.6172
2029-07-26 19:00 | 0 | 0 | 47.2151 | 48.4627 | 0
2029-07-27 20:00 | -703.762 | 2.8135 | 46.1268 | 48.4627 | -206.2523
2029-07-28 21:00 | -1196.05 | 4.5675 | 45.902 | 48.4627 | -350.5277
2029-07-29 22:00 | -1739.78 | 6.2955 | 45.7014 | 48.4627 | -509.8792
2029-07-30 23:00 | -3342.1 | 6.6648 | 44.8048 | 48.4627 | -979.4728
2029-08-01 | -3868.04 | 6.6648 | 44.2778 | 48.4627 | -1133.6106
2029-08-02 01:00 | -4448.34 | 6.6648 | 43.7812 | 48.4627 | -1303.6798
2029-08-03 02:00 | -4729.84 | 6.6648 | 43.4527 | 48.4627 | -1386.1793
2029-08-04 03:00 | -4900.55 | 6.6648 | 43.1998 | 48.4627 | -1436.2094
2029-08-05 04:00 | -4815.26 | 6.6648 | 43.0862 | 48.4627 | -1411.2134
2029-08-06 05:00 | -3714.1 | 6.6648 | 43.5494 | 48.4627 | -1088.4953
2029-08-07 06:00 | -3179.83 | 6.6648 | 43.8353 | 48.4627 | -931.9162
2029-08-08 07:00 | -2309.65 | 6.6648 | 44.3233 | 48.4627 | -676.8916
2029-08-09 08:00 | -1932.47 | 6.6648 | 44.6073 | 48.4627 | -566.3511
2029-08-10 09:00 | -1015.37 | 3.5463 | 44.6968 | 48.4627 | -297.5756
2029-08-11 10:00 | 1843.12 | 1 | 45.1691 | 48.4627 | 540.1652
2029-08-12 11:00 | 3067.42 | 1 | 45.0968 | 48.4627 | 898.9721
2029-08-13 12:00 | 3021.69 | 1 | 57.3392 | 48.4627 | 885.5699
2029-08-14 13:00 | 3572.42 | 1.1605 | 57.0437 | 48.4627 | 1046.973
2029-08-15 14:00 | 4058.23 | 1.3666 | 56.8644 | 48.4627 | 1189.3498
2029-08-16 15:00 | 5584.56 | 1.8323 | 57.326 | 48.4627 | 1636.673
2029-08-17 16:00 | 6068.7 | 2.0188 | 57.4412 | 48.4627 | 1778.5604
2029-08-18 17:00 | 5873.92 | 1.9441 | 57.7042 | 48.4627 | 1721.476
2029-08-19 18:00 | 4408.16 | 1.4259 | 58.0801 | 48.4627 | 1291.9042
2029-08-20 19:00 | 2931.58 | 1 | 61.3938 | 48.4627 | 859.1613
2029-08-21 20:00 | 0 | 0 | 47.5241 | 48.4627 | 0
2029-08-22 21:00 | -685.551 | 2.769 | 46.3745 | 48.4627 | -200.9152
2029-08-23 22:00 | -1779.97 | 6.6108 | 46.0548 | 48.4627 | -521.6577
2029-08-24 23:00 | -2550.05 | 6.6648 | 45.4251 | 48.4627 | -747.3459
2029-08-26 | -2929.06 | 6.6648 | 45.0014 | 48.4627 | -858.4227
2029-08-27 01:00 | -3185.08 | 6.6648 | 44.6852 | 48.4627 | -933.4548
2029-08-28 02:00 | -3328.99 | 6.6648 | 44.4823 | 48.4627 | -975.6307
2029-08-29 03:00 | -3408.68 | 6.6648 | 44.3181 | 48.4627 | -998.9855
2029-08-30 04:00 | -3472.45 | 6.6648 | 44.1803 | 48.4627 | -1017.6746
2029-08-31 05:00 | -2519.23 | 6.6648 | 44.5695 | 48.4627 | -738.3134
2029-09-01 06:00 | -1931.33 | 6.6648 | 44.8838 | 48.4627 | -566.0169
2029-09-02 07:00 | -1251.59 | 4.373 | 44.9396 | 48.4627 | -366.8048
2029-09-03 08:00 | -787.228 | 2.9928 | 45.1045 | 48.4627 | -230.7138
2029-09-04 09:00 | 1642.28 | 1 | 45.5293 | 48.4627 | 481.3048
2029-09-05 10:00 | 2979.42 | 1 | 61.3436 | 48.4627 | 873.1818
2029-09-06 11:00 | 3576.3 | 1.18 | 56.9075 | 48.4627 | 1048.1101
2029-09-07 12:00 | 4287.95 | 1.408 | 57.1895 | 48.4627 | 1256.6741
2029-09-08 13:00 | 4820.25 | 1.5908 | 57.3548 | 48.4627 | 1412.6758
2029-09-09 14:00 | 5014.12 | 1.7032 | 57.2797 | 48.4627 | 1469.4935
2029-09-10 15:00 | 6098.62 | 2.0406 | 57.5798 | 48.4627 | 1787.3291
2029-09-11 16:00 | 6631.96 | 2.1433 | 58.1442 | 48.4627 | 1943.6356
2029-09-12 17:00 | 6496.99 | 2.1277 | 58.2043 | 48.4627 | 1904.0798
2029-09-13 18:00 | 4938.52 | 1.5773 | 58.5996 | 48.4627 | 1447.3373
2029-09-14 19:00 | 3154.83 | 1.0257 | 58.3867 | 48.4627 | 924.5894
2029-09-15 20:00 | 2894.43 | 1 | 46.8637 | 48.4627 | 848.2737
2029-09-16 21:00 | -187.735 | 1.355 | 47.3117 | 48.4627 | -55.0197
2029-09-17 22:00 | -1186.33 | 4.6411 | 46.5843 | 48.4627 | -347.679
2029-09-18 23:00 | -1950 | 6.6648 | 46.1677 | 48.4627 | -571.4886
2029-09-20 | -2597.91 | 6.6648 | 45.6109 | 48.4627 | -761.3723
2029-09-21 01:00 | -2970.03 | 6.6648 | 45.214 | 48.4627 | -870.4299
2029-09-22 02:00 | -3239.55 | 6.6648 | 44.8823 | 48.4627 | -949.4184
2029-09-23 03:00 | -3207.03 | 6.6648 | 44.7513 | 48.4627 | -939.8877
2029-09-24 04:00 | -3271.97 | 6.6648 | 44.6063 | 48.4627 | -958.9197
2029-09-25 05:00 | -2244.58 | 6.6648 | 45.0232 | 48.4627 | -657.8215
2029-09-26 06:00 | -1696.96 | 5.9533 | 45.2132 | 48.4627 | -497.3299
2029-09-27 07:00 | -1128.66 | 4.0006 | 45.2649 | 48.4627 | -330.7776
2029-09-28 08:00 | -1208.48 | 4.5097 | 45.3671 | 48.4627 | -354.1705
2029-09-29 09:00 | 0 | 0 | 46.2964 | 48.4627 | 0
2029-09-30 10:00 | 2254.65 | 1 | 54.2987 | 48.4627 | 660.7727
2029-10-01 11:00 | 3994.49 | 1.3994 | 56.3607 | 48.4627 | 1170.6695
2029-10-02 12:00 | 3899.6 | 1.2838 | 57.2942 | 48.4627 | 1142.8599
2029-10-03 13:00 | 3633.41 | 1.1845 | 57.5663 | 48.4627 | 1064.8474
2029-10-04 14:00 | 3876.8 | 1.237 | 57.9002 | 48.4627 | 1136.1779
2029-10-05 15:00 | 5430.85 | 1.7488 | 57.9182 | 48.4627 | 1591.625
2029-10-06 16:00 | 6072.76 | 1.9826 | 57.9981 | 48.4627 | 1779.7503
2029-10-07 17:00 | 6570.38 | 2.0945 | 58.4316 | 48.4627 | 1925.5883
2029-10-08 18:00 | 5361.17 | 1.6752 | 58.8232 | 48.4627 | 1571.2038
2029-10-09 19:00 | 3431.01 | 1.1047 | 58.5412 | 48.4627 | 1005.5298
2029-10-10 20:00 | 2972.02 | 1 | 46.9077 | 48.4627 | 871.0131
2029-10-11 21:00 | 0 | 0 | 47.8606 | 48.4627 | 0
2029-10-12 22:00 | -1122.43 | 3.9486 | 46.5855 | 48.4627 | -328.9518
2029-10-13 23:00 | -1635.63 | 5.9552 | 46.3118 | 48.4627 | -479.3558
2029-10-15 | -1946.39 | 6.6648 | 46.0425 | 48.4627 | -570.4306
2029-10-16 01:00 | -2153.7 | 6.6648 | 45.7809 | 48.4627 | -631.1872
2029-10-17 02:00 | -2411.02 | 6.6648 | 45.5063 | 48.4627 | -706.6002
2029-10-18 03:00 | -2427.82 | 6.6648 | 45.3811 | 48.4627 | -711.5238
2029-10-19 04:00 | -2468.93 | 6.6648 | 45.2712 | 48.4627 | -723.572
2029-10-20 05:00 | -1635.94 | 5.7216 | 45.469 | 48.4627 | -479.4467
2029-10-21 06:00 | -1251.41 | 4.4476 | 45.4893 | 48.4627 | -366.7521
2029-10-22 07:00 | -633.721 | 2.4268 | 45.5813 | 48.4627 | -185.7253
2029-10-23 08:00 | -248.863 | 1.3196 | 45.8837 | 48.4627 | -72.9345
2029-10-24 09:00 | 1854.63 | 1 | 45.965 | 48.4627 | 543.5384
2029-10-25 10:00 | 2763.52 | 1 | 62.0152 | 48.4627 | 809.9078
2029-10-26 11:00 | 3341.86 | 1.0715 | 57.5985 | 48.4627 | 979.4025
2029-10-27 12:00 | 4080.04 | 1.3118 | 57.7592 | 48.4627 | 1195.7417
2029-10-28 13:00 | 4433.07 | 1.4159 | 58.022 | 48.4627 | 1299.2046
2029-10-29 14:00 | 5002.36 | 1.6094 | 58.1229 | 48.4627 | 1466.047
2029-10-30 15:00 | 6882.99 | 2.2389 | 58.1634 | 48.4627 | 2017.2052
2029-10-31 16:00 | 7098.13 | 2.3225 | 58.3926 | 48.4627 | 2080.2566
2029-11-01 17:00 | 7012.75 | 2.2543 | 58.7822 | 48.4627 | 2055.2341
2029-11-02 18:00 | 5999.53 | 1.8645 | 59.2808 | 48.4627 | 1758.2887
2029-11-03 19:00 | 4360.42 | 1.3513 | 59.353 | 48.4627 | 1277.913
2029-11-04 20:00 | 3143.63 | 1 | 47.2785 | 48.4627 | 921.307
2029-11-05 21:00 | 3037.39 | 1 | 47.1803 | 48.4627 | 890.1711
2029-11-06 22:00 | -335.881 | 1.8379 | 47.5325 | 48.4627 | -98.437
2029-11-07 23:00 | -668.523 | 2.7952 | 46.9843 | 48.4627 | -195.9248
2029-11-09 | -832.388 | 3.2623 | 46.6941 | 48.4627 | -243.9488
2029-11-10 01:00 | -950.489 | 3.6234 | 46.5405 | 48.4627 | -278.5608
2029-11-11 02:00 | -936.028 | 3.5378 | 46.424 | 48.4627 | -274.3227
2029-11-12 03:00 | -806.632 | 3.1048 | 46.328 | 48.4627 | -236.4005
2029-11-13 04:00 | -541.629 | 2.2399 | 46.3453 | 48.4627 | -158.7358
2029-11-14 05:00 | 136.182 | 1 | 47.0962 | 48.4627 | 39.911
2029-11-15 06:00 | 1849.28 | 1 | 46.547 | 48.4627 | 541.9705
2029-11-16 07:00 | 2698.92 | 1.0136 | 56.3976 | 48.4627 | 790.9754
2029-11-17 08:00 | 3042.19 | 1.0192 | 57.6416 | 48.4627 | 891.5779
2029-11-18 09:00 | 4892.9 | 1.5685 | 58.2154 | 48.4627 | 1433.9674
2029-11-19 10:00 | 6544.13 | 2.2735 | 57.6781 | 48.4627 | 1917.8952
2029-11-20 11:00 | 8079.52 | 2.868 | 57.8129 | 48.4627 | 2367.8736
2029-11-21 12:00 | 9038.49 | 3.079 | 58.5629 | 48.4627 | 2648.9199
2029-11-22 13:00 | 9473.67 | 3.1901 | 59.0037 | 48.4627 | 2776.4586
2029-11-23 14:00 | 9762.3 | 3.2453 | 59.4161 | 48.4627 | 2861.0477
2029-11-24 15:00 | 11236.2 | 3.635 | 59.9198 | 48.4627 | 3293.0052
2029-11-25 16:00 | 10600.2 | 3.2955 | 60.6599 | 48.4627 | 3106.612
2029-11-26 17:00 | 10461.1 | 3.3173 | 60.6015 | 48.4627 | 3065.8458
2029-11-27 18:00 | 8547.2 | 2.7224 | 60.6697 | 48.4627 | 2504.937
2029-11-28 19:00 | 6828.96 | 2.1366 | 60.8097 | 48.4627 | 2001.3706
2029-11-29 20:00 | 4399.05 | 1.3503 | 60.8827 | 48.4627 | 1289.2343
2029-11-30 21:00 | 3149.05 | 1.0094 | 60.1289 | 48.4627 | 922.8955
2029-12-01 22:00 | 3082.54 | 1 | 48.2677 | 48.4627 | 903.4033
2029-12-02 23:00 | 0 | 0 | 49.1676 | 48.4627 | 0
2029-12-04 | -366.919 | 1.5138 | 47.9429 | 48.4627 | -107.5333
2029-12-05 01:00 | -525.672 | 2.3206 | 47.7126 | 48.4627 | -154.0593
2029-12-06 02:00 | -650.314 | 2.6615 | 47.4809 | 48.4627 | -190.5882
2029-12-07 03:00 | -884.772 | 3.4285 | 47.2744 | 48.4627 | -259.3011
2029-12-08 04:00 | -1082.6 | 4.0293 | 47.0697 | 48.4627 | -317.2787
2029-12-09 05:00 | -766.87 | 2.8845 | 46.9484 | 48.4627 | -224.7474
2029-12-10 06:00 | 1642.6 | 1 | 47.2179 | 48.4627 | 481.3985
2029-12-11 07:00 | 3270.69 | 1.1683 | 57.4455 | 48.4627 | 958.5446
2029-12-12 08:00 | 3485.4 | 1.1764 | 58.2032 | 48.4627 | 1021.4699
2029-12-13 09:00 | 5231.6 | 1.684 | 58.816 | 48.4627 | 1533.2306
2029-12-14 10:00 | 6738.96 | 2.2976 | 58.4696 | 48.4627 | 1974.9942
2029-12-15 11:00 | 8360.9 | 2.7799 | 59.047 | 48.4627 | 2450.3379
2029-12-16 12:00 | 9254.23 | 3.0579 | 59.446 | 48.4627 | 2712.1471
2029-12-17 13:00 | 9254.21 | 3.0596 | 59.7342 | 48.4627 | 2712.1412
2029-12-18 14:00 | 6507.25 | 2.0117 | 60.6614 | 48.4627 | 1907.0867
2029-12-19 15:00 | 6995.47 | 2.2557 | 60.0922 | 48.4627 | 2050.1699
2029-12-20 16:00 | 9460.32 | 3.0821 | 60.0035 | 48.4627 | 2772.5461
2029-12-21 17:00 | 7990.97 | 2.4577 | 60.9035 | 48.4627 | 2341.9221
2029-12-22 18:00 | 5997.82 | 1.8338 | 60.9763 | 48.4627 | 1757.7875
2029-12-23 19:00 | 4571.32 | 1.4182 | 60.6286 | 48.4627 | 1339.7216
2029-12-24 20:00 | 3552.08 | 1.0925 | 60.5709 | 48.4627 | 1041.0119
2029-12-25 21:00 | 3149.82 | 1 | 64.4083 | 48.4627 | 923.1211
2029-12-26 22:00 | 3156.9 | 1 | 48.1663 | 48.4627 | 925.1961
2029-12-27 23:00 | -592.109 | 2.6523 | 48.3954 | 48.4627 | -173.53
2029-12-29 | -1073.68 | 4.0414 | 47.8242 | 48.4627 | -314.6645
2029-12-30 01:00 | -1413.78 | 5.0667 | 47.4812 | 48.4627 | -414.338
2029-12-31 02:00 | -1482.43 | 5.1993 | 47.2809 | 48.4627 | -434.4573
2030-01-01 03:00 | -1576.41 | 5.5205 | 47.1222 | 48.4627 | -462.0002
2030-01-02 04:00 | -1710.43 | 5.9625 | 46.9429 | 48.4627 | -501.2776
2030-01-03 05:00 | -1497.43 | 5.1822 | 46.8218 | 48.4627 | -438.8534
2030-01-04 06:00 | -494.484 | 1.8243 | 46.8056 | 48.4627 | -144.919
2030-01-05 07:00 | 1811.22 | 1 | 47.1335 | 48.4627 | 530.8162
2030-01-06 08:00 | 2624.6 | 1 | 47.0672 | 48.4627 | 769.1943
2030-01-07 09:00 | 3058.06 | 1 | 63.5279 | 48.4627 | 896.2289
2030-01-08 10:00 | 4698.92 | 1.4672 | 59.0492 | 48.4627 | 1377.1175
2030-01-09 11:00 | 5840.79 | 1.9055 | 58.8371 | 48.4627 | 1711.7666
2030-01-10 12:00 | 4974.58 | 1.5606 | 59.5113 | 48.4627 | 1457.9055
2030-01-11 13:00 | 3016.96 | 1 | 63.2754 | 48.4627 | 884.1837
2030-01-12 14:00 | 3129.9 | 1 | 47.574 | 48.4627 | 917.2831
2030-01-13 15:00 | 3107.39 | 1 | 47.5519 | 48.4627 | 910.6861
2030-01-14 16:00 | 4187.75 | 1.2736 | 59.738 | 48.4627 | 1227.3084
2030-01-15 17:00 | 3102.58 | 1 | 61.1215 | 48.4627 | 909.2764
2030-01-16 18:00 | 3017.88 | 1 | 47.5326 | 48.4627 | 884.4533
2030-01-17 19:00 | 3116.49 | 1 | 47.4694 | 48.4627 | 913.3531
2030-01-18 20:00 | 3117.8 | 1 | 47.4758 | 48.4627 | 913.737
2030-01-19 21:00 | 2205.82 | 1 | 47.7973 | 48.4627 | 646.462
2030-01-20 22:00 | 146.54 | 1 | 48.3889 | 48.4627 | 42.9466
2030-01-21 23:00 | -1118.9 | 4.4258 | 47.3385 | 48.4627 | -327.9172
2030-01-23 | -1478.86 | 5.2847 | 46.9981 | 48.4627 | -433.4111
2030-01-24 01:00 | -1624.56 | 5.7035 | 46.816 | 48.4627 | -476.1115
2030-01-25 02:00 | -1690.16 | 5.8947 | 46.6762 | 48.4627 | -495.337
2030-01-26 03:00 | -1787.54 | 6.2222 | 46.5655 | 48.4627 | -523.8763
2030-01-27 04:00 | -1869.91 | 6.4805 | 46.4751 | 48.4627 | -548.0165
2030-01-28 05:00 | -1768.43 | 6.1006 | 46.4087 | 48.4627 | -518.2757
2030-01-29 06:00 | -853.297 | 2.9643 | 46.3643 | 48.4627 | -250.0767
2030-01-30 07:00 | -265.637 | 1.3025 | 46.6739 | 48.4627 | -77.8505
2030-01-31 08:00 | -516.744 | 2.346 | 46.6587 | 48.4627 | -151.4427
2030-02-01 09:00 | -119.125 | 0.87188 | 46.9125 | 48.4627 | -34.9121
2030-02-02 10:00 | 1560.03 | 1 | 46.8563 | 48.4627 | 457.1997
2030-02-03 11:00 | 2558.87 | 1 | 56.962 | 48.4627 | 749.9308
2030-02-04 12:00 | 3349.58 | 1.1737 | 57.3834 | 48.4627 | 981.665
2030-02-05 13:00 | 3753.37 | 1.2449 | 58.0934 | 48.4627 | 1100.0042
2030-02-06 14:00 | 5102.99 | 1.6464 | 58.5334 | 48.4627 | 1495.5387
2030-02-07 15:00 | 5393.34 | 1.7344 | 58.812 | 48.4627 | 1580.6319
2030-02-08 16:00 | 7309.65 | 2.5054 | 58.3314 | 48.4627 | 2142.2469
2030-02-09 17:00 | 5376.13 | 1.718 | 59.3578 | 48.4627 | 1575.5882
2030-02-10 18:00 | 4363.85 | 1.3455 | 59.7609 | 48.4627 | 1278.9182
2030-02-11 19:00 | 3238.6 | 1 | 61.6572 | 48.4627 | 949.14
2030-02-12 20:00 | 3088.43 | 1 | 64.9597 | 48.4627 | 905.1295
2030-02-13 21:00 | 3171.02 | 1 | 47.5174 | 48.4627 | 929.3342
2030-02-14 22:00 | 3047.6 | 1 | 47.5373 | 48.4627 | 893.1634
2030-02-15 23:00 | -730.224 | 3.1785 | 47.7941 | 48.4627 | -214.0075
2030-02-17 | -1122.22 | 4.1791 | 47.3054 | 48.4627 | -328.8902
2030-02-18 01:00 | -1371.2 | 4.9368 | 47.0519 | 48.4627 | -401.8591
2030-02-19 02:00 | -1502.23 | 5.3139 | 46.8893 | 48.4627 | -440.2602
2030-02-20 03:00 | -1363.26 | 4.7997 | 46.7424 | 48.4627 | -399.5321
2030-02-21 04:00 | -1284.93 | 4.5967 | 46.6271 | 48.4627 | -376.5758
2030-02-22 05:00 | -749.943 | 2.7743 | 46.6075 | 48.4627 | -219.7866
2030-02-23 06:00 | -262.062 | 1.3095 | 46.8477 | 48.4627 | -76.8028
2030-02-24 07:00 | -54.8712 | 0.76883 | 47.3161 | 48.4627 | -16.0812
2030-02-25 08:00 | 14.4631 | 1 | 47.5741 | 48.4627 | 4.2387
2030-02-26 09:00 | 1734.3 | 1 | 57.1953 | 48.4627 | 508.2732
2030-02-27 10:00 | 2739 | 1.0746 | 56.3475 | 48.4627 | 802.7217
2030-02-28 11:00 | 4464.95 | 1.5297 | 57.7832 | 48.4627 | 1308.5477
2030-03-01 12:00 | 5443.38 | 1.9202 | 57.7562 | 48.4627 | 1595.2972
2030-03-02 13:00 | 6065.75 | 2.0088 | 58.6445 | 48.4627 | 1777.6958
2030-03-03 14:00 | 5541.47 | 1.7604 | 59.3125 | 48.4627 | 1624.0445
2030-03-04 15:00 | 6027.32 | 1.9032 | 59.4775 | 48.4627 | 1766.4331
2030-03-05 16:00 | 5610.18 | 1.7998 | 59.4386 | 48.4627 | 1644.1815
2030-03-06 17:00 | 4819.26 | 1.5252 | 59.6443 | 48.4627 | 1412.3857
2030-03-07 18:00 | 3518.69 | 1.1309 | 59.4571 | 48.4627 | 1031.2262
2030-03-08 19:00 | 3140.49 | 1 | 47.7445 | 48.4627 | 920.3868
2030-03-09 20:00 | 0 | 0 | 48.7566 | 48.4627 | 0
2030-03-10 21:00 | -340.825 | 1.7007 | 47.7314 | 48.4627 | -99.8859
2030-03-11 22:00 | -1219.96 | 4.6749 | 47.29 | 48.4627 | -357.535
2030-03-12 23:00 | -1638.2 | 5.8056 | 47.0075 | 48.4627 | -480.109
2030-03-14 | -1857.82 | 6.4556 | 46.7972 | 48.4627 | -544.4733
2030-03-15 01:00 | -2027.48 | 6.6648 | 46.5701 | 48.4627 | -594.1957
2030-03-16 02:00 | -2203.62 | 6.6648 | 46.3679 | 48.4627 | -645.8173
2030-03-17 03:00 | -2263.63 | 6.6648 | 46.2215 | 48.4627 | -663.4045
2030-03-18 04:00 | -2241.5 | 6.6648 | 46.1401 | 48.4627 | -656.9188
2030-03-19 05:00 | -1762.71 | 6.0902 | 46.225 | 48.4627 | -516.5993
2030-03-20 06:00 | -1569.43 | 5.4671 | 46.2137 | 48.4627 | -459.9545
2030-03-21 07:00 | -1267.8 | 4.487 | 46.21 | 48.4627 | -371.5555
2030-03-22 08:00 | -1584.7 | 5.7077 | 46.2465 | 48.4627 | -464.4297
2030-03-23 09:00 | -1252.17 | 4.4055 | 46.1873 | 48.4627 | -366.9748
2030-03-24 10:00 | -1000.35 | 3.6799 | 46.2274 | 48.4627 | -293.1736
2030-03-25 11:00 | -552.711 | 2.2127 | 46.3026 | 48.4627 | -161.9836
2030-03-26 12:00 | -318.612 | 1.5734 | 46.4811 | 48.4627 | -93.376
2030-03-27 13:00 | 168.448 | 1 | 47.1212 | 48.4627 | 49.3672
2030-03-28 14:00 | 2429.85 | 1 | 46.3943 | 48.4627 | 712.1187
2030-03-29 15:00 | 3011.41 | 1 | 60.143 | 48.4627 | 882.5572
2030-03-30 16:00 | 3807.96 | 1.2069 | 58.2971 | 48.4627 | 1116.0029
2030-03-31 17:00 | 4106.12 | 1.3277 | 58.2612 | 48.4627 | 1203.385
2030-04-01 18:00 | 3089.42 | 1 | 60.6124 | 48.4627 | 905.4196
2030-04-02 19:00 | 3033.17 | 1 | 46.9447 | 48.4627 | 888.9344
2030-04-03 20:00 | -294.024 | 1.6888 | 47.4287 | 48.4627 | -86.1699
2030-04-04 21:00 | -824.209 | 3.3456 | 46.9108 | 48.4627 | -241.5518
2030-04-05 22:00 | -1934.39 | 6.6648 | 46.5644 | 48.4627 | -566.9137
2030-04-06 23:00 | -2472.13 | 6.6648 | 46.0921 | 48.4627 | -724.5098
2030-04-08 | -2808.44 | 6.6648 | 45.7451 | 48.4627 | -823.0725
2030-04-09 01:00 | -3086.47 | 6.6648 | 45.4427 | 48.4627 | -904.5551
2030-04-10 02:00 | -3202.53 | 6.6648 | 45.2595 | 48.4627 | -938.5689
2030-04-11 03:00 | -3054.83 | 6.6648 | 45.2228 | 48.4627 | -895.2823
2030-04-12 04:00 | -2864.12 | 6.6648 | 45.2456 | 48.4627 | -839.3907
2030-04-13 05:00 | -2117.5 | 6.6648 | 45.5693 | 48.4627 | -620.578
2030-04-14 06:00 | -1642.98 | 5.7116 | 45.6866 | 48.4627 | -481.5099
2030-04-15 07:00 | -1081.2 | 3.8351 | 45.7326 | 48.4627 | -316.8684
2030-04-16 08:00 | -1187.62 | 4.4229 | 45.8523 | 48.4627 | -348.0571
2030-04-17 09:00 | -752.602 | 2.8327 | 45.8857 | 48.4627 | -220.5659
2030-04-18 10:00 | 12.2014 | 1 | 46.8411 | 48.4627 | 3.5759
2030-04-19 11:00 | 1053.36 | 1 | 46.5873 | 48.4627 | 308.7093
2030-04-20 12:00 | 2897.91 | 1 | 46.1109 | 48.4627 | 849.2936
2030-04-21 13:00 | 0 | 0 | 47.3647 | 48.4627 | 0
2030-04-22 14:00 | -12.541 | 0.69359 | 47.1784 | 48.4627 | -3.6754
2030-04-23 15:00 | 2575.07 | 1.2162 | 54.3619 | 48.4627 | 754.6785
2030-04-24 16:00 | 2655.73 | 1 | 57.0699 | 48.4627 | 778.3176
2030-04-25 17:00 | 2962.93 | 1 | 61.7115 | 48.4627 | 868.3491
2030-04-26 18:00 | 3041.49 | 1 | 46.5492 | 48.4627 | 891.3727
2030-04-27 19:00 | 1267.83 | 1 | 47.2588 | 48.4627 | 371.5643
2030-04-28 20:00 | -719.893 | 3.1728 | 46.8557 | 48.4627 | -210.9798
2030-04-29 21:00 | -1155.29 | 4.3453 | 46.4942 | 48.4627 | -338.5821
2030-04-30 22:00 | -2041.4 | 6.6648 | 46.212 | 48.4627 | -598.2753
2030-05-01 23:00 | -2414.08 | 6.6648 | 45.8477 | 48.4627 | -707.497
2030-05-03 | -2174.51 | 6.6648 | 45.7914 | 48.4627 | -637.286
2030-05-04 01:00 | -2217.89 | 6.6648 | 45.706 | 48.4627 | -649.9994
2030-05-05 02:00 | -2247.31 | 6.6648 | 45.6564 | 48.4627 | -658.6215
2030-05-06 03:00 | -2119.94 | 6.6648 | 45.6653 | 48.4627 | -621.2931
2030-05-07 04:00 | -2126.89 | 6.6648 | 45.6337 | 48.4627 | -623.3299
2030-05-08 05:00 | -1319.4 | 4.5671 | 45.7007 | 48.4627 | -386.678
2030-05-09 06:00 | -794.814 | 2.966 | 45.8044 | 48.4627 | -232.937
2030-05-10 07:00 | 334.756 | 1 | 46.6637 | 48.4627 | 98.1073
2030-05-11 08:00 | 2315.52 | 1 | 46.1376 | 48.4627 | 678.6119
2030-05-12 09:00 | 2902.7 | 1 | 46.2188 | 48.4627 | 850.6974
2030-05-13 10:00 | 3514.81 | 1.1524 | 57.7958 | 48.4627 | 1030.0891
2030-05-14 11:00 | 4051.22 | 1.3497 | 57.7958 | 48.4627 | 1187.2954
2030-05-15 12:00 | 4918.47 | 1.579 | 58.3726 | 48.4627 | 1441.4613
2030-05-16 13:00 | 5117.77 | 1.6732 | 58.416 | 48.4627 | 1499.8703
2030-05-17 14:00 | 5602.39 | 1.8455 | 58.5057 | 48.4627 | 1641.8984
2030-05-18 15:00 | 6737.85 | 2.2424 | 58.561 | 48.4627 | 1974.6689
2030-05-19 16:00 | 7438.28 | 2.4356 | 58.9603 | 48.4627 | 2179.9447
2030-05-20 17:00 | 7320.56 | 2.4125 | 59.1229 | 48.4627 | 2145.4444
2030-05-21 18:00 | 5935.47 | 1.9361 | 59.3783 | 48.4627 | 1739.5145
2030-05-22 19:00 | 4485.28 | 1.4626 | 59.3807 | 48.4627 | 1314.5058
2030-05-23 20:00 | 3053.29 | 1 | 47.871 | 48.4627 | 894.831
2030-05-24 21:00 | 2988.13 | 1 | 47.7385 | 48.4627 | 875.7345
2030-05-25 22:00 | -646.047 | 2.8806 | 47.9166 | 48.4627 | -189.3377
2030-05-26 23:00 | -1513.17 | 5.5484 | 47.3593 | 48.4627 | -443.4664
2030-05-28 | -2211.31 | 6.6648 | 46.8456 | 48.4627 | -648.071
2030-05-29 01:00 | -2449.82 | 6.6648 | 46.4898 | 48.4627 | -717.9714
2030-05-30 02:00 | -3054.42 | 6.6648 | 45.9941 | 48.4627 | -895.1621
2030-05-31 03:00 | -3309.31 | 6.6648 | 45.6347 | 48.4627 | -969.863
2030-06-01 04:00 | -3382.37 | 6.6648 | 45.4265 | 48.4627 | -991.2748
2030-06-02 05:00 | -2800.79 | 6.6648 | 45.5789 | 48.4627 | -820.8305
2030-06-03 06:00 | -1455.97 | 5.0538 | 45.967 | 48.4627 | -426.7027
2030-06-04 07:00 | 0 | 0 | 47.0039 | 48.4627 | 0
2030-06-05 08:00 | 484.312 | 1 | 46.9845 | 48.4627 | 141.9378
2030-06-06 09:00 | 2534.53 | 1 | 46.3832 | 48.4627 | 742.7974
2030-06-07 10:00 | 3072.17 | 1 | 62.3962 | 48.4627 | 900.3641
2030-06-08 11:00 | 3408.08 | 1.1208 | 58.0061 | 48.4627 | 998.8097
2030-06-09 12:00 | 4215.75 | 1.3444 | 58.4875 | 48.4627 | 1235.5144
2030-06-10 13:00 | 5073.48 | 1.607 | 58.7422 | 48.4627 | 1486.8902
2030-06-11 14:00 | 5850.55 | 1.8899 | 58.7556 | 48.4627 | 1714.6269
2030-06-12 15:00 | 6285.16 | 2.0589 | 58.811 | 48.4627 | 1841.9986
2030-06-13 16:00 | 8909.71 | 2.9508 | 58.8749 | 48.4627 | 2611.1782
2030-06-14 17:00 | 7765.32 | 2.5259 | 59.4529 | 48.4627 | 2275.7906
2030-06-15 18:00 | 6291.56 | 2.036 | 59.6551 | 48.4627 | 1843.8742
2030-06-16 19:00 | 4849.96 | 1.5492 | 59.7645 | 48.4627 | 1421.383
2030-06-17 20:00 | 3841.31 | 1.2333 | 59.6275 | 48.4627 | 1125.7768
2030-06-18 21:00 | 2948.06 | 1 | 60.0215 | 48.4627 | 863.9911
2030-06-19 22:00 | 3006.25 | 1 | 47.8064 | 48.4627 | 881.0449
2030-06-20 23:00 | 0 | 0 | 48.7787 | 48.4627 | 0
2030-06-22 | -726.884 | 2.9812 | 47.6371 | 48.4627 | -213.0287
2030-06-23 01:00 | -1204.5 | 4.4829 | 47.3069 | 48.4627 | -353.0041
2030-06-24 02:00 | -1550.5 | 5.5173 | 47.0888 | 48.4627 | -454.4067
2030-06-25 03:00 | -1795.93 | 6.2631 | 46.9085 | 48.4627 | -526.3351
2030-06-26 04:00 | -2168.9 | 6.6648 | 46.5961 | 48.4627 | -635.6418
2030-06-27 05:00 | -2058.35 | 6.6648 | 46.5062 | 48.4627 | -603.2428
2030-06-28 06:00 | -914.152 | 3.1068 | 46.4556 | 48.4627 | -267.9115
2030-06-29 07:00 | 0 | 1 | 47.4827 | 48.4627 | 0
2030-06-30 08:00 | 140.742 | 1 | 47.51 | 48.4627 | 41.2474
2030-07-01 09:00 | 42.9586 | 1 | 47.5672 | 48.4627 | 12.5899
2030-07-02 10:00 | 2392.41 | 1 | 46.7514 | 48.4627 | 701.1462
2030-07-03 11:00 | 3007.8 | 1.0561 | 57.4707 | 48.4627 | 881.4992
2030-07-04 12:00 | 4004.26 | 1.3633 | 57.9218 | 48.4627 | 1173.5328
2030-07-05 13:00 | 4253.57 | 1.4729 | 57.9358 | 48.4627 | 1246.5983
2030-07-06 14:00 | 4597.46 | 1.5073 | 58.6308 | 48.4627 | 1347.3825
2030-07-07 15:00 | 4864.63 | 1.6245 | 58.5845 | 48.4627 | 1425.6823
2030-07-08 16:00 | 6969.13 | 2.3807 | 58.4547 | 48.4627 | 2042.4504
2030-07-09 17:00 | 6243.6 | 2.0942 | 58.9202 | 48.4627 | 1829.8185
2030-07-10 18:00 | 5098 | 1.6943 | 59.1187 | 48.4627 | 1494.0763
2030-07-11 19:00 | 3509.86 | 1.189 | 58.898 | 48.4627 | 1028.6384
2030-07-12 20:00 | 3044.34 | 1 | 63.3555 | 48.4627 | 892.208
2030-07-13 21:00 | 2986.47 | 1 | 47.7031 | 48.4627 | 875.248
2030-07-14 22:00 | 1835.59 | 1 | 48.0429 | 48.4627 | 537.9583
2030-07-15 23:00 | -966.596 | 3.9762 | 47.7091 | 48.4627 | -283.2813
2030-07-17 | -1719.91 | 6.1479 | 47.24 | 48.4627 | -504.0559
2030-07-18 01:00 | -2173.04 | 6.6648 | 46.8328 | 48.4627 | -636.8552
2030-07-19 02:00 | -2536.19 | 6.6648 | 46.4606 | 48.4627 | -743.2839
2030-07-20 03:00 | -2698.17 | 6.6648 | 46.1922 | 48.4627 | -790.7556
2030-07-21 04:00 | -2500.7 | 6.6648 | 46.1201 | 48.4627 | -732.8828
2030-07-22 05:00 | -1564.34 | 5.3952 | 46.32 | 48.4627 | -458.4628
2030-07-23 06:00 | -919.984 | 3.2779 | 46.3623 | 48.4627 | -269.6207
2030-07-24 07:00 | 0 | 1 | 47.3587 | 48.4627 | 0
2030-07-25 08:00 | 2484.24 | 1 | 46.6022 | 48.4627 | 728.0589
2030-07-26 09:00 | 3010.24 | 1 | 46.7021 | 48.4627 | 882.2143
2030-07-27 10:00 | 3479.1 | 1.1746 | 57.9844 | 48.4627 | 1019.6236
2030-07-28 11:00 | 4868.15 | 1.6591 | 58.0189 | 48.4627 | 1426.7139
2030-07-29 12:00 | 5447.71 | 1.8453 | 58.3367 | 48.4627 | 1596.5662
2030-07-30 13:00 | 5552.36 | 1.8797 | 58.578 | 48.4627 | 1627.2361
2030-07-31 14:00 | 5730.45 | 1.9784 | 58.5314 | 48.4627 | 1679.4291
2030-08-01 15:00 | 7055.23 | 2.4101 | 58.7694 | 48.4627 | 2067.6838
2030-08-02 16:00 | 7310.57 | 2.5056 | 58.966 | 48.4627 | 2142.5166
2030-08-03 17:00 | 6985.28 | 2.4418 | 58.947 | 48.4627 | 2047.1835
2030-08-04 18:00 | 5561.31 | 1.9305 | 59.1094 | 48.4627 | 1629.8591
2030-08-05 19:00 | 3669.06 | 1.2816 | 59.0141 | 48.4627 | 1075.2953
2030-08-06 20:00 | 2846.5 | 1 | 48.1823 | 48.4627 | 834.2268
2030-08-07 21:00 | 2706.61 | 1 | 48.07 | 48.4627 | 793.2291
2030-08-08 22:00 | -960.01 | 3.9476 | 48.0694 | 48.4627 | -281.3512
2030-08-09 23:00 | -1575.86 | 5.6294 | 47.5265 | 48.4627 | -461.839
2030-08-11 | -1786.37 | 6.1898 | 47.1937 | 48.4627 | -523.5334
2030-08-12 01:00 | -2134.7 | 6.6648 | 46.9105 | 48.4627 | -625.6188
2030-08-13 02:00 | -2387.55 | 6.6648 | 46.6099 | 48.4627 | -699.7218
2030-08-14 03:00 | -2805.68 | 6.6648 | 46.2123 | 48.4627 | -822.2636
2030-08-15 04:00 | -2582.24 | 6.6648 | 46.1769 | 48.4627 | -756.7798
2030-08-16 05:00 | -1425.93 | 4.9058 | 46.4081 | 48.4627 | -417.8988
2030-08-17 06:00 | -643.543 | 2.3759 | 46.5011 | 48.4627 | -188.6038
2030-08-18 07:00 | 1693.61 | 1 | 46.908 | 48.4627 | 496.3481
2030-08-19 08:00 | 3106.79 | 1 | 46.6571 | 48.4627 | 910.5103
2030-08-20 09:00 | 3037.37 | 1 | 59.3066 | 48.4627 | 890.1653
2030-08-21 10:00 | 5097.74 | 1.6377 | 58.6578 | 48.4627 | 1494.0001
2030-08-22 11:00 | 6066.66 | 2.0136 | 58.6237 | 48.4627 | 1777.9625
2030-08-23 12:00 | 5003.45 | 1.6614 | 58.921 | 48.4627 | 1466.3664
2030-08-24 13:00 | 4955.61 | 1.61 | 59.2139 | 48.4627 | 1452.3459
2030-08-25 14:00 | 5859.38 | 1.9466 | 59.0415 | 48.4627 | 1717.2148
2030-08-26 15:00 | 7888.66 | 2.595 | 59.3127 | 48.4627 | 2311.938
2030-08-27 16:00 | 8435.39 | 2.769 | 59.626 | 48.4627 | 2472.1688
2030-08-28 17:00 | 8149.3 | 2.7376 | 59.6121 | 48.4627 | 2388.3241
2030-08-29 18:00 | 7058.77 | 2.2516 | 60.2915 | 48.4627 | 2068.7213
2030-08-30 19:00 | 5641.06 | 1.788 | 60.3892 | 48.4627 | 1653.2315
2030-08-31 20:00 | 3140.57 | 1 | 60.5548 | 48.4627 | 920.4102
2030-09-01 21:00 | 3089.42 | 1 | 48.3197 | 48.4627 | 905.4196
2030-09-02 22:00 | 2887.1 | 1 | 48.2523 | 48.4627 | 846.1255
2030-09-03 23:00 | -60.9609 | 0.91687 | 48.9228 | 48.4627 | -17.8659
2030-09-05 | -339.983 | 1.75 | 48.1502 | 48.4627 | -99.6392
2030-09-06 01:00 | -537.801 | 2.3334 | 47.8122 | 48.4627 | -157.6139
2030-09-07 02:00 | -674.245 | 2.7348 | 47.6431 | 48.4627 | -197.6017
2030-09-08 03:00 | -741.734 | 2.9243 | 47.4926 | 48.4627 | -217.3808
2030-09-09 04:00 | -570.887 | 2.3277 | 47.3957 | 48.4627 | -167.3105
2030-09-10 05:00 | 875.423 | 1 | 47.8702 | 48.4627 | 256.5612
2030-09-11 06:00 | 2995.52 | 1 | 47.2296 | 48.4627 | 877.9003
2030-09-12 07:00 | 3071.62 | 1 | 61.845 | 48.4627 | 900.203
2030-09-13 08:00 | 3165.84 | 1 | 60.2083 | 48.4627 | 927.8161
2030-09-14 09:00 | 4621.85 | 1.4829 | 59.2203 | 48.4627 | 1354.5305
2030-09-15 10:00 | 6419.48 | 2.128 | 59.0833 | 48.4627 | 1881.3639
2030-09-16 11:00 | 8172.86 | 2.7338 | 59.2971 | 48.4627 | 2395.2288
2030-09-17 12:00 | 9000.79 | 2.9713 | 59.7695 | 48.4627 | 2637.8712
2030-09-18 13:00 | 9674.63 | 3.1893 | 60.0863 | 48.4627 | 2835.3542
2030-09-19 14:00 | 10627.8 | 3.4199 | 60.6232 | 48.4627 | 3114.7007
2030-09-20 15:00 | 11777.5 | 3.8693 | 60.7031 | 48.4627 | 3451.6445
2030-09-21 16:00 | 12261 | 3.9845 | 61.1344 | 48.4627 | 3593.3444
2030-09-22 17:00 | 11992.5 | 3.9274 | 61.314 | 48.4627 | 3514.6548
2030-09-23 18:00 | 10302.1 | 3.3159 | 61.6625 | 48.4627 | 3019.2475
2030-09-24 19:00 | 8526.97 | 2.7329 | 61.709 | 48.4627 | 2499.0082
2030-09-25 20:00 | 5835.71 | 1.793 | 62.0682 | 48.4627 | 1710.2778
2030-09-26 21:00 | 4525.71 | 1.4107 | 61.6344 | 48.4627 | 1326.3547
2030-09-27 22:00 | 3174.44 | 1 | 65.4834 | 48.4627 | 930.3365
2030-09-28 23:00 | 3155.25 | 1 | 49.1699 | 48.4627 | 924.7125
2030-09-30 | 2997.91 | 1 | 49.0669 | 48.4627 | 878.6007
2030-10-01 01:00 | 2959.05 | 1 | 48.9606 | 48.4627 | 867.2119
2030-10-02 02:00 | 3101.71 | 1 | 48.8329 | 48.4627 | 909.0215
2030-10-03 03:00 | 3151.34 | 1 | 48.7699 | 48.4627 | 923.5666
2030-10-04 04:00 | 3205.66 | 1 | 48.7226 | 48.4627 | 939.4862
2030-10-05 05:00 | 3238.79 | 1 | 48.6759 | 48.4627 | 949.1957
2030-10-06 06:00 | 3257.6 | 1 | 65.8103 | 48.4627 | 954.7083
2030-10-07 07:00 | 3582.17 | 1.1115 | 60.6101 | 48.4627 | 1049.8304
2030-10-08 08:00 | 4166.71 | 1.2627 | 60.905 | 48.4627 | 1221.1422
2030-10-09 09:00 | 6183.07 | 1.9731 | 60.4091 | 48.4627 | 1812.0789
2030-10-10 10:00 | 7877.14 | 2.6146 | 60.2292 | 48.4627 | 2308.5618
2030-10-11 11:00 | 6515.23 | 2.1341 | 60.6568 | 48.4627 | 1909.4254
2030-10-12 12:00 | 4964.34 | 1.5549 | 61.1682 | 48.4627 | 1454.9044
2030-10-13 13:00 | 5847.48 | 1.8296 | 61.0666 | 48.4627 | 1713.7272
2030-10-14 14:00 | 5414.56 | 1.7985 | 60.4957 | 48.4627 | 1586.8509
2030-10-15 15:00 | 7504.99 | 2.462 | 60.5928 | 48.4627 | 2199.4954
2030-10-16 16:00 | 7402.22 | 2.5035 | 60.4208 | 48.4627 | 2169.3765
2030-10-17 17:00 | 7308.48 | 2.3761 | 60.902 | 48.4627 | 2141.9041
2030-10-18 18:00 | 6394.51 | 2.0086 | 61.3248 | 48.4627 | 1874.0459
2030-10-19 19:00 | 5115.48 | 1.5972 | 61.3616 | 48.4627 | 1499.1992
2030-10-20 20:00 | 3036.75 | 1 | 63.8604 | 48.4627 | 889.9836
2030-10-21 21:00 | 2970.51 | 1 | 49.1567 | 48.4627 | 870.5705
2030-10-22 22:00 | -483.472 | 2.2718 | 49.2939 | 48.4627 | -141.6917
2030-10-23 23:00 | -1132.75 | 4.2297 | 48.6845 | 48.4627 | -331.9763
2030-10-25 | -1636.86 | 5.7386 | 48.3107 | 48.4627 | -479.7163
2030-10-26 01:00 | -2049.92 | 6.6648 | 47.9971 | 48.4627 | -600.7722
2030-10-27 02:00 | -2414.64 | 6.6648 | 47.607 | 48.4627 | -707.6611
2030-10-28 03:00 | -2427.69 | 6.6648 | 47.3731 | 48.4627 | -711.4857
2030-10-29 04:00 | -2483.51 | 6.6648 | 47.1975 | 48.4627 | -727.8449
2030-10-30 05:00 | -2057.97 | 6.6648 | 47.2774 | 48.4627 | -603.1315
2030-10-31 06:00 | -2085.33 | 6.6648 | 47.1815 | 48.4627 | -611.1499
2030-11-01 07:00 | -1868.19 | 6.3605 | 47.1598 | 48.4627 | -547.5124
2030-11-02 08:00 | -2095.61 | 6.6648 | 47.0329 | 48.4627 | -614.1627
2030-11-03 09:00 | -1772.81 | 6.0453 | 47.0055 | 48.4627 | -519.5593
2030-11-04 10:00 | -1340.29 | 4.6184 | 46.9687 | 48.4627 | -392.8002
2030-11-05 11:00 | -942.562 | 3.4155 | 47.0026 | 48.4627 | -276.2377
2030-11-06 12:00 | -751.494 | 2.8977 | 47.066 | 48.4627 | -220.2412
2030-11-07 13:00 | -577.127 | 2.3609 | 47.1118 | 48.4627 | -169.1392
2030-11-08 14:00 | -335.791 | 1.5999 | 47.2301 | 48.4627 | -98.4106
2030-11-09 15:00 | 2594.43 | 1 | 47.0512 | 48.4627 | 760.3524
2030-11-10 16:00 | 2990.47 | 1 | 47.1745 | 48.4627 | 876.4202
2030-11-11 17:00 | 3003.94 | 1 | 47.3334 | 48.4627 | 880.3679
2030-11-12 18:00 | 0 | 0 | 48.4419 | 48.4627 | 0
2030-11-13 19:00 | -720.657 | 2.8316 | 47.3641 | 48.4627 | -211.2037
2030-11-14 20:00 | -1619.71 | 5.9384 | 47.1551 | 48.4627 | -474.6901
2030-11-15 21:00 | -2137.83 | 6.6648 | 46.8132 | 48.4627 | -626.5361
2030-11-16 22:00 | -3214.2 | 6.6648 | 46.1011 | 48.4627 | -941.989
2030-11-17 23:00 | -3767.22 | 6.6648 | 45.593 | 48.4627 | -1104.0632
2030-11-19 | -4025.12 | 6.6648 | 45.2875 | 48.4627 | -1179.6462
2030-11-20 01:00 | -4119.31 | 6.6648 | 45.1018 | 48.4627 | -1207.2506
2030-11-21 02:00 | -4147.17 | 6.6648 | 44.979 | 48.4627 | -1215.4155
2030-11-22 03:00 | -4176.08 | 6.6648 | 44.848 | 48.4627 | -1223.8882
2030-11-23 04:00 | -4349.86 | 6.6648 | 44.6581 | 48.4627 | -1274.8181
2030-11-24 05:00 | -4382.83 | 6.6648 | 44.5299 | 48.4627 | -1284.4807
2030-11-25 06:00 | -3301.64 | 6.6648 | 45.0013 | 48.4627 | -967.6152
2030-11-26 07:00 | -2464.59 | 6.6648 | 45.4627 | 48.4627 | -722.3
2030-11-27 08:00 | -3045.86 | 6.6648 | 45.2458 | 48.4627 | -892.6534
2030-11-28 09:00 | -2872.92 | 6.6648 | 45.2931 | 48.4627 | -841.9697
2030-11-29 10:00 | -2012.39 | 6.6648 | 45.7143 | 48.4627 | -589.7733
2030-11-30 11:00 | -1251.93 | 4.317 | 45.833 | 48.4627 | -366.9045
2030-12-01 12:00 | -558.945 | 2.1674 | 46.0428 | 48.4627 | -163.8106
2030-12-02 13:00 | 150.566 | 1 | 46.9696 | 48.4627 | 44.1265
2030-12-03 14:00 | 2735.38 | 1 | 46.2198 | 48.4627 | 801.6607
2030-12-04 15:00 | 3054.57 | 1 | 46.4285 | 48.4627 | 895.2061
2030-12-05 16:00 | 5095.38 | 1.6495 | 58.1663 | 48.4627 | 1493.3085
2030-12-06 17:00 | 4440.52 | 1.4562 | 58.3175 | 48.4627 | 1301.3879
2030-12-07 18:00 | 3316.94 | 1.0941 | 58.4232 | 48.4627 | 972.0992
2030-12-08 19:00 | 3048.62 | 1 | 47.1438 | 48.4627 | 893.4623
2030-12-09 20:00 | 2619.59 | 1 | 47.3262 | 48.4627 | 767.726
2030-12-10 21:00 | -257.183 | 1.5934 | 47.6949 | 48.4627 | -75.3729
2030-12-11 22:00 | -644.963 | 2.7334 | 47.1817 | 48.4627 | -189.02
2030-12-12 23:00 | -2104.53 | 6.6648 | 46.7533 | 48.4627 | -616.7769
2030-12-14 | -3079.56 | 6.6648 | 46.0571 | 48.4627 | -902.5299
2030-12-15 01:00 | -3352.48 | 6.6648 | 45.6913 | 48.4627 | -982.5149
2030-12-16 02:00 | -3698.91 | 6.6648 | 45.3244 | 48.4627 | -1084.0435
2030-12-17 03:00 | -3915.86 | 6.6648 | 45.0691 | 48.4627 | -1147.6253
2030-12-18 04:00 | -3933.92 | 6.6648 | 44.9049 | 48.4627 | -1152.9181
2030-12-19 05:00 | -3598.37 | 6.6648 | 44.9629 | 48.4627 | -1054.5781
2030-12-20 06:00 | -1884.29 | 6.6351 | 45.7748 | 48.4627 | -552.2309
2030-12-21 07:00 | -554.788 | 1.8849 | 45.8373 | 48.4627 | -162.5923
2030-12-22 08:00 | -106.818 | 0.88555 | 46.5909 | 48.4627 | -31.3053
2030-12-23 09:00 | 2408.32 | 1 | 46.3126 | 48.4627 | 705.8089
2030-12-24 10:00 | 2925.85 | 1 | 58.7595 | 48.4627 | 857.482
2030-12-25 11:00 | 3880.92 | 1.2955 | 57.8524 | 48.4627 | 1137.3854
2030-12-26 12:00 | 5042.84 | 1.6697 | 58.1839 | 48.4627 | 1477.9105
2030-12-27 13:00 | 5164.25 | 1.771 | 58.1166 | 48.4627 | 1513.4923
2030-12-28 14:00 | 5573.87 | 1.8625 | 58.586 | 48.4627 | 1633.54
2030-12-29 15:00 | 5878.06 | 1.9833 | 58.6554 | 48.4627 | 1722.6893
2030-12-30 16:00 | 8266.07 | 2.7995 | 58.7737 | 48.4627 | 2422.546
2030-12-31 17:00 | 7228.94 | 2.4767 | 59.0158 | 48.4627 | 2118.5932
2031-01-01 18:00 | 6066.83 | 2.037 | 59.3499 | 48.4627 | 1778.0124
2031-01-02 19:00 | 4253.93 | 1.4055 | 59.5091 | 48.4627 | 1246.7038
2031-01-03 20:00 | 3014.65 | 1 | 59.9538 | 48.4627 | 883.5067
2031-01-04 21:00 | 3032.22 | 1 | 47.9781 | 48.4627 | 888.656
2031-01-05 22:00 | 2993.18 | 1 | 47.9125 | 48.4627 | 877.2145
2031-01-06 23:00 | -678.93 | 2.9818 | 48.1222 | 48.4627 | -198.9747
2031-01-08 | -1231.83 | 4.5566 | 47.595 | 48.4627 | -361.0137
2031-01-09 01:00 | -1608.67 | 5.6918 | 47.2968 | 48.4627 | -471.4546
2031-01-10 02:00 | -1872.22 | 6.4874 | 47.1142 | 48.4627 | -548.6935
2031-01-11 03:00 | -1875.55 | 6.4224 | 46.9413 | 48.4627 | -549.6694
2031-01-12 04:00 | -1758.19 | 6.0368 | 46.784 | 48.4627 | -515.2746
2031-01-13 05:00 | -863.061 | 2.9904 | 46.7165 | 48.4627 | -252.9382
2031-01-14 06:00 | -188.082 | 1.0301 | 47.0919 | 48.4627 | -55.1214
2031-01-15 07:00 | 2485.86 | 1 | 46.9189 | 48.4627 | 728.5337
2031-01-16 08:00 | 3067.32 | 1 | 47.0002 | 48.4627 | 898.9428
2031-01-17 09:00 | 3143.05 | 1 | 61.9547 | 48.4627 | 921.137
2031-01-18 10:00 | 4643.62 | 1.469 | 59.0337 | 48.4627 | 1360.9107
2031-01-19 11:00 | 5862.6 | 1.9275 | 58.8814 | 48.4627 | 1718.1585
2031-01-20 12:00 | 6286.18 | 2.01 | 59.4627 | 48.4627 | 1842.2975
2031-01-21 13:00 | 7070.08 | 2.229 | 59.8134 | 48.4627 | 2072.0359
2031-01-22 14:00 | 6202.35 | 1.9952 | 59.8191 | 48.4627 | 1817.7294
2031-01-23 15:00 | 7213.06 | 2.3124 | 59.9403 | 48.4627 | 2113.9392
2031-01-24 16:00 | 7003.01 | 2.2014 | 60.3092 | 48.4627 | 2052.3796
2031-01-25 17:00 | 6648.15 | 2.0612 | 60.5572 | 48.4627 | 1948.3804
2031-01-26 18:00 | 5163.83 | 1.6014 | 60.6017 | 48.4627 | 1513.3692
2031-01-27 19:00 | 3984.37 | 1.2964 | 59.9882 | 48.4627 | 1167.7036
2031-01-28 20:00 | 3051.1 | 1 | 48.4194 | 48.4627 | 894.1891
2031-01-29 21:00 | 3088.67 | 1 | 48.2613 | 48.4627 | 905.1998
2031-01-30 22:00 | 0 | 0 | 49.2331 | 48.4627 | 0
2031-01-31 23:00 | -452.781 | 1.9215 | 48.0859 | 48.4627 | -132.697
2031-02-02 | -561.896 | 2.3944 | 47.8485 | 48.4627 | -164.6755
2031-02-03 01:00 | -787.026 | 3.1091 | 47.6446 | 48.4627 | -230.6546
2031-02-04 02:00 | -826.684 | 3.1702 | 47.4955 | 48.4627 | -242.2772
2031-02-05 03:00 | -819.858 | 3.1456 | 47.3724 | 48.4627 | -240.2767
2031-02-06 04:00 | -686.085 | 2.6955 | 47.3289 | 48.4627 | -201.0717
2031-02-07 05:00 | -196.742 | 1.0879 | 47.5332 | 48.4627 | -57.6594
2031-02-08 06:00 | 0 | 0 | 48.1516 | 48.4627 | 0
2031-02-09 07:00 | 1922.63 | 1 | 47.4934 | 48.4627 | 563.4672
2031-02-10 08:00 | 0 | 0 | 48.3197 | 48.4627 | 0
2031-02-11 09:00 | 3707.26 | 1 | 46.9451 | 48.4627 | 1086.4907
2031-02-12 10:00 | 3380.89 | 1 | 47.3568 | 48.4627 | 990.841
2031-02-13 11:00 | 3393.83 | 1 | 61.029 | 48.4627 | 994.6334
2031-02-14 12:00 | 4709.41 | 1.5404 | 59.0629 | 48.4627 | 1380.1918
2031-02-15 13:00 | 5157.35 | 1.7614 | 58.8014 | 48.4627 | 1511.4701
2031-02-16 14:00 | 5571.81 | 1.9049 | 58.9867 | 48.4627 | 1632.9363
2031-02-17 15:00 | 7215.54 | 2.3802 | 59.4606 | 48.4627 | 2114.666
2031-02-18 16:00 | 6691.02 | 2.1612 | 59.927 | 48.4627 | 1960.9444
2031-02-19 17:00 | 6566.26 | 2.1906 | 59.7139 | 48.4627 | 1924.3808
2031-02-20 18:00 | 4239.61 | 1.3755 | 60.0839 | 48.4627 | 1242.507
2031-02-21 19:00 | 2989.31 | 1 | 61.101 | 48.4627 | 876.0803
2031-02-22 20:00 | 0 | 1 | 49.3699 | 48.4627 | 0
2031-02-23 21:00 | -165.619 | 1.2595 | 48.5318 | 48.4627 | -48.5381
2031-02-24 22:00 | -1067.92 | 4.1623 | 47.88 | 48.4627 | -312.9765
2031-02-25 23:00 | -1474.57 | 5.254 | 47.5751 | 48.4627 | -432.1538
2031-02-27 | -2001.52 | 6.6648 | 47.3158 | 48.4627 | -586.5876
2031-02-28 01:00 | -2377.05 | 6.6648 | 46.9374 | 48.4627 | -696.6446
2031-03-01 02:00 | -2727.17 | 6.6648 | 46.6127 | 48.4627 | -799.2546
2031-03-02 03:00 | -2917.63 | 6.6648 | 46.3528 | 48.4627 | -855.0729
2031-03-03 04:00 | -2835.84 | 6.6648 | 46.2546 | 48.4627 | -831.1027
2031-03-04 05:00 | -1625.88 | 5.6011 | 46.6005 | 48.4627 | -476.4984
2031-03-05 06:00 | -996.039 | 3.5021 | 46.6506 | 48.4627 | -291.9102
2031-03-06 07:00 | 0 | 0 | 47.6584 | 48.4627 | 0
2031-03-07 08:00 | -193.536 | 1.312 | 47.2782 | 48.4627 | -56.7198
2031-03-08 09:00 | 2304.12 | 1 | 47.0278 | 48.4627 | 675.2709
2031-03-09 10:00 | 3075.4 | 1 | 47.0287 | 48.4627 | 901.3108
2031-03-10 11:00 | 3001.18 | 1 | 47.2767 | 48.4627 | 879.559
2031-03-11 12:00 | 3054.71 | 1 | 47.3684 | 48.4627 | 895.2471
2031-03-12 13:00 | 3081.55 | 1 | 63.8205 | 48.4627 | 903.1132
2031-03-13 14:00 | 3103.21 | 1 | 61.6188 | 48.4627 | 909.4611
2031-03-14 15:00 | 3736.74 | 1.2183 | 58.9824 | 48.4627 | 1095.1304
2031-03-15 16:00 | 3885.38 | 1.2455 | 59.2498 | 48.4627 | 1138.6925
2031-03-16 17:00 | 3935.22 | 1.2982 | 59.0171 | 48.4627 | 1153.2991
2031-03-17 18:00 | 3075.91 | 1 | 63.7301 | 48.4627 | 901.4602
2031-03-18 19:00 | 3003.65 | 1 | 47.7615 | 48.4627 | 880.2829
2031-03-19 20:00 | -650.877 | 2.8893 | 48.0421 | 48.4627 | -190.7532
2031-03-20 21:00 | -1266.73 | 4.6895 | 47.5427 | 48.4627 | -371.2419
2031-03-21 22:00 | -2512.52 | 6.6648 | 46.9252 | 48.4627 | -736.3469
2031-03-22 23:00 | -3382.37 | 6.6648 | 46.2259 | 48.4627 | -991.2748
2031-03-24 | -3570.33 | 6.6648 | 45.8713 | 48.4627 | -1046.3604
2031-03-25 01:00 | -4169.36 | 6.6648 | 45.3586 | 48.4627 | -1221.9188
2031-03-26 02:00 | -4367.5 | 6.6648 | 45.0816 | 48.4627 | -1279.9879
2031-03-27 03:00 | -4364.5 | 6.6648 | 44.9226 | 48.4627 | -1279.1087
2031-03-28 04:00 | -4128.39 | 6.6648 | 44.924 | 48.4627 | -1209.9117
2031-03-29 05:00 | -3585.6 | 6.6648 | 45.1161 | 48.4627 | -1050.8356
2031-03-30 06:00 | -3442.08 | 6.6648 | 45.1525 | 48.4627 | -1008.7741
2031-03-31 07:00 | -3215.89 | 6.6648 | 45.2178 | 48.4627 | -942.4843
2031-04-01 08:00 | -3410.12 | 6.6648 | 45.1092 | 48.4627 | -999.4075
2031-04-02 09:00 | -2828.8 | 6.6648 | 45.3469 | 48.4627 | -829.0394
2031-04-03 10:00 | -2187.56 | 6.6648 | 45.6765 | 48.4627 | -641.1105
2031-04-04 11:00 | -1725.44 | 5.9912 | 45.8559 | 48.4627 | -505.6765
2031-04-05 12:00 | -1342.68 | 4.7075 | 45.9071 | 48.4627 | -393.5007
2031-04-06 13:00 | -1263.78 | 4.5781 | 45.9829 | 48.4627 | -370.3774
2031-04-07 14:00 | -1025.14 | 3.7571 | 46.0217 | 48.4627 | -300.4389
2031-04-08 15:00 | 0 | 1 | 46.9707 | 48.4627 | 0
2031-04-09 16:00 | 2794.96 | 1 | 46.1131 | 48.4627 | 819.1219
2031-04-10 17:00 | 2997.98 | 1 | 46.356 | 48.4627 | 878.6212
2031-04-11 18:00 | 2915.83 | 1 | 46.5803 | 48.4627 | 854.5454
2031-04-12 19:00 | 0 | 0 | 47.6897 | 48.4627 | 0
2031-04-13 20:00 | -1117.32 | 4.5686 | 46.7094 | 48.4627 | -327.4542
2031-04-14 21:00 | -1685.56 | 6.0338 | 46.435 | 48.4627 | -493.9889
2031-04-15 22:00 | -3455.28 | 6.6648 | 45.4862 | 48.4627 | -1012.6426
2031-04-16 23:00 | -3872.52 | 6.6648 | 45.0136 | 48.4627 | -1134.9236
2031-04-18 | -4229.89 | 6.6648 | 44.6177 | 48.4627 | -1239.6584
2031-04-19 01:00 | -4707.09 | 6.6648 | 44.2368 | 48.4627 | -1379.5119
2031-04-20 02:00 | -4597.61 | 6.6648 | 44.1509 | 48.4627 | -1347.4265
2031-04-21 03:00 | -4454.39 | 6.6648 | 44.1227 | 48.4627 | -1305.4528
2031-04-22 04:00 | -4419.37 | 6.6648 | 44.0655 | 48.4627 | -1295.1895
2031-04-23 05:00 | -3173.23 | 6.6648 | 44.6195 | 48.4627 | -929.9819
2031-04-24 06:00 | -2167.17 | 6.6648 | 45.1721 | 48.4627 | -635.1348
2031-04-25 07:00 | -1173.04 | 4.0711 | 45.4091 | 48.4627 | -343.7841
2031-04-26 08:00 | -816.574 | 3.1077 | 45.6406 | 48.4627 | -239.3142
2031-04-27 09:00 | 485.628 | 1 | 46.4765 | 48.4627 | 142.3235
2031-04-28 10:00 | 3044.05 | 1 | 63.7224 | 48.4627 | 892.123
2031-04-29 11:00 | 3768.75 | 1.2327 | 57.5456 | 48.4627 | 1104.5116
2031-04-30 12:00 | 4353.78 | 1.4563 | 57.6243 | 48.4627 | 1275.967
2031-05-01 13:00 | 4660.09 | 1.5539 | 57.8988 | 48.4627 | 1365.7376
2031-05-02 14:00 | 5280.71 | 1.7027 | 58.4683 | 48.4627 | 1547.6233
2031-05-03 15:00 | 6401.33 | 2.1253 | 58.3913 | 48.4627 | 1876.0446
2031-05-04 16:00 | 6505.35 | 2.1917 | 58.4947 | 48.4627 | 1906.5299
2031-05-05 17:00 | 6298.59 | 2.1066 | 58.7473 | 48.4627 | 1845.9345
2031-05-06 18:00 | 5096.99 | 1.6792 | 59.0155 | 48.4627 | 1493.7803
2031-05-07 19:00 | 3124.54 | 1.0197 | 59.1189 | 48.4627 | 915.7123
2031-05-08 20:00 | 2915.45 | 1 | 47.6217 | 48.4627 | 854.4341
2031-05-09 21:00 | -72.2261 | 0.949 | 48.2941 | 48.4627 | -21.1674
2031-05-10 22:00 | -948.703 | 3.8134 | 47.3964 | 48.4627 | -278.0374
2031-05-11 23:00 | -1682.66 | 6.0576 | 47.0291 | 48.4627 | -493.139
2031-05-13 | -1996.85 | 6.6648 | 46.7402 | 48.4627 | -585.219
2031-05-14 01:00 | -2117.29 | 6.6648 | 46.5177 | 48.4627 | -620.5164
2031-05-15 02:00 | -2465.04 | 6.6648 | 46.1973 | 48.4627 | -722.4319
2031-05-16 03:00 | -2762.53 | 6.6648 | 45.9198 | 48.4627 | -809.6176
2031-05-17 04:00 | -2853.59 | 6.6648 | 45.7481 | 48.4627 | -836.3047
2031-05-18 05:00 | -2384.2 | 6.6648 | 45.8798 | 48.4627 | -698.74
2031-05-19 06:00 | -1020.38 | 3.5029 | 46.0637 | 48.4627 | -299.0439
2031-05-20 07:00 | 1248.38 | 1 | 46.7149 | 48.4627 | 365.8641
2031-05-21 08:00 | 635.067 | 1 | 47.1752 | 48.4627 | 186.1198
2031-05-22 09:00 | 2964.41 | 1 | 46.4634 | 48.4627 | 868.7828
2031-05-23 10:00 | 2930.16 | 1 | 58.2182 | 48.4627 | 858.7451
2031-05-24 11:00 | 3904.4 | 1.3137 | 57.9931 | 48.4627 | 1144.2667
2031-05-25 12:00 | 4595.89 | 1.5163 | 58.3937 | 48.4627 | 1346.9224
2031-05-26 13:00 | 4763.24 | 1.5861 | 58.4925 | 48.4627 | 1395.9678
2031-05-27 14:00 | 5082.6 | 1.6977 | 58.6284 | 48.4627 | 1489.563
2031-05-28 15:00 | 5208.97 | 1.7529 | 58.6823 | 48.4627 | 1526.5984
2031-05-29 16:00 | 7654.98 | 2.5776 | 58.7915 | 48.4627 | 2243.4532
2031-05-30 17:00 | 6501.3 | 2.2171 | 58.9928 | 48.4627 | 1905.3429
2031-05-31 18:00 | 5181.11 | 1.7372 | 59.2628 | 48.4627 | 1518.4335
2031-06-01 19:00 | 3316 | 1.1076 | 59.2551 | 48.4627 | 971.8237
2031-06-02 20:00 | 2960.35 | 1 | 47.9728 | 48.4627 | 867.5929
2031-06-03 21:00 | 2925.84 | 1 | 47.9139 | 48.4627 | 857.4791
2031-06-04 22:00 | -98.2575 | 1.0333 | 48.5408 | 48.4627 | -28.7964
2031-06-05 23:00 | -1711.6 | 6.3785 | 47.6354 | 48.4627 | -501.6204
2031-06-07 | -2358.11 | 6.6648 | 47.0106 | 48.4627 | -691.0938
2031-06-08 01:00 | -2751.96 | 6.6648 | 46.5828 | 48.4627 | -806.5199
2031-06-09 02:00 | -3143.31 | 6.6648 | 46.1885 | 48.4627 | -921.2132
2031-06-10 03:00 | -3372.87 | 6.6648 | 45.8706 | 48.4627 | -988.4906
2031-06-11 04:00 | -3506.89 | 6.6648 | 45.6343 | 48.4627 | -1027.768
2031-06-12 05:00 | -3081.24 | 6.6648 | 45.7184 | 48.4627 | -903.0223
2031-06-13 06:00 | -1578.92 | 5.4772 | 46.2409 | 48.4627 | -462.7358
2031-06-14 07:00 | -420.141 | 1.5446 | 46.3685 | 48.4627 | -123.1312
2031-06-15 08:00 | -204.031 | 1.2515 | 46.8658 | 48.4627 | -59.7956
2031-06-16 09:00 | 2625 | 1 | 46.5767 | 48.4627 | 769.3116
2031-06-17 10:00 | 3166.83 | 1 | 60.2337 | 48.4627 | 928.1063
2031-06-18 11:00 | 4855.62 | 1.5275 | 58.7736 | 48.4627 | 1423.0417
2031-06-19 12:00 | 6190.47 | 1.9793 | 58.8965 | 48.4627 | 1814.2477
2031-06-20 13:00 | 6692.51 | 2.2353 | 58.7693 | 48.4627 | 1961.3811
2031-06-21 14:00 | 7128.79 | 2.3904 | 59.004 | 48.4627 | 2089.2421
2031-06-22 15:00 | 7118.79 | 2.3836 | 59.2339 | 48.4627 | 2086.3114
2031-06-23 16:00 | 9019.36 | 2.9914 | 59.4925 | 48.4627 | 2643.3135
2031-06-24 17:00 | 8213.39 | 2.662 | 60.046 | 48.4627 | 2407.107
2031-06-25 18:00 | 6957.83 | 2.1876 | 60.5043 | 48.4627 | 2039.1387
2031-06-26 19:00 | 5223.76 | 1.6687 | 60.3305 | 48.4627 | 1530.9329
2031-06-27 20:00 | 4235.88 | 1.3027 | 60.6349 | 48.4627 | 1241.4139
2031-06-28 21:00 | 3225.33 | 1 | 61.5368 | 48.4627 | 945.2509
2031-06-29 22:00 | 3214.1 | 1 | 66.7215 | 48.4627 | 941.9597
2031-06-30 23:00 | 0 | 0 | 49.2968 | 48.4627 | 0
2031-07-02 | -488.709 | 1.8463 | 48.0446 | 48.4627 | -143.2265
2031-07-03 01:00 | -602.388 | 2.5368 | 47.8938 | 48.4627 | -176.5425
2031-07-04 02:00 | -708.632 | 2.8258 | 47.7084 | 48.4627 | -207.6795
2031-07-05 03:00 | -644.85 | 2.5822 | 47.596 | 48.4627 | -188.9869
2031-07-06 04:00 | -435.219 | 1.9035 | 47.5502 | 48.4627 | -127.5501
2031-07-07 05:00 | 83.3061 | 1 | 48.257 | 48.4627 | 24.4146
2031-07-08 06:00 | 1745.49 | 1 | 47.6966 | 48.4627 | 511.5526
2031-07-09 07:00 | 2608.56 | 1 | 47.5503 | 48.4627 | 764.4935
2031-07-10 08:00 | 2845.66 | 1 | 47.6319 | 48.4627 | 833.9806
2031-07-11 09:00 | 3070.82 | 1 | 47.6529 | 48.4627 | 899.9685
2031-07-12 10:00 | 3471.63 | 1.116 | 59.3395 | 48.4627 | 1017.4343
2031-07-13 11:00 | 5660.04 | 1.8766 | 59.0933 | 48.4627 | 1658.794
2031-07-14 12:00 | 6614.61 | 2.307 | 58.8631 | 48.4627 | 1938.5508
2031-07-15 13:00 | 7084.31 | 2.4171 | 59.3317 | 48.4627 | 2076.2063
2031-07-16 14:00 | 7546.19 | 2.5263 | 59.7205 | 48.4627 | 2211.57
2031-07-17 15:00 | 8978.76 | 3.0117 | 59.8953 | 48.4627 | 2631.4148
2031-07-18 16:00 | 9966.33 | 3.2493 | 60.465 | 48.4627 | 2920.843
2031-07-19 17:00 | 9814.64 | 3.2556 | 60.5613 | 48.4627 | 2876.387
2031-07-20 18:00 | 8444.74 | 2.7367 | 60.9686 | 48.4627 | 2474.909
2031-07-21 19:00 | 6876.22 | 2.1899 | 61.1673 | 48.4627 | 2015.2212
2031-07-22 20:00 | 4438.42 | 1.3718 | 61.4111 | 48.4627 | 1300.7725
2031-07-23 21:00 | 3143.08 | 1 | 62.0176 | 48.4627 | 921.1458
2031-07-24 22:00 | 2970.88 | 1 | 48.9685 | 48.4627 | 870.679
2031-07-25 23:00 | 0 | 0 | 49.8454 | 48.4627 | 0
2031-07-27 | -413.835 | 1.8847 | 48.7231 | 48.4627 | -121.2831
2031-07-28 01:00 | -755.753 | 3.0284 | 48.353 | 48.4627 | -221.4893
2031-07-29 02:00 | -949.844 | 3.5653 | 48.1211 | 48.4627 | -278.3718
2031-07-30 03:00 | -839.109 | 3.1397 | 47.9578 | 48.4627 | -245.9186
2031-07-31 04:00 | -674.485 | 2.6373 | 47.8576 | 48.4627 | -197.672
2031-08-01 05:00 | 1538.91 | 1 | 48.1228 | 48.4627 | 451.01
2031-08-02 06:00 | 2775.92 | 1 | 47.8357 | 48.4627 | 813.5418
2031-08-03 07:00 | 3568.57 | 1.2051 | 59.0039 | 48.4627 | 1045.8446
2031-08-04 08:00 | 4118.76 | 1.3678 | 59.3041 | 48.4627 | 1207.0894
2031-08-05 09:00 | 5692.66 | 1.9257 | 59.2714 | 48.4627 | 1668.354
2031-08-06 10:00 | 7433.06 | 2.4967 | 59.6006 | 48.4627 | 2178.4148
2031-08-07 11:00 | 8633.93 | 2.934 | 59.8091 | 48.4627 | 2530.3551
2031-08-08 12:00 | 9387.17 | 3.1375 | 60.2853 | 48.4627 | 2751.108
2031-08-09 13:00 | 9744.02 | 3.206 | 60.7232 | 48.4627 | 2855.6904
2031-08-10 14:00 | 10454.6 | 3.4048 | 61.0705 | 48.4627 | 3063.9408
2031-08-11 15:00 | 11655.4 | 3.8134 | 61.266 | 48.4627 | 3415.8605
2031-08-12 16:00 | 12077.2 | 3.8979 | 61.6941 | 48.4627 | 3539.4779
2031-08-13 17:00 | 12144.2 | 3.8698 | 62.0558 | 48.4627 | 3559.1137
2031-08-14 18:00 | 10440.7 | 3.3687 | 62.1027 | 48.4627 | 3059.8671
2031-08-15 19:00 | 8680.1 | 2.7697 | 62.2204 | 48.4627 | 2543.8862
2031-08-16 20:00 | 6307.67 | 1.8769 | 62.8802 | 48.4627 | 1848.5956
2031-08-17 21:00 | 5033.46 | 1.5697 | 62.11 | 48.4627 | 1475.1615
2031-08-18 22:00 | 3017.45 | 1 | 63.5065 | 48.4627 | 884.3273
2031-08-19 23:00 | 3013.94 | 1 | 49.6597 | 48.4627 | 883.2986
2031-08-21 | 3058.38 | 1 | 49.4581 | 48.4627 | 896.3227
2031-08-22 01:00 | 3012.34 | 1 | 49.3636 | 48.4627 | 882.8297
2031-08-23 02:00 | 1647.81 | 1 | 49.7483 | 48.4627 | 482.9254
2031-08-24 03:00 | 3144.35 | 1 | 49.0322 | 48.4627 | 921.518
2031-08-25 04:00 | 3134.73 | 1 | 49.0629 | 48.4627 | 918.6987
2031-08-26 05:00 | 3209.73 | 1 | 49.0248 | 48.4627 | 940.679
2031-08-27 06:00 | 3373.3 | 1 | 65.6924 | 48.4627 | 988.6166
2031-08-28 07:00 | 3778.27 | 1.1486 | 61.1703 | 48.4627 | 1107.3016
2031-08-29 08:00 | 4114.51 | 1.2732 | 61.0377 | 48.4627 | 1205.8438
2031-08-30 09:00 | 5589.62 | 1.8946 | 60.123 | 48.4627 | 1638.1559
2031-08-31 10:00 | 7184.92 | 2.4165 | 60.3675 | 48.4627 | 2105.6922
2031-09-01 11:00 | 7768.55 | 2.8 | 59.9372 | 48.4627 | 2276.7373
2031-09-02 12:00 | 8821.73 | 3.0179 | 60.6287 | 48.4627 | 2585.3939
2031-09-03 13:00 | 9137.5 | 2.9859 | 61.3101 | 48.4627 | 2677.9369
2031-09-04 14:00 | 9684.75 | 3.1744 | 61.4715 | 48.4627 | 2838.32
2031-09-05 15:00 | 11120.2 | 3.5999 | 61.7624 | 48.4627 | 3259.0089
2031-09-06 16:00 | 11594.8 | 3.7684 | 61.9624 | 48.4627 | 3398.1004
2031-09-07 17:00 | 11442.6 | 3.7348 | 62.127 | 48.4627 | 3353.495
2031-09-08 18:00 | 9796.22 | 3.167 | 62.3631 | 48.4627 | 2870.9887
2031-09-09 19:00 | 8338.91 | 2.6338 | 62.5842 | 48.4627 | 2443.8933
2031-09-10 20:00 | 5995.55 | 1.8651 | 62.6576 | 48.4627 | 1757.1223
2031-09-11 21:00 | 4940.44 | 1.5413 | 62.3783 | 48.4627 | 1447.9
2031-09-12 22:00 | 3080.31 | 1 | 63.7402 | 48.4627 | 902.7497
2031-09-13 23:00 | 3114.49 | 1 | 49.9431 | 48.4627 | 912.7669
2031-09-15 | 3112.83 | 1 | 49.7689 | 48.4627 | 912.2804
2031-09-16 01:00 | 3087.38 | 1 | 49.664 | 48.4627 | 904.8218
2031-09-17 02:00 | 3192.15 | 1 | 49.5517 | 48.4627 | 935.5268
2031-09-18 03:00 | 3184.36 | 1 | 49.4889 | 48.4627 | 933.2438
2031-09-19 04:00 | 3183.41 | 1 | 49.4455 | 48.4627 | 932.9654
2031-09-20 05:00 | 3216.72 | 1 | 49.3826 | 48.4627 | 942.7276
2031-09-21 06:00 | 3192.88 | 1 | 65.0475 | 48.4627 | 935.7408
2031-09-22 07:00 | 3677.43 | 1.1355 | 61.3415 | 48.4627 | 1077.7483
2031-09-23 08:00 | 3268.56 | 1.0113 | 61.3535 | 48.4627 | 957.9204
2031-09-24 09:00 | 3967.43 | 1.2304 | 61.2882 | 48.4627 | 1162.739
2031-09-25 10:00 | 5577 | 1.6608 | 61.7744 | 48.4627 | 1634.4574
2031-09-26 11:00 | 6305.1 | 2.033 | 61.0735 | 48.4627 | 1847.8424
2031-09-27 12:00 | 7430.81 | 2.3928 | 61.2379 | 48.4627 | 2177.7554
2031-09-28 13:00 | 8253.62 | 2.6751 | 61.3493 | 48.4627 | 2418.8972
2031-09-29 14:00 | 8735.18 | 2.8299 | 61.5522 | 48.4627 | 2560.0285
2031-09-30 15:00 | 10879.8 | 3.5547 | 61.6249 | 48.4627 | 3188.5546
2031-10-01 16:00 | 11251.7 | 3.7213 | 61.8022 | 48.4627 | 3297.5478
2031-10-02 17:00 | 11550.7 | 3.7268 | 62.288 | 48.4627 | 3385.176
2031-10-03 18:00 | 10355.1 | 3.2124 | 62.8944 | 48.4627 | 3034.7802
2031-10-04 19:00 | 8804.77 | 2.7734 | 62.7736 | 48.4627 | 2580.4234
2031-10-05 20:00 | 7054.87 | 2.0737 | 63.4909 | 48.4627 | 2067.5783
2031-10-06 21:00 | 5460.12 | 1.6256 | 63.1812 | 48.4627 | 1600.2032
2031-10-07 22:00 | 3224.81 | 1 | 64.3201 | 48.4627 | 945.0985
2031-10-08 23:00 | 3161.83 | 1 | 50.1964 | 48.4627 | 926.6409
2031-10-10 | 3037.08 | 1 | 50.0446 | 48.4627 | 890.0803
2031-10-11 01:00 | 78.0723 | 1 | 50.9205 | 48.4627 | 22.8807
2031-10-12 02:00 | -130.921 | 1.0703 | 50.1405 | 48.4627 | -38.3692
2031-10-13 03:00 | -256.418 | 1.4308 | 49.664 | 48.4627 | -75.1487
2031-10-14 04:00 | -175.239 | 1.1314 | 49.5652 | 48.4627 | -51.3575
2031-10-15 05:00 | 1536.01 | 1 | 49.4002 | 48.4627 | 450.1601
2031-10-16 06:00 | 2676.26 | 1 | 49.0205 | 48.4627 | 784.3344
2031-10-17 07:00 | 2916.14 | 1 | 49.0457 | 48.4627 | 854.6363
2031-10-18 08:00 | 2974.86 | 1 | 49.0862 | 48.4627 | 871.8454
2031-10-19 09:00 | 3114.75 | 1 | 49.0751 | 48.4627 | 912.8431
2031-10-20 10:00 | 3131.84 | 1 | 49.1168 | 48.4627 | 917.8517
2031-10-21 11:00 | 3291.68 | 1.0713 | 60.6157 | 48.4627 | 964.6962
2031-10-22 12:00 | 4044.58 | 1.2704 | 60.9489 | 48.4627 | 1185.3494
2031-10-23 13:00 | 4269.14 | 1.3598 | 60.8734 | 48.4627 | 1251.1614
2031-10-24 14:00 | 5468.17 | 1.7756 | 60.7289 | 48.4627 | 1602.5624
2031-10-25 15:00 | 6568.69 | 2.1413 | 60.8203 | 48.4627 | 1925.093
2031-10-26 16:00 | 6872.64 | 2.2298 | 61.0495 | 48.4627 | 2014.172
2031-10-27 17:00 | 7066.1 | 2.3387 | 60.9627 | 48.4627 | 2070.8695
2031-10-28 18:00 | 5810.27 | 1.7815 | 61.864 | 48.4627 | 1702.822
2031-10-29 19:00 | 4580.84 | 1.4262 | 61.6538 | 48.4627 | 1342.5117
2031-10-30 20:00 | 3076.74 | 1 | 67.3451 | 48.4627 | 901.7035
2031-10-31 21:00 | 3118.42 | 1 | 49.4116 | 48.4627 | 913.9187
2031-11-01 22:00 | 0 | 0 | 50.3945 | 48.4627 | 0
2031-11-02 23:00 | -619.039 | 2.5425 | 49.2071 | 48.4627 | -181.4224
2031-11-04 | -805.633 | 3.1015 | 48.8713 | 48.4627 | -236.1077
2031-11-05 01:00 | -1001.68 | 3.7024 | 48.6687 | 48.4627 | -293.5634
2031-11-06 02:00 | -1141.57 | 4.1133 | 48.4982 | 48.4627 | -334.5611
2031-11-07 03:00 | -1226.25 | 4.3622 | 48.3288 | 48.4627 | -359.3784
2031-11-08 04:00 | -1368.45 | 4.8218 | 48.2125 | 48.4627 | -401.0531
2031-11-09 05:00 | -1267.77 | 4.4372 | 48.0898 | 48.4627 | -371.5467
2031-11-10 06:00 | 0 | 0 | 48.9674 | 48.4627 | 0
2031-11-11 07:00 | 1867.65 | 1 | 48.3713 | 48.4627 | 547.3542
2031-11-12 08:00 | 2714.44 | 1 | 48.2663 | 48.4627 | 795.5238
2031-11-13 09:00 | 2864.43 | 1 | 61.6273 | 48.4627 | 839.4816
2031-11-14 10:00 | 4243.5 | 1.4391 | 59.4249 | 48.4627 | 1243.6471
2031-11-15 11:00 | 5488.44 | 1.8568 | 59.671 | 48.4627 | 1608.503
2031-11-16 12:00 | 6267.26 | 2.0861 | 60.088 | 48.4627 | 1836.7526
2031-11-17 13:00 | 6575.73 | 2.1561 | 60.4556 | 48.4627 | 1927.1562
2031-11-18 14:00 | 7049.69 | 2.3203 | 60.5784 | 48.4627 | 2066.0602
2031-11-19 15:00 | 7144.59 | 2.3551 | 60.7276 | 48.4627 | 2093.8726
2031-11-20 16:00 | 9518 | 3.174 | 60.7291 | 48.4627 | 2789.4504
2031-11-21 17:00 | 8829.94 | 2.8519 | 61.3767 | 48.4627 | 2587.8
2031-11-22 18:00 | 7356.29 | 2.3348 | 61.7018 | 48.4627 | 2155.9158
2031-11-23 19:00 | 5890.42 | 1.8736 | 61.6367 | 48.4627 | 1726.3117
2031-11-24 20:00 | 4499.64 | 1.4227 | 61.5913 | 48.4627 | 1318.7143
2031-11-25 21:00 | 3523.24 | 1.133 | 61.2643 | 48.4627 | 1032.5597
2031-11-26 22:00 | 3133.58 | 1 | 64.372 | 48.4627 | 918.3616
2031-11-27 23:00 | 0 | 0 | 50.4332 | 48.4627 | 0
2031-11-29 | -684.043 | 2.6874 | 49.1812 | 48.4627 | -200.4732
2031-11-30 01:00 | -1026.38 | 3.8208 | 48.8437 | 48.4627 | -300.8023
2031-12-01 02:00 | -1358.29 | 4.8211 | 48.6026 | 48.4627 | -398.0755
2031-12-02 03:00 | -1509.74 | 5.2337 | 48.3955 | 48.4627 | -442.4611
2031-12-03 04:00 | -1701.49 | 5.8528 | 48.1982 | 48.4627 | -498.6575
2031-12-04 05:00 | -1220.92 | 4.1631 | 48.0466 | 48.4627 | -357.8163
2031-12-05 06:00 | 0 | 1 | 48.9726 | 48.4627 | 0
2031-12-06 07:00 | 2831.44 | 1 | 61.6411 | 48.4627 | 829.8132
2031-12-07 08:00 | 2988.09 | 1 | 60.9459 | 48.4627 | 875.7227
2031-12-08 09:00 | 4351.6 | 1.395 | 59.9798 | 48.4627 | 1275.3281
2031-12-09 10:00 | 6041.81 | 2.0209 | 59.7456 | 48.4627 | 1770.6797
2031-12-10 11:00 | 7319.48 | 2.498 | 59.8644 | 48.4627 | 2145.1278
2031-12-11 12:00 | 7676.2 | 2.5773 | 60.3506 | 48.4627 | 2249.6721
2031-12-12 13:00 | 7759.58 | 2.521 | 60.9065 | 48.4627 | 2274.1084
2031-12-13 14:00 | 7312.81 | 2.3628 | 61.1407 | 48.4627 | 2143.1731
2031-12-14 15:00 | 6968.33 | 2.202 | 61.4713 | 48.4627 | 2042.2159
2031-12-15 16:00 | 8636.74 | 2.8219 | 61.1561 | 48.4627 | 2531.1786
2031-12-16 17:00 | 7131.12 | 2.2525 | 61.7209 | 48.4627 | 2089.925
2031-12-17 18:00 | 6289.19 | 1.9043 | 62.1793 | 48.4627 | 1843.1796
2031-12-18 19:00 | 4971.79 | 1.5003 | 62.139 | 48.4627 | 1457.0878
2031-12-19 20:00 | 3815.01 | 1.2174 | 61.4129 | 48.4627 | 1118.0691
2031-12-20 21:00 | 3172.98 | 1 | 61.6006 | 48.4627 | 929.9086
2031-12-21 22:00 | 3135.54 | 1 | 67.818 | 48.4627 | 918.9361
2031-12-22 23:00 | 0 | 0 | 50.4032 | 48.4627 | 0
2031-12-24 | -546.514 | 2.218 | 49.2011 | 48.4627 | -160.1674
2031-12-25 01:00 | -669.283 | 2.6828 | 48.9226 | 48.4627 | -196.1475
2031-12-26 02:00 | -727.46 | 2.8319 | 48.7408 | 48.4627 | -213.1975
2031-12-27 03:00 | -652.911 | 2.5721 | 48.6213 | 48.4627 | -191.3493
2031-12-28 04:00 | -621.614 | 2.5005 | 48.5103 | 48.4627 | -182.1771
2031-12-29 05:00 | -249.895 | 1.2724 | 48.6206 | 48.4627 | -73.237
2031-12-30 06:00 | 0 | 1 | 49.2615 | 48.4627 | 0
2031-12-31 07:00 | 2926.77 | 1 | 48.2394 | 48.4627 | 857.7516
2032-01-01 08:00 | -88.8568 | 1.011 | 49.195 | 48.4627 | -26.0414
2032-01-02 09:00 | 1673.37 | 1 | 48.7515 | 48.4627 | 490.4163
2032-01-03 10:00 | 2729.56 | 1 | 48.4303 | 48.4627 | 799.9551
2032-01-04 11:00 | 3012.67 | 1.0057 | 59.6815 | 48.4627 | 882.9264
2032-01-05 12:00 | 4978.08 | 1.6092 | 60.0677 | 48.4627 | 1458.9312
2032-01-06 13:00 | 6281.23 | 2.0622 | 60.1017 | 48.4627 | 1840.8468
2032-01-07 14:00 | 7429.17 | 2.4864 | 60.1909 | 48.4627 | 2177.2748
2032-01-08 15:00 | 9370.37 | 3.1731 | 60.338 | 48.4627 | 2746.1844
2032-01-09 16:00 | 9961.44 | 3.305 | 60.8908 | 48.4627 | 2919.4099
2032-01-10 17:00 | 10013.5 | 3.2877 | 61.2955 | 48.4627 | 2934.6672
2032-01-11 18:00 | 8628.24 | 2.7781 | 61.7076 | 48.4627 | 2528.6875
2032-01-12 19:00 | 7156.83 | 2.2611 | 61.9314 | 48.4627 | 2097.4598
2032-01-13 20:00 | 4716.8 | 1.3781 | 62.7529 | 48.4627 | 1382.3576
2032-01-14 21:00 | 3528.91 | 1.1249 | 61.5541 | 48.4627 | 1034.2214
2032-01-15 22:00 | 3075.63 | 1 | 49.6675 | 48.4627 | 901.3782
2032-01-16 23:00 | 1440.59 | 1 | 50.0839 | 48.4627 | 422.1953
2032-01-18 | 118.087 | 1 | 50.2862 | 48.4627 | 34.6079
2032-01-19 01:00 | -99.8308 | 0.98055 | 49.6972 | 48.4627 | -29.2575
2032-01-20 02:00 | -132.024 | 1.0398 | 49.4324 | 48.4627 | -38.6924
2032-01-21 03:00 | -275.009 | 1.5041 | 49.1053 | 48.4627 | -80.5972
2032-01-22 04:00 | -334.293 | 1.6548 | 48.898 | 48.4627 | -97.9716
2032-01-23 05:00 | 174.789 | 1 | 49.4044 | 48.4627 | 51.2256
2032-01-24 06:00 | 99.7491 | 1 | 49.3925 | 48.4627 | 29.2336
2032-01-25 07:00 | 2163.8 | 1 | 48.6199 | 48.4627 | 634.1472
2032-01-26 08:00 | 2815.14 | 1 | 48.5543 | 48.4627 | 825.0361
2032-01-27 09:00 | 3335.93 | 1.0435 | 60.5001 | 48.4627 | 977.6646
2032-01-28 10:00 | 4502.37 | 1.4645 | 60.1558 | 48.4627 | 1319.5144
2032-01-29 11:00 | 4815.33 | 1.6061 | 60.0841 | 48.4627 | 1411.2339
2032-01-30 12:00 | 5425.6 | 1.742 | 60.6351 | 48.4627 | 1590.0864
2032-01-31 13:00 | 6255.42 | 2.0431 | 60.5914 | 48.4627 | 1833.2826
2032-02-01 14:00 | 6823.57 | 2.2062 | 60.867 | 48.4627 | 1999.791
2032-02-02 15:00 | 8329.27 | 2.8314 | 60.5139 | 48.4627 | 2441.0681
2032-02-03 16:00 | 8874.81 | 2.946 | 60.9922 | 48.4627 | 2600.9501
2032-02-04 17:00 | 9193.07 | 3.0023 | 61.3691 | 48.4627 | 2694.2229
2032-02-05 18:00 | 7841.06 | 2.4916 | 61.8414 | 48.4627 | 2297.9878
2032-02-06 19:00 | 6323.48 | 1.9366 | 62.2496 | 48.4627 | 1853.229
2032-02-07 20:00 | 3550.81 | 1.147 | 61.5869 | 48.4627 | 1040.6397
2032-02-08 21:00 | 2880.67 | 1 | 66.1738 | 48.4627 | 844.241
2032-02-09 22:00 | 0 | 0 | 50.6141 | 48.4627 | 0
2032-02-10 23:00 | -496.715 | 2.0996 | 49.4133 | 48.4627 | -145.5728
2032-02-12 | -917.668 | 3.5125 | 49.0411 | 48.4627 | -268.9419
2032-02-13 01:00 | -1164.68 | 4.196 | 48.7664 | 48.4627 | -341.334
2032-02-14 02:00 | -1487.75 | 5.2171 | 48.5679 | 48.4627 | -436.0165
2032-02-15 03:00 | -1560.78 | 5.3638 | 48.3629 | 48.4627 | -457.4195
2032-02-16 04:00 | -1447.64 | 4.9741 | 48.232 | 48.4627 | -424.2614
2032-02-17 05:00 | -652.31 | 2.344 | 48.1666 | 48.4627 | -191.1732
2032-02-18 06:00 | 502.52 | 1 | 48.9227 | 48.4627 | 147.2741
2032-02-19 07:00 | 2213.24 | 1 | 60.4807 | 48.4627 | 648.6366
2032-02-20 08:00 | 2759.85 | 1 | 62.7272 | 48.4627 | 808.8322
2032-02-21 09:00 | 4055.52 | 1.3038 | 59.9978 | 48.4627 | 1188.5556
2032-02-22 10:00 | 5571.79 | 1.888 | 59.6835 | 48.4627 | 1632.9305
2032-02-23 11:00 | 6578.69 | 2.2824 | 59.7391 | 48.4627 | 1928.0237
2032-02-24 12:00 | 7233.64 | 2.402 | 60.445 | 48.4627 | 2119.9706
2032-02-25 13:00 | 7708.88 | 2.4577 | 61.0895 | 48.4627 | 2259.2497
2032-02-26 14:00 | 8215.09 | 2.67 | 61.0931 | 48.4627 | 2407.6052
2032-02-27 15:00 | 9584.08 | 3.1476 | 61.1731 | 48.4627 | 2808.8166
2032-02-28 16:00 | 10118.4 | 3.3119 | 61.467 | 48.4627 | 2965.4103
2032-02-29 17:00 | 10186.1 | 3.3052 | 61.7771 | 48.4627 | 2985.2512
2032-03-01 18:00 | 8948.95 | 2.8625 | 62.0924 | 48.4627 | 2622.6784
2032-03-02 19:00 | 7269.77 | 2.2872 | 62.2877 | 48.4627 | 2130.5593
2032-03-03 20:00 | 4888.05 | 1.4974 | 62.4899 | 48.4627 | 1432.546
2032-03-04 21:00 | 3498.9 | 1.0885 | 62.071 | 48.4627 | 1025.4264
2032-03-05 22:00 | 3095.25 | 1 | 49.8899 | 48.4627 | 907.1282
2032-03-06 23:00 | 3035.49 | 1 | 49.7348 | 48.4627 | 889.6143
2032-03-08 | 206.096 | 1 | 50.5862 | 48.4627 | 60.4008
2032-03-09 01:00 | -180.893 | 1.2501 | 49.8104 | 48.4627 | -53.0145
2032-03-10 02:00 | -414.124 | 1.9327 | 49.3349 | 48.4627 | -121.3678
2032-03-11 03:00 | -474.672 | 2.0656 | 49.1167 | 48.4627 | -139.1126
2032-03-12 04:00 | -493.084 | 2.1162 | 48.9556 | 48.4627 | -144.5087
2032-03-13 05:00 | 2066.5 | 1 | 48.8922 | 48.4627 | 605.6314
2032-03-14 06:00 | 2933.3 | 1 | 48.7499 | 48.4627 | 859.6654
2032-03-15 07:00 | 3057.13 | 1 | 60.8971 | 48.4627 | 895.9564
2032-03-16 08:00 | 3325.44 | 1.0523 | 60.6484 | 48.4627 | 974.5903
2032-03-17 09:00 | 5198.33 | 1.6466 | 60.7121 | 48.4627 | 1523.4801
2032-03-18 10:00 | 6704.49 | 2.2111 | 60.5256 | 48.4627 | 1964.8921
2032-03-19 11:00 | 7856.27 | 2.5698 | 60.8631 | 48.4627 | 2302.4455
2032-03-20 12:00 | 8289.51 | 2.7651 | 60.9259 | 48.4627 | 2429.4156
2032-03-21 13:00 | 8928.77 | 2.9166 | 61.3595 | 48.4627 | 2616.7642
2032-03-22 14:00 | 9440.34 | 3.0275 | 61.7808 | 48.4627 | 2766.6905
2032-03-23 15:00 | 10771.2 | 3.5225 | 61.7788 | 48.4627 | 3156.7271
2032-03-24 16:00 | 11339.6 | 3.6444 | 62.2282 | 48.4627 | 3323.3087
2032-03-25 17:00 | 10994.5 | 3.5573 | 62.3767 | 48.4627 | 3222.1699
2032-03-26 18:00 | 9555.15 | 3.0269 | 62.7282 | 48.4627 | 2800.338
2032-03-27 19:00 | 7897.36 | 2.4495 | 62.944 | 48.4627 | 2314.4877
2032-03-28 20:00 | 5314.87 | 1.5899 | 63.248 | 48.4627 | 1557.6346
2032-03-29 21:00 | 3851.23 | 1.2168 | 62.3697 | 48.4627 | 1128.6841
2032-03-30 22:00 | 3057.84 | 1 | 50.3376 | 48.4627 | 896.1644
2032-03-31 23:00 | 3026.63 | 1 | 50.1105 | 48.4627 | 887.0177
2032-04-02 | 85.7881 | 1 | 50.9714 | 48.4627 | 25.142
2032-04-03 01:00 | -163.737 | 1.1759 | 50.1407 | 48.4627 | -47.9866
2032-04-04 02:00 | -334.044 | 1.6715 | 49.6829 | 48.4627 | -97.8986
2032-04-05 03:00 | -363.659 | 1.7211 | 49.4711 | 48.4627 | -106.5779
2032-04-06 04:00 | -246.263 | 1.3338 | 49.4069 | 48.4627 | -72.1726
2032-04-07 05:00 | 1715.01 | 1 | 49.3007 | 48.4627 | 502.6198
2032-04-08 06:00 | 2649.32 | 1 | 49.0749 | 48.4627 | 776.439
2032-04-09 07:00 | 2994.99 | 1 | 62.792 | 48.4627 | 877.7449
2032-04-10 08:00 | 3039.64 | 1 | 66.4774 | 48.4627 | 890.8305
2032-04-11 09:00 | 3461.45 | 1.1172 | 60.6891 | 48.4627 | 1014.4509
2032-04-12 10:00 | 5105.5 | 1.6183 | 60.9666 | 48.4627 | 1496.2743
2032-04-13 11:00 | 6526.5 | 2.1567 | 60.7069 | 48.4627 | 1912.7283
2032-04-14 12:00 | 7573.35 | 2.4643 | 61.1083 | 48.4627 | 2219.5298
2032-04-15 13:00 | 7986.55 | 2.6194 | 61.263 | 48.4627 | 2340.6268
2032-04-16 14:00 | 8920.24 | 2.8648 | 61.6777 | 48.4627 | 2614.2643
2032-04-17 15:00 | 10296 | 3.3613 | 61.7314 | 48.4627 | 3017.4597
2032-04-18 16:00 | 10648.7 | 3.4988 | 61.9467 | 48.4627 | 3120.8259
2032-04-19 17:00 | 10339.8 | 3.3508 | 62.2899 | 48.4627 | 3030.2962
2032-04-20 18:00 | 9019.77 | 2.9091 | 62.4497 | 48.4627 | 2643.4336
2032-04-21 19:00 | 7558.01 | 2.3945 | 62.6267 | 48.4627 | 2215.0341
2032-04-22 20:00 | 5285.85 | 1.5905 | 63.1027 | 48.4627 | 1549.1297
2032-04-23 21:00 | 4057.67 | 1.2492 | 62.6134 | 48.4627 | 1189.1857
2032-04-24 22:00 | 3091.28 | 1 | 50.3364 | 48.4627 | 905.9647
2032-04-25 23:00 | 2999.58 | 1 | 50.1389 | 48.4627 | 879.0901
2032-04-27 | 651.927 | 1 | 50.8005 | 48.4627 | 191.0609
2032-04-28 01:00 | 0 | 0 | 50.7038 | 48.4627 | 0
2032-04-29 02:00 | -145.854 | 1.13 | 50.0109 | 48.4627 | -42.7456
2032-04-30 03:00 | -310.139 | 1.5999 | 49.6155 | 48.4627 | -90.8928
2032-05-01 04:00 | -455.18 | 2.0304 | 49.3553 | 48.4627 | -133.4001
2032-05-02 05:00 | -423.191 | 1.8842 | 49.1817 | 48.4627 | -124.025
2032-05-03 06:00 | 243.881 | 1 | 49.7447 | 48.4627 | 71.4745
2032-05-04 07:00 | 2106.42 | 1 | 49.078 | 48.4627 | 617.3308
2032-05-05 08:00 | 2746.62 | 1 | 49.0028 | 48.4627 | 804.9549
2032-05-06 09:00 | 3087.17 | 1.0179 | 60.3494 | 48.4627 | 904.7602
2032-05-07 10:00 | 5156.56 | 1.7071 | 60.3516 | 48.4627 | 1511.2386
2032-05-08 11:00 | 5418.59 | 1.6333 | 61.5989 | 48.4627 | 1588.032
2032-05-09 12:00 | 6806.22 | 2.1936 | 61.0481 | 48.4627 | 1994.7062
2032-05-10 13:00 | 7451.2 | 2.4271 | 61.1628 | 48.4627 | 2183.7312
2032-05-11 14:00 | 8399.01 | 2.7607 | 61.2779 | 48.4627 | 2461.5068
2032-05-12 15:00 | 9046.54 | 2.9305 | 61.655 | 48.4627 | 2651.2792
2032-05-13 16:00 | 11749.6 | 3.8194 | 61.8133 | 48.4627 | 3443.4678
2032-05-14 17:00 | 8632.47 | 2.5034 | 63.4865 | 48.4627 | 2529.9272
2032-05-15 18:00 | 7232.47 | 2.2176 | 62.8176 | 48.4627 | 2119.6277
2032-05-16 19:00 | 5792.43 | 1.7771 | 62.6898 | 48.4627 | 1697.5937
2032-05-17 20:00 | 4894.47 | 1.4862 | 62.6702 | 48.4627 | 1434.4276
2032-05-18 21:00 | 3686.42 | 1.1876 | 61.8978 | 48.4627 | 1080.3831
2032-05-19 22:00 | 2976 | 1 | 63.4378 | 48.4627 | 872.1795
2032-05-20 23:00 | 0 | 0 | 50.9995 | 48.4627 | 0
2032-05-22 | -330.754 | 1.5597 | 49.8955 | 48.4627 | -96.9344
2032-05-23 01:00 | -635.396 | 2.6184 | 49.5355 | 48.4627 | -186.2162
2032-05-24 02:00 | -945.003 | 3.5367 | 49.2612 | 48.4627 | -276.953
2032-05-25 03:00 | -1192.08 | 4.2682 | 49.0346 | 48.4627 | -349.3642
2032-05-26 04:00 | -1488.42 | 5.1927 | 48.81 | 48.4627 | -436.2128
2032-05-27 05:00 | -1461.8 | 5.0106 | 48.6497 | 48.4627 | -428.4113
2032-05-28 06:00 | -497.977 | 1.8134 | 48.5941 | 48.4627 | -145.9427
2032-05-29 07:00 | 2321.6 | 1 | 48.727 | 48.4627 | 680.3938
2032-05-30 08:00 | 3038.71 | 1 | 48.72 | 48.4627 | 890.558
2032-05-31 09:00 | 3117.08 | 1 | 48.8733 | 48.4627 | 913.526
2032-06-01 10:00 | 3178.84 | 1.0126 | 60.6717 | 48.4627 | 931.626
2032-06-02 11:00 | 4511.6 | 1.4356 | 60.733 | 48.4627 | 1322.2194
2032-06-03 12:00 | 5041.5 | 1.6905 | 60.3818 | 48.4627 | 1477.5178
2032-06-04 13:00 | 5203.04 | 1.6826 | 60.8955 | 48.4627 | 1524.8605
2032-06-05 14:00 | 5471.17 | 1.777 | 60.9346 | 48.4627 | 1603.4416
2032-06-06 15:00 | 5794.85 | 1.892 | 60.9659 | 48.4627 | 1698.3029
2032-06-07 16:00 | 8359.62 | 2.7591 | 60.9403 | 48.4627 | 2449.9628
2032-06-08 17:00 | 7452.38 | 2.4451 | 61.3159 | 48.4627 | 2184.077
2032-06-09 18:00 | 6446.93 | 2.0591 | 61.7047 | 48.4627 | 1889.4087
2032-06-10 19:00 | 5116.96 | 1.6232 | 61.7471 | 48.4627 | 1499.6329
2032-06-11 20:00 | 3985.26 | 1.2678 | 61.6222 | 48.4627 | 1167.9644
2032-06-12 21:00 | 3106.59 | 1 | 62.2392 | 48.4627 | 910.4517
2032-06-13 22:00 | 3108.56 | 1 | 49.6391 | 48.4627 | 911.029
2032-06-14 23:00 | 0 | 0 | 50.6213 | 48.4627 | 0
2032-06-16 | -865.814 | 3.3789 | 49.4056 | 48.4627 | -253.745
2032-06-17 01:00 | -1238.5 | 4.4397 | 49.0471 | 48.4627 | -362.9685
2032-06-18 02:00 | -1472.37 | 5.118 | 48.8295 | 48.4627 | -431.5091
2032-06-19 03:00 | -1487.6 | 5.1055 | 48.6555 | 48.4627 | -435.9725
2032-06-20 04:00 | -1250.47 | 4.3204 | 48.498 | 48.4627 | -366.4766
2032-06-21 05:00 | -364.633 | 1.4497 | 48.5461 | 48.4627 | -106.8634
2032-06-22 06:00 | 1945.63 | 1 | 48.7489 | 48.4627 | 570.2079
2032-06-23 07:00 | 2892.65 | 1 | 61.8743 | 48.4627 | 847.752
2032-06-24 08:00 | 3462.63 | 1.101 | 60.4204 | 48.4627 | 1014.7967
2032-06-25 09:00 | 5477.04 | 1.7622 | 60.4416 | 48.4627 | 1605.162
2032-06-26 10:00 | 7016.19 | 2.3565 | 60.2825 | 48.4627 | 2056.2423
2032-06-27 11:00 | 8718.98 | 2.8429 | 60.9253 | 48.4627 | 2555.2808
2032-06-28 12:00 | 9510.83 | 3.0671 | 61.3978 | 48.4627 | 2787.3491
2032-06-29 13:00 | 9771.42 | 3.2164 | 61.5 | 48.4627 | 2863.7205
2032-06-30 14:00 | 10128 | 3.2874 | 61.9013 | 48.4627 | 2968.2238
2032-07-01 15:00 | 11922.2 | 3.7725 | 62.3909 | 48.4627 | 3494.0519
2032-07-02 16:00 | 11661 | 3.8267 | 62.3424 | 48.4627 | 3417.5017
2032-07-03 17:00 | 11149.3 | 3.7067 | 62.4144 | 48.4627 | 3267.5373
2032-07-04 18:00 | 9982.55 | 3.0895 | 63.2683 | 48.4627 | 2925.5966
2032-07-05 19:00 | 8463.74 | 2.7056 | 62.9317 | 48.4627 | 2480.4773
2032-07-06 20:00 | 6405.44 | 1.9414 | 63.4355 | 48.4627 | 1877.2492
2032-07-07 21:00 | 5275.01 | 1.6317 | 62.9847 | 48.4627 | 1545.9528
2032-07-08 22:00 | 3086.7 | 1 | 62.2822 | 48.4627 | 904.6225
2032-07-09 23:00 | 3119.89 | 1 | 65.9182 | 48.4627 | 914.3495
2032-07-11 | 3261 | 1 | 50.2141 | 48.4627 | 955.7048
2032-07-12 01:00 | 3389.76 | 1 | 50.0843 | 48.4627 | 993.4406
2032-07-13 02:00 | 3165.68 | 1 | 50.1072 | 48.4627 | 927.7692
2032-07-14 03:00 | 3250.53 | 1 | 49.9981 | 48.4627 | 952.6363
2032-07-15 04:00 | 3213.73 | 1 | 49.9821 | 48.4627 | 941.8513
2032-07-16 05:00 | 3281.96 | 1 | 49.9262 | 48.4627 | 961.8475
2032-07-17 06:00 | 3245.33 | 1 | 64.1932 | 48.4627 | 951.1123
2032-07-18 07:00 | 4342.56 | 1.3356 | 61.9577 | 48.4627 | 1272.6787
2032-07-19 08:00 | 5310.93 | 1.5386 | 62.7236 | 48.4627 | 1556.4799
2032-07-20 09:00 | 7286.34 | 2.3924 | 61.4796 | 48.4627 | 2135.4155
2032-07-21 10:00 | 8877.4 | 2.9854 | 61.5065 | 48.4627 | 2601.7091
2032-07-22 11:00 | 10151.5 | 3.4909 | 61.5914 | 48.4627 | 2975.111
2032-07-23 12:00 | 11590.3 | 3.7872 | 62.4164 | 48.4627 | 3396.7816
2032-07-24 13:00 | 12146.3 | 3.9578 | 62.7833 | 48.4627 | 3559.7291
2032-07-25 14:00 | 13319.6 | 4.3149 | 63.129 | 48.4627 | 3903.5894
2032-07-26 15:00 | 14434.2 | 4.7038 | 63.3656 | 48.4627 | 4230.2464
2032-07-27 16:00 | 15220.3 | 4.8719 | 63.8688 | 48.4627 | 4460.6296
2032-07-28 17:00 | 15232.5 | 4.8037 | 64.3297 | 48.4627 | 4464.2051
2032-07-29 18:00 | 13534.4 | 4.305 | 64.4719 | 48.4627 | 3966.5411
2032-07-30 19:00 | 11781.5 | 3.6631 | 64.759 | 48.4627 | 3452.8168
2032-07-31 20:00 | 9774.39 | 2.9465 | 65.0281 | 48.4627 | 2864.5909
2032-08-01 21:00 | 8187.55 | 2.5744 | 64.3837 | 48.4627 | 2399.534
2032-08-02 22:00 | 6317.64 | 1.8238 | 65.1164 | 48.4627 | 1851.5175
2032-08-03 23:00 | 4628.25 | 1.414 | 64.1716 | 48.4627 | 1356.4062
2032-08-05 | 4224.65 | 1.2651 | 64.0669 | 48.4627 | 1238.1227
2032-08-06 01:00 | 3329.98 | 1.0615 | 63.1541 | 48.4627 | 975.9208
2032-08-07 02:00 | 3212.59 | 1 | 64.3936 | 48.4627 | 941.5172
2032-08-08 03:00 | 3037.55 | 1 | 65.8805 | 48.4627 | 890.218
2032-08-09 04:00 | 3109.75 | 1 | 67.5819 | 48.4627 | 911.3778
2032-08-10 05:00 | 3429.3 | 1 | 64.4545 | 48.4627 | 1005.0286
2032-08-11 06:00 | 6025.15 | 1.8119 | 63.0433 | 48.4627 | 1765.7972
2032-08-12 07:00 | 7046.84 | 2.2635 | 62.5251 | 48.4627 | 2065.2249
2032-08-13 08:00 | 6630.75 | 2.0353 | 63.2108 | 48.4627 | 1943.281
2032-08-14 09:00 | 8222.74 | 2.5777 | 63.0291 | 48.4627 | 2409.8472
2032-08-15 10:00 | 9924.8 | 3.2477 | 62.7745 | 48.4627 | 2908.6718
2032-08-16 11:00 | 10701.5 | 3.6491 | 62.6688 | 48.4627 | 3136.3001
2032-08-17 12:00 | 11552.5 | 3.8489 | 63.1309 | 48.4627 | 3385.7035
2032-08-18 13:00 | 8914.61 | 3.0548 | 63.0801 | 48.4627 | 2612.6143
2032-08-19 14:00 | 9532.2 | 3.0943 | 63.5442 | 48.4627 | 2793.6121
2032-08-20 15:00 | 9763.43 | 3.1749 | 63.5521 | 48.4627 | 2861.3789
2032-08-21 16:00 | 12725.4 | 4.1461 | 63.5827 | 48.4627 | 3729.4466
2032-08-22 17:00 | 12231.4 | 3.8629 | 64.2207 | 48.4627 | 3584.6695
2032-08-23 18:00 | 11152.5 | 3.4941 | 64.4201 | 48.4627 | 3268.4751
2032-08-24 19:00 | 9637.93 | 3.0154 | 64.4393 | 48.4627 | 2824.5985
2032-08-25 20:00 | 8466.98 | 2.5859 | 64.6238 | 48.4627 | 2481.4269
2032-08-26 21:00 | 7232.28 | 2.2637 | 64.2441 | 48.4627 | 2119.572
2032-08-27 22:00 | 6530.37 | 1.9665 | 64.4746 | 48.4627 | 1913.8625
2032-08-28 23:00 | 4059.57 | 1.2123 | 64.3979 | 48.4627 | 1189.7425
2032-08-30 | 3096.75 | 1.0279 | 62.9222 | 48.4627 | 907.5678
2032-08-31 01:00 | 3101.65 | 1 | 64.826 | 48.4627 | 909.0039
2032-09-01 02:00 | 3080.81 | 1 | 65.3227 | 48.4627 | 902.8963
2032-09-02 03:00 | 3139.89 | 1 | 64.7313 | 48.4627 | 920.2109
2032-09-03 04:00 | 3103.14 | 1 | 62.5915 | 48.4627 | 909.4406
2032-09-04 05:00 | 4542.34 | 1.4646 | 62.4807 | 48.4627 | 1331.2284
2032-09-05 06:00 | 5675.99 | 1.7377 | 63.1053 | 48.4627 | 1663.4685
2032-09-06 07:00 | 6860.79 | 2.1618 | 62.9123 | 48.4627 | 2010.6991
2032-09-07 08:00 | 7165.17 | 2.1932 | 63.3945 | 48.4627 | 2099.904
2032-09-08 09:00 | 8829.78 | 2.8515 | 62.9325 | 48.4627 | 2587.7531
2032-09-09 10:00 | 10307.8 | 3.3889 | 62.9793 | 48.4627 | 3020.918
2032-09-10 11:00 | 11997.6 | 3.8807 | 63.4366 | 48.4627 | 3516.1495
2032-09-11 12:00 | 12953.3 | 4.1424 | 63.8911 | 48.4627 | 3796.2375
2032-09-12 13:00 | 13383 | 4.2755 | 64.2159 | 48.4627 | 3922.1701
2032-09-13 14:00 | 14249.4 | 4.4863 | 64.6365 | 48.4627 | 4176.0869
2032-09-14 15:00 | 15994.5 | 5.0798 | 64.8181 | 48.4627 | 4687.5252
2032-09-15 16:00 | 16615 | 5.3433 | 65.0471 | 48.4627 | 4869.3758
2032-09-16 17:00 | 16055 | 5.3165 | 65.04 | 48.4627 | 4705.256
2032-09-17 18:00 | 14426.3 | 4.6235 | 65.5396 | 48.4627 | 4227.9312
2032-09-18 19:00 | 12488.4 | 3.955 | 65.6702 | 48.4627 | 3659.9888
2032-09-19 20:00 | 9901.02 | 3.0281 | 65.9406 | 48.4627 | 2901.7025
2032-09-20 21:00 | 8966.43 | 2.7562 | 65.6077 | 48.4627 | 2627.8012
2032-09-21 22:00 | 7155.58 | 2.149 | 65.6384 | 48.4627 | 2097.0935
2032-09-22 23:00 | 6434.55 | 1.9353 | 65.3286 | 48.4627 | 1885.7805
2032-09-24 | 5507.2 | 1.6283 | 65.282 | 48.4627 | 1614.001
2032-09-25 01:00 | 4722.75 | 1.46 | 64.5565 | 48.4627 | 1384.1014
2032-09-26 02:00 | 4249.46 | 1.3296 | 64.2137 | 48.4627 | 1245.3938
2032-09-27 03:00 | 4193.1 | 1.3281 | 63.879 | 48.4627 | 1228.8763
2032-09-28 04:00 | 4158.03 | 1.3496 | 63.4743 | 48.4627 | 1218.5983
2032-09-29 05:00 | 5907.4 | 1.8884 | 63.5027 | 48.4627 | 1731.288
2032-09-30 06:00 | 7073.65 | 2.31 | 63.3364 | 48.4627 | 2073.0822
2032-10-01 07:00 | 8223.79 | 2.7983 | 63.0422 | 48.4627 | 2410.1549
2032-10-02 08:00 | 7525.92 | 2.3629 | 64.0487 | 48.4627 | 2205.6294
2032-10-03 09:00 | 6482.39 | 1.9735 | 64.4092 | 48.4627 | 1899.801
2032-10-04 10:00 | 7013.69 | 2.3133 | 63.4794 | 48.4627 | 2055.5096
2032-10-05 11:00 | 8012.72 | 2.4432 | 64.3195 | 48.4627 | 2348.2964
2032-10-06 12:00 | 8648.73 | 2.721 | 64.0611 | 48.4627 | 2534.6926
2032-10-07 13:00 | 7814.36 | 2.3993 | 64.4134 | 48.4627 | 2290.1628
2032-10-08 14:00 | 7357.8 | 2.3019 | 64.1723 | 48.4627 | 2156.3583
2032-10-09 15:00 | 8288.98 | 2.7117 | 63.6434 | 48.4627 | 2429.2602
2032-10-10 16:00 | 9868.63 | 3.2304 | 63.6919 | 48.4627 | 2892.21
2032-10-11 17:00 | 9684.25 | 3.1917 | 63.78 | 48.4627 | 2838.1735
2032-10-12 18:00 | 8876.99 | 2.8407 | 64.1323 | 48.4627 | 2601.589
2032-10-13 19:00 | 7852.32 | 2.4467 | 64.3707 | 48.4627 | 2301.2878
2032-10-14 20:00 | 6024.97 | 1.7304 | 65.2131 | 48.4627 | 1765.7444
2032-10-15 21:00 | 5171.12 | 1.5877 | 64.2582 | 48.4627 | 1515.5057
2032-10-16 22:00 | 3263.73 | 1 | 66.002 | 48.4627 | 956.5048
2032-10-17 23:00 | 3094.92 | 1 | 51.6994 | 48.4627 | 907.0315
2032-10-19 | 3060.63 | 1 | 51.5129 | 48.4627 | 896.9821
2032-10-20 01:00 | 3191.1 | 1 | 51.3412 | 48.4627 | 935.2191
2032-10-21 02:00 | 3046.09 | 1 | 51.3181 | 48.4627 | 892.7209
2032-10-22 03:00 | 0 | 0 | 52.2753 | 48.4627 | 0
2032-10-23 04:00 | 0 | 1 | 51.9134 | 48.4627 | 0
2032-10-24 05:00 | 1625.74 | 1 | 51.1157 | 48.4627 | 476.4574
2032-10-25 06:00 | 3204.68 | 1.2611 | 60.2771 | 48.4627 | 939.199
2032-10-26 07:00 | 5457.14 | 2.0293 | 60.8288 | 48.4627 | 1599.3299
2032-10-27 08:00 | 6190.18 | 2.0647 | 62.0819 | 48.4627 | 1814.1627
2032-10-28 09:00 | 7874.21 | 2.5522 | 62.5791 | 48.4627 | 2307.7032
2032-10-29 10:00 | 9350.06 | 3.2109 | 62.2847 | 48.4627 | 2740.2321
2032-10-30 11:00 | 10474.1 | 3.4728 | 62.953 | 48.4627 | 3069.6557
2032-10-31 12:00 | 10836.3 | 3.6857 | 62.9886 | 48.4627 | 3175.806
2032-11-01 13:00 | 11804 | 3.6812 | 64.0988 | 48.4627 | 3459.4109
2032-11-02 14:00 | 11892 | 3.8439 | 63.9662 | 48.4627 | 3485.2012
2032-11-03 15:00 | 11878.8 | 3.9104 | 63.9766 | 48.4627 | 3481.3326
2032-11-04 16:00 | 14063.1 | 4.5969 | 64.1831 | 48.4627 | 4121.4878
2032-11-05 17:00 | 12517.7 | 4.0131 | 64.7072 | 48.4627 | 3668.5757
2032-11-06 18:00 | 11332.8 | 3.5715 | 64.9618 | 48.4627 | 3321.3158
2032-11-07 19:00 | 9665.16 | 2.9748 | 65.1619 | 48.4627 | 2832.5788
2032-11-08 20:00 | 8536.04 | 2.6316 | 65.0193 | 48.4627 | 2501.6664
2032-11-09 21:00 | 6982.77 | 2.2376 | 64.4621 | 48.4627 | 2046.4479
2032-11-10 22:00 | 6236.35 | 1.9621 | 64.4167 | 48.4627 | 1827.6938
2032-11-11 23:00 | 3203.74 | 1 | 65.6419 | 48.4627 | 938.9235
2032-11-13 | 3205.53 | 1 | 51.9652 | 48.4627 | 939.4481
2032-11-14 01:00 | 3091.11 | 1 | 51.7613 | 48.4627 | 905.9149
2032-11-15 02:00 | 2980.72 | 1 | 51.6332 | 48.4627 | 873.5628
2032-11-16 03:00 | 0 | 0 | 52.5192 | 48.4627 | 0
2032-11-17 04:00 | -148.608 | 1.1169 | 51.6442 | 48.4627 | -43.5527
2032-11-18 05:00 | 320.761 | 1 | 51.7222 | 48.4627 | 94.0058
2032-11-19 06:00 | 1845.14 | 1 | 58.3622 | 48.4627 | 540.7572
2032-11-20 07:00 | 3214.46 | 1.2685 | 60.2567 | 48.4627 | 942.0652
2032-11-21 08:00 | 2988.77 | 1.0373 | 61.4909 | 48.4627 | 875.922
2032-11-22 09:00 | 3673.23 | 1.202 | 62.0801 | 48.4627 | 1076.5174
2032-11-23 10:00 | 5290.42 | 1.7052 | 62.278 | 48.4627 | 1550.4691
2032-11-24 11:00 | 6307.66 | 2.0959 | 62.1503 | 48.4627 | 1848.5927
2032-11-25 12:00 | 6952.18 | 2.2568 | 62.5662 | 48.4627 | 2037.4828
2032-11-26 13:00 | 6988.59 | 2.25 | 62.7887 | 48.4627 | 2048.1535
2032-11-27 14:00 | 7122.49 | 2.3241 | 62.7414 | 48.4627 | 2087.3958
2032-11-28 15:00 | 6962.9 | 2.2601 | 62.8953 | 48.4627 | 2040.6246
2032-11-29 16:00 | 9147.07 | 3.0172 | 62.7607 | 48.4627 | 2680.7416
2032-11-30 17:00 | 8101.99 | 2.6757 | 62.9905 | 48.4627 | 2374.4589
2032-12-01 18:00 | 7094.05 | 2.2649 | 63.3839 | 48.4627 | 2079.0608
2032-12-02 19:00 | 5527.06 | 1.7272 | 63.5447 | 48.4627 | 1619.8214
2032-12-03 20:00 | 4282.65 | 1.3516 | 63.2938 | 48.4627 | 1255.1208
2032-12-04 21:00 | 3014.72 | 1 | 62.9006 | 48.4627 | 883.5272
2032-12-05 22:00 | 2978.97 | 1 | 51.1477 | 48.4627 | 873.0499
2032-12-06 23:00 | 0 | 0 | 52.0288 | 48.4627 | 0
2032-12-08 | -751.048 | 2.987 | 50.7874 | 48.4627 | -220.1104
2032-12-09 01:00 | -1143.68 | 4.0888 | 50.3768 | 48.4627 | -335.1795
2032-12-10 02:00 | -1434.86 | 4.9386 | 50.111 | 48.4627 | -420.516
2032-12-11 03:00 | -1513.62 | 5.1184 | 49.9103 | 48.4627 | -443.5982
2032-12-12 04:00 | -1515.34 | 5.1179 | 49.7233 | 48.4627 | -444.1023
2032-12-13 05:00 | -659.98 | 2.3073 | 49.6308 | 48.4627 | -193.421
2032-12-14 06:00 | 11.3222 | 1 | 50.5669 | 48.4627 | 3.3182
2032-12-15 07:00 | 2384.11 | 1 | 49.7618 | 48.4627 | 698.7137
2032-12-16 08:00 | 2966.15 | 1 | 49.766 | 48.4627 | 869.2928
2032-12-17 09:00 | 3051.62 | 1 | 62.1163 | 48.4627 | 894.3415
2032-12-18 10:00 | 4733.98 | 1.5387 | 61.3903 | 48.4627 | 1387.3926
2032-12-19 11:00 | 6099.87 | 1.9953 | 61.5368 | 48.4627 | 1787.6954
2032-12-20 12:00 | 7171.99 | 2.3428 | 61.8157 | 48.4627 | 2101.9028
2032-12-21 13:00 | 7810.33 | 2.5274 | 62.1486 | 48.4627 | 2288.9818
2032-12-22 14:00 | 8425.62 | 2.7225 | 62.3753 | 48.4627 | 2469.3055
2032-12-23 15:00 | 9805.05 | 3.2215 | 62.418 | 48.4627 | 2873.5765
2032-12-24 16:00 | 9555.48 | 3.1127 | 62.7764 | 48.4627 | 2800.4347
2032-12-25 17:00 | 8996.92 | 2.8474 | 63.2335 | 48.4627 | 2636.737
2032-12-26 18:00 | 7532.4 | 2.4044 | 63.2055 | 48.4627 | 2207.5285
2032-12-27 19:00 | 5896.58 | 1.8435 | 63.3613 | 48.4627 | 1728.117
2032-12-28 20:00 | 3304.84 | 1.0472 | 63.0611 | 48.4627 | 968.553
2032-12-29 21:00 | 3098.17 | 1 | 67.5516 | 48.4627 | 907.984
2032-12-30 22:00 | 2893.86 | 1 | 50.8747 | 48.4627 | 848.1066
2032-12-31 23:00 | -17.2159 | 0.75244 | 51.6605 | 48.4627 | -5.0455
2033-01-02 | -264.677 | 1.4692 | 50.7429 | 48.4627 | -77.5692
2033-01-03 01:00 | -482.627 | 2.1072 | 50.3162 | 48.4627 | -141.444
2033-01-04 02:00 | -549.119 | 2.2617 | 50.1085 | 48.4627 | -160.9309
2033-01-05 03:00 | -373.526 | 1.6781 | 50.0228 | 48.4627 | -109.4697
2033-01-06 04:00 | -249.58 | 1.3395 | 50.0227 | 48.4627 | -73.1447
2033-01-07 05:00 | 1191.27 | 1 | 50.1767 | 48.4627 | 349.1268
2033-01-08 06:00 | 2912.92 | 1 | 49.6554 | 48.4627 | 853.6926
2033-01-09 07:00 | 2993.8 | 1 | 49.8042 | 48.4627 | 877.3962
2033-01-10 08:00 | 1525.8 | 1 | 50.4062 | 48.4627 | 447.1678
2033-01-11 09:00 | 3166.82 | 1 | 49.7517 | 48.4627 | 928.1033
2033-01-12 10:00 | 3134.8 | 1 | 67.9968 | 48.4627 | 918.7192
2033-01-13 11:00 | 3387.66 | 1.0585 | 61.818 | 48.4627 | 992.8251
2033-01-14 12:00 | 3706.24 | 1.1778 | 61.673 | 48.4627 | 1086.1917
2033-01-15 13:00 | 3869.53 | 1.1976 | 62.0008 | 48.4627 | 1134.0473
2033-01-16 14:00 | 4680.01 | 1.4522 | 62.0311 | 48.4627 | 1371.5755
2033-01-17 15:00 | 6629.04 | 2.1935 | 61.4405 | 48.4627 | 1942.7798
2033-01-18 16:00 | 6823.66 | 2.2348 | 61.7848 | 48.4627 | 1999.8173
2033-01-19 17:00 | 6959.8 | 2.2599 | 62.0202 | 48.4627 | 2039.716
2033-01-20 18:00 | 6463.94 | 2.0036 | 62.6114 | 48.4627 | 1894.3938
2033-01-21 19:00 | 5014.51 | 1.5854 | 62.4448 | 48.4627 | 1469.6078
2033-01-22 20:00 | 3115.8 | 1 | 64.7335 | 48.4627 | 913.1508
2033-01-23 21:00 | 3121.51 | 1 | 50.405 | 48.4627 | 914.8243
2033-01-24 22:00 | 0 | 0 | 51.3749 | 48.4627 | 0
2033-01-25 23:00 | -206.352 | 1.0547 | 50.3629 | 48.4627 | -60.4758
2033-01-27 | -278.227 | 1.4937 | 50.1615 | 48.4627 | -81.5403
2033-01-28 01:00 | -349.411 | 1.6831 | 49.9577 | 48.4627 | -102.4023
2033-01-29 02:00 | -374.288 | 1.7466 | 49.8302 | 48.4627 | -109.693
2033-01-30 03:00 | -252.13 | 1.344 | 49.8045 | 48.4627 | -73.892
2033-01-31 04:00 | -123.34 | 0.96796 | 49.9561 | 48.4627 | -36.1474
2033-02-01 05:00 | 1794.36 | 1 | 49.724 | 48.4627 | 525.875
2033-02-02 06:00 | 2706.56 | 1 | 49.5347 | 48.4627 | 793.2144
2033-02-03 07:00 | 3058.45 | 1 | 61.0462 | 48.4627 | 896.3432
2033-02-04 08:00 | 3351.91 | 1.0409 | 61.5846 | 48.4627 | 982.3479
2033-02-05 09:00 | 4868.98 | 1.5962 | 61.0919 | 48.4627 | 1426.9572
2033-02-06 10:00 | 6585.72 | 2.238 | 60.957 | 48.4627 | 1930.084
2033-02-07 11:00 | 8135.07 | 2.6305 | 61.7553 | 48.4627 | 2384.1537
2033-02-08 12:00 | 7714.78 | 2.4868 | 62.1056 | 48.4627 | 2260.9788
2033-02-09 13:00 | 8597.37 | 2.7187 | 62.4707 | 48.4627 | 2519.6404
2033-02-10 14:00 | 9018.73 | 2.9055 | 62.4909 | 48.4627 | 2643.1289
2033-02-11 15:00 | 10723.9 | 3.5383 | 62.4378 | 48.4627 | 3142.8648
2033-02-12 16:00 | 11085.4 | 3.7525 | 62.4709 | 48.4627 | 3248.81
2033-02-13 17:00 | 11117.5 | 3.6824 | 62.8999 | 48.4627 | 3258.2176
2033-02-14 18:00 | 9902.09 | 3.1964 | 63.3308 | 48.4627 | 2902.0161
2033-02-15 19:00 | 8123.3 | 2.5799 | 63.5338 | 48.4627 | 2380.7042
2033-02-16 20:00 | 5676.45 | 1.6826 | 64.2081 | 48.4627 | 1663.6033
2033-02-17 21:00 | 4456.43 | 1.3756 | 63.4929 | 48.4627 | 1306.0507
2033-02-18 22:00 | 3126.1 | 1 | 68.0009 | 48.4627 | 916.1695
2033-02-19 23:00 | 3045.92 | 1 | 50.9929 | 48.4627 | 892.671
2033-02-21 | 1825.75 | 1 | 51.2518 | 48.4627 | 535.0745
2033-02-22 01:00 | 0 | 0 | 51.6504 | 48.4627 | 0
2033-02-23 02:00 | -190.496 | 1.261 | 50.822 | 48.4627 | -55.8289
2033-02-24 03:00 | -208.291 | 1.2427 | 50.5437 | 48.4627 | -61.0441
2033-02-25 04:00 | -295.231 | 1.5272 | 50.3035 | 48.4627 | -86.5237
2033-02-26 05:00 | 47.8977 | 1 | 50.7764 | 48.4627 | 14.0374
2033-02-27 06:00 | 2994.67 | 1 | 49.6589 | 48.4627 | 877.6511
2033-02-28 07:00 | 3134.85 | 1 | 49.8179 | 48.4627 | 918.7338
2033-03-01 08:00 | 3097.7 | 1 | 49.9479 | 48.4627 | 907.8463
2033-03-02 09:00 | 3092.29 | 1 | 61.5318 | 48.4627 | 906.2607
2033-03-03 10:00 | 4606.34 | 1.4645 | 61.7032 | 48.4627 | 1349.985
2033-03-04 11:00 | 6126.25 | 2.0065 | 61.5586 | 48.4627 | 1795.4266
2033-03-05 12:00 | 7117.5 | 2.285 | 61.984 | 48.4627 | 2085.9333
2033-03-06 13:00 | 7499.92 | 2.4992 | 61.8233 | 48.4627 | 2198.0096
2033-03-07 14:00 | 8289.92 | 2.6978 | 62.2498 | 48.4627 | 2429.5357
2033-03-08 15:00 | 9522.98 | 3.1798 | 62.1933 | 48.4627 | 2790.9099
2033-03-09 16:00 | 9993.74 | 3.2911 | 62.5932 | 48.4627 | 2928.8761
2033-03-10 17:00 | 10075.5 | 3.2247 | 63.0984 | 48.4627 | 2952.8376
2033-03-11 18:00 | 8608.43 | 2.741 | 63.2904 | 48.4627 | 2522.8818
2033-03-12 19:00 | 6884.03 | 2.1858 | 63.3063 | 48.4627 | 2017.51
2033-03-13 20:00 | 4456.7 | 1.3906 | 63.3742 | 48.4627 | 1306.1298
2033-03-14 21:00 | 3166.78 | 1 | 64.7819 | 48.4627 | 928.0916
2033-03-15 22:00 | 3016.26 | 1 | 50.9839 | 48.4627 | 883.9785
2033-03-16 23:00 | 0 | 0 | 51.8508 | 48.4627 | 0
2033-03-18 | -557.236 | 2.3763 | 50.6503 | 48.4627 | -163.3098
2033-03-19 01:00 | -842.899 | 3.1818 | 50.2467 | 48.4627 | -247.0293
2033-03-20 02:00 | -854.123 | 3.1412 | 50.0256 | 48.4627 | -250.3187
2033-03-21 03:00 | -932.095 | 3.408 | 49.8582 | 48.4627 | -273.1701
2033-03-22 04:00 | -915.315 | 3.3318 | 49.6903 | 48.4627 | -268.2523
2033-03-23 05:00 | 0 | 0 | 50.5046 | 48.4627 | 0
2033-03-24 06:00 | 2189.19 | 1 | 49.7352 | 48.4627 | 641.5883
2033-03-25 07:00 | 2900.5 | 1 | 61.2816 | 48.4627 | 850.0526
2033-03-26 08:00 | 3202.06 | 1.052 | 61.0855 | 48.4627 | 938.4312
2033-03-27 09:00 | 5374.63 | 1.7128 | 61.5001 | 48.4627 | 1575.1486
2033-03-28 10:00 | 6961.33 | 2.2945 | 61.4153 | 48.4627 | 2040.1644
2033-03-29 11:00 | 8416.68 | 2.7766 | 61.7313 | 48.4627 | 2466.6854
2033-03-30 12:00 | 9187.97 | 2.9399 | 62.3627 | 48.4627 | 2692.7282
2033-03-31 13:00 | 9966.44 | 3.1976 | 62.6111 | 48.4627 | 2920.8752
2033-04-01 14:00 | 11497.9 | 3.5431 | 63.3197 | 48.4627 | 3369.7019
2033-04-02 15:00 | 12892 | 4.1288 | 63.2327 | 48.4627 | 3778.2722
2033-04-03 16:00 | 13731.1 | 4.3444 | 63.7182 | 48.4627 | 4024.1882
2033-04-04 17:00 | 13876.8 | 4.417 | 63.9676 | 48.4627 | 4066.8886
2033-04-05 18:00 | 12344.3 | 3.8821 | 64.3403 | 48.4627 | 3617.7572
2033-04-06 19:00 | 10684.8 | 3.3379 | 64.4751 | 48.4627 | 3131.4058
2033-04-07 20:00 | 8563.84 | 2.574 | 64.8533 | 48.4627 | 2509.8138
2033-04-08 21:00 | 7535.68 | 2.2597 | 64.6961 | 48.4627 | 2208.4898
2033-04-09 22:00 | 5718.74 | 1.643 | 65.0122 | 48.4627 | 1675.9973
2033-04-10 23:00 | 4064.34 | 1.2264 | 64.1898 | 48.4627 | 1191.1405
2033-04-12 | 3285.75 | 1.0497 | 63.2732 | 48.4627 | 962.9583
2033-04-13 01:00 | 3424.85 | 1.114 | 62.8487 | 48.4627 | 1003.7245
2033-04-14 02:00 | 3095.27 | 1.0165 | 62.622 | 48.4627 | 907.1341
2033-04-15 03:00 | 3169.95 | 1 | 64.5408 | 48.4627 | 929.0206
2033-04-16 04:00 | 3042.14 | 1 | 66.1017 | 48.4627 | 891.5632
2033-04-17 05:00 | 3129.12 | 1 | 64.8602 | 48.4627 | 917.0545
2033-04-18 06:00 | 5358.43 | 1.6027 | 63.2144 | 48.4627 | 1570.4008
2033-04-19 07:00 | 7159.65 | 2.3255 | 62.4749 | 48.4627 | 2098.2863
2033-04-20 08:00 | 7024.64 | 2.2172 | 63.0391 | 48.4627 | 2058.7188
2033-04-21 09:00 | 8042.97 | 2.6695 | 62.6266 | 48.4627 | 2357.1618
2033-04-22 10:00 | 9608.59 | 3.2293 | 62.6808 | 48.4627 | 2815.9998
2033-04-23 11:00 | 10959.9 | 3.5979 | 63.2165 | 48.4627 | 3212.0296
2033-04-24 12:00 | 11567.1 | 3.6997 | 63.7922 | 48.4627 | 3389.9824
2033-04-25 13:00 | 9204.33 | 2.8286 | 64.4639 | 48.4627 | 2697.5228
2033-04-26 14:00 | 9144.06 | 2.8282 | 64.3382 | 48.4627 | 2679.8594
2033-04-27 15:00 | 8526.13 | 2.7212 | 63.9941 | 48.4627 | 2498.762
2033-04-28 16:00 | 10440.3 | 3.5763 | 63.2318 | 48.4627 | 3059.7499
2033-04-29 17:00 | 9484.46 | 3.0629 | 63.9864 | 48.4627 | 2779.6208
2033-04-30 18:00 | 8729.7 | 2.735 | 64.2878 | 48.4627 | 2558.4225
2033-05-01 19:00 | 7590.29 | 2.3425 | 64.3871 | 48.4627 | 2224.4944
2033-05-02 20:00 | 6104.78 | 1.916 | 64.1034 | 48.4627 | 1789.1344
2033-05-03 21:00 | 4925.65 | 1.5865 | 63.6571 | 48.4627 | 1443.5655
2033-05-04 22:00 | 3829.24 | 1.2706 | 63.1203 | 48.4627 | 1122.2395
2033-05-05 23:00 | 2813.41 | 1 | 51.7354 | 48.4627 | 824.5291
2033-05-07 | 0 | 0 | 52.4517 | 48.4627 | 0
2033-05-08 01:00 | -228.973 | 1.3498 | 51.4566 | 48.4627 | -67.1054
2033-05-09 02:00 | -523.672 | 2.2325 | 50.9598 | 48.4627 | -153.4731
2033-05-10 03:00 | -622.891 | 2.4682 | 50.698 | 48.4627 | -182.5513
2033-05-11 04:00 | -1083.56 | 3.9447 | 50.432 | 48.4627 | -317.5601
2033-05-12 05:00 | -852.997 | 3.0463 | 50.2074 | 48.4627 | -249.9887
2033-05-13 06:00 | 1816.75 | 1 | 50.41 | 48.4627 | 532.4369
2033-05-14 07:00 | 2853.45 | 1.0055 | 60.7928 | 48.4627 | 836.2636
2033-05-15 08:00 | 2947.31 | 1 | 61.7124 | 48.4627 | 863.7713
2033-05-16 09:00 | 4481.74 | 1.4586 | 61.7399 | 48.4627 | 1313.4683
2033-05-17 10:00 | 6168.11 | 2.1273 | 61.32 | 48.4627 | 1807.6946
2033-05-18 11:00 | 7667.72 | 2.562 | 61.8964 | 48.4627 | 2247.1869
2033-05-19 12:00 | 8462.08 | 2.8133 | 62.2225 | 48.4627 | 2479.9908
2033-05-20 13:00 | 9091.99 | 2.9042 | 62.8801 | 48.4627 | 2664.5992
2033-05-21 14:00 | 9590.24 | 3.0832 | 63.0444 | 48.4627 | 2810.6219
2033-05-22 15:00 | 10071.2 | 3.2515 | 63.2108 | 48.4627 | 2951.5774
2033-05-23 16:00 | 12376.1 | 4.161 | 62.9786 | 48.4627 | 3627.0769
2033-05-24 17:00 | 11313 | 3.6389 | 63.7949 | 48.4627 | 3315.513
2033-05-25 18:00 | 9867.52 | 3.158 | 63.9732 | 48.4627 | 2891.8846
2033-05-26 19:00 | 8478.6 | 2.6861 | 64.0448 | 48.4627 | 2484.8324
2033-05-27 20:00 | 7374.73 | 2.3123 | 64.0742 | 48.4627 | 2161.32
2033-05-28 21:00 | 6210.02 | 1.9147 | 64.1477 | 48.4627 | 1819.9772
2033-05-29 22:00 | 5412.42 | 1.6565 | 64.0443 | 48.4627 | 1586.2237
2033-05-30 23:00 | 3247.09 | 1 | 65.69 | 48.4627 | 951.6281
2033-06-01 | 3113.48 | 1 | 68.7908 | 48.4627 | 912.4709
2033-06-02 01:00 | 3211.93 | 1 | 51.2564 | 48.4627 | 941.3238
2033-06-03 02:00 | 3133.93 | 1 | 51.1954 | 48.4627 | 918.4642
2033-06-04 03:00 | 3292.05 | 1 | 51.055 | 48.4627 | 964.8046
2033-06-05 04:00 | 3255.14 | 1 | 50.9942 | 48.4627 | 953.9874
2033-06-06 05:00 | 3226.59 | 1 | 65.1717 | 48.4627 | 945.6202
2033-06-07 06:00 | 3502.24 | 1.0802 | 62.9663 | 48.4627 | 1026.4052
2033-06-08 07:00 | 4934.68 | 1.5288 | 62.8999 | 48.4627 | 1446.2119
2033-06-09 08:00 | 5809.51 | 1.6822 | 63.7798 | 48.4627 | 1702.5993
2033-06-10 09:00 | 7677.38 | 2.5078 | 62.5877 | 48.4627 | 2250.018
2033-06-11 10:00 | 9375.03 | 3.0418 | 62.9006 | 48.4627 | 2747.5501
2033-06-12 11:00 | 11393.9 | 3.6993 | 63.2085 | 48.4627 | 3339.2225
2033-06-13 12:00 | 11484.1 | 3.9028 | 63.1352 | 48.4627 | 3365.6575
2033-06-14 13:00 | 12737.2 | 4.1786 | 63.7451 | 48.4627 | 3732.9048
2033-06-15 14:00 | 13739.4 | 4.3261 | 64.4801 | 48.4627 | 4026.6207
2033-06-16 15:00 | 13785.7 | 4.4739 | 64.4771 | 48.4627 | 4040.1898
2033-06-17 16:00 | 13624.7 | 4.3364 | 64.8897 | 48.4627 | 3993.0054
2033-06-18 17:00 | 13047.6 | 4.1196 | 65.1154 | 48.4627 | 3823.8741
2033-06-19 18:00 | 10844.4 | 3.6235 | 64.6252 | 48.4627 | 3178.1799
2033-06-20 19:00 | 8939.52 | 2.9862 | 64.5193 | 48.4627 | 2619.9147
2033-06-21 20:00 | 6331.41 | 2.0031 | 64.8802 | 48.4627 | 1855.5531
2033-06-22 21:00 | 5629.2 | 1.654 | 65.3615 | 48.4627 | 1649.7557
2033-06-23 22:00 | 3268.1 | 1.0569 | 64.0539 | 48.4627 | 957.7856
2033-06-24 23:00 | 3008.53 | 1 | 66.3899 | 48.4627 | 881.7131
2033-06-26 | 3125.27 | 1 | 51.8905 | 48.4627 | 915.9262
2033-06-27 01:00 | 3155.4 | 1 | 51.7298 | 48.4627 | 924.7565
2033-06-28 02:00 | 3178.5 | 1 | 51.6058 | 48.4627 | 931.5264
2033-06-29 03:00 | 3182.62 | 1 | 51.4972 | 48.4627 | 932.7338
2033-06-30 04:00 | 3199.36 | 1 | 51.424 | 48.4627 | 937.6399
2033-07-01 05:00 | 3250.2 | 1 | 65.13 | 48.4627 | 952.5396
2033-07-02 06:00 | 3835.53 | 1.1422 | 63.7496 | 48.4627 | 1124.0829
2033-07-03 07:00 | 5573.05 | 1.6081 | 64.123 | 48.4627 | 1633.2997
2033-07-04 08:00 | 4405.83 | 1.4221 | 63.0539 | 48.4627 | 1291.2213
2033-07-05 09:00 | 5550.52 | 1.7762 | 63.1103 | 48.4627 | 1626.6968
2033-07-06 10:00 | 6677.29 | 2.2754 | 62.5515 | 48.4627 | 1956.9205
2033-07-07 11:00 | 7146.99 | 2.4125 | 62.8127 | 48.4627 | 2094.576
2033-07-08 12:00 | 8115 | 2.4581 | 64.0793 | 48.4627 | 2378.2717
2033-07-09 13:00 | 7992.78 | 2.4938 | 63.8874 | 48.4627 | 2342.4526
2033-07-10 14:00 | 8643.97 | 2.7704 | 63.6851 | 48.4627 | 2533.2975
2033-07-11 15:00 | 9856.28 | 3.2411 | 63.524 | 48.4627 | 2888.5905
2033-07-12 16:00 | 9702.47 | 3.2227 | 63.6006 | 48.4627 | 2843.5133
2033-07-13 17:00 | 9958.13 | 3.2329 | 63.9306 | 48.4627 | 2918.4398
2033-07-14 18:00 | 9151.16 | 2.8744 | 64.3713 | 48.4627 | 2681.9403
2033-07-15 19:00 | 7851.93 | 2.4257 | 64.5601 | 48.4627 | 2301.1735
2033-07-16 20:00 | 5562.68 | 1.6121 | 65.2072 | 48.4627 | 1630.2606
2033-07-17 21:00 | 4269.79 | 1.3141 | 64.2765 | 48.4627 | 1251.3519
2033-07-18 22:00 | 3126.33 | 1 | 51.9851 | 48.4627 | 916.2369
2033-07-19 23:00 | 3162.92 | 1 | 51.7304 | 48.4627 | 926.9603
2033-07-21 | 3063.15 | 1 | 51.6055 | 48.4627 | 897.7206
2033-07-22 01:00 | 1068.39 | 1 | 52.1681 | 48.4627 | 313.1142
2033-07-23 02:00 | 1235.22 | 1 | 51.8312 | 48.4627 | 362.0072
2033-07-24 03:00 | 3030.54 | 1 | 51.0472 | 48.4627 | 888.1636
2033-07-25 04:00 | 1906.44 | 1 | 51.501 | 48.4627 | 558.7224
2033-07-26 05:00 | 2687.17 | 1 | 65.1348 | 48.4627 | 787.5318
2033-07-27 06:00 | 3342.02 | 1.1095 | 62.1597 | 48.4627 | 979.4494
2033-07-28 07:00 | 5025.5 | 1.5545 | 62.956 | 48.4627 | 1472.8287
2033-07-29 08:00 | 5754.83 | 1.7723 | 63.1863 | 48.4627 | 1686.5742
2033-07-30 09:00 | 7750.96 | 2.5582 | 62.5916 | 48.4627 | 2271.5821
2033-07-31 10:00 | 9882.08 | 3.2191 | 63.0086 | 48.4627 | 2896.1518
2033-08-01 11:00 | 11723.4 | 3.7936 | 63.4461 | 48.4627 | 3435.7894
2033-08-02 12:00 | 12821.1 | 4.0955 | 63.9809 | 48.4627 | 3757.4935
2033-08-03 13:00 | 13296.9 | 4.2593 | 64.3205 | 48.4627 | 3896.9367
2033-08-04 14:00 | 13932.7 | 4.492 | 64.5596 | 48.4627 | 4083.2713
2033-08-05 15:00 | 15727.6 | 5.0376 | 64.8969 | 48.4627 | 4609.3046
2033-08-06 16:00 | 15852.1 | 5.157 | 65.1162 | 48.4627 | 4645.7919
2033-08-07 17:00 | 15964 | 5.0873 | 65.6041 | 48.4627 | 4678.5866
2033-08-08 18:00 | 14402.1 | 4.5248 | 65.9771 | 48.4627 | 4220.8389
2033-08-09 19:00 | 12470.9 | 3.8917 | 66.1023 | 48.4627 | 3654.86
2033-08-10 20:00 | 10087 | 3.0365 | 66.4257 | 48.4627 | 2956.2079
2033-08-11 21:00 | 8793.98 | 2.6872 | 66.0306 | 48.4627 | 2577.2611
2033-08-12 22:00 | 6880.78 | 2.0246 | 66.2412 | 48.4627 | 2016.5576
2033-08-13 23:00 | 6432.02 | 1.9763 | 65.4459 | 48.4627 | 1885.039
2033-08-15 | 5632.93 | 1.8171 | 64.7025 | 48.4627 | 1650.8488
2033-08-16 01:00 | 5105.1 | 1.6335 | 64.5888 | 48.4627 | 1496.1571
2033-08-17 02:00 | 4819.43 | 1.5471 | 64.3797 | 48.4627 | 1412.4355
2033-08-18 03:00 | 4684.82 | 1.5074 | 64.1918 | 48.4627 | 1372.9852
2033-08-19 04:00 | 4670.76 | 1.5144 | 63.9951 | 48.4627 | 1368.8646
2033-08-20 05:00 | 5763.35 | 1.9105 | 63.6612 | 48.4627 | 1689.0712
2033-08-21 06:00 | 6521.95 | 2.1342 | 63.8181 | 48.4627 | 1911.3949
2033-08-22 07:00 | 7592.29 | 2.461 | 63.9816 | 48.4627 | 2225.0806
2033-08-23 08:00 | 7799.23 | 2.4682 | 64.3708 | 48.4627 | 2285.7287
2033-08-24 09:00 | 9660.94 | 3.0818 | 64.3764 | 48.4627 | 2831.342
2033-08-25 10:00 | 11338 | 3.7145 | 64.3383 | 48.4627 | 3322.8398
2033-08-26 11:00 | 12680 | 4.1228 | 64.7153 | 48.4627 | 3716.1412
2033-08-27 12:00 | 13499 | 4.3149 | 65.1966 | 48.4627 | 3956.1664
2033-08-28 13:00 | 14173.9 | 4.4677 | 65.6162 | 48.4627 | 4153.96
2033-08-29 14:00 | 15113.9 | 4.8195 | 65.7573 | 48.4627 | 4429.4468
2033-08-30 15:00 | 16536 | 5.3462 | 65.8801 | 48.4627 | 4846.2232
2033-08-31 16:00 | 16912.9 | 5.4716 | 66.1967 | 48.4627 | 4956.6817
2033-09-01 17:00 | 16508.9 | 5.254 | 66.6193 | 48.4627 | 4838.281
2033-09-02 18:00 | 14465.2 | 4.6615 | 66.6415 | 48.4627 | 4239.3316
2033-09-03 19:00 | 12452.3 | 4.0521 | 66.4961 | 48.4627 | 3649.4089
2033-09-04 20:00 | 9713.49 | 3.0475 | 66.7362 | 48.4627 | 2846.7429
2033-09-05 21:00 | 8872.12 | 2.7396 | 66.5952 | 48.4627 | 2600.1617
2033-09-06 22:00 | 7134.04 | 2.1361 | 66.6959 | 48.4627 | 2090.7807
2033-09-07 23:00 | 6222.66 | 1.9268 | 66.0134 | 48.4627 | 1823.6816
2033-09-09 | 5491.59 | 1.7294 | 65.5551 | 48.4627 | 1609.4262
2033-09-10 01:00 | 5313.49 | 1.6486 | 65.4806 | 48.4627 | 1557.2302
2033-09-11 02:00 | 5370.8 | 1.6337 | 65.5355 | 48.4627 | 1574.0261
2033-09-12 03:00 | 5595.54 | 1.7655 | 65.0023 | 48.4627 | 1639.8909
2033-09-13 04:00 | 5686.42 | 1.8124 | 64.8141 | 48.4627 | 1666.5252
2033-09-14 05:00 | 6460.99 | 2.0619 | 64.728 | 48.4627 | 1893.5293
2033-09-15 06:00 | 6685.52 | 2.1106 | 64.8592 | 48.4627 | 1959.3325
2033-09-16 07:00 | 6971.78 | 2.2382 | 64.6946 | 48.4627 | 2043.227
2033-09-17 08:00 | 5564.12 | 1.6773 | 65.4126 | 48.4627 | 1630.6826
2033-09-18 09:00 | 5557.16 | 1.6717 | 65.3013 | 48.4627 | 1628.6428
2033-09-19 10:00 | 5729.67 | 1.8552 | 64.4197 | 48.4627 | 1679.2005
2033-09-20 11:00 | 6113.68 | 1.9575 | 64.4863 | 48.4627 | 1791.7427
2033-09-21 12:00 | 7059.64 | 2.316 | 64.206 | 48.4627 | 2068.9762
2033-09-22 13:00 | 7906.59 | 2.5635 | 64.3666 | 48.4627 | 2317.1928
2033-09-23 14:00 | 8628.92 | 2.7849 | 64.5029 | 48.4627 | 2528.8868
2033-09-24 15:00 | 9837.67 | 3.4076 | 63.8776 | 48.4627 | 2883.1365
2033-09-25 16:00 | 10534.2 | 3.5262 | 64.3695 | 48.4627 | 3087.2693
2033-09-26 17:00 | 9800.04 | 3.2939 | 64.4722 | 48.4627 | 2872.1082
2033-09-27 18:00 | 8583.88 | 2.7915 | 64.8229 | 48.4627 | 2515.6869
2033-09-28 19:00 | 7451.51 | 2.323 | 65.1771 | 48.4627 | 2183.822
2033-09-29 20:00 | 5193.79 | 1.5681 | 65.4151 | 48.4627 | 1522.1496
2033-09-30 21:00 | 4026.03 | 1.2573 | 64.7701 | 48.4627 | 1179.9129
2033-10-01 22:00 | 3099.76 | 1 | 52.6242 | 48.4627 | 908.45
2033-10-02 23:00 | 0 | 0 | 53.4508 | 48.4627 | 0
2033-10-04 | -208.209 | 1.1022 | 52.3509 | 48.4627 | -61.02
2033-10-05 01:00 | -454.522 | 2.0109 | 51.908 | 48.4627 | -133.2072
2033-10-06 02:00 | -550.243 | 2.2312 | 51.6128 | 48.4627 | -161.2603
2033-10-07 03:00 | -673.858 | 2.609 | 51.3622 | 48.4627 | -197.4883
2033-10-08 04:00 | -852.521 | 3.1502 | 51.1163 | 48.4627 | -249.8492
2033-10-09 05:00 | -604.85 | 2.3034 | 50.9787 | 48.4627 | -177.264
2033-10-10 06:00 | 1948.77 | 1 | 51.0817 | 48.4627 | 571.1281
2033-10-11 07:00 | 2868.68 | 1 | 62.7339 | 48.4627 | 840.7271
2033-10-12 08:00 | 3057.91 | 1 | 63.871 | 48.4627 | 896.185
2033-10-13 09:00 | 4542.61 | 1.4485 | 62.6652 | 48.4627 | 1331.3076
2033-10-14 10:00 | 6094.6 | 2.0664 | 62.2127 | 48.4627 | 1786.1509
2033-10-15 11:00 | 7697.57 | 2.5107 | 62.8845 | 48.4627 | 2255.9351
2033-10-16 12:00 | 8074.06 | 2.6994 | 62.9192 | 48.4627 | 2366.2734
2033-10-17 13:00 | 8176.35 | 2.7308 | 63.1352 | 48.4627 | 2396.2516
2033-10-18 14:00 | 8947.22 | 2.863 | 63.7273 | 48.4627 | 2622.1713
2033-10-19 15:00 | 9147.6 | 2.9719 | 63.7467 | 48.4627 | 2680.8969
2033-10-20 16:00 | 11566.1 | 3.792 | 63.7865 | 48.4627 | 3389.6893
2033-10-21 17:00 | 10590.4 | 3.4197 | 64.2684 | 48.4627 | 3103.7399
2033-10-22 18:00 | 9144.35 | 2.9739 | 64.3045 | 48.4627 | 2679.9444
2033-10-23 19:00 | 7556.79 | 2.4299 | 64.3759 | 48.4627 | 2214.6765
2033-10-24 20:00 | 6273.47 | 1.9293 | 64.7394 | 48.4627 | 1838.5726
2033-10-25 21:00 | 5061.15 | 1.617 | 64.1797 | 48.4627 | 1483.2766
2033-10-26 22:00 | 3994.46 | 1.3003 | 63.7684 | 48.4627 | 1170.6607
2033-10-27 23:00 | 2922.19 | 1 | 52.1648 | 48.4627 | 856.4094
2033-10-29 | 0 | 0 | 52.9376 | 48.4627 | 0
2033-10-30 01:00 | -157.04 | 1.0776 | 52.0239 | 48.4627 | -46.0239
2033-10-31 02:00 | -533.328 | 2.2741 | 51.4486 | 48.4627 | -156.303
2033-11-01 03:00 | -847.951 | 3.1706 | 51.1202 | 48.4627 | -248.5099
2033-11-02 04:00 | -1087.35 | 3.8599 | 50.8431 | 48.4627 | -318.6708
2033-11-03 05:00 | -844.147 | 3.009 | 50.6376 | 48.4627 | -247.3951
2033-11-04 06:00 | 1492.1 | 1 | 50.9573 | 48.4627 | 437.2913
2033-11-05 07:00 | 3059.75 | 1 | 65.3475 | 48.4627 | 896.7242
2033-11-06 08:00 | 3071.6 | 1 | 62.615 | 48.4627 | 900.1971
2033-11-07 09:00 | 4173.26 | 1.344 | 62.3187 | 48.4627 | 1223.0618
2033-11-08 10:00 | 6076.99 | 1.987 | 62.2978 | 48.4627 | 1780.99
2033-11-09 11:00 | 7847.45 | 2.549 | 62.638 | 48.4627 | 2299.8606
2033-11-10 12:00 | 8493.77 | 2.7766 | 62.8941 | 48.4627 | 2489.2783
2033-11-11 13:00 | 8785.33 | 2.836 | 63.2674 | 48.4627 | 2574.7261
2033-11-12 14:00 | 8540.59 | 2.7772 | 63.3905 | 48.4627 | 2502.9998
2033-11-13 15:00 | 8851.73 | 2.8518 | 63.6139 | 48.4627 | 2594.186
2033-11-14 16:00 | 11088.5 | 3.7441 | 63.2476 | 48.4627 | 3249.7186
2033-11-15 17:00 | 10328 | 3.3516 | 63.9602 | 48.4627 | 3026.838
2033-11-16 18:00 | 9242.94 | 2.9315 | 64.3163 | 48.4627 | 2708.8383
2033-11-17 19:00 | 7467.39 | 2.3276 | 64.4837 | 48.4627 | 2188.476
2033-11-18 20:00 | 5869.55 | 1.801 | 64.5434 | 48.4627 | 1720.1953
2033-11-19 21:00 | 4965.35 | 1.5642 | 64.0823 | 48.4627 | 1455.2004
2033-11-20 22:00 | 3562.44 | 1.1493 | 63.6342 | 48.4627 | 1044.0481
2033-11-21 23:00 | 2846.13 | 1 | 51.9355 | 48.4627 | 834.1184
2033-11-23 | 0 | 0 | 52.6999 | 48.4627 | 0
2033-11-24 01:00 | -99.6275 | 0.95895 | 51.947 | 48.4627 | -29.1979
2033-11-25 02:00 | -215.617 | 1.2826 | 51.4823 | 48.4627 | -63.1911
2033-11-26 03:00 | -109.954 | 0.91684 | 51.4763 | 48.4627 | -32.2243
2033-11-27 04:00 | -81.9948 | 0.86679 | 51.4166 | 48.4627 | -24.0303
2033-11-28 05:00 | 2238.81 | 1 | 50.8422 | 48.4627 | 656.1304
2033-11-29 06:00 | 3031.95 | 1 | 50.7019 | 48.4627 | 888.5768
2033-11-30 07:00 | 3124.85 | 1 | 64.2821 | 48.4627 | 915.8031
2033-12-01 08:00 | 3144.92 | 1 | 50.8307 | 48.4627 | 921.6851
2033-12-02 09:00 | 3322.52 | 1.0171 | 63.0123 | 48.4627 | 973.7345
2033-12-03 10:00 | 4324.31 | 1.3433 | 62.8523 | 48.4627 | 1267.3302
2033-12-04 11:00 | 4414.5 | 1.395 | 62.7505 | 48.4627 | 1293.7622
2033-12-05 12:00 | 4565.36 | 1.372 | 63.3536 | 48.4627 | 1337.9749
2033-12-06 13:00 | 4517.52 | 1.381 | 63.197 | 48.4627 | 1323.9544
2033-12-07 14:00 | 4784.59 | 1.4897 | 63.0179 | 48.4627 | 1402.2249
2033-12-08 15:00 | 6553.05 | 2.1209 | 62.6409 | 48.4627 | 1920.5094
2033-12-09 16:00 | 7501.08 | 2.439 | 62.7602 | 48.4627 | 2198.3495
2033-12-10 17:00 | 8065.45 | 2.6322 | 62.8892 | 48.4627 | 2363.7501
2033-12-11 18:00 | 7065.92 | 2.2024 | 63.5213 | 48.4627 | 2070.8167
2033-12-12 19:00 | 6584.23 | 1.9507 | 64.0987 | 48.4627 | 1929.6473
2033-12-13 20:00 | 4562.19 | 1.3316 | 64.2745 | 48.4627 | 1337.0459
2033-12-14 21:00 | 3905.14 | 1.1956 | 63.5624 | 48.4627 | 1144.4836
2033-12-15 22:00 | 3152.96 | 1 | 51.29 | 48.4627 | 924.0414
2033-12-16 23:00 | 3163.59 | 1 | 51.1357 | 48.4627 | 927.1567
2033-12-18 | 2989.18 | 1 | 51.1208 | 48.4627 | 876.0422
2033-12-19 01:00 | 3098.44 | 1 | 51.0188 | 48.4627 | 908.0631
2033-12-20 02:00 | 3071.47 | 1 | 51.0134 | 48.4627 | 900.159
2033-12-21 03:00 | 3153.51 | 1 | 50.9648 | 48.4627 | 924.2025
2033-12-22 04:00 | 3197.58 | 1 | 50.9405 | 48.4627 | 937.1182
2033-12-23 05:00 | 3222.72 | 1 | 67.1392 | 48.4627 | 944.486
2033-12-24 06:00 | 3726.2 | 1.1045 | 63.3756 | 48.4627 | 1092.0414
2033-12-25 07:00 | 4340.47 | 1.329 | 63.0411 | 48.4627 | 1272.0662
2033-12-26 08:00 | 3498.42 | 1.0823 | 63.008 | 48.4627 | 1025.2857
2033-12-27 09:00 | 5347.81 | 1.6317 | 63.1163 | 48.4627 | 1567.2884
2033-12-28 10:00 | 6339.05 | 2.0836 | 62.4739 | 48.4627 | 1857.7922
2033-12-29 11:00 | 8549.75 | 3 | 62.012 | 48.4627 | 2505.6844
2033-12-30 12:00 | 10310.9 | 3.506 | 62.6284 | 48.4627 | 3021.8265
2033-12-31 13:00 | 11576.2 | 3.7262 | 63.5411 | 48.4627 | 3392.6493
2034-01-01 14:00 | 11973.2 | 4.0253 | 63.4578 | 48.4627 | 3508.9985
2034-01-02 15:00 | 12626.8 | 4.0851 | 64.1206 | 48.4627 | 3700.5498
2034-01-03 16:00 | 11792.1 | 3.9065 | 64.1369 | 48.4627 | 3455.9234
2034-01-04 17:00 | 11231.2 | 3.6053 | 64.5714 | 48.4627 | 3291.5398
2034-01-05 18:00 | 10369.2 | 3.2111 | 65.0034 | 48.4627 | 3038.9125
2034-01-06 19:00 | 8629.77 | 2.8302 | 64.3857 | 48.4627 | 2529.1359
2034-01-07 20:00 | 6077.38 | 1.9615 | 64.4407 | 48.4627 | 1781.1043
2034-01-08 21:00 | 5146.91 | 1.6026 | 64.5311 | 48.4627 | 1508.4104
2034-01-09 22:00 | 3098.21 | 1 | 65.2443 | 48.4627 | 907.9957
2034-01-10 23:00 | 3019.08 | 1 | 52.0957 | 48.4627 | 884.805
2034-01-12 | 3018.53 | 1 | 51.8785 | 48.4627 | 884.6438
2034-01-13 01:00 | 2964.36 | 1 | 51.7461 | 48.4627 | 868.7682
2034-01-14 02:00 | 185.078 | 1 | 52.582 | 48.4627 | 54.241
2034-01-15 03:00 | -33.7599 | 0.75872 | 52.1185 | 48.4627 | -9.8941
2034-01-16 04:00 | -180.31 | 1.1906 | 51.513 | 48.4627 | -52.8436
2034-01-17 05:00 | 2138.9 | 1 | 51.1159 | 48.4627 | 626.8497
2034-01-18 06:00 | 2982.55 | 1 | 50.8862 | 48.4627 | 874.0991
2034-01-19 07:00 | 3010.37 | 1 | 65.8755 | 48.4627 | 882.2524
2034-01-20 08:00 | 2952.09 | 1 | 65.5678 | 48.4627 | 865.1722
2034-01-21 09:00 | 3949.14 | 1.306 | 62.2324 | 48.4627 | 1157.3787
2034-01-22 10:00 | 5400.3 | 1.7982 | 62.292 | 48.4627 | 1582.6717
2034-01-23 11:00 | 6455.89 | 2.1572 | 62.4331 | 48.4627 | 1892.0346
2034-01-24 12:00 | 7036.01 | 2.3356 | 62.6746 | 48.4627 | 2062.051
2034-01-25 13:00 | 7366.37 | 2.4315 | 62.8794 | 48.4627 | 2158.8699
2034-01-26 14:00 | 7854.85 | 2.5901 | 63.0401 | 48.4627 | 2302.0293
2034-01-27 15:00 | 9209.39 | 3.0355 | 63.1908 | 48.4627 | 2699.0058
2034-01-28 16:00 | 9791.12 | 3.1679 | 63.6118 | 48.4627 | 2869.494
2034-01-29 17:00 | 9664.93 | 3.1769 | 63.6336 | 48.4627 | 2832.5114
2034-01-30 18:00 | 8211.58 | 2.6289 | 64.0197 | 48.4627 | 2406.5765
2034-01-31 19:00 | 6383.71 | 2.058 | 63.9121 | 48.4627 | 1870.8807
2034-02-01 20:00 | 3679.81 | 1.1778 | 63.8495 | 48.4627 | 1078.4459
2034-02-02 21:00 | 3103.75 | 1 | 68.0557 | 48.4627 | 909.6193
2034-02-03 22:00 | 2769.13 | 1 | 51.7909 | 48.4627 | 811.5519
2034-02-04 23:00 | -127.855 | 1.1002 | 52.1715 | 48.4627 | -37.4706
2034-02-06 | -614.908 | 2.534 | 51.3316 | 48.4627 | -180.2117
2034-02-07 01:00 | -840.01 | 3.1258 | 50.9383 | 48.4627 | -246.1826
2034-02-08 02:00 | -855.183 | 3.12 | 50.736 | 48.4627 | -250.6294
2034-02-09 03:00 | -847.602 | 3.103 | 50.5732 | 48.4627 | -248.4076
2034-02-10 04:00 | -810.123 | 2.9897 | 50.4235 | 48.4627 | -237.4236
2034-02-11 05:00 | 0 | 0 | 51.2266 | 48.4627 | 0
2034-02-12 06:00 | 2016.71 | 1 | 50.5108 | 48.4627 | 591.0394
2034-02-13 07:00 | 2730.84 | 1 | 50.4179 | 48.4627 | 800.3302
2034-02-14 08:00 | 3026.06 | 1 | 50.4605 | 48.4627 | 886.8506
2034-02-15 09:00 | 2978.16 | 1 | 62.5504 | 48.4627 | 872.8125
2034-02-16 10:00 | 4490.02 | 1.4855 | 61.8385 | 48.4627 | 1315.895
2034-02-17 11:00 | 6328.7 | 2.1193 | 61.8999 | 48.4627 | 1854.7589
2034-02-18 12:00 | 7159.34 | 2.3534 | 62.3555 | 48.4627 | 2098.1954
2034-02-19 13:00 | 7426.65 | 2.433 | 62.6129 | 48.4627 | 2176.5363
2034-02-20 14:00 | 8353.9 | 2.747 | 62.7361 | 48.4627 | 2448.2864
2034-02-21 15:00 | 9473.16 | 3.1207 | 62.93 | 48.4627 | 2776.3091
2034-02-22 16:00 | 8937.02 | 2.9077 | 63.3105 | 48.4627 | 2619.182
2034-02-23 17:00 | 8703.66 | 2.8228 | 63.4405 | 48.4627 | 2550.7909
2034-02-24 18:00 | 7202.85 | 2.2739 | 63.7761 | 48.4627 | 2110.947
2034-02-25 19:00 | 6025.25 | 1.8683 | 63.9 | 48.4627 | 1765.8265
2034-02-26 20:00 | 3762.19 | 1.1755 | 63.7033 | 48.4627 | 1102.589
2034-02-27 21:00 | 3111.98 | 1 | 67.3243 | 48.4627 | 912.0313
2034-02-28 22:00 | 2810.24 | 1 | 51.4562 | 48.4627 | 823.6
2034-03-01 23:00 | 0 | 0 | 52.275 | 48.4627 | 0
2034-03-03 | -262.139 | 1.4566 | 51.2925 | 48.4627 | -76.8254
2034-03-04 01:00 | -416.943 | 1.883 | 50.8939 | 48.4627 | -122.1939
2034-03-05 02:00 | -578.029 | 2.3617 | 50.6571 | 48.4627 | -169.4036
2034-03-06 03:00 | -529.303 | 2.1592 | 50.4965 | 48.4627 | -155.1234
2034-03-07 04:00 | -478.284 | 2.0191 | 50.3899 | 48.4627 | -140.1712
2034-03-08 05:00 | 0 | 0 | 51.1021 | 48.4627 | 0
2034-03-09 06:00 | 2151.86 | 1 | 50.3234 | 48.4627 | 630.6479
2034-03-10 07:00 | 3006.3 | 1 | 50.1861 | 48.4627 | 881.0596
2034-03-11 08:00 | 3123.25 | 1 | 50.3056 | 48.4627 | 915.3342
2034-03-12 09:00 | 3146.95 | 1 | 64.0007 | 48.4627 | 922.28
2034-03-13 10:00 | 4752.34 | 1.5006 | 62.2037 | 48.4627 | 1392.7734
2034-03-14 11:00 | 6422.75 | 2.0505 | 62.2958 | 48.4627 | 1882.3222
2034-03-15 12:00 | 6680.77 | 2.1446 | 62.5043 | 48.4627 | 1957.9404
2034-03-16 13:00 | 6085.86 | 1.9204 | 62.8576 | 48.4627 | 1783.5895
2034-03-17 14:00 | 6009.25 | 1.8145 | 63.3935 | 48.4627 | 1761.1373
2034-03-18 15:00 | 7728.31 | 2.5451 | 62.5125 | 48.4627 | 2264.9441
2034-03-19 16:00 | 7853.75 | 2.5929 | 62.7002 | 48.4627 | 2301.7069
2034-03-20 17:00 | 8063.28 | 2.5968 | 63.0831 | 48.4627 | 2363.1141
2034-03-21 18:00 | 6964.3 | 2.2423 | 63.1757 | 48.4627 | 2041.0349
2034-03-22 19:00 | 6030.92 | 1.782 | 64.1016 | 48.4627 | 1767.4882
2034-03-23 20:00 | 3249.27 | 1 | 65.6079 | 48.4627 | 952.267
2034-03-24 21:00 | 3126.6 | 1 | 51.2695 | 48.4627 | 916.316
2034-03-25 22:00 | 0 | 0 | 52.1794 | 48.4627 | 0
2034-03-26 23:00 | -547.771 | 2.3344 | 50.9867 | 48.4627 | -160.5358
2034-03-28 | -814.01 | 3.0781 | 50.584 | 48.4627 | -238.5628
2034-03-29 01:00 | -980.011 | 3.5481 | 50.3372 | 48.4627 | -287.2129
2034-03-30 02:00 | -1114.86 | 3.9459 | 50.1635 | 48.4627 | -326.7332
2034-03-31 03:00 | -1242.6 | 4.3313 | 49.9843 | 48.4627 | -364.1701
2034-04-01 04:00 | -1391.1 | 4.7858 | 49.8538 | 48.4627 | -407.6912
2034-04-02 05:00 | -1299.56 | 4.442 | 49.7262 | 48.4627 | -380.8634
2034-04-03 06:00 | -380.085 | 1.4658 | 49.7338 | 48.4627 | -111.3919
2034-04-04 07:00 | 2063.43 | 1 | 49.899 | 48.4627 | 604.7316
2034-04-05 08:00 | 2790.87 | 1 | 49.8645 | 48.4627 | 817.9233
2034-04-06 09:00 | 3069.16 | 1 | 49.9346 | 48.4627 | 899.482
2034-04-07 10:00 | 3164.41 | 1 | 64.452 | 48.4627 | 927.397
2034-04-08 11:00 | 4829.13 | 1.5724 | 61.5626 | 48.4627 | 1415.2783
2034-04-09 12:00 | 5631.33 | 1.8595 | 61.6459 | 48.4627 | 1650.3799
2034-04-10 13:00 | 6537.45 | 2.1535 | 61.8618 | 48.4627 | 1915.9375
2034-04-11 14:00 | 7128.84 | 2.3225 | 62.1685 | 48.4627 | 2089.2568
2034-04-12 15:00 | 7312.15 | 2.3801 | 62.3577 | 48.4627 | 2142.9796
2034-04-13 16:00 | 9761.43 | 3.263 | 62.2341 | 48.4627 | 2860.7927
2034-04-14 17:00 | 8769.92 | 2.8465 | 62.8813 | 48.4627 | 2570.2098
2034-04-15 18:00 | 7680.01 | 2.4046 | 63.395 | 48.4627 | 2250.7887
2034-04-16 19:00 | 6082.4 | 1.8634 | 63.6138 | 48.4627 | 1782.5755
2034-04-17 20:00 | 4725.71 | 1.4641 | 63.3902 | 48.4627 | 1384.9689
2034-04-18 21:00 | 3426.5 | 1.0904 | 62.9599 | 48.4627 | 1004.208
2034-04-19 22:00 | 3111.56 | 1 | 65.123 | 48.4627 | 911.9082
2034-04-20 23:00 | 0 | 0 | 52.0082 | 48.4627 | 0
2034-04-22 | -573.301 | 2.296 | 50.7814 | 48.4627 | -168.0179
2034-04-23 01:00 | -729.245 | 2.8127 | 50.4667 | 48.4627 | -213.7206
2034-04-24 02:00 | -992.952 | 3.6236 | 50.2406 | 48.4627 | -291.0055
2034-04-25 03:00 | -1184.4 | 4.172 | 50.0461 | 48.4627 | -347.1134
2034-04-26 04:00 | -1338.76 | 4.6313 | 49.8491 | 48.4627 | -392.3518
2034-04-27 05:00 | -1152.14 | 3.9736 | 49.72 | 48.4627 | -337.6589
2034-04-28 06:00 | 780.276 | 1 | 50.3466 | 48.4627 | 228.6763
2034-04-29 07:00 | 2555.37 | 1.2918 | 57.4215 | 48.4627 | 748.905
2034-04-30 08:00 | 2826.48 | 1.054 | 59.986 | 48.4627 | 828.3595
2034-05-01 09:00 | 4578.7 | 1.5711 | 60.882 | 48.4627 | 1341.8845
2034-05-02 10:00 | 6359.66 | 2.2362 | 60.8715 | 48.4627 | 1863.8324
2034-05-03 11:00 | 8168.17 | 2.7062 | 61.7961 | 48.4627 | 2393.8543
2034-05-04 12:00 | 8986.72 | 2.9711 | 62.183 | 48.4627 | 2633.7476
2034-05-05 13:00 | 9389.72 | 3.0517 | 62.6585 | 48.4627 | 2751.8553
2034-05-06 14:00 | 9690.51 | 3.1189 | 63.0154 | 48.4627 | 2840.0081
2034-05-07 15:00 | 9323.34 | 3.0589 | 63.0323 | 48.4627 | 2732.4012
2034-05-08 16:00 | 11780.3 | 3.9134 | 63.0187 | 48.4627 | 3452.4651
2034-05-09 17:00 | 10524.5 | 3.4366 | 63.536 | 48.4627 | 3084.4265
2034-05-10 18:00 | 9267.19 | 2.8883 | 64.1366 | 48.4627 | 2715.9453
2034-05-11 19:00 | 7826.95 | 2.4661 | 63.9853 | 48.4627 | 2293.8526
2034-05-12 20:00 | 6778.91 | 2.0543 | 64.327 | 48.4627 | 1986.7024
2034-05-13 21:00 | 5799.55 | 1.7686 | 64.1576 | 48.4627 | 1699.6803
2034-05-14 22:00 | 4774.96 | 1.4974 | 63.6916 | 48.4627 | 1399.4026
2034-05-15 23:00 | 3177.58 | 1 | 51.6558 | 48.4627 | 931.2568
2034-05-17 | 3158.77 | 1 | 51.4218 | 48.4627 | 925.7441
2034-05-18 01:00 | 3106.26 | 1 | 51.3036 | 48.4627 | 910.3549
2034-05-19 02:00 | 0 | 0 | 52.2817 | 48.4627 | 0
2034-05-20 03:00 | 305.063 | 1 | 51.8116 | 48.4627 | 89.4051
2034-05-21 04:00 | 1679.27 | 1 | 51.1308 | 48.4627 | 492.1455
2034-05-22 05:00 | 2118.95 | 1 | 51.0017 | 48.4627 | 621.0029
2034-05-23 06:00 | 2791.67 | 1 | 50.7694 | 48.4627 | 818.1577
2034-05-24 07:00 | 3034.78 | 1 | 65.674 | 48.4627 | 889.4062
2034-05-25 08:00 | 3103.62 | 1 | 50.7193 | 48.4627 | 909.5812
2034-05-26 09:00 | 3187.11 | 1 | 64.6174 | 48.4627 | 934.0497
2034-05-27 10:00 | 3472.68 | 1.1151 | 62.333 | 48.4627 | 1017.742
2034-05-28 11:00 | 4510.09 | 1.3384 | 63.2155 | 48.4627 | 1321.7769
2034-05-29 12:00 | 4785.88 | 1.4468 | 63.0907 | 48.4627 | 1402.603
2034-05-30 13:00 | 5103.08 | 1.5688 | 62.9627 | 48.4627 | 1495.5651
2034-05-31 14:00 | 5698.31 | 1.8148 | 62.6537 | 48.4627 | 1670.0098
2034-06-01 15:00 | 7429.72 | 2.477 | 62.2843 | 48.4627 | 2177.436
2034-06-02 16:00 | 8064.51 | 2.6851 | 62.5099 | 48.4627 | 2363.4746
2034-06-03 17:00 | 8647.05 | 2.8192 | 62.9012 | 48.4627 | 2534.2002
2034-06-04 18:00 | 7361.64 | 2.4328 | 62.9294 | 48.4627 | 2157.4837
2034-06-05 19:00 | 5994.87 | 1.8662 | 63.5672 | 48.4627 | 1756.923
2034-06-06 20:00 | 3463.51 | 1.1004 | 63.2608 | 48.4627 | 1015.0546
2034-06-07 21:00 | 3117.73 | 1 | 51.2864 | 48.4627 | 913.7165
2034-06-08 22:00 | 0 | 0 | 52.1839 | 48.4627 | 0
2034-06-09 23:00 | -33.7333 | 0.78514 | 51.6337 | 48.4627 | -9.8863
2034-06-11 | -259.872 | 1.4484 | 50.9207 | 48.4627 | -76.161
2034-06-12 01:00 | -700.699 | 2.8058 | 50.5092 | 48.4627 | -205.3546
2034-06-13 02:00 | -902.469 | 3.3281 | 50.2801 | 48.4627 | -264.4876
2034-06-14 03:00 | -886.293 | 3.2267 | 50.1059 | 48.4627 | -259.7468
2034-06-15 04:00 | -780.297 | 2.8957 | 50.0219 | 48.4627 | -228.6825
2034-06-16 05:00 | -221.397 | 1.1146 | 50.1667 | 48.4627 | -64.8851
2034-06-17 06:00 | 0 | 1 | 50.8002 | 48.4627 | 0
2034-06-18 07:00 | 3079.73 | 1 | 49.7147 | 48.4627 | 902.5798
2034-06-19 08:00 | 3061.28 | 1 | 49.9903 | 48.4627 | 897.1726
2034-06-20 09:00 | 3064.29 | 1 | 50.1243 | 48.4627 | 898.0547
2034-06-21 10:00 | 2988.68 | 1 | 50.2264 | 48.4627 | 875.8956
2034-06-22 11:00 | 3549.24 | 1.1414 | 61.8408 | 48.4627 | 1040.1796
2034-06-23 12:00 | 4574.59 | 1.4651 | 61.9509 | 48.4627 | 1340.68
2034-06-24 13:00 | 5326.25 | 1.7232 | 61.9764 | 48.4627 | 1560.9698
2034-06-25 14:00 | 5734.27 | 1.8758 | 62.0106 | 48.4627 | 1680.5486
2034-06-26 15:00 | 7022.8 | 2.3745 | 61.7977 | 48.4627 | 2058.1795
2034-06-27 16:00 | 7565.07 | 2.4762 | 62.3341 | 48.4627 | 2217.1032
2034-06-28 17:00 | 7714.62 | 2.4856 | 62.681 | 48.4627 | 2260.9319
2034-06-29 18:00 | 6428.49 | 2.0402 | 62.9787 | 48.4627 | 1884.0044
2034-06-30 19:00 | 4794.12 | 1.5254 | 62.9184 | 48.4627 | 1405.0179
2034-07-01 20:00 | 3137.58 | 1 | 67.5437 | 48.4627 | 919.5339
2034-07-02 21:00 | 3182.64 | 1 | 50.854 | 48.4627 | 932.7397
2034-07-03 22:00 | 738.362 | 1 | 51.6029 | 48.4627 | 216.3925
2034-07-04 23:00 | 522.749 | 1 | 51.3797 | 48.4627 | 153.2026
2034-07-06 | 2023.13 | 1 | 50.6606 | 48.4627 | 592.9209
2034-07-07 01:00 | 2913.71 | 1 | 50.3885 | 48.4627 | 853.9241
2034-07-08 02:00 | 3205.9 | 1 | 50.3837 | 48.4627 | 939.5565
2034-07-09 03:00 | 3335.87 | 1 | 50.378 | 48.4627 | 977.647
2034-07-10 04:00 | 3261.26 | 1 | 64.8674 | 48.4627 | 955.781
2034-07-11 05:00 | 4325.13 | 1.3693 | 62.2635 | 48.4627 | 1267.5705
2034-07-12 06:00 | 5645.17 | 1.7224 | 62.7846 | 48.4627 | 1654.436
2034-07-13 07:00 | 6968.98 | 2.2987 | 62.1362 | 48.4627 | 2042.4064
2034-07-14 08:00 | 7621.31 | 2.5053 | 62.4141 | 48.4627 | 2233.5855
2034-07-15 09:00 | 9551.61 | 3.0962 | 62.7714 | 48.4627 | 2799.3006
2034-07-16 10:00 | 11267.4 | 3.6859 | 63.0381 | 48.4627 | 3302.149
2034-07-17 11:00 | 11536.2 | 3.7835 | 63.4259 | 48.4627 | 3380.9265
2034-07-18 12:00 | 12324.6 | 3.8501 | 64.2214 | 48.4627 | 3611.9837
2034-07-19 13:00 | 12616.9 | 3.9336 | 64.5142 | 48.4627 | 3697.6484
2034-07-20 14:00 | 11591.3 | 3.7574 | 64.3476 | 48.4627 | 3397.0747
2034-07-21 15:00 | 12469.5 | 3.9375 | 64.6965 | 48.4627 | 3654.4497
2034-07-22 16:00 | 13262.3 | 4.296 | 64.5848 | 48.4627 | 3886.7965
2034-07-23 17:00 | 12657.8 | 4.1378 | 64.7054 | 48.4627 | 3709.635
2034-07-24 18:00 | 11226.2 | 3.5781 | 65.0606 | 48.4627 | 3290.0744
2034-07-25 19:00 | 9803.59 | 3.1547 | 64.9115 | 48.4627 | 2873.1486
2034-07-26 20:00 | 8134.28 | 2.4439 | 65.5712 | 48.4627 | 2383.9221
2034-07-27 21:00 | 7161.42 | 2.1899 | 65.1883 | 48.4627 | 2098.805
2034-07-28 22:00 | 5337.55 | 1.5637 | 65.4883 | 48.4627 | 1564.2815
2034-07-29 23:00 | 4513.02 | 1.3752 | 64.7715 | 48.4627 | 1322.6356
2034-07-31 | 3832.37 | 1.207 | 64.1699 | 48.4627 | 1123.1568
2034-08-01 01:00 | 3463.84 | 1.0796 | 64.0711 | 48.4627 | 1015.1513
2034-08-02 02:00 | 3330.78 | 1.0342 | 63.9475 | 48.4627 | 976.1553
2034-08-03 03:00 | 3398.76 | 1.0949 | 63.4156 | 48.4627 | 996.0782
2034-08-04 04:00 | 3748.55 | 1.1639 | 63.7171 | 48.4627 | 1098.5916
2034-08-05 05:00 | 5203.09 | 1.6112 | 63.6951 | 48.4627 | 1524.8752
2034-08-06 06:00 | 5984.38 | 1.922 | 63.3962 | 48.4627 | 1753.8486
2034-08-07 07:00 | 7277.62 | 2.4324 | 63.089 | 48.4627 | 2132.8599
2034-08-08 08:00 | 8063.52 | 2.5054 | 64.0308 | 48.4627 | 2363.1844
2034-08-09 09:00 | 9457.65 | 3.2358 | 63.2064 | 48.4627 | 2771.7636
2034-08-10 10:00 | 11078.5 | 3.7773 | 63.4903 | 48.4627 | 3246.7878
2034-08-11 11:00 | 12008.2 | 4.1742 | 63.6099 | 48.4627 | 3519.256
2034-08-12 12:00 | 13126.9 | 4.3422 | 64.3902 | 48.4627 | 3847.1146
2034-08-13 13:00 | 13652.6 | 4.3888 | 64.982 | 48.4627 | 4001.1821
2034-08-14 14:00 | 13910.4 | 4.4914 | 65.2069 | 48.4627 | 4076.7358
2034-08-15 15:00 | 15049.3 | 4.9413 | 65.2495 | 48.4627 | 4410.5145
2034-08-16 16:00 | 16029.5 | 5.204 | 65.6346 | 48.4627 | 4697.7827
2034-08-17 17:00 | 16219.5 | 5.1655 | 66.1248 | 48.4627 | 4753.4662
2034-08-18 18:00 | 14439.9 | 4.5312 | 66.5118 | 48.4627 | 4231.9169
2034-08-19 19:00 | 12831 | 3.9644 | 66.6962 | 48.4627 | 3760.3949
2034-08-20 20:00 | 10252.6 | 3.1662 | 66.633 | 48.4627 | 3004.7405
2034-08-21 21:00 | 9032.35 | 2.7866 | 66.4057 | 48.4627 | 2647.1205
2034-08-22 22:00 | 7237.01 | 2.1107 | 66.8112 | 48.4627 | 2120.9583
2034-08-23 23:00 | 6263.05 | 1.9103 | 66.0089 | 48.4627 | 1835.5188
2034-08-25 | 5704.54 | 1.7438 | 65.7189 | 48.4627 | 1671.8356
2034-08-26 01:00 | 5100.67 | 1.6186 | 65.098 | 48.4627 | 1494.8588
2034-08-27 02:00 | 4856.11 | 1.5474 | 64.8688 | 48.4627 | 1423.1854
2034-08-28 03:00 | 4774.59 | 1.5605 | 64.4413 | 48.4627 | 1399.2942
2034-08-29 04:00 | 4906.86 | 1.5851 | 64.4366 | 48.4627 | 1438.0587
2034-08-30 05:00 | 6014.71 | 1.9488 | 64.3031 | 48.4627 | 1762.7375
2034-08-31 06:00 | 6485.96 | 1.9372 | 65.2064 | 48.4627 | 1900.8472
2034-09-01 07:00 | 5603.46 | 1.6861 | 65.1543 | 48.4627 | 1642.212
2034-09-02 08:00 | 5290.07 | 1.7045 | 64.333 | 48.4627 | 1550.3665
2034-09-03 09:00 | 5067.79 | 1.6336 | 64.2443 | 48.4627 | 1485.2226
2034-09-04 10:00 | 5512.71 | 1.8361 | 63.8338 | 48.4627 | 1615.6158
2034-09-05 11:00 | 7361.19 | 2.5311 | 63.4832 | 48.4627 | 2157.3518
2034-09-06 12:00 | 7560.53 | 2.5379 | 63.8501 | 48.4627 | 2215.7726
2034-09-07 13:00 | 9748.18 | 3.2094 | 64.1201 | 48.4627 | 2856.9095
2034-09-08 14:00 | 10957.4 | 3.4938 | 64.6953 | 48.4627 | 3211.2969
2034-09-09 15:00 | 11991.5 | 3.9811 | 64.537 | 48.4627 | 3514.3617
2034-09-10 16:00 | 12317.5 | 3.948 | 65.1485 | 48.4627 | 3609.9029
2034-09-11 17:00 | 11760.6 | 3.8329 | 65.1427 | 48.4627 | 3446.6916
2034-09-12 18:00 | 9634.53 | 3.235 | 64.9233 | 48.4627 | 2823.602
2034-09-13 19:00 | 8001.95 | 2.6328 | 65.0053 | 48.4627 | 2345.14
2034-09-14 20:00 | 5782.76 | 1.7777 | 65.5436 | 48.4627 | 1694.7597
2034-09-15 21:00 | 4545.93 | 1.3988 | 65.2426 | 48.4627 | 1332.2806
2034-09-16 22:00 | 3103.8 | 1 | 67.9323 | 48.4627 | 909.634
2034-09-17 23:00 | 2944.25 | 1 | 52.6698 | 48.4627 | 862.8745
2034-09-19 | 1369.63 | 1 | 53.0144 | 48.4627 | 401.3989
2034-09-20 01:00 | -24.4702 | 0.76565 | 53.0747 | 48.4627 | -7.1715
2034-09-21 02:00 | -345.277 | 1.6949 | 52.152 | 48.4627 | -101.1907
2034-09-22 03:00 | -546.132 | 2.2465 | 51.754 | 48.4627 | -160.0555
2034-09-23 04:00 | -813.757 | 3.0499 | 51.4565 | 48.4627 | -238.4886
2034-09-24 05:00 | -772.177 | 2.8422 | 51.2109 | 48.4627 | -226.3027
2034-09-25 06:00 | 0 | 1 | 51.9605 | 48.4627 | 0
2034-09-26 07:00 | 3017.54 | 1 | 50.87 | 48.4627 | 884.3537
2034-09-27 08:00 | 3028.77 | 1 | 51.094 | 48.4627 | 887.6449
2034-09-28 09:00 | 3138.63 | 1 | 51.1539 | 48.4627 | 919.8417
2034-09-29 10:00 | 3118.85 | 1 | 51.2041 | 48.4627 | 914.0447
2034-09-30 11:00 | 3107.79 | 1 | 64.7049 | 48.4627 | 910.8033
2034-10-01 12:00 | 3121.01 | 1 | 63.3642 | 48.4627 | 914.6777
2034-10-02 13:00 | 3937.37 | 1.2842 | 62.6448 | 48.4627 | 1153.9292
2034-10-03 14:00 | 4422 | 1.4295 | 62.7857 | 48.4627 | 1295.9603
2034-10-04 15:00 | 4811.65 | 1.5374 | 62.9595 | 48.4627 | 1410.1554
2034-10-05 16:00 | 7174.72 | 2.4147 | 62.469 | 48.4627 | 2102.7029
2034-10-06 17:00 | 6794.87 | 2.1952 | 63.1433 | 48.4627 | 1991.3798
2034-10-07 18:00 | 5670.92 | 1.827 | 63.2927 | 48.4627 | 1661.9826
2034-10-08 19:00 | 4187.24 | 1.369 | 63.0842 | 48.4627 | 1227.1589
2034-10-09 20:00 | 3279.72 | 1.0436 | 63.2334 | 48.4627 | 961.191
2034-10-10 21:00 | 3154.4 | 1 | 68.0402 | 48.4627 | 924.4634
2034-10-11 22:00 | 3263.5 | 1 | 51.2535 | 48.4627 | 956.4374
2034-10-12 23:00 | 0 | 0 | 52.3248 | 48.4627 | 0
2034-10-14 | -910.208 | 3.5081 | 51.0975 | 48.4627 | -266.7556
2034-10-15 01:00 | -1174.72 | 4.1136 | 50.7254 | 48.4627 | -344.2764
2034-10-16 02:00 | -1406.77 | 4.8149 | 50.5235 | 48.4627 | -412.2836
2034-10-17 03:00 | -1587.5 | 5.3428 | 50.3373 | 48.4627 | -465.2503
2034-10-18 04:00 | -1633.15 | 5.45 | 50.1373 | 48.4627 | -478.629
2034-10-19 05:00 | -1665.25 | 5.5543 | 50.0065 | 48.4627 | -488.0366
2034-10-20 06:00 | -616.454 | 2.1082 | 49.9203 | 48.4627 | -180.6648
2034-10-21 07:00 | 2113.99 | 1 | 50.1882 | 48.4627 | 619.5493
2034-10-22 08:00 | 2907.11 | 1 | 50.1514 | 48.4627 | 851.9898
2034-10-23 09:00 | 3034.02 | 1 | 63.7011 | 48.4627 | 889.1835
2034-10-24 10:00 | 4508.93 | 1.4954 | 61.5929 | 48.4627 | 1321.4369
2034-10-25 11:00 | 6063.76 | 2.0088 | 61.8355 | 48.4627 | 1777.1126
2034-10-26 12:00 | 6913.11 | 2.2546 | 62.2999 | 48.4627 | 2026.0325
2034-10-27 13:00 | 7234.9 | 2.3625 | 62.5244 | 48.4627 | 2120.3399
2034-10-28 14:00 | 7389.14 | 2.3985 | 62.768 | 48.4627 | 2165.5432
2034-10-29 15:00 | 7360.44 | 2.3771 | 62.9785 | 48.4627 | 2157.132
2034-10-30 16:00 | 9616.98 | 3.1867 | 62.8133 | 48.4627 | 2818.4586
2034-10-31 17:00 | 8817.84 | 2.7964 | 63.5737 | 48.4627 | 2584.2538
2034-11-01 18:00 | 7489.61 | 2.356 | 63.7825 | 48.4627 | 2194.988
2034-11-02 19:00 | 6067.32 | 1.8519 | 64.0665 | 48.4627 | 1778.156
2034-11-03 20:00 | 5177.42 | 1.5687 | 64.0398 | 48.4627 | 1517.352
2034-11-04 21:00 | 4249.61 | 1.357 | 63.3688 | 48.4627 | 1245.4377
2034-11-05 22:00 | 3554.53 | 1.1308 | 63.2462 | 48.4627 | 1041.7299
2034-11-06 23:00 | 3086.93 | 1 | 51.41 | 48.4627 | 904.6899
2034-11-08 | 3104.29 | 1 | 51.2812 | 48.4627 | 909.7776
2034-11-09 01:00 | 2948.99 | 1 | 51.269 | 48.4627 | 864.2637
2034-11-10 02:00 | 431.699 | 1 | 52.0761 | 48.4627 | 126.5185
2034-11-11 03:00 | 2250.18 | 1 | 51.1757 | 48.4627 | 659.4627
2034-11-12 04:00 | 3146.26 | 1 | 50.8682 | 48.4627 | 922.0778
2034-11-13 05:00 | 3170.91 | 1 | 50.9469 | 48.4627 | 929.302
2034-11-14 06:00 | 3268.62 | 1 | 67.0434 | 48.4627 | 957.938
2034-11-15 07:00 | 3961.2 | 1.2095 | 63.0877 | 48.4627 | 1160.9131
2034-11-16 08:00 | 4199.47 | 1.2928 | 63.105 | 48.4627 | 1230.7432
2034-11-17 09:00 | 6153.66 | 1.9723 | 62.7336 | 48.4627 | 1803.4597
2034-11-18 10:00 | 6694.99 | 2.246 | 62.4745 | 48.4627 | 1962.1079
2034-11-19 11:00 | 7652.08 | 2.484 | 62.9844 | 48.4627 | 2242.6033
2034-11-20 12:00 | 7619.75 | 2.4289 | 63.3649 | 48.4627 | 2233.1283
2034-11-21 13:00 | 8057.31 | 2.7084 | 62.937 | 48.4627 | 2361.3645
2034-11-22 14:00 | 8971.4 | 2.9789 | 63.2166 | 48.4627 | 2629.2578
2034-11-23 15:00 | 10030.6 | 3.429 | 63.1024 | 48.4627 | 2939.6787
2034-11-24 16:00 | 10648.6 | 3.4662 | 63.8001 | 48.4627 | 3120.7966
2034-11-25 17:00 | 10522.4 | 3.4186 | 64.0051 | 48.4627 | 3083.811
2034-11-26 18:00 | 8995.2 | 2.8659 | 64.3459 | 48.4627 | 2636.2329
2034-11-27 19:00 | 7307.01 | 2.2832 | 64.53 | 48.4627 | 2141.4732
2034-11-28 20:00 | 4928.98 | 1.4764 | 64.8658 | 48.4627 | 1444.5414
2034-11-29 21:00 | 3638.15 | 1.1298 | 64.181 | 48.4627 | 1066.2365
2034-11-30 22:00 | 3112.58 | 1 | 51.9506 | 48.4627 | 912.2072
2034-12-01 23:00 | 3028.85 | 1 | 51.7643 | 48.4627 | 887.6683
2034-12-03 | 2498.91 | 1 | 51.7993 | 48.4627 | 732.3582
2034-12-04 01:00 | 249.417 | 1 | 52.4127 | 48.4627 | 73.0969
2034-12-05 02:00 | -71.7209 | 0.88377 | 51.9137 | 48.4627 | -21.0193
2034-12-06 03:00 | 0 | 0 | 51.9587 | 48.4627 | 0
2034-12-07 04:00 | -14.1729 | 0.69312 | 51.7336 | 48.4627 | -4.1537
2034-12-08 05:00 | 2008.66 | 1 | 50.9645 | 48.4627 | 588.6801
2034-12-09 06:00 | 2791.79 | 1 | 64.2307 | 48.4627 | 818.1929
2034-12-10 07:00 | 3834 | 1.2638 | 62.058 | 48.4627 | 1123.6345
2034-12-11 08:00 | 4094.19 | 1.3157 | 62.4679 | 48.4627 | 1199.8886
2034-12-12 09:00 | 5654.86 | 1.9224 | 61.996 | 48.4627 | 1657.2759
2034-12-13 10:00 | 7382.17 | 2.5168 | 62.1873 | 48.4627 | 2163.5005
2034-12-14 11:00 | 8408.49 | 2.8096 | 62.6641 | 48.4627 | 2464.2852
2034-12-15 12:00 | 9300.08 | 3.0006 | 63.2812 | 48.4627 | 2725.5844
2034-12-16 13:00 | 9411.61 | 3.1148 | 63.2751 | 48.4627 | 2758.2706
2034-12-17 14:00 | 9749.69 | 3.221 | 63.494 | 48.4627 | 2857.3521
2034-12-18 15:00 | 10913.2 | 3.5784 | 63.7438 | 48.4627 | 3198.3432
2034-12-19 16:00 | 10778.8 | 3.4436 | 64.2507 | 48.4627 | 3158.9544
2034-12-20 17:00 | 10054.2 | 3.2256 | 64.3434 | 48.4627 | 2946.5952
2034-12-21 18:00 | 8726.67 | 2.7432 | 64.5965 | 48.4627 | 2557.5345
2034-12-22 19:00 | 7463.25 | 2.3195 | 64.6607 | 48.4627 | 2187.2627
2034-12-23 20:00 | 5350.97 | 1.5998 | 64.9896 | 48.4627 | 1568.2145
2034-12-24 21:00 | 4117.85 | 1.267 | 64.4219 | 48.4627 | 1206.8227
2034-12-25 22:00 | 3116.33 | 1 | 69.8198 | 48.4627 | 913.3062
2034-12-26 23:00 | 3110.93 | 1 | 51.8685 | 48.4627 | 911.7236
2034-12-28 | 3122.77 | 1 | 51.7123 | 48.4627 | 915.1935
2034-12-29 01:00 | 3149.9 | 1 | 51.6007 | 48.4627 | 923.1446
2034-12-30 02:00 | 3173.78 | 1 | 51.5309 | 48.4627 | 930.1431
2034-12-31 03:00 | 3106.92 | 1 | 51.5005 | 48.4627 | 910.5484
2035-01-01 04:00 | 3152.29 | 1 | 51.4394 | 48.4627 | 923.845
2035-01-02 05:00 | 3152.27 | 1 | 51.3969 | 48.4627 | 923.8391
2035-01-03 06:00 | 3161.14 | 1 | 69.5772 | 48.4627 | 926.4387
2035-01-04 07:00 | 3178.68 | 1 | 65.41 | 48.4627 | 931.5791
2035-01-05 08:00 | 3187.38 | 1 | 51.2823 | 48.4627 | 934.1289
2035-01-06 09:00 | 3231.93 | 1 | 67.8835 | 48.4627 | 947.1852
2035-01-07 10:00 | 3649.6 | 1.1345 | 63.1951 | 48.4627 | 1069.5922
2035-01-08 11:00 | 4772.78 | 1.4709 | 63.3117 | 48.4627 | 1398.7637
2035-01-09 12:00 | 4644.37 | 1.4308 | 63.4163 | 48.4627 | 1361.1305
2035-01-10 13:00 | 4306.47 | 1.3526 | 63.2357 | 48.4627 | 1262.1018
2035-01-11 14:00 | 4689.04 | 1.4705 | 63.2214 | 48.4627 | 1374.222
2035-01-12 15:00 | 6321.32 | 2.0546 | 62.855 | 48.4627 | 1852.596
2035-01-13 16:00 | 6627.79 | 2.178 | 62.8974 | 48.4627 | 1942.4135
2035-01-14 17:00 | 6966.59 | 2.1755 | 63.5309 | 48.4627 | 2041.706
2035-01-15 18:00 | 6057.5 | 1.8484 | 63.8725 | 48.4627 | 1775.278
2035-01-16 19:00 | 5135.35 | 1.5791 | 63.784 | 48.4627 | 1505.0225
2035-01-17 20:00 | 3188.06 | 1 | 64.7156 | 48.4627 | 934.3282
2035-01-18 21:00 | 3178.58 | 1 | 51.4469 | 48.4627 | 931.5498
2035-01-19 22:00 | 0 | 0 | 52.4333 | 48.4627 | 0
2035-01-20 23:00 | -252.206 | 1.1338 | 51.2987 | 48.4627 | -73.9143
2035-01-22 | -272.702 | 1.4507 | 51.1578 | 48.4627 | -79.9211
2035-01-23 01:00 | -340.235 | 1.6378 | 50.9413 | 48.4627 | -99.713
2035-01-24 02:00 | -429.127 | 1.9065 | 50.7624 | 48.4627 | -125.7647
2035-01-25 03:00 | -375.156 | 1.7083 | 50.643 | 48.4627 | -109.9474
2035-01-26 04:00 | -302.781 | 1.4974 | 50.624 | 48.4627 | -88.7364
2035-01-27 05:00 | 394.281 | 1 | 51.1011 | 48.4627 | 115.5524
2035-01-28 06:00 | 2072.7 | 1 | 50.5202 | 48.4627 | 607.4484
2035-01-29 07:00 | 2998.2 | 1.0487 | 61.0518 | 48.4627 | 878.6857
2035-01-30 08:00 | 3550.21 | 1.1842 | 61.643 | 48.4627 | 1040.4638
2035-01-31 09:00 | 5696.45 | 1.8723 | 61.9087 | 48.4627 | 1669.4647
2035-02-01 10:00 | 7665.89 | 2.5974 | 61.8979 | 48.4627 | 2246.6506
2035-02-02 11:00 | 9363.34 | 3.0419 | 62.698 | 48.4627 | 2744.1241
2035-02-03 12:00 | 10213.4 | 3.2731 | 63.2151 | 48.4627 | 2993.2521
2035-02-04 13:00 | 10484.1 | 3.3202 | 63.6687 | 48.4627 | 3072.5864
2035-02-05 14:00 | 10765.8 | 3.4742 | 63.7375 | 48.4627 | 3155.1445
2035-02-06 15:00 | 11605.2 | 3.8943 | 63.5549 | 48.4627 | 3401.1484
2035-02-07 16:00 | 11704.9 | 3.8866 | 63.9088 | 48.4627 | 3430.3676
2035-02-08 17:00 | 11420.3 | 3.7801 | 64.1249 | 48.4627 | 3346.9595
2035-02-09 18:00 | 9833.65 | 3.1339 | 64.6344 | 48.4627 | 2881.9583
2035-02-10 19:00 | 8233.58 | 2.6358 | 64.5529 | 48.4627 | 2413.0241
2035-02-11 20:00 | 6019.23 | 1.795 | 65.2175 | 48.4627 | 1764.0622
2035-02-12 21:00 | 4729.31 | 1.4479 | 64.6706 | 48.4627 | 1386.0239
2035-02-13 22:00 | 3157.26 | 1 | 68.067 | 48.4627 | 925.3016
2035-02-14 23:00 | 3029.76 | 1 | 52.0427 | 48.4627 | 887.935
2035-02-16 | 2997.69 | 1 | 51.8573 | 48.4627 | 878.5362
2035-02-17 01:00 | 2976.96 | 1 | 51.727 | 48.4627 | 872.4609
2035-02-18 02:00 | 383.92 | 1 | 52.5171 | 48.4627 | 112.5158
2035-02-19 03:00 | 75.5854 | 1 | 52.2853 | 48.4627 | 22.1519
2035-02-20 04:00 | -18.0468 | 0.69985 | 51.9854 | 48.4627 | -5.289
2035-02-21 05:00 | 2141.79 | 1 | 51.1693 | 48.4627 | 627.6967
2035-02-22 06:00 | 2977.32 | 1 | 50.9407 | 48.4627 | 872.5664
2035-02-23 07:00 | 3343.12 | 1.09 | 62.417 | 48.4627 | 979.7718
2035-02-24 08:00 | 3900.52 | 1.2184 | 62.905 | 48.4627 | 1143.1296
2035-02-25 09:00 | 6089.25 | 1.9338 | 62.8128 | 48.4627 | 1784.583
2035-02-26 10:00 | 7710.2 | 2.5726 | 62.573 | 48.4627 | 2259.6366
2035-02-27 11:00 | 8970.31 | 3.0141 | 62.7872 | 48.4627 | 2628.9383
2035-02-28 12:00 | 9663.86 | 3.2181 | 63.1494 | 48.4627 | 2832.1978
2035-03-01 13:00 | 9983.26 | 3.2987 | 63.4697 | 48.4627 | 2925.8047
2035-03-02 14:00 | 10383.8 | 3.3348 | 63.9869 | 48.4627 | 3043.1914
2035-03-03 15:00 | 11292.4 | 3.6577 | 64.0852 | 48.4627 | 3309.4758
2035-03-04 16:00 | 11500.5 | 3.7787 | 64.164 | 48.4627 | 3370.4638
2035-03-05 17:00 | 11318.3 | 3.6538 | 64.5107 | 48.4627 | 3317.0663
2035-03-06 18:00 | 9717.39 | 3.0706 | 64.8469 | 48.4627 | 2847.8859
2035-03-07 19:00 | 8234.1 | 2.5203 | 65.1522 | 48.4627 | 2413.1765
2035-03-08 20:00 | 6018.25 | 1.7545 | 65.595 | 48.4627 | 1763.775
2035-03-09 21:00 | 4810.9 | 1.4415 | 65.0291 | 48.4627 | 1409.9356
2035-03-10 22:00 | 3136.59 | 1 | 67.7647 | 48.4627 | 919.2438
2035-03-11 23:00 | 3095.75 | 1 | 52.1375 | 48.4627 | 907.2748
2035-03-13 | 1902.86 | 1 | 52.3557 | 48.4627 | 557.6732
2035-03-14 01:00 | 0 | 0 | 52.7608 | 48.4627 | 0
2035-03-15 02:00 | -154.741 | 1.1122 | 51.9505 | 48.4627 | -45.3501
2035-03-16 03:00 | -228.311 | 1.3057 | 51.5956 | 48.4627 | -66.9113
2035-03-17 04:00 | -345.561 | 1.6615 | 51.3214 | 48.4627 | -101.2739
2035-03-18 05:00 | -273.056 | 1.3977 | 51.1864 | 48.4627 | -80.0248
2035-03-19 06:00 | 1683.85 | 1 | 51.1333 | 48.4627 | 493.4877
2035-03-20 07:00 | 2682.05 | 1.0019 | 60.8736 | 48.4627 | 786.0313
2035-03-21 08:00 | 2907.76 | 1 | 63.9636 | 48.4627 | 852.1803
2035-03-22 09:00 | 4190.24 | 1.3129 | 62.7544 | 48.4627 | 1228.0381
2035-03-23 10:00 | 6297.72 | 2.066 | 62.4165 | 48.4627 | 1845.6795
2035-03-24 11:00 | 7634.6 | 2.5852 | 62.3772 | 48.4627 | 2237.4804
2035-03-25 12:00 | 8532.26 | 2.7349 | 63.2078 | 48.4627 | 2500.5586
2035-03-26 13:00 | 8496.61 | 2.7017 | 63.5378 | 48.4627 | 2490.1106
2035-03-27 14:00 | 8916.55 | 2.8421 | 63.6792 | 48.4627 | 2613.1828
2035-03-28 15:00 | 8888.62 | 2.9079 | 63.5676 | 48.4627 | 2604.9974
2035-03-29 16:00 | 11588.4 | 3.8511 | 63.51 | 48.4627 | 3396.2248
2035-03-30 17:00 | 10511.3 | 3.4301 | 64.0404 | 48.4627 | 3080.5579
2035-03-31 18:00 | 9439 | 2.9937 | 64.4504 | 48.4627 | 2766.2978
2035-04-01 19:00 | 7882.45 | 2.4699 | 64.5694 | 48.4627 | 2310.1181
2035-04-02 20:00 | 6930.69 | 2.0959 | 64.8744 | 48.4627 | 2031.1847
2035-04-03 21:00 | 6023.24 | 1.8447 | 64.6443 | 48.4627 | 1765.2374
2035-04-04 22:00 | 5510.66 | 1.6491 | 64.7532 | 48.4627 | 1615.015
2035-04-05 23:00 | 3118.74 | 1 | 69.435 | 48.4627 | 914.0125
2035-04-07 | 3170.34 | 1 | 51.9396 | 48.4627 | 929.1349
2035-04-08 01:00 | 3092.9 | 1 | 51.8148 | 48.4627 | 906.4395
2035-04-09 02:00 | 3125.16 | 1 | 51.7128 | 48.4627 | 915.894
2035-04-10 03:00 | 3183.65 | 1 | 51.6229 | 48.4627 | 933.0357
2035-04-11 04:00 | 2297.55 | 1 | 51.8501 | 48.4627 | 673.3454
2035-04-12 05:00 | 1050.33 | 1 | 52.1533 | 48.4627 | 307.8213
2035-04-13 06:00 | 3274.09 | 1 | 51.1778 | 48.4627 | 959.5411
2035-04-14 07:00 | 3232.83 | 1 | 63.5585 | 48.4627 | 947.4489
2035-04-15 08:00 | 3232.54 | 1 | 70.0127 | 48.4627 | 947.364
2035-04-16 09:00 | 3194.98 | 1 | 63.9611 | 48.4627 | 936.3562
2035-04-17 10:00 | 4208.97 | 1.2806 | 63.4456 | 48.4627 | 1233.5273
2035-04-18 11:00 | 3792.68 | 1.2379 | 62.7958 | 48.4627 | 1111.5248
2035-04-19 12:00 | 4789.49 | 1.5436 | 62.9063 | 48.4627 | 1403.661
2035-04-20 13:00 | 5167.6 | 1.6283 | 63.2141 | 48.4627 | 1514.4741
2035-04-21 14:00 | 5213.97 | 1.7567 | 62.5907 | 48.4627 | 1528.0638
2035-04-22 15:00 | 5675.99 | 1.8338 | 63.0535 | 48.4627 | 1663.4685
2035-04-23 16:00 | 8002.15 | 2.7759 | 62.3753 | 48.4627 | 2345.1987
2035-04-24 17:00 | 7011.19 | 2.3257 | 63.0973 | 48.4627 | 2054.777
2035-04-25 18:00 | 6184.61 | 1.9573 | 63.6331 | 48.4627 | 1812.5303
2035-04-26 19:00 | 4906.79 | 1.547 | 63.6288 | 48.4627 | 1438.0382
2035-04-27 20:00 | 4240.31 | 1.3103 | 63.7458 | 48.4627 | 1242.7122
2035-04-28 21:00 | 3550.87 | 1.1492 | 63.1565 | 48.4627 | 1040.6573
2035-04-29 22:00 | 3047.94 | 1 | 62.9315 | 48.4627 | 893.263
2035-04-30 23:00 | 2799.06 | 1 | 51.5023 | 48.4627 | 820.3235
2035-05-02 | 0 | 0 | 52.3717 | 48.4627 | 0
2035-05-03 01:00 | 8.7037 | 1 | 52.0471 | 48.4627 | 2.5508
2035-05-04 02:00 | -39.0787 | 0.7644 | 51.6866 | 48.4627 | -11.4528
2035-05-05 03:00 | 0 | 1 | 51.7413 | 48.4627 | 0
2035-05-06 04:00 | 108.771 | 1 | 51.584 | 48.4627 | 31.8776
2035-05-07 05:00 | 2169.22 | 1 | 50.7855 | 48.4627 | 635.7356
2035-05-08 06:00 | 2921.05 | 1 | 50.6671 | 48.4627 | 856.0752
2035-05-09 07:00 | 3079.58 | 1 | 50.7443 | 48.4627 | 902.5358
2035-05-10 08:00 | 3120.8 | 1 | 50.8005 | 48.4627 | 914.6162
2035-05-11 09:00 | 3469.07 | 1.0655 | 62.9536 | 48.4627 | 1016.6841
2035-05-12 10:00 | 5560.79 | 1.7293 | 62.8467 | 48.4627 | 1629.7067
2035-05-13 11:00 | 6964.59 | 2.3125 | 62.3776 | 48.4627 | 2041.1198
2035-05-14 12:00 | 8288.14 | 2.6326 | 63.1068 | 48.4627 | 2429.0141
2035-05-15 13:00 | 7894.37 | 2.443 | 63.6715 | 48.4627 | 2313.6115
2035-05-16 14:00 | 8580.79 | 2.7656 | 63.391 | 48.4627 | 2514.7813
2035-05-17 15:00 | 9851.42 | 3.2707 | 63.2813 | 48.4627 | 2887.1662
2035-05-18 16:00 | 9826.64 | 3.2138 | 63.6877 | 48.4627 | 2879.9039
2035-05-19 17:00 | 10170.7 | 3.2807 | 63.9788 | 48.4627 | 2980.7379
2035-05-20 18:00 | 8904.5 | 2.7938 | 64.4073 | 48.4627 | 2609.6513
2035-05-21 19:00 | 7322.45 | 2.3025 | 64.3982 | 48.4627 | 2145.9983
2035-05-22 20:00 | 5107.55 | 1.5168 | 64.9315 | 48.4627 | 1496.8751
2035-05-23 21:00 | 3764.83 | 1.1553 | 64.3252 | 48.4627 | 1103.3628
2035-05-24 22:00 | 3032.93 | 1 | 52.0231 | 48.4627 | 888.864
2035-05-25 23:00 | 3039.07 | 1 | 51.7996 | 48.4627 | 890.6635
2035-05-27 | 0 | 0 | 52.698 | 48.4627 | 0
2035-05-28 01:00 | 97.9139 | 1 | 52.2728 | 48.4627 | 28.6957
2035-05-29 02:00 | 95.0652 | 1 | 52.0494 | 48.4627 | 27.8609
2035-05-30 03:00 | 0 | 1 | 51.9388 | 48.4627 | 0
2035-05-31 04:00 | 2627.12 | 1 | 50.8983 | 48.4627 | 769.9329
2035-06-01 05:00 | 2969.1 | 1 | 50.8895 | 48.4627 | 870.1573
2035-06-02 06:00 | 3088.49 | 1 | 50.9364 | 48.4627 | 905.1471
2035-06-03 07:00 | 3146.2 | 1 | 50.9468 | 48.4627 | 922.0602
2035-06-04 08:00 | 3160.48 | 1 | 50.9816 | 48.4627 | 926.2453
2035-06-05 09:00 | 3236.11 | 1 | 69.9474 | 48.4627 | 948.4102
2035-06-06 10:00 | 3233.06 | 1 | 66.6611 | 48.4627 | 947.5164
2035-06-07 11:00 | 3245.98 | 1 | 63.8067 | 48.4627 | 951.3028
2035-06-08 12:00 | 3366.41 | 1.0311 | 63.1097 | 48.4627 | 986.5974
2035-06-09 13:00 | 4335.93 | 1.3585 | 62.8672 | 48.4627 | 1270.7356
2035-06-10 14:00 | 5253.3 | 1.667 | 62.8199 | 48.4627 | 1539.5903
2035-06-11 15:00 | 7018.14 | 2.3894 | 62.2232 | 48.4627 | 2056.8138
2035-06-12 16:00 | 7518.11 | 2.4776 | 62.7656 | 48.4627 | 2203.3405
2035-06-13 17:00 | 7815.19 | 2.4757 | 63.3438 | 48.4627 | 2290.4061
2035-06-14 18:00 | 6821.38 | 2.1089 | 63.7461 | 48.4627 | 1999.1491
2035-06-15 19:00 | 6060.91 | 1.8532 | 63.8808 | 48.4627 | 1776.2774
2035-06-16 20:00 | 4045.69 | 1.2346 | 63.8767 | 48.4627 | 1185.6747
2035-06-17 21:00 | 3328.93 | 1.0347 | 63.4868 | 48.4627 | 975.6131
2035-06-18 22:00 | 3116.04 | 1 | 51.3859 | 48.4627 | 913.2212
2035-06-19 23:00 | 3150.18 | 1 | 51.2718 | 48.4627 | 923.2266
2035-06-21 | 3228.43 | 1 | 51.202 | 48.4627 | 946.1594
2035-06-22 01:00 | 3183.5 | 1 | 51.1932 | 48.4627 | 932.9918
2035-06-23 02:00 | 3178.56 | 1 | 51.1888 | 48.4627 | 931.544
2035-06-24 03:00 | 3219.36 | 1 | 51.1657 | 48.4627 | 943.5013
2035-06-25 04:00 | 3230.88 | 1 | 51.1463 | 48.4627 | 946.8775
2035-06-26 05:00 | 3202.16 | 1 | 64.7146 | 48.4627 | 938.4605
2035-06-27 06:00 | 3836.97 | 1.1725 | 63.2487 | 48.4627 | 1124.5049
2035-06-28 07:00 | 4999.57 | 1.5817 | 62.9128 | 48.4627 | 1465.2293
2035-06-29 08:00 | 5622.82 | 1.674 | 63.7253 | 48.4627 | 1647.8859
2035-06-30 09:00 | 7027.19 | 2.3733 | 62.5203 | 48.4627 | 2059.4661
2035-07-01 10:00 | 8922.57 | 3.0312 | 62.682 | 48.4627 | 2614.9471
2035-07-02 11:00 | 10728.2 | 3.553 | 63.2637 | 48.4627 | 3144.1251
2035-07-03 12:00 | 11832.2 | 3.8586 | 63.7975 | 48.4627 | 3467.6755
2035-07-04 13:00 | 11902.6 | 3.7888 | 64.3945 | 48.4627 | 3488.3077
2035-07-05 14:00 | 12783.5 | 4.02 | 64.768 | 48.4627 | 3746.474
2035-07-06 15:00 | 13885.4 | 4.5214 | 64.6658 | 48.4627 | 4069.409
2035-07-07 16:00 | 14063.5 | 4.531 | 65.0793 | 48.4627 | 4121.605
2035-07-08 17:00 | 13767.4 | 4.4505 | 65.2679 | 48.4627 | 4034.8266
2035-07-09 18:00 | 11995.5 | 3.7117 | 65.8843 | 48.4627 | 3515.534
2035-07-10 19:00 | 10716 | 3.3709 | 65.6866 | 48.4627 | 3140.5496
2035-07-11 20:00 | 8940.82 | 2.6459 | 66.2957 | 48.4627 | 2620.2957
2035-07-12 21:00 | 7682.3 | 2.3887 | 65.5765 | 48.4627 | 2251.4599
2035-07-13 22:00 | 4424.6 | 1.3361 | 65.7022 | 48.4627 | 1296.7223
2035-07-14 23:00 | 3112.63 | 1.0006 | 64.5927 | 48.4627 | 912.2218
2035-07-16 | 3035.97 | 1 | 52.67 | 48.4627 | 889.755
2035-07-17 01:00 | 3174.31 | 1 | 52.4002 | 48.4627 | 930.2984
2035-07-18 02:00 | 3090.35 | 1 | 52.2727 | 48.4627 | 905.6922
2035-07-19 03:00 | 3200.51 | 1 | 52.0782 | 48.4627 | 937.9769
2035-07-20 04:00 | 3170.63 | 1 | 51.9896 | 48.4627 | 929.2199
2035-07-21 05:00 | 3177.36 | 1 | 67.2785 | 48.4627 | 931.1923
2035-07-22 06:00 | 3284.75 | 1 | 65.6 | 48.4627 | 962.6652
2035-07-23 07:00 | 3932.8 | 1.2476 | 63.5103 | 48.4627 | 1152.5899
2035-07-24 08:00 | 3986.99 | 1.2522 | 63.6364 | 48.4627 | 1168.4714
2035-07-25 09:00 | 6063.51 | 1.9828 | 63.2005 | 48.4627 | 1777.0394
2035-07-26 10:00 | 7298.25 | 2.4169 | 63.2653 | 48.4627 | 2138.9059
2035-07-27 11:00 | 7020.81 | 2.2941 | 63.6367 | 48.4627 | 2057.5963
2035-07-28 12:00 | 7988.64 | 2.6585 | 63.5455 | 48.4627 | 2341.2393
2035-07-29 13:00 | 8580.95 | 2.6312 | 64.5694 | 48.4627 | 2514.8282
2035-07-30 14:00 | 9529.62 | 3.0981 | 64.1183 | 48.4627 | 2792.8559
2035-07-31 15:00 | 10211.1 | 3.5332 | 63.6694 | 48.4627 | 2992.578
2035-08-01 16:00 | 10507.6 | 3.5228 | 64.1509 | 48.4627 | 3079.4736
2035-08-02 17:00 | 10035.2 | 3.336 | 64.3884 | 48.4627 | 2941.0268
2035-08-03 18:00 | 8579.34 | 2.7353 | 64.8955 | 48.4627 | 2514.3564
2035-08-04 19:00 | 7051.21 | 2.198 | 65.0735 | 48.4627 | 2066.5057
2035-08-05 20:00 | 4589.41 | 1.3939 | 65.2176 | 48.4627 | 1345.0233
2035-08-06 21:00 | 3152.9 | 1.0241 | 64.1888 | 48.4627 | 924.0238
2035-08-07 22:00 | 3037.65 | 1 | 52.437 | 48.4627 | 890.2473
2035-08-08 23:00 | 1414.67 | 1 | 52.8112 | 48.4627 | 414.5989
2035-08-10 | -26.4638 | 0.77327 | 52.8924 | 48.4627 | -7.7558
2035-08-11 01:00 | -385.423 | 1.8238 | 51.9526 | 48.4627 | -112.9563
2035-08-12 02:00 | -529.587 | 2.1854 | 51.6041 | 48.4627 | -155.2066
2035-08-13 03:00 | -550.244 | 2.2194 | 51.3949 | 48.4627 | -161.2606
2035-08-14 04:00 | -479.162 | 1.9937 | 51.2424 | 48.4627 | -140.4285
2035-08-15 05:00 | -160.91 | 1.0043 | 51.3747 | 48.4627 | -47.1581
2035-08-16 06:00 | 1895.98 | 1 | 51.191 | 48.4627 | 555.6569
2035-08-17 07:00 | 2970.92 | 1 | 50.9428 | 48.4627 | 870.6907
2035-08-18 08:00 | 3009.45 | 1 | 51.0835 | 48.4627 | 881.9827
2035-08-19 09:00 | 3518.04 | 1.1292 | 62.7346 | 48.4627 | 1031.0357
2035-08-20 10:00 | 5622.81 | 1.8088 | 62.7445 | 48.4627 | 1647.8829
2035-08-21 11:00 | 7148.21 | 2.3973 | 62.5706 | 48.4627 | 2094.9336
2035-08-22 12:00 | 7718.61 | 2.5697 | 62.9229 | 48.4627 | 2262.1013
2035-08-23 13:00 | 7982.73 | 2.6583 | 63.1227 | 48.4627 | 2339.5072
2035-08-24 14:00 | 8391.45 | 2.6959 | 63.6554 | 48.4627 | 2459.2912
2035-08-25 15:00 | 9695.36 | 3.1564 | 63.6762 | 48.4627 | 2841.4295
2035-08-26 16:00 | 9359.26 | 3.0678 | 63.8369 | 48.4627 | 2742.9283
2035-08-27 17:00 | 9081.88 | 2.9681 | 63.9776 | 48.4627 | 2661.6363
2035-08-28 18:00 | 7612.32 | 2.4118 | 64.3561 | 48.4627 | 2230.9508
2035-08-29 19:00 | 6261.28 | 1.9458 | 64.4913 | 48.4627 | 1835
2035-08-30 20:00 | 3381.24 | 1.0261 | 64.6275 | 48.4627 | 990.9436
2035-08-31 21:00 | 3204.57 | 1 | 68.474 | 48.4627 | 939.1668
2035-09-01 22:00 | 3045.46 | 1 | 51.9115 | 48.4627 | 892.5362
2035-09-02 23:00 | -130.369 | 1.1016 | 52.4193 | 48.4627 | -38.2074
2035-09-04 | -316.142 | 1.5804 | 51.7317 | 48.4627 | -92.6521
2035-09-05 01:00 | -449.327 | 1.9621 | 51.3586 | 48.4627 | -131.6847
2035-09-06 02:00 | -475.534 | 2.0108 | 51.1766 | 48.4627 | -139.3653
2035-09-07 03:00 | -541.703 | 2.2218 | 50.9951 | 48.4627 | -158.7575
2035-09-08 04:00 | -642.444 | 2.5286 | 50.8038 | 48.4627 | -188.2818
2035-09-09 05:00 | -756.135 | 2.8674 | 50.6591 | 48.4627 | -221.6013
2035-09-10 06:00 | 0 | 1 | 51.4411 | 48.4627 | 0
2035-09-11 07:00 | 2449.23 | 1 | 50.5789 | 48.4627 | 717.7985
2035-09-12 08:00 | 2845.25 | 1 | 50.6538 | 48.4627 | 833.8605
2035-09-13 09:00 | 3074.27 | 1.0116 | 62.0546 | 48.4627 | 900.9796
2035-09-14 10:00 | 5119.74 | 1.6441 | 62.3347 | 48.4627 | 1500.4477
2035-09-15 11:00 | 5939.47 | 2.0081 | 62.0677 | 48.4627 | 1740.6868
2035-09-16 12:00 | 6267.03 | 2.0974 | 62.4094 | 48.4627 | 1836.6852
2035-09-17 13:00 | 5627.85 | 1.8292 | 62.8545 | 48.4627 | 1649.36
2035-09-18 14:00 | 6476.23 | 2.0812 | 63.0092 | 48.4627 | 1897.9957
2035-09-19 15:00 | 6522.74 | 2.1485 | 62.8788 | 48.4627 | 1911.6264
2035-09-20 16:00 | 8422.79 | 2.7696 | 62.973 | 48.4627 | 2468.4761
2035-09-21 17:00 | 7446.95 | 2.4078 | 63.3804 | 48.4627 | 2182.4856
2035-09-22 18:00 | 6240.74 | 1.9974 | 63.5467 | 48.4627 | 1828.9803
2035-09-23 19:00 | 4529.35 | 1.4225 | 63.6851 | 48.4627 | 1327.4215
2035-09-24 20:00 | 3388.14 | 1.0731 | 63.441 | 48.4627 | 992.9658
2035-09-25 21:00 | 3135.97 | 1 | 67.1612 | 48.4627 | 919.0621
2035-09-26 22:00 | 3139.99 | 1 | 51.3823 | 48.4627 | 920.2402
2035-09-27 23:00 | -443.844 | 2.0677 | 51.653 | 48.4627 | -130.0778
2035-09-29 | -813.705 | 3.0836 | 51.0813 | 48.4627 | -238.4734
2035-09-30 01:00 | -1146.68 | 4.066 | 50.76 | 48.4627 | -336.0587
2035-10-01 02:00 | -1429.32 | 4.892 | 50.5487 | 48.4627 | -418.8923
2035-10-02 03:00 | -1625.73 | 5.4587 | 50.3514 | 48.4627 | -476.4544
2035-10-03 04:00 | -1866.12 | 6.2045 | 50.1486 | 48.4627 | -546.9058
2035-10-04 05:00 | -1897.72 | 6.2388 | 50.0012 | 48.4627 | -556.1668
2035-10-05 06:00 | -718.539 | 2.3661 | 49.8831 | 48.4627 | -210.583
2035-10-06 07:00 | 1909.75 | 1 | 50.2709 | 48.4627 | 559.6925
2035-10-07 08:00 | 2690.14 | 1 | 50.2352 | 48.4627 | 788.4022
2035-10-08 09:00 | 3005.68 | 1.0628 | 60.9171 | 48.4627 | 880.8779
2035-10-09 10:00 | 4973.14 | 1.6465 | 61.6305 | 48.4627 | 1457.4835
2035-10-10 11:00 | 6468.01 | 2.1319 | 61.9473 | 48.4627 | 1895.5866
2035-10-11 12:00 | 7430.54 | 2.4442 | 62.2791 | 48.4627 | 2177.6763
2035-10-12 13:00 | 7647.64 | 2.5028 | 62.5907 | 48.4627 | 2241.302
2035-10-13 14:00 | 7918.86 | 2.56 | 62.9061 | 48.4627 | 2320.7888
2035-10-14 15:00 | 7845.54 | 2.5032 | 63.219 | 48.4627 | 2299.3008
2035-10-15 16:00 | 9469.03 | 3.1223 | 62.9857 | 48.4627 | 2775.0988
2035-10-16 17:00 | 8442.27 | 2.7092 | 63.5188 | 48.4627 | 2474.1851
2035-10-17 18:00 | 6844.24 | 2.1714 | 63.7123 | 48.4627 | 2005.8487
2035-10-18 19:00 | 5256.36 | 1.6462 | 63.7567 | 48.4627 | 1540.487
2035-10-19 20:00 | 3957.11 | 1.2385 | 63.6073 | 48.4627 | 1159.7145
2035-10-20 21:00 | 3155.38 | 1 | 64.5164 | 48.4627 | 924.7506
2035-10-21 22:00 | 3119.76 | 1 | 68.6996 | 48.4627 | 914.3114
2035-10-22 23:00 | 0 | 0 | 52.318 | 48.4627 | 0
2035-10-24 | -472.288 | 2.1392 | 51.1918 | 48.4627 | -138.4139
2035-10-25 01:00 | -746.421 | 2.8725 | 50.789 | 48.4627 | -218.7544
2035-10-26 02:00 | -930.011 | 3.397 | 50.5613 | 48.4627 | -272.5593
2035-10-27 03:00 | -977.366 | 3.5027 | 50.382 | 48.4627 | -286.4377
2035-10-28 04:00 | -926.577 | 3.3335 | 50.2228 | 48.4627 | -271.5529
2035-10-29 05:00 | -426.298 | 1.7279 | 50.2367 | 48.4627 | -124.9356
2035-10-30 06:00 | 359.115 | 1 | 50.9208 | 48.4627 | 105.2462
2035-10-31 07:00 | 2201.39 | 1 | 61.3314 | 48.4627 | 645.1637
2035-11-01 08:00 | 2663.52 | 1 | 61.1701 | 48.4627 | 780.6007
2035-11-02 09:00 | 4735.19 | 1.5295 | 61.8241 | 48.4627 | 1387.7472
2035-11-03 10:00 | 6635.28 | 2.2289 | 61.6651 | 48.4627 | 1944.6086
2035-11-04 11:00 | 8304.67 | 2.7219 | 62.2609 | 48.4627 | 2433.8585
2035-11-05 12:00 | 9023.38 | 2.9717 | 62.5769 | 48.4627 | 2644.4916
2035-11-06 13:00 | 9772.97 | 3.2359 | 62.8154 | 48.4627 | 2864.1748
2035-11-07 14:00 | 10560.4 | 3.3547 | 63.5331 | 48.4627 | 3094.9477
2035-11-08 15:00 | 11677.9 | 3.7739 | 63.6313 | 48.4627 | 3422.4546
2035-11-09 16:00 | 11283.4 | 3.6307 | 63.9744 | 48.4627 | 3306.8381
2035-11-10 17:00 | 11166.9 | 3.5539 | 64.2603 | 48.4627 | 3272.6953
2035-11-11 18:00 | 9326.5 | 2.9261 | 64.5561 | 48.4627 | 2733.3273
2035-11-12 19:00 | 7999.74 | 2.4788 | 64.6537 | 48.4627 | 2344.4924
2035-11-13 20:00 | 6033 | 1.8257 | 64.8206 | 48.4627 | 1768.0978
2035-11-14 21:00 | 5315.87 | 1.5461 | 65.0542 | 48.4627 | 1557.9277
2035-11-15 22:00 | 3311.15 | 1 | 64.9027 | 48.4627 | 970.4023
2035-11-16 23:00 | 3160.05 | 1 | 68.2179 | 48.4627 | 926.1192
2035-11-18 | 3131.39 | 1 | 51.7119 | 48.4627 | 917.7198
2035-11-19 01:00 | 3131.25 | 1 | 51.6108 | 48.4627 | 917.6788
2035-11-20 02:00 | 3151.2 | 1 | 51.5283 | 48.4627 | 923.5256
2035-11-21 03:00 | 3154.9 | 1 | 51.4573 | 48.4627 | 924.6099
2035-11-22 04:00 | 3213.15 | 1 | 51.4031 | 48.4627 | 941.6813
2035-11-23 05:00 | 3069.85 | 1 | 67.9063 | 48.4627 | 899.6842
2035-11-24 06:00 | 3255.91 | 1 | 65.9614 | 48.4627 | 954.213
2035-11-25 07:00 | 3894.59 | 1.201 | 63.362 | 48.4627 | 1141.3917
2035-11-26 08:00 | 3738 | 1.1834 | 63.135 | 48.4627 | 1095.4997
2035-11-27 09:00 | 5256.46 | 1.6326 | 63.3391 | 48.4627 | 1540.5164
2035-11-28 10:00 | 5291.56 | 1.623 | 63.6155 | 48.4627 | 1550.8032
2035-11-29 11:00 | 5773.53 | 1.8978 | 62.9534 | 48.4627 | 1692.0546
2035-11-30 12:00 | 6232.62 | 2.0405 | 63.0701 | 48.4627 | 1826.6006
2035-12-01 13:00 | 6178.73 | 1.9023 | 63.8091 | 48.4627 | 1810.807
2035-12-02 14:00 | 6965.03 | 2.1653 | 63.7471 | 48.4627 | 2041.2488
2035-12-03 15:00 | 8461.59 | 2.8673 | 62.9312 | 48.4627 | 2479.8472
2035-12-04 16:00 | 9172.93 | 3.0636 | 63.2734 | 48.4627 | 2688.3204
2035-12-05 17:00 | 9401.82 | 3.0376 | 63.7953 | 48.4627 | 2755.4014
2035-12-06 18:00 | 8161.22 | 2.5489 | 64.2999 | 48.4627 | 2391.8175
2035-12-07 19:00 | 6994.89 | 2.1307 | 64.5764 | 48.4627 | 2049.9999
2035-12-08 20:00 | 4894.47 | 1.4572 | 64.7729 | 48.4627 | 1434.4276
2035-12-09 21:00 | 3447.95 | 1.1871 | 63.0191 | 48.4627 | 1010.4944
2035-12-10 22:00 | 2793.39 | 1 | 51.9981 | 48.4627 | 818.6618
2035-12-11 23:00 | 2757.59 | 1 | 51.8123 | 48.4627 | 808.1699
2035-12-13 | -85.6525 | 0.96552 | 52.3308 | 48.4627 | -25.1023
2035-12-14 01:00 | -466.162 | 2.0707 | 51.5039 | 48.4627 | -136.6186
2035-12-15 02:00 | -836.314 | 3.1547 | 51.112 | 48.4627 | -245.0994
2035-12-16 03:00 | -959.544 | 3.4476 | 50.8709 | 48.4627 | -281.2146
2035-12-17 04:00 | -947.509 | 3.3859 | 50.6848 | 48.4627 | -277.6875
2035-12-18 05:00 | -742.119 | 2.7343 | 50.5455 | 48.4627 | -217.4936
2035-12-19 06:00 | -309.954 | 1.4105 | 50.6282 | 48.4627 | -90.8386
2035-12-20 07:00 | 2080.85 | 1 | 50.6103 | 48.4627 | 609.8369
2035-12-21 08:00 | 2920.44 | 1 | 50.5045 | 48.4627 | 855.8965
2035-12-22 09:00 | 2986.83 | 1 | 65.2162 | 48.4627 | 875.3535
2035-12-23 10:00 | 3783.31 | 1.2318 | 62.1033 | 48.4627 | 1108.7787
2035-12-24 11:00 | 5086.63 | 1.6645 | 62.1706 | 48.4627 | 1490.7441
2035-12-25 12:00 | 5562.32 | 1.8671 | 62.131 | 48.4627 | 1630.1551
2035-12-26 13:00 | 6225.37 | 2.0623 | 62.4209 | 48.4627 | 1824.4758
2035-12-27 14:00 | 6219.34 | 2.0442 | 62.6547 | 48.4627 | 1822.7086
2035-12-28 15:00 | 7198.81 | 2.3702 | 62.7399 | 48.4627 | 2109.7629
2035-12-29 16:00 | 6806.22 | 2.2046 | 63.0761 | 48.4627 | 1994.7062
2035-12-30 17:00 | 6647.02 | 2.1595 | 63.1108 | 48.4627 | 1948.0493
2035-12-31 18:00 | 4633.97 | 1.5209 | 63.0514 | 48.4627 | 1358.0825
2036-01-01 19:00 | 3124.52 | 1.0299 | 62.852 | 48.4627 | 915.7064
2036-01-02 20:00 | 3014.46 | 1 | 51.3542 | 48.4627 | 883.451
2036-01-03 21:00 | 0 | 0 | 52.2712 | 48.4627 | 0
2036-01-04 22:00 | -987.024 | 3.6385 | 50.9867 | 48.4627 | -289.2682
2036-01-05 23:00 | -1553.98 | 5.3432 | 50.5808 | 48.4627 | -455.4266
2036-01-07 | -1922.76 | 6.3896 | 50.3069 | 48.4627 | -563.5053
2036-01-08 01:00 | -2275.01 | 6.6648 | 49.9629 | 48.4627 | -666.7396
2036-01-09 02:00 | -2589.78 | 6.6648 | 49.594 | 48.4627 | -758.9896
2036-01-10 03:00 | -2574.05 | 6.6648 | 49.4273 | 48.4627 | -754.3796
2036-01-11 04:00 | -2506.27 | 6.6648 | 49.3295 | 48.4627 | -734.5152
2036-01-12 05:00 | -1982.28 | 6.5412 | 49.4677 | 48.4627 | -580.9489
2036-01-13 06:00 | -1557.71 | 5.1205 | 49.4205 | 48.4627 | -456.5197
2036-01-14 07:00 | -712.877 | 2.486 | 49.4576 | 48.4627 | -208.9236
2036-01-15 08:00 | -242.053 | 1.231 | 49.7964 | 48.4627 | -70.9387
2036-01-16 09:00 | 2649.52 | 1 | 49.612 | 48.4627 | 776.4977
2036-01-17 10:00 | 3048.17 | 1.0364 | 60.7877 | 48.4627 | 893.3304
2036-01-18 11:00 | 4262.13 | 1.426 | 61.1097 | 48.4627 | 1249.107
2036-01-19 12:00 | 5119.18 | 1.719 | 61.2864 | 48.4627 | 1500.2836
2036-01-20 13:00 | 5426.98 | 1.823 | 61.5085 | 48.4627 | 1590.4908
2036-01-21 14:00 | 5836.2 | 1.9512 | 61.7401 | 48.4627 | 1710.4214
2036-01-22 15:00 | 6613.84 | 2.2329 | 61.7765 | 48.4627 | 1938.3252
2036-01-23 16:00 | 6435.65 | 2.1625 | 62.003 | 48.4627 | 1886.1028
2036-01-24 17:00 | 6385.43 | 2.1009 | 62.3144 | 48.4627 | 1871.3848
2036-01-25 18:00 | 4519.51 | 1.4877 | 62.389 | 48.4627 | 1324.5376
2036-01-26 19:00 | 3008 | 1 | 62.6936 | 48.4627 | 881.5578
2036-01-27 20:00 | 2942.61 | 1 | 50.8427 | 48.4627 | 862.3939
2036-01-28 21:00 | -115.96 | 1.0578 | 51.3912 | 48.4627 | -33.9845
2036-01-29 22:00 | -1122.38 | 4.1992 | 50.5148 | 48.4627 | -328.9371
2036-01-30 23:00 | -1569.44 | 5.3695 | 50.1121 | 48.4627 | -459.9575
2036-02-01 | -1904.77 | 6.3677 | 49.8751 | 48.4627 | -558.233
2036-02-02 01:00 | -2085.84 | 6.6648 | 49.6488 | 48.4627 | -611.2994
2036-02-03 02:00 | -2234.23 | 6.6648 | 49.4007 | 48.4627 | -654.7882
2036-02-04 03:00 | -2219.08 | 6.6648 | 49.2805 | 48.4627 | -650.3482
2036-02-05 04:00 | -2182.36 | 6.6648 | 49.2007 | 48.4627 | -639.5866
2036-02-06 05:00 | -1764.12 | 5.8203 | 49.1952 | 48.4627 | -517.0125
2036-02-07 06:00 | -1141.34 | 3.8344 | 49.1813 | 48.4627 | -334.4937
2036-02-08 07:00 | -611.712 | 2.3017 | 49.3051 | 48.4627 | -179.2751
2036-02-09 08:00 | 0 | 0 | 50.2383 | 48.4627 | 0
2036-02-10 09:00 | 2549.42 | 1 | 62.9715 | 48.4627 | 747.1612
2036-02-11 10:00 | 3800.98 | 1.2657 | 60.7232 | 48.4627 | 1113.9573
2036-02-12 11:00 | 5546.83 | 1.8417 | 61.0236 | 48.4627 | 1625.6154
2036-02-13 12:00 | 6560.63 | 2.1656 | 61.3923 | 48.4627 | 1922.7309
2036-02-14 13:00 | 7168.95 | 2.3179 | 61.9032 | 48.4627 | 2101.0118
2036-02-15 14:00 | 7695.77 | 2.5133 | 62.0588 | 48.4627 | 2255.4075
2036-02-16 15:00 | 8710.93 | 2.8278 | 62.334 | 48.4627 | 2552.9216
2036-02-17 16:00 | 7974.36 | 2.5772 | 62.6395 | 48.4627 | 2337.0542
2036-02-18 17:00 | 7072.64 | 2.291 | 62.7181 | 48.4627 | 2072.7862
2036-02-19 18:00 | 5543.85 | 1.7327 | 63.1115 | 48.4627 | 1624.7421
2036-02-20 19:00 | 4175.1 | 1.336 | 62.7758 | 48.4627 | 1223.601
2036-02-21 20:00 | 3080.71 | 1 | 69.156 | 48.4627 | 902.867
2036-02-22 21:00 | 2980.66 | 1 | 50.8727 | 48.4627 | 873.5452
2036-02-23 22:00 | -313.77 | 1.6822 | 51.1704 | 48.4627 | -91.9569
2036-02-24 23:00 | -988.385 | 3.7113 | 50.518 | 48.4627 | -289.667
2036-02-26 | -1323.06 | 4.6102 | 50.1553 | 48.4627 | -387.7506
2036-02-27 01:00 | -1616.78 | 5.4938 | 49.933 | 48.4627 | -473.8314
2036-02-28 02:00 | -1834.62 | 6.1337 | 49.7353 | 48.4627 | -537.674
2036-02-29 03:00 | -1977.66 | 6.5566 | 49.5374 | 48.4627 | -579.5949
2036-03-01 04:00 | -2018.79 | 6.6592 | 49.404 | 48.4627 | -591.6489
2036-03-02 05:00 | -2151.39 | 6.6648 | 49.2318 | 48.4627 | -630.5102
2036-03-03 06:00 | -1261.96 | 4.1429 | 49.1912 | 48.4627 | -369.844
2036-03-04 07:00 | -495.66 | 1.8853 | 49.3346 | 48.4627 | -145.2636
2036-03-05 08:00 | -800.145 | 3.1295 | 49.414 | 48.4627 | -234.4994
2036-03-06 09:00 | -387.536 | 1.6411 | 49.4353 | 48.4627 | -113.5756
2036-03-07 10:00 | 2400.78 | 1 | 49.4257 | 48.4627 | 703.5992
2036-03-08 11:00 | 3071.59 | 1 | 64.4015 | 48.4627 | 900.1942
2036-03-09 12:00 | 3122.2 | 1 | 66.5209 | 48.4627 | 915.0265
2036-03-10 13:00 | 3099.58 | 1 | 49.7282 | 48.4627 | 908.3972
2036-03-11 14:00 | 3083.73 | 1 | 49.8103 | 48.4627 | 903.7521
2036-03-12 15:00 | 3042.04 | 1 | 49.8785 | 48.4627 | 891.5339
2036-03-13 16:00 | 4184.39 | 1.3659 | 61.3138 | 48.4627 | 1226.3237
2036-03-14 17:00 | 3198.17 | 1.0367 | 61.4704 | 48.4627 | 937.2911
2036-03-15 18:00 | 2941.1 | 1 | 50.0129 | 48.4627 | 861.9513
2036-03-16 19:00 | 3085.79 | 1 | 49.9398 | 48.4627 | 904.3558
2036-03-17 20:00 | 3044.14 | 1 | 49.9864 | 48.4627 | 892.1494
2036-03-18 21:00 | 0 | 0 | 51.062 | 48.4627 | 0
2036-03-19 22:00 | 0 | 0 | 50.7729 | 48.4627 | 0
2036-03-20 23:00 | -1172.76 | 4.4513 | 49.7316 | 48.4627 | -343.702
2036-03-22 | -1537.77 | 5.2875 | 49.4596 | 48.4627 | -450.6759
2036-03-23 01:00 | -1807.01 | 6.1065 | 49.2752 | 48.4627 | -529.5824
2036-03-24 02:00 | -1926.63 | 6.4295 | 49.1158 | 48.4627 | -564.6395
2036-03-25 03:00 | -1904.86 | 6.3282 | 49.0233 | 48.4627 | -558.2594
2036-03-26 04:00 | -1939 | 6.4624 | 48.9432 | 48.4627 | -568.2648
2036-03-27 05:00 | -1932.58 | 6.4311 | 48.8828 | 48.4627 | -566.3833
2036-03-28 06:00 | -1241.98 | 4.121 | 48.8233 | 48.4627 | -363.9884
2036-03-29 07:00 | -627.399 | 2.3329 | 48.9403 | 48.4627 | -183.8725
2036-03-30 08:00 | -878.005 | 3.3577 | 49.0067 | 48.4627 | -257.3179
2036-03-31 09:00 | -736.183 | 2.7767 | 48.985 | 48.4627 | -215.7539
2036-04-01 10:00 | -219.548 | 1.1336 | 49.2109 | 48.4627 | -64.3432
2036-04-02 11:00 | 1875.19 | 1 | 49.2635 | 48.4627 | 549.5639
2036-04-03 12:00 | 3092.59 | 1 | 49.0518 | 48.4627 | 906.3487
2036-04-04 13:00 | 3100.85 | 1 | 49.2656 | 48.4627 | 908.7694
2036-04-05 14:00 | 3079.86 | 1 | 49.3925 | 48.4627 | 902.6179
2036-04-06 15:00 | 3084.86 | 1 | 49.4725 | 48.4627 | 904.0832
2036-04-07 16:00 | 4337.46 | 1.3701 | 61.3322 | 48.4627 | 1271.184
2036-04-08 17:00 | 3418.26 | 1.096 | 61.3047 | 48.4627 | 1001.7931
2036-04-09 18:00 | 3093.85 | 1 | 64.2393 | 48.4627 | 906.7179
2036-04-10 19:00 | 3057.36 | 1 | 49.7013 | 48.4627 | 896.0238
2036-04-11 20:00 | 3043.7 | 1 | 49.7328 | 48.4627 | 892.0204
2036-04-12 21:00 | 3015.66 | 1 | 49.7862 | 48.4627 | 883.8027
2036-04-13 22:00 | 328.6 | 1 | 50.7313 | 48.4627 | 96.3032
2036-04-14 23:00 | -797.557 | 3.2791 | 49.7908 | 48.4627 | -233.7409
2036-04-16 | -1149.67 | 4.1318 | 49.4422 | 48.4627 | -336.935
2036-04-17 01:00 | -1303.79 | 4.5586 | 49.2668 | 48.4627 | -382.1031
2036-04-18 02:00 | -1394.18 | 4.8207 | 49.1356 | 48.4627 | -408.5938
2036-04-19 03:00 | -1244.68 | 4.3004 | 49.0209 | 48.4627 | -364.7797
2036-04-20 04:00 | -1042.3 | 3.6871 | 48.9858 | 48.4627 | -305.468
2036-04-21 05:00 | -610.766 | 2.3234 | 49.0361 | 48.4627 | -178.9978
2036-04-22 06:00 | -427.836 | 1.8678 | 49.1667 | 48.4627 | -125.3864
2036-04-23 07:00 | -128.033 | 0.93128 | 49.4847 | 48.4627 | -37.5228
2036-04-24 08:00 | -242.363 | 1.4039 | 49.3864 | 48.4627 | -71.0296
2036-04-25 09:00 | 201.4 | 1 | 49.8895 | 48.4627 | 59.0245
2036-04-26 10:00 | 2938.4 | 1 | 48.9887 | 48.4627 | 861.16
2036-04-27 11:00 | 3056.18 | 1 | 49.2256 | 48.4627 | 895.6779
2036-04-28 12:00 | 3046.49 | 1 | 66.8022 | 48.4627 | 892.8381
2036-04-29 13:00 | 4693.47 | 1.4853 | 61.1766 | 48.4627 | 1375.5203
2036-04-30 14:00 | 4973.75 | 1.6054 | 61.2235 | 48.4627 | 1457.6622
2036-05-01 15:00 | 6229.94 | 2.0398 | 61.2675 | 48.4627 | 1825.8152
2036-05-02 16:00 | 5755.1 | 1.8529 | 61.6531 | 48.4627 | 1686.6533
2036-05-03 17:00 | 5273.54 | 1.6602 | 61.9988 | 48.4627 | 1545.522
2036-05-04 18:00 | 3952.63 | 1.2488 | 62.0143 | 48.4627 | 1158.4015
2036-05-05 19:00 | 3079.47 | 1 | 63.0945 | 48.4627 | 902.5036
2036-05-06 20:00 | 3073.76 | 1 | 50.0969 | 48.4627 | 900.8301
2036-05-07 21:00 | 0 | 0 | 51.113 | 48.4627 | 0
2036-05-08 22:00 | -769.552 | 3.1277 | 49.9569 | 48.4627 | -225.5334
2036-05-09 23:00 | -1038.59 | 3.7725 | 49.6027 | 48.4627 | -304.3807
2036-05-11 | -1261 | 4.4463 | 49.4247 | 48.4627 | -369.5626
2036-05-12 01:00 | -1380.77 | 4.7794 | 49.2673 | 48.4627 | -404.6637
2036-05-13 02:00 | -1356.3 | 4.6703 | 49.1251 | 48.4627 | -397.4923
2036-05-14 03:00 | -1248.7 | 4.3291 | 49.0466 | 48.4627 | -365.9578
2036-05-15 04:00 | -1069.47 | 3.7731 | 49.0065 | 48.4627 | -313.4307
2036-05-16 05:00 | -620.24 | 2.3452 | 49.0321 | 48.4627 | -181.7744
2036-05-17 06:00 | -369.15 | 1.6723 | 49.1865 | 48.4627 | -108.1872
2036-05-18 07:00 | 0 | 1 | 49.9488 | 48.4627 | 0
2036-05-19 08:00 | -90.7249 | 0.9489 | 49.652 | 48.4627 | -26.5888
2036-05-20 09:00 | 2024.75 | 1 | 49.2999 | 48.4627 | 593.3956
2036-05-21 10:00 | 2753.5 | 1 | 59.7243 | 48.4627 | 806.9712
2036-05-22 11:00 | 5299.26 | 1.7858 | 60.4064 | 48.4627 | 1553.0598
2036-05-23 12:00 | 6687.75 | 2.263 | 60.7014 | 48.4627 | 1959.986
2036-05-24 13:00 | 7205.48 | 2.3539 | 61.3997 | 48.4627 | 2111.7177
2036-05-25 14:00 | 7614.67 | 2.573 | 61.327 | 48.4627 | 2231.6395
2036-05-26 15:00 | 9815.37 | 3.2851 | 61.6349 | 48.4627 | 2876.601
2036-05-27 16:00 | 9556.13 | 3.1001 | 62.3417 | 48.4627 | 2800.6252
2036-05-28 17:00 | 8911.16 | 2.8764 | 62.6167 | 48.4627 | 2611.6032
2036-05-29 18:00 | 6787.58 | 2.0978 | 63.1849 | 48.4627 | 1989.2433
2036-05-30 19:00 | 5239.73 | 1.5813 | 63.3699 | 48.4627 | 1535.6133
2036-05-31 20:00 | 3113.58 | 1 | 66.0614 | 48.4627 | 912.5002
2036-06-01 21:00 | 3098.24 | 1 | 50.7158 | 48.4627 | 908.0045
2036-06-02 22:00 | -271.66 | 1.5373 | 51.0523 | 48.4627 | -79.6157
2036-06-03 23:00 | -546.424 | 2.3022 | 50.4343 | 48.4627 | -160.1411
2036-06-05 | -1012 | 3.7499 | 50.0484 | 48.4627 | -296.5879
2036-06-06 01:00 | -1308.99 | 4.5837 | 49.79 | 48.4627 | -383.6271
2036-06-07 02:00 | -1497.38 | 5.128 | 49.5913 | 48.4627 | -438.8388
2036-06-08 03:00 | -1446.43 | 4.9126 | 49.3925 | 48.4627 | -423.9068
2036-06-09 04:00 | -1417.17 | 4.847 | 49.2849 | 48.4627 | -415.3315
2036-06-10 05:00 | -1061.76 | 3.6795 | 49.1948 | 48.4627 | -311.1711
2036-06-11 06:00 | -609.797 | 2.315 | 49.2316 | 48.4627 | -178.7139
2036-06-12 07:00 | 0 | 1 | 50.1204 | 48.4627 | 0
2036-06-13 08:00 | 3002.79 | 1 | 49.1424 | 48.4627 | 880.0309
2036-06-14 09:00 | 3057.42 | 1 | 62.7316 | 48.4627 | 896.0414
2036-06-15 10:00 | 4000.64 | 1.3222 | 60.8642 | 48.4627 | 1172.4718
2036-06-16 11:00 | 5423.22 | 1.6824 | 61.713 | 48.4627 | 1589.3889
2036-06-17 12:00 | 6551.27 | 2.1839 | 61.2211 | 48.4627 | 1919.9877
2036-06-18 13:00 | 7320.48 | 2.2936 | 62.1539 | 48.4627 | 2145.4209
2036-06-19 14:00 | 7722.54 | 2.4159 | 62.3959 | 48.4627 | 2263.2531
2036-06-20 15:00 | 9541.8 | 3.038 | 62.3988 | 48.4627 | 2796.4255
2036-06-21 16:00 | 9980.73 | 3.1619 | 62.7731 | 48.4627 | 2925.0632
2036-06-22 17:00 | 10013.8 | 3.1884 | 62.9783 | 48.4627 | 2934.7551
2036-06-23 18:00 | 8043.25 | 2.6206 | 62.9312 | 48.4627 | 2357.2439
2036-06-24 19:00 | 7116.15 | 2.1896 | 63.5217 | 48.4627 | 2085.5377
2036-06-25 20:00 | 5055.71 | 1.5884 | 63.2435 | 48.4627 | 1481.6823
2036-06-26 21:00 | 4193.19 | 1.3253 | 62.9939 | 48.4627 | 1228.9027
2036-06-27 22:00 | 3121.65 | 1 | 67.9453 | 48.4627 | 914.8653
2036-06-28 23:00 | 3101.13 | 1 | 50.8801 | 48.4627 | 908.8515
2036-06-30 | 3149.22 | 1 | 50.7682 | 48.4627 | 922.9453
2036-07-01 01:00 | 2455.69 | 1 | 50.946 | 48.4627 | 719.6917
2036-07-02 02:00 | 0 | 0 | 51.6883 | 48.4627 | 0
2036-07-03 03:00 | -234.883 | 1.3797 | 50.7989 | 48.4627 | -68.8374
2036-07-04 04:00 | -575.34 | 2.4136 | 50.3627 | 48.4627 | -168.6155
2036-07-05 05:00 | -338.576 | 1.5441 | 50.2558 | 48.4627 | -99.2268
2036-07-06 06:00 | -285.931 | 1.4676 | 50.2219 | 48.4627 | -83.7981
2036-07-07 07:00 | 1552.31 | 1 | 50.2531 | 48.4627 | 454.9372
2036-07-08 08:00 | 2656.89 | 1 | 49.992 | 48.4627 | 778.6576
2036-07-09 09:00 | 3038.04 | 1 | 50.0163 | 48.4627 | 890.3616
2036-07-10 10:00 | 3112.75 | 1 | 63.3555 | 48.4627 | 912.257
2036-07-11 11:00 | 4607.7 | 1.4517 | 61.9415 | 48.4627 | 1350.3836
2036-07-12 12:00 | 4530.08 | 1.5016 | 61.5935 | 48.4627 | 1327.6354
2036-07-13 13:00 | 5605.52 | 1.8214 | 61.8787 | 48.4627 | 1642.8157
2036-07-14 14:00 | 4524.22 | 1.5351 | 61.5908 | 48.4627 | 1325.918
2036-07-15 15:00 | 5757.8 | 1.8965 | 61.8763 | 48.4627 | 1687.4446
2036-07-16 16:00 | 6190.88 | 2.0256 | 62.0666 | 48.4627 | 1814.3678
2036-07-17 17:00 | 5879.33 | 1.9251 | 62.1775 | 48.4627 | 1723.0615
2036-07-18 18:00 | 4021.83 | 1.3244 | 62.1766 | 48.4627 | 1178.682
2036-07-19 19:00 | 3100.51 | 1 | 65.3768 | 48.4627 | 908.6698
2036-07-20 20:00 | 2866.57 | 1 | 50.648 | 48.4627 | 840.1087
2036-07-21 21:00 | -161.201 | 1.2149 | 51.0927 | 48.4627 | -47.2433
2036-07-22 22:00 | -1135.13 | 4.2422 | 50.2883 | 48.4627 | -332.6738
2036-07-23 23:00 | -1636.72 | 5.6047 | 49.8865 | 48.4627 | -479.6753
2036-07-25 | -2059.12 | 6.6648 | 49.6075 | 48.4627 | -603.4685
2036-07-26 01:00 | -2467.88 | 6.6648 | 49.1907 | 48.4627 | -723.2642
2036-07-27 02:00 | -2550.12 | 6.6648 | 48.9528 | 48.4627 | -747.3664
2036-07-28 03:00 | -2707.15 | 6.6648 | 48.736 | 48.4627 | -793.3873
2036-07-29 04:00 | -2852.23 | 6.6648 | 48.5365 | 48.4627 | -835.9061
2036-07-30 05:00 | -2429.5 | 6.6648 | 48.6279 | 48.4627 | -712.0162
2036-07-31 06:00 | -1962.71 | 6.5386 | 48.7939 | 48.4627 | -575.2135
2036-08-01 07:00 | -1252.5 | 4.1468 | 48.7708 | 48.4627 | -367.0715
2036-08-02 08:00 | -801.25 | 2.9084 | 48.8769 | 48.4627 | -234.8232
2036-08-03 09:00 | 1885.75 | 1 | 49.211 | 48.4627 | 552.6588
2036-08-04 10:00 | 3090.27 | 1 | 63.6478 | 48.4627 | 905.6687
2036-08-05 11:00 | 4100.52 | 1.3631 | 60.5503 | 48.4627 | 1201.7438
2036-08-06 12:00 | 4691.7 | 1.5564 | 60.8138 | 48.4627 | 1375.0015
2036-08-07 13:00 | 5098.39 | 1.6997 | 60.9694 | 48.4627 | 1494.1906
2036-08-08 14:00 | 5699.77 | 1.9082 | 61.1202 | 48.4627 | 1670.4377
2036-08-09 15:00 | 6507.56 | 2.2058 | 61.1625 | 48.4627 | 1907.1776
2036-08-10 16:00 | 5969.44 | 2.0514 | 61.2199 | 48.4627 | 1749.4702
2036-08-11 17:00 | 5519.36 | 1.8444 | 61.5739 | 48.4627 | 1617.5647
2036-08-12 18:00 | 3872.78 | 1.2905 | 61.6381 | 48.4627 | 1134.9998
2036-08-13 19:00 | 3042.65 | 1 | 63.1905 | 48.4627 | 891.7127
2036-08-14 20:00 | 2929.84 | 1 | 50.2771 | 48.4627 | 858.6513
2036-08-15 21:00 | 0 | 0 | 51.2204 | 48.4627 | 0
2036-08-16 22:00 | -921.267 | 3.5947 | 50.0341 | 48.4627 | -269.9967
2036-08-17 23:00 | -1545.01 | 5.3922 | 49.648 | 48.4627 | -452.7977
2036-08-19 | -1779.84 | 5.9926 | 49.4015 | 48.4627 | -521.6196
2036-08-20 01:00 | -1915.92 | 6.3966 | 49.2204 | 48.4627 | -561.5007
2036-08-21 02:00 | -2021.12 | 6.6648 | 49.0492 | 48.4627 | -592.3318
2036-08-22 03:00 | -2036.58 | 6.6648 | 48.9257 | 48.4627 | -596.8627
2036-08-23 04:00 | -2241.44 | 6.6648 | 48.7327 | 48.4627 | -656.9012
2036-08-24 05:00 | -2158.13 | 6.6648 | 48.6799 | 48.4627 | -632.4855
2036-08-25 06:00 | -932.183 | 3.0707 | 48.683 | 48.4627 | -273.1959
2036-08-26 07:00 | 1456.2 | 1 | 49.2747 | 48.4627 | 426.7701
2036-08-27 08:00 | 2784.36 | 1 | 49.0595 | 48.4627 | 816.0154
2036-08-28 09:00 | 3630.81 | 1.2335 | 60.2436 | 48.4627 | 1064.0854
2036-08-29 10:00 | 5705.19 | 1.9644 | 60.3 | 48.4627 | 1672.0261
2036-08-30 11:00 | 7009.05 | 2.3649 | 60.8513 | 48.4627 | 2054.1498
2036-08-31 12:00 | 7853.35 | 2.5283 | 61.6825 | 48.4627 | 2301.5897
2036-09-01 13:00 | 7797.12 | 2.524 | 61.9116 | 48.4627 | 2285.1103
2036-09-02 14:00 | 8218.25 | 2.6702 | 62.0665 | 48.4627 | 2408.5313
2036-09-03 15:00 | 8044.12 | 2.5856 | 62.3739 | 48.4627 | 2357.4989
2036-09-04 16:00 | 9651.73 | 3.1608 | 62.3075 | 48.4627 | 2828.6428
2036-09-05 17:00 | 8297.09 | 2.6763 | 62.7345 | 48.4627 | 2431.637
2036-09-06 18:00 | 6527.8 | 2.0788 | 62.9358 | 48.4627 | 1913.1093
2036-09-07 19:00 | 4863.93 | 1.5058 | 63.139 | 48.4627 | 1425.4772
2036-09-08 20:00 | 3750.35 | 1.1853 | 62.7431 | 48.4627 | 1099.1191
2036-09-09 21:00 | 3102.49 | 1 | 64.8984 | 48.4627 | 909.2501
2036-09-10 22:00 | 3060.35 | 1 | 68.5492 | 48.4627 | 896.9
2036-09-11 23:00 | 0 | 0 | 51.6284 | 48.4627 | 0
2036-09-13 | -747.271 | 2.7865 | 50.3611 | 48.4627 | -219.0035
2036-09-14 01:00 | -958.246 | 3.5217 | 50.0718 | 48.4627 | -280.8342
2036-09-15 02:00 | -1089.95 | 3.8836 | 49.8673 | 48.4627 | -319.4328
2036-09-16 03:00 | -1212.98 | 4.2579 | 49.704 | 48.4627 | -355.4893
2036-09-17 04:00 | -1339.94 | 4.647 | 49.5305 | 48.4627 | -392.6976
2036-09-18 05:00 | -1256.25 | 4.3337 | 49.4183 | 48.4627 | -368.1705
2036-09-19 06:00 | -359.748 | 1.4161 | 49.467 | 48.4627 | -105.4317
2036-09-20 07:00 | 2115.91 | 1 | 49.6265 | 48.4627 | 620.112
2036-09-21 08:00 | 2876.5 | 1 | 49.5917 | 48.4627 | 843.0189
2036-09-22 09:00 | 3658.03 | 1.1771 | 61.2878 | 48.4627 | 1072.0628
2036-09-23 10:00 | 5849.5 | 1.9665 | 60.9475 | 48.4627 | 1714.3192
2036-09-24 11:00 | 7627.09 | 2.5199 | 61.4467 | 48.4627 | 2235.2794
2036-09-25 12:00 | 8825.97 | 2.9157 | 61.8211 | 48.4627 | 2586.6365
2036-09-26 13:00 | 9726.92 | 3.1548 | 62.3362 | 48.4627 | 2850.6789
2036-09-27 14:00 | 9872.86 | 3.1574 | 62.7908 | 48.4627 | 2893.4496
2036-09-28 15:00 | 9972.93 | 3.1738 | 63.0837 | 48.4627 | 2922.7773
2036-09-29 16:00 | 11786.9 | 3.9057 | 62.8421 | 48.4627 | 3454.3994
2036-09-30 17:00 | 9927.44 | 3.1901 | 63.4929 | 48.4627 | 2909.4455
2036-10-01 18:00 | 8245.7 | 2.65 | 63.5516 | 48.4627 | 2416.5761
2036-10-02 19:00 | 7236.8 | 2.1993 | 64.0574 | 48.4627 | 2120.8967
2036-10-03 20:00 | 6648.4 | 1.976 | 64.2222 | 48.4627 | 1948.4537
2036-10-04 21:00 | 5667.58 | 1.708 | 64.0094 | 48.4627 | 1661.0037
2036-10-05 22:00 | 5057.89 | 1.5701 | 63.5348 | 48.4627 | 1482.3212
2036-10-06 23:00 | 3127.67 | 1 | 51.4588 | 48.4627 | 916.6296
2036-10-08 | 3090.06 | 1 | 51.2358 | 48.4627 | 905.6072
2036-10-09 01:00 | 2862.59 | 1 | 51.1736 | 48.4627 | 838.9423
2036-10-10 02:00 | 83.0478 | 1 | 52.0229 | 48.4627 | 24.3389
2036-10-11 03:00 | -127.867 | 1.0475 | 51.2898 | 48.4627 | -37.4741
2036-10-12 04:00 | -281.263 | 1.4926 | 50.8115 | 48.4627 | -82.43
2036-10-13 05:00 | -342.039 | 1.6461 | 50.6004 | 48.4627 | -100.2417
2036-10-14 06:00 | 1782.85 | 1 | 50.5633 | 48.4627 | 522.5018
2036-10-15 07:00 | 2687.98 | 1 | 60.5271 | 48.4627 | 787.7692
2036-10-16 08:00 | 3327.19 | 1.1256 | 61.3625 | 48.4627 | 975.1031
2036-10-17 09:00 | 5720.08 | 1.9177 | 61.5485 | 48.4627 | 1676.39
2036-10-18 10:00 | 6716.25 | 2.2768 | 61.7147 | 48.4627 | 1968.3386
2036-10-19 11:00 | 8372.92 | 2.7501 | 62.3001 | 48.4627 | 2453.8606
2036-10-20 12:00 | 9457.75 | 3.1357 | 62.4905 | 48.4627 | 2771.7929
2036-10-21 13:00 | 9557.56 | 3.1492 | 62.8393 | 48.4627 | 2801.0443
2036-10-22 14:00 | 9634.65 | 3.1456 | 63.1562 | 48.4627 | 2823.6372
2036-10-23 15:00 | 10174.5 | 3.2223 | 63.6353 | 48.4627 | 2981.8516
2036-10-24 16:00 | 11958.7 | 3.9545 | 63.3609 | 48.4627 | 3504.749
2036-10-25 17:00 | 10463.7 | 3.366 | 63.9659 | 48.4627 | 3066.6078
2036-10-26 18:00 | 8933.71 | 2.7788 | 64.389 | 48.4627 | 2618.2119
2036-10-27 19:00 | 7639.03 | 2.3681 | 64.3568 | 48.4627 | 2238.7787
2036-10-28 20:00 | 6711.5 | 2.0443 | 64.4533 | 48.4627 | 1966.9465
2036-10-29 21:00 | 5872.49 | 1.782 | 64.3775 | 48.4627 | 1721.0569
2036-10-30 22:00 | 5159.47 | 1.6031 | 63.9563 | 48.4627 | 1512.0914
2036-10-31 23:00 | 3117.52 | 1 | 68.8207 | 48.4627 | 913.6549
2036-11-02 | 3110.45 | 1 | 51.5884 | 48.4627 | 911.5829
2036-11-03 01:00 | 3044.64 | 1 | 51.4596 | 48.4627 | 892.2959
2036-11-04 02:00 | 3139.61 | 1 | 51.3393 | 48.4627 | 920.1289
2036-11-05 03:00 | 2267.72 | 1 | 51.5729 | 48.4627 | 664.6031
2036-11-06 04:00 | 3141.13 | 1 | 51.1191 | 48.4627 | 920.5743
2036-11-07 05:00 | 3139.17 | 1 | 51.1285 | 48.4627 | 919.9999
2036-11-08 06:00 | 3214.87 | 1 | 51.098 | 48.4627 | 942.1854
2036-11-09 07:00 | 3334.02 | 1.0584 | 62.8581 | 48.4627 | 977.1048
2036-11-10 08:00 | 4176.79 | 1.3277 | 62.8008 | 48.4627 | 1224.0963
2036-11-11 09:00 | 6593.44 | 2.1603 | 62.5543 | 48.4627 | 1932.3465
2036-11-12 10:00 | 9113.57 | 3.0354 | 62.6363 | 48.4627 | 2670.9237
2036-11-13 11:00 | 10862.5 | 3.636 | 62.9683 | 48.4627 | 3183.4845
2036-11-14 12:00 | 11722.6 | 3.8634 | 63.5102 | 48.4627 | 3435.5549
2036-11-15 13:00 | 12085.5 | 3.9716 | 63.8698 | 48.4627 | 3541.9104
2036-11-16 14:00 | 12616.8 | 4.1022 | 64.2518 | 48.4627 | 3697.6191
2036-11-17 15:00 | 13532.6 | 4.4166 | 64.4635 | 48.4627 | 3966.0136
2036-11-18 16:00 | 13048.3 | 4.2493 | 64.7397 | 48.4627 | 3824.0792
2036-11-19 17:00 | 12541.1 | 3.9954 | 65.1086 | 48.4627 | 3675.4336
2036-11-20 18:00 | 10229.1 | 3.2621 | 65.1852 | 48.4627 | 2997.8533
2036-11-21 19:00 | 8757 | 2.7177 | 65.3726 | 48.4627 | 2566.4234
2036-11-22 20:00 | 6430.32 | 1.9224 | 65.6359 | 48.4627 | 1884.5408
2036-11-23 21:00 | 5426.66 | 1.6544 | 65.1289 | 48.4627 | 1590.3971
2036-11-24 22:00 | 3093.76 | 1 | 65.0864 | 48.4627 | 906.6916
2036-11-25 23:00 | 3082.45 | 1 | 69.5384 | 48.4627 | 903.3769
2036-11-27 | 3122.38 | 1 | 52.0944 | 48.4627 | 915.0792
2036-11-28 01:00 | 3134.59 | 1 | 51.9446 | 48.4627 | 918.6576
2036-11-29 02:00 | 3192.72 | 1 | 51.8113 | 48.4627 | 935.6939
2036-11-30 03:00 | 3076.73 | 1 | 51.7547 | 48.4627 | 901.7006
2036-12-01 04:00 | 3122.68 | 1 | 51.6674 | 48.4627 | 915.1672
2036-12-02 05:00 | 3117.53 | 1 | 51.6094 | 48.4627 | 913.6579
2036-12-03 06:00 | 3268.94 | 1 | 51.5099 | 48.4627 | 958.0317
2036-12-04 07:00 | 3202.57 | 1 | 66.8815 | 48.4627 | 938.5806
2036-12-05 08:00 | 3231.59 | 1 | 66.6782 | 48.4627 | 947.0855
2036-12-06 09:00 | 4576.12 | 1.4267 | 63.3646 | 48.4627 | 1341.1284
2036-12-07 10:00 | 5681.99 | 1.8074 | 63.2556 | 48.4627 | 1665.2269
2036-12-08 11:00 | 8255.22 | 2.7493 | 62.9151 | 48.4627 | 2419.3662
2036-12-09 12:00 | 9154.66 | 3.0561 | 63.1936 | 48.4627 | 2682.966
2036-12-10 13:00 | 9795.7 | 3.2493 | 63.5153 | 48.4627 | 2870.8363
2036-12-11 14:00 | 8814.49 | 2.8557 | 63.9763 | 48.4627 | 2583.272
2036-12-12 15:00 | 9728.46 | 3.1683 | 63.9659 | 48.4627 | 2851.1302
2036-12-13 16:00 | 9572.73 | 3.1174 | 64.104 | 48.4627 | 2805.4902
2036-12-14 17:00 | 9357.99 | 2.9703 | 64.448 | 48.4627 | 2742.5561
2036-12-15 18:00 | 8439.5 | 2.5712 | 64.9313 | 48.4627 | 2473.3733
2036-12-16 19:00 | 7718.82 | 2.3716 | 64.8002 | 48.4627 | 2262.1628
2036-12-17 20:00 | 6071.73 | 1.7629 | 65.4073 | 48.4627 | 1779.4484
2036-12-18 21:00 | 5334.57 | 1.6218 | 64.7207 | 48.4627 | 1563.4081
2036-12-19 22:00 | 3298.74 | 1.0397 | 64.1873 | 48.4627 | 966.7653
2036-12-20 23:00 | 3192.12 | 1 | 67.128 | 48.4627 | 935.518
2036-12-22 | 3290.02 | 1 | 69.6462 | 48.4627 | 964.2097
2036-12-23 01:00 | 3318.2 | 1 | 51.75 | 48.4627 | 972.4684
2036-12-24 02:00 | 3063.72 | 1 | 51.7681 | 48.4627 | 897.8877
2036-12-25 03:00 | 3058 | 1 | 51.672 | 48.4627 | 896.2113
2036-12-26 04:00 | 3245.47 | 1 | 69.5211 | 48.4627 | 951.1534
2036-12-27 05:00 | 3468.08 | 1.0944 | 63.3246 | 48.4627 | 1016.3939
2036-12-28 06:00 | 4006.07 | 1.2066 | 63.8382 | 48.4627 | 1174.0632
2036-12-29 07:00 | 5110.76 | 1.5708 | 63.6411 | 48.4627 | 1497.8159
2036-12-30 08:00 | 4417.39 | 1.3355 | 63.9499 | 48.4627 | 1294.6092
2036-12-31 09:00 | 4650.08 | 1.4123 | 63.8907 | 48.4627 | 1362.8039
2037-01-01 10:00 | 7294.23 | 2.4108 | 63.0032 | 48.4627 | 2137.7278
2037-01-02 11:00 | 9512.34 | 3.3692 | 62.5816 | 48.4627 | 2787.7917
2037-01-03 12:00 | 11180.3 | 3.6823 | 63.6499 | 48.4627 | 3276.6225
2037-01-04 13:00 | 11228.1 | 3.6287 | 64.1794 | 48.4627 | 3290.6313
2037-01-05 14:00 | 10487.8 | 3.4942 | 64.1009 | 48.4627 | 3073.6708
2037-01-06 15:00 | 11202.8 | 3.8931 | 63.7899 | 48.4627 | 3283.2166
2037-01-07 16:00 | 10900.3 | 3.5972 | 64.4677 | 48.4627 | 3194.5626
2037-01-08 17:00 | 9844.02 | 3.2309 | 64.611 | 48.4627 | 2884.9975
2037-01-09 18:00 | 8241.46 | 2.5658 | 65.1298 | 48.4627 | 2415.3335
2037-01-10 19:00 | 7215.84 | 2.2386 | 65.0189 | 48.4627 | 2114.7539
2037-01-11 20:00 | 5386.06 | 1.613 | 65.2859 | 48.4627 | 1578.4984
2037-01-12 21:00 | 4343.77 | 1.3058 | 65.0129 | 48.4627 | 1273.0333
2037-01-13 22:00 | 2749.48 | 1 | 52.5992 | 48.4627 | 805.793
2037-01-14 23:00 | -168.516 | 1.2073 | 52.7685 | 48.4627 | -49.3872
2037-01-16 | -585.332 | 2.4116 | 51.934 | 48.4627 | -171.5439
2037-01-17 01:00 | -1230.68 | 4.3665 | 51.4507 | 48.4627 | -360.6767
2037-01-18 02:00 | -1622.23 | 5.4452 | 51.1122 | 48.4627 | -475.4287
2037-01-19 03:00 | -1802.2 | 5.9368 | 50.8184 | 48.4627 | -528.1727
2037-01-20 04:00 | -1797.79 | 5.8883 | 50.5796 | 48.4627 | -526.8802
2037-01-21 05:00 | -1498.08 | 4.9245 | 50.4225 | 48.4627 | -439.0439
2037-01-22 06:00 | -1574.64 | 5.2888 | 50.3327 | 48.4627 | -461.4814
2037-01-23 07:00 | -1658.93 | 5.5352 | 50.2064 | 48.4627 | -486.1844
2037-01-24 08:00 | -2086.31 | 6.6648 | 50.0522 | 48.4627 | -611.4371
2037-01-25 09:00 | -1167.04 | 3.7863 | 49.9256 | 48.4627 | -342.0257
2037-01-26 10:00 | 0 | 1 | 50.937 | 48.4627 | 0
2037-01-27 11:00 | 2810.64 | 1 | 50.0311 | 48.4627 | 823.7173
2037-01-28 12:00 | 2889.77 | 1 | 62.4087 | 48.4627 | 846.908
2037-01-29 13:00 | 2947.65 | 1.0267 | 61.0738 | 48.4627 | 863.8709
2037-01-30 14:00 | 3754.13 | 1.2842 | 61.3247 | 48.4627 | 1100.2269
2037-01-31 15:00 | 4400.27 | 1.5002 | 61.4838 | 48.4627 | 1289.5918
2037-02-01 16:00 | 4202.26 | 1.4451 | 61.5353 | 48.4627 | 1231.5608
2037-02-02 17:00 | 3326.64 | 1.1497 | 61.5176 | 48.4627 | 974.9419
2037-02-03 18:00 | 2849.45 | 1 | 50.7073 | 48.4627 | 835.0914
2037-02-04 19:00 | 2740.67 | 1 | 50.698 | 48.4627 | 803.2111
2037-02-05 20:00 | -767.177 | 3.1723 | 50.7975 | 48.4627 | -224.8374
2037-02-06 21:00 | -1401.57 | 4.9158 | 50.2977 | 48.4627 | -410.7596
2037-02-07 22:00 | -2467.34 | 6.6648 | 49.7457 | 48.4627 | -723.106
2037-02-08 23:00 | -3372.03 | 6.6648 | 49.0349 | 48.4627 | -988.2444
2037-02-10 | -3676.9 | 6.6648 | 48.6082 | 48.4627 | -1077.593
2037-02-11 01:00 | -4008.69 | 6.6648 | 48.2056 | 48.4627 | -1174.8311
2037-02-12 02:00 | -4412.67 | 6.6648 | 47.8212 | 48.4627 | -1293.2259
2037-02-13 03:00 | -4564.61 | 6.6648 | 47.5532 | 48.4627 | -1337.7551
2037-02-14 04:00 | -4984.67 | 6.6648 | 47.1764 | 48.4627 | -1460.8626
2037-02-15 05:00 | -4940.89 | 6.6648 | 47.0299 | 48.4627 | -1448.0319
2037-02-16 06:00 | -3795.58 | 6.6648 | 47.4767 | 48.4627 | -1112.3747
2037-02-17 07:00 | -2404.14 | 6.6648 | 48.1729 | 48.4627 | -704.5839
2037-02-18 08:00 | -1748.19 | 5.838 | 48.4943 | 48.4627 | -512.3439
2037-02-19 09:00 | -470.021 | 1.6263 | 48.6199 | 48.4627 | -137.7496
2037-02-20 10:00 | 2617.57 | 1 | 48.8646 | 48.4627 | 767.134
2037-02-21 11:00 | 2820.77 | 1 | 59.7417 | 48.4627 | 826.6861
2037-02-22 12:00 | 3626.62 | 1.3031 | 59.7696 | 48.4627 | 1062.8574
2037-02-23 13:00 | 4035.01 | 1.4468 | 59.9837 | 48.4627 | 1182.5447
2037-02-24 14:00 | 4702.85 | 1.6835 | 60.1843 | 48.4627 | 1378.2693
2037-02-25 15:00 | 4510.69 | 1.6156 | 60.3697 | 48.4627 | 1321.9527
2037-02-26 16:00 | 6073.48 | 2.1426 | 60.6005 | 48.4627 | 1779.9613
2037-02-27 17:00 | 4167.02 | 1.4723 | 60.8252 | 48.4627 | 1221.233
2037-02-28 18:00 | 2947.15 | 1 | 63.1927 | 48.4627 | 863.7244
2037-03-01 19:00 | 2998.37 | 1 | 50.092 | 48.4627 | 878.7355
2037-03-02 20:00 | 0 | 0 | 51.1139 | 48.4627 | 0
2037-03-03 21:00 | -435.227 | 1.8222 | 50.0302 | 48.4627 | -127.5524
2037-03-04 22:00 | -865.644 | 3.3369 | 49.7261 | 48.4627 | -253.6952
2037-03-05 23:00 | -2477.79 | 6.6648 | 49.2009 | 48.4627 | -726.1686
2037-03-07 | -3234.66 | 6.6648 | 48.556 | 48.4627 | -947.9853
2037-03-08 01:00 | -3333.46 | 6.6648 | 48.246 | 48.4627 | -976.9407
2037-03-09 02:00 | -3658.44 | 6.6648 | 47.928 | 48.4627 | -1072.1829
2037-03-10 03:00 | -3928.79 | 6.6648 | 47.6384 | 48.4627 | -1151.4147
2037-03-11 04:00 | -3818.64 | 6.6648 | 47.5275 | 48.4627 | -1119.1329
2037-03-12 05:00 | -3837.9 | 6.6648 | 47.4216 | 48.4627 | -1124.7775
2037-03-13 06:00 | -2773.7 | 6.6648 | 47.8836 | 48.4627 | -812.8912
2037-03-14 07:00 | -1469.39 | 4.921 | 48.2987 | 48.4627 | -430.6357
2037-03-15 08:00 | -808.501 | 2.8609 | 48.4812 | 48.4627 | -236.9483
2037-03-16 09:00 | 89.8705 | 1 | 49.5225 | 48.4627 | 26.3384
2037-03-17 10:00 | 2844.04 | 1 | 48.7068 | 48.4627 | 833.5058
2037-03-18 11:00 | 3839.78 | 1.2794 | 60.2029 | 48.4627 | 1125.3284
2037-03-19 12:00 | 5100.88 | 1.6588 | 60.7091 | 48.4627 | 1494.9204
2037-03-20 13:00 | 5482.78 | 1.8373 | 60.6849 | 48.4627 | 1606.8442
2037-03-21 14:00 | 5421.85 | 1.7637 | 61.2235 | 48.4627 | 1588.9874
2037-03-22 15:00 | 5024.68 | 1.6427 | 61.3388 | 48.4627 | 1472.5883
2037-03-23 16:00 | 6971.63 | 2.3068 | 61.2816 | 48.4627 | 2043.1831
2037-03-24 17:00 | 5266.41 | 1.7381 | 61.5825 | 48.4627 | 1543.4324
2037-03-25 18:00 | 3603.05 | 1.1604 | 61.8541 | 48.4627 | 1055.9497
2037-03-26 19:00 | 3084.69 | 1 | 67.9231 | 48.4627 | 904.0334
2037-03-27 20:00 | 2995.53 | 1 | 50.1247 | 48.4627 | 877.9032
2037-03-28 21:00 | 2607.22 | 1 | 50.2572 | 48.4627 | 764.1008
2037-03-29 22:00 | -58.8784 | 0.89522 | 50.8495 | 48.4627 | -17.2556
2037-03-30 23:00 | -1274.21 | 4.7463 | 49.8747 | 48.4627 | -373.4341
2037-04-01 | -1921.91 | 6.5294 | 49.519 | 48.4627 | -563.2562
2037-04-02 01:00 | -2253.05 | 6.6648 | 49.1606 | 48.4627 | -660.3038
2037-04-03 02:00 | -2419.41 | 6.6648 | 48.8938 | 48.4627 | -709.0591
2037-04-04 03:00 | -2568.71 | 6.6648 | 48.6601 | 48.4627 | -752.8146
2037-04-05 04:00 | -2450.59 | 6.6648 | 48.5904 | 48.4627 | -718.197
2037-04-06 05:00 | -2100.83 | 6.6648 | 48.6936 | 48.4627 | -615.6925
2037-04-07 06:00 | -1755.52 | 5.8302 | 48.7155 | 48.4627 | -514.4921
2037-04-08 07:00 | -1040.26 | 3.5209 | 48.7232 | 48.4627 | -304.8701
2037-04-09 08:00 | -207.857 | 1.0141 | 49.0661 | 48.4627 | -60.9169
2037-04-10 09:00 | 2662.74 | 1.0715 | 58.2707 | 48.4627 | 780.3721
2037-04-11 10:00 | 5295.57 | 1.819 | 59.99 | 48.4627 | 1551.9784
2037-04-12 11:00 | 6325.72 | 2.1338 | 60.586 | 48.4627 | 1853.8855
2037-04-13 12:00 | 4869.42 | 1.5813 | 61.3111 | 48.4627 | 1427.0861
2037-04-14 13:00 | 5635.91 | 1.8544 | 61.2475 | 48.4627 | 1651.7222
2037-04-15 14:00 | 6440.05 | 2.0821 | 61.5987 | 48.4627 | 1887.3923
2037-04-16 15:00 | 6813.56 | 2.2491 | 61.5923 | 48.4627 | 1996.8573
2037-04-17 16:00 | 6607.26 | 2.1506 | 61.8763 | 48.4627 | 1936.3968
2037-04-18 17:00 | 6099.65 | 1.9388 | 62.2031 | 48.4627 | 1787.631
2037-04-19 18:00 | 4024.95 | 1.2954 | 62.1338 | 48.4627 | 1179.5964
2037-04-20 19:00 | 3108.06 | 1 | 63.4208 | 48.4627 | 910.8825
2037-04-21 20:00 | 2982 | 1 | 50.3432 | 48.4627 | 873.9379
2037-04-22 21:00 | -75.772 | 0.93773 | 51.01 | 48.4627 | -22.2066
2037-04-23 22:00 | -984.969 | 3.7908 | 50.044 | 48.4627 | -288.6659
2037-04-24 23:00 | -1276.23 | 4.4807 | 49.6506 | 48.4627 | -374.0261
2037-04-26 | -1707.52 | 5.8492 | 49.4525 | 48.4627 | -500.4247
2037-04-27 01:00 | -1904.87 | 6.3723 | 49.2575 | 48.4627 | -558.2623
2037-04-28 02:00 | -2070.37 | 6.6648 | 49.0508 | 48.4627 | -606.7656
2037-04-29 03:00 | -2018.25 | 6.6648 | 48.9609 | 48.4627 | -591.4907
2037-04-30 04:00 | -1978.69 | 6.564 | 48.8817 | 48.4627 | -579.8968
2037-05-01 05:00 | -1672.71 | 5.5507 | 48.8105 | 48.4627 | -490.2229
2037-05-02 06:00 | -1276.89 | 4.3386 | 48.8087 | 48.4627 | -374.2195
2037-05-03 07:00 | -527.021 | 1.9775 | 48.9066 | 48.4627 | -154.4546
2037-05-04 08:00 | 605.142 | 1 | 49.6582 | 48.4627 | 177.3496
2037-05-05 09:00 | 2501.18 | 1 | 58.5105 | 48.4627 | 733.0235
2037-05-06 10:00 | 4554.33 | 1.4896 | 60.5767 | 48.4627 | 1334.7424
2037-05-07 11:00 | 5808.66 | 1.9446 | 60.6547 | 48.4627 | 1702.3502
2037-05-08 12:00 | 6932.03 | 2.3161 | 60.9887 | 48.4627 | 2031.5774
2037-05-09 13:00 | 7327.47 | 2.4086 | 61.4633 | 48.4627 | 2147.4695
2037-05-10 14:00 | 7973.87 | 2.5976 | 61.8045 | 48.4627 | 2336.9106
2037-05-11 15:00 | 8336.08 | 2.7311 | 61.9813 | 48.4627 | 2443.0639
2037-05-12 16:00 | 7635.63 | 2.4706 | 62.3101 | 48.4627 | 2237.7823
2037-05-13 17:00 | 6886.55 | 2.1687 | 62.6811 | 48.4627 | 2018.2486
2037-05-14 18:00 | 5082.35 | 1.6058 | 62.6704 | 48.4627 | 1489.4898
2037-05-15 19:00 | 3445.68 | 1.126 | 62.206 | 48.4627 | 1009.8291
2037-05-16 20:00 | 3079.8 | 1 | 50.6118 | 48.4627 | 902.6003
2037-05-17 21:00 | 2162.05 | 1 | 50.8031 | 48.4627 | 633.6343
2037-05-18 22:00 | -547.637 | 2.4661 | 50.6328 | 48.4627 | -160.4966
2037-05-19 23:00 | -908.472 | 3.3917 | 50.1107 | 48.4627 | -266.2469
2037-05-21 | -1164.8 | 4.1464 | 49.8208 | 48.4627 | -341.3692
2037-05-22 01:00 | -1276.41 | 4.4425 | 49.6352 | 48.4627 | -374.0788
2037-05-23 02:00 | -1387.59 | 4.7882 | 49.4734 | 48.4627 | -406.6625
2037-05-24 03:00 | -1171.7 | 4.043 | 49.3321 | 48.4627 | -343.3914
2037-05-25 04:00 | -901.995 | 3.2353 | 49.306 | 48.4627 | -264.3486
2037-05-26 05:00 | -501.905 | 2.0057 | 49.3693 | 48.4627 | -147.0938
2037-05-27 06:01 | -174.261 | 1.0649 | 49.6679 | 48.4627 | -51.0709
2037-05-28 07:01 | 2166.07 | 1 | 49.5061 | 48.4627 | 634.8125
2037-05-29 08:01 | 2957.23 | 1 | 49.4615 | 48.4627 | 866.6786
2037-05-30 09:01 | 3616.95 | 1.1644 | 61.1936 | 48.4627 | 1060.0234
2037-05-31 10:01 | 6500.09 | 2.1612 | 60.9816 | 48.4627 | 1904.9883
2037-06-01 11:01 | 7969.19 | 2.6346 | 61.4221 | 48.4627 | 2335.539
2037-06-02 12:01 | 8479.18 | 2.7682 | 61.9379 | 48.4627 | 2485.0024
2037-06-03 13:01 | 7930.29 | 2.571 | 62.2772 | 48.4627 | 2324.1386
2037-06-04 14:01 | 8355.56 | 2.7196 | 62.3737 | 48.4627 | 2448.7729
2037-06-05 15:01 | 8890.74 | 2.8609 | 62.6667 | 48.4627 | 2605.6187
2037-06-06 16:01 | 8344.92 | 2.6056 | 63.1638 | 48.4627 | 2445.6546
2037-06-07 17:01 | 8105.8 | 2.5615 | 63.1039 | 48.4627 | 2375.5755
2037-06-08 18:01 | 6053.57 | 1.8629 | 63.4535 | 48.4627 | 1774.1262
2037-06-09 19:01 | 4819.55 | 1.4702 | 63.4326 | 48.4627 | 1412.4707
2037-06-10 20:01 | 3175.88 | 1 | 67.4765 | 48.4627 | 930.7585
2037-06-11 21:01 | 3043.33 | 1 | 50.9354 | 48.4627 | 891.912
2037-06-12 22:01 | -180.532 | 1.2494 | 51.3572 | 48.4627 | -52.9087
2037-06-13 23:01 | -614.377 | 2.5429 | 50.6192 | 48.4627 | -180.0561
2037-06-15 00:01 | -820.768 | 3.092 | 50.2531 | 48.4627 | -240.5434
2037-06-16 01:01 | -853.725 | 3.1486 | 50.0509 | 48.4627 | -250.2021
2037-06-17 02:01 | -890.214 | 3.2681 | 49.904 | 48.4627 | -260.896
2037-06-18 03:01 | -852.966 | 3.1394 | 49.7636 | 48.4627 | -249.9797
2037-06-19 04:01 | -779.601 | 2.9159 | 49.6971 | 48.4627 | -228.4785
2037-06-20 05:01 | -545.551 | 2.1751 | 49.6852 | 48.4627 | -159.8852
2037-06-21 06:01 | -256.704 | 1.312 | 49.8397 | 48.4627 | -75.2325
2037-06-22 07:01 | 1929.57 | 1 | 49.8272 | 48.4627 | 565.5011
2037-06-23 08:01 | 2716.14 | 1 | 62.3459 | 48.4627 | 796.0221
2037-06-24 09:01 | 4985.07 | 1.764 | 60.3792 | 48.4627 | 1460.9798
2037-06-25 10:01 | 7347.75 | 2.4764 | 61.1571 | 48.4627 | 2153.413
2037-06-26 11:01 | 8690.18 | 3.0501 | 61.1629 | 48.4627 | 2546.8404
2037-06-27 12:01 | 9599.32 | 3.2444 | 61.9105 | 48.4627 | 2813.283
2037-06-28 13:01 | 9738.54 | 3.2306 | 62.4172 | 48.4627 | 2854.0843
2037-06-29 14:01 | 9763.04 | 3.2497 | 62.6306 | 48.4627 | 2861.2646
2037-06-30 15:01 | 10251.1 | 3.3887 | 62.8817 | 48.4627 | 3004.3008
2037-07-01 16:01 | 9689.6 | 3.1772 | 63.153 | 48.4627 | 2839.7414
2037-07-02 17:01 | 8189.13 | 2.7092 | 63.157 | 48.4627 | 2399.9971
2037-07-03 18:01 | 6288.13 | 2.0038 | 63.5056 | 48.4627 | 1842.869
2037-07-04 19:01 | 4901.45 | 1.5569 | 63.3753 | 48.4627 | 1436.4732
2037-07-05 20:01 | 3027.73 | 1 | 67.2296 | 48.4627 | 887.3401
2037-07-06 21:01 | 3064.72 | 1 | 51.2135 | 48.4627 | 898.1808
2037-07-07 22:01 | -123.78 | 1.065 | 51.7125 | 48.4627 | -36.2763
2037-07-08 23:01 | -611.899 | 2.5427 | 50.8797 | 48.4627 | -179.3299
2037-07-10 00:01 | -890.321 | 3.3077 | 50.4786 | 48.4627 | -260.9273
2037-07-11 01:01 | -1191.3 | 4.2184 | 50.2231 | 48.4627 | -349.1356
2037-07-12 02:01 | -1407.11 | 4.8402 | 50.009 | 48.4627 | -412.3832
2037-07-13 03:01 | -1649.68 | 5.5877 | 49.8008 | 48.4627 | -483.4735
2037-07-14 04:01 | -1723.59 | 5.7622 | 49.6424 | 48.4627 | -505.1344
2037-07-15 05:01 | -1550.82 | 5.1784 | 49.5211 | 48.4627 | -454.5005
2037-07-16 06:01 | -1458.15 | 4.9409 | 49.4589 | 48.4627 | -427.3416
2037-07-17 07:01 | -861.279 | 2.9961 | 49.412 | 48.4627 | -252.416
2037-07-18 08:01 | -415.744 | 1.7451 | 49.5697 | 48.4627 | -121.8425
2037-07-19 09:01 | 2013.04 | 1 | 49.6884 | 48.4627 | 589.9638
2037-07-20 10:01 | 3071.75 | 1 | 49.5361 | 48.4627 | 900.2411
2037-07-21 11:01 | 4548.17 | 1.4808 | 61.1932 | 48.4627 | 1332.937
2037-07-22 12:01 | 5656.66 | 1.8612 | 61.2797 | 48.4627 | 1657.8034
2037-07-23 13:01 | 6620.23 | 2.2036 | 61.4058 | 48.4627 | 1940.1979
2037-07-24 14:01 | 7142.09 | 2.3389 | 61.8233 | 48.4627 | 2093.14
2037-07-25 15:01 | 8316.12 | 2.7685 | 61.8468 | 48.4627 | 2437.2142
2037-07-26 16:01 | 7886.32 | 2.606 | 62.1743 | 48.4627 | 2311.2522
2037-07-27 17:01 | 6718.32 | 2.2071 | 62.3667 | 48.4627 | 1968.9452
2037-07-28 18:01 | 4491.8 | 1.4411 | 62.6184 | 48.4627 | 1316.4166
2037-07-29 19:01 | 3032.54 | 1 | 63.8301 | 48.4627 | 888.7497
2037-07-30 20:01 | 2894.11 | 1 | 50.7349 | 48.4627 | 848.1799
2037-07-31 21:01 | -260.322 | 1.5334 | 51.0291 | 48.4627 | -76.2928
2037-08-01 22:01 | -1348.56 | 4.9086 | 50.3028 | 48.4627 | -395.2239
2037-08-02 23:01 | -2126.08 | 6.6648 | 49.8186 | 48.4627 | -623.0925
2037-08-04 00:01 | -2546.84 | 6.6648 | 49.3455 | 48.4627 | -746.4051
2037-08-05 01:01 | -2908.82 | 6.6648 | 48.9372 | 48.4627 | -852.491
2037-08-06 02:01 | -3096.52 | 6.6648 | 48.6183 | 48.4627 | -907.5004
2037-08-07 03:01 | -3156.02 | 6.6648 | 48.4141 | 48.4627 | -924.9382
2037-08-08 04:01 | -3254.26 | 6.6648 | 48.2221 | 48.4627 | -953.7295
2037-08-09 05:01 | -3250.67 | 6.6648 | 48.0997 | 48.4627 | -952.6773
2037-08-10 06:01 | -2041.68 | 6.6648 | 48.6195 | 48.4627 | -598.3573
2037-08-11 07:01 | -1617.36 | 5.3657 | 48.6709 | 48.4627 | -474.0014
2037-08-12 08:01 | -2085.37 | 6.6648 | 48.6599 | 48.4627 | -611.1616
2037-08-13 09:01 | -2132.65 | 6.6648 | 48.5797 | 48.4627 | -625.018
2037-08-14 10:01 | -1890.93 | 6.3008 | 48.5932 | 48.4627 | -554.1769
2037-08-15 11:01 | -1430.6 | 4.7844 | 48.5739 | 48.4627 | -419.2675
2037-08-16 12:01 | 191.546 | 1 | 49.5125 | 48.4627 | 56.1366
2037-08-17 13:01 | 2338.02 | 1.0168 | 57.4945 | 48.4627 | 685.206
2037-08-18 14:01 | 3809.85 | 1.3434 | 59.5401 | 48.4627 | 1116.5568
2037-08-19 15:01 | 4131.02 | 1.3449 | 60.5959 | 48.4627 | 1210.6825
2037-08-20 16:01 | 6202.88 | 2.0282 | 60.7289 | 48.4627 | 1817.8847
2037-08-21 17:01 | 5349.39 | 1.7193 | 61.2484 | 48.4627 | 1567.7515
2037-08-22 18:01 | 4122.91 | 1.3129 | 61.4904 | 48.4627 | 1208.3056
2037-08-23 19:01 | 3095.51 | 1.0103 | 61.2132 | 48.4627 | 907.2044
2037-08-24 20:01 | 3073.51 | 1 | 63.8348 | 48.4627 | 900.7569
2037-08-25 21:01 | 3080.26 | 1 | 66.827 | 48.4627 | 902.7351
2037-08-26 22:01 | 3124.38 | 1 | 49.7563 | 48.4627 | 915.6654
2037-08-27 23:01 | 0 | 0 | 50.8737 | 48.4627 | 0
2037-08-29 00:01 | -194.356 | 1.1456 | 50.0419 | 48.4627 | -56.9601
2037-08-30 01:01 | -297.431 | 1.5531 | 49.8205 | 48.4627 | -87.1684
2037-08-31 02:01 | -326.552 | 1.6081 | 49.6984 | 48.4627 | -95.7029
2037-09-01 03:01 | -307.159 | 1.5405 | 49.6321 | 48.4627 | -90.0194
2037-09-02 04:01 | -484.793 | 2.1309 | 49.4467 | 48.4627 | -142.0788
2037-09-03 05:01 | -568.066 | 2.3444 | 49.3458 | 48.4627 | -166.4837
2037-09-04 06:01 | 529.443 | 1 | 49.9419 | 48.4627 | 155.1644
2037-09-05 07:01 | 2796.92 | 1 | 49.24 | 48.4627 | 819.6963
2037-09-06 08:01 | 2935.61 | 1 | 66.1462 | 48.4627 | 860.3424
2037-09-07 09:01 | 3905.7 | 1.385 | 60.1086 | 48.4627 | 1144.6477
2037-09-08 10:01 | 5321.04 | 1.8565 | 60.4429 | 48.4627 | 1559.4429
2037-09-09 11:01 | 6102.39 | 2.1 | 60.8578 | 48.4627 | 1788.434
2037-09-10 12:01 | 5629.32 | 1.8991 | 61.3062 | 48.4627 | 1649.7908
2037-09-11 13:01 | 5779.67 | 1.9309 | 61.4958 | 48.4627 | 1693.8541
2037-09-12 14:01 | 5537.25 | 1.8498 | 61.5933 | 48.4627 | 1622.8078
2037-09-13 15:01 | 3809.95 | 1.2676 | 61.6954 | 48.4627 | 1116.5861
2037-09-14 16:01 | 5923.6 | 1.9831 | 61.4955 | 48.4627 | 1736.0358
2037-09-15 17:01 | 3728.01 | 1.25 | 61.6273 | 48.4627 | 1092.5719
2037-09-16 18:01 | 2911.47 | 1 | 50.446 | 48.4627 | 853.2676
2037-09-17 19:01 | 2901.27 | 1 | 50.2972 | 48.4627 | 850.2783
2037-09-18 20:01 | -35.5039 | 0.80812 | 51.0761 | 48.4627 | -10.4052
2037-09-19 21:01 | -503.35 | 2.2411 | 50.1607 | 48.4627 | -147.5173
2037-09-20 22:01 | -1067.2 | 3.9542 | 49.7387 | 48.4627 | -312.7654
2037-09-21 23:01 | -2150.93 | 6.6648 | 49.3737 | 48.4627 | -630.3754
2037-09-23 00:01 | -2587.18 | 6.6648 | 48.9127 | 48.4627 | -758.2276
2037-09-24 01:01 | -3050.52 | 6.6648 | 48.4532 | 48.4627 | -894.0192
2037-09-25 02:01 | -3314.81 | 6.6648 | 48.1445 | 48.4627 | -971.4749
2037-09-26 03:01 | -3446.17 | 6.6648 | 47.929 | 48.4627 | -1009.9727
2037-09-27 04:01 | -3432.36 | 6.6648 | 47.7894 | 48.4627 | -1005.9254
2037-09-28 05:01 | -3015.37 | 6.6648 | 47.9037 | 48.4627 | -883.7177
2037-09-29 06:01 | -2532.52 | 6.6648 | 48.1006 | 48.4627 | -742.2083
2037-09-30 07:01 | -1495.63 | 4.9977 | 48.3485 | 48.4627 | -438.3259
2037-10-01 08:01 | -789.446 | 2.7888 | 48.4762 | 48.4627 | -231.3638
2037-10-02 09:01 | 2431.31 | 1 | 48.6939 | 48.4627 | 712.5466
2037-10-03 10:01 | 3061.16 | 1 | 61.6734 | 48.4627 | 897.1374
2037-10-04 11:01 | 5105.86 | 1.7095 | 60.2079 | 48.4627 | 1496.3799
2037-10-05 12:01 | 5791.27 | 1.9194 | 60.6512 | 48.4627 | 1697.2537
2037-10-06 13:01 | 4775.2 | 1.5854 | 60.9225 | 48.4627 | 1399.473
2037-10-07 14:01 | 6030.04 | 2.0197 | 60.9302 | 48.4627 | 1767.2303
2037-10-08 15:01 | 6824.11 | 2.305 | 61.0451 | 48.4627 | 1999.9492
2037-10-09 16:01 | 5830.19 | 1.9138 | 61.5648 | 48.4627 | 1708.66
2037-10-10 17:01 | 4782.76 | 1.5701 | 61.6094 | 48.4627 | 1401.6886
2037-10-11 18:01 | 3170.85 | 1.0404 | 61.5756 | 48.4627 | 929.2844
2037-10-12 19:01 | 3011.74 | 1 | 66.7486 | 48.4627 | 882.6539
2037-10-13 20:01 | 2738.25 | 1 | 50.1556 | 48.4627 | 802.5019
2037-10-14 21:01 | -171.156 | 1.2608 | 50.5638 | 48.4627 | -50.1609
2037-10-15 22:01 | -1085.26 | 4.1046 | 49.8032 | 48.4627 | -318.0583
2037-10-16 23:01 | -1387.92 | 4.8291 | 49.4492 | 48.4627 | -406.7592
2037-10-18 00:01 | -1717.33 | 5.8598 | 49.2572 | 48.4627 | -503.2997
2037-10-19 01:01 | -1904.54 | 6.3865 | 49.0828 | 48.4627 | -558.1656
2037-10-20 02:01 | -2166.4 | 6.6648 | 48.8331 | 48.4627 | -634.9092
2037-10-21 03:01 | -2008.77 | 6.6648 | 48.7862 | 48.4627 | -588.7124
2037-10-22 04:01 | -1981.17 | 6.5886 | 48.7155 | 48.4627 | -580.6236
2037-10-23 05:01 | -1693.86 | 5.632 | 48.656 | 48.4627 | -496.4214
2037-10-24 06:01 | -1585.7 | 5.3771 | 48.6535 | 48.4627 | -464.7228
2037-10-25 07:01 | -1026.88 | 3.5321 | 48.6363 | 48.4627 | -300.9488
2037-10-26 08:01 | -506.51 | 2.0033 | 48.7793 | 48.4627 | -148.4434
2037-10-27 09:01 | 2441.32 | 1 | 48.8457 | 48.4627 | 715.4803
2037-10-28 10:01 | 3863.05 | 1.2422 | 60.5208 | 48.4627 | 1132.1482
2037-10-29 11:01 | 4994.56 | 1.6157 | 60.7054 | 48.4627 | 1463.761
2037-10-30 12:01 | 4199.6 | 1.3542 | 61.0043 | 48.4627 | 1230.7813
2037-10-31 13:01 | 3023.78 | 1 | 63.2647 | 48.4627 | 886.1824
2037-11-01 14:01 | 3119.96 | 1 | 64.8876 | 48.4627 | 914.37
2037-11-02 15:01 | 3237 | 1.0457 | 61.0577 | 48.4627 | 948.6711
2037-11-03 16:01 | 3157.05 | 1.0075 | 61.2118 | 48.4627 | 925.24
2037-11-04 17:01 | 3074.56 | 1 | 63.7444 | 48.4627 | 901.0646
2037-11-05 18:01 | 3106.91 | 1 | 49.5509 | 48.4627 | 910.5454
2037-11-06 19:01 | 2762.99 | 1 | 49.7091 | 48.4627 | 809.7524
2037-11-07 20:01 | -653.848 | 2.8454 | 49.8777 | 48.4627 | -191.6239
2037-11-08 21:01 | -1032.38 | 3.7928 | 49.4089 | 48.4627 | -302.5607
2037-11-09 22:01 | -1876.39 | 6.5196 | 49.1385 | 48.4627 | -549.9156
2037-11-10 23:01 | -2148.76 | 6.6648 | 48.817 | 48.4627 | -629.7394
2037-11-12 00:01 | -2403.71 | 6.6648 | 48.5087 | 48.4627 | -704.4579
2037-11-13 01:01 | -2584.91 | 6.6648 | 48.2623 | 48.4627 | -757.5623
2037-11-14 02:01 | -2566.03 | 6.6648 | 48.1745 | 48.4627 | -752.0292
2037-11-15 03:01 | -2260.91 | 6.6648 | 48.2526 | 48.4627 | -662.6073
2037-11-16 04:01 | -2021.87 | 6.6648 | 48.3451 | 48.4627 | -592.5516
2037-11-17 05:01 | -1500.39 | 4.996 | 48.339 | 48.4627 | -439.7209
2037-11-18 06:01 | -1505.36 | 5.1989 | 48.3942 | 48.4627 | -441.1775
2037-11-19 07:01 | -1435.42 | 4.9405 | 48.3817 | 48.4627 | -420.6801
2037-11-20 08:01 | -2443.83 | 6.6648 | 48.1335 | 48.4627 | -716.2159
2037-11-21 09:01 | -2551.69 | 6.6648 | 47.9638 | 48.4627 | -747.8265
2037-11-22 10:01 | -2675.53 | 6.6648 | 47.8088 | 48.4627 | -784.1204
2037-11-23 11:01 | -2706.84 | 6.6648 | 47.7011 | 48.4627 | -793.2965
2037-11-24 12:01 | -2616.14 | 6.6648 | 47.6615 | 48.4627 | -766.7149
2037-11-25 13:01 | -2955.61 | 6.6648 | 47.4212 | 48.4627 | -866.2038
2037-11-26 14:01 | -2823.8 | 6.6648 | 47.3956 | 48.4627 | -827.5741
2037-11-27 15:01 | -1861.35 | 6.3128 | 47.7605 | 48.4627 | -545.5078
2037-11-28 16:01 | -1517.74 | 5.1359 | 47.7834 | 48.4627 | -444.8057
2037-11-29 17:01 | -1203.58 | 4.1999 | 47.8306 | 48.4627 | -352.7345
2037-11-30 18:01 | -1549.25 | 5.4813 | 47.8594 | 48.4627 | -454.0404
2037-12-01 19:01 | -1869.01 | 6.4328 | 47.8022 | 48.4627 | -547.7528
2037-12-02 20:01 | -2970.38 | 6.6648 | 47.2421 | 48.4627 | -870.5324
2037-12-03 21:01 | -3604.35 | 6.6648 | 46.792 | 48.4627 | -1056.3307
2037-12-04 22:01 | -4554.41 | 6.6648 | 46.174 | 48.4627 | -1334.7658
2037-12-05 23:01 | -4859.23 | 6.6648 | 45.845 | 48.4627 | -1424.0997
2037-12-07 00:01 | -5175.1 | 6.6648 | 45.5421 | 48.4627 | -1516.6721
2037-12-08 01:01 | -5313.17 | 6.6648 | 45.3439 | 48.4627 | -1557.1364
2037-12-09 02:01 | -5536.27 | 6.6648 | 45.1268 | 48.4627 | -1622.5206
2037-12-10 03:01 | -5694.25 | 6.6648 | 44.9353 | 48.4627 | -1668.8199
2037-12-11 04:01 | -5666.59 | 6.6648 | 44.847 | 48.4627 | -1660.7136
2037-12-12 05:01 | -5233.41 | 6.6648 | 44.9795 | 48.4627 | -1533.7611
2037-12-13 06:01 | -5058.76 | 6.6648 | 45.032 | 48.4627 | -1482.5762
2037-12-14 07:01 | -3761.35 | 6.6648 | 45.6544 | 48.4627 | -1102.3429
2037-12-15 08:01 | -3188.89 | 6.6648 | 46.032 | 48.4627 | -934.5714
2037-12-16 09:01 | -2299.55 | 6.6648 | 46.5695 | 48.4627 | -673.9316
2037-12-17 10:01 | -2242.76 | 6.6648 | 46.7161 | 48.4627 | -657.2881
2037-12-18 11:01 | -1905.72 | 6.5217 | 46.9299 | 48.4627 | -558.5114
2037-12-19 12:01 | -1877.44 | 6.4184 | 47.0022 | 48.4627 | -550.2233
2037-12-20 13:01 | -1853.63 | 6.3436 | 47.0479 | 48.4627 | -543.2453
2037-12-21 14:01 | -1541.51 | 5.2696 | 47.0754 | 48.4627 | -451.772
2037-12-22 15:01 | -926.31 | 3.277 | 47.1496 | 48.4627 | -271.4747
2037-12-23 16:01 | -521.177 | 2.1201 | 47.3585 | 48.4627 | -152.7419
2037-12-24 17:01 | -535.185 | 2.2941 | 47.4849 | 48.4627 | -156.8472
2037-12-25 18:01 | -1208.74 | 4.5643 | 47.4319 | 48.4627 | -354.2467
2037-12-26 19:01 | -1695.1 | 5.9847 | 47.3402 | 48.4627 | -496.7848
2037-12-27 20:01 | -3124.4 | 6.6648 | 46.6683 | 48.4627 | -915.6713
2037-12-28 21:01 | -3809.86 | 6.6648 | 46.1595 | 48.4627 | -1116.5597
2037-12-29 22:01 | -4962.52 | 6.6648 | 45.4173 | 48.4627 | -1454.371
2037-12-30 23:01 | -5570.05 | 6.6648 | 44.9032 | 48.4627 | -1632.4205
2038-01-01 00:01 | -5671.23 | 6.6648 | 44.6647 | 48.4627 | -1662.0734
2038-01-02 01:01 | -5563.3 | 6.6648 | 44.5855 | 48.4627 | -1630.4423
2038-01-03 02:01 | -5568.47 | 6.6648 | 44.5005 | 48.4627 | -1631.9575
2038-01-04 03:01 | -5697.47 | 6.6648 | 44.3562 | 48.4627 | -1669.7636
2038-01-05 04:01 | -5464.06 | 6.6648 | 44.3963 | 48.4627 | -1601.3579
2038-01-06 05:01 | -5204.24 | 6.6648 | 44.4847 | 48.4627 | -1525.2122
2038-01-07 06:01 | -5116.73 | 6.6648 | 44.5102 | 48.4627 | -1499.5655
2038-01-08 07:01 | -3931.43 | 6.6648 | 45.0812 | 48.4627 | -1152.1884
2038-01-09 08:01 | -3797.33 | 6.6648 | 45.2336 | 48.4627 | -1112.8876
2038-01-10 09:01 | -4023.71 | 6.6648 | 45.1639 | 48.4627 | -1179.233
2038-01-11 10:01 | -4173.06 | 6.6648 | 45.0796 | 48.4627 | -1223.0032
2038-01-12 11:01 | -4069.89 | 6.6648 | 45.1109 | 48.4627 | -1192.767
2038-01-13 12:01 | -3936.38 | 6.6648 | 45.177 | 48.4627 | -1153.6391
2038-01-14 13:01 | -4025.34 | 6.6648 | 45.1235 | 48.4627 | -1179.7107
2038-01-15 14:01 | -3824.4 | 6.6648 | 45.1959 | 48.4627 | -1120.821
2038-01-16 15:01 | -2772.55 | 6.6648 | 45.7203 | 48.4627 | -812.5542
2038-01-17 16:01 | -1956.93 | 6.6648 | 46.221 | 48.4627 | -573.5196
2038-01-18 17:01 | -2618.45 | 6.6648 | 45.9996 | 48.4627 | -767.3919
2038-01-19 18:01 | -3312.58 | 6.6648 | 45.6413 | 48.4627 | -970.8214
2038-01-20 19:01 | -3808.98 | 6.6648 | 45.318 | 48.4627 | -1116.3018
2038-01-21 20:01 | -4983.12 | 6.6648 | 44.6514 | 48.4627 | -1460.4083
2038-01-22 21:01 | -5261.66 | 6.6648 | 44.3546 | 48.4627 | -1542.0403
2038-01-23 22:01 | -6141.07 | 6.6648 | 43.7828 | 48.4627 | -1799.77
2038-01-24 23:01 | -6852.47 | 6.6648 | 43.2638 | 48.4627 | -2008.2607
2038-01-26 00:01 | -7022.07 | 6.6648 | 43.0058 | 48.4627 | -2057.9656
2038-01-27 01:01 | -7159 | 6.6648 | 42.8078 | 48.4627 | -2098.0958
2038-01-28 02:01 | -7349.11 | 6.6648 | 42.6122 | 48.4627 | -2153.8115
2038-01-29 03:01 | -7478.73 | 6.6648 | 42.4353 | 48.4627 | -2191.7994
2038-01-30 04:01 | -7617.81 | 6.6648 | 42.2586 | 48.4627 | -2232.5597
2038-01-31 05:01 | -7627.34 | 6.6648 | 42.159 | 48.4627 | -2235.3527
2038-02-01 06:01 | -6766.77 | 6.6648 | 42.5186 | 48.4627 | -1983.1445
2038-02-02 07:01 | -5788.71 | 6.6648 | 43.0244 | 48.4627 | -1696.5034
2038-02-03 08:01 | -6115.1 | 6.6648 | 42.9365 | 48.4627 | -1792.1589
2038-02-04 09:01 | -4754.47 | 6.6648 | 43.6137 | 48.4627 | -1393.3976
2038-02-05 10:01 | -3600.31 | 6.6648 | 44.3159 | 48.4627 | -1055.1467
2038-02-06 11:01 | -3055.37 | 6.6648 | 44.7752 | 48.4627 | -895.4406
2038-02-07 12:01 | -2587.72 | 6.6648 | 45.1541 | 48.4627 | -758.3859
2038-02-08 13:01 | -1701.86 | 5.9478 | 45.6223 | 48.4627 | -498.7659
2038-02-09 14:01 | -1309.58 | 4.6031 | 45.8086 | 48.4627 | -383.8
2038-02-10 15:01 | -1217.4 | 4.4278 | 45.9853 | 48.4627 | -356.7847
2038-02-11 16:01 | -253.822 | 1.0982 | 46.2268 | 48.4627 | -74.3879
2038-02-12 17:01 | -1063.33 | 4.2552 | 46.3341 | 48.4627 | -311.6313
2038-02-13 18:01 | -2335.03 | 6.6648 | 46.0348 | 48.4627 | -684.3297
2038-02-14 19:01 | -3196.95 | 6.6648 | 45.5035 | 48.4627 | -936.9336
2038-02-15 20:01 | -3754.74 | 6.6648 | 45.1223 | 48.4627 | -1100.4057
2038-02-16 21:01 | -4047.87 | 6.6648 | 44.88 | 48.4627 | -1186.3136
2038-02-17 22:01 | -4360.17 | 6.6648 | 44.6261 | 48.4627 | -1277.8397
2038-02-18 23:01 | -5803.04 | 6.6648 | 43.8058 | 48.4627 | -1700.7031
2038-02-20 00:01 | -6182.37 | 6.6648 | 43.4237 | 48.4627 | -1811.8738
2038-02-21 01:01 | -6292.42 | 6.6648 | 43.2166 | 48.4627 | -1844.1263
2038-02-22 02:01 | -6248.47 | 6.6648 | 43.1353 | 48.4627 | -1831.2458
2038-02-23 03:01 | -6445.39 | 6.6648 | 42.9541 | 48.4627 | -1888.9573
2038-02-24 04:01 | -6419.73 | 6.6648 | 42.8649 | 48.4627 | -1881.4371
2038-02-25 05:01 | -6439.44 | 6.6648 | 42.7912 | 48.4627 | -1887.2136
2038-02-26 06:01 | -5595.6 | 6.6648 | 43.1718 | 48.4627 | -1639.9085
2038-02-27 07:01 | -4971.99 | 6.6648 | 43.5251 | 48.4627 | -1457.1464
2038-02-28 08:01 | -4872.26 | 6.6648 | 43.6444 | 48.4627 | -1427.9185
2038-03-01 09:01 | -4026.09 | 6.6648 | 44.1077 | 48.4627 | -1179.9305
2038-03-02 10:01 | -2438.23 | 6.6648 | 45.0095 | 48.4627 | -714.5747
2038-03-03 11:01 | -1475.29 | 5.1458 | 45.4973 | 48.4627 | -432.3648
2038-03-04 12:01 | -1828.26 | 6.536 | 45.7363 | 48.4627 | -535.8101
2038-03-05 13:01 | -1872.37 | 6.5196 | 45.7993 | 48.4627 | -548.7375
2038-03-06 14:01 | -1898.06 | 6.6056 | 45.8683 | 48.4627 | -556.2665
2038-03-07 15:01 | -1844.56 | 6.4 | 45.9266 | 48.4627 | -540.5872
2038-03-08 16:01 | -866.845 | 2.9933 | 45.9558 | 48.4627 | -254.0472
2038-03-09 17:01 | -1145.23 | 4.3515 | 46.1654 | 48.4627 | -335.6338
2038-03-10 18:01 | -1604.36 | 5.7985 | 46.1781 | 48.4627 | -470.1915
2038-03-11 19:01 | -1939.62 | 6.6648 | 46.1314 | 48.4627 | -568.4465
2038-03-12 20:01 | -2338.58 | 6.6648 | 45.9291 | 48.4627 | -685.3701
2038-03-13 21:01 | -2474.63 | 6.6648 | 45.8417 | 48.4627 | -725.2425
2038-03-14 22:01 | -2735.96 | 6.6648 | 45.6772 | 48.4627 | -801.8307
2038-03-15 23:01 | -3978.39 | 6.6648 | 45.0095 | 48.4627 | -1165.951
2038-03-17 00:01 | -4257.21 | 6.6648 | 44.737 | 48.4627 | -1247.6651
2038-03-18 01:01 | -4328.49 | 6.6648 | 44.6072 | 48.4627 | -1268.5552
2038-03-19 02:01 | -4345.45 | 6.6648 | 44.5474 | 48.4627 | -1273.5257
2038-03-20 03:01 | -4208.64 | 6.6648 | 44.5771 | 48.4627 | -1233.4306
2038-03-21 04:01 | -4211.84 | 6.6648 | 44.5481 | 48.4627 | -1234.3685
2038-03-22 05:01 | -3853.98 | 6.6648 | 44.7196 | 48.4627 | -1129.49
2038-03-23 06:01 | -3803.61 | 6.6648 | 44.7683 | 48.4627 | -1114.7281
2038-03-24 07:01 | -3645.83 | 6.6648 | 44.8582 | 48.4627 | -1068.4873
2038-03-25 08:01 | -4175.64 | 6.6648 | 44.6057 | 48.4627 | -1223.7593
2038-03-26 09:01 | -3997.28 | 6.6648 | 44.6443 | 48.4627 | -1171.4871
2038-03-27 10:01 | -3776.38 | 6.6648 | 44.7317 | 48.4627 | -1106.7477
2038-03-28 11:01 | -3603.71 | 6.6648 | 44.82 | 48.4627 | -1056.1431
2038-03-29 12:01 | -3592.83 | 6.6648 | 44.8313 | 48.4627 | -1052.9545
2038-03-30 13:01 | -3476.45 | 6.6648 | 44.8808 | 48.4627 | -1018.8469
2038-03-31 14:01 | -3116.79 | 6.6648 | 45.0686 | 48.4627 | -913.441
2038-04-01 15:01 | -2205.01 | 6.6648 | 45.5635 | 48.4627 | -646.2246
2038-04-02 16:01 | -1844.21 | 6.4185 | 45.8019 | 48.4627 | -540.4846
2038-04-03 17:01 | -1768.4 | 6.1576 | 45.8812 | 48.4627 | -518.2669
2038-04-04 18:01 | -2028.19 | 6.6648 | 45.8782 | 48.4627 | -594.4038
2038-04-05 19:01 | -2375.05 | 6.6648 | 45.7199 | 48.4627 | -696.0584
2038-04-06 20:01 | -3125.86 | 6.6648 | 45.3358 | 48.4627 | -916.0991
2038-04-07 21:01 | -3533.32 | 6.6648 | 45.0596 | 48.4627 | -1035.5139
2038-04-08 22:01 | -4471.34 | 6.6648 | 44.5082 | 48.4627 | -1310.4204
2038-04-09 23:01 | -4503.34 | 6.6648 | 44.3682 | 48.4627 | -1319.7987
2038-04-11 00:01 | -4502.08 | 6.6648 | 44.2974 | 48.4627 | -1319.4294
2038-04-12 01:01 | -5045.84 | 6.6648 | 43.9789 | 48.4627 | -1478.7897
2038-04-13 02:01 | -5157.28 | 6.6648 | 43.8374 | 48.4627 | -1511.4496
2038-04-14 03:01 | -4885.68 | 6.6648 | 43.9017 | 48.4627 | -1431.8515
2038-04-15 04:01 | -4705.08 | 6.6648 | 43.9765 | 48.4627 | -1378.9228
2038-04-16 05:01 | -4346.52 | 6.6648 | 44.1491 | 48.4627 | -1273.8393
2038-04-17 06:01 | -4250.63 | 6.6648 | 44.2085 | 48.4627 | -1245.7367
2038-04-18 07:01 | -4274.97 | 6.6648 | 44.2045 | 48.4627 | -1252.87
2038-04-19 08:01 | -4595.14 | 6.6648 | 44.0436 | 48.4627 | -1346.7026
2038-04-20 09:01 | -2291.93 | 6.6648 | 45.1807 | 48.4627 | -671.6984
2038-04-21 10:01 | -696.536 | 2.3896 | 45.5594 | 48.4627 | -204.1346
2038-04-22 11:01 | 2540.63 | 1 | 45.9461 | 48.4627 | 744.5852
2038-04-23 12:01 | 2983.64 | 1 | 46.2507 | 48.4627 | 874.4186
2038-04-24 13:01 | 3044.64 | 1 | 46.5633 | 48.4627 | 892.2959
2038-04-25 14:01 | 3064.08 | 1 | 46.8022 | 48.4627 | 897.9932
2038-04-26 15:01 | 3072.34 | 1 | 62.594 | 48.4627 | 900.414
2038-04-27 16:01 | 3039.09 | 1 | 61.9382 | 48.4627 | 890.6694
2038-04-28 17:01 | 3089.91 | 1 | 63.1049 | 48.4627 | 905.5632
2038-04-29 18:01 | 3093.85 | 1 | 47.3276 | 48.4627 | 906.7179
2038-04-30 19:01 | 2250.38 | 1 | 47.7248 | 48.4627 | 659.5213
2038-05-01 20:01 | -648.326 | 2.9053 | 47.7612 | 48.4627 | -190.0056
2038-05-02 21:01 | -1121.19 | 4.2021 | 47.3749 | 48.4627 | -328.5884
2038-05-03 22:01 | -1945.5 | 6.6648 | 47.139 | 48.4627 | -570.1698
2038-05-04 23:01 | -2557.43 | 6.6648 | 46.6624 | 48.4627 | -749.5087
2038-05-06 00:01 | -2778.4 | 6.6648 | 46.3671 | 48.4627 | -814.2687
2038-05-07 01:01 | -3281.7 | 6.6648 | 45.9678 | 48.4627 | -961.7713
2038-05-08 02:01 | -3218.96 | 6.6648 | 45.8792 | 48.4627 | -943.3841
2038-05-09 03:01 | -3366.41 | 6.6648 | 45.7222 | 48.4627 | -986.5974
2038-05-10 04:01 | -3326.06 | 6.6648 | 45.6692 | 48.4627 | -974.772
2038-05-11 05:01 | -2846.9 | 6.6648 | 45.8552 | 48.4627 | -834.344
2038-05-12 06:01 | -2720.29 | 6.6648 | 45.9126 | 48.4627 | -797.2383
2038-05-13 07:01 | -1799.23 | 6.2328 | 46.3156 | 48.4627 | -527.3023
2038-05-14 08:01 | -809.814 | 2.7966 | 46.4071 | 48.4627 | -237.3331
2038-05-15 09:01 | 2397.54 | 1 | 46.7174 | 48.4627 | 702.6496
2038-05-16 10:01 | 4541.45 | 1.5122 | 58.1192 | 48.4627 | 1330.9676
2038-05-17 11:01 | 6344.49 | 2.111 | 58.5163 | 48.4627 | 1859.3865
2038-05-18 12:01 | 7276.96 | 2.4368 | 58.8864 | 48.4627 | 2132.6665
2038-05-19 13:01 | 7553.55 | 2.5109 | 59.3501 | 48.4627 | 2213.727
2038-05-20 14:01 | 8218.97 | 2.6975 | 59.7957 | 48.4627 | 2408.7423
2038-05-21 15:01 | 8745.33 | 2.9207 | 59.9108 | 48.4627 | 2563.0032
2038-05-22 16:01 | 7972.85 | 2.6081 | 60.3994 | 48.4627 | 2336.6117
2038-05-23 17:01 | 6374.37 | 2.0881 | 60.5168 | 48.4627 | 1868.1434
2038-05-24 18:01 | 4008.67 | 1.2692 | 60.857 | 48.4627 | 1174.8252
2038-05-25 19:01 | 3123.86 | 1 | 48.9321 | 48.4627 | 915.513
2038-05-26 20:01 | 0 | 0 | 49.8754 | 48.4627 | 0
2038-05-27 21:01 | -531.192 | 2.3443 | 48.7351 | 48.4627 | -155.677
2038-05-28 22:01 | -1480.08 | 5.4166 | 48.3047 | 48.4627 | -433.7686
2038-05-29 23:01 | -2028.22 | 6.6648 | 47.948 | 48.4627 | -594.4126
2038-05-31 00:01 | -2564.07 | 6.6648 | 47.4542 | 48.4627 | -751.4547
2038-06-01 01:01 | -2793.4 | 6.6648 | 47.1249 | 48.4627 | -818.6647
2038-06-02 02:01 | -2838.97 | 6.6648 | 46.9476 | 48.4627 | -832.02
2038-06-03 03:01 | -2818.82 | 6.6648 | 46.8263 | 48.4627 | -826.1146
2038-06-04 04:01 | -2781.48 | 6.6648 | 46.7444 | 48.4627 | -815.1713
2038-06-05 05:01 | -2372.28 | 6.6648 | 46.8743 | 48.4627 | -695.2466
2038-06-06 06:01 | -2376.34 | 6.6648 | 46.8583 | 48.4627 | -696.4365
2038-06-07 07:01 | -1264.59 | 4.2933 | 47.0416 | 48.4627 | -370.6147
2038-06-08 08:01 | 0 | 1 | 48.1373 | 48.4627 | 0
2038-06-09 09:01 | 3497 | 1.1223 | 58.8707 | 48.4627 | 1024.8695
2038-06-10 10:01 | 6072.67 | 2.0313 | 58.8173 | 48.4627 | 1779.7239
2038-06-11 11:01 | 7418.51 | 2.5032 | 59.204 | 48.4627 | 2174.1507
2038-06-12 12:01 | 8546.26 | 2.8685 | 59.6716 | 48.4627 | 2504.6616
2038-06-13 13:01 | 9232.36 | 3.0609 | 60.186 | 48.4627 | 2705.7376
2038-06-14 14:01 | 9310.89 | 3.0805 | 60.5632 | 48.4627 | 2728.7525
2038-06-15 15:01 | 10123.5 | 3.3487 | 60.8121 | 48.4627 | 2966.905
2038-06-16 16:01 | 9354.81 | 3.0614 | 61.1914 | 48.4627 | 2741.6242
2038-06-17 17:01 | 7550.35 | 2.4779 | 61.3041 | 48.4627 | 2212.7892
2038-06-18 18:01 | 5310.85 | 1.6851 | 61.6287 | 48.4627 | 1556.4565
2038-06-19 19:01 | 4078.61 | 1.2796 | 61.5773 | 48.4627 | 1195.3226
2038-06-20 20:01 | 3001.94 | 1 | 49.6243 | 48.4627 | 879.7818
2038-06-21 21:01 | 2912.65 | 1 | 49.4716 | 48.4627 | 853.6135
2038-06-22 22:01 | -641.244 | 2.8159 | 49.5704 | 48.4627 | -187.9301
2038-06-23 23:01 | -1151.94 | 4.2159 | 48.9986 | 48.4627 | -337.6003
2038-06-25 00:01 | -1520.98 | 5.3193 | 48.6651 | 48.4627 | -445.7552
2038-06-26 01:01 | -1827.85 | 6.2501 | 48.4413 | 48.4627 | -535.69
2038-06-27 02:01 | -1959.25 | 6.6093 | 48.2405 | 48.4627 | -574.1995
2038-06-28 03:01 | -1940.69 | 6.5229 | 48.053 | 48.4627 | -568.7601
2038-06-29 04:01 | -1984.86 | 6.6648 | 47.9468 | 48.4627 | -581.705
2038-06-30 05:01 | -1607.15 | 5.3951 | 47.8584 | 48.4627 | -471.0092
2038-07-01 06:01 | -1354.47 | 4.6808 | 47.8613 | 48.4627 | -396.956
2038-07-02 07:01 | -663.279 | 2.4227 | 47.9051 | 48.4627 | -194.3879
2038-07-03 08:01 | -116.468 | 0.84146 | 48.4082 | 48.4627 | -34.1334
2038-07-04 09:01 | 2982.49 | 1.191 | 57.4164 | 48.4627 | 874.0815
2038-07-05 10:01 | 4135.89 | 1.446 | 58.9139 | 48.4627 | 1212.1097
2038-07-06 11:01 | 6765.46 | 2.3328 | 59.3211 | 48.4627 | 1982.7606
2038-07-07 12:01 | 7459.74 | 2.5163 | 59.9429 | 48.4627 | 2186.234
2038-07-08 13:01 | 8496.48 | 2.8177 | 60.4387 | 48.4627 | 2490.0725
2038-07-09 14:01 | 8864.01 | 2.841 | 61.1154 | 48.4627 | 2597.7849
2038-07-10 15:01 | 10465.3 | 3.3223 | 61.458 | 48.4627 | 3067.0767
2038-07-11 16:01 | 9914.42 | 3.1613 | 61.7586 | 48.4627 | 2905.6297
2038-07-12 17:01 | 8751.15 | 2.7672 | 62.033 | 48.4627 | 2564.7089
2038-07-13 18:01 | 6662.05 | 2.0382 | 62.4501 | 48.4627 | 1952.4541
2038-07-14 19:01 | 5510.25 | 1.7082 | 62.2041 | 48.4627 | 1614.8949
2038-07-15 20:01 | 3167.52 | 1.0168 | 61.7356 | 48.4627 | 928.3085
2038-07-16 21:01 | 3130.58 | 1 | 68.3135 | 48.4627 | 917.4824
2038-07-17 22:01 | 2830.48 | 1 | 49.8147 | 48.4627 | 829.5318
2038-07-18 23:01 | -312.007 | 1.7261 | 50.0665 | 48.4627 | -91.4402
2038-07-20 00:01 | -653.907 | 2.664 | 49.4749 | 48.4627 | -191.6412
2038-07-21 01:01 | -917.673 | 3.447 | 49.1463 | 48.4627 | -268.9434
2038-07-22 02:01 | -1092.07 | 3.9499 | 48.9548 | 48.4627 | -320.0541
2038-07-23 03:01 | -1019.86 | 3.6626 | 48.7802 | 48.4627 | -298.8915
2038-07-24 04:01 | -1105.63 | 3.9886 | 48.6467 | 48.4627 | -324.0282
2038-07-25 05:01 | -1121.01 | 4.0091 | 48.5512 | 48.4627 | -328.5356
2038-07-26 06:01 | -481.954 | 1.874 | 48.5606 | 48.4627 | -141.2468
2038-07-27 07:01 | 0 | 1 | 49.4405 | 48.4627 | 0
2038-07-28 08:01 | -431.265 | 2.0677 | 48.7781 | 48.4627 | -126.3913
2038-07-29 09:01 | -314.136 | 1.5309 | 48.7334 | 48.4627 | -92.0642
2038-07-30 10:01 | 216.794 | 1 | 49.309 | 48.4627 | 63.536
2038-07-31 11:01 | 0 | 0 | 49.4019 | 48.4627 | 0
2038-08-01 12:01 | 194.237 | 1 | 49.2951 | 48.4627 | 56.9252
2038-08-02 13:01 | 136.526 | 1 | 49.2776 | 48.4627 | 40.0118
2038-08-03 14:01 | 958.416 | 1 | 48.9581 | 48.4627 | 280.884
2038-08-04 15:01 | 2959.52 | 1 | 48.3013 | 48.4627 | 867.3497
2038-08-05 16:01 | 3126.25 | 1.4416 | 56.8573 | 48.4627 | 916.2134
2038-08-06 17:01 | 2793.42 | 1 | 61.6436 | 48.4627 | 818.6706
2038-08-07 18:01 | 2911.11 | 1 | 48.6454 | 48.4627 | 853.1621
2038-08-08 19:01 | 3030.26 | 1 | 48.669 | 48.4627 | 888.0815
2038-08-09 20:01 | 3116 | 1 | 48.7197 | 48.4627 | 913.2095
2038-08-10 21:01 | 3081.53 | 1 | 48.7797 | 48.4627 | 903.1073
2038-08-11 22:01 | 3143.69 | 1 | 48.8009 | 48.4627 | 921.3246
2038-08-12 23:01 | -807.857 | 3.38 | 49.1347 | 48.4627 | -236.7595
2038-08-14 00:01 | -1058.46 | 3.8597 | 48.6966 | 48.4627 | -310.204
2038-08-15 01:01 | -1110.92 | 3.9929 | 48.4996 | 48.4627 | -325.5785
2038-08-16 02:01 | -1163.19 | 4.1588 | 48.4066 | 48.4627 | -340.8973
2038-08-17 03:01 | -1202.86 | 4.2801 | 48.3013 | 48.4627 | -352.5235
2038-08-18 04:01 | -1255.23 | 4.4498 | 48.1947 | 48.4627 | -367.8716
2038-08-19 05:01 | -1256.39 | 4.4372 | 48.1517 | 48.4627 | -368.2116
2038-08-20 06:01 | -522.066 | 1.969 | 48.1745 | 48.4627 | -153.0024
2038-08-21 07:01 | 0 | 1 | 49.1054 | 48.4627 | 0
2038-08-22 08:01 | -364.057 | 1.8579 | 48.4915 | 48.4627 | -106.6946
2038-08-23 09:01 | -224.245 | 1.2604 | 48.5183 | 48.4627 | -65.7197
2038-08-24 10:01 | 2386.75 | 1 | 48.2813 | 48.4627 | 699.4874
2038-08-25 11:01 | 2402.41 | 1 | 59.2265 | 48.4627 | 704.0769
2038-08-26 12:01 | 2819.82 | 1 | 60.0547 | 48.4627 | 826.4077
2038-08-27 13:01 | 3766.59 | 1.275 | 59.5791 | 48.4627 | 1103.8786
2038-08-28 14:01 | 4553.14 | 1.5009 | 60.0241 | 48.4627 | 1334.3936
2038-08-29 15:01 | 4103.4 | 1.2736 | 60.851 | 48.4627 | 1202.5878
2038-08-30 16:01 | 6322.38 | 2.1577 | 59.9101 | 48.4627 | 1852.9067
2038-08-31 17:01 | 4986.85 | 1.6034 | 60.7945 | 48.4627 | 1461.5015
2038-09-01 18:01 | 3057.54 | 1.0158 | 60.5145 | 48.4627 | 896.0765
2038-09-02 19:01 | 3029.33 | 1 | 49.1523 | 48.4627 | 887.809
2038-09-03 20:01 | 2900.78 | 1 | 49.1607 | 48.4627 | 850.1347
2038-09-04 21:01 | 0 | 0 | 50.1556 | 48.4627 | 0
2038-09-05 22:01 | -429.062 | 1.8734 | 49.0484 | 48.4627 | -125.7457
2038-09-06 23:01 | -1749.66 | 6.3403 | 48.6862 | 48.4627 | -512.7747
2038-09-08 00:01 | -2838.44 | 6.6648 | 47.9637 | 48.4627 | -831.8646
2038-09-09 01:01 | -3540.41 | 6.6648 | 47.3434 | 48.4627 | -1037.5917
2038-09-10 02:01 | -3979.72 | 6.6648 | 46.8612 | 48.4627 | -1166.3408
2038-09-11 03:01 | -4368.84 | 6.6648 | 46.4681 | 48.4627 | -1280.3806
2038-09-12 04:01 | -4467.8 | 6.6648 | 46.2089 | 48.4627 | -1309.3829
2038-09-13 05:01 | -4295.72 | 6.6648 | 46.1367 | 48.4627 | -1258.9513
2038-09-14 06:01 | -4175.62 | 6.6648 | 46.0969 | 48.4627 | -1223.7534
2038-09-15 07:01 | -3664.3 | 6.6648 | 46.2701 | 48.4627 | -1073.9003
2038-09-16 08:01 | -2851.79 | 6.6648 | 46.6467 | 48.4627 | -835.7771
2038-09-17 09:01 | -1397.36 | 4.7612 | 47.1455 | 48.4627 | -409.5258
2038-09-18 10:01 | -299.493 | 1.1992 | 47.4229 | 48.4627 | -87.7727
2038-09-19 11:01 | 2836.28 | 1 | 47.4673 | 48.4627 | 831.2316
2038-09-20 12:01 | 2978.48 | 1 | 47.8129 | 48.4627 | 872.9063
2038-09-21 13:01 | 3026.87 | 1 | 63.7314 | 48.4627 | 887.088
2038-09-22 14:01 | 2908.04 | 1 | 61.7327 | 48.4627 | 852.2624
2038-09-23 15:01 | 2994.25 | 1 | 61.4998 | 48.4627 | 877.5281
2038-09-24 16:01 | 2839.22 | 1 | 48.463 | 48.4627 | 832.0932
2038-09-25 17:01 | 2748.02 | 1 | 48.537 | 48.4627 | 805.3652
2038-09-26 18:01 | -304.363 | 1.7021 | 48.9088 | 48.4627 | -89.2
2038-09-27 19:01 | -1045.29 | 4.014 | 48.3787 | 48.4627 | -306.3443
2038-09-28 20:01 | -2300.79 | 6.6648 | 47.8892 | 48.4627 | -674.295
2038-09-29 21:01 | -3062.39 | 6.6648 | 47.2802 | 48.4627 | -897.4979
2038-09-30 22:01 | -4204.9 | 6.6648 | 46.4711 | 48.4627 | -1232.3345
2038-10-01 23:01 | -4788.17 | 6.6648 | 45.8874 | 48.4627 | -1403.2741
2038-10-03 00:01 | -5127.59 | 6.6648 | 45.4902 | 48.4627 | -1502.7483
2038-10-04 01:01 | -5581.23 | 6.6648 | 45.0687 | 48.4627 | -1635.697
2038-10-05 02:01 | -5785.52 | 6.6648 | 44.7813 | 48.4627 | -1695.5685
2038-10-06 03:01 | -5877.73 | 6.6648 | 44.5713 | 48.4627 | -1722.5926
2038-10-07 04:01 | -5657.11 | 6.6648 | 44.5517 | 48.4627 | -1657.9353
2038-10-08 05:01 | -5276.75 | 6.6648 | 44.653 | 48.4627 | -1546.4628
2038-10-09 06:01 | -4993.55 | 6.6648 | 44.7632 | 48.4627 | -1463.465
2038-10-10 07:01 | -3759.86 | 6.6648 | 45.3729 | 48.4627 | -1101.9062
2038-10-11 08:01 | -2643.19 | 6.6648 | 46.0337 | 48.4627 | -774.6425
2038-10-12 09:01 | -1016.42 | 3.4714 | 46.526 | 48.4627 | -297.8833
2038-10-13 10:01 | 2000.3 | 1 | 47.0564 | 48.4627 | 586.2301
2038-10-14 11:01 | 2942.22 | 1 | 62.157 | 48.4627 | 862.2796
2038-10-15 12:01 | 3370.35 | 1.1421 | 58.4422 | 48.4627 | 987.7521
2038-10-16 13:01 | 3851.64 | 1.336 | 58.4587 | 48.4627 | 1128.8043
2038-10-17 14:01 | 4398.35 | 1.5422 | 58.5795 | 48.4627 | 1289.0291
2038-10-18 15:01 | 5002.25 | 1.7446 | 58.8522 | 48.4627 | 1466.0148
2038-10-19 16:01 | 4011.88 | 1.4301 | 58.8364 | 48.4627 | 1175.766
2038-10-20 17:01 | 2755.82 | 1 | 63.4216 | 48.4627 | 807.6511
2038-10-21 18:01 | 2674.31 | 1 | 48.4321 | 48.4627 | 783.7629
2038-10-22 19:01 | -657.573 | 2.9022 | 48.5935 | 48.4627 | -192.7156
2038-10-23 20:01 | -1788.61 | 6.4186 | 48.1286 | 48.4627 | -524.1898
2038-10-24 21:01 | -2739.82 | 6.6648 | 47.4035 | 48.4627 | -802.962
2038-10-25 22:01 | -4023.62 | 6.6648 | 46.5071 | 48.4627 | -1179.2066
2038-10-26 23:01 | -4359.48 | 6.6648 | 46.0547 | 48.4627 | -1277.6375
2038-10-28 00:01 | -4850.4 | 6.6648 | 45.5683 | 48.4627 | -1421.5119
2038-10-29 01:01 | -4968.13 | 6.6648 | 45.3234 | 48.4627 | -1456.0152
2038-10-30 02:01 | -5114.87 | 6.6648 | 45.0967 | 48.4627 | -1499.0204
2038-10-31 03:01 | -5058.79 | 6.6648 | 44.9874 | 48.4627 | -1482.585
2038-11-01 04:01 | -5048.47 | 6.6648 | 44.8976 | 48.4627 | -1479.5605
2038-11-02 05:01 | -4734.81 | 6.6648 | 44.9781 | 48.4627 | -1387.6358
2038-11-03 06:01 | -4545.68 | 6.6648 | 45.0304 | 48.4627 | -1332.2073
2038-11-04 07:01 | -3373.94 | 6.6648 | 45.6102 | 48.4627 | -988.8042
2038-11-05 08:01 | -2333.83 | 6.6648 | 46.2281 | 48.4627 | -683.9781
2038-11-06 09:01 | -614.627 | 2.0747 | 46.5416 | 48.4627 | -180.1294
2038-11-07 10:01 | 2623.45 | 1 | 46.8762 | 48.4627 | 768.8573
2038-11-08 11:01 | 3304.69 | 1.1406 | 58.0356 | 48.4627 | 968.509
2038-11-09 12:01 | 4519.27 | 1.5243 | 58.5487 | 48.4627 | 1324.4673
2038-11-10 13:01 | 5135.02 | 1.7274 | 58.8857 | 48.4627 | 1504.9258
2038-11-11 14:01 | 5272.61 | 1.8051 | 58.9973 | 48.4627 | 1545.2495
2038-11-12 15:01 | 5718.57 | 1.9568 | 59.2139 | 48.4627 | 1675.9474
2038-11-13 16:01 | 4568.53 | 1.5664 | 59.383 | 48.4627 | 1338.904
2038-11-14 17:01 | 2849.21 | 1 | 60.6692 | 48.4627 | 835.021
2038-11-15 18:01 | 2524.49 | 1 | 48.5998 | 48.4627 | 739.855
2038-11-16 19:01 | -169.708 | 1.2777 | 48.9772 | 48.4627 | -49.7365
2038-11-17 20:01 | -1346.3 | 5.0699 | 48.2798 | 48.4627 | -394.5616
2038-11-18 21:01 | -2092.86 | 6.6648 | 47.8552 | 48.4627 | -613.3567
2038-11-19 22:01 | -3284.33 | 6.6648 | 47.0301 | 48.4627 | -962.5421
2038-11-20 23:01 | -3682.9 | 6.6648 | 46.5803 | 48.4627 | -1079.3514
2038-11-22 00:01 | -4055.75 | 6.6648 | 46.1701 | 48.4627 | -1188.623
2038-11-23 01:01 | -4864.25 | 6.6648 | 45.5879 | 48.4627 | -1425.571
2038-11-24 02:01 | -4836.92 | 6.6648 | 45.3957 | 48.4627 | -1417.5613
2038-11-25 03:01 | -4770.21 | 6.6648 | 45.2774 | 48.4627 | -1398.0105
2038-11-26 04:01 | -4724.09 | 6.6648 | 45.2023 | 48.4627 | -1384.4941
2038-11-27 05:01 | -4205.45 | 6.6648 | 45.387 | 48.4627 | -1232.4957
2038-11-28 06:01 | -3997.38 | 6.6648 | 45.4674 | 48.4627 | -1171.5164
2038-11-29 07:01 | -3372.07 | 6.6648 | 45.7844 | 48.4627 | -988.2562
2038-11-30 08:01 | -3379.5 | 6.6648 | 45.8216 | 48.4627 | -990.4337
2038-12-01 09:01 | -2518.39 | 6.6648 | 46.2613 | 48.4627 | -738.0673
2038-12-02 10:01 | -1794.77 | 6.1785 | 46.6132 | 48.4627 | -525.9952
2038-12-03 11:01 | -915.487 | 3.1549 | 46.6931 | 48.4627 | -268.3028
2038-12-04 12:01 | -449.371 | 1.9004 | 46.9836 | 48.4627 | -131.6976
2038-12-05 13:01 | 2521.07 | 1 | 47.0189 | 48.4627 | 738.8527
2038-12-06 14:01 | 1773.08 | 1 | 47.6139 | 48.4627 | 519.6385
2038-12-07 15:01 | 3161.04 | 1 | 47.2561 | 48.4627 | 926.4094
2038-12-08 16:01 | 0 | 0 | 48.5379 | 48.4627 | 0
2038-12-09 17:01 | 1414.08 | 1 | 47.9037 | 48.4627 | 414.4259
2038-12-10 18:01 | -161.15 | 1.2622 | 48.0294 | 48.4627 | -47.2284
2038-12-11 19:01 | -726.404 | 3.0271 | 47.5569 | 48.4627 | -212.888
2038-12-12 20:01 | -1680.78 | 6.1105 | 47.3433 | 48.4627 | -492.588
2038-12-13 21:01 | -2302.84 | 6.6648 | 46.9561 | 48.4627 | -674.8958
2038-12-14 22:01 | -3296.59 | 6.6648 | 46.3483 | 48.4627 | -966.1352
2038-12-15 23:01 | -3849.53 | 6.6648 | 45.8899 | 48.4627 | -1128.1859
2038-12-17 00:01 | -4388.82 | 6.6648 | 45.4659 | 48.4627 | -1286.2362
2038-12-18 01:01 | -4746.33 | 6.6648 | 45.118 | 48.4627 | -1391.012
2038-12-19 02:01 | -4904.98 | 6.6648 | 44.8947 | 48.4627 | -1437.5077
2038-12-20 03:01 | -5257.94 | 6.6648 | 44.5835 | 48.4627 | -1540.9501
2038-12-21 04:01 | -5355.14 | 6.6648 | 44.425 | 48.4627 | -1569.4366
2038-12-22 05:01 | -5341.25 | 6.6648 | 44.326 | 48.4627 | -1565.3659
2038-12-23 06:01 | -5184.94 | 6.6648 | 44.3336 | 48.4627 | -1519.5559
2038-12-24 07:01 | -4072.13 | 6.6648 | 44.8499 | 48.4627 | -1193.4235
2038-12-25 08:01 | -3129.62 | 6.6648 | 45.3888 | 48.4627 | -917.2011
2038-12-26 09:01 | -1832.57 | 6.3913 | 46.1112 | 48.4627 | -537.0733
2038-12-27 10:01 | -601.043 | 2.0626 | 46.2541 | 48.4627 | -176.1483
2038-12-28 11:01 | 2311.63 | 1 | 46.6556 | 48.4627 | 677.4719
2038-12-29 12:01 | 2772.3 | 1 | 46.8979 | 48.4627 | 812.4809
2038-12-30 13:01 | 2778.31 | 1 | 47.163 | 48.4627 | 814.2423
2038-12-31 14:01 | 2753.92 | 1 | 47.3375 | 48.4627 | 807.0943
2039-01-01 15:01 | 2776.24 | 1 | 47.4564 | 48.4627 | 813.6356
2039-01-02 16:01 | 2550.98 | 1 | 47.6589 | 48.4627 | 747.6184
2039-01-03 17:01 | -370.801 | 1.9686 | 47.9448 | 48.4627 | -108.671
2039-01-04 18:01 | -1228.74 | 4.6644 | 47.4715 | 48.4627 | -360.1081
2039-01-05 19:01 | -1842.52 | 6.4937 | 47.2243 | 48.4627 | -539.9893
2039-01-06 20:01 | -3226.9 | 6.6648 | 46.4141 | 48.4627 | -945.711
2039-01-07 21:01 | -3755.81 | 6.6648 | 45.9184 | 48.4627 | -1100.7193
2039-01-08 22:01 | -4844.15 | 6.6648 | 45.1613 | 48.4627 | -1419.6802
2039-01-09 23:01 | -5488.36 | 6.6648 | 44.6069 | 48.4627 | -1608.4795
2039-01-11 00:01 | -5874.85 | 6.6648 | 44.1918 | 48.4627 | -1721.7486
2039-01-12 01:01 | -6017.97 | 6.6648 | 43.9298 | 48.4627 | -1763.6929
2039-01-13 02:01 | -6141.38 | 6.6648 | 43.7193 | 48.4627 | -1799.8608
2039-01-14 03:01 | -6457.71 | 6.6648 | 43.4238 | 48.4627 | -1892.568
2039-01-15 04:01 | -6446.12 | 6.6648 | 43.2924 | 48.4627 | -1889.1713
2039-01-16 05:01 | -6699.72 | 6.6648 | 43.0755 | 48.4627 | -1963.4941
2039-01-17 06:01 | -5554.47 | 6.6648 | 43.5658 | 48.4627 | -1627.8545
2039-01-18 07:01 | -4471.21 | 6.6648 | 44.1469 | 48.4627 | -1310.3823
2039-01-19 08:01 | -4778.14 | 6.6648 | 44.093 | 48.4627 | -1400.3346
2039-01-20 09:01 | -4329.6 | 6.6648 | 44.3196 | 48.4627 | -1268.8805
2039-01-21 10:01 | -2886.7 | 6.6648 | 45.0808 | 48.4627 | -846.0083
2039-01-22 11:01 | -2966.35 | 6.6648 | 45.1903 | 48.4627 | -869.3514
2039-01-23 12:01 | -3013.01 | 6.6648 | 45.2193 | 48.4627 | -883.0261
2039-01-24 13:01 | -1859.55 | 6.516 | 45.7769 | 48.4627 | -544.9803
2039-01-25 14:01 | -824.213 | 2.8343 | 45.8725 | 48.4627 | -241.553
2039-01-26 15:01 | -1048.28 | 4.0336 | 46.1398 | 48.4627 | -307.2205
2039-01-27 16:01 | 1630.42 | 1 | 46.52 | 48.4627 | 477.8289
2039-01-28 17:01 | -856.142 | 3.6715 | 46.5988 | 48.4627 | -250.9105
2039-01-29 18:01 | -1698.38 | 6.184 | 46.427 | 48.4627 | -497.746
2039-01-30 19:01 | -2585.16 | 6.6648 | 45.944 | 48.4627 | -757.6356
2039-01-31 20:01 | -3032.37 | 6.6648 | 45.622 | 48.4627 | -888.6999
2039-02-01 21:01 | -3479.61 | 6.6648 | 45.3177 | 48.4627 | -1019.773
2039-02-02 22:01 | -3408.02 | 6.6648 | 45.227 | 48.4627 | -998.7921
2039-02-03 23:01 | -5266.26 | 6.6648 | 44.2372 | 48.4627 | -1543.3885
2039-02-05 00:01 | -5841.03 | 6.6648 | 43.7433 | 48.4627 | -1711.8369
2039-02-06 01:01 | -6098.86 | 6.6648 | 43.4356 | 48.4627 | -1787.3994
2039-02-07 02:01 | -6117.64 | 6.6648 | 43.2939 | 48.4627 | -1792.9033
2039-02-08 03:01 | -6178.19 | 6.6648 | 43.165 | 48.4627 | -1810.6488
2039-02-09 04:01 | -6166.48 | 6.6648 | 43.0513 | 48.4627 | -1807.2169
2039-02-10 05:01 | -6237.02 | 6.6648 | 42.951 | 48.4627 | -1827.8901
2039-02-11 06:01 | -5436.46 | 6.6648 | 43.2994 | 48.4627 | -1593.2691
2039-02-12 07:01 | -5099.17 | 6.6648 | 43.496 | 48.4627 | -1494.4192
2039-02-13 08:01 | -5777.41 | 6.6648 | 43.1794 | 48.4627 | -1693.1917
2039-02-14 09:01 | -5766.08 | 6.6648 | 43.1118 | 48.4627 | -1689.8712
2039-02-15 10:01 | -5751.56 | 6.6648 | 43.0539 | 48.4627 | -1685.6158
2039-02-16 11:01 | -5663.03 | 6.6648 | 43.061 | 48.4627 | -1659.6703
2039-02-17 12:01 | -5719.73 | 6.6648 | 42.9913 | 48.4627 | -1676.2874
2039-02-18 13:01 | -5809.21 | 6.6648 | 42.8865 | 48.4627 | -1702.5114
2039-02-19 14:01 | -5740.22 | 6.6648 | 42.8603 | 48.4627 | -1682.2924
2039-02-20 15:01 | -5610.6 | 6.6648 | 42.8762 | 48.4627 | -1644.3045
2039-02-21 16:01 | -4304.15 | 6.6648 | 43.4941 | 48.4627 | -1261.4218
2039-02-22 17:01 | -4567.08 | 6.6648 | 43.4509 | 48.4627 | -1338.479
2039-02-23 18:01 | -5028.42 | 6.6648 | 43.224 | 48.4627 | -1473.6844
2039-02-24 19:01 | -5336.39 | 6.6648 | 43.0151 | 48.4627 | -1563.9415
2039-02-25 20:01 | -5531.95 | 6.6648 | 42.8694 | 48.4627 | -1621.2545
2039-02-26 21:01 | -5597.41 | 6.6648 | 42.7965 | 48.4627 | -1640.4389
2039-02-27 22:01 | -5515.72 | 6.6648 | 42.79 | 48.4627 | -1616.498
2039-02-28 23:01 | -6670.6 | 6.6648 | 42.184 | 48.4627 | -1954.9599
2039-03-02 00:01 | -6878.41 | 6.6648 | 41.9566 | 48.4627 | -2015.863
2039-03-03 01:01 | -6705.08 | 6.6648 | 41.9571 | 48.4627 | -1965.065
2039-03-04 02:01 | -6926.91 | 6.6648 | 41.8133 | 48.4627 | -2030.0769
2039-03-05 03:01 | -6975.98 | 6.6648 | 41.7346 | 48.4627 | -2044.4579
2039-03-06 04:01 | -7154.52 | 6.6648 | 41.5778 | 48.4627 | -2096.7828
2039-03-07 05:01 | -7104.07 | 6.6648 | 41.5489 | 48.4627 | -2081.9974
2039-03-08 06:01 | -6352.03 | 6.6648 | 41.8922 | 48.4627 | -1861.5962
2039-03-09 07:01 | -5855.69 | 6.6648 | 42.1762 | 48.4627 | -1716.1333
2039-03-10 08:01 | -6620.63 | 6.6648 | 41.8422 | 48.4627 | -1940.3151
2039-03-11 09:01 | -6656.79 | 6.6648 | 41.7643 | 48.4627 | -1950.9126
2039-03-12 10:01 | -6343.58 | 6.6648 | 41.877 | 48.4627 | -1859.1198
2039-03-13 11:01 | -5846.68 | 6.6648 | 42.1416 | 48.4627 | -1713.4928
2039-03-14 12:01 | -5751.28 | 6.6648 | 42.2269 | 48.4627 | -1685.5338
2039-03-15 13:01 | -5836.52 | 6.6648 | 42.1859 | 48.4627 | -1710.5152
2039-03-16 14:01 | -5565.33 | 6.6648 | 42.3144 | 48.4627 | -1631.0372
2039-03-17 15:01 | -5298.97 | 6.6648 | 42.4678 | 48.4627 | -1552.9748
2039-03-18 16:01 | -3738.52 | 6.6648 | 43.2855 | 48.4627 | -1095.6521
2039-03-19 17:01 | -4165.34 | 6.6648 | 43.2232 | 48.4627 | -1220.7407
2039-03-20 18:01 | -4446.32 | 6.6648 | 43.1216 | 48.4627 | -1303.0878
2039-03-21 19:01 | -4709.33 | 6.6648 | 42.9822 | 48.4627 | -1380.1684
2039-03-22 20:01 | -4874.38 | 6.6648 | 42.8939 | 48.4627 | -1428.5398
2039-03-23 21:01 | -4953.9 | 6.6648 | 42.8502 | 48.4627 | -1451.8448
2039-03-24 22:01 | -4984.74 | 6.6648 | 42.8099 | 48.4627 | -1460.8831
2039-03-25 23:01 | -6130.31 | 6.6648 | 42.219 | 48.4627 | -1796.6165
2039-03-27 00:01 | -6189.67 | 6.6648 | 42.0791 | 48.4627 | -1814.0132
2039-03-28 01:01 | -6536.51 | 6.6648 | 41.8407 | 48.4627 | -1915.662
2039-03-29 02:01 | -6633.5 | 6.6648 | 41.728 | 48.4627 | -1944.0869
2039-03-30 03:01 | -6413.12 | 6.6648 | 41.7836 | 48.4627 | -1879.4999
2039-03-31 04:01 | -6263.67 | 6.6648 | 41.8258 | 48.4627 | -1835.7005
2039-04-01 05:01 | -6150.43 | 6.6648 | 41.8796 | 48.4627 | -1802.5131
2039-04-02 06:01 | -5837.46 | 6.6648 | 42.0328 | 48.4627 | -1710.7906
2039-04-03 07:01 | -5197.11 | 6.6648 | 42.3791 | 48.4627 | -1523.1226
2039-04-04 08:01 | -5723.35 | 6.6648 | 42.1839 | 48.4627 | -1677.3483
2039-04-05 09:01 | -3814.14 | 6.6648 | 43.1392 | 48.4627 | -1117.8141
2039-04-06 10:01 | -2578.96 | 6.6648 | 43.9382 | 48.4627 | -755.8186
2039-04-07 11:01 | -1945.14 | 6.6648 | 44.4863 | 48.4627 | -570.0643
2039-04-08 12:01 | -674.731 | 2.337 | 44.6793 | 48.4627 | -197.7441
2039-04-09 13:01 | -287.093 | 1.4739 | 45.2438 | 48.4627 | -84.1387
2039-04-10 14:01 | 0 | 1 | 46.1302 | 48.4627 | 0
2039-04-11 15:01 | 2891.8 | 1 | 45.314 | 48.4627 | 847.5029
2039-04-12 16:01 | -279.899 | 1.6988 | 46.1424 | 48.4627 | -82.0303
2039-04-13 17:01 | -819.515 | 3.3806 | 45.8407 | 48.4627 | -240.1761
2039-04-14 18:01 | -1454.13 | 5.4249 | 45.7023 | 48.4627 | -426.1634
2039-04-15 19:01 | -2087.15 | 6.6648 | 45.5269 | 48.4627 | -611.6833
2039-04-16 20:01 | -3393.01 | 6.6648 | 44.8199 | 48.4627 | -994.3931
2039-04-17 21:01 | -3556.63 | 6.6648 | 44.5461 | 48.4627 | -1042.3454
2039-04-18 22:01 | -4268.89 | 6.6648 | 44.0896 | 48.4627 | -1251.0882
2039-04-19 23:01 | -4473.39 | 6.6648 | 43.8726 | 48.4627 | -1311.0212
2039-04-21 00:01 | -4807.61 | 6.6648 | 43.6039 | 48.4627 | -1408.9714
2039-04-22 01:01 | -5029.05 | 6.6648 | 43.3945 | 48.4627 | -1473.8691
2039-04-23 02:01 | -4973.23 | 6.6648 | 43.3436 | 48.4627 | -1457.5098
2039-04-24 03:01 | -4978.86 | 6.6648 | 43.2628 | 48.4627 | -1459.1598
2039-04-25 04:01 | -4738.66 | 6.6648 | 43.3471 | 48.4627 | -1388.7642
2039-04-26 05:01 | -4353.93 | 6.6648 | 43.5345 | 48.4627 | -1276.0109
2039-04-27 06:01 | -4324.86 | 6.6648 | 43.5751 | 48.4627 | -1267.4913
2039-04-28 07:01 | -4322.48 | 6.6648 | 43.5863 | 48.4627 | -1266.7938
2039-04-29 08:01 | -4185.21 | 6.6648 | 43.669 | 48.4627 | -1226.564
2039-04-30 09:01 | -3971.69 | 6.6648 | 43.7954 | 48.4627 | -1163.9874
2039-05-01 10:01 | -4533.9 | 6.6648 | 43.5344 | 48.4627 | -1328.7549
2039-05-02 11:01 | -4692.48 | 6.6648 | 43.4028 | 48.4627 | -1375.2301
2039-05-03 12:01 | -5345.74 | 6.6648 | 43.0179 | 48.4627 | -1566.6817
2039-05-04 13:01 | -5316.79 | 6.6648 | 42.9355 | 48.4627 | -1558.1973
2039-05-05 14:01 | -5349.95 | 6.6648 | 42.8492 | 48.4627 | -1567.9156
2039-05-06 15:01 | -4617.31 | 6.6648 | 43.1488 | 48.4627 | -1353.2
2039-05-07 16:01 | -4535.56 | 6.6648 | 43.2038 | 48.4627 | -1329.2414
2039-05-08 17:01 | -4608.88 | 6.6648 | 43.1644 | 48.4627 | -1350.7294
2039-05-09 18:01 | -4730.23 | 6.6648 | 43.0867 | 48.4627 | -1386.2936
2039-05-10 19:01 | -5240.89 | 6.6648 | 42.805 | 48.4627 | -1535.9532
2039-05-11 20:01 | -6010.58 | 6.6648 | 42.3545 | 48.4627 | -1761.5271
2039-05-12 21:01 | -6221.41 | 6.6648 | 42.1253 | 48.4627 | -1823.3153
2039-05-13 22:01 | -6969.61 | 6.6648 | 41.6529 | 48.4627 | -2042.5911
2039-05-14 23:01 | -7070.12 | 6.6648 | 41.4725 | 48.4627 | -2072.0476
2039-05-16 00:01 | -7265.92 | 6.6648 | 41.2796 | 48.4627 | -2129.4309
2039-05-17 01:01 | -7341.97 | 6.6648 | 41.1613 | 48.4627 | -2151.719
2039-05-18 02:01 | -7381.01 | 6.6648 | 41.0779 | 48.4627 | -2163.1605
2039-05-19 03:01 | -7251.76 | 6.6648 | 41.0817 | 48.4627 | -2125.2811
2039-05-20 04:01 | -7289.27 | 6.6648 | 41.0268 | 48.4627 | -2136.2742
2039-05-21 05:01 | -6876.6 | 6.6648 | 41.1939 | 48.4627 | -2015.3325
2039-05-22 06:01 | -6460.12 | 6.6648 | 41.4042 | 48.4627 | -1893.2743
2039-05-23 07:01 | -6118.75 | 6.6648 | 41.6042 | 48.4627 | -1793.2286
2039-05-24 08:01 | -6476.96 | 6.6648 | 41.4609 | 48.4627 | -1898.2096
2039-05-25 09:01 | -6105.12 | 6.6648 | 41.6236 | 48.4627 | -1789.2341
2039-05-26 10:01 | -5481.82 | 6.6648 | 41.9617 | 48.4627 | -1606.5629
2039-05-27 11:01 | -5262.47 | 6.6648 | 42.1405 | 48.4627 | -1542.2777
2039-05-28 12:01 | -4992.65 | 6.6648 | 42.3257 | 48.4627 | -1463.2013
2039-05-29 13:01 | -4851.75 | 6.6648 | 42.4411 | 48.4627 | -1421.9076
2039-05-30 14:01 | -4609.02 | 6.6648 | 42.6114 | 48.4627 | -1350.7704
2039-05-31 15:01 | -3720.26 | 6.6648 | 43.1059 | 48.4627 | -1090.3006
2039-06-01 16:01 | -3536.86 | 6.6648 | 43.31 | 48.4627 | -1036.5513
2039-06-02 17:01 | -3623 | 6.6648 | 43.348 | 48.4627 | -1061.7965
2039-06-03 18:01 | -4033.83 | 6.6648 | 43.1777 | 48.4627 | -1182.1989
2039-06-04 19:01 | -4049.49 | 6.6648 | 43.1677 | 48.4627 | -1186.7884
2039-06-05 20:01 | -5263.16 | 6.6648 | 42.5711 | 48.4627 | -1542.4799
2039-06-06 21:01 | -5735.29 | 6.6648 | 42.2278 | 48.4627 | -1680.8476
2039-06-07 22:01 | -6650.22 | 6.6648 | 41.6602 | 48.4627 | -1948.9871
2039-06-08 23:01 | -6905.87 | 6.6648 | 41.39 | 48.4627 | -2023.9107
2039-06-10 00:01 | -7254.99 | 6.6648 | 41.1031 | 48.4627 | -2126.2277
2039-06-11 01:01 | -7322.77 | 6.6648 | 40.9586 | 48.4627 | -2146.092
2039-06-12 02:01 | -7284.99 | 6.6648 | 40.9003 | 48.4627 | -2135.0198
2039-06-13 03:01 | -7085.78 | 6.6648 | 40.9396 | 48.4627 | -2076.6371
2039-06-14 04:01 | -6787.71 | 6.6648 | 41.0624 | 48.4627 | -1989.2814
2039-06-15 05:01 | -6501.56 | 6.6648 | 41.2012 | 48.4627 | -1905.4191
2039-06-16 06:01 | -6549.64 | 6.6648 | 41.1866 | 48.4627 | -1919.51
2039-06-17 07:01 | -6079.19 | 6.6648 | 41.4112 | 48.4627 | -1781.6347
2039-06-18 08:01 | -5943.52 | 6.6648 | 41.5172 | 48.4627 | -1741.8738
2039-06-19 09:01 | -5213.44 | 6.6648 | 41.9184 | 48.4627 | -1527.9084
2039-06-20 10:01 | -3500.26 | 6.6648 | 42.875 | 48.4627 | -1025.8249
2039-06-21 11:01 | -1891.86 | 6.6648 | 43.9076 | 48.4627 | -554.4494
2039-06-22 12:01 | -1623.21 | 5.7664 | 44.2009 | 48.4627 | -475.7159
2039-06-23 13:01 | -1130.79 | 4.0833 | 44.4103 | 48.4627 | -331.4018
2039-06-24 14:01 | -944.803 | 3.6081 | 44.6502 | 48.4627 | -276.8944
2039-06-25 15:01 | -239.465 | 1.161 | 44.9987 | 48.4627 | -70.1803
2039-06-26 16:01 | -240.525 | 1.4446 | 45.3129 | 48.4627 | -70.4909
2039-06-27 17:01 | -864.606 | 3.599 | 45.1805 | 48.4627 | -253.391
2039-06-28 18:01 | -2340.54 | 6.6648 | 44.8445 | 48.4627 | -685.9446
2039-06-29 19:01 | -2847.45 | 6.6648 | 44.4967 | 48.4627 | -834.5052
2039-06-30 20:01 | -4094.81 | 6.6648 | 43.8015 | 48.4627 | -1200.0703
2039-07-01 21:01 | -4553.92 | 6.6648 | 43.4279 | 48.4627 | -1334.6222
2039-07-02 22:01 | -5740.33 | 6.6648 | 42.6944 | 48.4627 | -1682.3247
2039-07-03 23:01 | -6339.12 | 6.6648 | 42.1929 | 48.4627 | -1857.8127
2039-07-05 00:01 | -6892.01 | 6.6648 | 41.7401 | 48.4627 | -2019.8487
2039-07-06 01:01 | -7087.77 | 6.6648 | 41.4742 | 48.4627 | -2077.2203
2039-07-07 02:01 | -7415.54 | 6.6648 | 41.1785 | 48.4627 | -2173.2802
2039-07-08 03:01 | -7579.36 | 6.6648 | 40.9563 | 48.4627 | -2221.2911
2039-07-09 04:01 | -7706.36 | 6.6648 | 40.7733 | 48.4627 | -2258.5112
2039-07-10 05:01 | -7814 | 6.6648 | 40.615 | 48.4627 | -2290.0573
2039-07-11 06:01 | -6983.75 | 6.6648 | 40.9541 | 48.4627 | -2046.7351
2039-07-12 07:01 | -5483.4 | 6.6648 | 41.7279 | 48.4627 | -1607.0259
2039-07-13 08:01 | -4636.23 | 6.6648 | 42.2995 | 48.4627 | -1358.7449
2039-07-14 09:01 | -2968.82 | 6.6648 | 43.2887 | 48.4627 | -870.0753
2039-07-15 10:01 | -1348.85 | 4.8222 | 44.0821 | 48.4627 | -395.3089
2039-07-16 11:01 | 0 | 0 | 45.3299 | 48.4627 | 0
2039-07-17 12:01 | 2776.32 | 1 | 44.693 | 48.4627 | 813.6591
2039-07-18 13:01 | 2777.51 | 1 | 45.1538 | 48.4627 | 814.0078
2039-07-19 14:01 | 2773.94 | 1 | 45.4573 | 48.4627 | 812.9616
2039-07-20 15:01 | 2759.9 | 1 | 45.662 | 48.4627 | 808.8468
2039-07-21 16:01 | 2822.39 | 1 | 58.3897 | 48.4627 | 827.1609
2039-07-22 17:01 | 2611.9 | 1 | 46.0512 | 48.4627 | 765.4723
2039-07-23 18:01 | -436.295 | 2.2292 | 46.3841 | 48.4627 | -127.8654
2039-07-24 19:01 | -1345.53 | 5.1517 | 45.9649 | 48.4627 | -394.3359
2039-07-25 20:01 | -1667.36 | 5.9652 | 45.7483 | 48.4627 | -488.655
2039-07-26 21:01 | -2066.73 | 6.6648 | 45.5607 | 48.4627 | -605.6988
2039-07-27 22:01 | -2441.19 | 6.6648 | 45.2774 | 48.4627 | -715.4422
2039-07-28 23:01 | -4155.35 | 6.6648 | 44.2956 | 48.4627 | -1217.8129
2039-07-30 00:01 | -4541.98 | 6.6648 | 43.8769 | 48.4627 | -1331.1229
2039-07-31 01:01 | -4703.25 | 6.6648 | 43.6309 | 48.4627 | -1378.3865
2039-08-01 02:01 | -4916.58 | 6.6648 | 43.4072 | 48.4627 | -1440.9074
2039-08-02 03:01 | -5092.22 | 6.6648 | 43.2048 | 48.4627 | -1492.3824
2039-08-03 04:01 | -5189.62 | 6.6648 | 43.0431 | 48.4627 | -1520.9275
2039-08-04 05:01 | -5111.5 | 6.6648 | 43.0029 | 48.4627 | -1498.0328
2039-08-05 06:01 | -4333.89 | 6.6648 | 43.3622 | 48.4627 | -1270.1378
2039-08-06 07:01 | -3192.32 | 6.6648 | 43.9845 | 48.4627 | -935.5766
2039-08-07 08:01 | -2641.31 | 6.6648 | 44.386 | 48.4627 | -774.0915
2039-08-08 09:01 | -1648.08 | 5.8274 | 44.8761 | 48.4627 | -483.0046
2039-08-09 10:01 | -619.513 | 2.23 | 45.0371 | 48.4627 | -181.5613
2039-08-10 11:01 | 1299.54 | 1 | 45.7336 | 48.4627 | 380.8576
2039-08-11 12:01 | 2787.26 | 1 | 45.5216 | 48.4627 | 816.8653
2039-08-12 13:01 | 2723.92 | 1 | 45.8618 | 48.4627 | 798.3021
2039-08-13 14:01 | 203.143 | 1 | 46.9185 | 48.4627 | 59.5353
2039-08-14 15:01 | -176.263 | 1.3268 | 46.435 | 48.4627 | -51.6576
2039-08-15 16:01 | 2645.01 | 1 | 45.9319 | 48.4627 | 775.1759
2039-08-16 17:01 | -131.426 | 1.1586 | 46.722 | 48.4627 | -38.5172
2039-08-17 18:01 | -661.812 | 2.8735 | 46.2082 | 48.4627 | -193.958
2039-08-18 19:01 | -1333.94 | 5.0396 | 45.9645 | 48.4627 | -390.9392
2039-08-19 20:01 | -1846.37 | 6.6017 | 45.8531 | 48.4627 | -541.1176
2039-08-20 21:01 | -2501.96 | 6.6648 | 45.4587 | 48.4627 | -733.2521
2039-08-21 22:01 | -2928.84 | 6.6648 | 45.0954 | 48.4627 | -858.3583
2039-08-22 23:01 | -4261.6 | 6.6648 | 44.3083 | 48.4627 | -1248.9517
2039-08-24 00:01 | -4724.55 | 6.6648 | 43.8663 | 48.4627 | -1384.6289
2039-08-25 01:01 | -5094.19 | 6.6648 | 43.5043 | 48.4627 | -1492.9597
2039-08-26 02:01 | -5361.78 | 6.6648 | 43.2403 | 48.4627 | -1571.3826
2039-08-27 03:01 | -5373.66 | 6.6648 | 43.1216 | 48.4627 | -1574.8643
2039-08-28 04:01 | -5481.52 | 6.6648 | 42.9577 | 48.4627 | -1606.4749
2039-08-29 05:01 | -5284.55 | 6.6648 | 42.9896 | 48.4627 | -1548.7487
2039-08-30 06:01 | -5326.63 | 6.6648 | 42.9296 | 48.4627 | -1561.0812
2039-08-31 07:01 | -4808.13 | 6.6648 | 43.1487 | 48.4627 | -1409.1238
2039-09-01 08:01 | -4062.57 | 6.6648 | 43.5366 | 48.4627 | -1190.6217
2039-09-02 09:01 | -2618.58 | 6.6648 | 44.3305 | 48.4627 | -767.43
2039-09-03 10:01 | -1614.18 | 5.7058 | 44.8564 | 48.4627 | -473.0695
2039-09-04 11:01 | -1158.74 | 4.1506 | 45.039 | 48.4627 | -339.5932
2039-09-05 12:01 | -604.744 | 2.3716 | 45.2514 | 48.4627 | -177.233
2039-09-06 13:01 | -1270.82 | 4.9181 | 45.3775 | 48.4627 | -372.4406
2039-09-07 14:01 | -1028.37 | 3.765 | 45.3644 | 48.4627 | -301.3855
2039-09-08 15:01 | -742.385 | 2.8916 | 45.471 | 48.4627 | -217.5716
2039-09-09 16:01 | -1047.23 | 4.0607 | 45.5252 | 48.4627 | -306.9128
2039-09-10 17:01 | -1639.93 | 6.0213 | 45.4905 | 48.4627 | -480.616
2039-09-11 18:01 | -2540.42 | 6.6648 | 45.0832 | 48.4627 | -744.5236
2039-09-12 19:01 | -3348.55 | 6.6648 | 44.5883 | 48.4627 | -981.3631
2039-09-13 20:01 | -4221.68 | 6.6648 | 44.0265 | 48.4627 | -1237.2523
2039-09-14 21:01 | -5038.41 | 6.6648 | 43.4502 | 48.4627 | -1476.6122
2039-09-15 22:01 | -6120.19 | 6.6648 | 42.7148 | 48.4627 | -1793.6506
2039-09-16 23:01 | -6559.51 | 6.6648 | 42.2719 | 48.4627 | -1922.4026
2039-09-18 00:01 | -6726.2 | 6.6648 | 42.0031 | 48.4627 | -1971.2546
2039-09-19 01:01 | -7146.09 | 6.6648 | 41.654 | 48.4627 | -2094.3122
2039-09-20 02:01 | -7495.54 | 6.6648 | 41.331 | 48.4627 | -2196.7259
2039-09-21 03:01 | -7117.88 | 6.6648 | 41.3773 | 48.4627 | -2086.0447
2039-09-22 04:01 | -7075.54 | 6.6648 | 41.3354 | 48.4627 | -2073.6361
2039-09-23 05:01 | -6763.84 | 6.6648 | 41.4386 | 48.4627 | -1982.2858
2039-09-24 06:01 | -7004.97 | 6.6648 | 41.2876 | 48.4627 | -2052.9541
2039-09-25 07:01 | -5576.63 | 6.6648 | 41.9586 | 48.4627 | -1634.3489
2039-09-26 08:01 | -4612.07 | 6.6648 | 42.545 | 48.4627 | -1351.6643
2039-09-27 09:01 | -2802.02 | 6.6648 | 43.5953 | 48.4627 | -821.191
2039-09-28 10:01 | -1226.6 | 4.3559 | 44.295 | 48.4627 | -359.481
2039-09-29 11:01 | 0 | 1 | 45.528 | 48.4627 | 0
2039-09-30 12:01 | 2760.89 | 1 | 44.8732 | 48.4627 | 809.137
2039-10-01 13:01 | 2778.67 | 1 | 45.3178 | 48.4627 | 814.3478
2039-10-02 14:01 | 2774.07 | 1 | 45.6198 | 48.4627 | 812.9997
2039-10-03 15:01 | 2783.8 | 1 | 60.3517 | 48.4627 | 815.8512
2039-10-04 16:01 | 2739.61 | 1 | 45.9891 | 48.4627 | 802.9004
2039-10-05 17:01 | -383.45 | 2.0167 | 46.4325 | 48.4627 | -112.3781
2039-10-06 18:01 | -1373.4 | 5.2691 | 46.0033 | 48.4627 | -402.5038
2039-10-07 19:01 | -2205.66 | 6.6648 | 45.5992 | 48.4627 | -646.4151
2039-10-08 20:01 | -3382.29 | 6.6648 | 44.8681 | 48.4627 | -991.2513
2039-10-09 21:01 | -3977.64 | 6.6648 | 44.3668 | 48.4627 | -1165.7312
2039-10-10 22:01 | -4930.15 | 6.6648 | 43.6884 | 48.4627 | -1444.8843
2039-10-11 23:01 | -5350.35 | 6.6648 | 43.2877 | 48.4627 | -1568.0328
2039-10-13 00:01 | -5357 | 6.6648 | 43.1067 | 48.4627 | -1569.9817
2039-10-14 01:01 | -5614.93 | 6.6648 | 42.8542 | 48.4627 | -1645.5735
2039-10-15 02:01 | -5934.35 | 6.6648 | 42.5773 | 48.4627 | -1739.1863
2039-10-16 03:01 | -5440.86 | 6.6648 | 42.7025 | 48.4627 | -1594.5587
2039-10-17 04:01 | -5265.06 | 6.6648 | 42.7498 | 48.4627 | -1543.0368
2039-10-18 05:01 | -4839.99 | 6.6648 | 42.9597 | 48.4627 | -1418.461
2039-10-19 06:01 | -4658.84 | 6.6648 | 43.0757 | 48.4627 | -1365.3712
2039-10-20 07:01 | -3492.29 | 6.6648 | 43.6918 | 48.4627 | -1023.4892
2039-10-21 08:01 | -2512.73 | 6.6648 | 44.3177 | 48.4627 | -736.4085
2039-10-22 09:01 | -1188.16 | 4.1754 | 44.7843 | 48.4627 | -348.2153
2039-10-23 10:01 | 83.1881 | 1 | 45.9311 | 48.4627 | 24.38
2039-10-24 11:01 | 2786.41 | 1 | 45.2516 | 48.4627 | 816.6162
2039-10-25 12:01 | 2758.97 | 1 | 45.665 | 48.4627 | 808.5743
2039-10-26 13:01 | -486.84 | 2.3864 | 46.1569 | 48.4627 | -142.6787
2039-10-27 14:01 | -877.1 | 3.5051 | 45.8473 | 48.4627 | -257.0526
2039-10-28 15:01 | -1038.38 | 3.9472 | 45.7172 | 48.4627 | -304.3191
2039-10-29 16:01 | -970.3 | 3.6586 | 45.683 | 48.4627 | -284.3669
2039-10-30 17:01 | -858.637 | 3.3026 | 45.6637 | 48.4627 | -251.6417
2039-10-31 18:01 | -1372.36 | 5.1513 | 45.6272 | 48.4627 | -402.199
2039-11-01 19:01 | -1642.7 | 5.8947 | 45.5642 | 48.4627 | -481.4278
2039-11-02 20:01 | -2712.3 | 6.6648 | 45.1058 | 48.4627 | -794.8967
2039-11-03 21:01 | -3121.62 | 6.6648 | 44.7892 | 48.4627 | -914.8565
2039-11-04 22:01 | -3992.37 | 6.6648 | 44.2435 | 48.4627 | -1170.0481
2039-11-05 23:01 | -4270.57 | 6.6648 | 43.9381 | 48.4627 | -1251.5805
2039-11-07 00:01 | -4393.94 | 6.6648 | 43.7398 | 48.4627 | -1287.7367
2039-11-08 01:01 | -4585.39 | 6.6648 | 43.5607 | 48.4627 | -1343.8452
2039-11-09 02:01 | -4583.32 | 6.6648 | 43.4962 | 48.4627 | -1343.2385
2039-11-10 03:01 | -4359.9 | 6.6648 | 43.5611 | 48.4627 | -1277.7606
2039-11-11 04:01 | -4202.54 | 6.6648 | 43.6317 | 48.4627 | -1231.6429
2039-11-12 05:01 | -3695.3 | 6.6648 | 43.8877 | 48.4627 | -1082.9855
2039-11-13 06:01 | -3724.99 | 6.6648 | 43.9129 | 48.4627 | -1091.6868
2039-11-14 07:01 | -3778.79 | 6.6648 | 43.894 | 48.4627 | -1107.454
2039-11-15 08:01 | -4202.02 | 6.6648 | 43.672 | 48.4627 | -1231.4905
2039-11-16 09:01 | -4154.2 | 6.6648 | 43.6402 | 48.4627 | -1217.4758
2039-11-17 10:01 | -3800.12 | 6.6648 | 43.7821 | 48.4627 | -1113.7052
2039-11-18 11:01 | -3263.75 | 6.6648 | 44.0382 | 48.4627 | -956.5107
2039-11-19 12:01 | -3126.92 | 6.6648 | 44.1224 | 48.4627 | -916.4098
2039-11-20 13:01 | -2224.5 | 6.6648 | 44.5947 | 48.4627 | -651.9366
2039-11-21 14:01 | -1277.23 | 4.4803 | 44.8521 | 48.4627 | -374.3192
2039-11-22 15:01 | -313.5 | 1.3143 | 45.1528 | 48.4627 | -91.8778
2039-11-23 16:01 | -324.629 | 1.7162 | 45.488 | 48.4627 | -95.1394
2039-11-24 17:01 | -728.861 | 3.0823 | 45.4278 | 48.4627 | -213.6081
2039-11-25 18:01 | -1693.38 | 6.3382 | 45.3652 | 48.4627 | -496.2807
2039-11-26 19:01 | -2233.63 | 6.6648 | 45.0878 | 48.4627 | -654.6123
2039-11-27 20:01 | -3437.77 | 6.6648 | 44.4206 | 48.4627 | -1007.5109
2039-11-28 21:01 | -3869.74 | 6.6648 | 44.0618 | 48.4627 | -1134.1088
2039-11-29 22:01 | -4886.09 | 6.6648 | 43.4297 | 48.4627 | -1431.9716
2039-11-30 23:01 | -5532.19 | 6.6648 | 42.9392 | 48.4627 | -1621.3248
2039-12-02 00:01 | -5744.29 | 6.6648 | 42.6747 | 48.4627 | -1683.4852
2039-12-03 01:01 | -5960.44 | 6.6648 | 42.4422 | 48.4627 | -1746.8325
2039-12-04 02:01 | -5950.58 | 6.6648 | 42.3412 | 48.4627 | -1743.9428
2039-12-05 03:01 | -6203.74 | 6.6648 | 42.1185 | 48.4627 | -1818.1367
2039-12-06 04:01 | -6059.14 | 6.6648 | 42.0943 | 48.4627 | -1775.7586
2039-12-07 05:01 | -5574.31 | 6.6648 | 42.2786 | 48.4627 | -1633.669
2039-12-08 06:01 | -5526 | 6.6648 | 42.299 | 48.4627 | -1619.5107
2039-12-09 07:01 | -4526.3 | 6.6648 | 42.7904 | 48.4627 | -1326.5276
2039-12-10 08:01 | -3285.73 | 6.6648 | 43.4973 | 48.4627 | -962.9524
2039-12-11 09:01 | -1494.13 | 5.3413 | 44.377 | 48.4627 | -437.8863
2039-12-12 10:01 | 0 | 1 | 45.5825 | 48.4627 | 0
2039-12-13 11:01 | 2821.68 | 1 | 57.6826 | 48.4627 | 826.9528
2039-12-14 12:01 | 3246.03 | 1.1025 | 56.2867 | 48.4627 | 951.3175
2039-12-15 13:01 | 3750.27 | 1.2827 | 56.5562 | 48.4627 | 1099.0956
2039-12-16 14:01 | 3927.58 | 1.3289 | 56.9384 | 48.4627 | 1151.0601
2039-12-17 15:01 | 4178.83 | 1.4265 | 57.0783 | 48.4627 | 1224.6942
2039-12-18 16:01 | 2810.69 | 1 | 59.745 | 48.4627 | 823.7319
2039-12-19 17:01 | 2709.41 | 1 | 46.4617 | 48.4627 | 794.0497
2039-12-20 18:01 | -509.383 | 2.465 | 46.7428 | 48.4627 | -149.2854
2039-12-21 19:01 | -1349.12 | 5.1112 | 46.3131 | 48.4627 | -395.388
2039-12-22 20:01 | -2719.42 | 6.6648 | 45.6361 | 48.4627 | -796.9833
2039-12-23 21:01 | -3073 | 6.6648 | 45.2316 | 48.4627 | -900.6074
2039-12-24 22:01 | -4230.28 | 6.6648 | 44.4779 | 48.4627 | -1239.7727
2039-12-25 23:01 | -5073.83 | 6.6648 | 43.8008 | 48.4627 | -1486.9928
2039-12-27 00:01 | -4965.44 | 6.6648 | 43.6325 | 48.4627 | -1455.2268
2039-12-28 01:01 | -5358.93 | 6.6648 | 43.294 | 48.4627 | -1570.5473
2039-12-29 02:01 | -5762.58 | 6.6648 | 42.9491 | 48.4627 | -1688.8455
2039-12-30 03:01 | -5825.51 | 6.6648 | 42.7553 | 48.4627 | -1707.2884
2039-12-31 04:01 | -5843.19 | 6.6648 | 42.6338 | 48.4627 | -1712.4699
2040-01-01 05:01 | -6016.08 | 6.6648 | 42.4548 | 48.4627 | -1763.139
2040-01-02 06:01 | -5129.05 | 6.6648 | 42.826 | 48.4627 | -1503.1762
2040-01-03 07:01 | -3973.48 | 6.6648 | 43.4362 | 48.4627 | -1164.512
2040-01-04 08:01 | -3363.44 | 6.6648 | 43.8619 | 48.4627 | -985.727
2040-01-05 09:01 | -2419.66 | 6.6648 | 44.4418 | 48.4627 | -709.1323
2040-01-06 10:01 | -1156.2 | 4.0543 | 44.8429 | 48.4627 | -338.8488
2040-01-07 11:01 | 0 | 1 | 46.0143 | 48.4627 | 0
2040-01-08 12:01 | 1154.06 | 1 | 45.8417 | 48.4627 | 338.2216
2040-01-09 13:01 | 2976.94 | 1 | 45.4546 | 48.4627 | 872.455
2040-01-10 14:01 | 2934.94 | 1 | 45.798 | 48.4627 | 860.146
2040-01-11 15:01 | 2937.88 | 1 | 46.0006 | 48.4627 | 861.0076
2040-01-12 16:01 | 3153.06 | 1.0685 | 57.1694 | 48.4627 | 924.0707
2040-01-13 17:01 | 2844.89 | 1 | 46.3296 | 48.4627 | 833.755
2040-01-14 18:01 | 182.863 | 1 | 47.3513 | 48.4627 | 53.5919
2040-01-15 19:01 | -430.146 | 2.1851 | 46.5668 | 48.4627 | -126.0633
2040-01-16 20:01 | -994.564 | 3.914 | 46.2568 | 48.4627 | -291.4779
2040-01-17 21:01 | -1348.02 | 4.9573 | 46.1115 | 48.4627 | -395.0657
2040-01-18 22:01 | -1657.69 | 5.9309 | 45.9995 | 48.4627 | -485.821
2040-01-19 23:01 | -3660.43 | 6.6648 | 44.9976 | 48.4627 | -1072.7661
2040-01-21 00:01 | -4226.56 | 6.6648 | 44.481 | 48.4627 | -1238.6825
2040-01-22 01:01 | -4155.01 | 6.6648 | 44.3208 | 48.4627 | -1217.7132
2040-01-23 02:01 | -4652.43 | 6.6648 | 43.9622 | 48.4627 | -1363.4926
2040-01-24 03:01 | -4871.91 | 6.6648 | 43.7132 | 48.4627 | -1427.8159
2040-01-25 04:01 | -4935.8 | 6.6648 | 43.5436 | 48.4627 | -1446.5402
2040-01-26 05:01 | -5161.67 | 6.6648 | 43.341 | 48.4627 | -1512.7361
2040-01-27 06:01 | -4620.5 | 6.6648 | 43.5415 | 48.4627 | -1354.1349
2040-01-28 07:01 | -3625.34 | 6.6648 | 44.0321 | 48.4627 | -1062.4823
2040-01-29 08:01 | -3860.65 | 6.6648 | 43.983 | 48.4627 | -1131.4448
2040-01-30 09:01 | -2960.22 | 6.6648 | 44.4315 | 48.4627 | -867.5548
2040-01-31 10:01 | -1129.14 | 3.9622 | 45.0266 | 48.4627 | -330.9183
2040-02-01 11:01 | -247.442 | 1.1405 | 45.4664 | 48.4627 | -72.5181
2040-02-02 12:01 | 2503.75 | 1 | 45.538 | 48.4627 | 733.7767
2040-02-03 13:01 | 0 | 0 | 46.7462 | 48.4627 | 0
2040-02-04 14:01 | 2956.83 | 1 | 45.7213 | 48.4627 | 866.5613
2040-02-05 15:01 | 2900.85 | 1 | 46.034 | 48.4627 | 850.1552
2040-02-06 16:01 | 2934.66 | 1 | 46.2244 | 48.4627 | 860.0639
2040-02-07 17:01 | 2697.04 | 1 | 46.4301 | 48.4627 | 790.4244
2040-02-08 18:01 | -244.89 | 1.5621 | 46.8896 | 48.4627 | -71.7702
2040-02-09 19:01 | -812.581 | 3.3422 | 46.428 | 48.4627 | -238.144
2040-02-10 20:01 | -1377.28 | 5.119 | 46.2021 | 48.4627 | -403.6409
2040-02-11 21:01 | -2040.32 | 6.6648 | 45.9754 | 48.4627 | -597.9588
2040-02-12 22:01 | -2687.26 | 6.6648 | 45.5061 | 48.4627 | -787.5582
2040-02-13 23:01 | -4269.75 | 6.6648 | 44.546 | 48.4627 | -1251.3402
2040-02-15 00:01 | -4754.89 | 6.6648 | 44.0596 | 48.4627 | -1393.5207
2040-02-16 01:01 | -5270.09 | 6.6648 | 43.6216 | 48.4627 | -1544.5109
2040-02-17 02:01 | -5696.83 | 6.6648 | 43.2249 | 48.4627 | -1669.5761
2040-02-18 03:01 | -5876.78 | 6.6648 | 42.9574 | 48.4627 | -1722.3142
2040-02-19 04:01 | -5965.69 | 6.6648 | 42.7593 | 48.4627 | -1748.3712
2040-02-20 05:01 | -5798.73 | 6.6648 | 42.7293 | 48.4627 | -1699.44
2040-02-21 06:01 | -5797.16 | 6.6648 | 42.6667 | 48.4627 | -1698.9799
2040-02-22 07:01 | -5394.87 | 6.6648 | 42.8094 | 48.4627 | -1581.0803
2040-02-23 08:01 | -5068.88 | 6.6648 | 42.96 | 48.4627 | -1485.5421
2040-02-24 09:01 | -4421.36 | 6.6648 | 43.2919 | 48.4627 | -1295.7727
2040-02-25 10:01 | -4023.28 | 6.6648 | 43.5322 | 48.4627 | -1179.107
2040-02-26 11:01 | -1675.54 | 6.0102 | 44.6795 | 48.4627 | -491.0523
2040-02-27 12:01 | -1513.11 | 5.3857 | 44.9037 | 48.4627 | -443.4488
2040-02-28 13:01 | -812.918 | 2.9636 | 45.0701 | 48.4627 | -238.2427
2040-02-29 14:01 | -208.907 | 1.1238 | 45.5051 | 48.4627 | -61.2246
2040-03-01 15:01 | 61.0943 | 1 | 46.2686 | 48.4627 | 17.905
2040-03-02 16:01 | -762.518 | 3.3041 | 45.6338 | 48.4627 | -223.472
2040-03-03 17:01 | -1225.13 | 4.6413 | 45.5076 | 48.4627 | -359.0502
2040-03-04 18:01 | -2053.62 | 6.6648 | 45.3429 | 48.4627 | -601.8566
2040-03-05 19:01 | -2868.65 | 6.6648 | 44.8603 | 48.4627 | -840.7183
2040-03-06 20:01 | -3769.84 | 6.6648 | 44.2917 | 48.4627 | -1104.831
2040-03-07 21:01 | -4223.72 | 6.6648 | 43.9107 | 48.4627 | -1237.8501
2040-03-08 22:01 | -5277.44 | 6.6648 | 43.2513 | 48.4627 | -1546.665
2040-03-09 23:01 | -5549.95 | 6.6648 | 42.9279 | 48.4627 | -1626.5298
2040-03-11 00:01 | -5805.86 | 6.6648 | 42.6566 | 48.4627 | -1701.5296
2040-03-12 01:01 | -6042.79 | 6.6648 | 42.417 | 48.4627 | -1770.9669
2040-03-13 02:01 | -6293.16 | 6.6648 | 42.1771 | 48.4627 | -1844.3431
2040-03-14 03:01 | -6232.24 | 6.6648 | 42.0941 | 48.4627 | -1826.4892
2040-03-15 04:01 | -5916.2 | 6.6648 | 42.1877 | 48.4627 | -1733.8671
2040-03-16 05:01 | -5421.58 | 6.6648 | 42.4146 | 48.4627 | -1588.9083
2040-03-17 06:01 | -5479.55 | 6.6648 | 42.4034 | 48.4627 | -1605.8976
2040-03-18 07:01 | -5422.79 | 6.6648 | 42.4219 | 48.4627 | -1589.2629
2040-03-19 08:01 | -5426.38 | 6.6648 | 42.4146 | 48.4627 | -1590.315
2040-03-20 09:01 | -4792.11 | 6.6648 | 42.7269 | 48.4627 | -1404.4288
2040-03-21 10:01 | -4233.31 | 6.6648 | 43.0577 | 48.4627 | -1240.6607
2040-03-22 11:01 | -3772.28 | 6.6648 | 43.3471 | 48.4627 | -1105.5461
2040-03-23 12:01 | -3669.44 | 6.6648 | 43.4565 | 48.4627 | -1075.4067
2040-03-24 13:01 | -3580.35 | 6.6648 | 43.5393 | 48.4627 | -1049.297
2040-03-25 14:01 | -3280.79 | 6.6648 | 43.7158 | 48.4627 | -961.5046
2040-03-26 15:01 | -2459.42 | 6.6648 | 44.1688 | 48.4627 | -720.7849
2040-03-27 16:01 | -2154.04 | 6.6648 | 44.4178 | 48.4627 | -631.2868
2040-03-28 17:01 | -1939.69 | 6.6648 | 44.6009 | 48.4627 | -568.467
2040-03-29 18:01 | -2333.99 | 6.6648 | 44.4745 | 48.4627 | -684.0249
2040-03-30 19:01 | -2917.7 | 6.6648 | 44.2009 | 48.4627 | -855.0935
2040-03-31 20:01 | -3884.32 | 6.6648 | 43.6879 | 48.4627 | -1138.3818
2040-04-01 21:01 | -4184.92 | 6.6648 | 43.4381 | 48.4627 | -1226.479
2040-04-02 22:01 | -4982.08 | 6.6648 | 42.9579 | 48.4627 | -1460.1035
2040-04-03 23:01 | -5249.69 | 6.6648 | 42.7036 | 48.4627 | -1538.5323
2040-04-05 00:01 | -5286.08 | 6.6648 | 42.5888 | 48.4627 | -1549.1971
2040-04-06 01:01 | -5302.97 | 6.6648 | 42.5225 | 48.4627 | -1554.1471
2040-04-07 02:01 | -5128.23 | 6.6648 | 42.5764 | 48.4627 | -1502.9359
2040-04-08 03:01 | -4913.88 | 6.6648 | 42.6675 | 48.4627 | -1440.1161
2040-04-09 04:01 | -4565.48 | 6.6648 | 42.8507 | 48.4627 | -1338.0101
2040-04-10 05:01 | -4038.9 | 6.6648 | 43.1461 | 48.4627 | -1183.6847
2040-04-11 06:01 | -3988.85 | 6.6648 | 43.2336 | 48.4627 | -1169.0165
2040-04-12 07:01 | -3932.45 | 6.6648 | 43.3008 | 48.4627 | -1152.4873
2040-04-13 08:01 | -4469.09 | 6.6648 | 43.0599 | 48.4627 | -1309.761
2040-04-14 09:01 | -4144.06 | 6.6648 | 43.1946 | 48.4627 | -1214.5041
2040-04-15 10:01 | -3892.66 | 6.6648 | 43.3397 | 48.4627 | -1140.826
2040-04-16 11:01 | -3067.87 | 6.6648 | 43.7865 | 48.4627 | -899.1039
2040-04-17 12:01 | -2576.8 | 6.6648 | 44.1218 | 48.4627 | -755.1855
2040-04-18 13:01 | -2741.82 | 6.6648 | 44.1266 | 48.4627 | -803.5481
2040-04-19 14:01 | -2738.71 | 6.6648 | 44.1652 | 48.4627 | -802.6367
2040-04-20 15:01 | -1881.25 | 6.6648 | 44.6226 | 48.4627 | -551.34
2040-04-21 16:01 | -1732.77 | 6.1124 | 44.7197 | 48.4627 | -507.8248
2040-04-22 17:01 | -1528.88 | 5.4406 | 44.7932 | 48.4627 | -448.0705
2040-04-23 18:01 | -1814.74 | 6.5427 | 44.8627 | 48.4627 | -531.8478
2040-04-24 19:01 | -2074.08 | 6.6648 | 44.7724 | 48.4627 | -607.8528
2040-04-25 20:01 | -2986.41 | 6.6648 | 44.3251 | 48.4627 | -875.2304
2040-04-26 21:01 | -3219.57 | 6.6648 | 44.1379 | 48.4627 | -943.5628
2040-04-27 22:01 | -4016.98 | 6.6648 | 43.6859 | 48.4627 | -1177.2606
2040-04-28 23:01 | -4225.58 | 6.6648 | 43.4818 | 48.4627 | -1238.3953
2040-04-30 00:01 | -4299.91 | 6.6648 | 43.3663 | 48.4627 | -1260.1792
2040-05-01 01:01 | -4285.98 | 6.6648 | 43.323 | 48.4627 | -1256.0967
2040-05-02 02:01 | -4264.77 | 6.6648 | 43.3083 | 48.4627 | -1249.8807
2040-05-03 03:01 | -4290.81 | 6.6648 | 43.2687 | 48.4627 | -1257.5123
2040-05-04 04:01 | -4141.35 | 6.6648 | 43.3244 | 48.4627 | -1213.7099
2040-05-05 05:01 | -3686.26 | 6.6648 | 43.5496 | 48.4627 | -1080.3362
2040-05-06 06:01 | -3663.82 | 6.6648 | 43.5961 | 48.4627 | -1073.7596
2040-05-07 07:01 | -3665.45 | 6.6648 | 43.6096 | 48.4627 | -1074.2374
2040-05-08 08:01 | -3966.48 | 6.6648 | 43.4675 | 48.4627 | -1162.4605
2040-05-09 09:01 | -3654.53 | 6.6648 | 43.605 | 48.4627 | -1071.037
2040-05-10 10:01 | -3100 | 6.6648 | 43.908 | 48.4627 | -908.5203
2040-05-11 11:01 | -2506.24 | 6.6648 | 44.2673 | 48.4627 | -734.5064
2040-05-12 12:01 | -2270.07 | 6.6648 | 44.4671 | 48.4627 | -665.2918
2040-05-13 13:01 | -2200.29 | 6.6648 | 44.5719 | 48.4627 | -644.8413
2040-05-14 14:01 | -2090.38 | 6.6648 | 44.6809 | 48.4627 | -612.6299
2040-05-15 15:01 | -1536.97 | 5.4081 | 44.8246 | 48.4627 | -450.4414
2040-05-16 16:01 | -1407.95 | 5.082 | 44.9303 | 48.4627 | -412.6294
2040-05-17 17:01 | -1585.37 | 5.7507 | 44.9899 | 48.4627 | -464.6261
2040-05-18 18:01 | -2333.27 | 6.6648 | 44.7579 | 48.4627 | -683.8139
2040-05-19 19:01 | -2758.13 | 6.6648 | 44.4945 | 48.4627 | -808.3281
2040-05-20 20:01 | -3788.26 | 6.6648 | 43.9239 | 48.4627 | -1110.2294
2040-05-21 21:01 | -4103.71 | 6.6648 | 43.6429 | 48.4627 | -1202.6787
2040-05-22 22:01 | -4946.19 | 6.6648 | 43.1146 | 48.4627 | -1449.5852
2040-05-23 23:01 | -5215.54 | 6.6648 | 42.8352 | 48.4627 | -1528.5239
2040-05-25 00:01 | -5349.23 | 6.6648 | 42.6523 | 48.4627 | -1567.7046
2040-05-26 01:01 | -5150.14 | 6.6648 | 42.6648 | 48.4627 | -1509.357
2040-05-27 02:01 | -5426.39 | 6.6648 | 42.4827 | 48.4627 | -1590.3179
2040-05-28 03:01 | -5279.52 | 6.6648 | 42.4844 | 48.4627 | -1547.2746
2040-05-29 04:01 | -5100.16 | 6.6648 | 42.5351 | 48.4627 | -1494.7093
2040-05-30 05:01 | -4663.13 | 6.6648 | 42.7378 | 48.4627 | -1366.6285
2040-05-31 06:01 | -4640.89 | 6.6648 | 42.7691 | 48.4627 | -1360.1106
2040-06-01 07:01 | -3929.67 | 6.6648 | 43.131 | 48.4627 | -1151.6726
2040-06-02 08:01 | -2746.55 | 6.6648 | 43.8066 | 48.4627 | -804.9343
2040-06-03 09:01 | -870.976 | 3.0642 | 44.3954 | 48.4627 | -255.2579
2040-06-04 10:01 | 2232.61 | 1 | 44.8753 | 48.4627 | 654.3134
2040-06-05 11:01 | 3122.64 | 1.0206 | 56.4896 | 48.4627 | 915.1554
2040-06-06 12:01 | 4134.47 | 1.3618 | 56.7434 | 48.4627 | 1211.6935
2040-06-07 13:01 | 4378.71 | 1.4411 | 57.0972 | 48.4627 | 1283.2732
2040-06-08 14:01 | 4557.57 | 1.4633 | 57.6424 | 48.4627 | 1335.6919
2040-06-09 15:01 | 4976.41 | 1.5946 | 57.8959 | 48.4627 | 1458.4418
2040-06-10 16:01 | 3090.23 | 1 | 59.2082 | 48.4627 | 905.657
2040-06-11 17:01 | 2885.68 | 1 | 46.5487 | 48.4627 | 845.7093
2040-06-12 18:01 | -350.298 | 1.9132 | 46.9393 | 48.4627 | -102.6622
2040-06-13 19:01 | -786.757 | 3.2134 | 46.4842 | 48.4627 | -230.5757
2040-06-14 20:01 | -1955.2 | 6.6648 | 46.1643 | 48.4627 | -573.0126
2040-06-15 21:01 | -2670.64 | 6.6648 | 45.6071 | 48.4627 | -782.6873
2040-06-16 22:01 | -3211.04 | 6.6648 | 45.1394 | 48.4627 | -941.0629
2040-06-17 23:01 | -3847.69 | 6.6648 | 44.6259 | 48.4627 | -1127.6466
2040-06-19 00:01 | -3923.55 | 6.6648 | 44.4207 | 48.4627 | -1149.879
2040-06-20 01:01 | -4063.94 | 6.6648 | 44.2194 | 48.4627 | -1191.0232
2040-06-21 02:01 | -4135.31 | 6.6648 | 44.0772 | 48.4627 | -1211.9397
2040-06-22 03:01 | -4164.37 | 6.6648 | 43.9649 | 48.4627 | -1220.4564
2040-06-23 04:01 | -4044.47 | 6.6648 | 43.9548 | 48.4627 | -1185.3172
2040-06-24 05:01 | -4047.5 | 6.6648 | 43.9052 | 48.4627 | -1186.2052
2040-06-25 06:01 | -3476.52 | 6.6648 | 44.1708 | 48.4627 | -1018.8674
2040-06-26 07:01 | -2892.31 | 6.6648 | 44.4986 | 48.4627 | -847.6524
2040-06-27 08:01 | -2266.95 | 6.6648 | 44.8873 | 48.4627 | -664.3775
2040-06-28 09:01 | -812.427 | 2.8124 | 45.1488 | 48.4627 | -238.0989
2040-06-29 10:01 | 2216.42 | 1 | 45.5535 | 48.4627 | 649.5686
2040-06-30 11:01 | 2938.04 | 1 | 57.6231 | 48.4627 | 861.0545
2040-07-01 12:01 | 3918.66 | 1.3171 | 57.0675 | 48.4627 | 1148.4459
2040-07-02 13:01 | 4047.13 | 1.3965 | 57.086 | 48.4627 | 1186.0967
2040-07-03 14:01 | 4207.4 | 1.4664 | 57.2109 | 48.4627 | 1233.0672
2040-07-04 15:01 | 4203.43 | 1.4341 | 57.6007 | 48.4627 | 1231.9037
2040-07-05 16:01 | 4083 | 1.4522 | 57.3248 | 48.4627 | 1196.6092
2040-07-06 17:01 | 2740.61 | 1 | 61.8115 | 48.4627 | 803.1935
2040-07-07 18:01 | 2524.92 | 1 | 47.0215 | 48.4627 | 739.981
2040-07-08 19:01 | -696.473 | 3.1001 | 47.132 | 48.4627 | -204.1161
2040-07-09 20:01 | -1495.7 | 5.5179 | 46.7096 | 48.4627 | -438.3464
2040-07-10 21:01 | -1983.41 | 6.6648 | 46.4045 | 48.4627 | -581.2801
2040-07-11 22:01 | -2804.19 | 6.6648 | 45.8185 | 48.4627 | -821.827
2040-07-12 23:01 | -4346.33 | 6.6648 | 44.8441 | 48.4627 | -1273.7836
2040-07-14 00:01 | -4628.99 | 6.6648 | 44.4008 | 48.4627 | -1356.6231
2040-07-15 01:01 | -5124.48 | 6.6648 | 43.9568 | 48.4627 | -1501.8368
2040-07-16 02:01 | -5423.09 | 6.6648 | 43.6265 | 48.4627 | -1589.3508
2040-07-17 03:01 | -5796.01 | 6.6648 | 43.2638 | 48.4627 | -1698.6429
2040-07-18 04:01 | -5855.76 | 6.6648 | 43.0616 | 48.4627 | -1716.1538
2040-07-19 05:01 | -5662.07 | 6.6648 | 43.0401 | 48.4627 | -1659.3889
2040-07-20 06:01 | -5852.86 | 6.6648 | 42.8568 | 48.4627 | -1715.3039
2040-07-21 07:01 | -4178.72 | 6.6648 | 43.6284 | 48.4627 | -1224.6619
2040-07-22 08:01 | -2559.28 | 6.6648 | 44.546 | 48.4627 | -750.0509
2040-07-23 09:01 | -1822.7 | 6.4341 | 45.0737 | 48.4627 | -534.1806
2040-07-24 10:01 | -802.93 | 2.7971 | 45.1971 | 48.4627 | -235.3156
2040-07-25 11:01 | 0 | 0 | 46.3429 | 48.4627 | 0
2040-07-26 12:01 | 202.656 | 1 | 46.4611 | 48.4627 | 59.3926
2040-07-27 13:01 | 1505.19 | 1 | 46.141 | 48.4627 | 441.1276
2040-07-28 14:01 | 0 | 0 | 46.8528 | 48.4627 | 0
2040-07-29 15:01 | -420.128 | 2.1621 | 46.175 | 48.4627 | -123.1274
2040-07-30 16:01 | -874.618 | 3.516 | 45.949 | 48.4627 | -256.3252
2040-07-31 17:01 | 0 | 0 | 46.7534 | 48.4627 | 0
2040-08-01 18:01 | -667.689 | 2.9561 | 46.0684 | 48.4627 | -195.6803
2040-08-02 19:01 | -1300.15 | 4.9159 | 45.9104 | 48.4627 | -381.0364
2040-08-03 20:01 | -1871.29 | 6.6648 | 45.791 | 48.4627 | -548.421
2040-08-04 21:01 | -2401.61 | 6.6648 | 45.4476 | 48.4627 | -703.8424
2040-08-05 22:01 | -2846.24 | 6.6648 | 45.1394 | 48.4627 | -834.1506
2040-08-06 23:01 | -3026.89 | 6.6648 | 44.946 | 48.4627 | -887.0939
2040-08-08 00:01 | -4304.83 | 6.6648 | 44.2186 | 48.4627 | -1261.6211
2040-08-09 01:01 | -4753.08 | 6.6648 | 43.8081 | 48.4627 | -1392.9902
2040-08-10 02:01 | -4745.83 | 6.6648 | 43.6659 | 48.4627 | -1390.8655
2040-08-11 03:01 | -4748.89 | 6.6648 | 43.583 | 48.4627 | -1391.7623
2040-08-12 04:01 | -4785.19 | 6.6648 | 43.5045 | 48.4627 | -1402.4008
2040-08-13 05:01 | -4621.63 | 6.6648 | 43.5187 | 48.4627 | -1354.466
2040-08-14 06:01 | -4198.71 | 6.6648 | 43.7082 | 48.4627 | -1230.5204
2040-08-15 07:01 | -3900.66 | 6.6648 | 43.8731 | 48.4627 | -1143.1706
2040-08-16 08:01 | -2680.91 | 6.6648 | 44.5121 | 48.4627 | -785.6972
2040-08-17 09:01 | -2127.88 | 6.6648 | 44.9052 | 48.4627 | -623.6201
2040-08-18 10:01 | -738.203 | 2.5494 | 45.1041 | 48.4627 | -216.3459
2040-08-19 11:01 | 1311.87 | 1 | 45.8167 | 48.4627 | 384.4711
2040-08-20 12:01 | 3089.59 | 1 | 45.5143 | 48.4627 | 905.4694
2040-08-21 13:01 | 3046.32 | 1 | 45.884 | 48.4627 | 892.7883
2040-08-22 14:01 | 2941.45 | 1 | 46.1321 | 48.4627 | 862.0539
2040-08-23 15:01 | 1445.36 | 1 | 46.7952 | 48.4627 | 423.5932
2040-08-24 16:01 | 211.243 | 1 | 47.2068 | 48.4627 | 61.9092
2040-08-25 17:01 | -100.114 | 1.0226 | 46.8445 | 48.4627 | -29.3405
2040-08-26 18:01 | -186.405 | 1.2527 | 46.6005 | 48.4627 | -54.6299
2040-08-27 19:01 | -515.612 | 2.3578 | 46.3356 | 48.4627 | -151.111
2040-08-28 20:01 | -918.611 | 3.6358 | 46.1692 | 48.4627 | -269.2183
2040-08-29 21:01 | -1892.13 | 6.6648 | 46.013 | 48.4627 | -554.5286
2040-08-30 22:01 | -2519.26 | 6.6648 | 45.5858 | 48.4627 | -738.3222
2040-08-31 23:01 | -3472.99 | 6.6648 | 44.9741 | 48.4627 | -1017.8329
2040-09-02 00:01 | -3839.84 | 6.6648 | 44.6102 | 48.4627 | -1125.346
2040-09-03 01:01 | -4316.77 | 6.6648 | 44.2174 | 48.4627 | -1265.1204
2040-09-04 02:01 | -4698.26 | 6.6648 | 43.8733 | 48.4627 | -1376.9241
2040-09-05 03:01 | -4683.21 | 6.6648 | 43.7512 | 48.4627 | -1372.5134
2040-09-06 04:01 | -4640.15 | 6.6648 | 43.6928 | 48.4627 | -1359.8937
2040-09-07 05:01 | -4635.55 | 6.6648 | 43.6442 | 48.4627 | -1358.5456
2040-09-08 06:01 | -4223.51 | 6.6648 | 43.8066 | 48.4627 | -1237.7886
2040-09-09 07:01 | -4166.26 | 6.6648 | 43.8319 | 48.4627 | -1221.0103
2040-09-10 08:01 | -4098.85 | 6.6648 | 43.8505 | 48.4627 | -1201.2544
2040-09-11 09:01 | -4217.71 | 6.6648 | 43.7695 | 48.4627 | -1236.0888
2040-09-12 10:01 | -3487.06 | 6.6648 | 44.098 | 48.4627 | -1021.9564
2040-09-13 11:01 | -2986.07 | 6.6648 | 44.3794 | 48.4627 | -875.1307
2040-09-14 12:01 | -2558.25 | 6.6648 | 44.6325 | 48.4627 | -749.7491
2040-09-15 13:01 | -2379.05 | 6.6648 | 44.7621 | 48.4627 | -697.2307
2040-09-16 14:01 | -2387.12 | 6.6648 | 44.7896 | 48.4627 | -699.5958
2040-09-17 15:01 | -2153.17 | 6.6648 | 44.9297 | 48.4627 | -631.0318
2040-09-18 16:01 | -1450.92 | 5.0805 | 45.0913 | 48.4627 | -425.2227
2040-09-19 17:01 | -1213.49 | 4.409 | 45.2134 | 48.4627 | -355.6388
2040-09-20 18:01 | -1091.18 | 4.0508 | 45.3049 | 48.4627 | -319.7933
2040-09-21 19:01 | -1394.44 | 5.1627 | 45.3603 | 48.4627 | -408.67
2040-09-22 20:01 | -1645.09 | 5.9209 | 45.3558 | 48.4627 | -482.1283
2040-09-23 21:01 | -2862.38 | 6.6648 | 44.8515 | 48.4627 | -838.8808
2040-09-24 22:01 | -3212.75 | 6.6648 | 44.5684 | 48.4627 | -941.5641
2040-09-25 23:01 | -4179.31 | 6.6648 | 43.9909 | 48.4627 | -1224.8349
2040-09-27 00:01 | -4524.58 | 6.6648 | 43.6778 | 48.4627 | -1326.0235
2040-09-28 01:01 | -4445.25 | 6.6648 | 43.6023 | 48.4627 | -1302.7742
2040-09-29 02:01 | -4563.48 | 6.6648 | 43.4778 | 48.4627 | -1337.424
2040-09-30 03:01 | -4463.7 | 6.6648 | 43.476 | 48.4627 | -1308.1813
2040-10-01 04:01 | -4202.66 | 6.6648 | 43.5687 | 48.4627 | -1231.6781
2040-10-02 05:01 | -3997.37 | 6.6648 | 43.6706 | 48.4627 | -1171.5135
2040-10-03 06:01 | -3419.22 | 6.6648 | 43.9708 | 48.4627 | -1002.0745
2040-10-04 07:01 | -3218.75 | 6.6648 | 44.12 | 48.4627 | -943.3225
2040-10-05 08:01 | -3044.78 | 6.6648 | 44.247 | 48.4627 | -892.3369
2040-10-06 09:01 | -3215.23 | 6.6648 | 44.1984 | 48.4627 | -942.2909
2040-10-07 10:01 | -1172.46 | 4.1352 | 44.8707 | 48.4627 | -343.6141
2040-10-08 11:01 | 0 | 1 | 46.032 | 48.4627 | 0
2040-10-09 12:01 | -79.8617 | 0.95151 | 45.9673 | 48.4627 | -23.4052
2040-10-10 13:01 | 2344.85 | 1 | 45.5631 | 48.4627 | 687.2077
2040-10-11 14:01 | 2918.21 | 1 | 45.6872 | 48.4627 | 855.2429
2040-10-12 15:01 | 3014.32 | 1 | 45.9368 | 48.4627 | 883.41
2040-10-13 16:01 | 2889.1 | 1 | 46.1526 | 48.4627 | 846.7116
2040-10-14 17:01 | -255.964 | 1.6088 | 46.7211 | 48.4627 | -75.0156
2040-10-15 18:01 | -571.368 | 2.5127 | 46.3051 | 48.4627 | -167.4514
2040-10-16 19:01 | -1164.47 | 4.4796 | 46.0754 | 48.4627 | -341.2725
2040-10-17 20:01 | -1592.92 | 5.766 | 45.9258 | 48.4627 | -466.8388
2040-10-18 21:01 | -2877.4 | 6.6648 | 45.3016 | 48.4627 | -843.2827
2040-10-19 22:01 | -3463.12 | 6.6648 | 44.802 | 48.4627 | -1014.9403
2040-10-20 23:01 | -4711.55 | 6.6648 | 44.0203 | 48.4627 | -1380.819
2040-10-22 00:01 | -5674.31 | 6.6648 | 43.3248 | 48.4627 | -1662.9761
2040-10-23 01:01 | -6199.66 | 6.6648 | 42.8142 | 48.4627 | -1816.941
2040-10-24 02:01 | -6670.3 | 6.6648 | 42.354 | 48.4627 | -1954.872
2040-10-25 03:01 | -7168.35 | 6.6648 | 41.8986 | 48.4627 | -2100.836
2040-10-26 04:01 | -7235.16 | 6.6648 | 41.6556 | 48.4627 | -2120.4161
2040-10-27 05:01 | -7542.44 | 6.6648 | 41.3603 | 48.4627 | -2210.471
2040-10-28 06:01 | -7022.05 | 6.6648 | 41.4872 | 48.4627 | -2057.9597
2040-10-29 07:01 | -7162.98 | 6.6648 | 41.3527 | 48.4627 | -2099.2622
2040-10-30 08:01 | -6650.36 | 6.6648 | 41.5323 | 48.4627 | -1949.0281
2040-10-31 09:01 | -5462.07 | 6.6648 | 42.1184 | 48.4627 | -1600.7747
2040-11-01 10:01 | -5419.48 | 6.6648 | 42.2133 | 48.4627 | -1588.2928
2040-11-02 11:01 | -5263.8 | 6.6648 | 42.3161 | 48.4627 | -1542.6675
2040-11-03 12:01 | -3703.88 | 6.6648 | 43.1166 | 48.4627 | -1085.5001
2040-11-04 13:01 | -4160.03 | 6.6648 | 43.0302 | 48.4627 | -1219.1844
2040-11-05 14:01 | -4691.72 | 6.6648 | 42.7869 | 48.4627 | -1375.0074
2040-11-06 15:01 | -5400.78 | 6.6648 | 42.3647 | 48.4627 | -1582.8124
2040-11-07 16:01 | -4942.68 | 6.6648 | 42.5 | 48.4627 | -1448.5565
2040-11-08 17:01 | -4816.52 | 6.6648 | 42.5658 | 48.4627 | -1411.5827
2040-11-09 18:01 | -4583.53 | 6.6648 | 42.6699 | 48.4627 | -1343.3
2040-11-10 19:01 | -5040.6 | 6.6648 | 42.4413 | 48.4627 | -1477.254
2040-11-11 20:01 | -5187.86 | 6.6648 | 42.3213 | 48.4627 | -1520.4117
2040-11-12 21:01 | -5961.34 | 6.6648 | 41.8914 | 48.4627 | -1747.0963
2040-11-13 22:01 | -6249.64 | 6.6648 | 41.6465 | 48.4627 | -1831.5887
2040-11-14 23:01 | -6965.5 | 6.6648 | 41.1948 | 48.4627 | -2041.3865
2040-11-16 00:01 | -7256.36 | 6.6648 | 40.9098 | 48.4627 | -2126.6292
2040-11-17 01:01 | -7392.54 | 6.6648 | 40.7257 | 48.4627 | -2166.5396
2040-11-18 02:01 | -7315.31 | 6.6648 | 40.6759 | 48.4627 | -2143.9057
2040-11-19 03:01 | -7226.45 | 6.6648 | 40.6728 | 48.4627 | -2117.8634
2040-11-20 04:01 | -7184.04 | 6.6648 | 40.6556 | 48.4627 | -2105.4343
2040-11-21 05:01 | -6763.82 | 6.6648 | 40.8408 | 48.4627 | -1982.28
2040-11-22 06:01 | -6586.28 | 6.6648 | 40.9387 | 48.4627 | -1930.2481
2040-11-23 07:01 | -6542.28 | 6.6648 | 40.9728 | 48.4627 | -1917.353
2040-11-24 08:01 | -6473.76 | 6.6648 | 41.0021 | 48.4627 | -1897.2718
2040-11-25 09:01 | -7061.84 | 6.6648 | 40.6958 | 48.4627 | -2069.621
2040-11-26 10:01 | -5582.05 | 6.6648 | 41.3782 | 48.4627 | -1635.9374
2040-11-27 11:01 | -3143.04 | 6.6648 | 42.7105 | 48.4627 | -921.1341
2040-11-28 12:01 | -2604.47 | 6.6648 | 43.2573 | 48.4627 | -763.2948
2040-11-29 13:01 | -3679.89 | 6.6648 | 42.896 | 48.4627 | -1078.4693
2040-11-30 14:01 | -3494.72 | 6.6648 | 42.9886 | 48.4627 | -1024.2013
2040-12-01 15:01 | -4169.75 | 6.6648 | 42.7047 | 48.4627 | -1222.0331
2040-12-02 16:01 | -4277.65 | 6.6648 | 42.6373 | 48.4627 | -1253.6555
2040-12-03 17:01 | -4416.36 | 6.6648 | 42.53 | 48.4627 | -1294.3074
2040-12-04 18:01 | -4399.15 | 6.6648 | 42.5001 | 48.4627 | -1289.2636
2040-12-05 19:01 | -4817.41 | 6.6648 | 42.2794 | 48.4627 | -1411.8435
2040-12-06 20:01 | -5110.62 | 6.6648 | 42.0833 | 48.4627 | -1497.7749
2040-12-07 21:01 | -5933.73 | 6.6648 | 41.628 | 48.4627 | -1739.0046
2040-12-08 22:01 | -6096.18 | 6.6648 | 41.4443 | 48.4627 | -1786.614
2040-12-09 23:01 | -7271.99 | 6.6648 | 40.7579 | 48.4627 | -2131.2099
2040-12-11 00:01 | -7954.98 | 6.6648 | 40.2325 | 48.4627 | -2331.3745
2040-12-12 01:01 | -8191.08 | 6.6648 | 39.9382 | 48.4627 | -2400.5686
2040-12-13 02:01 | -8541.15 | 6.6648 | 39.6244 | 48.4627 | -2503.164
2040-12-14 03:01 | -8610.85 | 6.6648 | 39.4653 | 48.4627 | -2523.591
2040-12-15 04:01 | -8762.88 | 6.6648 | 39.281 | 48.4627 | -2568.1466
2040-12-16 05:01 | -8842.53 | 6.6648 | 39.1489 | 48.4627 | -2591.4897
2040-12-17 06:01 | -8960.8 | 6.6648 | 39.006 | 48.4627 | -2626.1512
2040-12-18 07:01 | -8167.8 | 6.6648 | 39.331 | 48.4627 | -2393.7459
2040-12-19 08:01 | -7705.65 | 6.6648 | 39.5786 | 48.4627 | -2258.3031
2040-12-20 09:01 | -8785.08 | 6.6648 | 39.0604 | 48.4627 | -2574.6528
2040-12-21 10:01 | -8699.02 | 6.6648 | 38.9865 | 48.4627 | -2549.4311
2040-12-22 11:01 | -8705.41 | 6.6648 | 38.9072 | 48.4627 | -2551.3038
2040-12-23 12:01 | -8555.75 | 6.6648 | 38.931 | 48.4627 | -2507.4428
2040-12-24 13:01 | -8556.79 | 6.6648 | 38.8845 | 48.4627 | -2507.7476
2040-12-25 14:01 | -8488.31 | 6.6648 | 38.8625 | 48.4627 | -2487.6781
2040-12-26 15:01 | -8270.45 | 6.6648 | 38.9415 | 48.4627 | -2423.8296
2040-12-27 16:01 | -8338.02 | 6.6648 | 38.8931 | 48.4627 | -2443.6324
2040-12-28 17:01 | -6732.84 | 6.6648 | 39.6835 | 48.4627 | -1973.2006
2040-12-29 18:01 | -7004.85 | 6.6648 | 39.6706 | 48.4627 | -2052.9189
2040-12-30 19:01 | -7078.16 | 6.6648 | 39.6645 | 48.4627 | -2074.4039
2040-12-31 20:01 | -7146.06 | 6.6648 | 39.6236 | 48.4627 | -2094.3035
2041-01-01 21:01 | -7349.75 | 6.6648 | 39.5285 | 48.4627 | -2153.9991
2041-01-02 22:01 | -7446.03 | 6.6648 | 39.4756 | 48.4627 | -2182.216
2041-01-03 23:01 | -7505.55 | 6.6648 | 39.4238 | 48.4627 | -2199.6596
2041-01-05 00:01 | -8880.03 | 6.6648 | 38.7103 | 48.4627 | -2602.4799
2041-01-06 01:01 | -8969.05 | 6.6648 | 38.5245 | 48.4627 | -2628.5691
2041-01-07 02:01 | -8973.11 | 6.6648 | 38.4346 | 48.4627 | -2629.7589
2041-01-08 03:01 | -8949.79 | 6.6648 | 38.3975 | 48.4627 | -2622.9245
2041-01-09 04:01 | -8831.67 | 6.6648 | 38.416 | 48.4627 | -2588.307
2041-01-10 05:01 | -8776.45 | 6.6648 | 38.4001 | 48.4627 | -2572.1236
2041-01-11 06:01 | -8651.11 | 6.6648 | 38.4438 | 48.4627 | -2535.3901
2041-01-12 07:01 | -7943.54 | 6.6648 | 38.79 | 48.4627 | -2328.0218
2041-01-13 08:01 | -6575.49 | 6.6648 | 39.5349 | 48.4627 | -1927.0859
2041-01-14 09:01 | -7087.53 | 6.6648 | 39.4271 | 48.4627 | -2077.15
2041-01-15 10:01 | -7741.55 | 6.6648 | 39.1124 | 48.4627 | -2268.8243
2041-01-16 11:01 | -7676.87 | 6.6648 | 39.0798 | 48.4627 | -2249.8685
2041-01-17 12:01 | -7860.72 | 6.6648 | 38.9734 | 48.4627 | -2303.7496
2041-01-18 13:01 | -7849.33 | 6.6648 | 38.9506 | 48.4627 | -2300.4115
2041-01-19 14:01 | -7982.29 | 6.6648 | 38.8374 | 48.4627 | -2339.3783
2041-01-20 15:01 | -7904.52 | 6.6648 | 38.8312 | 48.4627 | -2316.5861
2041-01-21 16:01 | -7748.55 | 6.6648 | 38.8888 | 48.4627 | -2270.8758
2041-01-22 17:01 | -6387.87 | 6.6648 | 39.5741 | 48.4627 | -1872.0999
2041-01-23 18:01 | -6677.52 | 6.6648 | 39.5467 | 48.4627 | -1956.9879
2041-01-24 19:01 | -6965.31 | 6.6648 | 39.4291 | 48.4627 | -2041.3309
2041-01-25 20:01 | -7293.5 | 6.6648 | 39.2342 | 48.4627 | -2137.5138
2041-01-26 21:01 | -7570.21 | 6.6648 | 39.0595 | 48.4627 | -2218.6095
2041-01-27 22:01 | -7774.32 | 6.6648 | 38.9202 | 48.4627 | -2278.4283
2041-01-28 23:01 | -7834.58 | 6.6648 | 38.8363 | 48.4627 | -2296.0887
2041-01-30 00:01 | -9061.93 | 6.6648 | 38.1795 | 48.4627 | -2655.7895
2041-01-31 01:01 | -9096.02 | 6.6648 | 38.0246 | 48.4627 | -2665.7803
2041-02-01 02:01 | -9275.43 | 6.6648 | 37.8532 | 48.4627 | -2718.3602
2041-02-02 03:01 | -9105.1 | 6.6648 | 37.8792 | 48.4627 | -2668.4414
2041-02-03 04:01 | -8940.85 | 6.6648 | 37.9295 | 48.4627 | -2620.3045
2041-02-04 05:01 | -8819.49 | 6.6648 | 37.9613 | 48.4627 | -2584.7374
2041-02-05 06:01 | -8322.83 | 6.6648 | 38.2075 | 48.4627 | -2439.1807
2041-02-06 07:01 | -8360.64 | 6.6648 | 38.2177 | 48.4627 | -2450.2617
2041-02-07 08:01 | -8409.05 | 6.6648 | 38.1923 | 48.4627 | -2464.4493
2041-02-08 09:01 | -8872.9 | 6.6648 | 37.9407 | 48.4627 | -2600.3903
2041-02-09 10:01 | -8820.35 | 6.6648 | 37.9104 | 48.4627 | -2584.9894
2041-02-10 11:01 | -8771.99 | 6.6648 | 37.9011 | 48.4627 | -2570.8165
2041-02-11 12:01 | -8684.08 | 6.6648 | 37.9263 | 48.4627 | -2545.0526
2041-02-12 13:01 | -8597.22 | 6.6648 | 37.9561 | 48.4627 | -2519.5965
2041-02-13 14:01 | -8272.73 | 6.6648 | 38.1153 | 48.4627 | -2424.4978
2041-02-14 15:01 | -7418.72 | 6.6648 | 38.5779 | 48.4627 | -2174.2122
2041-02-15 16:01 | -7300.06 | 6.6648 | 38.7305 | 48.4627 | -2139.4364
2041-02-16 17:01 | -7625.05 | 6.6648 | 38.6132 | 48.4627 | -2234.6816
2041-02-17 18:01 | -7521.3 | 6.6648 | 38.6541 | 48.4627 | -2204.2754
2041-02-18 19:01 | -8245.54 | 6.6648 | 38.294 | 48.4627 | -2416.5292
2041-02-19 20:01 | -8716.09 | 6.6648 | 37.9927 | 48.4627 | -2554.4338
2041-02-20 21:01 | -9648.2 | 6.6648 | 37.4289 | 48.4627 | -2827.6083
2041-02-21 22:01 | -9987.95 | 6.6648 | 37.1122 | 48.4627 | -2927.1792
2041-02-22 23:01 | -10568.1 | 6.6648 | 36.6963 | 48.4627 | -3097.2044
2041-02-24 00:01 | -11021.9 | 6.6648 | 36.3311 | 48.4627 | -3230.2
2041-02-25 01:01 | -11201 | 6.6648 | 36.106 | 48.4627 | -3282.6891
2041-02-26 02:01 | -11622.6 | 6.6648 | 35.7784 | 48.4627 | -3406.2478
2041-02-27 03:01 | -11924.6 | 6.6648 | 35.4962 | 48.4627 | -3494.7553
2041-02-28 04:01 | -11874.4 | 6.6648 | 35.3904 | 48.4627 | -3480.0431
2041-03-01 05:01 | -11923.1 | 6.6648 | 35.2733 | 48.4627 | -3494.3157
2041-03-02 06:01 | -11662.5 | 6.6648 | 35.3189 | 48.4627 | -3417.9414
2041-03-03 07:01 | -11592.9 | 6.6648 | 35.3005 | 48.4627 | -3397.5436
2041-03-04 08:01 | -10095.1 | 6.6648 | 36.0188 | 48.4627 | -2958.5818
2041-03-05 09:01 | -9009.91 | 6.6648 | 36.6807 | 48.4627 | -2640.544
2041-03-06 10:01 | -7568.63 | 6.6648 | 37.5672 | 48.4627 | -2218.1465
2041-03-07 11:01 | -6363.57 | 6.6648 | 38.3934 | 48.4627 | -1864.9783
2041-03-08 12:01 | -5505.54 | 6.6648 | 39.0709 | 48.4627 | -1613.5145
2041-03-09 13:01 | -5251.63 | 6.6648 | 39.4402 | 48.4627 | -1539.1008
2041-03-10 14:01 | -6694.66 | 6.6648 | 38.8794 | 48.4627 | -1962.0112
2041-03-11 15:01 | -6675.49 | 6.6648 | 38.8736 | 48.4627 | -1956.393
2041-03-12 16:01 | -6451.56 | 6.6648 | 39.0042 | 48.4627 | -1890.7656
2041-03-13 17:01 | -6821.74 | 6.6648 | 38.8681 | 48.4627 | -1999.2546
2041-03-14 18:01 | -6995.83 | 6.6648 | 38.7709 | 48.4627 | -2050.2754
2041-03-15 19:01 | -7639.04 | 6.6648 | 38.4262 | 48.4627 | -2238.7816
2041-03-16 20:01 | -7957.19 | 6.6648 | 38.2151 | 48.4627 | -2332.0222
2041-03-17 21:01 | -8935.87 | 6.6648 | 37.6627 | 48.4627 | -2618.845
2041-03-18 22:01 | -9333.76 | 6.6648 | 37.3262 | 48.4627 | -2735.455
2041-03-19 23:01 | -10109.3 | 6.6648 | 36.8067 | 48.4627 | -2962.7434
2041-03-21 00:01 | -10377.6 | 6.6648 | 36.5116 | 48.4627 | -3041.3743
2041-03-22 01:01 | -10643.9 | 6.6648 | 36.2432 | 48.4627 | -3119.4192
2041-03-23 02:01 | -10583.5 | 6.6648 | 36.166 | 48.4627 | -3101.7177
2041-03-24 03:01 | -10774.7 | 6.6648 | 36.0008 | 48.4627 | -3157.7529
2041-03-25 04:01 | -10636.4 | 6.6648 | 35.9936 | 48.4627 | -3117.2211
2041-03-26 05:01 | -11114.5 | 6.6648 | 35.7066 | 48.4627 | -3257.3384
2041-03-27 06:01 | -10664.3 | 6.6648 | 35.8499 | 48.4627 | -3125.3978
2041-03-28 07:01 | -10997.1 | 6.6648 | 35.6623 | 48.4627 | -3222.9319
2041-03-29 08:01 | -10445.9 | 6.6648 | 35.882 | 48.4627 | -3061.3911
2041-03-30 09:01 | -9826.72 | 6.6648 | 36.2033 | 48.4627 | -2879.9273
2041-03-31 10:01 | -8422 | 6.6648 | 36.9675 | 48.4627 | -2468.2446
2041-04-01 11:01 | -7280.91 | 6.6648 | 37.7042 | 48.4627 | -2133.8241
2041-04-02 12:01 | -6838.61 | 6.6648 | 38.1124 | 48.4627 | -2004.1988
2041-04-03 13:01 | -6597.48 | 6.6648 | 38.3851 | 48.4627 | -1933.5305
2041-04-04 14:01 | -7015.33 | 6.6648 | 38.2934 | 48.4627 | -2055.9903
2041-04-05 15:01 | -7716.18 | 6.6648 | 37.9837 | 48.4627 | -2261.3891
2041-04-06 16:01 | -8068.33 | 6.6648 | 37.7686 | 48.4627 | -2364.5941
2041-04-07 17:01 | -8580.19 | 6.6648 | 37.4625 | 48.4627 | -2514.6055
2041-04-08 18:01 | -8676.53 | 6.6648 | 37.3405 | 48.4627 | -2542.8399
2041-04-09 19:01 | -9335.84 | 6.6648 | 36.9544 | 48.4627 | -2736.0646
2041-04-10 20:01 | -9614.1 | 6.6648 | 36.7197 | 48.4627 | -2817.6146
2041-04-11 21:01 | -10595.2 | 6.6648 | 36.1407 | 48.4627 | -3105.1466
2041-04-12 22:01 | -10883.8 | 6.6648 | 35.8436 | 48.4627 | -3189.7269
2041-04-13 23:01 | -11680.2 | 6.6648 | 35.3102 | 48.4627 | -3423.1287
2041-04-15 00:01 | -11717.6 | 6.6648 | 35.1241 | 48.4627 | -3434.0896
2041-04-16 01:01 | -12035.7 | 6.6648 | 34.842 | 48.4627 | -3527.3155
2041-04-17 02:01 | -11981.9 | 6.6648 | 34.7488 | 48.4627 | -3511.5483
2041-04-18 03:01 | -11738.8 | 6.6648 | 34.7959 | 48.4627 | -3440.3027
2041-04-19 04:01 | -11749.6 | 6.6648 | 34.7493 | 48.4627 | -3443.4678
2041-04-20 05:01 | -11570.4 | 6.6648 | 34.8063 | 48.4627 | -3390.9495
2041-04-21 06:01 | -11216.7 | 6.6648 | 34.9637 | 48.4627 | -3287.2903
2041-04-22 07:01 | -11238.9 | 6.6648 | 34.9672 | 48.4627 | -3293.7964
2041-04-23 08:01 | -9689.58 | 6.6648 | 35.7495 | 48.4627 | -2839.7356
2041-04-24 09:01 | -9432.13 | 6.6648 | 36.0158 | 48.4627 | -2764.2844
2041-04-25 10:01 | -7412.37 | 6.6648 | 37.1382 | 48.4627 | -2172.3512
2041-04-26 11:01 | -6004.84 | 6.6648 | 38.0929 | 48.4627 | -1759.8449
2041-04-27 12:01 | -5115.22 | 6.6648 | 38.8214 | 48.4627 | -1499.123
2041-04-28 13:01 | -5683.36 | 6.6648 | 38.7845 | 48.4627 | -1665.6284
2041-04-29 14:01 | -5299.64 | 6.6648 | 39.085 | 48.4627 | -1553.1712
2041-04-30 15:01 | -5830.36 | 6.6648 | 38.9539 | 48.4627 | -1708.7098
2041-05-01 16:01 | -6480.26 | 6.6648 | 38.6753 | 48.4627 | -1899.1767
2041-05-02 17:01 | -6917.66 | 6.6648 | 38.4321 | 48.4627 | -2027.366
2041-05-03 18:01 | -7115.19 | 6.6648 | 38.2924 | 48.4627 | -2085.2563
2041-05-04 19:01 | -7865.08 | 6.6648 | 37.8993 | 48.4627 | -2305.0274
2041-05-05 20:01 | -8319.06 | 6.6648 | 37.5858 | 48.4627 | -2438.0758
2041-05-06 21:01 | -9420.07 | 6.6648 | 36.946 | 48.4627 | -2760.75
2041-05-07 22:01 | -9856.08 | 6.6648 | 36.5712 | 48.4627 | -2888.5319
2041-05-08 23:01 | -10493.4 | 6.6648 | 36.1089 | 48.4627 | -3075.312
2041-05-10 00:01 | -10920.2 | 6.6648 | 35.7346 | 48.4627 | -3200.3947
2041-05-11 01:01 | -11222.8 | 6.6648 | 35.4381 | 48.4627 | -3289.078
2041-05-12 02:01 | -11083.5 | 6.6648 | 35.3763 | 48.4627 | -3248.2532
2041-05-13 03:01 | -11358.9 | 6.6648 | 35.1611 | 48.4627 | -3328.965
2041-05-14 04:01 | -11291.3 | 6.6648 | 35.1078 | 48.4627 | -3309.1534
2041-05-15 05:01 | -11260.6 | 6.6648 | 35.0646 | 48.4627 | -3300.1561
2041-05-16 06:01 | -10850.6 | 6.6648 | 35.2284 | 48.4627 | -3179.997
2041-05-17 07:01 | -10469.8 | 6.6648 | 35.427 | 48.4627 | -3068.3955
2041-05-18 08:01 | -8766.5 | 6.6648 | 36.3174 | 48.4627 | -2569.2075
2041-05-19 09:01 | -7582.55 | 6.6648 | 37.0951 | 48.4627 | -2222.226
2041-05-20 10:01 | -5722.85 | 6.6648 | 38.245 | 48.4627 | -1677.2018
2041-05-21 11:01 | -4794.49 | 6.6648 | 39.0061 | 48.4627 | -1405.1263
2041-05-22 12:01 | -3631.63 | 6.6648 | 39.8628 | 48.4627 | -1064.3257
2041-05-23 13:01 | -3129.53 | 6.6648 | 40.4102 | 48.4627 | -917.1747
2041-05-24 14:01 | -4392.55 | 6.6648 | 40.0058 | 48.4627 | -1287.3293
2041-05-25 15:01 | -4081.02 | 6.6648 | 40.2169 | 48.4627 | -1196.0289
2041-05-26 16:01 | -4059.07 | 6.6648 | 40.3224 | 48.4627 | -1189.596
2041-05-27 17:01 | -4732.05 | 6.6648 | 40.0815 | 48.4627 | -1386.827
2041-05-28 18:01 | -4679.13 | 6.6648 | 40.115 | 48.4627 | -1371.3176
2041-05-29 19:01 | -5227.5 | 6.6648 | 39.8682 | 48.4627 | -1532.029
2041-05-30 20:01 | -5464.17 | 6.6648 | 39.751 | 48.4627 | -1601.3901
2041-05-31 21:01 | -6386.38 | 6.6648 | 39.2749 | 48.4627 | -1871.6632
2041-06-01 22:01 | -6677.89 | 6.6648 | 39.0407 | 48.4627 | -1957.0964
2041-06-02 23:01 | -7365.17 | 6.6648 | 38.6285 | 48.4627 | -2158.5183
2041-06-04 00:01 | -7830.34 | 6.6648 | 38.2886 | 48.4627 | -2294.8461
2041-06-05 01:01 | -7949.91 | 6.6648 | 38.1222 | 48.4627 | -2329.8886
2041-06-06 02:01 | -7912.44 | 6.6648 | 38.0747 | 48.4627 | -2318.9073
2041-06-07 03:01 | -7867.8 | 6.6648 | 38.0645 | 48.4627 | -2305.8246
2041-06-08 04:01 | -7892.17 | 6.6648 | 38.029 | 48.4627 | -2312.9667
2041-06-09 05:01 | -7848.45 | 6.6648 | 38.0391 | 48.4627 | -2300.1536
2041-06-10 06:01 | -7695.84 | 6.6648 | 38.1134 | 48.4627 | -2255.4281
2041-06-11 07:01 | -7065.64 | 6.6648 | 38.4505 | 48.4627 | -2070.7347
2041-06-12 08:01 | -6380.33 | 6.6648 | 38.8605 | 48.4627 | -1869.8901
2041-06-13 09:01 | -7204.26 | 6.6648 | 38.537 | 48.4627 | -2111.3602
2041-06-14 10:01 | -7126.65 | 6.6648 | 38.5369 | 48.4627 | -2088.6149
2041-06-15 11:01 | -6863.27 | 6.6648 | 38.6523 | 48.4627 | -2011.4259
2041-06-16 12:01 | -6822.03 | 6.6648 | 38.6907 | 48.4627 | -1999.3396
2041-06-17 13:01 | -6566.52 | 6.6648 | 38.8198 | 48.4627 | -1924.457
2041-06-18 14:01 | -6676.81 | 6.6648 | 38.7732 | 48.4627 | -1956.7799
2041-06-19 15:01 | -6755.61 | 6.6648 | 38.7327 | 48.4627 | -1979.8739
2041-06-20 16:01 | -6464.73 | 6.6648 | 38.872 | 48.4627 | -1894.6253
2041-06-21 17:01 | -5010.08 | 6.6648 | 39.6403 | 48.4627 | -1468.3095
2041-06-22 18:01 | -5215.51 | 6.6648 | 39.6926 | 48.4627 | -1528.5151
2041-06-23 19:01 | -5537.7 | 6.6648 | 39.5931 | 48.4627 | -1622.9397
2041-06-24 20:01 | -5418.94 | 6.6648 | 39.6589 | 48.4627 | -1588.1345
2041-06-25 21:01 | -5374.08 | 6.6648 | 39.7327 | 48.4627 | -1574.9874
2041-06-26 22:01 | -5403.3 | 6.6648 | 39.7737 | 48.4627 | -1583.5509
2041-06-27 23:01 | -5257.54 | 6.6648 | 39.8762 | 48.4627 | -1540.8329
2041-06-29 00:01 | -6443.99 | 6.6648 | 39.3194 | 48.4627 | -1888.547
2041-06-30 01:01 | -6697.71 | 6.6648 | 39.1208 | 48.4627 | -1962.905
2041-07-01 02:01 | -6804.78 | 6.6648 | 39.0166 | 48.4627 | -1994.2842
2041-07-02 03:01 | -6843.43 | 6.6648 | 38.977 | 48.4627 | -2005.6114
2041-07-03 04:01 | -7061.44 | 6.6648 | 38.8507 | 48.4627 | -2069.5038
2041-07-04 05:01 | -7224.51 | 6.6648 | 38.7209 | 48.4627 | -2117.2949
2041-07-05 06:01 | -7327.48 | 6.6648 | 38.6348 | 48.4627 | -2147.4724
2041-07-06 07:01 | -6722.11 | 6.6648 | 38.9159 | 48.4627 | -1970.056
2041-07-07 08:01 | -4869.02 | 6.6648 | 39.8961 | 48.4627 | -1426.9689
2041-07-08 09:01 | -4280.19 | 6.6648 | 40.3906 | 48.4627 | -1254.3999
2041-07-09 10:01 | -3030.81 | 6.6648 | 41.1858 | 48.4627 | -888.2427
2041-07-10 11:01 | -1734.23 | 6.4544 | 42.0256 | 48.4627 | -508.2526
2041-07-11 12:01 | -844.074 | 3.0699 | 42.2797 | 48.4627 | -247.3737
2041-07-12 13:01 | -468.264 | 2.0935 | 42.7238 | 48.4627 | -137.2346
2041-07-13 14:01 | -425.929 | 2.0501 | 42.9907 | 48.4627 | -124.8275
2041-07-14 15:01 | -858.574 | 3.6267 | 43.0631 | 48.4627 | -251.6232
2041-07-15 16:01 | -1840.72 | 6.6648 | 43.0284 | 48.4627 | -539.4618
2041-07-16 17:01 | -1270.71 | 4.5783 | 43.0167 | 48.4627 | -372.4083
2041-07-17 18:01 | -2113.04 | 6.6648 | 42.9721 | 48.4627 | -619.2709
2041-07-18 19:01 | -2814.42 | 6.6648 | 42.6141 | 48.4627 | -824.8251
2041-07-19 20:01 | -3357.63 | 6.6648 | 42.2731 | 48.4627 | -984.0242
2041-07-20 21:01 | -3743.04 | 6.6648 | 42.0139 | 48.4627 | -1096.9767
2041-07-21 22:01 | -4468.84 | 6.6648 | 41.5899 | 48.4627 | -1309.6877
2041-07-22 23:01 | -4978.62 | 6.6648 | 41.2157 | 48.4627 | -1459.0895
2041-07-24 00:01 | -6231.28 | 6.6648 | 40.4646 | 48.4627 | -1826.2079
2041-07-25 01:01 | -6615.17 | 6.6648 | 40.082 | 48.4627 | -1938.715
2041-07-26 02:01 | -6450.64 | 6.6648 | 40.015 | 48.4627 | -1890.496
2041-07-27 03:01 | -6614.91 | 6.6648 | 39.8528 | 48.4627 | -1938.6388
2041-07-28 04:01 | -7047.65 | 6.6648 | 39.5605 | 48.4627 | -2065.4623
2041-07-29 05:01 | -6943.65 | 6.6648 | 39.5062 | 48.4627 | -2034.9829
2041-07-30 06:01 | -7140.25 | 6.6648 | 39.3575 | 48.4627 | -2092.6007
2041-07-31 07:01 | -6744.45 | 6.6648 | 39.5059 | 48.4627 | -1976.6032
2041-08-01 08:01 | -5525.87 | 6.6648 | 40.1098 | 48.4627 | -1619.4726
2041-08-02 09:01 | -6727.54 | 6.6648 | 39.5909 | 48.4627 | -1971.6473
2041-08-03 10:01 | -7465.06 | 6.6648 | 39.1345 | 48.4627 | -2187.7931
2041-08-04 11:01 | -8167.54 | 6.6648 | 38.6375 | 48.4627 | -2393.6697
2041-08-05 12:01 | -8414.67 | 6.6648 | 38.3724 | 48.4627 | -2466.0963
2041-08-06 13:01 | -8142.95 | 6.6648 | 38.3909 | 48.4627 | -2386.4631
2041-08-07 14:01 | -7084.58 | 6.6648 | 38.8448 | 48.4627 | -2076.2854
2041-08-08 15:01 | -6622.9 | 6.6648 | 39.1163 | 48.4627 | -1940.9804
2041-08-09 16:01 | -7168.39 | 6.6648 | 38.8873 | 48.4627 | -2100.8477
2041-08-10 17:01 | -6139.76 | 6.6648 | 39.3689 | 48.4627 | -1799.386
2041-08-11 18:01 | -6643.49 | 6.6648 | 39.1907 | 48.4627 | -1947.0147
2041-08-12 19:01 | -7053.15 | 6.6648 | 38.9789 | 48.4627 | -2067.0742
2041-08-13 20:01 | -7351.19 | 6.6648 | 38.7551 | 48.4627 | -2154.4211
2041-08-14 21:01 | -7502.98 | 6.6648 | 38.6113 | 48.4627 | -2198.9064
2041-08-15 22:01 | -7728.52 | 6.6648 | 38.4563 | 48.4627 | -2265.0056
2041-08-16 23:01 | -7909.92 | 6.6648 | 38.307 | 48.4627 | -2318.1687
2041-08-18 00:01 | -8964.92 | 6.6648 | 37.7252 | 48.4627 | -2627.3587
2041-08-19 01:01 | -9208.72 | 6.6648 | 37.4734 | 48.4627 | -2698.8094
2041-08-20 02:01 | -9511.61 | 6.6648 | 37.2118 | 48.4627 | -2787.5777
2041-08-21 03:01 | -9555.91 | 6.6648 | 37.0885 | 48.4627 | -2800.5608
2041-08-22 04:01 | -9557.99 | 6.6648 | 37.0112 | 48.4627 | -2801.1704
2041-08-23 05:01 | -9674.74 | 6.6648 | 36.8786 | 48.4627 | -2835.3864
2041-08-24 06:01 | -9429.09 | 6.6648 | 36.9429 | 48.4627 | -2763.3935
2041-08-25 07:01 | -9547.31 | 6.6648 | 36.8539 | 48.4627 | -2798.0404
2041-08-26 08:01 | -7938 | 6.6648 | 37.6266 | 48.4627 | -2326.3982
2041-08-27 09:01 | -6780.18 | 6.6648 | 38.3307 | 48.4627 | -1987.0746
2041-08-28 10:01 | -5417.57 | 6.6648 | 39.1888 | 48.4627 | -1587.733
2041-08-29 11:01 | -4545.36 | 6.6648 | 39.8446 | 48.4627 | -1332.1135
2041-08-30 12:01 | -3490.04 | 6.6648 | 40.597 | 48.4627 | -1022.8298
2041-08-31 13:01 | -2687.32 | 6.6648 | 41.2554 | 48.4627 | -787.5757
2041-09-01 14:01 | -3248.83 | 6.6648 | 41.205 | 48.4627 | -952.1381
2041-09-02 15:01 | -3987.14 | 6.6648 | 40.93 | 48.4627 | -1168.5154
2041-09-03 16:01 | -4447.22 | 6.6648 | 40.7095 | 48.4627 | -1303.3515
2041-09-04 17:01 | -4926.51 | 6.6648 | 40.4601 | 48.4627 | -1443.8176
2041-09-05 18:01 | -5139.22 | 6.6648 | 40.3216 | 48.4627 | -1506.1567
2041-09-06 19:01 | -6001.57 | 6.6648 | 39.8538 | 48.4627 | -1758.8865
2041-09-07 20:01 | -6282.66 | 6.6648 | 39.6174 | 48.4627 | -1841.2659
2041-09-08 21:01 | -7418.67 | 6.6648 | 38.9632 | 48.4627 | -2174.1976
2041-09-09 22:01 | -7512.96 | 6.6648 | 38.761 | 48.4627 | -2201.8312
2041-09-10 23:01 | -8376.53 | 6.6648 | 38.2143 | 48.4627 | -2454.9186
2041-09-12 00:01 | -8417.11 | 6.6648 | 38.0373 | 48.4627 | -2466.8114
2041-09-13 01:01 | -8420.72 | 6.6648 | 37.9234 | 48.4627 | -2467.8694
2041-09-14 02:01 | -8426.25 | 6.6648 | 37.8416 | 48.4627 | -2469.4901
2041-09-15 03:01 | -8339.71 | 6.6648 | 37.8327 | 48.4627 | -2444.1277
2041-09-16 04:01 | -8229.35 | 6.6648 | 37.8511 | 48.4627 | -2411.7844
2041-09-17 05:01 | -8100.55 | 6.6648 | 37.9047 | 48.4627 | -2374.0369
2041-09-18 06:01 | -7584.89 | 6.6648 | 38.1634 | 48.4627 | -2222.9118
2041-09-19 07:01 | -7505.42 | 6.6648 | 38.2477 | 48.4627 | -2199.6215
2041-09-20 08:01 | -5793.85 | 6.6648 | 39.141 | 48.4627 | -1698.0098
2041-09-21 09:01 | -4924.47 | 6.6648 | 39.7618 | 48.4627 | -1443.2197
2041-09-22 10:01 | -4795.36 | 6.6648 | 40.0104 | 48.4627 | -1405.3813
2041-09-23 11:01 | -4273.26 | 6.6648 | 40.3953 | 48.4627 | -1252.3689
2041-09-24 12:01 | -2410.76 | 6.6648 | 41.4754 | 48.4627 | -706.524
2041-09-25 13:01 | -3235.85 | 6.6648 | 41.337 | 48.4627 | -948.334
2041-09-26 14:01 | -4369.22 | 6.6648 | 40.8441 | 48.4627 | -1280.492
2041-09-27 15:01 | -4856.88 | 6.6648 | 40.5443 | 48.4627 | -1423.411
2041-09-28 16:01 | -4090.68 | 6.6648 | 40.9034 | 48.4627 | -1198.86
2041-09-29 17:01 | -4208.69 | 6.6648 | 40.9239 | 48.4627 | -1233.4453
2041-09-30 18:01 | -3940.91 | 6.6648 | 41.0782 | 48.4627 | -1154.9667
2041-10-01 19:01 | -4350.59 | 6.6648 | 40.9174 | 48.4627 | -1275.0321
2041-10-02 20:01 | -4623.53 | 6.6648 | 40.7845 | 48.4627 | -1355.0229
2041-10-03 21:01 | -5510.08 | 6.6648 | 40.3284 | 48.4627 | -1614.845
2041-10-04 22:01 | -5651.67 | 6.6648 | 40.1743 | 48.4627 | -1656.341
2041-10-05 23:01 | -6514.48 | 6.6648 | 39.6838 | 48.4627 | -1909.2056
2041-10-07 00:01 | -6655.38 | 6.6648 | 39.4885 | 48.4627 | -1950.4993
2041-10-08 01:01 | -6694.8 | 6.6648 | 39.3849 | 48.4627 | -1962.0522
2041-10-09 02:01 | -6781.12 | 6.6648 | 39.2952 | 48.4627 | -1987.3501
2041-10-10 03:01 | -6872.35 | 6.6648 | 39.2179 | 48.4627 | -2014.087
2041-10-11 04:01 | -6796.31 | 6.6648 | 39.2174 | 48.4627 | -1991.8018
2041-10-12 05:01 | -6524.02 | 6.6648 | 39.3457 | 48.4627 | -1912.0015
2041-10-13 06:01 | -6057.88 | 6.6648 | 39.5962 | 48.4627 | -1775.3894
2041-10-14 07:01 | -5943.62 | 6.6648 | 39.703 | 48.4627 | -1741.9031
2041-10-15 08:01 | -5856.14 | 6.6648 | 39.7723 | 48.4627 | -1716.2652
2041-10-16 09:01 | -6366.95 | 6.6648 | 39.5301 | 48.4627 | -1865.9688
2041-10-17 10:01 | -6402.3 | 6.6648 | 39.4678 | 48.4627 | -1876.3289
2041-10-18 11:01 | -6268.63 | 6.6648 | 39.5039 | 48.4627 | -1837.1541
2041-10-19 12:01 | -6096.25 | 6.6648 | 39.5692 | 48.4627 | -1786.6345
2041-10-20 13:01 | -6161.91 | 6.6648 | 39.525 | 48.4627 | -1805.8776
2041-10-21 14:01 | -4643.49 | 6.6648 | 40.2784 | 48.4627 | -1360.8726
2041-10-22 15:01 | -5532.96 | 6.6648 | 39.9637 | 48.4627 | -1621.5505
2041-10-23 16:01 | -4801.87 | 6.6648 | 40.3258 | 48.4627 | -1407.2892
2041-10-24 17:01 | -4548.4 | 6.6648 | 40.5126 | 48.4627 | -1333.0045
2041-10-25 18:01 | -4226.88 | 6.6648 | 40.7447 | 48.4627 | -1238.7762
2041-10-26 19:01 | -4384.84 | 6.6648 | 40.7402 | 48.4627 | -1285.0698
2041-10-27 20:01 | -4529.45 | 6.6648 | 40.6846 | 48.4627 | -1327.4508
2041-10-28 21:01 | -5356.44 | 6.6648 | 40.2911 | 48.4627 | -1569.8176
2041-10-29 22:01 | -5541.4 | 6.6648 | 40.1438 | 48.4627 | -1624.024
2041-10-30 23:01 | -6283.37 | 6.6648 | 39.7331 | 48.4627 | -1841.474
2041-11-01 00:01 | -6384.21 | 6.6648 | 39.6 | 48.4627 | -1871.0273
2041-11-02 01:01 | -6337.78 | 6.6648 | 39.5714 | 48.4627 | -1857.42
2041-11-03 02:01 | -6445.31 | 6.6648 | 39.4814 | 48.4627 | -1888.9339
2041-11-04 03:01 | -6279.01 | 6.6648 | 39.5423 | 48.4627 | -1840.1962
2041-11-05 04:01 | -6038.36 | 6.6648 | 39.6578 | 48.4627 | -1769.6686
2041-11-06 05:01 | -5952.69 | 6.6648 | 39.722 | 48.4627 | -1744.5612
2041-11-07 06:01 | -5247.99 | 6.6648 | 40.0926 | 48.4627 | -1538.034
2041-11-08 07:01 | -5300.14 | 6.6648 | 40.1359 | 48.4627 | -1553.3177
2041-11-09 08:01 | -5291.02 | 6.6648 | 40.1709 | 48.4627 | -1550.6449
2041-11-10 09:01 | -5690.77 | 6.6648 | 39.988 | 48.4627 | -1667.8001
2041-11-11 10:01 | -6029.81 | 6.6648 | 39.7938 | 48.4627 | -1767.1629
2041-11-12 11:01 | -5974.12 | 6.6648 | 39.7865 | 48.4627 | -1750.8417
2041-11-13 12:01 | -5698.09 | 6.6648 | 39.9057 | 48.4627 | -1669.9453
2041-11-14 13:01 | -5667.56 | 6.6648 | 39.9348 | 48.4627 | -1660.9979
2041-11-15 14:01 | -4928.84 | 6.6648 | 40.311 | 48.4627 | -1444.5004
2041-11-16 15:01 | -4960.09 | 6.6648 | 40.3683 | 48.4627 | -1453.6589
2041-11-17 16:01 | -4312.77 | 6.6648 | 40.7376 | 48.4627 | -1263.9481
2041-11-18 17:01 | -4167.73 | 6.6648 | 40.8951 | 48.4627 | -1221.4411
2041-11-19 18:01 | -3911.08 | 6.6648 | 41.0867 | 48.4627 | -1146.2244
2041-11-20 19:01 | -4238.83 | 6.6648 | 40.9861 | 48.4627 | -1242.2784
2041-11-21 20:01 | -4633.06 | 6.6648 | 40.7952 | 48.4627 | -1357.8159
2041-11-22 21:01 | -5627.97 | 6.6648 | 40.2761 | 48.4627 | -1649.3952
2041-11-23 22:01 | -6010.91 | 6.6648 | 39.9895 | 48.4627 | -1761.6238
2041-11-24 23:01 | -6610.38 | 6.6648 | 39.6084 | 48.4627 | -1937.3111
2041-11-26 00:01 | -7014.53 | 6.6648 | 39.304 | 48.4627 | -2055.7558
2041-11-27 01:01 | -7270.35 | 6.6648 | 39.0752 | 48.4627 | -2130.7293
2041-11-28 02:01 | -7181.04 | 6.6648 | 39.0306 | 48.4627 | -2104.5551
2041-11-29 03:01 | -7313.07 | 6.6648 | 38.9187 | 48.4627 | -2143.2492
2041-11-30 04:01 | -7335.88 | 6.6648 | 38.8518 | 48.4627 | -2149.9342
2041-12-01 05:01 | -7395.41 | 6.6648 | 38.7751 | 48.4627 | -2167.3807
2041-12-02 06:01 | -7351.17 | 6.6648 | 38.7499 | 48.4627 | -2154.4153
2041-12-03 07:01 | -6234.69 | 6.6648 | 39.2866 | 48.4627 | -1827.2073
2041-12-04 08:01 | -5561.81 | 6.6648 | 39.7052 | 48.4627 | -1630.0056
2041-12-05 09:01 | -4763.06 | 6.6648 | 40.2173 | 48.4627 | -1395.9151
2041-12-06 10:01 | -4503.75 | 6.6648 | 40.4795 | 48.4627 | -1319.9188
2041-12-07 11:01 | -4621.8 | 6.6648 | 40.5286 | 48.4627 | -1354.5159
2041-12-08 12:01 | -4783.3 | 6.6648 | 40.5122 | 48.4627 | -1401.8468
2041-12-09 13:01 | -4780.64 | 6.6648 | 40.545 | 48.4627 | -1401.0673
2041-12-10 14:01 | -4837.1 | 6.6648 | 40.541 | 48.4627 | -1417.6141
2041-12-11 15:01 | -4861.07 | 6.6648 | 40.5425 | 48.4627 | -1424.639
2041-12-12 16:01 | -4822.44 | 6.6648 | 40.568 | 48.4627 | -1413.3177
2041-12-13 17:01 | -3208.88 | 6.6648 | 41.406 | 48.4627 | -940.4299
2041-12-14 18:01 | -3454.06 | 6.6648 | 41.4542 | 48.4627 | -1012.2851
2041-12-15 19:01 | -3491.37 | 6.6648 | 41.5111 | 48.4627 | -1023.2195
2041-12-16 20:01 | -3538.88 | 6.6648 | 41.5274 | 48.4627 | -1037.1433
2041-12-17 21:01 | -3652.11 | 6.6648 | 41.5148 | 48.4627 | -1070.3278
2041-12-18 22:01 | -3731.58 | 6.6648 | 41.5109 | 48.4627 | -1093.6181
2041-12-19 23:01 | -3618.47 | 6.6648 | 41.5835 | 48.4627 | -1060.4689
2041-12-21 00:01 | -5001.14 | 6.6648 | 40.9179 | 48.4627 | -1465.6895
2041-12-22 01:01 | -5004.1 | 6.6648 | 40.8187 | 48.4627 | -1466.5569
2041-12-23 02:01 | -5247.41 | 6.6648 | 40.6521 | 48.4627 | -1537.8641
2041-12-24 03:01 | -5235.07 | 6.6648 | 40.6282 | 48.4627 | -1534.2476
2041-12-25 04:01 | -5414.11 | 6.6648 | 40.5184 | 48.4627 | -1586.719
2041-12-26 05:01 | -5481.16 | 6.6648 | 40.4383 | 48.4627 | -1606.3694
2041-12-27 06:01 | -5812.44 | 6.6648 | 40.246 | 48.4627 | -1703.458
2041-12-28 07:01 | -5226.27 | 6.6648 | 40.4918 | 48.4627 | -1531.6685
2041-12-29 08:01 | -3855.69 | 6.6648 | 41.2105 | 48.4627 | -1129.9912
2041-12-30 09:01 | -3659.56 | 6.6648 | 41.4463 | 48.4627 | -1072.5112
2041-12-31 10:01 | -2485.46 | 6.6648 | 42.1316 | 48.4627 | -728.4164
2042-01-01 11:01 | -1503.45 | 5.4958 | 42.6274 | 48.4627 | -440.6177
2042-01-02 12:01 | -1163.57 | 4.3368 | 42.8615 | 48.4627 | -341.0087
2042-01-03 13:01 | -952.747 | 3.694 | 43.0691 | 48.4627 | -279.2226
2042-01-04 14:01 | -1250.8 | 4.8561 | 43.2056 | 48.4627 | -366.5733
2042-01-05 15:01 | -1964.59 | 6.6648 | 43.1663 | 48.4627 | -575.7645
2042-01-06 16:01 | -3393.91 | 6.6648 | 42.441 | 48.4627 | -994.6568
2042-01-07 17:01 | -2595.36 | 6.6648 | 42.7242 | 48.4627 | -760.6249
2042-01-08 18:01 | -3369.86 | 6.6648 | 42.3579 | 48.4627 | -987.6085
2042-01-09 19:01 | -4032.28 | 6.6648 | 41.9684 | 48.4627 | -1181.7446
2042-01-10 20:01 | -4509.34 | 6.6648 | 41.6154 | 48.4627 | -1321.5571
2042-01-11 21:01 | -4773.6 | 6.6648 | 41.384 | 48.4627 | -1399.0041
2042-01-12 22:01 | -5095.32 | 6.6648 | 41.1483 | 48.4627 | -1493.2909
2042-01-13 23:01 | -5506.21 | 6.6648 | 40.8392 | 48.4627 | -1613.7109
2042-01-15 00:01 | -6968.58 | 6.6648 | 39.9898 | 48.4627 | -2042.2892
2042-01-16 01:01 | -7177.49 | 6.6648 | 39.6703 | 48.4627 | -2103.5147
2042-01-17 02:01 | -7123.47 | 6.6648 | 39.5467 | 48.4627 | -2087.683
2042-01-18 03:01 | -7229.78 | 6.6648 | 39.4018 | 48.4627 | -2118.8394
2042-01-19 04:01 | -7136.54 | 6.6648 | 39.369 | 48.4627 | -2091.5134
2042-01-20 05:01 | -6851.14 | 6.6648 | 39.4471 | 48.4627 | -2007.8709
2042-01-21 06:01 | -6284.88 | 6.6648 | 39.7266 | 48.4627 | -1841.9165
2042-01-22 07:01 | -6010.64 | 6.6648 | 39.902 | 48.4627 | -1761.5447
2042-01-23 08:01 | -4541.31 | 6.6648 | 40.6791 | 48.4627 | -1330.9266
2042-01-24 09:01 | -3629.41 | 6.6648 | 41.2925 | 48.4627 | -1063.6751
2042-01-25 10:01 | -2067.27 | 6.6648 | 42.2544 | 48.4627 | -605.857
2042-01-26 11:01 | -1289.45 | 4.6825 | 42.6105 | 48.4627 | -377.9005
2042-01-27 12:01 | -570.765 | 2.2625 | 42.9175 | 48.4627 | -167.2747
2042-01-28 13:01 | -458.407 | 2.1392 | 43.2726 | 48.4627 | -134.3458
2042-01-29 14:01 | -500.528 | 2.3012 | 43.4254 | 48.4627 | -146.6903
2042-01-30 15:01 | -1041.5 | 4.2401 | 43.4577 | 48.4627 | -305.2335
2042-01-31 16:01 | -1775.62 | 6.6648 | 43.4405 | 48.4627 | -520.3829
2042-02-01 17:01 | -2149.66 | 6.6648 | 43.2312 | 48.4627 | -630.0032
2042-02-02 18:01 | -2092.67 | 6.6648 | 43.2357 | 48.4627 | -613.301
2042-02-03 19:01 | -3077.14 | 6.6648 | 42.7479 | 48.4627 | -901.8207
2042-02-04 20:01 | -3643.87 | 6.6648 | 42.3746 | 48.4627 | -1067.9129
2042-02-05 21:01 | -4636.87 | 6.6648 | 41.771 | 48.4627 | -1358.9325
2042-02-06 22:01 | -5176.69 | 6.6648 | 41.3495 | 48.4627 | -1517.1381
2042-02-07 23:01 | -5817 | 6.6648 | 40.8807 | 48.4627 | -1704.7944
2042-02-09 00:01 | -6305.05 | 6.6648 | 40.4762 | 48.4627 | -1847.8277
2042-02-10 01:01 | -6624.91 | 6.6648 | 40.1654 | 48.4627 | -1941.5695
2042-02-11 02:01 | -6436.49 | 6.6648 | 40.1284 | 48.4627 | -1886.349
2042-02-12 03:01 | -6140.02 | 6.6648 | 40.2116 | 48.4627 | -1799.4622
2042-02-13 04:01 | -5793.9 | 6.6648 | 40.3642 | 48.4627 | -1698.0245
2042-02-14 05:01 | -5259.17 | 6.6648 | 40.6425 | 48.4627 | -1541.3106
2042-02-15 06:01 | -4615.46 | 6.6648 | 41.0126 | 48.4627 | -1352.6578
2042-02-16 07:01 | -4349.88 | 6.6648 | 41.2328 | 48.4627 | -1274.824
2042-02-17 08:01 | -3653.22 | 6.6648 | 41.651 | 48.4627 | -1070.6531
2042-02-18 09:01 | -4413.91 | 6.6648 | 41.3673 | 48.4627 | -1293.5893
2042-02-19 10:01 | -2511.86 | 6.6648 | 42.3223 | 48.4627 | -736.1535
2042-02-20 11:01 | -2416.74 | 6.6648 | 42.5476 | 48.4627 | -708.2766
2042-02-21 12:01 | -2055.33 | 6.6648 | 42.8485 | 48.4627 | -602.3578
2042-02-22 13:01 | -2697.25 | 6.6648 | 42.62 | 48.4627 | -790.4859
2042-02-23 14:01 | -3036.99 | 6.6648 | 42.4518 | 48.4627 | -890.0539
2042-02-24 15:01 | -3728.67 | 6.6648 | 42.1015 | 48.4627 | -1092.7653
2042-02-25 16:01 | -3213.58 | 6.6648 | 42.2999 | 48.4627 | -941.8073
2042-02-26 17:01 | -3417.06 | 6.6648 | 42.2125 | 48.4627 | -1001.4414
2042-02-27 18:01 | -3768.75 | 6.6648 | 42.0161 | 48.4627 | -1104.5116
2042-02-28 19:01 | -4281.97 | 6.6648 | 41.713 | 48.4627 | -1254.9215
2042-03-01 20:01 | -5122.65 | 6.6648 | 41.2156 | 48.4627 | -1501.3005
2042-03-02 21:01 | -5883.64 | 6.6648 | 40.7292 | 48.4627 | -1724.3247
2042-03-03 22:01 | -6279.86 | 6.6648 | 40.3808 | 48.4627 | -1840.4453
2042-03-04 23:01 | -7468.4 | 6.6648 | 39.6477 | 48.4627 | -2188.772
2042-03-06 00:01 | -7721.92 | 6.6648 | 39.3185 | 48.4627 | -2263.0714
2042-03-07 01:01 | -8035.43 | 6.6648 | 39.0088 | 48.4627 | -2354.9521
2042-03-08 02:01 | -8355.38 | 6.6648 | 38.7203 | 48.4627 | -2448.7202
2042-03-09 03:01 | -8544.96 | 6.6648 | 38.5033 | 48.4627 | -2504.2806
2042-03-10 04:01 | -8568.32 | 6.6648 | 38.3742 | 48.4627 | -2511.1267
2042-03-11 05:01 | -8510.25 | 6.6648 | 38.3186 | 48.4627 | -2494.1081
2042-03-12 06:01 | -8059.05 | 6.6648 | 38.4784 | 48.4627 | -2361.8744
2042-03-13 07:01 | -8050.88 | 6.6648 | 38.4609 | 48.4627 | -2359.48
2042-03-14 08:01 | -7256.56 | 6.6648 | 38.8305 | 48.4627 | -2126.6878
2042-03-15 09:01 | -7191.69 | 6.6648 | 38.9033 | 48.4627 | -2107.6763
2042-03-16 10:01 | -5969.15 | 6.6648 | 39.5321 | 48.4627 | -1749.3852
2042-03-17 11:01 | -6372.98 | 6.6648 | 39.4346 | 48.4627 | -1867.7361
2042-03-18 12:01 | -6302.76 | 6.6648 | 39.4782 | 48.4627 | -1847.1566
2042-03-19 13:01 | -6784.71 | 6.6648 | 39.2374 | 48.4627 | -1988.4022
2042-03-20 14:01 | -7159.92 | 6.6648 | 39.0019 | 48.4627 | -2098.3654
2042-03-21 15:01 | -7106.39 | 6.6648 | 38.9711 | 48.4627 | -2082.6773
2042-03-22 16:01 | -6433.66 | 6.6648 | 39.2694 | 48.4627 | -1885.5196
2042-03-23 17:01 | -6020.73 | 6.6648 | 39.5149 | 48.4627 | -1764.5018
2042-03-24 18:01 | -5868.72 | 6.6648 | 39.6359 | 48.4627 | -1719.952
2042-03-25 19:01 | -6272.18 | 6.6648 | 39.4671 | 48.4627 | -1838.1945
2042-03-26 20:01 | -6661.1 | 6.6648 | 39.2541 | 48.4627 | -1952.1757
2042-03-27 21:01 | -7666.64 | 6.6648 | 38.7053 | 48.4627 | -2246.8704
2042-03-28 22:01 | -7787.54 | 6.6648 | 38.5171 | 48.4627 | -2282.3027
2042-03-29 23:01 | -8585.18 | 6.6648 | 38.026 | 48.4627 | -2516.0679
2042-03-31 00:01 | -8993.34 | 6.6648 | 37.6851 | 48.4627 | -2635.6878
2042-04-01 01:01 | -9161.98 | 6.6648 | 37.4752 | 48.4627 | -2685.1113
2042-04-02 02:01 | -9287.6 | 6.6648 | 37.3181 | 48.4627 | -2721.9269
2042-04-03 03:01 | -9187.74 | 6.6648 | 37.2974 | 48.4627 | -2692.6608
2042-04-04 04:01 | -9353.93 | 6.6648 | 37.1558 | 48.4627 | -2741.3663
2042-04-05 05:01 | -9299.76 | 6.6648 | 37.1177 | 48.4627 | -2725.4906
2042-04-06 06:01 | -9327.89 | 6.6648 | 37.0496 | 48.4627 | -2733.7347
2042-04-07 07:01 | -8555.74 | 6.6648 | 37.3949 | 48.4627 | -2507.4399
2042-04-08 08:01 | -7855.5 | 6.6648 | 37.7779 | 48.4627 | -2302.2198
2042-04-09 09:01 | -8663.07 | 6.6648 | 37.4338 | 48.4627 | -2538.8952
2042-04-10 10:01 | -8215.29 | 6.6648 | 37.5962 | 48.4627 | -2407.6638
2042-04-11 11:01 | -8221.05 | 6.6648 | 37.593 | 48.4627 | -2409.3519
2042-04-12 12:01 | -8204.01 | 6.6648 | 37.603 | 48.4627 | -2404.358
2042-04-13 13:01 | -8375.93 | 6.6648 | 37.4996 | 48.4627 | -2454.7428
2042-04-14 14:01 | -8374.52 | 6.6648 | 37.4599 | 48.4627 | -2454.3295
2042-04-15 15:01 | -8360.83 | 6.6648 | 37.4478 | 48.4627 | -2450.3174
2042-04-16 16:01 | -8440.65 | 6.6648 | 37.3847 | 48.4627 | -2473.7103
2042-04-17 17:01 | -6779.46 | 6.6648 | 38.2016 | 48.4627 | -1986.8636
2042-04-18 18:01 | -7301.79 | 6.6648 | 38.0704 | 48.4627 | -2139.9434
2042-04-19 19:01 | -7417.38 | 6.6648 | 38.0283 | 48.4627 | -2173.8195
2042-04-20 20:01 | -7570.64 | 6.6648 | 37.9347 | 48.4627 | -2218.7356
2042-04-21 21:01 | -7824.9 | 6.6648 | 37.8053 | 48.4627 | -2293.2518
2042-04-22 22:01 | -7894.93 | 6.6648 | 37.7537 | 48.4627 | -2313.7756
2042-04-23 23:01 | -8071.38 | 6.6648 | 37.6351 | 48.4627 | -2365.488
2042-04-25 00:01 | -9212.05 | 6.6648 | 37.0271 | 48.4627 | -2699.7854
2042-04-26 01:01 | -9325.13 | 6.6648 | 36.8453 | 48.4627 | -2732.9258
2042-04-27 02:01 | -9272.92 | 6.6648 | 36.7931 | 48.4627 | -2717.6246
2042-04-28 03:01 | -9142.78 | 6.6648 | 36.8233 | 48.4627 | -2679.4843
2042-04-29 04:01 | -8895.62 | 6.6648 | 36.9293 | 48.4627 | -2607.0489
2042-04-30 05:01 | -8511.51 | 6.6648 | 37.1118 | 48.4627 | -2494.4773
2042-05-01 06:01 | -8026.43 | 6.6648 | 37.3916 | 48.4627 | -2352.3144
2042-05-02 07:01 | -8062.76 | 6.6648 | 37.4297 | 48.4627 | -2362.9617
2042-05-03 08:01 | -7758.8 | 6.6648 | 37.6026 | 48.4627 | -2273.8798
2042-05-04 09:01 | -9089.55 | 6.6648 | 36.9608 | 48.4627 | -2663.8841
2042-05-05 10:01 | -8043.55 | 6.6648 | 37.3812 | 48.4627 | -2357.3318
2042-05-06 11:01 | -7292.62 | 6.6648 | 37.7974 | 48.4627 | -2137.2559
2042-05-07 12:01 | -8976.78 | 6.6648 | 37.0314 | 48.4627 | -2630.8345
2042-05-08 13:01 | -9637.99 | 6.6648 | 36.5664 | 48.4627 | -2824.616
2042-05-09 14:01 | -8789.04 | 6.6648 | 36.8559 | 48.4627 | -2575.8134
2042-05-10 15:01 | -8299.24 | 6.6648 | 37.1371 | 48.4627 | -2432.2671
2042-05-11 16:01 | -9004.89 | 6.6648 | 36.816 | 48.4627 | -2639.0727
2042-05-12 17:01 | -9005.46 | 6.6648 | 36.7214 | 48.4627 | -2639.2398
2042-05-13 18:01 | -8889.08 | 6.6648 | 36.7297 | 48.4627 | -2605.1322
2042-05-14 19:01 | -9441.25 | 6.6648 | 36.4386 | 48.4627 | -2766.9572
2042-05-15 20:01 | -9770.23 | 6.6648 | 36.1878 | 48.4627 | -2863.3718
2042-05-16 21:01 | -10856 | 6.6648 | 35.5445 | 48.4627 | -3181.5795
2042-05-17 22:01 | -11049.6 | 6.6648 | 35.2817 | 48.4627 | -3238.3181
2042-05-18 23:01 | -11779.6 | 6.6648 | 34.7764 | 48.4627 | -3452.26
2042-05-20 00:01 | -12133.8 | 6.6648 | 34.4435 | 48.4627 | -3556.0657
2042-05-21 01:01 | -12371.7 | 6.6648 | 34.1865 | 48.4627 | -3625.7874
2042-05-22 02:01 | -12321.9 | 6.6648 | 34.0849 | 48.4627 | -3611.1924
2042-05-23 03:01 | -12327.1 | 6.6648 | 33.9917 | 48.4627 | -3612.7164
2042-05-24 04:01 | -12561.7 | 6.6648 | 33.7917 | 48.4627 | -3681.4709
2042-05-25 05:01 | -12674.7 | 6.6648 | 33.6361 | 48.4627 | -3714.5879
2042-05-26 06:01 | -12730.1 | 6.6648 | 33.5135 | 48.4627 | -3730.824
2042-05-27 07:01 | -12544.1 | 6.6648 | 33.5267 | 48.4627 | -3676.3128
2042-05-28 08:01 | -11799.9 | 6.6648 | 33.8491 | 48.4627 | -3458.2093
2042-05-29 09:01 | -11075.5 | 6.6648 | 34.2488 | 48.4627 | -3245.9086
2042-05-30 10:01 | -10226.5 | 6.6648 | 34.7432 | 48.4627 | -2997.0913
2042-05-31 11:01 | -9475.8 | 6.6648 | 35.2266 | 48.4627 | -2777.0828
2042-06-01 12:01 | -8817.88 | 6.6648 | 35.6929 | 48.4627 | -2584.2655
2042-06-02 13:01 | -8757.78 | 6.6648 | 35.8682 | 48.4627 | -2566.652
2042-06-03 14:01 | -8926.09 | 6.6648 | 35.8699 | 48.4627 | -2615.9787
2042-06-04 15:01 | -9310.46 | 6.6648 | 35.7121 | 48.4627 | -2728.6265
2042-06-05 16:01 | -10948.1 | 6.6648 | 34.8694 | 48.4627 | -3208.5714
2042-06-06 17:01 | -9736.52 | 6.6648 | 35.3294 | 48.4627 | -2853.4923
2042-06-07 18:01 | -10401.2 | 6.6648 | 35.0188 | 48.4627 | -3048.2908
2042-06-08 19:01 | -10582.2 | 6.6648 | 34.8792 | 48.4627 | -3101.3367
2042-06-09 20:01 | -10827.1 | 6.6648 | 34.687 | 48.4627 | -3173.1098
2042-06-10 21:01 | -11051.2 | 6.6648 | 34.512 | 48.4627 | -3238.787
2042-06-11 22:01 | -11280 | 6.6648 | 34.3487 | 48.4627 | -3305.8417
2042-06-12 23:01 | -11310.2 | 6.6648 | 34.2593 | 48.4627 | -3314.6924
2042-06-14 00:01 | -11905.6 | 6.6648 | 33.9019 | 48.4627 | -3489.1869
2042-06-15 01:01 | -12096.8 | 6.6648 | 33.7006 | 48.4627 | -3545.2221
2042-06-16 02:01 | -11895.2 | 6.6648 | 33.7161 | 48.4627 | -3486.139
2042-06-17 03:01 | -11746 | 6.6648 | 33.755 | 48.4627 | -3442.4128
2042-06-18 04:01 | -11439.5 | 6.6648 | 33.9059 | 48.4627 | -3352.5865
2042-06-19 05:01 | -10962.7 | 6.6648 | 34.1511 | 48.4627 | -3212.8502
2042-06-20 06:01 | -10806.4 | 6.6648 | 34.2765 | 48.4627 | -3167.0432
2042-06-21 07:01 | -10030.2 | 6.6648 | 34.7107 | 48.4627 | -2939.5614
2042-06-22 08:01 | -8968.21 | 6.6648 | 35.3439 | 48.4627 | -2628.3229
2042-06-23 09:01 | -8431.13 | 6.6648 | 35.775 | 48.4627 | -2470.9203
2042-06-24 10:01 | -8852.34 | 6.6648 | 35.6936 | 48.4627 | -2594.3648
2042-06-25 11:01 | -8488.93 | 6.6648 | 35.9111 | 48.4627 | -2487.8598
2042-06-26 12:01 | -6828.02 | 6.6648 | 36.8366 | 48.4627 | -2001.0951
2042-06-27 13:01 | -6190.97 | 6.6648 | 37.3875 | 48.4627 | -1814.3942
2042-06-28 14:01 | -6439.95 | 6.6648 | 37.4502 | 48.4627 | -1887.363
2042-06-29 15:01 | -6852.29 | 6.6648 | 37.3276 | 48.4627 | -2008.208
2042-06-30 16:01 | -7585.14 | 6.6648 | 37.0064 | 48.4627 | -2222.9851
2042-07-01 17:01 | -6198.88 | 6.6648 | 37.7044 | 48.4627 | -1816.7124
2042-07-02 18:01 | -6877.25 | 6.6648 | 37.4983 | 48.4627 | -2015.523
2042-07-03 19:01 | -7174.12 | 6.6648 | 37.3662 | 48.4627 | -2102.527
2042-07-04 20:01 | -7495.83 | 6.6648 | 37.1837 | 48.4627 | -2196.8109
2042-07-05 21:01 | -7845.25 | 6.6648 | 36.9911 | 48.4627 | -2299.2158
2042-07-06 22:01 | -8160.87 | 6.6648 | 36.819 | 48.4627 | -2391.7149
2042-07-07 23:01 | -8506.13 | 6.6648 | 36.6001 | 48.4627 | -2492.9006
2042-07-09 00:01 | -9780.02 | 6.6648 | 35.8951 | 48.4627 | -2866.2409
2042-07-10 01:01 | -10191 | 6.6648 | 35.528 | 48.4627 | -2986.6873
2042-07-11 02:01 | -10472.9 | 6.6648 | 35.2551 | 48.4627 | -3069.304
2042-07-12 03:01 | -10367.6 | 6.6648 | 35.2099 | 48.4627 | -3038.4436
2042-07-13 04:01 | -10900.6 | 6.6648 | 34.8807 | 48.4627 | -3194.6505
2042-07-14 05:01 | -10069.8 | 6.6648 | 35.1925 | 48.4627 | -2951.1671
2042-07-15 06:01 | -10066.9 | 6.6648 | 35.2091 | 48.4627 | -2950.3172
2042-07-16 07:01 | -9889.32 | 6.6648 | 35.2975 | 48.4627 | -2898.2736
2042-07-17 08:01 | -8446.22 | 6.6648 | 36.0315 | 48.4627 | -2475.3427
2042-07-18 09:01 | -7365.02 | 6.6648 | 36.714 | 48.4627 | -2158.4743
2042-07-19 10:01 | -5915.56 | 6.6648 | 37.6364 | 48.4627 | -1733.6795
2042-07-20 11:01 | -4854.48 | 6.6648 | 38.4075 | 48.4627 | -1422.7076
2042-07-21 12:01 | -4947.49 | 6.6648 | 38.6082 | 48.4627 | -1449.9662
2042-07-22 13:01 | -5374.9 | 6.6648 | 38.5468 | 48.4627 | -1575.2277
2042-07-23 14:01 | -5815.28 | 6.6648 | 38.3945 | 48.4627 | -1704.2903
2042-07-24 15:01 | -6288.32 | 6.6648 | 38.1862 | 48.4627 | -1842.9247
2042-07-25 16:01 | -5913.64 | 6.6648 | 38.3809 | 48.4627 | -1733.1168
2042-07-26 17:01 | -5928.71 | 6.6648 | 38.4093 | 48.4627 | -1737.5334
2042-07-27 18:01 | -5639.35 | 6.6648 | 38.5948 | 48.4627 | -1652.7303
2042-07-28 19:01 | -6236.97 | 6.6648 | 38.3546 | 48.4627 | -1827.8755
2042-07-29 20:01 | -6442.79 | 6.6648 | 38.2417 | 48.4627 | -1888.1954
2042-07-30 21:01 | -7283.33 | 6.6648 | 37.8028 | 48.4627 | -2134.5333
2042-07-31 22:01 | -7531.93 | 6.6648 | 37.5907 | 48.4627 | -2207.3908
2042-08-01 23:01 | -7994.66 | 6.6648 | 37.2782 | 48.4627 | -2343.0036
2042-08-03 00:01 | -8167.12 | 6.6648 | 37.104 | 48.4627 | -2393.5466
2042-08-04 01:01 | -8315.33 | 6.6648 | 36.9663 | 48.4627 | -2436.9827
2042-08-05 02:01 | -8557.78 | 6.6648 | 36.7919 | 48.4627 | -2508.0377
2042-08-06 03:01 | -8614.17 | 6.6648 | 36.7159 | 48.4627 | -2524.564
2042-08-07 04:01 | -8544.4 | 6.6648 | 36.715 | 48.4627 | -2504.1165
2042-08-08 05:01 | -8324.48 | 6.6648 | 36.8091 | 48.4627 | -2439.6643
2042-08-09 06:01 | -7889.06 | 6.6648 | 37.0331 | 48.4627 | -2312.0553
2042-08-10 07:01 | -8179.45 | 6.6648 | 36.9226 | 48.4627 | -2397.1602
2042-08-11 08:01 | -8361.35 | 6.6648 | 36.8108 | 48.4627 | -2450.4698
2042-08-12 09:01 | -7295.94 | 6.6648 | 37.3236 | 48.4627 | -2138.2289
2042-08-13 10:01 | -5634.18 | 6.6648 | 38.2549 | 48.4627 | -1651.2152
2042-08-14 11:01 | -4621.63 | 6.6648 | 38.9711 | 48.4627 | -1354.466
2042-08-15 12:01 | -4306.79 | 6.6648 | 39.3273 | 48.4627 | -1262.1956
2042-08-16 13:01 | -5069.88 | 6.6648 | 39.088 | 48.4627 | -1485.8352
2042-08-17 14:01 | -5538.57 | 6.6648 | 38.8921 | 48.4627 | -1623.1946
2042-08-18 15:01 | -7063.24 | 6.6648 | 38.1196 | 48.4627 | -2070.0313
2042-08-19 16:01 | -6989.57 | 6.6648 | 38.0249 | 48.4627 | -2048.4408
2042-08-20 17:01 | -7098.62 | 6.6648 | 37.8983 | 48.4627 | -2080.4002
2042-08-21 18:01 | -7616.29 | 6.6648 | 37.5786 | 48.4627 | -2232.1143
2042-08-22 19:01 | -7640.26 | 6.6648 | 37.4819 | 48.4627 | -2239.1392
2042-08-23 20:01 | -8043.76 | 6.6648 | 37.2248 | 48.4627 | -2357.3934
2042-08-24 21:01 | -8895.46 | 6.6648 | 36.7341 | 48.4627 | -2607.002
2042-08-25 22:01 | -9210.42 | 6.6648 | 36.4385 | 48.4627 | -2699.3076
2042-08-26 23:01 | -9616.94 | 6.6648 | 36.1078 | 48.4627 | -2818.4469
2042-08-28 00:01 | -9910.87 | 6.6648 | 35.8387 | 48.4627 | -2904.5893
2042-08-29 01:01 | -10134.4 | 6.6648 | 35.61 | 48.4627 | -2970.0995
2042-08-30 02:01 | -10103 | 6.6648 | 35.5239 | 48.4627 | -2960.897
2042-08-31 03:01 | -10227.4 | 6.6648 | 35.4041 | 48.4627 | -2997.3551
2042-09-01 04:01 | -10175.9 | 6.6648 | 35.3718 | 48.4627 | -2982.2619
2042-09-02 05:01 | -10021.2 | 6.6648 | 35.4068 | 48.4627 | -2936.9238
2042-09-03 06:01 | -9713.5 | 6.6648 | 35.5435 | 48.4627 | -2846.7458
2042-09-04 07:01 | -9678.38 | 6.6648 | 35.5675 | 48.4627 | -2836.4532
2042-09-05 08:01 | -10028.2 | 6.6648 | 35.3798 | 48.4627 | -2938.9753
2042-09-06 09:01 | -10133.6 | 6.6648 | 35.2753 | 48.4627 | -2969.865
2042-09-07 10:01 | -10082.1 | 6.6648 | 35.2447 | 48.4627 | -2954.7718
2042-09-08 11:01 | -10109.5 | 6.6648 | 35.1854 | 48.4627 | -2962.802
2042-09-09 12:01 | -9886.38 | 6.6648 | 35.2475 | 48.4627 | -2897.412
2042-09-10 13:01 | -9859.6 | 6.6648 | 35.2365 | 48.4627 | -2889.5635
2042-09-11 14:01 | -10087.8 | 6.6648 | 35.097 | 48.4627 | -2956.4423
2042-09-12 15:01 | -9679.26 | 6.6648 | 35.2649 | 48.4627 | -2836.7111
2042-09-13 16:01 | -9347.56 | 6.6648 | 35.4425 | 48.4627 | -2739.4994
2042-09-14 17:01 | -8882.62 | 6.6648 | 35.7081 | 48.4627 | -2603.2389
2042-09-15 18:01 | -8460.05 | 6.6648 | 35.9707 | 48.4627 | -2479.3959
2042-09-16 19:01 | -8697.89 | 6.6648 | 35.9107 | 48.4627 | -2549.0999
2042-09-17 20:01 | -9023.73 | 6.6648 | 35.7624 | 48.4627 | -2644.5942
2042-09-18 21:01 | -9566.93 | 6.6648 | 35.4699 | 48.4627 | -2803.7904
2042-09-19 22:01 | -10125.3 | 6.6648 | 35.1317 | 48.4627 | -2967.4325
2042-09-20 23:01 | -11016.5 | 6.6648 | 34.5939 | 48.4627 | -3228.6174
2042-09-22 00:01 | -11455.2 | 6.6648 | 34.2298 | 48.4627 | -3357.1877
2042-09-23 01:01 | -11758.6 | 6.6648 | 33.9483 | 48.4627 | -3446.1055
2042-09-24 02:01 | -11820.7 | 6.6648 | 33.8089 | 48.4627 | -3464.3052
2042-09-25 03:01 | -11849.2 | 6.6648 | 33.708 | 48.4627 | -3472.6577
2042-09-26 04:01 | -11868.1 | 6.6648 | 33.6276 | 48.4627 | -3478.1968
2042-09-27 05:01 | -11831.3 | 6.6648 | 33.5859 | 48.4627 | -3467.4118
2042-09-28 06:01 | -11205.3 | 6.6648 | 33.8535 | 48.4627 | -3283.9493
2042-09-29 07:01 | -10922.5 | 6.6648 | 34.015 | 48.4627 | -3201.0688
2042-09-30 08:01 | -10082.2 | 6.6648 | 34.4641 | 48.4627 | -2954.8011
2042-10-01 09:01 | -9938.42 | 6.6648 | 34.6141 | 48.4627 | -2912.6634
2042-10-02 10:01 | -8959.36 | 6.6648 | 35.1646 | 48.4627 | -2625.7292
2042-10-03 11:01 | -8989.31 | 6.6648 | 35.2724 | 48.4627 | -2634.5067
2042-10-04 12:01 | -8591.46 | 6.6648 | 35.541 | 48.4627 | -2517.9084
2042-10-05 13:01 | -8287.31 | 6.6648 | 35.7769 | 48.4627 | -2428.7708
2042-10-06 14:01 | -8231.72 | 6.6648 | 35.8891 | 48.4627 | -2412.479
2042-10-07 15:01 | -7589.66 | 6.6648 | 36.2843 | 48.4627 | -2224.3098
2042-10-08 16:01 | -6866.9 | 6.6648 | 36.758 | 48.4627 | -2012.4897
2042-10-09 17:01 | -6680.28 | 6.6648 | 36.9974 | 48.4627 | -1957.7968
2042-10-10 18:01 | -6576.35 | 6.6648 | 37.1555 | 48.4627 | -1927.3379
2042-10-11 19:01 | -6891.53 | 6.6648 | 37.0785 | 48.4627 | -2019.7081
2042-10-12 20:01 | -6872.3 | 6.6648 | 37.1277 | 48.4627 | -2014.0723
2042-10-13 21:01 | -7598.28 | 6.6648 | 36.8017 | 48.4627 | -2226.836
2042-10-14 22:01 | -7740.78 | 6.6648 | 36.6928 | 48.4627 | -2268.5987
2042-10-15 23:01 | -8459.94 | 6.6648 | 36.3072 | 48.4627 | -2479.3637
2042-10-17 00:01 | -8804.46 | 6.6648 | 36.0648 | 48.4627 | -2580.3325
2042-10-18 01:01 | -8934.69 | 6.6648 | 35.9366 | 48.4627 | -2618.4992
2042-10-19 02:01 | -8963.31 | 6.6648 | 35.8796 | 48.4627 | -2626.8869
2042-10-20 03:01 | -9115.07 | 6.6648 | 35.7775 | 48.4627 | -2671.3633
2042-10-21 04:01 | -8825 | 6.6648 | 35.8881 | 48.4627 | -2586.3522
2042-10-22 05:01 | -8707.71 | 6.6648 | 35.9549 | 48.4627 | -2551.9779
2042-10-23 06:01 | -8162.09 | 6.6648 | 36.2458 | 48.4627 | -2392.0724
2042-10-24 07:01 | -8278.94 | 6.6648 | 36.2422 | 48.4627 | -2426.3178
2042-10-25 08:01 | -6915.58 | 6.6648 | 36.9541 | 48.4627 | -2026.7564
2042-10-26 09:01 | -5538.66 | 6.6648 | 37.8059 | 48.4627 | -1623.221
2042-10-27 10:01 | -4363.28 | 6.6648 | 38.6261 | 48.4627 | -1278.7511
2042-10-28 11:01 | -4126.86 | 6.6648 | 38.9939 | 48.4627 | -1209.4633
2042-10-29 12:01 | -3106.25 | 6.6648 | 39.6939 | 48.4627 | -910.352
2042-10-30 13:01 | -3227.01 | 6.6648 | 39.8751 | 48.4627 | -945.7433
2042-10-31 14:01 | -3084.78 | 6.6648 | 40.1098 | 48.4627 | -904.0598
2042-11-01 15:01 | -3983.98 | 6.6648 | 39.7828 | 48.4627 | -1167.5893
2042-11-02 16:01 | -5269.29 | 6.6648 | 39.1415 | 48.4627 | -1544.2765
2042-11-03 17:01 | -5172.31 | 6.6648 | 39.1056 | 48.4627 | -1515.8544
2042-11-04 18:01 | -5362.41 | 6.6648 | 38.9858 | 48.4627 | -1571.5672
2042-11-05 19:01 | -6134.99 | 6.6648 | 38.5828 | 48.4627 | -1797.9881
2042-11-06 20:01 | -6429.79 | 6.6648 | 38.3405 | 48.4627 | -1884.3854
2042-11-07 21:01 | -7387.62 | 6.6648 | 37.7758 | 48.4627 | -2165.0977
2042-11-08 22:01 | -7866.77 | 6.6648 | 37.4059 | 48.4627 | -2305.5227
2042-11-09 23:01 | -8709.41 | 6.6648 | 36.8517 | 48.4627 | -2552.4761
2042-11-11 00:01 | -9567.36 | 6.6648 | 36.2473 | 48.4627 | -2803.9164
2042-11-12 01:01 | -9786.47 | 6.6648 | 35.9467 | 48.4627 | -2868.1312
2042-11-13 02:01 | -10053 | 6.6648 | 35.6612 | 48.4627 | -2946.2435
2042-11-14 03:01 | -10143.5 | 6.6648 | 35.4936 | 48.4627 | -2972.7664
2042-11-15 04:01 | -10079.5 | 6.6648 | 35.4298 | 48.4627 | -2954.0099
2042-11-16 05:01 | -10097.9 | 6.6648 | 35.3525 | 48.4627 | -2959.4024
2042-11-17 06:01 | -10433.6 | 6.6648 | 35.1214 | 48.4627 | -3057.7863
2042-11-18 07:01 | -9881.38 | 6.6648 | 35.3211 | 48.4627 | -2895.9466
2042-11-19 08:01 | -9159.86 | 6.6648 | 35.6769 | 48.4627 | -2684.49
2042-11-20 09:01 | -8930.83 | 6.6648 | 35.8399 | 48.4627 | -2617.3679
2042-11-21 10:01 | -8133.43 | 6.6648 | 36.2662 | 48.4627 | -2383.673
2042-11-22 11:01 | -7008.64 | 6.6648 | 36.9165 | 48.4627 | -2054.0296
2042-11-23 12:01 | -6338.27 | 6.6648 | 37.414 | 48.4627 | -1857.5636
2042-11-24 13:01 | -5609.58 | 6.6648 | 37.9344 | 48.4627 | -1644.0056
2042-11-25 14:01 | -5883.35 | 6.6648 | 37.9478 | 48.4627 | -1724.2397
2042-11-26 15:01 | -5959.38 | 6.6648 | 37.9892 | 48.4627 | -1746.5219
2042-11-27 16:01 | -7258.64 | 6.6648 | 37.3811 | 48.4627 | -2127.2974
2042-11-28 17:01 | -6429.49 | 6.6648 | 37.7238 | 48.4627 | -1884.2975
2042-11-29 18:01 | -7745.3 | 6.6648 | 37.1006 | 48.4627 | -2269.9234
2042-11-30 19:01 | -8142.59 | 6.6648 | 36.8018 | 48.4627 | -2386.3576
2042-12-01 20:01 | -8228.92 | 6.6648 | 36.6579 | 48.4627 | -2411.6584
2042-12-02 21:01 | -8401.54 | 6.6648 | 36.5171 | 48.4627 | -2462.2483
2042-12-03 22:01 | -8757.41 | 6.6648 | 36.2961 | 48.4627 | -2566.5435
2042-12-04 23:01 | -8947.28 | 6.6648 | 36.1176 | 48.4627 | -2622.1889
2042-12-06 00:01 | -10498.4 | 6.6648 | 35.2629 | 48.4627 | -3076.7773
2042-12-07 01:01 | -10719.5 | 6.6648 | 34.9531 | 48.4627 | -3141.5753
2042-12-08 02:01 | -10877.3 | 6.6648 | 34.7292 | 48.4627 | -3187.8219
2042-12-09 03:01 | -10950.2 | 6.6648 | 34.5851 | 48.4627 | -3209.1868
2042-12-10 04:01 | -10806.4 | 6.6648 | 34.5726 | 48.4627 | -3167.0432
2042-12-11 05:01 | -10639.7 | 6.6648 | 34.5894 | 48.4627 | -3118.1883
2042-12-12 06:01 | -10438.6 | 6.6648 | 34.672 | 48.4627 | -3059.2517
2042-12-13 07:01 | -9520.49 | 6.6648 | 35.1363 | 48.4627 | -2790.1802
2042-12-14 08:01 | -8703.2 | 6.6648 | 35.6253 | 48.4627 | -2550.6561
2042-12-15 09:01 | -8322.4 | 6.6648 | 35.9265 | 48.4627 | -2439.0547
2042-12-16 10:01 | -7866.4 | 6.6648 | 36.241 | 48.4627 | -2305.4143
2042-12-17 11:01 | -6622.74 | 6.6648 | 36.9609 | 48.4627 | -1940.9335
2042-12-18 12:01 | -5655.89 | 6.6648 | 37.6372 | 48.4627 | -1657.5777
2042-12-19 13:01 | -5193.45 | 6.6648 | 38.0713 | 48.4627 | -1522.0499
2042-12-20 14:01 | -5837.4 | 6.6648 | 37.9034 | 48.4627 | -1710.7731
2042-12-21 15:01 | -6138.6 | 6.6648 | 37.8001 | 48.4627 | -1799.0461
2042-12-22 16:01 | -6453.12 | 6.6648 | 37.6751 | 48.4627 | -1891.2228
2042-12-23 17:01 | -5335.23 | 6.6648 | 38.2541 | 48.4627 | -1563.6016
2042-12-24 18:01 | -6135.89 | 6.6648 | 37.9714 | 48.4627 | -1798.2518
2042-12-25 19:01 | -6518.88 | 6.6648 | 37.7729 | 48.4627 | -1910.4951
2042-12-26 20:01 | -6843.26 | 6.6648 | 37.5777 | 48.4627 | -2005.5615
2042-12-27 21:01 | -7127.62 | 6.6648 | 37.412 | 48.4627 | -2088.8992
2042-12-28 22:01 | -7420.54 | 6.6648 | 37.2415 | 48.4627 | -2174.7456
2042-12-29 23:01 | -7681.59 | 6.6648 | 37.0537 | 48.4627 | -2251.2518
2042-12-31 00:01 | -8950.99 | 6.6648 | 36.3574 | 48.4627 | -2623.2762
2043-01-01 01:01 | -9476.43 | 6.6648 | 35.9377 | 48.4627 | -2777.2675
2043-01-02 02:01 | -9321.08 | 6.6648 | 35.8863 | 48.4627 | -2731.7389
2043-01-03 03:01 | -9555.74 | 6.6648 | 35.7119 | 48.4627 | -2800.5109
2043-01-04 04:01 | -9712.39 | 6.6648 | 35.5669 | 48.4627 | -2846.4205
2043-01-05 05:01 | -9566.62 | 6.6648 | 35.5616 | 48.4627 | -2803.6996
2043-01-06 06:01 | -9649.08 | 6.6648 | 35.4926 | 48.4627 | -2827.8662
2043-01-07 07:01 | -9478.75 | 6.6648 | 35.5484 | 48.4627 | -2777.9474
2043-01-08 08:01 | -8287.89 | 6.6648 | 36.1378 | 48.4627 | -2428.9408
2043-01-09 09:01 | -6863.41 | 6.6648 | 36.963 | 48.4627 | -2011.4669
2043-01-10 10:01 | -5641.84 | 6.6648 | 37.7709 | 48.4627 | -1653.4601
2043-01-11 11:01 | -4726.35 | 6.6648 | 38.4458 | 48.4627 | -1385.1565
2043-01-12 12:01 | -3772.44 | 6.6648 | 39.1493 | 48.4627 | -1105.593
2043-01-13 13:01 | -5657.9 | 6.6648 | 38.4258 | 48.4627 | -1658.1668
2043-01-14 14:01 | -6773.62 | 6.6648 | 37.8295 | 48.4627 | -1985.1521
2043-01-15 15:01 | -7162.8 | 6.6648 | 37.5284 | 48.4627 | -2099.2095
2043-01-16 16:01 | -6788.6 | 6.6648 | 37.6569 | 48.4627 | -1989.5423
2043-01-17 17:01 | -6854.19 | 6.6648 | 37.6177 | 48.4627 | -2008.7648
2043-01-18 18:01 | -6998.6 | 6.6648 | 37.5172 | 48.4627 | -2051.0872
2043-01-19 19:01 | -7996.41 | 6.6648 | 36.9916 | 48.4627 | -2343.5164
2043-01-20 20:01 | -8426.12 | 6.6648 | 36.6752 | 48.4627 | -2469.452
2043-01-21 21:01 | -9498.39 | 6.6648 | 36.0299 | 48.4627 | -2783.7033
2043-01-22 22:01 | -9977.6 | 6.6648 | 35.6102 | 48.4627 | -2924.1459
2043-01-23 23:01 | -10816.1 | 6.6648 | 35.0104 | 48.4627 | -3169.886
2043-01-25 00:01 | -10771.9 | 6.6648 | 34.8303 | 48.4627 | -3156.9323
2043-01-26 01:01 | -10765.3 | 6.6648 | 34.7179 | 48.4627 | -3154.998
2043-01-27 02:01 | -11602.4 | 6.6648 | 34.2081 | 48.4627 | -3400.3278
2043-01-28 03:01 | -11468 | 6.6648 | 34.1333 | 48.4627 | -3360.939
2043-01-29 04:01 | -11733.7 | 6.6648 | 33.9076 | 48.4627 | -3438.808
2043-01-30 05:01 | -11605.7 | 6.6648 | 33.8849 | 48.4627 | -3401.2949
2043-01-31 06:01 | -10919.6 | 6.6648 | 34.1698 | 48.4627 | -3200.2189
2043-02-01 07:01 | -10876.4 | 6.6648 | 34.1996 | 48.4627 | -3187.5582
2043-02-02 08:01 | -10564.6 | 6.6648 | 34.3472 | 48.4627 | -3096.1786
2043-02-03 09:01 | -10767.7 | 6.6648 | 34.2409 | 48.4627 | -3155.7014
2043-02-04 10:01 | -9988.58 | 6.6648 | 34.6035 | 48.4627 | -2927.3638
2043-02-05 11:01 | -9317.05 | 6.6648 | 34.9867 | 48.4627 | -2730.5578
2043-02-06 12:01 | -9022.8 | 6.6648 | 35.1965 | 48.4627 | -2644.3217
2043-02-07 13:01 | -9042.44 | 6.6648 | 35.2334 | 48.4627 | -2650.0776
2043-02-08 14:01 | -9281.8 | 6.6648 | 35.1343 | 48.4627 | -2720.2271
2043-02-09 15:01 | -8662.93 | 6.6648 | 35.4506 | 48.4627 | -2538.8542
2043-02-10 16:01 | -7916.7 | 6.6648 | 35.8945 | 48.4627 | -2320.1557
2043-02-11 17:01 | -7369.27 | 6.6648 | 36.276 | 48.4627 | -2159.7198
2043-02-12 18:01 | -7046.15 | 6.6648 | 36.5426 | 48.4627 | -2065.0227
2043-02-13 19:01 | -7184.05 | 6.6648 | 36.57 | 48.4627 | -2105.4372
2043-02-14 20:01 | -7291.22 | 6.6648 | 36.577 | 48.4627 | -2136.8456
2043-02-15 21:01 | -7929.28 | 6.6648 | 36.2975 | 48.4627 | -2323.8426
2043-02-16 22:01 | -7865.05 | 6.6648 | 36.3069 | 48.4627 | -2305.0186
2043-02-17 23:01 | -8446.8 | 6.6648 | 36.0122 | 48.4627 | -2475.5127
2043-02-19 00:01 | -8715.24 | 6.6648 | 35.8293 | 48.4627 | -2554.1847
2043-02-20 01:01 | -8879.13 | 6.6648 | 35.7 | 48.4627 | -2602.2161
2043-02-21 02:01 | -8797.46 | 6.6648 | 35.7132 | 48.4627 | -2578.281
2043-02-22 03:01 | -9004.31 | 6.6648 | 35.6057 | 48.4627 | -2638.9028
2043-02-23 04:01 | -10055.8 | 6.6648 | 35.0393 | 48.4627 | -2947.0641
2043-02-24 05:01 | -10530.9 | 6.6648 | 34.6737 | 48.4627 | -3086.3021
2043-02-25 06:01 | -10598.2 | 6.6648 | 34.5186 | 48.4627 | -3106.0258
2043-02-26 07:01 | -10672.3 | 6.6648 | 34.4022 | 48.4627 | -3127.7424
2043-02-27 08:01 | -9573.99 | 6.6648 | 34.8893 | 48.4627 | -2805.8595
2043-02-28 09:01 | -9155.71 | 6.6648 | 35.1476 | 48.4627 | -2683.2737
2043-03-01 10:01 | -8301.74 | 6.6648 | 35.6346 | 48.4627 | -2432.9998
2043-03-02 11:01 | -7344.41 | 6.6648 | 36.2204 | 48.4627 | -2152.4341
2043-03-03 12:01 | -6742.37 | 6.6648 | 36.6716 | 48.4627 | -1975.9936
2043-03-04 13:01 | -6888.93 | 6.6648 | 36.7441 | 48.4627 | -2018.9461
2043-03-05 14:01 | -7073.64 | 6.6648 | 36.7189 | 48.4627 | -2073.0792
2043-03-06 15:01 | -7789.44 | 6.6648 | 36.3887 | 48.4627 | -2282.8595
2043-03-07 16:01 | -8316.61 | 6.6648 | 36.0875 | 48.4627 | -2437.3578
2043-03-08 17:01 | -8766.84 | 6.6648 | 35.7932 | 48.4627 | -2569.3072
2043-03-09 18:01 | -8793.39 | 6.6648 | 35.7023 | 48.4627 | -2577.0882
2043-03-10 19:01 | -9221.59 | 6.6648 | 35.4415 | 48.4627 | -2702.5812
2043-03-11 20:01 | -9696.7 | 6.6648 | 35.122 | 48.4627 | -2841.8222
2043-03-12 21:01 | -10525.8 | 6.6648 | 34.6062 | 48.4627 | -3084.8075
2043-03-13 22:01 | -11722 | 6.6648 | 33.8527 | 48.4627 | -3435.3791
2043-03-14 23:01 | -11938.4 | 6.6648 | 33.5302 | 48.4627 | -3498.7997
2043-03-16 00:01 | -12139.9 | 6.6648 | 33.2665 | 48.4627 | -3557.8535
2043-03-17 01:01 | -12208.1 | 6.6648 | 33.0993 | 48.4627 | -3577.8409
2043-03-18 02:01 | -12272.2 | 6.6648 | 32.9522 | 48.4627 | -3596.6268
2043-03-19 03:01 | -12292.1 | 6.6648 | 32.8495 | 48.4627 | -3602.4589
2043-03-20 04:01 | -12258 | 6.6648 | 32.8056 | 48.4627 | -3592.4652
2043-03-21 05:01 | -12212 | 6.6648 | 32.7822 | 48.4627 | -3578.9839
2043-03-22 06:01 | -12084.1 | 6.6648 | 32.8064 | 48.4627 | -3541.5001
2043-03-23 07:01 | -12005.1 | 6.6648 | 32.8193 | 48.4627 | -3518.3475
2043-03-24 08:01 | -11165.3 | 6.6648 | 33.2235 | 48.4627 | -3272.2264
2043-03-25 09:01 | -10415.9 | 6.6648 | 33.6648 | 48.4627 | -3052.599
2043-03-26 10:01 | -9357.69 | 6.6648 | 34.3062 | 48.4627 | -2742.4682
2043-03-27 11:01 | -8382.43 | 6.6648 | 34.9494 | 48.4627 | -2456.6477
2043-03-28 12:01 | -7768.16 | 6.6648 | 35.436 | 48.4627 | -2276.623
2043-03-29 13:01 | -7668.75 | 6.6648 | 35.652 | 48.4627 | -2247.4888
2043-03-30 14:01 | -7799.58 | 6.6648 | 35.6988 | 48.4627 | -2285.8313
2043-03-31 15:01 | -8519.97 | 6.6648 | 35.401 | 48.4627 | -2496.9567
2043-04-01 16:01 | -8901.55 | 6.6648 | 35.1911 | 48.4627 | -2608.7868
2043-04-02 17:01 | -9130.82 | 6.6648 | 35.0379 | 48.4627 | -2675.9792
2043-04-03 18:01 | -9336.54 | 6.6648 | 34.897 | 48.4627 | -2736.2698
2043-04-04 19:01 | -9876.87 | 6.6648 | 34.5837 | 48.4627 | -2894.6249
2043-04-05 20:01 | -10363.8 | 6.6648 | 34.2563 | 48.4627 | -3037.33
2043-04-06 21:01 | -11157.9 | 6.6648 | 33.7618 | 48.4627 | -3270.0577
2043-04-07 22:01 | -11482.4 | 6.6648 | 33.4632 | 48.4627 | -3365.1593
2043-04-08 23:01 | -12024.5 | 6.6648 | 33.0674 | 48.4627 | -3524.0331
2043-04-10 00:01 | -12345.6 | 6.6648 | 32.7654 | 48.4627 | -3618.1382
2043-04-11 01:01 | -12546.3 | 6.6648 | 32.534 | 48.4627 | -3676.9576
2043-04-12 02:01 | -12769.2 | 6.6648 | 32.3074 | 48.4627 | -3742.2831
2043-04-13 03:01 | -12973 | 6.6648 | 32.1045 | 48.4627 | -3802.011
2043-04-14 04:01 | -13046.8 | 6.6648 | 31.9731 | 48.4627 | -3823.6396
2043-04-15 05:01 | -13089.5 | 6.6648 | 31.8761 | 48.4627 | -3836.1538
2043-04-16 06:01 | -12997 | 6.6648 | 31.8589 | 48.4627 | -3809.0447
2043-04-17 07:01 | -12707.3 | 6.6648 | 31.9637 | 48.4627 | -3724.142
2043-04-18 08:01 | -11996.6 | 6.6648 | 32.3118 | 48.4627 | -3515.8564
2043-04-19 09:01 | -11057.4 | 6.6648 | 32.8388 | 48.4627 | -3240.604
2043-04-20 10:01 | -8767.95 | 6.6648 | 34.1115 | 48.4627 | -2569.6325
2043-04-21 11:01 | -7334.68 | 6.6648 | 35.1128 | 48.4627 | -2149.5825
2043-04-22 12:01 | -6345.52 | 6.6648 | 35.9017 | 48.4627 | -1859.6883
2043-04-23 13:01 | -6539.59 | 6.6648 | 36.0641 | 48.4627 | -1916.5646
2043-04-24 14:01 | -6857.93 | 6.6648 | 36.0593 | 48.4627 | -2009.8609
2043-04-25 15:01 | -7902.4 | 6.6648 | 35.6252 | 48.4627 | -2315.9648
2043-04-26 16:01 | -8751.85 | 6.6648 | 35.1701 | 48.4627 | -2564.914
2043-04-27 17:01 | -9264.15 | 6.6648 | 34.8333 | 48.4627 | -2715.0544
2043-04-28 18:01 | -9658.15 | 6.6648 | 34.5518 | 48.4627 | -2830.5244
2043-04-29 19:01 | -10178 | 6.6648 | 34.2144 | 48.4627 | -2982.8774
2043-04-30 20:01 | -10288.3 | 6.6648 | 34.0675 | 48.4627 | -3015.2031
2043-05-01 21:01 | -11058 | 6.6648 | 33.6193 | 48.4627 | -3240.7799
2043-05-02 22:01 | -11229.5 | 6.6648 | 33.4155 | 48.4627 | -3291.0416
2043-05-03 23:01 | -11813.7 | 6.6648 | 33.0213 | 48.4627 | -3462.2537
2043-05-05 00:01 | -11893.7 | 6.6648 | 32.8539 | 48.4627 | -3485.6994
2043-05-06 01:01 | -11993.6 | 6.6648 | 32.7092 | 48.4627 | -3514.9772
2043-05-07 02:01 | -11974.7 | 6.6648 | 32.64 | 48.4627 | -3509.4381
2043-05-08 03:01 | -11996.9 | 6.6648 | 32.5799 | 48.4627 | -3515.9443
2043-05-09 04:01 | -11983.1 | 6.6648 | 32.548 | 48.4627 | -3511.8999
2043-05-10 05:01 | -11952.5 | 6.6648 | 32.5402 | 48.4627 | -3502.932
2043-05-11 06:01 | -11901.1 | 6.6648 | 32.549 | 48.4627 | -3487.8681
2043-05-12 07:01 | -11138.9 | 6.6648 | 32.9313 | 48.4627 | -3264.4893
2043-05-13 08:01 | -10623.8 | 6.6648 | 33.255 | 48.4627 | -3113.5284
2043-05-14 09:01 | -11225.2 | 6.6648 | 33.0229 | 48.4627 | -3289.7814
2043-05-15 10:01 | -11298.3 | 6.6648 | 32.948 | 48.4627 | -3311.2049
2043-05-16 11:01 | -11004.2 | 6.6648 | 33.0633 | 48.4627 | -3225.0127
2043-05-17 12:01 | -11560.8 | 6.6648 | 32.7824 | 48.4627 | -3388.136
2043-05-18 13:01 | -12407.2 | 6.6648 | 32.2739 | 48.4627 | -3636.1914
2043-05-19 14:01 | -13284.8 | 6.6648 | 31.6731 | 48.4627 | -3893.3906
2043-05-20 15:01 | -13753.3 | 6.6648 | 31.2597 | 48.4627 | -4030.6943
2043-05-21 16:01 | -14155.8 | 6.6648 | 30.8975 | 48.4627 | -4148.6555
2043-05-22 17:01 | -13915.5 | 6.6648 | 30.8649 | 48.4627 | -4078.2305
2043-05-23 18:01 | -13900.7 | 6.6648 | 30.7812 | 48.4627 | -4073.893
2043-05-24 19:01 | -14472.9 | 6.6648 | 30.4069 | 48.4627 | -4241.5883
2043-05-25 20:01 | -14882.9 | 6.6648 | 30.0626 | 48.4627 | -4361.7474
2043-05-26 21:01 | 0 | 0 | 37.6027 | 48.4627 | 0
2043-05-27 22:01 | -13098.5 | 6.6648 | 32.2728 | 48.4627 | -3838.7914
2043-05-28 23:01 | -14358.5 | 6.6648 | 31.0763 | 48.4627 | -4208.061
2043-05-30 00:01 | -15663.1 | 6.6648 | 29.9338 | 48.4627 | -4590.4015
2043-05-31 01:01 | 0 | 0 | 37.8041 | 48.4627 | 0
2043-06-01 02:01 | -12378.4 | 6.6648 | 32.8771 | 48.4627 | -3627.7509
2043-06-02 03:01 | -14550.8 | 6.6648 | 31.1381 | 48.4627 | -4264.4185
2043-06-03 04:01 | -14619 | 6.6648 | 30.593 | 48.4627 | -4284.406
2043-06-04 05:01 | -14910.2 | 6.6648 | 30.3498 | 48.4627 | -4369.7483
2043-06-05 06:01 | -14896.8 | 6.6648 | 30.3117 | 48.4627 | -4365.8211
2043-06-06 07:01 | -14588.3 | 6.6648 | 30.1855 | 48.4627 | -4275.4087
2043-06-07 08:01 | -14600.8 | 6.6648 | 30.1336 | 48.4627 | -4279.0721
2043-06-08 09:01 | 0 | 0 | 37.5104 | 48.4627 | 0
2043-06-09 10:01 | -12475.1 | 6.6648 | 32.4775 | 48.4627 | -3656.0909
2043-06-10 11:01 | -14469.1 | 6.6648 | 31.0202 | 48.4627 | -4240.4746
2043-06-11 12:01 | -13823.2 | 6.6648 | 30.8764 | 48.4627 | -4051.18
2043-06-12 13:01 | -14187.9 | 6.6648 | 30.5466 | 48.4627 | -4158.063
2043-06-13 14:01 | -14824.1 | 6.6648 | 30.1658 | 48.4627 | -4344.5148
2043-06-14 15:01 | 0 | 0 | 37.4718 | 48.4627 | 0
2043-06-15 16:01 | -12283.2 | 6.6648 | 32.5245 | 48.4627 | -3599.8506
2043-06-16 17:01 | -13912.9 | 6.6648 | 31.2952 | 48.4627 | -4077.4685
2043-06-17 18:01 | -14733 | 6.6648 | 30.4394 | 48.4627 | -4317.8161
2043-06-18 19:01 | -15235.8 | 6.6648 | 30.0479 | 48.4627 | -4465.1722
2043-06-19 20:01 | 0 | 0 | 37.8077 | 48.4627 | 0
2043-06-20 21:01 | -12231.2 | 6.6648 | 32.5466 | 48.4627 | -3584.6109
2043-06-21 22:01 | -14228.4 | 6.6648 | 31.0931 | 48.4627 | -4169.9324
2043-06-22 23:01 | -14462.3 | 6.6648 | 30.5143 | 48.4627 | -4238.4817
2043-06-24 00:01 | -15070.3 | 6.6648 | 30.1263 | 48.4627 | -4416.6689
2043-06-25 01:01 | -14841 | 6.6648 | 30.1154 | 48.4627 | -4349.4677
2043-06-26 02:01 | 0 | 0 | 37.4987 | 48.4627 | 0
2043-06-27 03:01 | -12254.7 | 6.6648 | 32.4822 | 48.4627 | -3591.498
2043-06-28 04:01 | -14471.9 | 6.6648 | 30.9434 | 48.4627 | -4241.2952
2043-06-29 05:01 | -14609.5 | 6.6648 | 30.3986 | 48.4627 | -4281.6218
2043-06-30 06:01 | -14564.8 | 6.6648 | 30.3538 | 48.4627 | -4268.5215
2043-07-01 07:01 | -14784.1 | 6.6648 | 30.2355 | 48.4627 | -4332.792
2043-07-02 08:01 | 0 | 0 | 37.4576 | 48.4627 | 0
2043-07-03 09:01 | -12089.1 | 6.6648 | 32.5464 | 48.4627 | -3542.9655
2043-07-04 10:01 | -13837.8 | 6.6648 | 31.2685 | 48.4627 | -4055.4589
2043-07-05 11:01 | -14118.7 | 6.6648 | 30.7033 | 48.4627 | -4137.7825
2043-07-06 12:01 | -14809.8 | 6.6648 | 30.2769 | 48.4627 | -4340.3239
2043-07-07 13:01 | -14948.4 | 6.6648 | 30.1251 | 48.4627 | -4380.9436
2043-07-08 14:01 | 0 | 0 | 37.415 | 48.4627 | 0
2043-07-09 15:01 | -12333.3 | 6.6648 | 32.3896 | 48.4627 | -3614.5334
2043-07-10 16:01 | -14210.6 | 6.6648 | 31.0192 | 48.4627 | -4164.7157
2043-07-11 17:01 | -15006.1 | 6.6648 | 30.1576 | 48.4627 | -4397.8538
2043-07-12 18:01 | -15844.5 | 6.6648 | 29.5968 | 48.4627 | -4643.5646
2043-07-13 19:01 | 0 | 0 | 37.6454 | 48.4627 | 0
2043-07-14 20:01 | -12301.5 | 6.6648 | 32.3852 | 48.4627 | -3605.2138
2043-07-15 21:01 | -14668.1 | 6.6648 | 30.7188 | 48.4627 | -4298.7958
2043-07-16 22:01 | -14746.6 | 6.6648 | 30.1777 | 48.4627 | -4321.8018
2043-07-17 23:01 | -15066.9 | 6.6648 | 29.9356 | 48.4627 | -4415.6725
2043-07-19 00:01 | 0 | 0 | 37.6799 | 48.4627 | 0
2043-07-20 01:01 | -12494.8 | 6.6648 | 32.4399 | 48.4627 | -3661.8644
2043-07-21 02:01 | -14449 | 6.6648 | 30.8256 | 48.4627 | -4234.5839
2043-07-22 03:01 | -14783.5 | 6.6648 | 30.177 | 48.4627 | -4332.6162
2043-07-23 04:01 | -14810.2 | 6.6648 | 30.0769 | 48.4627 | -4340.4412
2043-07-24 05:01 | -14741.2 | 6.6648 | 30.1001 | 48.4627 | -4320.2193
2043-07-25 06:01 | 0 | 0 | 37.461 | 48.4627 | 0
2043-07-26 07:01 | -12214.2 | 6.6648 | 32.4631 | 48.4627 | -3579.6287
2043-07-27 08:01 | -14311.4 | 6.6648 | 30.9348 | 48.4627 | -4194.2573
2043-07-28 09:01 | -14699.1 | 6.6648 | 30.2461 | 48.4627 | -4307.881
2043-07-29 10:01 | -13658.1 | 6.6648 | 30.6832 | 48.4627 | -4002.794
2043-07-30 11:01 | -14168.4 | 6.6648 | 30.5005 | 48.4627 | -4152.3481
2043-07-31 12:01 | -15295.4 | 6.6648 | 29.5426 | 48.4627 | -4482.6392
2043-08-01 13:01 | 0 | 0 | 37.242 | 48.4627 | 0
2043-08-02 14:01 | -11923.9 | 6.6648 | 32.4785 | 48.4627 | -3494.5501
2043-08-03 15:01 | -14296.5 | 6.6648 | 30.8896 | 48.4627 | -4189.8906
2043-08-04 16:01 | -14485.2 | 6.6648 | 30.3053 | 48.4627 | -4245.1931
2043-08-05 17:01 | -14462.4 | 6.6648 | 30.228 | 48.4627 | -4238.511
2043-08-06 18:01 | -14602.8 | 6.6648 | 30.0395 | 48.4627 | -4279.6582
2043-08-07 19:01 | 0 | 0 | 37.2267 | 48.4627 | 0
2043-08-08 20:01 | -12262.2 | 6.6648 | 32.2536 | 48.4627 | -3593.6961
2043-08-09 21:01 | -14542.1 | 6.6648 | 30.6922 | 48.4627 | -4261.8688
2043-08-10 22:01 | -14610.5 | 6.6648 | 30.175 | 48.4627 | -4281.9149
2043-08-11 23:01 | -14884.8 | 6.6648 | 29.9584 | 48.4627 | -4362.3043
2043-08-13 00:01 | 0 | 0 | 37.5384 | 48.4627 | 0
2043-08-14 01:01 | -12303 | 6.6648 | 32.283 | 48.4627 | -3605.6534
2043-08-15 02:01 | -14443.6 | 6.6648 | 30.7182 | 48.4627 | -4233.0013
2043-08-16 03:01 | -14588.8 | 6.6648 | 30.1781 | 48.4627 | -4275.5552
2043-08-17 04:01 | -14646.9 | 6.6648 | 30.0773 | 48.4627 | -4292.5827
2043-08-18 05:01 | -14648.5 | 6.6648 | 30.0635 | 48.4627 | -4293.0516
2043-08-19 06:01 | 0 | 0 | 37.3029 | 48.4627 | 0
2043-08-20 07:01 | -12075.4 | 6.6648 | 32.3535 | 48.4627 | -3538.9504
2043-08-21 08:01 | -13999.8 | 6.6648 | 30.953 | 48.4627 | -4102.9364
2043-08-22 09:01 | -14452.9 | 6.6648 | 30.2896 | 48.4627 | -4235.7269
2043-08-23 10:01 | -14157.1 | 6.6648 | 30.3519 | 48.4627 | -4149.0364
2043-08-24 11:01 | -14857.3 | 6.6648 | 30.0027 | 48.4627 | -4354.2448
2043-08-25 12:01 | 0 | 0 | 37.2442 | 48.4627 | 0
2043-08-26 13:01 | -12115.5 | 6.6648 | 32.3169 | 48.4627 | -3550.7025
2043-08-27 14:01 | -14302.5 | 6.6648 | 30.7831 | 48.4627 | -4191.649
2043-08-28 15:01 | -14317.4 | 6.6648 | 30.3139 | 48.4627 | -4196.0157
2043-08-29 16:01 | -14223 | 6.6648 | 30.2989 | 48.4627 | -4168.3498
2043-08-30 17:01 | -14837.2 | 6.6648 | 29.9951 | 48.4627 | -4348.3541
2043-08-31 18:01 | 0 | 0 | 37.2287 | 48.4627 | 0
2043-09-01 19:01 | -11973 | 6.6648 | 32.345 | 48.4627 | -3508.9399
2043-09-02 20:01 | -14065.8 | 6.6648 | 30.903 | 48.4627 | -4122.2791
2043-09-03 21:01 | -14890.1 | 6.6648 | 30.0227 | 48.4627 | -4363.8575
2043-09-04 22:01 | 0 | 0 | 37.5587 | 48.4627 | 0
2043-09-05 23:01 | -12458.9 | 6.6648 | 32.5865 | 48.4627 | -3651.3432
2043-09-07 00:01 | -14188 | 6.6648 | 30.8602 | 48.4627 | -4158.0923
2043-09-08 01:01 | -14343.2 | 6.6648 | 30.2643 | 48.4627 | -4203.577
2043-09-09 02:01 | -14588.7 | 6.6648 | 30.0705 | 48.4627 | -4275.5259
2043-09-10 03:01 | -14873.6 | 6.6648 | 29.8983 | 48.4627 | -4359.0219
2043-09-11 04:01 | 0 | 0 | 37.2828 | 48.4627 | 0
2043-09-12 05:01 | -12003.9 | 6.6648 | 32.5148 | 48.4627 | -3517.9958
2043-09-13 06:01 | -13811 | 6.6648 | 31.0292 | 48.4627 | -4047.6045
2043-09-14 07:01 | -14654.4 | 6.6648 | 30.1488 | 48.4627 | -4294.7807
2043-09-15 08:01 | -15158.6 | 6.6648 | 29.7675 | 48.4627 | -4442.5471
2043-09-16 09:01 | 0 | 0 | 37.4916 | 48.4627 | 0
2043-09-17 10:01 | -11928.9 | 6.6648 | 32.4429 | 48.4627 | -3496.0155
2043-09-18 11:01 | -13886.1 | 6.6648 | 31.0457 | 48.4627 | -4069.6142
2043-09-19 12:01 | -15099.7 | 6.6648 | 29.9243 | 48.4627 | -4425.2852
2043-09-20 13:01 | 0 | 0 | 37.5061 | 48.4627 | 0
2043-09-21 14:01 | -11718.5 | 6.6648 | 32.9112 | 48.4627 | -3434.3533
2043-09-22 15:01 | -14930.6 | 6.6648 | 30.6946 | 48.4627 | -4375.7269
2043-09-23 16:01 | -13118.6 | 6.6648 | 30.9267 | 48.4627 | -3844.6821
2043-09-24 17:01 | -12451.8 | 6.6648 | 31.3238 | 48.4627 | -3649.2623
2043-09-25 18:01 | -11880.9 | 6.6648 | 31.7133 | 48.4627 | -3481.9481
2043-09-26 19:01 | -11647.1 | 6.6648 | 31.6918 | 48.4627 | -3413.4281
2043-09-27 20:01 | -11483.3 | 6.6648 | 31.8313 | 48.4627 | -3365.423
2043-09-28 21:01 | -11677.8 | 6.6648 | 31.7282 | 48.4627 | -3422.4253
2043-09-29 22:01 | -11709.8 | 6.6648 | 31.6861 | 48.4627 | -3431.8036
2043-09-30 23:01 | -11870.3 | 6.6648 | 31.6365 | 48.4627 | -3478.8415
2043-10-02 00:01 | -12032.1 | 6.6648 | 31.5542 | 48.4627 | -3526.2604
2043-10-03 01:01 | -11950.8 | 6.6648 | 31.4867 | 48.4627 | -3502.4337
2043-10-04 02:01 | -11886.8 | 6.6648 | 31.5133 | 48.4627 | -3483.6772
2043-10-05 03:01 | -11821.7 | 6.6648 | 31.5909 | 48.4627 | -3464.5983
2043-10-06 04:01 | -11675.8 | 6.6648 | 31.6392 | 48.4627 | -3421.8392
2043-10-07 05:01 | -11165.8 | 6.6648 | 31.9316 | 48.4627 | -3272.373
2043-10-08 06:01 | -10762.6 | 6.6648 | 32.1878 | 48.4627 | -3154.2067
2043-10-09 07:01 | -10772 | 6.6648 | 32.2714 | 48.4627 | -3156.9616
2043-10-10 08:01 | -10380.8 | 6.6648 | 32.518 | 48.4627 | -3042.3122
2043-10-11 09:01 | -9654.15 | 6.6648 | 32.9183 | 48.4627 | -2829.3521
2043-10-12 10:01 | -8347.66 | 6.6648 | 33.72 | 48.4627 | -2446.4576
2043-10-13 11:01 | -7174.38 | 6.6648 | 34.5455 | 48.4627 | -2102.6032
2043-10-14 12:01 | -6302.81 | 6.6648 | 35.2268 | 48.4627 | -1847.1713
2043-10-15 13:01 | -5943.05 | 6.6648 | 35.613 | 48.4627 | -1741.736
2043-10-16 14:01 | -6140.37 | 6.6648 | 35.7142 | 48.4627 | -1799.5648
2043-10-17 15:01 | -7451.96 | 6.6648 | 35.202 | 48.4627 | -2183.9539
2043-10-18 16:01 | -8053.48 | 6.6648 | 34.8943 | 48.4627 | -2360.242
2043-10-19 17:01 | -8884.15 | 6.6648 | 34.4451 | 48.4627 | -2603.6873
2043-10-20 18:01 | -9025.25 | 6.6648 | 34.275 | 48.4627 | -2645.0397
2043-10-21 19:01 | -9726.76 | 6.6648 | 33.8554 | 48.4627 | -2850.632
2043-10-22 20:01 | -10161.8 | 6.6648 | 33.5453 | 48.4627 | -2978.1296
2043-10-23 21:01 | -11406.2 | 6.6648 | 32.8278 | 48.4627 | -3342.8272
2043-10-24 22:01 | -11798.1 | 6.6648 | 32.4295 | 48.4627 | -3457.6818
2043-10-25 23:01 | -12212.5 | 6.6648 | 32.0761 | 48.4627 | -3579.1304
2043-10-27 00:01 | -12781 | 6.6648 | 31.6334 | 48.4627 | -3745.7413
2043-10-28 01:01 | -13082.4 | 6.6648 | 31.3197 | 48.4627 | -3834.073
2043-10-29 02:01 | -13227.5 | 6.6648 | 31.1023 | 48.4627 | -3876.5976
2043-10-30 03:01 | -13264 | 6.6648 | 30.9856 | 48.4627 | -3887.2947
2043-10-31 04:01 | -13393.2 | 6.6648 | 30.8116 | 48.4627 | -3925.1595
2043-11-01 05:01 | -13531.1 | 6.6648 | 30.6611 | 48.4627 | -3965.574
2043-11-02 06:01 | -13645.7 | 6.6648 | 30.5124 | 48.4627 | -3999.1599
2043-11-03 07:01 | -13476 | 6.6648 | 30.5327 | 48.4627 | -3949.4257
2043-11-04 08:01 | -13021.6 | 6.6648 | 30.7327 | 48.4627 | -3816.2542
2043-11-05 09:01 | -12510.2 | 6.6648 | 30.9802 | 48.4627 | -3666.3777
2043-11-06 10:01 | -12186.4 | 6.6648 | 31.1802 | 48.4627 | -3571.4813
2043-11-07 11:01 | -10714.5 | 6.6648 | 31.9751 | 48.4627 | -3140.11
2043-11-08 12:01 | -9833.28 | 6.6648 | 32.5929 | 48.4627 | -2881.8499
2043-11-09 13:01 | -9373.3 | 6.6648 | 32.9615 | 48.4627 | -2747.0431
2043-11-10 14:01 | -9289.57 | 6.6648 | 33.1393 | 48.4627 | -2722.5042
2043-11-11 15:01 | -9917.36 | 6.6648 | 32.9248 | 48.4627 | -2906.4913
2043-11-12 16:01 | -10989.7 | 6.6648 | 32.3983 | 48.4627 | -3220.7631
2043-11-13 17:01 | -9622.76 | 6.6648 | 33.0224 | 48.4627 | -2820.1526
2043-11-14 18:01 | -10911.2 | 6.6648 | 32.4674 | 48.4627 | -3197.7571
2043-11-15 19:01 | -11045.7 | 6.6648 | 32.3217 | 48.4627 | -3237.1751
2043-11-16 20:01 | -11089.6 | 6.6648 | 32.2405 | 48.4627 | -3250.0409
2043-11-17 21:01 | -11287.8 | 6.6648 | 32.1278 | 48.4627 | -3308.1276
2043-11-18 22:01 | -11682.3 | 6.6648 | 31.9161 | 48.4627 | -3423.7442
2043-11-19 23:01 | -11834.5 | 6.6648 | 31.7674 | 48.4627 | -3468.3496
2043-11-21 00:01 | -12416.2 | 6.6648 | 31.4058 | 48.4627 | -3638.829
2043-11-22 01:01 | -13022.9 | 6.6648 | 31.0004 | 48.4627 | -3816.6352
2043-11-23 02:01 | -13046.5 | 6.6648 | 30.8658 | 48.4627 | -3823.5517
2043-11-24 03:01 | -13015 | 6.6648 | 30.8073 | 48.4627 | -3814.32
2043-11-25 04:01 | -13007.1 | 6.6648 | 30.7715 | 48.4627 | -3812.0047
2043-11-26 05:01 | -13069.2 | 6.6648 | 30.6903 | 48.4627 | -3830.2044
2043-11-27 06:01 | -13110.2 | 6.6648 | 30.6169 | 48.4627 | -3842.2203
2043-11-28 07:01 | -12847.8 | 6.6648 | 30.7206 | 48.4627 | -3765.3185
2043-11-29 08:01 | -12436.2 | 6.6648 | 30.9307 | 48.4627 | -3644.6904
2043-11-30 09:01 | -12297 | 6.6648 | 31.0291 | 48.4627 | -3603.8949
2043-12-01 10:01 | -11619 | 6.6648 | 31.3932 | 48.4627 | -3405.1928
2043-12-02 11:01 | -10129.3 | 6.6648 | 32.2216 | 48.4627 | -2968.6048
2043-12-03 12:01 | -9368.88 | 6.6648 | 32.7755 | 48.4627 | -2745.7477
2043-12-04 13:01 | -9481.06 | 6.6648 | 32.8865 | 48.4627 | -2778.6244
2043-12-05 14:01 | -9294.76 | 6.6648 | 33.0663 | 48.4627 | -2724.0253
2043-12-06 15:01 | -9444.91 | 6.6648 | 33.0812 | 48.4627 | -2768.0299
2043-12-07 16:01 | -9967.67 | 6.6648 | 32.879 | 48.4627 | -2921.2357
2043-12-08 17:01 | -8921.05 | 6.6648 | 33.4054 | 48.4627 | -2614.5017
2043-12-09 18:01 | -9388.65 | 6.6648 | 33.2655 | 48.4627 | -2751.5417
2043-12-10 19:01 | -9686.3 | 6.6648 | 33.1445 | 48.4627 | -2838.7743
2043-12-11 20:01 | -10021.9 | 6.6648 | 32.9674 | 48.4627 | -2937.129
2043-12-12 21:01 | -10093 | 6.6648 | 32.9152 | 48.4627 | -2957.9663
2043-12-13 22:01 | -10185.1 | 6.6648 | 32.8639 | 48.4627 | -2984.9582
2043-12-14 23:01 | -10712.1 | 6.6648 | 32.5772 | 48.4627 | -3139.4066
2043-12-16 00:01 | -11664.4 | 6.6648 | 32.0317 | 48.4627 | -3418.4982
2043-12-17 01:01 | -11733.7 | 6.6648 | 31.8701 | 48.4627 | -3438.808
2043-12-18 02:01 | -11801.2 | 6.6648 | 31.7684 | 48.4627 | -3458.5903
2043-12-19 03:01 | -11806.4 | 6.6648 | 31.7222 | 48.4627 | -3460.1143
2043-12-20 04:01 | -11651.3 | 6.6648 | 31.7536 | 48.4627 | -3414.659
2043-12-21 05:01 | -11435.7 | 6.6648 | 31.8469 | 48.4627 | -3351.4728
2043-12-22 06:01 | -10891.7 | 6.6648 | 32.146 | 48.4627 | -3192.0422
2043-12-23 07:01 | -10947.7 | 6.6648 | 32.1806 | 48.4627 | -3208.4542
2043-12-24 08:01 | -10485.9 | 6.6648 | 32.4483 | 48.4627 | -3073.1139
2043-12-25 09:01 | -9406.87 | 6.6648 | 33.045 | 48.4627 | -2756.8815
2043-12-26 10:01 | -9319.25 | 6.6648 | 33.2346 | 48.4627 | -2731.2026
2043-12-27 11:01 | -7896.74 | 6.6648 | 34.0564 | 48.4627 | -2314.306
2043-12-28 12:01 | -7916.69 | 6.6648 | 34.2416 | 48.4627 | -2320.1528
2043-12-29 13:01 | -7173.5 | 6.6648 | 34.7394 | 48.4627 | -2102.3453
2043-12-30 14:01 | -7686.28 | 6.6648 | 34.6372 | 48.4627 | -2252.6263
2043-12-31 15:01 | -8215.13 | 6.6648 | 34.425 | 48.4627 | -2407.6169
2044-01-01 16:01 | -7831.94 | 6.6648 | 34.6371 | 48.4627 | -2295.315
2044-01-02 17:01 | -7430.35 | 6.6648 | 34.8998 | 48.4627 | -2177.6206
2044-01-03 18:01 | -7488.57 | 6.6648 | 34.9643 | 48.4627 | -2194.6832
2044-01-04 19:01 | -7746.4 | 6.6648 | 34.8843 | 48.4627 | -2270.2457
2044-01-05 20:01 | -8306.94 | 6.6648 | 34.6143 | 48.4627 | -2434.5238
2044-01-06 21:01 | -9092.21 | 6.6648 | 34.1926 | 48.4627 | -2664.6637
2044-01-07 22:01 | -9330.35 | 6.6648 | 33.9984 | 48.4627 | -2734.4557
2044-01-08 23:01 | -10087.9 | 6.6648 | 33.5459 | 48.4627 | -2956.4716
2044-01-10 00:01 | -10137.6 | 6.6648 | 33.4151 | 48.4627 | -2971.0373
2044-01-11 01:01 | -10298.4 | 6.6648 | 33.2623 | 48.4627 | -3018.1631
2044-01-12 02:01 | -10337.6 | 6.6648 | 33.1827 | 48.4627 | -3029.6515
2044-01-13 03:01 | -10496.3 | 6.6648 | 33.0694 | 48.4627 | -3076.1619
2044-01-14 04:01 | -10254.5 | 6.6648 | 33.1525 | 48.4627 | -3005.2973
2044-01-15 05:01 | -10230.6 | 6.6648 | 33.1637 | 48.4627 | -2998.2929
2044-01-16 06:01 | -9928.23 | 6.6648 | 33.3124 | 48.4627 | -2909.677
2044-01-17 07:01 | -9756.05 | 6.6648 | 33.4219 | 48.4627 | -2859.216
2044-01-18 08:01 | -9655.97 | 6.6648 | 33.4923 | 48.4627 | -2829.8855
2044-01-19 09:01 | -9944.72 | 6.6648 | 33.3697 | 48.4627 | -2914.5097
2044-01-20 10:01 | -7743.07 | 6.6648 | 34.4816 | 48.4627 | -2269.2698
2044-01-21 11:01 | -8028.61 | 6.6648 | 34.5416 | 48.4627 | -2352.9533
2044-01-22 12:01 | -8409.26 | 6.6648 | 34.4317 | 48.4627 | -2464.5108
2044-01-23 13:01 | -8765.08 | 6.6648 | 34.2495 | 48.4627 | -2568.7914
2044-01-24 14:01 | -9208.86 | 6.6648 | 34.0028 | 48.4627 | -2698.8505
2044-01-25 15:01 | -9123.01 | 6.6648 | 34.0241 | 48.4627 | -2673.6903
2044-01-26 16:01 | -8356.19 | 6.6648 | 34.3942 | 48.4627 | -2448.9575
2044-01-27 17:01 | -7900.61 | 6.6648 | 34.6899 | 48.4627 | -2315.4402
2044-01-28 18:01 | -7611.16 | 6.6648 | 34.917 | 48.4627 | -2230.6108
2044-01-29 19:01 | -7900.82 | 6.6648 | 34.8367 | 48.4627 | -2315.5018
2044-01-30 20:01 | -7819.18 | 6.6648 | 34.911 | 48.4627 | -2291.5754
2044-01-31 21:01 | -8676.72 | 6.6648 | 34.524 | 48.4627 | -2542.8956
2044-02-01 22:01 | -8777.04 | 6.6648 | 34.4147 | 48.4627 | -2572.2965
2044-02-02 23:01 | -9659.56 | 6.6648 | 33.9283 | 48.4627 | -2830.9376
2044-02-04 00:01 | -9430.29 | 6.6648 | 33.9431 | 48.4627 | -2763.7452
2044-02-05 01:01 | -9626.17 | 6.6648 | 33.8182 | 48.4627 | -2821.1519
2044-02-06 02:01 | -9778.95 | 6.6648 | 33.7115 | 48.4627 | -2865.9273
2044-02-07 03:01 | -9786.18 | 6.6648 | 33.6811 | 48.4627 | -2868.0462
2044-02-08 04:01 | -9550.57 | 6.6648 | 33.7803 | 48.4627 | -2798.9958
2044-02-09 05:01 | -9514.17 | 6.6648 | 33.8151 | 48.4627 | -2788.328
2044-02-10 06:01 | -8912.4 | 6.6648 | 34.118 | 48.4627 | -2611.9666
2044-02-11 07:01 | -8929.01 | 6.6648 | 34.167 | 48.4627 | -2616.8345
2044-02-12 08:01 | -8915.32 | 6.6648 | 34.2042 | 48.4627 | -2612.8224
2044-02-13 09:01 | -9362.63 | 6.6648 | 33.9972 | 48.4627 | -2743.916
2044-02-14 10:01 | -9140.92 | 6.6648 | 34.075 | 48.4627 | -2678.9392
2044-02-15 11:01 | -9109.83 | 6.6648 | 34.0993 | 48.4627 | -2669.8276
2044-02-16 12:01 | -8281 | 6.6648 | 34.5267 | 48.4627 | -2426.9215
2044-02-17 13:01 | -7743.03 | 6.6648 | 34.8746 | 48.4627 | -2269.2581
2044-02-18 14:01 | -7231.75 | 6.6648 | 35.2366 | 48.4627 | -2119.4167
2044-02-19 15:01 | -7122.55 | 6.6648 | 35.4101 | 48.4627 | -2087.4133
2044-02-20 16:01 | -7390.6 | 6.6648 | 35.3581 | 48.4627 | -2165.971
2044-02-21 17:01 | -7510.16 | 6.6648 | 35.3333 | 48.4627 | -2201.0106
2044-02-22 18:01 | -7341.34 | 6.6648 | 35.4349 | 48.4627 | -2151.5344
2044-02-23 19:01 | -8176.89 | 6.6648 | 35.0365 | 48.4627 | -2396.4099
2044-02-24 20:01 | -8734.73 | 6.6648 | 34.6918 | 48.4627 | -2559.8967
2044-02-25 21:01 | -9872.92 | 6.6648 | 34.0334 | 48.4627 | -2893.4672
2044-02-26 22:01 | -10345.2 | 6.6648 | 33.6507 | 48.4627 | -3031.8788
2044-02-27 23:01 | -11145.3 | 6.6648 | 33.1196 | 48.4627 | -3266.365
2044-02-29 00:01 | -11321.7 | 6.6648 | 32.8612 | 48.4627 | -3318.0627
2044-03-01 01:01 | -11661.8 | 6.6648 | 32.5646 | 48.4627 | -3417.7362
2044-03-02 02:01 | -11827 | 6.6648 | 32.358 | 48.4627 | -3466.1515
2044-03-03 03:01 | -11839.6 | 6.6648 | 32.2506 | 48.4627 | -3469.8442
2044-03-04 04:01 | -11647.9 | 6.6648 | 32.2713 | 48.4627 | -3413.6625
2044-03-05 05:01 | -11716 | 6.6648 | 32.1962 | 48.4627 | -3433.6207
2044-03-06 06:01 | -11684.6 | 6.6648 | 32.1482 | 48.4627 | -3424.4182
2044-03-07 07:01 | -11812.6 | 6.6648 | 32.0375 | 48.4627 | -3461.9313
2044-03-08 08:01 | -10909.1 | 6.6648 | 32.4523 | 48.4627 | -3197.1416
2044-03-09 09:01 | -10445.9 | 6.6648 | 32.7486 | 48.4627 | -3061.3911
2044-03-10 10:01 | -9403.06 | 6.6648 | 33.3473 | 48.4627 | -2755.7649
2044-03-11 11:01 | -8320.15 | 6.6648 | 34.0365 | 48.4627 | -2438.3953
2044-03-12 12:01 | -7588.34 | 6.6648 | 34.5846 | 48.4627 | -2223.9229
2044-03-13 13:01 | -7533.94 | 6.6648 | 34.7962 | 48.4627 | -2207.9799
2044-03-14 14:01 | -8198.21 | 6.6648 | 34.5736 | 48.4627 | -2402.6582
2044-03-15 15:01 | -8676.13 | 6.6648 | 34.3518 | 48.4627 | -2542.7227
2044-03-16 16:01 | -9290.35 | 6.6648 | 34.0205 | 48.4627 | -2722.7328
2044-03-17 17:01 | -9366.52 | 6.6648 | 33.9218 | 48.4627 | -2745.056
2044-03-18 18:01 | -9415.69 | 6.6648 | 33.8468 | 48.4627 | -2759.4663
2044-03-19 19:01 | -9927.71 | 6.6648 | 33.5585 | 48.4627 | -2909.5246
2044-03-20 20:01 | -10182.6 | 6.6648 | 33.3598 | 48.4627 | -2984.2255
2044-03-21 21:01 | -11267.5 | 6.6648 | 32.7452 | 48.4627 | -3302.1783
2044-03-22 22:01 | -11542.4 | 6.6648 | 32.4569 | 48.4627 | -3382.7435
2044-03-23 23:01 | -11922.2 | 6.6648 | 32.145 | 48.4627 | -3494.0519
2044-03-25 00:01 | -12106.4 | 6.6648 | 31.9311 | 48.4627 | -3548.0356
2044-03-26 01:01 | -12219.9 | 6.6648 | 31.7685 | 48.4627 | -3581.2992
2044-03-27 02:01 | -12257.8 | 6.6648 | 31.6616 | 48.4627 | -3592.4066
2044-03-28 03:01 | -12168.5 | 6.6648 | 31.648 | 48.4627 | -3566.2353
2044-03-29 04:01 | -12062.2 | 6.6648 | 31.6575 | 48.4627 | -3535.0819
2044-03-30 05:01 | -11814.9 | 6.6648 | 31.7603 | 48.4627 | -3462.6054
2044-03-31 06:01 | -11285.4 | 6.6648 | 32.0291 | 48.4627 | -3307.4243
2044-04-01 07:01 | -11238.7 | 6.6648 | 32.0964 | 48.4627 | -3293.7378
2044-04-02 08:01 | -11214.5 | 6.6648 | 32.1259 | 48.4627 | -3286.6455
2044-04-03 09:01 | -11611 | 6.6648 | 31.9235 | 48.4627 | -3402.8482
2044-04-04 10:01 | -10687 | 6.6648 | 32.3597 | 48.4627 | -3132.0505
2044-04-05 11:01 | -8128.5 | 6.6648 | 33.7401 | 48.4627 | -2382.2282
2044-04-06 12:01 | -9606.62 | 6.6648 | 33.2618 | 48.4627 | -2815.4224
2044-04-07 13:01 | -7937.83 | 6.6648 | 34.1076 | 48.4627 | -2326.3483
2044-04-08 14:01 | -9014.72 | 6.6648 | 33.7186 | 48.4627 | -2641.9536
2044-04-09 15:01 | -9137.78 | 6.6648 | 33.6869 | 48.4627 | -2678.019
2044-04-10 16:01 | -9342.87 | 6.6648 | 33.5913 | 48.4627 | -2738.1249
2044-04-11 17:01 | -9505.11 | 6.6648 | 33.4852 | 48.4627 | -2785.6728
2044-04-12 18:01 | -9279.06 | 6.6648 | 33.5935 | 48.4627 | -2719.424
2044-04-13 19:01 | -9626.71 | 6.6648 | 33.4185 | 48.4627 | -2821.3102
2044-04-14 20:01 | -9927.29 | 6.6648 | 33.2454 | 48.4627 | -2909.4015
2044-04-15 21:01 | -10704.2 | 6.6648 | 32.8218 | 48.4627 | -3137.0913
2044-04-16 22:01 | -11104.6 | 6.6648 | 32.5333 | 48.4627 | -3254.437
2044-04-17 23:01 | -11915.7 | 6.6648 | 32.02 | 48.4627 | -3492.1469
2044-04-19 00:01 | -12286.7 | 6.6648 | 31.6971 | 48.4627 | -3600.8763
2044-04-20 01:01 | -12524.8 | 6.6648 | 31.4438 | 48.4627 | -3670.6565
2044-04-21 02:01 | -12690 | 6.6648 | 31.2545 | 48.4627 | -3719.0719
2044-04-22 03:01 | -12949 | 6.6648 | 31.0333 | 48.4627 | -3794.9773
2044-04-23 04:01 | -12995.2 | 6.6648 | 30.9156 | 48.4627 | -3808.5172
2044-04-24 05:01 | -12818 | 6.6648 | 30.9374 | 48.4627 | -3756.585
2044-04-25 06:01 | -12594.5 | 6.6648 | 31.011 | 48.4627 | -3691.0836
2044-04-26 07:01 | -12223.6 | 6.6648 | 31.1831 | 48.4627 | -3582.3835
2044-04-27 08:01 | -11600.9 | 6.6648 | 31.511 | 48.4627 | -3399.8882
2044-04-28 09:01 | -11887.8 | 6.6648 | 31.4224 | 48.4627 | -3483.9703
2044-04-29 10:01 | -11896.5 | 6.6648 | 31.4058 | 48.4627 | -3486.52
2044-04-30 11:01 | -11641.6 | 6.6648 | 31.5117 | 48.4627 | -3411.8162
2044-05-01 12:01 | -11543.5 | 6.6648 | 31.5739 | 48.4627 | -3383.0659
2044-05-02 13:01 | -11285.1 | 6.6648 | 31.7066 | 48.4627 | -3307.3363
2044-05-03 14:01 | -11337 | 6.6648 | 31.6926 | 48.4627 | -3322.5467
2044-05-04 15:01 | -10983.3 | 6.6648 | 31.8776 | 48.4627 | -3218.8875
2044-05-05 16:01 | -10810.3 | 6.6648 | 32.0034 | 48.4627 | -3168.1862
2044-05-06 17:01 | -9269.06 | 6.6648 | 32.8319 | 48.4627 | -2716.4933
2044-05-07 18:01 | -9658.64 | 6.6648 | 32.8016 | 48.4627 | -2830.668
2044-05-08 19:01 | -9794.71 | 6.6648 | 32.7877 | 48.4627 | -2870.5461
2044-05-09 20:01 | -10085.1 | 6.6648 | 32.6575 | 48.4627 | -2955.651
2044-05-10 21:01 | -9992.27 | 6.6648 | 32.7144 | 48.4627 | -2928.4453
2044-05-11 22:01 | -9997.3 | 6.6648 | 32.7462 | 48.4627 | -2929.9194
2044-05-12 23:01 | -9977.02 | 6.6648 | 32.772 | 48.4627 | -2923.9759
2044-05-14 00:01 | -11136.7 | 6.6648 | 32.1986 | 48.4627 | -3263.8446
2044-05-15 01:01 | -11279.7 | 6.6648 | 32.0317 | 48.4627 | -3305.7537
2044-05-16 02:01 | -11582.2 | 6.6648 | 31.8245 | 48.4627 | -3394.4077
2044-05-17 03:01 | -11468.8 | 6.6648 | 31.8324 | 48.4627 | -3361.1735
2044-05-18 04:01 | -11533.4 | 6.6648 | 31.7754 | 48.4627 | -3380.1059
2044-05-19 05:01 | -11684.6 | 6.6648 | 31.6556 | 48.4627 | -3424.4182
2044-05-20 06:01 | -11570.4 | 6.6648 | 31.6767 | 48.4627 | -3390.9495
2044-05-21 07:01 | -10776.9 | 6.6648 | 32.069 | 48.4627 | -3158.3976
2044-05-22 08:01 | -10515.8 | 6.6648 | 32.2703 | 48.4627 | -3081.8768
2044-05-23 09:01 | -11158.2 | 6.6648 | 31.9947 | 48.4627 | -3270.1456
2044-05-24 10:01 | -11199.7 | 6.6648 | 31.9302 | 48.4627 | -3282.3081
2044-05-25 11:01 | -10996.5 | 6.6648 | 32.0039 | 48.4627 | -3222.756
2044-05-26 12:01 | -10744.1 | 6.6648 | 32.1499 | 48.4627 | -3148.7849
2044-05-27 13:01 | -10708.2 | 6.6648 | 32.1851 | 48.4627 | -3138.2636
2044-05-28 14:01 | -10161.7 | 6.6648 | 32.4707 | 48.4627 | -2978.1003
2044-05-29 15:01 | -9818.04 | 6.6648 | 32.7081 | 48.4627 | -2877.3835
2044-05-30 16:01 | -10317.8 | 6.6648 | 32.5236 | 48.4627 | -3023.8487
2044-05-31 17:01 | -9284.99 | 6.6648 | 33.0399 | 48.4627 | -2721.162
2044-06-01 18:01 | -9740.1 | 6.6648 | 32.905 | 48.4627 | -2854.5415
2044-06-02 19:01 | -9932.35 | 6.6648 | 32.8226 | 48.4627 | -2910.8844
2044-06-03 20:01 | -10361.3 | 6.6648 | 32.5846 | 48.4627 | -3036.5973
2044-06-04 21:01 | -10567 | 6.6648 | 32.4401 | 48.4627 | -3096.882
2044-06-05 22:01 | -10442.4 | 6.6648 | 32.4783 | 48.4627 | -3060.3653
2044-06-06 23:01 | -10383.9 | 6.6648 | 32.4989 | 48.4627 | -3043.2207
2044-06-08 00:01 | -11210.6 | 6.6648 | 32.0813 | 48.4627 | -3285.5025
2044-06-09 01:01 | -11253.3 | 6.6648 | 31.9822 | 48.4627 | -3298.0167
2044-06-10 02:01 | -11277.8 | 6.6648 | 31.9272 | 48.4627 | -3305.1969
2044-06-11 03:01 | -11366.9 | 6.6648 | 31.8595 | 48.4627 | -3331.3095
2044-06-12 04:01 | -10858.1 | 6.6648 | 32.0948 | 48.4627 | -3182.195
2044-06-13 05:01 | -10511.1 | 6.6648 | 32.2938 | 48.4627 | -3080.4993
2044-06-14 06:01 | -10069.3 | 6.6648 | 32.5729 | 48.4627 | -2951.0205
2044-06-15 07:01 | -10004.2 | 6.6648 | 32.6728 | 48.4627 | -2931.9416
2044-06-16 08:01 | -10196.5 | 6.6648 | 32.6195 | 48.4627 | -2988.2992
2044-06-17 09:01 | -10508.6 | 6.6648 | 32.4774 | 48.4627 | -3079.7666
2044-06-18 10:01 | -10327 | 6.6648 | 32.5537 | 48.4627 | -3026.5449
2044-06-19 11:01 | -9372.03 | 6.6648 | 33.0548 | 48.4627 | -2746.6709
2044-06-20 12:01 | -9714.37 | 6.6648 | 32.9819 | 48.4627 | -2847.0008
2044-06-21 13:01 | -9977.93 | 6.6648 | 32.8683 | 48.4627 | -2924.2426
2044-06-22 14:01 | -10304.4 | 6.6648 | 32.6888 | 48.4627 | -3019.9215
2044-06-23 15:01 | -10178.6 | 6.6648 | 32.733 | 48.4627 | -2983.0532
2044-06-24 16:01 | -9284.82 | 6.6648 | 33.201 | 48.4627 | -2721.1121
2044-06-25 17:01 | -9295.08 | 6.6648 | 33.2702 | 48.4627 | -2724.119
2044-06-26 18:01 | -9020.58 | 6.6648 | 33.4481 | 48.4627 | -2643.671
2044-06-27 19:01 | -8987.45 | 6.6648 | 33.5155 | 48.4627 | -2633.9616
2044-06-28 20:01 | -9512.2 | 6.6648 | 33.2964 | 48.4627 | -2787.7506
2044-06-29 21:01 | -10444.3 | 6.6648 | 32.8034 | 48.4627 | -3060.9222
2044-06-30 22:01 | -10770.2 | 6.6648 | 32.5385 | 48.4627 | -3156.434
2044-07-01 23:01 | -11764.5 | 6.6648 | 31.9433 | 48.4627 | -3447.8346
2044-07-03 00:01 | -12030.7 | 6.6648 | 31.6642 | 48.4627 | -3525.8501
2044-07-04 01:01 | -12303.4 | 6.6648 | 31.4047 | 48.4627 | -3605.7706
2044-07-05 02:01 | -12400.4 | 6.6648 | 31.2595 | 48.4627 | -3634.1985
2044-07-06 03:01 | -12464.1 | 6.6648 | 31.1551 | 48.4627 | -3652.8671
2044-07-07 04:01 | -12554.1 | 6.6648 | 31.0376 | 48.4627 | -3679.2435
2044-07-08 05:01 | -12500.3 | 6.6648 | 31.0052 | 48.4627 | -3663.4763
2044-07-09 06:01 | -12347.1 | 6.6648 | 31.0342 | 48.4627 | -3618.5778
2044-07-10 07:01 | -12125.4 | 6.6648 | 31.1162 | 48.4627 | -3553.604
2044-07-11 08:01 | -11778.8 | 6.6648 | 31.2829 | 48.4627 | -3452.0255
2044-07-12 09:01 | -11674 | 6.6648 | 31.3541 | 48.4627 | -3421.3117
2044-07-13 10:01 | -11386.6 | 6.6648 | 31.5146 | 48.4627 | -3337.083
2044-07-14 11:01 | -9343.33 | 6.6648 | 32.5949 | 48.4627 | -2738.2597
2044-07-15 12:01 | -7821.28 | 6.6648 | 33.5979 | 48.4627 | -2292.1909
2044-07-16 13:01 | -8250.19 | 6.6648 | 33.6543 | 48.4627 | -2417.892
2044-07-17 14:01 | -8934.72 | 6.6648 | 33.4167 | 48.4627 | -2618.508
2044-07-18 15:01 | -9958.95 | 6.6648 | 32.9086 | 48.4627 | -2918.6801
2044-07-19 16:01 | -10606.2 | 6.6648 | 32.529 | 48.4627 | -3108.3704
2044-07-20 17:01 | -9372.33 | 6.6648 | 33.0771 | 48.4627 | -2746.7588
2044-07-21 18:01 | -9927.76 | 6.6648 | 32.8565 | 48.4627 | -2909.5392
2044-07-22 19:01 | -10086.7 | 6.6648 | 32.7527 | 48.4627 | -2956.12
2044-07-23 20:01 | -10362.3 | 6.6648 | 32.5747 | 48.4627 | -3036.8903
2044-07-24 21:01 | -10233.7 | 6.6648 | 32.622 | 48.4627 | -2999.2014
2044-07-25 22:01 | -10081.9 | 6.6648 | 32.7207 | 48.4627 | -2954.7132
2044-07-26 23:01 | -10288.3 | 6.6648 | 32.6202 | 48.4627 | -3015.2031
2044-07-28 00:01 | -11303.9 | 6.6648 | 32.0728 | 48.4627 | -3312.8461
2044-07-29 01:01 | -11100.7 | 6.6648 | 32.0623 | 48.4627 | -3253.294
2044-07-30 02:01 | -11002.7 | 6.6648 | 32.0749 | 48.4627 | -3224.5731
2044-07-31 03:01 | -10871.9 | 6.6648 | 32.1407 | 48.4627 | -3186.2394
2044-08-01 04:01 | -10551.3 | 6.6648 | 32.3109 | 48.4627 | -3092.2808
2044-08-02 05:01 | -10596.3 | 6.6648 | 32.3092 | 48.4627 | -3105.469
2044-08-03 06:01 | -9981.5 | 6.6648 | 32.6445 | 48.4627 | -2925.2889
2044-08-04 07:01 | -10259 | 6.6648 | 32.5733 | 48.4627 | -3006.6161
2044-08-05 08:01 | -10055.8 | 6.6648 | 32.6907 | 48.4627 | -2947.0641
2044-08-06 09:01 | -10386.8 | 6.6648 | 32.551 | 48.4627 | -3044.0706
2044-08-07 10:01 | -9039.04 | 6.6648 | 33.2303 | 48.4627 | -2649.0811
2044-08-08 11:01 | -9718.05 | 6.6648 | 33.0044 | 48.4627 | -2848.0793
2044-08-09 12:01 | -9608.81 | 6.6648 | 33.0581 | 48.4627 | -2816.0642
2044-08-10 13:01 | -9489.69 | 6.6648 | 33.129 | 48.4627 | -2781.1536
2044-08-11 14:01 | -8739.92 | 6.6648 | 33.5438 | 48.4627 | -2561.4177
2044-08-12 15:01 | -9353.74 | 6.6648 | 33.3383 | 48.4627 | -2741.3106
2044-08-13 16:01 | -8787.14 | 6.6648 | 33.6168 | 48.4627 | -2575.2565
2044-08-14 17:01 | -8546.01 | 6.6648 | 33.7972 | 48.4627 | -2504.5883
2044-08-15 18:01 | -8437.99 | 6.6648 | 33.9199 | 48.4627 | -2472.9308
2044-08-16 19:01 | -8615.92 | 6.6648 | 33.8798 | 48.4627 | -2525.0769
2044-08-17 20:01 | -8826.55 | 6.6648 | 33.7864 | 48.4627 | -2586.8065
2044-08-18 21:01 | -9625.93 | 6.6648 | 33.3899 | 48.4627 | -2821.0816
2044-08-19 22:01 | -9886.59 | 6.6648 | 33.1808 | 48.4627 | -2897.4735
2044-08-20 23:01 | -10711.6 | 6.6648 | 32.7018 | 48.4627 | -3139.2601
2044-08-22 00:01 | -11228.3 | 6.6648 | 32.3282 | 48.4627 | -3290.6899
2044-08-23 01:01 | -11261.7 | 6.6648 | 32.1982 | 48.4627 | -3300.4785
2044-08-24 02:01 | -11212.8 | 6.6648 | 32.1483 | 48.4627 | -3286.1473
2044-08-25 03:01 | -11583.3 | 6.6648 | 31.9194 | 48.4627 | -3394.7301
2044-08-26 04:01 | -11319.1 | 6.6648 | 31.9767 | 48.4627 | -3317.3007
2044-08-27 05:01 | -11166.5 | 6.6648 | 32.03 | 48.4627 | -3272.5781
2044-08-28 06:01 | -10712.7 | 6.6648 | 32.2519 | 48.4627 | -3139.5825
2044-08-29 07:01 | -10732.9 | 6.6648 | 32.2674 | 48.4627 | -3145.5025
2044-08-30 08:01 | -10830.1 | 6.6648 | 32.2171 | 48.4627 | -3173.989
2044-08-31 09:01 | -11342.2 | 6.6648 | 31.9476 | 48.4627 | -3324.0707
2044-09-01 10:01 | -9178.49 | 6.6648 | 32.9993 | 48.4627 | -2689.9499
2044-09-02 11:01 | -7250.58 | 6.6648 | 34.1745 | 48.4627 | -2124.9352
2044-09-03 12:01 | -6641.62 | 6.6648 | 34.7737 | 48.4627 | -1946.4667
2044-09-04 13:01 | -6295.96 | 6.6648 | 35.1601 | 48.4627 | -1845.1637
2044-09-05 14:01 | -7110.95 | 6.6648 | 34.9148 | 48.4627 | -2084.0137
2044-09-06 15:01 | -7927.87 | 6.6648 | 34.5741 | 48.4627 | -2323.4293
2044-09-07 16:01 | -8606.2 | 6.6648 | 34.2109 | 48.4627 | -2522.2282
2044-09-08 17:01 | -8922.11 | 6.6648 | 33.9829 | 48.4627 | -2614.8123
2044-09-09 18:01 | -9150.34 | 6.6648 | 33.805 | 48.4627 | -2681.6999
2044-09-10 19:01 | -9434.55 | 6.6648 | 33.5982 | 48.4627 | -2764.9937
2044-09-11 20:01 | -9603.04 | 6.6648 | 33.4595 | 48.4627 | -2814.3732
2044-09-12 21:01 | -11053.9 | 6.6648 | 32.6826 | 48.4627 | -3239.5783
2044-09-13 22:01 | -11465.7 | 6.6648 | 32.3033 | 48.4627 | -3360.265
2044-09-14 23:01 | -11989.1 | 6.6648 | 31.8857 | 48.4627 | -3513.6584
2044-09-16 00:01 | -12297.1 | 6.6648 | 31.5801 | 48.4627 | -3603.9243
2044-09-17 01:01 | -12634.2 | 6.6648 | 31.2662 | 48.4627 | -3702.7185
2044-09-18 02:01 | -12796.3 | 6.6648 | 31.0443 | 48.4627 | -3750.2253
2044-09-19 03:01 | -12896.7 | 6.6648 | 30.8922 | 48.4627 | -3779.6497
2044-09-20 04:01 | -12880.9 | 6.6648 | 30.8154 | 48.4627 | -3775.0191
2044-09-21 05:01 | -12828.9 | 6.6648 | 30.7775 | 48.4627 | -3759.7794
2044-09-22 06:01 | -12632.3 | 6.6648 | 30.8209 | 48.4627 | -3702.1617
2044-09-23 07:01 | -12368.4 | 6.6648 | 30.9279 | 48.4627 | -3624.8202
2044-09-24 08:01 | -12236.8 | 6.6648 | 30.9876 | 48.4627 | -3586.2521
2044-09-25 09:01 | -12283.9 | 6.6648 | 30.9683 | 48.4627 | -3600.0557
2044-09-26 10:01 | -10854.5 | 6.6648 | 31.6832 | 48.4627 | -3181.1399
2044-09-27 11:01 | -9134.68 | 6.6648 | 32.6857 | 48.4627 | -2677.1104
2044-09-28 12:01 | -8052.94 | 6.6648 | 33.463 | 48.4627 | -2360.0837
2044-09-29 13:01 | -7681.06 | 6.6648 | 33.8755 | 48.4627 | -2251.0965
2044-09-30 14:01 | -7444.53 | 6.6648 | 34.1675 | 48.4627 | -2181.7764
2044-10-01 15:01 | -7832.07 | 6.6648 | 34.1268 | 48.4627 | -2295.3531
2044-10-02 16:01 | -8165.28 | 6.6648 | 34.0337 | 48.4627 | -2393.0073
2044-10-03 17:01 | -8657.68 | 6.6648 | 33.8086 | 48.4627 | -2537.3155
2044-10-04 18:01 | -8697.16 | 6.6648 | 33.768 | 48.4627 | -2548.886
2044-10-05 19:01 | -9359.78 | 6.6648 | 33.4294 | 48.4627 | -2743.0807
2044-10-06 20:01 | -9706.8 | 6.6648 | 33.1957 | 48.4627 | -2844.7823
2044-10-07 21:01 | -10593.6 | 6.6648 | 32.697 | 48.4627 | -3104.6777
2044-10-08 22:01 | -10997.7 | 6.6648 | 32.3807 | 48.4627 | -3223.1077
2044-10-09 23:01 | -11809.3 | 6.6648 | 31.8632 | 48.4627 | -3460.9642
2044-10-11 00:01 | -11973.3 | 6.6648 | 31.6311 | 48.4627 | -3509.0278
2044-10-12 01:01 | -12129 | 6.6648 | 31.4419 | 48.4627 | -3554.659
2044-10-13 02:01 | -12184.2 | 6.6648 | 31.3205 | 48.4627 | -3570.8365
2044-10-14 03:01 | -12288.9 | 6.6648 | 31.1979 | 48.4627 | -3601.5211
2044-10-15 04:01 | -12300 | 6.6648 | 31.1243 | 48.4627 | -3604.7742
2044-10-16 05:01 | -12154.7 | 6.6648 | 31.1557 | 48.4627 | -3562.1909
2044-10-17 06:01 | -11990.7 | 6.6648 | 31.2159 | 48.4627 | -3514.1273
2044-10-18 07:01 | -11272.7 | 6.6648 | 31.579 | 48.4627 | -3303.7023
2044-10-19 08:01 | -10741 | 6.6648 | 31.9111 | 48.4627 | -3147.8764
2044-10-20 09:01 | -11191.7 | 6.6648 | 31.7618 | 48.4627 | -3279.9635
2044-10-21 10:01 | -11252.8 | 6.6648 | 31.7213 | 48.4627 | -3297.8701
2044-10-22 11:01 | -10815.8 | 6.6648 | 31.928 | 48.4627 | -3169.7981
2044-10-23 12:01 | -10585.9 | 6.6648 | 32.0784 | 48.4627 | -3102.421
2044-10-24 13:01 | -10683.1 | 6.6648 | 32.0492 | 48.4627 | -3130.9075
2044-10-25 14:01 | -10550.2 | 6.6648 | 32.1044 | 48.4627 | -3091.9584
2044-10-26 15:01 | -9984.03 | 6.6648 | 32.4081 | 48.4627 | -2926.0304
2044-10-27 16:01 | -9855.1 | 6.6648 | 32.5446 | 48.4627 | -2888.2447
2044-10-28 17:01 | -8126.9 | 6.6648 | 33.4816 | 48.4627 | -2381.7593
2044-10-29 18:01 | -8256.45 | 6.6648 | 33.6146 | 48.4627 | -2419.7266
2044-10-30 19:01 | -8341.34 | 6.6648 | 33.6783 | 48.4627 | -2444.6054
2044-10-31 20:01 | -8627.64 | 6.6648 | 33.5888 | 48.4627 | -2528.5117
2044-11-01 21:01 | -8875.75 | 6.6648 | 33.4986 | 48.4627 | -2601.2255
2044-11-02 22:01 | -9038.69 | 6.6648 | 33.4425 | 48.4627 | -2648.9785
2044-11-03 23:01 | -9348.09 | 6.6648 | 33.2861 | 48.4627 | -2739.6547
2044-11-05 00:01 | -10757.4 | 6.6648 | 32.5472 | 48.4627 | -3152.6827
2044-11-06 01:01 | -10824.7 | 6.6648 | 32.3782 | 48.4627 | -3172.4064
2044-11-07 02:01 | -11288.1 | 6.6648 | 32.0717 | 48.4627 | -3308.2155
2044-11-08 03:01 | -11118.9 | 6.6648 | 32.0817 | 48.4627 | -3258.6279
2044-11-09 04:01 | -11259.6 | 6.6648 | 31.9725 | 48.4627 | -3299.863
2044-11-10 05:01 | -11099.1 | 6.6648 | 31.9983 | 48.4627 | -3252.8251
2044-11-11 06:01 | -11034.9 | 6.6648 | 32.0148 | 48.4627 | -3234.01
2044-11-12 07:01 | -10296.8 | 6.6648 | 32.3795 | 48.4627 | -3017.6942
2044-11-13 08:01 | -9775.14 | 6.6648 | 32.7072 | 48.4627 | -2864.8107
2044-11-14 09:01 | -10324.8 | 6.6648 | 32.5043 | 48.4627 | -3025.9002
2044-11-15 10:01 | -10103.4 | 6.6648 | 32.6006 | 48.4627 | -2961.0142
2044-11-16 11:01 | -9534.14 | 6.6648 | 32.9039 | 48.4627 | -2794.1806
2044-11-17 12:01 | -9222.5 | 6.6648 | 33.1427 | 48.4627 | -2702.8479
2044-11-18 13:01 | -9136.05 | 6.6648 | 33.2548 | 48.4627 | -2677.5119
2044-11-19 14:01 | -9173.59 | 6.6648 | 33.2778 | 48.4627 | -2688.5138
2044-11-20 15:01 | -9173.65 | 6.6648 | 33.3118 | 48.4627 | -2688.5314
2044-11-21 16:01 | -8893.93 | 6.6648 | 33.4878 | 48.4627 | -2606.5536
2044-11-22 17:01 | -7405.48 | 6.6648 | 34.2936 | 48.4627 | -2170.3319
2044-11-23 18:01 | -7705.74 | 6.6648 | 34.3129 | 48.4627 | -2258.3295
2044-11-24 19:01 | -7882.3 | 6.6648 | 34.2909 | 48.4627 | -2310.0741
2044-11-25 20:01 | -8062.08 | 6.6648 | 34.2245 | 48.4627 | -2362.7624
2044-11-26 21:01 | -8073.37 | 6.6648 | 34.2501 | 48.4627 | -2366.0712
2044-11-27 22:01 | -8313.62 | 6.6648 | 34.1646 | 48.4627 | -2436.4815
2044-11-28 23:01 | -8381.24 | 6.6648 | 34.1238 | 48.4627 | -2456.299
2044-11-30 00:01 | -9253.05 | 6.6648 | 33.684 | 48.4627 | -2711.8013
2044-12-01 01:01 | -9110.78 | 6.6648 | 33.6892 | 48.4627 | -2670.106
2044-12-02 02:01 | -9482.47 | 6.6648 | 33.489 | 48.4627 | -2779.0376
2044-12-03 03:01 | -9441.44 | 6.6648 | 33.479 | 48.4627 | -2767.0129
2044-12-04 04:01 | -9310.89 | 6.6648 | 33.5334 | 48.4627 | -2728.7525
2044-12-05 05:01 | -9108.88 | 6.6648 | 33.633 | 48.4627 | -2669.5492
2044-12-06 06:01 | -8637.44 | 6.6648 | 33.8999 | 48.4627 | -2531.3838
2044-12-07 07:01 | -8600.67 | 6.6648 | 33.973 | 48.4627 | -2520.6076
2044-12-08 08:01 | -8210.91 | 6.6648 | 34.2099 | 48.4627 | -2406.3802
2044-12-09 09:01 | -7690.49 | 6.6648 | 34.5425 | 48.4627 | -2253.8601
2044-12-10 10:01 | -7332.83 | 6.6648 | 34.8225 | 48.4627 | -2149.0403
2044-12-11 11:01 | -7903.35 | 6.6648 | 34.6221 | 48.4627 | -2316.2432
2044-12-12 12:01 | -7990.93 | 6.6648 | 34.5811 | 48.4627 | -2341.9104
2044-12-13 13:01 | -8163.51 | 6.6648 | 34.5005 | 48.4627 | -2392.4886
2044-12-14 14:01 | -8363.55 | 6.6648 | 34.4036 | 48.4627 | -2451.1145
2044-12-15 15:01 | -8293.26 | 6.6648 | 34.4256 | 48.4627 | -2430.5146
2044-12-16 16:01 | -7542.76 | 6.6648 | 34.8089 | 48.4627 | -2210.5647
2044-12-17 17:01 | -7232.63 | 6.6648 | 35.0405 | 48.4627 | -2119.6746
2044-12-18 18:01 | -7095.86 | 6.6648 | 35.1806 | 48.4627 | -2079.5913
2044-12-19 19:01 | -7247.69 | 6.6648 | 35.1589 | 48.4627 | -2124.0883
2044-12-20 20:01 | -7436.12 | 6.6648 | 35.0918 | 48.4627 | -2179.3116
2044-12-21 21:01 | -8247.94 | 6.6648 | 34.6864 | 48.4627 | -2417.2326
2044-12-22 22:01 | -8467.01 | 6.6648 | 34.5023 | 48.4627 | -2481.4357
2044-12-23 23:01 | -9020.42 | 6.6648 | 34.1649 | 48.4627 | -2643.6241
[5 empty] | -8354244.5254 | -953.6809

## Indianapolis
| Property | Soil |  |  |  |  | Property | Soil
| Thermal conductivity [W/m K] | 1.72 |  | W/M-K | 0.57779 | BTU/HR-FT-R | Thermal conductivity [Btu/Hr-ft-R] | 0.99379
| Specific heat [J/kg K] | 1900
| Density [kg/m3] | 1300
| Volumeric specific heat [MJ/K-M3] | 2.47
| Thermal diffusivity [m2/hr] | 0.0025069 |  | m2/hr | 10.7639 | ft2/hr | Thermal diffusivity [ft2/hr] | 0.026984
VBGHE design and performance
| Borehole number | 2
| Borehole depth | 220 | ft | 67 | m
| Annual Max. LFT | 84.7 | F
| Annual Min. LFT | 29.3 | F
Time | Thermal load | Fluid flow | Outlet temperature | Far field ground temperature | Load
| Btu/hr | GPM | F | F | W
2020-01-01 | -10411.5 | 6.8587 | 46.7704 | 53.895 | -3051.3094
2020-01-02 01:00 | -10294.6 | 6.8587 | 45.5483 | 53.895 | -3017.0494
2020-01-03 02:00 | -10498.6 | 6.8587 | 44.663 | 53.895 | -3076.8359
2020-01-04 03:00 | -10773.2 | 6.8587 | 44.0241 | 53.895 | -3157.3133
2020-01-05 04:00 | -10828.2 | 6.8587 | 43.5081 | 53.895 | -3173.4322
2020-01-06 05:00 | -10819.4 | 6.8587 | 43.05 | 53.895 | -3170.8531
2020-01-07 06:00 | -10756.4 | 6.8587 | 42.8586 | 53.895 | -3152.3897
2020-01-08 07:00 | -10145 | 6.8587 | 43.0503 | 53.895 | -2973.206
2020-01-09 08:00 | -9553.75 | 6.8587 | 43.3065 | 53.895 | -2799.9277
2020-01-10 09:00 | -10136.8 | 6.8587 | 42.8027 | 53.895 | -2970.8028
2020-01-11 10:00 | -9518.63 | 6.8587 | 42.9991 | 53.895 | -2789.6351
2020-01-12 11:00 | -8983.87 | 6.8587 | 43.2294 | 53.895 | -2632.9124
2020-01-13 12:00 | -8939.22 | 6.8587 | 43.2833 | 53.895 | -2619.8268
2020-01-14 13:00 | -8926.4 | 6.8587 | 43.2589 | 53.895 | -2616.0696
2020-01-15 14:00 | -8764.24 | 6.8587 | 43.3092 | 53.895 | -2568.5452
2020-01-16 15:00 | -8791.99 | 6.8587 | 43.2626 | 53.895 | -2576.6779
2020-01-17 16:00 | -8695.05 | 6.8587 | 43.2767 | 53.895 | -2548.2676
2020-01-18 17:00 | -7302.64 | 6.8587 | 44.1767 | 53.895 | -2140.1925
2020-01-19 18:00 | -7897.08 | 6.8587 | 43.8842 | 53.895 | -2314.4057
2020-01-20 19:00 | -8177.25 | 6.8587 | 43.6481 | 53.895 | -2396.5154
2020-01-21 20:00 | -8264.39 | 6.8587 | 43.4874 | 53.895 | -2422.0536
2020-01-22 21:00 | -8625.04 | 6.8587 | 43.1683 | 53.895 | -2527.7497
2020-01-23 22:00 | -8745.7 | 6.8587 | 42.9732 | 53.895 | -2563.1117
2020-01-24 23:00 | -8772.35 | 6.8587 | 42.8149 | 53.895 | -2570.922
2020-01-26 | -9654.21 | 6.8587 | 42.1502 | 53.895 | -2829.3697
2020-01-27 01:00 | -9714.14 | 6.8587 | 41.9477 | 53.895 | -2846.9334
2020-01-28 02:00 | -9897.29 | 6.8587 | 41.7027 | 53.895 | -2900.6094
2020-01-29 03:00 | -9678.68 | 6.8587 | 41.7503 | 53.895 | -2836.5411
2020-01-30 04:00 | -9417.14 | 6.8587 | 41.8688 | 53.895 | -2759.8913
2020-01-31 05:00 | -9172.23 | 6.8587 | 41.989 | 53.895 | -2688.1153
2020-02-01 06:00 | -8543.95 | 6.8587 | 42.4066 | 53.895 | -2503.9846
2020-02-02 07:00 | -8385.45 | 6.8587 | 42.5609 | 53.895 | -2457.5328
2020-02-03 08:00 | -8077.36 | 6.8587 | 42.7981 | 53.895 | -2367.2405
2020-02-04 09:00 | -8575.68 | 6.8587 | 42.4952 | 53.895 | -2513.2837
2020-02-05 10:00 | -8378.45 | 6.8587 | 42.5773 | 53.895 | -2455.4813
2020-02-06 11:00 | -7977.37 | 6.8587 | 42.8338 | 53.895 | -2337.9364
2020-02-07 12:00 | -7523.6 | 6.8587 | 43.1781 | 53.895 | -2204.9495
2020-02-08 13:00 | -7406.03 | 6.8587 | 43.3186 | 53.895 | -2170.4931
2020-02-09 14:00 | -7314.33 | 6.8587 | 43.4141 | 53.895 | -2143.6185
2020-02-10 15:00 | -6874.3 | 6.8587 | 43.7478 | 53.895 | -2014.6585
2020-02-11 16:00 | -6465.26 | 6.8587 | 44.0997 | 53.895 | -1894.7807
2020-02-12 17:00 | -6364.79 | 6.8587 | 44.2472 | 53.895 | -1865.3358
2020-02-13 18:00 | -6337.24 | 6.8587 | 44.3091 | 53.895 | -1857.2617
2020-02-14 19:00 | -6951.47 | 6.8587 | 43.9137 | 53.895 | -2037.2748
2020-02-15 20:00 | -7107.64 | 6.8587 | 43.7455 | 53.895 | -2083.0437
2020-02-16 21:00 | -7971.19 | 6.8587 | 43.1023 | 53.895 | -2336.1252
2020-02-17 22:00 | -8148.05 | 6.8587 | 42.8383 | 53.895 | -2387.9577
2020-02-18 23:00 | -9069.75 | 6.8587 | 42.0858 | 53.895 | -2658.0813
2020-02-20 | -9314.93 | 6.8587 | 41.7434 | 53.895 | -2729.9365
2020-02-21 01:00 | -9520.21 | 6.8587 | 41.464 | 53.895 | -2790.0981
2020-02-22 02:00 | -10027.9 | 6.8587 | 40.9967 | 53.895 | -2938.8874
2020-02-23 03:00 | -10066.2 | 6.8587 | 40.8189 | 53.895 | -2950.112
2020-02-24 04:00 | -10053.2 | 6.8587 | 40.7036 | 53.895 | -2946.3021
2020-02-25 05:00 | -10089.5 | 6.8587 | 40.591 | 53.895 | -2956.9406
2020-02-26 06:00 | -9575.99 | 6.8587 | 40.8533 | 53.895 | -2806.4456
2020-02-27 07:00 | -9948.29 | 6.8587 | 40.5823 | 53.895 | -2915.556
2020-02-28 08:00 | -9699.45 | 6.8587 | 40.6729 | 53.895 | -2842.6282
2020-02-29 09:00 | -10656.7 | 6.8587 | 39.9846 | 53.895 | -3123.1705
2020-03-01 10:00 | -10024.2 | 6.8587 | 40.2637 | 53.895 | -2937.803
2020-03-02 11:00 | -8919.84 | 6.8587 | 40.9985 | 53.895 | -2614.1471
2020-03-03 12:00 | -8036.82 | 6.8587 | 41.7063 | 53.895 | -2355.3594
2020-03-04 13:00 | -7899.2 | 6.8587 | 41.9438 | 53.895 | -2315.027
2020-03-05 14:00 | -9097.28 | 6.8587 | 41.1992 | 53.895 | -2666.1496
2020-03-06 15:00 | -9670.02 | 6.8587 | 40.7146 | 53.895 | -2834.0031
2020-03-07 16:00 | -9614.16 | 6.8587 | 40.6333 | 53.895 | -2817.6322
2020-03-08 17:00 | -9674.91 | 6.8587 | 40.5209 | 53.895 | -2835.4362
2020-03-09 18:00 | -9756.89 | 6.8587 | 40.3788 | 53.895 | -2859.4622
2020-03-10 19:00 | -10530.5 | 6.8587 | 39.7576 | 53.895 | -3086.1849
2020-03-11 20:00 | -10765.7 | 6.8587 | 39.4373 | 53.895 | -3155.1152
2020-03-12 21:00 | -11854.3 | 6.8587 | 38.5721 | 53.895 | -3474.1524
2020-03-13 22:00 | -12088.1 | 6.8587 | 38.1857 | 53.895 | -3542.6724
2020-03-14 23:00 | -12402 | 6.8587 | 37.776 | 53.895 | -3634.6674
2020-03-16 | -12712.4 | 6.8587 | 37.3714 | 53.895 | -3725.6367
2020-03-17 01:00 | -12903.6 | 6.8587 | 37.0496 | 53.895 | -3781.6719
2020-03-18 02:00 | -13024.9 | 6.8587 | 36.7989 | 53.895 | -3817.2214
2020-03-19 03:00 | -13058.9 | 6.8587 | 36.6413 | 53.895 | -3827.1858
2020-03-20 04:00 | -13161.9 | 6.8587 | 36.4482 | 53.895 | -3857.3721
2020-03-21 05:00 | -13355.9 | 6.8587 | 36.1915 | 53.895 | -3914.2279
2020-03-22 06:00 | -13172.3 | 6.8587 | 36.1797 | 53.895 | -3860.4201
2020-03-23 07:00 | -13132.1 | 6.8587 | 36.1205 | 53.895 | -3848.6386
2020-03-24 08:00 | -13188.1 | 6.8587 | 35.999 | 53.895 | -3865.0506
2020-03-25 09:00 | -13190.2 | 6.8587 | 35.9176 | 53.895 | -3865.666
2020-03-26 10:00 | -12908.2 | 6.8587 | 36.0346 | 53.895 | -3783.02
2020-03-27 11:00 | -12791.9 | 6.8587 | 36.076 | 53.895 | -3748.9358
2020-03-28 12:00 | -11962.3 | 6.8587 | 36.602 | 53.895 | -3505.8041
2020-03-29 13:00 | -11397.8 | 6.8587 | 37.0366 | 53.895 | -3340.3654
2020-03-30 14:00 | -11020.6 | 6.8587 | 37.3732 | 53.895 | -3229.819
2020-03-31 15:00 | -10243.8 | 6.8587 | 37.9781 | 53.895 | -3002.1614
2020-04-01 16:00 | -10344.2 | 6.8587 | 38.0339 | 53.895 | -3031.5858
2020-04-02 17:00 | -10585.1 | 6.8587 | 37.9255 | 53.895 | -3102.1866
2020-04-03 18:00 | -10988.8 | 6.8587 | 37.6365 | 53.895 | -3220.4994
2020-04-04 19:00 | -11545 | 6.8587 | 37.2006 | 53.895 | -3383.5055
2020-04-05 20:00 | -11914.9 | 6.8587 | 36.8455 | 53.895 | -3491.9125
2020-04-06 21:00 | -12309 | 6.8587 | 36.4612 | 53.895 | -3607.4118
2020-04-07 22:00 | -12695.4 | 6.8587 | 36.0702 | 53.895 | -3720.6545
2020-04-08 23:00 | -13119.8 | 6.8587 | 35.6445 | 53.895 | -3845.0338
2020-04-10 | -13430 | 6.8587 | 35.2921 | 53.895 | -3935.9445
2020-04-11 01:00 | -13381 | 6.8587 | 35.1901 | 53.895 | -3921.584
2020-04-12 02:00 | -13401 | 6.8587 | 35.0838 | 53.895 | -3927.4454
2020-04-13 03:00 | -13622.2 | 6.8587 | 34.8438 | 53.895 | -3992.2727
2020-04-14 04:00 | -13680 | 6.8587 | 34.6971 | 53.895 | -4009.2122
2020-04-15 05:00 | -13621.8 | 6.8587 | 34.6485 | 53.895 | -3992.1555
2020-04-16 06:00 | -13477.7 | 6.8587 | 34.6853 | 53.895 | -3949.924
2020-04-17 07:00 | -13325.6 | 6.8587 | 34.7496 | 53.895 | -3905.3479
2020-04-18 08:00 | -13284.6 | 6.8587 | 34.7501 | 53.895 | -3893.3319
2020-04-19 09:00 | -13264.9 | 6.8587 | 34.7401 | 53.895 | -3887.5584
2020-04-20 10:00 | -13168.8 | 6.8587 | 34.7797 | 53.895 | -3859.3943
2020-04-21 11:00 | -12792 | 6.8587 | 35.0219 | 53.895 | -3748.9651
2020-04-22 12:00 | -12164.8 | 6.8587 | 35.4729 | 53.895 | -3565.151
2020-04-23 13:00 | -9921.97 | 6.8587 | 37.0869 | 53.895 | -2907.8424
2020-04-24 14:00 | -8876.86 | 6.8587 | 38.1146 | 53.895 | -2601.5509
2020-04-25 15:00 | -8148.61 | 6.8587 | 38.9136 | 53.895 | -2388.1219
2020-04-26 16:00 | -7956.92 | 6.8587 | 39.3076 | 53.895 | -2331.9431
2020-04-27 17:00 | -8835.16 | 6.8587 | 38.9097 | 53.895 | -2589.3298
2020-04-28 18:00 | -9316.68 | 6.8587 | 38.6281 | 53.895 | -2730.4494
2020-04-29 19:00 | -9963.72 | 6.8587 | 38.1697 | 53.895 | -2920.0781
2020-04-30 20:00 | -10543.8 | 6.8587 | 37.7089 | 53.895 | -3090.0827
2020-05-01 21:00 | -11564.2 | 6.8587 | 36.9111 | 53.895 | -3389.1325
2020-05-02 22:00 | -11771.9 | 6.8587 | 36.5914 | 53.895 | -3450.0033
2020-05-03 23:00 | -12234.5 | 6.8587 | 36.1613 | 53.895 | -3585.578
2020-05-05 | -12567.4 | 6.8587 | 35.8117 | 53.895 | -3683.1414
2020-05-06 01:00 | -12632.1 | 6.8587 | 35.6265 | 53.895 | -3702.1031
2020-05-07 02:00 | -12637.9 | 6.8587 | 35.5086 | 53.895 | -3703.8029
2020-05-08 03:00 | -12656.5 | 6.8587 | 35.4099 | 53.895 | -3709.254
2020-05-09 04:00 | -12719.6 | 6.8587 | 35.283 | 53.895 | -3727.7468
2020-05-10 05:00 | -12711.2 | 6.8587 | 35.2172 | 53.895 | -3725.285
2020-05-11 06:00 | -12650.4 | 6.8587 | 35.2026 | 53.895 | -3707.4663
2020-05-12 07:00 | -12356.9 | 6.8587 | 35.3649 | 53.895 | -3621.4499
2020-05-13 08:00 | -11866.1 | 6.8587 | 35.703 | 53.895 | -3477.6106
2020-05-14 09:00 | -11755.6 | 6.8587 | 35.8354 | 53.895 | -3445.2263
2020-05-15 10:00 | -10917.6 | 6.8587 | 36.4489 | 53.895 | -3199.6327
2020-05-16 11:00 | -10176.3 | 6.8587 | 37.0831 | 53.895 | -2982.3791
2020-05-17 12:00 | -8795.85 | 6.8587 | 38.1981 | 53.895 | -2577.8092
2020-05-18 13:00 | -8016.8 | 6.8587 | 38.9887 | 53.895 | -2349.4922
2020-05-19 14:00 | -7655.89 | 6.8587 | 39.4756 | 53.895 | -2243.7199
2020-05-20 15:00 | -8020.34 | 6.8587 | 39.416 | 53.895 | -2350.5296
2020-05-21 16:00 | -8100.04 | 6.8587 | 39.4439 | 53.895 | -2373.8874
2020-05-22 17:00 | -6712.75 | 6.8587 | 40.4675 | 53.895 | -1967.3128
2020-05-23 18:00 | -6936.52 | 6.8587 | 40.5494 | 53.895 | -2032.8933
2020-05-24 19:00 | -7201.33 | 6.8587 | 40.4896 | 53.895 | -2110.5015
2020-05-25 20:00 | -7561.23 | 6.8587 | 40.2911 | 53.895 | -2215.9778
2020-05-26 21:00 | -7555.39 | 6.8587 | 40.3332 | 53.895 | -2214.2662
2020-05-27 22:00 | -7429.2 | 6.8587 | 40.4815 | 53.895 | -2177.2836
2020-05-28 23:00 | -7392.95 | 6.8587 | 40.5632 | 53.895 | -2166.6598
2020-05-30 | -8768.21 | 6.8587 | 39.6664 | 53.895 | -2569.7087
2020-05-31 01:00 | -8734.3 | 6.8587 | 39.5546 | 53.895 | -2559.7706
2020-06-01 02:00 | -8812.47 | 6.8587 | 39.4477 | 53.895 | -2582.68
2020-06-02 03:00 | -9280.25 | 6.8587 | 39.1088 | 53.895 | -2719.7728
2020-06-03 04:00 | -9436.53 | 6.8587 | 38.9263 | 53.895 | -2765.5739
2020-06-04 05:00 | -9518.35 | 6.8587 | 38.7875 | 53.895 | -2789.553
2020-06-05 06:00 | -9627.73 | 6.8587 | 38.6722 | 53.895 | -2821.6091
2020-06-06 07:00 | -8596.75 | 6.8587 | 39.337 | 53.895 | -2519.4587
2020-06-07 08:00 | -8170.63 | 6.8587 | 39.7276 | 53.895 | -2394.5753
2020-06-08 09:00 | -8798.71 | 6.8587 | 39.4059 | 53.895 | -2578.6474
2020-06-09 10:00 | -8923.7 | 6.8587 | 39.2913 | 53.895 | -2615.2783
2020-06-10 11:00 | -8657.87 | 6.8587 | 39.4449 | 53.895 | -2537.3712
2020-06-11 12:00 | -8379.68 | 6.8587 | 39.674 | 53.895 | -2455.8418
2020-06-12 13:00 | -8946.16 | 6.8587 | 39.3156 | 53.895 | -2621.8607
2020-06-13 14:00 | -9553.02 | 6.8587 | 38.8229 | 53.895 | -2799.7138
2020-06-14 15:00 | -10001.7 | 6.8587 | 38.402 | 53.895 | -2931.2089
2020-06-15 16:00 | -10164.7 | 6.8587 | 38.1752 | 53.895 | -2978.9795
2020-06-16 17:00 | -9159.67 | 6.8587 | 38.7649 | 53.895 | -2684.4343
2020-06-17 18:00 | -9757.87 | 6.8587 | 38.4009 | 53.895 | -2859.7494
2020-06-18 19:00 | -10015.5 | 6.8587 | 38.1504 | 53.895 | -2935.2533
2020-06-19 20:00 | -10290.9 | 6.8587 | 37.8677 | 53.895 | -3015.9651
2020-06-20 21:00 | -10810.2 | 6.8587 | 37.4347 | 53.895 | -3168.1569
2020-06-21 22:00 | -11503.1 | 6.8587 | 36.8435 | 53.895 | -3371.2258
2020-06-22 23:00 | -11955.7 | 6.8587 | 36.3436 | 53.895 | -3503.8698
2020-06-24 | -12510.7 | 6.8587 | 35.7872 | 53.895 | -3666.5242
2020-06-25 01:00 | -13217.9 | 6.8587 | 35.1126 | 53.895 | -3873.7841
2020-06-26 02:00 | -13582.2 | 6.8587 | 34.6404 | 53.895 | -3980.5499
2020-06-27 03:00 | -13942.6 | 6.8587 | 34.1988 | 53.895 | -4086.1727
2020-06-28 04:00 | -14081.5 | 6.8587 | 33.92 | 53.895 | -4126.8803
2020-06-29 05:00 | -14174.2 | 6.8587 | 33.6893 | 53.895 | -4154.048
2020-06-30 06:00 | -14231 | 6.8587 | 33.5087 | 53.895 | -4170.6944
2020-07-01 07:00 | -14244.5 | 6.8587 | 33.3715 | 53.895 | -4174.6509
2020-07-02 08:00 | -14241 | 6.8587 | 33.2577 | 53.895 | -4173.6251
2020-07-03 09:00 | -13933.3 | 6.8587 | 33.3731 | 53.895 | -4083.4471
2020-07-04 10:00 | -13255.4 | 6.8587 | 33.7934 | 53.895 | -3884.7743
2020-07-05 11:00 | -12244.4 | 6.8587 | 34.5202 | 53.895 | -3588.4794
2020-07-06 12:00 | -11443.8 | 6.8587 | 35.181 | 53.895 | -3353.8467
2020-07-07 13:00 | -10826.1 | 6.8587 | 35.7483 | 53.895 | -3172.8167
2020-07-08 14:00 | -10684.6 | 6.8587 | 35.9956 | 53.895 | -3131.3472
2020-07-09 15:00 | -10489.2 | 6.8587 | 36.2385 | 53.895 | -3074.0811
2020-07-10 16:00 | -10569.2 | 6.8587 | 36.278 | 53.895 | -3097.5268
2020-07-11 17:00 | -11825.5 | 6.8587 | 35.4531 | 53.895 | -3465.7119
2020-07-12 18:00 | -12094.6 | 6.8587 | 35.1329 | 53.895 | -3544.5774
2020-07-13 19:00 | -12563.8 | 6.8587 | 34.7021 | 53.895 | -3682.0863
2020-07-14 20:00 | -13154 | 6.8587 | 34.1815 | 53.895 | -3855.0569
2020-07-15 21:00 | -13666 | 6.8587 | 33.6688 | 53.895 | -4005.1092
2020-07-16 22:00 | -14012.3 | 6.8587 | 33.2462 | 53.895 | -4106.5998
2020-07-17 23:00 | -14411.1 | 6.8587 | 32.8113 | 53.895 | -4223.4765
2020-07-19 | -14746.9 | 6.8587 | 32.4144 | 53.895 | -4321.8898
2020-07-20 01:00 | -14831.2 | 6.8587 | 32.1882 | 53.895 | -4346.5957
2020-07-21 02:00 | -14870.3 | 6.8587 | 32.0275 | 53.895 | -4358.0547
2020-07-22 03:00 | -15014.9 | 6.8587 | 31.8165 | 53.895 | -4400.4328
2020-07-23 04:00 | -15065.6 | 6.8587 | 31.6655 | 53.895 | -4415.2915
2020-07-24 05:00 | -14927 | 6.8587 | 31.6709 | 53.895 | -4374.6719
2020-07-25 06:00 | -14763.9 | 6.8587 | 31.7294 | 53.895 | -4326.872
2020-07-26 07:00 | -14626.5 | 6.8587 | 31.7886 | 53.895 | -4286.604
2020-07-27 08:00 | -14639.8 | 6.8587 | 31.7531 | 53.895 | -4290.5019
2020-07-28 09:00 | -14358.5 | 6.8587 | 31.9153 | 53.895 | -4208.061
2020-07-29 10:00 | -13616.7 | 6.8587 | 32.4308 | 53.895 | -3990.6608
2020-07-30 11:00 | -12962.8 | 6.8587 | 32.9612 | 53.895 | -3799.0217
2020-07-31 12:00 | -12135.5 | 6.8587 | 33.6391 | 53.895 | -3556.564
2020-08-01 13:00 | -11822 | 6.8587 | 34.0043 | 53.895 | -3464.6862
2020-08-02 14:00 | -11098.5 | 6.8587 | 34.6221 | 53.895 | -3252.6493
2020-08-03 15:00 | -10680.2 | 6.8587 | 35.0736 | 53.895 | -3130.0576
2020-08-04 16:00 | -10759.8 | 6.8587 | 35.1709 | 53.895 | -3153.3861
2020-08-05 17:00 | -11111.2 | 6.8587 | 35.0139 | 53.895 | -3256.3713
2020-08-06 18:00 | -10947 | 6.8587 | 35.1434 | 53.895 | -3208.249
2020-08-07 19:00 | -11508.7 | 6.8587 | 34.8117 | 53.895 | -3372.867
2020-08-08 20:00 | -11711.2 | 6.8587 | 34.6469 | 53.895 | -3432.2139
2020-08-09 21:00 | -12154.9 | 6.8587 | 34.3095 | 53.895 | -3562.2495
2020-08-10 22:00 | -12392 | 6.8587 | 34.0842 | 53.895 | -3631.7367
2020-08-11 23:00 | -12774.6 | 6.8587 | 33.7633 | 53.895 | -3743.8657
2020-08-13 | -13148.4 | 6.8587 | 33.415 | 53.895 | -3853.4157
2020-08-14 01:00 | -13230.6 | 6.8587 | 33.262 | 53.895 | -3877.5061
2020-08-15 02:00 | -13354.6 | 6.8587 | 33.1009 | 53.895 | -3913.8469
2020-08-16 03:00 | -13386.2 | 6.8587 | 33.0104 | 53.895 | -3923.108
2020-08-17 04:00 | -13269.9 | 6.8587 | 33.0342 | 53.895 | -3889.0238
2020-08-18 05:00 | -13130.9 | 6.8587 | 33.1056 | 53.895 | -3848.2869
2020-08-19 06:00 | -12867.7 | 6.8587 | 33.2803 | 53.895 | -3771.1506
2020-08-20 07:00 | -12721.3 | 6.8587 | 33.4035 | 53.895 | -3728.245
2020-08-21 08:00 | -12657.2 | 6.8587 | 33.4733 | 53.895 | -3709.4591
2020-08-22 09:00 | -12611.2 | 6.8587 | 33.5254 | 53.895 | -3695.9779
2020-08-23 10:00 | -12407.5 | 6.8587 | 33.6774 | 53.895 | -3636.2793
2020-08-24 11:00 | -11793.9 | 6.8587 | 34.1283 | 53.895 | -3456.4509
2020-08-25 12:00 | -11464.8 | 6.8587 | 34.441 | 53.895 | -3360.0012
2020-08-26 13:00 | -10729.9 | 6.8587 | 35.0261 | 53.895 | -3144.6233
2020-08-27 14:00 | -10427 | 6.8587 | 35.3651 | 53.895 | -3055.852
2020-08-28 15:00 | -10324.8 | 6.8587 | 35.5505 | 53.895 | -3025.9002
2020-08-29 16:00 | -9781.41 | 6.8587 | 36.008 | 53.895 | -2866.6483
2020-08-30 17:00 | -9273.85 | 6.8587 | 36.4841 | 53.895 | -2717.8971
2020-08-31 18:00 | -8896.69 | 6.8587 | 36.8926 | 53.895 | -2607.3625
2020-09-01 19:00 | -9176.23 | 6.8587 | 36.8403 | 53.895 | -2689.2875
2020-09-02 20:00 | -8790.14 | 6.8587 | 37.1703 | 53.895 | -2576.1357
2020-09-03 21:00 | -9378.97 | 6.8587 | 36.8834 | 53.895 | -2748.7048
2020-09-04 22:00 | -9541.29 | 6.8587 | 36.7914 | 53.895 | -2796.2761
2020-09-05 23:00 | -10140.3 | 6.8587 | 36.3846 | 53.895 | -2971.8286
2020-09-07 | -10219.4 | 6.8587 | 36.28 | 53.895 | -2995.0105
2020-09-08 01:00 | -9828.84 | 6.8587 | 36.5255 | 53.895 | -2880.5487
2020-09-09 02:00 | -9619.52 | 6.8587 | 36.7092 | 53.895 | -2819.203
2020-09-10 03:00 | -9439.18 | 6.8587 | 36.8932 | 53.895 | -2766.3506
2020-09-11 04:00 | -9021.69 | 6.8587 | 37.2371 | 53.895 | -2643.9963
2020-09-12 05:00 | -8919.93 | 6.8587 | 37.4067 | 53.895 | -2614.1734
2020-09-13 06:00 | -8190.46 | 6.8587 | 37.9885 | 53.895 | -2400.3869
2020-09-14 07:00 | -8161.93 | 6.8587 | 38.1547 | 53.895 | -2392.0256
2020-09-15 08:00 | -7988.06 | 6.8587 | 38.3723 | 53.895 | -2341.0693
2020-09-16 09:00 | -8557.06 | 6.8587 | 38.0797 | 53.895 | -2507.8267
2020-09-17 10:00 | -8573.29 | 6.8587 | 38.0742 | 53.895 | -2512.5833
2020-09-18 11:00 | -8203.72 | 6.8587 | 38.3556 | 53.895 | -2404.273
2020-09-19 12:00 | -8370.94 | 6.8587 | 38.3143 | 53.895 | -2453.2803
2020-09-20 13:00 | -8760.18 | 6.8587 | 38.071 | 53.895 | -2567.3553
2020-09-21 14:00 | -9078.1 | 6.8587 | 37.8169 | 53.895 | -2660.5285
2020-09-22 15:00 | -9111.58 | 6.8587 | 37.7536 | 53.895 | -2670.3405
2020-09-23 16:00 | -8340.39 | 6.8587 | 38.2626 | 53.895 | -2444.327
2020-09-24 17:00 | -8242.02 | 6.8587 | 38.4068 | 53.895 | -2415.4976
2020-09-25 18:00 | -8118.88 | 6.8587 | 38.5342 | 53.895 | -2379.4088
2020-09-26 19:00 | -8425.53 | 6.8587 | 38.3638 | 53.895 | -2469.2791
2020-09-27 20:00 | -8800.61 | 6.8587 | 38.1015 | 53.895 | -2579.2042
2020-09-28 21:00 | -9554.3 | 6.8587 | 37.5558 | 53.895 | -2800.0889
2020-09-29 22:00 | -9885.25 | 6.8587 | 37.2213 | 53.895 | -2897.0808
2020-09-30 23:00 | -10731.1 | 6.8587 | 36.5418 | 53.895 | -3144.975
2020-10-02 | -10897.6 | 6.8587 | 36.2648 | 53.895 | -3193.7713
2020-10-03 01:00 | -10730.5 | 6.8587 | 36.2628 | 53.895 | -3144.7991
2020-10-04 02:00 | -10625.6 | 6.8587 | 36.286 | 53.895 | -3114.056
2020-10-05 03:00 | -10641.9 | 6.8587 | 36.251 | 53.895 | -3118.833
2020-10-06 04:00 | -10488.4 | 6.8587 | 36.3164 | 53.895 | -3073.8466
2020-10-07 05:00 | -10383.4 | 6.8587 | 36.3816 | 53.895 | -3043.0741
2020-10-08 06:00 | -9782.08 | 6.8587 | 36.7918 | 53.895 | -2866.8447
2020-10-09 07:00 | -9969.89 | 6.8587 | 36.724 | 53.895 | -2921.8863
2020-10-10 08:00 | -9620.43 | 6.8587 | 36.9666 | 53.895 | -2819.4697
2020-10-11 09:00 | -9340.23 | 6.8587 | 37.2081 | 53.895 | -2737.3512
2020-10-12 10:00 | -8073.24 | 6.8587 | 38.1498 | 53.895 | -2366.0331
2020-10-13 11:00 | -6845.42 | 6.8587 | 39.2003 | 53.895 | -2006.1946
2020-10-14 12:00 | -5646.31 | 6.8587 | 40.296 | 53.895 | -1654.7701
2020-10-15 13:00 | -5150.97 | 6.8587 | 40.9547 | 53.895 | -1509.6003
2020-10-16 14:00 | -4483.08 | 6.8587 | 41.6838 | 53.895 | -1313.8611
2020-10-17 15:00 | -5164.44 | 6.8587 | 41.5008 | 53.895 | -1513.548
2020-10-18 16:00 | -5472.7 | 6.8587 | 41.4041 | 53.895 | -1603.89
2020-10-19 17:00 | -5719.01 | 6.8587 | 41.2995 | 53.895 | -1676.0764
2020-10-20 18:00 | -6032.78 | 6.8587 | 41.123 | 53.895 | -1768.0333
2020-10-21 19:00 | -6737.52 | 6.8587 | 40.6564 | 53.895 | -1974.5722
2020-10-22 20:00 | -6999.97 | 6.8587 | 40.413 | 53.895 | -2051.4887
2020-10-23 21:00 | -8011.46 | 6.8587 | 39.6871 | 53.895 | -2347.9272
2020-10-24 22:00 | -8234.02 | 6.8587 | 39.407 | 53.895 | -2413.1531
2020-10-25 23:00 | -8732.89 | 6.8587 | 38.9703 | 53.895 | -2559.3574
2020-10-27 | -9242.34 | 6.8587 | 38.5024 | 53.895 | -2708.6625
2020-10-28 01:00 | -9455.04 | 6.8587 | 38.2152 | 53.895 | -2770.9987
2020-10-29 02:00 | -9643.25 | 6.8587 | 37.9586 | 53.895 | -2826.1576
2020-10-30 03:00 | -9677.85 | 6.8587 | 37.8392 | 53.895 | -2836.2979
2020-10-31 04:00 | -9560.15 | 6.8587 | 37.8432 | 53.895 | -2801.8034
2020-11-01 05:00 | -9553.89 | 6.8587 | 37.8053 | 53.895 | -2799.9688
2020-11-02 06:00 | -9434.36 | 6.8587 | 37.8493 | 53.895 | -2764.938
2020-11-03 07:00 | -8715.77 | 6.8587 | 38.3291 | 53.895 | -2554.34
2020-11-04 08:00 | -8183.68 | 6.8587 | 38.7694 | 53.895 | -2398.3999
2020-11-05 09:00 | -8684.35 | 6.8587 | 38.5354 | 53.895 | -2545.1317
2020-11-06 10:00 | -8712.7 | 6.8587 | 38.5036 | 53.895 | -2553.4403
2020-11-07 11:00 | -8525.33 | 6.8587 | 38.6234 | 53.895 | -2498.5276
2020-11-08 12:00 | -8126.66 | 6.8587 | 38.9251 | 53.895 | -2381.6889
2020-11-09 13:00 | -7487.04 | 6.8587 | 39.4175 | 53.895 | -2194.2348
2020-11-10 14:00 | -7168.2 | 6.8587 | 39.7296 | 53.895 | -2100.792
2020-11-11 15:00 | -7497.89 | 6.8587 | 39.603 | 53.895 | -2197.4146
2020-11-12 16:00 | -7782.26 | 6.8587 | 39.4276 | 53.895 | -2280.7553
2020-11-13 17:00 | -6851.57 | 6.8587 | 40.0568 | 53.895 | -2007.997
2020-11-14 18:00 | -7284.47 | 6.8587 | 39.8844 | 53.895 | -2134.8674
2020-11-15 19:00 | -7691.06 | 6.8587 | 39.6192 | 53.895 | -2254.0272
2020-11-16 20:00 | -8107.14 | 6.8587 | 39.2807 | 53.895 | -2375.9682
2020-11-17 21:00 | -8498.64 | 6.8587 | 38.9622 | 53.895 | -2490.7055
2020-11-18 22:00 | -8984.06 | 6.8587 | 38.5731 | 53.895 | -2632.9681
2020-11-19 23:00 | -9232.14 | 6.8587 | 38.3039 | 53.895 | -2705.6731
2020-11-21 | -10631.7 | 6.8587 | 37.2582 | 53.895 | -3115.8437
2020-11-22 01:00 | -10824.2 | 6.8587 | 36.895 | 53.895 | -3172.2599
2020-11-23 02:00 | -10964.3 | 6.8587 | 36.6338 | 53.895 | -3213.3191
2020-11-24 03:00 | -11048.1 | 6.8587 | 36.46 | 53.895 | -3237.8785
2020-11-25 04:00 | -11250.2 | 6.8587 | 36.2196 | 53.895 | -3297.1082
2020-11-26 05:00 | -11369.1 | 6.8587 | 36.0145 | 53.895 | -3331.9543
2020-11-27 06:00 | -11622.7 | 6.8587 | 35.7462 | 53.895 | -3406.2771
2020-11-28 07:00 | -10973.1 | 6.8587 | 36.0853 | 53.895 | -3215.8982
2020-11-29 08:00 | -10781.1 | 6.8587 | 36.2134 | 53.895 | -3159.6285
2020-11-30 09:00 | -10793.2 | 6.8587 | 36.2052 | 53.895 | -3163.1747
2020-12-01 10:00 | -9668.95 | 6.8587 | 36.9524 | 53.895 | -2833.6895
2020-12-02 11:00 | -8471.1 | 6.8587 | 37.8875 | 53.895 | -2482.6343
2020-12-03 12:00 | -7717.27 | 6.8587 | 38.6213 | 53.895 | -2261.7086
2020-12-04 13:00 | -7146.9 | 6.8587 | 39.2064 | 53.895 | -2094.5496
2020-12-05 14:00 | -6760.44 | 6.8587 | 39.6524 | 53.895 | -1981.2894
2020-12-06 15:00 | -6844.21 | 6.8587 | 39.7747 | 53.895 | -2005.8399
2020-12-07 16:00 | -7358.08 | 6.8587 | 39.5328 | 53.895 | -2156.4404
2020-12-08 17:00 | -6940.67 | 6.8587 | 39.8285 | 53.895 | -2034.1096
2020-12-09 18:00 | -7616.41 | 6.8587 | 39.4458 | 53.895 | -2232.1494
2020-12-10 19:00 | -8377.8 | 6.8587 | 38.8983 | 53.895 | -2455.2908
2020-12-11 20:00 | -9003.37 | 6.8587 | 38.3629 | 53.895 | -2638.6273
2020-12-12 21:00 | -9433.12 | 6.8587 | 37.9519 | 53.895 | -2764.5746
2020-12-13 22:00 | -9542.15 | 6.8587 | 37.7668 | 53.895 | -2796.5281
2020-12-14 23:00 | -9707.15 | 6.8587 | 37.5545 | 53.895 | -2844.8848
2020-12-16 | -11069.9 | 6.8587 | 36.5321 | 53.895 | -3244.2674
2020-12-17 01:00 | -11359.9 | 6.8587 | 36.0964 | 53.895 | -3329.258
2020-12-18 02:00 | -11617 | 6.8587 | 35.7361 | 53.895 | -3404.6066
2020-12-19 03:00 | -11868.3 | 6.8587 | 35.4162 | 53.895 | -3478.2554
2020-12-20 04:00 | -11854.2 | 6.8587 | 35.2781 | 53.895 | -3474.1231
2020-12-21 05:00 | -12001.5 | 6.8587 | 35.0522 | 53.895 | -3517.2924
2020-12-22 06:00 | -12102.1 | 6.8587 | 34.8822 | 53.895 | -3546.7754
2020-12-23 07:00 | -11305.6 | 6.8587 | 35.3337 | 53.895 | -3313.3443
2020-12-24 08:00 | -10612.3 | 6.8587 | 35.8355 | 53.895 | -3110.1581
2020-12-25 09:00 | -11005.8 | 6.8587 | 35.6485 | 53.895 | -3225.4816
2020-12-26 10:00 | -10431.9 | 6.8587 | 36.0095 | 53.895 | -3057.2881
2020-12-27 11:00 | -9896.35 | 6.8587 | 36.4147 | 53.895 | -2900.3339
2020-12-28 12:00 | -8955.37 | 6.8587 | 37.1596 | 53.895 | -2624.5599
2020-12-29 13:00 | -8783.18 | 6.8587 | 37.4303 | 53.895 | -2574.096
2020-12-30 14:00 | -7835.81 | 6.8587 | 38.1743 | 53.895 | -2296.4492
2020-12-31 15:00 | -8148.54 | 6.8587 | 38.1453 | 53.895 | -2388.1013
2021-01-01 16:00 | -7994.15 | 6.8587 | 38.3318 | 53.895 | -2342.8541
2021-01-02 17:00 | -6550.47 | 6.8587 | 39.3963 | 53.895 | -1919.7533
2021-01-03 18:00 | -7208.48 | 6.8587 | 39.1866 | 53.895 | -2112.5969
2021-01-04 19:00 | -7512.05 | 6.8587 | 39.0488 | 53.895 | -2201.5645
2021-01-05 20:00 | -7830.27 | 6.8587 | 38.8304 | 53.895 | -2294.8256
2021-01-06 21:00 | -7985.47 | 6.8587 | 38.7358 | 53.895 | -2340.3102
2021-01-07 22:00 | -7923.79 | 6.8587 | 38.7909 | 53.895 | -2322.2336
2021-01-08 23:00 | -8027.67 | 6.8587 | 38.7255 | 53.895 | -2352.6778
2021-01-10 | -9010.82 | 6.8587 | 38.0593 | 53.895 | -2640.8107
2021-01-11 01:00 | -9089.75 | 6.8587 | 37.9 | 53.895 | -2663.9428
2021-01-12 02:00 | -9015.04 | 6.8587 | 37.8914 | 53.895 | -2642.0474
2021-01-13 03:00 | -8701.9 | 6.8587 | 38.0998 | 53.895 | -2550.2751
2021-01-14 04:00 | -8596.3 | 6.8587 | 38.2012 | 53.895 | -2519.3268
2021-01-15 05:00 | -8375.33 | 6.8587 | 38.3642 | 53.895 | -2454.5669
2021-01-16 06:00 | -7980.92 | 6.8587 | 38.6866 | 53.895 | -2338.9768
2021-01-17 07:00 | -7979.15 | 6.8587 | 38.7731 | 53.895 | -2338.458
2021-01-18 08:00 | -8367.65 | 6.8587 | 38.5605 | 53.895 | -2452.3161
2021-01-19 09:00 | -9004.33 | 6.8587 | 38.1121 | 53.895 | -2638.9086
2021-01-20 10:00 | -8849.72 | 6.8587 | 38.1368 | 53.895 | -2593.5969
2021-01-21 11:00 | -8496.88 | 6.8587 | 38.3525 | 53.895 | -2490.1897
2021-01-22 12:00 | -8217.77 | 6.8587 | 38.5671 | 53.895 | -2408.3906
2021-01-23 13:00 | -8421.75 | 6.8587 | 38.4583 | 53.895 | -2468.1713
2021-01-24 14:00 | -7946.33 | 6.8587 | 38.7651 | 53.895 | -2328.8394
2021-01-25 15:00 | -8063.32 | 6.8587 | 38.7397 | 53.895 | -2363.1258
2021-01-26 16:00 | -7492.73 | 6.8587 | 39.1496 | 53.895 | -2195.9024
2021-01-27 17:00 | -8248.81 | 6.8587 | 38.6942 | 53.895 | -2417.4876
2021-01-28 18:00 | -9104.75 | 6.8587 | 38.0428 | 53.895 | -2668.3388
2021-01-29 19:00 | -9754.46 | 6.8587 | 37.4559 | 53.895 | -2858.75
2021-01-30 20:00 | -9940.92 | 6.8587 | 37.173 | 53.895 | -2913.3961
2021-01-31 21:00 | -10900.9 | 6.8587 | 36.4087 | 53.895 | -3194.7384
2021-02-01 22:00 | -11342.4 | 6.8587 | 35.8956 | 53.895 | -3324.1293
2021-02-02 23:00 | -12114.1 | 6.8587 | 35.1707 | 53.895 | -3550.2922
2021-02-04 | -12415.8 | 6.8587 | 34.7525 | 53.895 | -3638.7118
2021-02-05 01:00 | -12550.5 | 6.8587 | 34.4845 | 53.895 | -3678.1885
2021-02-06 02:00 | -12673.7 | 6.8587 | 34.2478 | 53.895 | -3714.2948
2021-02-07 03:00 | -12766.2 | 6.8587 | 34.0538 | 53.895 | -3741.4039
2021-02-08 04:00 | -12748 | 6.8587 | 33.9379 | 53.895 | -3736.07
2021-02-09 05:00 | -12627.4 | 6.8587 | 33.9273 | 53.895 | -3700.7256
2021-02-10 06:00 | -12447 | 6.8587 | 33.9887 | 53.895 | -3647.8556
2021-02-11 07:00 | -12350.6 | 6.8587 | 34.0143 | 53.895 | -3619.6036
2021-02-12 08:00 | -12306.3 | 6.8587 | 34.0064 | 53.895 | -3606.6205
2021-02-13 09:00 | -11731.5 | 6.8587 | 34.3762 | 53.895 | -3438.1633
2021-02-14 10:00 | -10143.8 | 6.8587 | 35.5143 | 53.895 | -2972.8543
2021-02-15 11:00 | -8606.51 | 6.8587 | 36.7879 | 53.895 | -2522.3191
2021-02-16 12:00 | -7978.49 | 6.8587 | 37.5192 | 53.895 | -2338.2646
2021-02-17 13:00 | -7595.11 | 6.8587 | 38.0274 | 53.895 | -2225.907
2021-02-18 14:00 | -7444.54 | 6.8587 | 38.3362 | 53.895 | -2181.7793
2021-02-19 15:00 | -7496.51 | 6.8587 | 38.4751 | 53.895 | -2197.0102
2021-02-20 16:00 | -7722.34 | 6.8587 | 38.4315 | 53.895 | -2263.1944
2021-02-21 17:00 | -8601.75 | 6.8587 | 37.8735 | 53.895 | -2520.9241
2021-02-22 18:00 | -8839.38 | 6.8587 | 37.6505 | 53.895 | -2590.5666
2021-02-23 19:00 | -9352.99 | 6.8587 | 37.2582 | 53.895 | -2741.0908
2021-02-24 20:00 | -9768.01 | 6.8587 | 36.9076 | 53.895 | -2862.7211
2021-02-25 21:00 | -10921.3 | 6.8587 | 36.0324 | 53.895 | -3200.7171
2021-02-26 22:00 | -11370.7 | 6.8587 | 35.5236 | 53.895 | -3332.4232
2021-02-27 23:00 | -12081.3 | 6.8587 | 34.8605 | 53.895 | -3540.6795
2021-03-01 | -12343.7 | 6.8587 | 34.4808 | 53.895 | -3617.5814
2021-03-02 01:00 | -12550.1 | 6.8587 | 34.1673 | 53.895 | -3678.0712
2021-03-03 02:00 | -12689.6 | 6.8587 | 33.9183 | 53.895 | -3718.9546
2021-03-04 03:00 | -12792.8 | 6.8587 | 33.7173 | 53.895 | -3749.1996
2021-03-05 04:00 | -12800.8 | 6.8587 | 33.5972 | 53.895 | -3751.5442
2021-03-06 05:00 | -12771 | 6.8587 | 33.5354 | 53.895 | -3742.8106
2021-03-07 06:00 | -12478.2 | 6.8587 | 33.6689 | 53.895 | -3656.9994
2021-03-08 07:00 | -12285.3 | 6.8587 | 33.7782 | 53.895 | -3600.466
2021-03-09 08:00 | -12218.9 | 6.8587 | 33.8153 | 53.895 | -3581.0061
2021-03-10 09:00 | -10645.7 | 6.8587 | 34.8963 | 53.895 | -3119.9467
2021-03-11 10:00 | -9345.02 | 6.8587 | 35.9724 | 53.895 | -2738.755
2021-03-12 11:00 | -8134.72 | 6.8587 | 37.058 | 53.895 | -2384.0511
2021-03-13 12:00 | -8565.01 | 6.8587 | 37.0387 | 53.895 | -2510.1566
2021-03-14 13:00 | -7878.27 | 6.8587 | 37.6224 | 53.895 | -2308.893
2021-03-15 14:00 | -6919.41 | 6.8587 | 38.4626 | 53.895 | -2027.8789
2021-03-16 15:00 | -6634.42 | 6.8587 | 38.906 | 53.895 | -1944.3566
2021-03-17 16:00 | -6584.21 | 6.8587 | 39.1239 | 53.895 | -1929.6415
2021-03-18 17:00 | -7827.15 | 6.8587 | 38.3943 | 53.895 | -2293.9112
2021-03-19 18:00 | -8357.74 | 6.8587 | 37.9948 | 53.895 | -2449.4118
2021-03-20 19:00 | -9059.34 | 6.8587 | 37.4649 | 53.895 | -2655.0305
2021-03-21 20:00 | -9573.92 | 6.8587 | 37.0244 | 53.895 | -2805.839
2021-03-22 21:00 | -10535.7 | 6.8587 | 36.2524 | 53.895 | -3087.7089
2021-03-23 22:00 | -10970.3 | 6.8587 | 35.7593 | 53.895 | -3215.0776
2021-03-24 23:00 | -11799.4 | 6.8587 | 35.0272 | 53.895 | -3458.0628
2021-03-26 | -12049.4 | 6.8587 | 34.6611 | 53.895 | -3531.3306
2021-03-27 01:00 | -12150.9 | 6.8587 | 34.4341 | 53.895 | -3561.0773
2021-03-28 02:00 | -12239.3 | 6.8587 | 34.2452 | 53.895 | -3586.9847
2021-03-29 03:00 | -12237.5 | 6.8587 | 34.1386 | 53.895 | -3586.4572
2021-03-30 04:00 | -12072.5 | 6.8587 | 34.1614 | 53.895 | -3538.1005
2021-03-31 05:00 | -11835.1 | 6.8587 | 34.288 | 53.895 | -3468.5254
2021-04-01 06:00 | -11148.1 | 6.8587 | 34.7544 | 53.895 | -3267.1856
2021-04-02 07:00 | -10790.6 | 6.8587 | 35.0706 | 53.895 | -3162.4127
2021-04-03 08:00 | -10552.9 | 6.8587 | 35.3101 | 53.895 | -3092.7497
2021-04-04 09:00 | -11153.8 | 6.8587 | 34.9621 | 53.895 | -3268.8561
2021-04-05 10:00 | -10791.6 | 6.8587 | 35.1656 | 53.895 | -3162.7058
2021-04-06 11:00 | -10172.3 | 6.8587 | 35.6107 | 53.895 | -2981.2068
2021-04-07 12:00 | -9808.23 | 6.8587 | 35.9455 | 53.895 | -2874.5085
2021-04-08 13:00 | -9355.72 | 6.8587 | 36.3312 | 53.895 | -2741.8909
2021-04-09 14:00 | -9181.28 | 6.8587 | 36.5337 | 53.895 | -2690.7676
2021-04-10 15:00 | -8797.81 | 6.8587 | 36.878 | 53.895 | -2578.3836
2021-04-11 16:00 | -7803.75 | 6.8587 | 37.6577 | 53.895 | -2287.0534
2021-04-12 17:00 | -7547.49 | 6.8587 | 38.021 | 53.895 | -2211.951
2021-04-13 18:00 | -7610.04 | 6.8587 | 38.1213 | 53.895 | -2230.2826
2021-04-14 19:00 | -7544.2 | 6.8587 | 38.2496 | 53.895 | -2210.9868
2021-04-15 20:00 | -7905.03 | 6.8587 | 38.0866 | 53.895 | -2316.7356
2021-04-16 21:00 | -8400.01 | 6.8587 | 37.7913 | 53.895 | -2461.7999
2021-04-17 22:00 | -8502.84 | 6.8587 | 37.6993 | 53.895 | -2491.9364
2021-04-18 23:00 | -9137.67 | 6.8587 | 37.2614 | 53.895 | -2677.9867
2021-04-20 | -9534.4 | 6.8587 | 36.9285 | 53.895 | -2794.2568
2021-04-21 01:00 | -9794.33 | 6.8587 | 36.6719 | 53.895 | -2870.4348
2021-04-22 02:00 | -9845.2 | 6.8587 | 36.5739 | 53.895 | -2885.3433
2021-04-23 03:00 | -9980.92 | 6.8587 | 36.4438 | 53.895 | -2925.1189
2021-04-24 04:00 | -9856.65 | 6.8587 | 36.4772 | 53.895 | -2888.699
2021-04-25 05:00 | -9924.79 | 6.8587 | 36.4119 | 53.895 | -2908.6688
2021-04-26 06:00 | -10164.8 | 6.8587 | 36.2206 | 53.895 | -2979.0088
2021-04-27 07:00 | -10036.5 | 6.8587 | 36.2545 | 53.895 | -2941.4078
2021-04-28 08:00 | -10341.3 | 6.8587 | 36.0256 | 53.895 | -3030.7359
2021-04-29 09:00 | -10965.9 | 6.8587 | 35.5454 | 53.895 | -3213.788
2021-04-30 10:00 | -10338.8 | 6.8587 | 35.8523 | 53.895 | -3030.0032
2021-05-01 11:00 | -8933.36 | 6.8587 | 36.8201 | 53.895 | -2618.1094
2021-05-02 12:00 | -8952.74 | 6.8587 | 36.9776 | 53.895 | -2623.7891
2021-05-03 13:00 | -8850.82 | 6.8587 | 37.1156 | 53.895 | -2593.9193
2021-05-04 14:00 | -9745.27 | 6.8587 | 36.54 | 53.895 | -2856.0567
2021-05-05 15:00 | -9999.94 | 6.8587 | 36.2975 | 53.895 | -2930.6931
2021-05-06 16:00 | -10200.5 | 6.8587 | 36.0851 | 53.895 | -2989.4714
2021-05-07 17:00 | -9472.83 | 6.8587 | 36.5031 | 53.895 | -2776.2124
2021-05-08 18:00 | -10040.2 | 6.8587 | 36.1472 | 53.895 | -2942.4922
2021-05-09 19:00 | -10283 | 6.8587 | 35.9082 | 53.895 | -3013.6498
2021-05-10 20:00 | -10879.8 | 6.8587 | 35.4279 | 53.895 | -3188.5546
2021-05-11 21:00 | -11142.3 | 6.8587 | 35.1514 | 53.895 | -3265.4858
2021-05-12 22:00 | -11275.9 | 6.8587 | 34.9707 | 53.895 | -3304.6401
2021-05-13 23:00 | -11431.6 | 6.8587 | 34.768 | 53.895 | -3350.2712
2021-05-15 | -12155.7 | 6.8587 | 34.1843 | 53.895 | -3562.484
2021-05-16 01:00 | -12415.6 | 6.8587 | 33.846 | 53.895 | -3638.6532
2021-05-17 02:00 | -12274.9 | 6.8587 | 33.8157 | 53.895 | -3597.4181
2021-05-18 03:00 | -12229.1 | 6.8587 | 33.7874 | 53.895 | -3583.9954
2021-05-19 04:00 | -12229.7 | 6.8587 | 33.737 | 53.895 | -3584.1713
2021-05-20 05:00 | -12093.9 | 6.8587 | 33.7688 | 53.895 | -3544.3722
2021-05-21 06:00 | -11919.1 | 6.8587 | 33.8667 | 53.895 | -3493.1434
2021-05-22 07:00 | -10880.6 | 6.8587 | 34.5785 | 53.895 | -3188.7891
2021-05-23 08:00 | -11036.1 | 6.8587 | 34.5897 | 53.895 | -3234.3616
2021-05-24 09:00 | -11799.4 | 6.8587 | 34.1049 | 53.895 | -3458.0628
2021-05-25 10:00 | -10061.8 | 6.8587 | 35.2179 | 53.895 | -2948.8225
2021-05-26 11:00 | -9306.6 | 6.8587 | 35.9104 | 53.895 | -2727.4952
2021-05-27 12:00 | -8638 | 6.8587 | 36.5694 | 53.895 | -2531.5479
2021-05-28 13:00 | -9533.13 | 6.8587 | 36.1188 | 53.895 | -2793.8846
2021-05-29 14:00 | -8391.32 | 6.8587 | 36.9015 | 53.895 | -2459.2531
2021-05-30 15:00 | -9561.23 | 6.8587 | 36.2817 | 53.895 | -2802.1199
2021-05-31 16:00 | -9974.77 | 6.8587 | 35.9619 | 53.895 | -2923.3165
2021-06-01 17:00 | -8925.1 | 6.8587 | 36.6043 | 53.895 | -2615.6886
2021-06-02 18:00 | -9283.56 | 6.8587 | 36.4582 | 53.895 | -2720.7429
2021-06-03 19:00 | -9724.3 | 6.8587 | 36.1757 | 53.895 | -2849.911
2021-06-04 20:00 | -9794.86 | 6.8587 | 36.0611 | 53.895 | -2870.5901
2021-06-05 21:00 | -10572.1 | 6.8587 | 35.5231 | 53.895 | -3098.3767
2021-06-06 22:00 | -10575.5 | 6.8587 | 35.4287 | 53.895 | -3099.3731
2021-06-07 23:00 | -10539.6 | 6.8587 | 35.38 | 53.895 | -3088.8518
2021-06-09 | -11634.7 | 6.8587 | 34.5875 | 53.895 | -3409.794
2021-06-10 01:00 | -11626 | 6.8587 | 34.4339 | 53.895 | -3407.2443
2021-06-11 02:00 | -11457.3 | 6.8587 | 34.4409 | 53.895 | -3357.8032
2021-06-12 03:00 | -11367.5 | 6.8587 | 34.4778 | 53.895 | -3331.4854
2021-06-13 04:00 | -11189.5 | 6.8587 | 34.5817 | 53.895 | -3279.3187
2021-06-14 05:00 | -10890.4 | 6.8587 | 34.7696 | 53.895 | -3191.6612
2021-06-15 06:00 | -10822.2 | 6.8587 | 34.85 | 53.895 | -3171.6737
2021-06-16 07:00 | -10736.2 | 6.8587 | 34.9271 | 53.895 | -3146.4696
2021-06-17 08:00 | -10770.6 | 6.8587 | 34.9176 | 53.895 | -3156.5513
2021-06-18 09:00 | -10474.7 | 6.8587 | 35.1342 | 53.895 | -3069.8315
2021-06-19 10:00 | -9212.37 | 6.8587 | 36.0369 | 53.895 | -2699.8791
2021-06-20 11:00 | -8339.17 | 6.8587 | 36.8001 | 53.895 | -2443.9695
2021-06-21 12:00 | -7753.67 | 6.8587 | 37.4039 | 53.895 | -2272.3764
2021-06-22 13:00 | -7119.66 | 6.8587 | 38.0291 | 53.895 | -2086.5664
2021-06-23 14:00 | -6711.79 | 6.8587 | 38.5137 | 53.895 | -1967.0315
2021-06-24 15:00 | -7430.65 | 6.8587 | 38.2224 | 53.895 | -2177.7085
2021-06-25 16:00 | -6906.71 | 6.8587 | 38.6275 | 53.895 | -2024.1569
2021-06-26 17:00 | -7692.12 | 6.8587 | 38.1968 | 53.895 | -2254.3378
2021-06-27 18:00 | -7772.74 | 6.8587 | 38.1372 | 53.895 | -2277.9652
2021-06-28 19:00 | -8243.97 | 6.8587 | 37.8148 | 53.895 | -2416.0691
2021-06-29 20:00 | -8606.35 | 6.8587 | 37.5314 | 53.895 | -2522.2722
2021-06-30 21:00 | -9817.1 | 6.8587 | 36.6641 | 53.895 | -2877.108
2021-07-01 22:00 | -10429.6 | 6.8587 | 36.0649 | 53.895 | -3056.614
2021-07-02 23:00 | -11346.3 | 6.8587 | 35.2635 | 53.895 | -3325.2723
2021-07-04 | -11826.4 | 6.8587 | 34.7213 | 53.895 | -3465.9757
2021-07-05 01:00 | -11953.2 | 6.8587 | 34.435 | 53.895 | -3503.1371
2021-07-06 02:00 | -12127.4 | 6.8587 | 34.1576 | 53.895 | -3554.1901
2021-07-07 03:00 | -12221.6 | 6.8587 | 33.9675 | 53.895 | -3581.7974
2021-07-08 04:00 | -12126.7 | 6.8587 | 33.9157 | 53.895 | -3553.9849
2021-07-09 05:00 | -12042 | 6.8587 | 33.9051 | 53.895 | -3529.1618
2021-07-10 06:00 | -11569.1 | 6.8587 | 34.1803 | 53.895 | -3390.5685
2021-07-11 07:00 | -11435.9 | 6.8587 | 34.2774 | 53.895 | -3351.5314
2021-07-12 08:00 | -10660.7 | 6.8587 | 34.8125 | 53.895 | -3124.3428
2021-07-13 09:00 | -9543.63 | 6.8587 | 35.6766 | 53.895 | -2796.9619
2021-07-14 10:00 | -7621.96 | 6.8587 | 37.1823 | 53.895 | -2233.776
2021-07-15 11:00 | -5696.67 | 6.8587 | 38.8471 | 53.895 | -1669.5292
2021-07-16 12:00 | -4021.97 | 6.8587 | 40.4312 | 53.895 | -1178.7231
2021-07-17 13:00 | -3127.63 | 6.8587 | 41.5231 | 53.895 | -916.6179
2021-07-18 14:00 | -2722.04 | 6.8587 | 42.2227 | 53.895 | -797.7512
2021-07-19 15:00 | -2532.07 | 6.8587 | 42.7102 | 53.895 | -742.0765
2021-07-20 16:00 | -1912.46 | 6.8587 | 43.4227 | 53.895 | -560.4867
2021-07-21 17:00 | -2803.52 | 6.8587 | 43.1137 | 53.895 | -821.6306
2021-07-22 18:00 | -3749.88 | 6.8587 | 42.5792 | 53.895 | -1098.9813
2021-07-23 19:00 | -4528.7 | 6.8587 | 42.0518 | 53.895 | -1327.231
2021-07-24 20:00 | -4852.75 | 6.8587 | 41.8023 | 53.895 | -1422.2006
2021-07-25 21:00 | -5799.83 | 6.8587 | 41.149 | 53.895 | -1699.7624
2021-07-26 22:00 | -5943.49 | 6.8587 | 40.9397 | 53.895 | -1741.865
2021-07-27 23:00 | -6910.61 | 6.8587 | 40.2116 | 53.895 | -2025.2999
2021-07-29 | -7319.21 | 6.8587 | 39.7908 | 53.895 | -2145.0487
2021-07-30 01:00 | -7522.14 | 6.8587 | 39.5239 | 53.895 | -2204.5216
2021-07-31 02:00 | -7615.17 | 6.8587 | 39.3621 | 53.895 | -2231.786
2021-08-01 03:00 | -7795.69 | 6.8587 | 39.1702 | 53.895 | -2284.6912
2021-08-02 04:00 | -8060.92 | 6.8587 | 38.9039 | 53.895 | -2362.4224
2021-08-03 05:00 | -8024.17 | 6.8587 | 38.8523 | 53.895 | -2351.6521
2021-08-04 06:00 | -7856.7 | 6.8587 | 38.9309 | 53.895 | -2302.5715
2021-08-05 07:00 | -8046.51 | 6.8587 | 38.8028 | 53.895 | -2358.1993
2021-08-06 08:00 | -7904.43 | 6.8587 | 38.8706 | 53.895 | -2316.5598
2021-08-07 09:00 | -8140.16 | 6.8587 | 38.7099 | 53.895 | -2385.6454
2021-08-08 10:00 | -7041.31 | 6.8587 | 39.4275 | 53.895 | -2063.6043
2021-08-09 11:00 | -6266.09 | 6.8587 | 40.0643 | 53.895 | -1836.4097
2021-08-10 12:00 | -6235.18 | 6.8587 | 40.2262 | 53.895 | -1827.3509
2021-08-11 13:00 | -6177.87 | 6.8587 | 40.3339 | 53.895 | -1810.555
2021-08-12 14:00 | -5881.07 | 6.8587 | 40.583 | 53.895 | -1723.5715
2021-08-13 15:00 | -5151.29 | 6.8587 | 41.1707 | 53.895 | -1509.6941
2021-08-14 16:00 | -4675.98 | 6.8587 | 41.633 | 53.895 | -1370.3945
2021-08-15 17:00 | -5295.75 | 6.8587 | 41.346 | 53.895 | -1552.0311
2021-08-16 18:00 | -5529.3 | 6.8587 | 41.202 | 53.895 | -1620.4779
2021-08-17 19:00 | -6560.86 | 6.8587 | 40.5057 | 53.895 | -1922.7983
2021-08-18 20:00 | -6936.45 | 6.8587 | 40.1572 | 53.895 | -2032.8728
2021-08-19 21:00 | -8077.49 | 6.8587 | 39.2941 | 53.895 | -2367.2786
2021-08-20 22:00 | -8586.29 | 6.8587 | 38.7544 | 53.895 | -2516.3932
2021-08-21 23:00 | -9544.44 | 6.8587 | 37.9271 | 53.895 | -2797.1992
2021-08-23 | -9851.3 | 6.8587 | 37.4979 | 53.895 | -2887.131
2021-08-24 01:00 | -9792.42 | 6.8587 | 37.372 | 53.895 | -2869.875
2021-08-25 02:00 | -9878.92 | 6.8587 | 37.2059 | 53.895 | -2895.2257
2021-08-26 03:00 | -10168.9 | 6.8587 | 36.9126 | 53.895 | -2980.2104
2021-08-27 04:00 | -9912.77 | 6.8587 | 36.9678 | 53.895 | -2905.1461
2021-08-28 05:00 | -9513.03 | 6.8587 | 37.1988 | 53.895 | -2787.9939
2021-08-29 06:00 | -9153.81 | 6.8587 | 37.4544 | 53.895 | -2682.7169
2021-08-30 07:00 | -9012.7 | 6.8587 | 37.5844 | 53.895 | -2641.3616
2021-08-31 08:00 | -8815.72 | 6.8587 | 37.7419 | 53.895 | -2583.6325
2021-09-01 09:00 | -9074.61 | 6.8587 | 37.6087 | 53.895 | -2659.5057
2021-09-02 10:00 | -8800.51 | 6.8587 | 37.7798 | 53.895 | -2579.1749
2021-09-03 11:00 | -8456.82 | 6.8587 | 38.0318 | 53.895 | -2478.4493
2021-09-04 12:00 | -7959.59 | 6.8587 | 38.4161 | 53.895 | -2332.7256
2021-09-05 13:00 | -7682.81 | 6.8587 | 38.6792 | 53.895 | -2251.6093
2021-09-06 14:00 | -7399.21 | 6.8587 | 38.9368 | 53.895 | -2168.4944
2021-09-07 15:00 | -6702.29 | 6.8587 | 39.4894 | 53.895 | -1964.2473
2021-09-08 16:00 | -5406.2 | 6.8587 | 40.5058 | 53.895 | -1584.4008
2021-09-09 17:00 | -4783.7 | 6.8587 | 41.1698 | 53.895 | -1401.9641
2021-09-10 18:00 | -4316.75 | 6.8587 | 41.7047 | 53.895 | -1265.1145
2021-09-11 19:00 | -4951.27 | 6.8587 | 41.4703 | 53.895 | -1451.074
2021-09-12 20:00 | -5236.16 | 6.8587 | 41.3471 | 53.895 | -1534.567
2021-09-13 21:00 | -6330.33 | 6.8587 | 40.65 | 53.895 | -1855.2366
2021-09-14 22:00 | -6754.56 | 6.8587 | 40.2831 | 53.895 | -1979.5661
2021-09-15 23:00 | -7808.49 | 6.8587 | 39.4887 | 53.895 | -2288.4425
2021-09-17 | -8360.32 | 6.8587 | 38.9518 | 53.895 | -2450.1679
2021-09-18 01:00 | -8548.09 | 6.8587 | 38.6756 | 53.895 | -2505.1979
2021-09-19 02:00 | -9132.3 | 6.8587 | 38.1693 | 53.895 | -2676.4129
2021-09-20 03:00 | -9229.4 | 6.8587 | 37.9686 | 53.895 | -2704.8701
2021-09-21 04:00 | -9102.39 | 6.8587 | 37.9416 | 53.895 | -2667.6472
2021-09-22 05:00 | -8760.23 | 6.8587 | 38.1153 | 53.895 | -2567.37
2021-09-23 06:00 | -8379.13 | 6.8587 | 38.3594 | 53.895 | -2455.6806
2021-09-24 07:00 | -8343.68 | 6.8587 | 38.4016 | 53.895 | -2445.2912
2021-09-25 08:00 | -8351.28 | 6.8587 | 38.4011 | 53.895 | -2447.5186
2021-09-26 09:00 | -8841.79 | 6.8587 | 38.0676 | 53.895 | -2591.2729
2021-09-27 10:00 | -8498.14 | 6.8587 | 38.2397 | 53.895 | -2490.559
2021-09-28 11:00 | -8210.23 | 6.8587 | 38.4417 | 53.895 | -2406.1809
2021-09-29 12:00 | -7975.18 | 6.8587 | 38.6353 | 53.895 | -2337.2945
2021-09-30 13:00 | -7708.36 | 6.8587 | 38.8524 | 53.895 | -2259.0973
2021-10-01 14:00 | -8034 | 6.8587 | 38.6771 | 53.895 | -2354.533
2021-10-02 15:00 | -8006.72 | 6.8587 | 38.6877 | 53.895 | -2346.538
2021-10-03 16:00 | -7353.78 | 6.8587 | 39.1236 | 53.895 | -2155.1802
2021-10-04 17:00 | -7709.53 | 6.8587 | 38.9483 | 53.895 | -2259.4402
2021-10-05 18:00 | -7687.4 | 6.8587 | 38.9412 | 53.895 | -2252.9545
2021-10-06 19:00 | -8340.22 | 6.8587 | 38.4729 | 53.895 | -2444.2772
2021-10-07 20:00 | -8853.46 | 6.8587 | 38.0374 | 53.895 | -2594.693
2021-10-08 21:00 | -9984.67 | 6.8587 | 37.1615 | 53.895 | -2926.2179
2021-10-09 22:00 | -10443 | 6.8587 | 36.6395 | 53.895 | -3060.5412
2021-10-10 23:00 | -11323.1 | 6.8587 | 35.8605 | 53.895 | -3318.473
2021-10-12 | -11961.2 | 6.8587 | 35.197 | 53.895 | -3505.4817
2021-10-13 01:00 | -12088.6 | 6.8587 | 34.8779 | 53.895 | -3542.8189
2021-10-14 02:00 | -12293.1 | 6.8587 | 34.5701 | 53.895 | -3602.752
2021-10-15 03:00 | -12373.4 | 6.8587 | 34.3733 | 53.895 | -3626.2856
2021-10-16 04:00 | -12479.1 | 6.8587 | 34.165 | 53.895 | -3657.2632
2021-10-17 05:00 | -12680.4 | 6.8587 | 33.907 | 53.895 | -3716.2584
2021-10-18 06:00 | -12692.7 | 6.8587 | 33.7678 | 53.895 | -3719.8632
2021-10-19 07:00 | -12491.8 | 6.8587 | 33.8001 | 53.895 | -3660.9852
2021-10-20 08:00 | -12228.5 | 6.8587 | 33.9168 | 53.895 | -3583.8196
2021-10-21 09:00 | -11811.6 | 6.8587 | 34.181 | 53.895 | -3461.6383
2021-10-22 10:00 | -10983.7 | 6.8587 | 34.7604 | 53.895 | -3219.0047
2021-10-23 11:00 | -8838.63 | 6.8587 | 36.3302 | 53.895 | -2590.3468
2021-10-24 12:00 | -8524.98 | 6.8587 | 36.8537 | 53.895 | -2498.425
2021-10-25 13:00 | -8092.92 | 6.8587 | 37.3494 | 53.895 | -2371.8007
2021-10-26 14:00 | -7671.92 | 6.8587 | 37.8048 | 53.895 | -2248.4178
2021-10-27 15:00 | -7841.11 | 6.8587 | 37.8642 | 53.895 | -2298.0025
2021-10-28 16:00 | -8515.16 | 6.8587 | 37.4941 | 53.895 | -2495.5471
2021-10-29 17:00 | -8052.75 | 6.8587 | 37.7745 | 53.895 | -2360.0281
2021-10-30 18:00 | -8836.39 | 6.8587 | 37.2918 | 53.895 | -2589.6903
2021-10-31 19:00 | -9700.19 | 6.8587 | 36.6451 | 53.895 | -2842.8451
2021-11-01 20:00 | -10036.1 | 6.8587 | 36.2719 | 53.895 | -2941.2906
2021-11-02 21:00 | -10059.5 | 6.8587 | 36.1525 | 53.895 | -2948.1484
2021-11-03 22:00 | -10681.6 | 6.8587 | 35.6725 | 53.895 | -3130.4679
2021-11-04 23:00 | -11065.1 | 6.8587 | 35.2661 | 53.895 | -3242.8607
2021-11-06 | -12148.4 | 6.8587 | 34.3814 | 53.895 | -3560.3446
2021-11-07 01:00 | -12467.4 | 6.8587 | 33.9395 | 53.895 | -3653.8343
2021-11-08 02:00 | -12567 | 6.8587 | 33.6826 | 53.895 | -3683.0241
2021-11-09 03:00 | -12726.9 | 6.8587 | 33.4289 | 53.895 | -3729.8862
2021-11-10 04:00 | -12834.8 | 6.8587 | 33.2266 | 53.895 | -3761.5086
2021-11-11 05:00 | -12800.2 | 6.8587 | 33.1241 | 53.895 | -3751.3683
2021-11-12 06:00 | -12836.6 | 6.8587 | 33.0181 | 53.895 | -3762.0361
2021-11-13 07:00 | -12604.6 | 6.8587 | 33.109 | 53.895 | -3694.0436
2021-11-14 08:00 | -12118.9 | 6.8587 | 33.4108 | 53.895 | -3551.699
2021-11-15 09:00 | -11949 | 6.8587 | 33.5488 | 53.895 | -3501.9062
2021-11-16 10:00 | -11513.7 | 6.8587 | 33.8584 | 53.895 | -3374.3324
2021-11-17 11:00 | -9956.9 | 6.8587 | 34.9644 | 53.895 | -2918.0793
2021-11-18 12:00 | -8957.78 | 6.8587 | 35.8615 | 53.895 | -2625.2662
2021-11-19 13:00 | -8219.65 | 6.8587 | 36.6015 | 53.895 | -2408.9416
2021-11-20 14:00 | -8221.01 | 6.8587 | 36.8123 | 53.895 | -2409.3402
2021-11-21 15:00 | -7549.2 | 6.8587 | 37.4131 | 53.895 | -2212.4521
2021-11-22 16:00 | -7489.9 | 6.8587 | 37.648 | 53.895 | -2195.073
2021-11-23 17:00 | -6318.47 | 6.8587 | 38.5852 | 53.895 | -1851.7608
2021-11-24 18:00 | -7045.11 | 6.8587 | 38.3255 | 53.895 | -2064.7179
2021-11-25 19:00 | -7416.33 | 6.8587 | 38.1438 | 53.895 | -2173.5118
2021-11-26 20:00 | -7869.76 | 6.8587 | 37.8596 | 53.895 | -2306.399
2021-11-27 21:00 | -8094.96 | 6.8587 | 37.7069 | 53.895 | -2372.3986
2021-11-28 22:00 | -8114.53 | 6.8587 | 37.7026 | 53.895 | -2378.134
2021-11-29 23:00 | -8169.59 | 6.8587 | 37.663 | 53.895 | -2394.2705
2021-12-01 | -9058.71 | 6.8587 | 37.0639 | 53.895 | -2654.8458
2021-12-02 01:00 | -9004.04 | 6.8587 | 37.0065 | 53.895 | -2638.8236
2021-12-03 02:00 | -9176.36 | 6.8587 | 36.8605 | 53.895 | -2689.3256
2021-12-04 03:00 | -9195.67 | 6.8587 | 36.8219 | 53.895 | -2694.9848
2021-12-05 04:00 | -9110.49 | 6.8587 | 36.8606 | 53.895 | -2670.0211
2021-12-06 05:00 | -9168.26 | 6.8587 | 36.807 | 53.895 | -2686.9518
2021-12-07 06:00 | -8822.35 | 6.8587 | 37.0456 | 53.895 | -2585.5756
2021-12-08 07:00 | -9122.14 | 6.8587 | 36.8841 | 53.895 | -2673.4353
2021-12-09 08:00 | -9031.48 | 6.8587 | 36.941 | 53.895 | -2646.8655
2021-12-10 09:00 | -9031.86 | 6.8587 | 36.954 | 53.895 | -2646.9769
2021-12-11 10:00 | -8281.78 | 6.8587 | 37.4804 | 53.895 | -2427.1501
2021-12-12 11:00 | -6552.19 | 6.8587 | 38.7599 | 53.895 | -1920.2573
2021-12-13 12:00 | -6488.59 | 6.8587 | 39.0664 | 53.895 | -1901.618
2021-12-14 13:00 | -6213.37 | 6.8587 | 39.411 | 53.895 | -1820.959
2021-12-15 14:00 | -6458.21 | 6.8587 | 39.373 | 53.895 | -1892.7145
2021-12-16 15:00 | -5986.66 | 6.8587 | 39.7766 | 53.895 | -1754.5169
2021-12-17 16:00 | -5379.37 | 6.8587 | 40.3209 | 53.895 | -1576.5377
2021-12-18 17:00 | -6258.71 | 6.8587 | 39.859 | 53.895 | -1834.2468
2021-12-19 18:00 | -6811.42 | 6.8587 | 39.4639 | 53.895 | -1996.2301
2021-12-20 19:00 | -7399.03 | 6.8587 | 39.0055 | 53.895 | -2168.4416
2021-12-21 20:00 | -7839.84 | 6.8587 | 38.6384 | 53.895 | -2297.6303
2021-12-22 21:00 | -8756.75 | 6.8587 | 37.9304 | 53.895 | -2566.3501
2021-12-23 22:00 | -9043.75 | 6.8587 | 37.5628 | 53.895 | -2650.4615
2021-12-24 23:00 | -9930.16 | 6.8587 | 36.8127 | 53.895 | -2910.2426
2021-12-26 | -10185.8 | 6.8587 | 36.4478 | 53.895 | -2985.1633
2021-12-27 01:00 | -10047.9 | 6.8587 | 36.3888 | 53.895 | -2944.7488
2021-12-28 02:00 | -10195 | 6.8587 | 36.2067 | 53.895 | -2987.8596
2021-12-29 03:00 | -10012.9 | 6.8587 | 36.2478 | 53.895 | -2934.4913
2021-12-30 04:00 | -9522.19 | 6.8587 | 36.5278 | 53.895 | -2790.6784
2021-12-31 05:00 | -9097.13 | 6.8587 | 36.847 | 53.895 | -2666.1056
2022-01-01 06:00 | -8537.91 | 6.8587 | 37.289 | 53.895 | -2502.2144
2022-01-02 07:00 | -8463.05 | 6.8587 | 37.4341 | 53.895 | -2480.2751
2022-01-03 08:00 | -8605.86 | 6.8587 | 37.4012 | 53.895 | -2522.1286
2022-01-04 09:00 | -8801.53 | 6.8587 | 37.2979 | 53.895 | -2579.4738
2022-01-05 10:00 | -8856.48 | 6.8587 | 37.258 | 53.895 | -2595.5781
2022-01-06 11:00 | -8352.09 | 6.8587 | 37.597 | 53.895 | -2447.756
2022-01-07 12:00 | -8438.82 | 6.8587 | 37.5898 | 53.895 | -2473.174
2022-01-08 13:00 | -8244.32 | 6.8587 | 37.7321 | 53.895 | -2416.1717
2022-01-09 14:00 | -8237.45 | 6.8587 | 37.7648 | 53.895 | -2414.1583
2022-01-10 15:00 | -8226.06 | 6.8587 | 37.792 | 53.895 | -2410.8202
2022-01-11 16:00 | -7605.19 | 6.8587 | 38.2252 | 53.895 | -2228.8612
2022-01-12 17:00 | -7565.92 | 6.8587 | 38.3236 | 53.895 | -2217.3523
2022-01-13 18:00 | -7550.44 | 6.8587 | 38.3779 | 53.895 | -2212.8155
2022-01-14 19:00 | -7794.57 | 6.8587 | 38.2347 | 53.895 | -2284.363
2022-01-15 20:00 | -8056.21 | 6.8587 | 38.0523 | 53.895 | -2361.0421
2022-01-16 21:00 | -8803.48 | 6.8587 | 37.5248 | 53.895 | -2580.0453
2022-01-17 22:00 | -9094.08 | 6.8587 | 37.2282 | 53.895 | -2665.2118
2022-01-18 23:00 | -9671.74 | 6.8587 | 36.7462 | 53.895 | -2834.5072
2022-01-20 | -9925.12 | 6.8587 | 36.4586 | 53.895 | -2908.7655
2022-01-21 01:00 | -9605.32 | 6.8587 | 36.5766 | 53.895 | -2815.0414
2022-01-22 02:00 | -9873.72 | 6.8587 | 36.3694 | 53.895 | -2893.7017
2022-01-23 03:00 | -10134.4 | 6.8587 | 36.1385 | 53.895 | -2970.0995
2022-01-24 04:00 | -9960.17 | 6.8587 | 36.1752 | 53.895 | -2919.0377
2022-01-25 05:00 | -9631.92 | 6.8587 | 36.3729 | 53.895 | -2822.8371
2022-01-26 06:00 | -9197.96 | 6.8587 | 36.685 | 53.895 | -2695.656
2022-01-27 07:00 | -9268.87 | 6.8587 | 36.677 | 53.895 | -2716.4376
2022-01-28 08:00 | -8904.84 | 6.8587 | 36.9333 | 53.895 | -2609.751
2022-01-29 09:00 | -8553.25 | 6.8587 | 37.2305 | 53.895 | -2506.7101
2022-01-30 10:00 | -7683.15 | 6.8587 | 37.9069 | 53.895 | -2251.709
2022-01-31 11:00 | -7969.15 | 6.8587 | 37.8556 | 53.895 | -2335.5273
2022-02-01 12:00 | -7186.2 | 6.8587 | 38.4374 | 53.895 | -2106.0673
2022-02-02 13:00 | -7117.54 | 6.8587 | 38.6104 | 53.895 | -2085.9451
2022-02-03 14:00 | -7874.46 | 6.8587 | 38.1862 | 53.895 | -2307.7764
2022-02-04 15:00 | -7824.02 | 6.8587 | 38.1871 | 53.895 | -2292.9939
2022-02-05 16:00 | -7485.72 | 6.8587 | 38.4065 | 53.895 | -2193.848
2022-02-06 17:00 | -7490.87 | 6.8587 | 38.4579 | 53.895 | -2195.3573
2022-02-07 18:00 | -7487.17 | 6.8587 | 38.4774 | 53.895 | -2194.2729
2022-02-08 19:00 | -7914.07 | 6.8587 | 38.1948 | 53.895 | -2319.385
2022-02-09 20:00 | -8269.06 | 6.8587 | 37.9225 | 53.895 | -2423.4223
2022-02-10 21:00 | -9428.11 | 6.8587 | 37.0772 | 53.895 | -2763.1063
2022-02-11 22:00 | -10148.4 | 6.8587 | 36.405 | 53.895 | -2974.2024
2022-02-12 23:00 | -11387.5 | 6.8587 | 35.3668 | 53.895 | -3337.3468
2022-02-14 | -12030.6 | 6.8587 | 34.6511 | 53.895 | -3525.8208
2022-02-15 01:00 | -12402.7 | 6.8587 | 34.137 | 53.895 | -3634.8726
2022-02-16 02:00 | -12836.9 | 6.8587 | 33.6238 | 53.895 | -3762.124
2022-02-17 03:00 | -13241.2 | 6.8587 | 33.1371 | 53.895 | -3880.6127
2022-02-18 04:00 | -13377.3 | 6.8587 | 32.8316 | 53.895 | -3920.4996
2022-02-19 05:00 | -13328.7 | 6.8587 | 32.6959 | 53.895 | -3906.2564
2022-02-20 06:00 | -13213.1 | 6.8587 | 32.6432 | 53.895 | -3872.3774
2022-02-21 07:00 | -13167.1 | 6.8587 | 32.5712 | 53.895 | -3858.8961
2022-02-22 08:00 | -13195.1 | 6.8587 | 32.4566 | 53.895 | -3867.1021
2022-02-23 09:00 | -13304.2 | 6.8587 | 32.2952 | 53.895 | -3899.0761
2022-02-24 10:00 | -13246 | 6.8587 | 32.24 | 53.895 | -3882.0194
2022-02-25 11:00 | -12772.1 | 6.8587 | 32.4968 | 53.895 | -3743.133
2022-02-26 12:00 | -12478.8 | 6.8587 | 32.6898 | 53.895 | -3657.1753
2022-02-27 13:00 | -12413.8 | 6.8587 | 32.7353 | 53.895 | -3638.1256
2022-02-28 14:00 | -12299.9 | 6.8587 | 32.7999 | 53.895 | -3604.7449
2022-03-01 15:00 | -12101.2 | 6.8587 | 32.9299 | 53.895 | -3546.5116
2022-03-02 16:00 | -11726.5 | 6.8587 | 33.1952 | 53.895 | -3436.6979
2022-03-03 17:00 | -11237.3 | 6.8587 | 33.562 | 53.895 | -3293.3275
2022-03-04 18:00 | -11484.5 | 6.8587 | 33.45 | 53.895 | -3365.7747
2022-03-05 19:00 | -11908.9 | 6.8587 | 33.1463 | 53.895 | -3490.1541
2022-03-06 20:00 | -12147.8 | 6.8587 | 32.9153 | 53.895 | -3560.1687
2022-03-07 21:00 | -12601.7 | 6.8587 | 32.5427 | 53.895 | -3693.1937
2022-03-08 22:00 | -12970.5 | 6.8587 | 32.193 | 53.895 | -3801.2783
2022-03-09 23:00 | -13307.2 | 6.8587 | 31.8444 | 53.895 | -3899.9553
2022-03-11 | -13634.3 | 6.8587 | 31.5029 | 53.895 | -3995.8189
2022-03-12 01:00 | -13716.9 | 6.8587 | 31.328 | 53.895 | -4020.0266
2022-03-13 02:00 | -13730.8 | 6.8587 | 31.2266 | 53.895 | -4024.1002
2022-03-14 03:00 | -13683.1 | 6.8587 | 31.1918 | 53.895 | -4010.1208
2022-03-15 04:00 | -13592.8 | 6.8587 | 31.1999 | 53.895 | -3983.6564
2022-03-16 05:00 | -13510.8 | 6.8587 | 31.2125 | 53.895 | -3959.6246
2022-03-17 06:00 | -13350.6 | 6.8587 | 31.2903 | 53.895 | -3912.6746
2022-03-18 07:00 | -13268.6 | 6.8587 | 31.3336 | 53.895 | -3888.6428
2022-03-19 08:00 | -13183.4 | 6.8587 | 31.3796 | 53.895 | -3863.6731
2022-03-20 09:00 | -13161.6 | 6.8587 | 31.3865 | 53.895 | -3857.2842
2022-03-21 10:00 | -13014.7 | 6.8587 | 31.473 | 53.895 | -3814.2321
2022-03-22 11:00 | -12583.2 | 6.8587 | 31.769 | 53.895 | -3687.7719
2022-03-23 12:00 | -11781.8 | 6.8587 | 32.364 | 53.895 | -3452.9047
2022-03-24 13:00 | -10705.2 | 6.8587 | 33.2218 | 53.895 | -3137.3844
2022-03-25 14:00 | -10684.6 | 6.8587 | 33.4296 | 53.895 | -3131.3472
2022-03-26 15:00 | -10256.1 | 6.8587 | 33.8346 | 53.895 | -3005.7662
2022-03-27 16:00 | -8888.91 | 6.8587 | 34.8959 | 53.895 | -2605.0824
2022-03-28 17:00 | -10079.5 | 6.8587 | 34.3324 | 53.895 | -2954.0099
2022-03-29 18:00 | -10834.5 | 6.8587 | 33.8114 | 53.895 | -3175.2785
2022-03-30 19:00 | -11551.7 | 6.8587 | 33.2229 | 53.895 | -3385.4691
2022-03-31 20:00 | -12035.9 | 6.8587 | 32.78 | 53.895 | -3527.3741
2022-04-01 21:00 | -12582 | 6.8587 | 32.2965 | 53.895 | -3687.4202
2022-04-02 22:00 | -13163.9 | 6.8587 | 31.7413 | 53.895 | -3857.9583
2022-04-03 23:00 | -13700.7 | 6.8587 | 31.2148 | 53.895 | -4015.2788
2022-04-05 | -14128.8 | 6.8587 | 30.755 | 53.895 | -4140.7425
2022-04-06 01:00 | -14669.4 | 6.8587 | 30.2153 | 53.895 | -4299.1768
2022-04-07 02:00 | -15252.4 | 6.8587 | 29.6278 | 53.895 | -4470.0372
2022-04-08 03:00 | 0 | 0 | 39.9873 | 53.895 | 0
2022-04-09 04:00 | -14004.7 | 6.8587 | 32.1148 | 53.895 | -4104.3724
2022-04-10 05:00 | -14986.6 | 6.8587 | 30.6168 | 53.895 | -4392.1389
2022-04-11 06:00 | -15075.1 | 6.8587 | 29.9315 | 53.895 | -4418.0757
2022-04-12 07:00 | 0 | 0 | 40.2543 | 53.895 | 0
2022-04-13 08:00 | -12011.4 | 6.8587 | 33.7735 | 53.895 | -3520.1939
2022-04-14 09:00 | -14231.8 | 6.8587 | 31.4766 | 53.895 | -4170.9289
2022-04-15 10:00 | -14940.3 | 6.8587 | 30.365 | 53.895 | -4378.5697
2022-04-16 11:00 | -12163.4 | 6.8587 | 32.1067 | 53.895 | -3564.7407
2022-04-17 12:00 | -10643.1 | 6.8587 | 33.4521 | 53.895 | -3119.1847
2022-04-18 13:00 | -9459.94 | 6.8587 | 34.3091 | 53.895 | -2772.4347
2022-04-19 14:00 | -9262.25 | 6.8587 | 34.7175 | 53.895 | -2714.4975
2022-04-20 15:00 | -9152.84 | 6.8587 | 34.8619 | 53.895 | -2682.4326
2022-04-21 16:00 | -9384.06 | 6.8587 | 34.8886 | 53.895 | -2750.1965
2022-04-22 17:00 | -9621.98 | 6.8587 | 34.8268 | 53.895 | -2819.924
2022-04-23 18:00 | -11106.4 | 6.8587 | 33.8583 | 53.895 | -3254.9645
2022-04-24 19:00 | -11341.3 | 6.8587 | 33.4019 | 53.895 | -3323.8069
2022-04-25 20:00 | -12072.1 | 6.8587 | 32.7896 | 53.895 | -3537.9833
2022-04-26 21:00 | -12338.8 | 6.8587 | 32.4898 | 53.895 | -3616.1453
2022-04-27 22:00 | -12598.1 | 6.8587 | 32.2263 | 53.895 | -3692.1386
2022-04-28 23:00 | -12897 | 6.8587 | 31.9212 | 53.895 | -3779.7376
2022-04-30 | -13768.5 | 6.8587 | 31.2228 | 53.895 | -4035.149
2022-05-01 01:00 | -14529.8 | 6.8587 | 30.5058 | 53.895 | -4258.264
2022-05-02 02:00 | -14720.8 | 6.8587 | 30.16 | 53.895 | -4314.2406
2022-05-03 03:00 | 0 | 0 | 40.1113 | 53.895 | 0
2022-05-04 04:00 | -12585.7 | 6.8587 | 33.138 | 53.895 | -3688.5046
2022-05-05 05:00 | -14483.1 | 6.8587 | 31.2188 | 53.895 | -4244.5776
2022-05-06 06:00 | -16330.6 | 6.8587 | 29.3051 | 53.895 | -4786.0264
2022-05-07 07:00 | 0 | 0 | 40.1954 | 53.895 | 0
2022-05-08 08:00 | -12094.2 | 6.8587 | 33.7005 | 53.895 | -3544.4601
2022-05-09 09:00 | -14318 | 6.8587 | 31.4265 | 53.895 | -4196.1916
2022-05-10 10:00 | -14244 | 6.8587 | 30.8251 | 53.895 | -4174.5043
2022-05-11 11:00 | -12433.1 | 6.8587 | 31.9756 | 53.895 | -3643.7819
2022-05-12 12:00 | -10812.3 | 6.8587 | 33.3322 | 53.895 | -3168.7723
2022-05-13 13:00 | -9789.96 | 6.8587 | 34.0346 | 53.895 | -2869.1541
2022-05-14 14:00 | -9355.42 | 6.8587 | 34.5694 | 53.895 | -2741.8029
2022-05-15 15:00 | -9425.71 | 6.8587 | 34.5932 | 53.895 | -2762.4029
2022-05-16 16:00 | -10412.5 | 6.8587 | 34.0469 | 53.895 | -3051.6025
2022-05-17 17:00 | -9554.71 | 6.8587 | 34.6223 | 53.895 | -2800.2091
2022-05-18 18:00 | -10412.9 | 6.8587 | 34.1765 | 53.895 | -3051.7197
2022-05-19 19:00 | -10604.8 | 6.8587 | 33.8767 | 53.895 | -3107.9601
2022-05-20 20:00 | -11098.6 | 6.8587 | 33.4871 | 53.895 | -3252.6786
2022-05-21 21:00 | -11141.7 | 6.8587 | 33.4091 | 53.895 | -3265.3099
2022-05-22 22:00 | -11201.3 | 6.8587 | 33.3743 | 53.895 | -3282.777
2022-05-23 23:00 | -11077.1 | 6.8587 | 33.4452 | 53.895 | -3246.3775
2022-05-25 | -11982.1 | 6.8587 | 32.8343 | 53.895 | -3511.6069
2022-05-26 01:00 | -12238.9 | 6.8587 | 32.5474 | 53.895 | -3586.8675
2022-05-27 02:00 | -12338.9 | 6.8587 | 32.392 | 53.895 | -3616.1746
2022-05-28 03:00 | -12230.8 | 6.8587 | 32.2963 | 53.895 | -3584.4936
2022-05-29 04:00 | -12043.5 | 6.8587 | 32.3974 | 53.895 | -3529.6014
2022-05-30 05:00 | -11767.9 | 6.8587 | 32.582 | 53.895 | -3448.831
2022-05-31 06:00 | -11138.1 | 6.8587 | 33.0708 | 53.895 | -3264.2549
2022-06-01 07:00 | -11140.4 | 6.8587 | 33.0655 | 53.895 | -3264.9289
2022-06-02 08:00 | -10845.1 | 6.8587 | 33.3225 | 53.895 | -3178.3851
2022-06-03 09:00 | -10931.8 | 6.8587 | 33.3501 | 53.895 | -3203.7943
2022-06-04 10:00 | -10271.4 | 6.8587 | 33.8633 | 53.895 | -3010.2502
2022-06-05 11:00 | -9107.11 | 6.8587 | 34.7806 | 53.895 | -2669.0305
2022-06-06 12:00 | -8386.04 | 6.8587 | 35.487 | 53.895 | -2457.7057
2022-06-07 13:00 | -7661.32 | 6.8587 | 36.1965 | 53.895 | -2245.3113
2022-06-08 14:00 | -7272.83 | 6.8587 | 36.6828 | 53.895 | -2131.4561
2022-06-09 15:00 | -7616.8 | 6.8587 | 36.6524 | 53.895 | -2232.2637
2022-06-10 16:00 | -6950.52 | 6.8587 | 37.2194 | 53.895 | -2036.9963
2022-06-11 17:00 | -7121.21 | 6.8587 | 37.2688 | 53.895 | -2087.0206
2022-06-12 18:00 | -7236.94 | 6.8587 | 37.2971 | 53.895 | -2120.9377
2022-06-13 19:00 | -7906.48 | 6.8587 | 36.9056 | 53.895 | -2317.1606
2022-06-14 20:00 | -8274.35 | 6.8587 | 36.6422 | 53.895 | -2424.9726
2022-06-15 21:00 | -9283.3 | 6.8587 | 35.9403 | 53.895 | -2720.6667
2022-06-16 22:00 | -9558.49 | 6.8587 | 35.6364 | 53.895 | -2801.3169
2022-06-17 23:00 | -10458.3 | 6.8587 | 34.9256 | 53.895 | -3065.0252
2022-06-19 | -10997.7 | 6.8587 | 34.3974 | 53.895 | -3223.1077
2022-06-20 01:00 | -11169.8 | 6.8587 | 34.1212 | 53.895 | -3273.5452
2022-06-21 02:00 | -11318.3 | 6.8587 | 33.9019 | 53.895 | -3317.0663
2022-06-22 03:00 | -11312.5 | 6.8587 | 33.7823 | 53.895 | -3315.3665
2022-06-23 04:00 | -11399 | 6.8587 | 33.6438 | 53.895 | -3340.7171
2022-06-24 05:00 | -11279.6 | 6.8587 | 33.662 | 53.895 | -3305.7244
2022-06-25 06:00 | -10988.5 | 6.8587 | 33.8373 | 53.895 | -3220.4115
2022-06-26 07:00 | -11145.5 | 6.8587 | 33.7022 | 53.895 | -3266.4236
2022-06-27 08:00 | -11154.2 | 6.8587 | 33.6659 | 53.895 | -3268.9733
2022-06-28 09:00 | -11570.4 | 6.8587 | 33.3611 | 53.895 | -3390.9495
2022-06-29 10:00 | -10276.7 | 6.8587 | 34.1908 | 53.895 | -3011.8035
2022-06-30 11:00 | -9695.97 | 6.8587 | 34.7144 | 53.895 | -2841.6083
2022-07-01 12:00 | -8934.73 | 6.8587 | 35.3656 | 53.895 | -2618.5109
2022-07-02 13:00 | -7980.58 | 6.8587 | 36.171 | 53.895 | -2338.8771
2022-07-03 14:00 | -7608.51 | 6.8587 | 36.6349 | 53.895 | -2229.8342
2022-07-04 15:00 | -7348.9 | 6.8587 | 37.0029 | 53.895 | -2153.75
2022-07-05 16:00 | -6935.05 | 6.8587 | 37.4308 | 53.895 | -2032.4625
2022-07-06 17:00 | -7455.76 | 6.8587 | 37.2299 | 53.895 | -2185.0676
2022-07-07 18:00 | -8798.88 | 6.8587 | 36.352 | 53.895 | -2578.6972
2022-07-08 19:00 | -9816.79 | 6.8587 | 35.5286 | 53.895 | -2877.0171
2022-07-09 20:00 | -9911.33 | 6.8587 | 35.2967 | 53.895 | -2904.7241
2022-07-10 21:00 | -11589.4 | 6.8587 | 34.0652 | 53.895 | -3396.5179
2022-07-11 22:00 | -12097.8 | 6.8587 | 33.4408 | 53.895 | -3545.5152
2022-07-12 23:00 | -12708.5 | 6.8587 | 32.7829 | 53.895 | -3724.4937
2022-07-14 | -13182.5 | 6.8587 | 32.2503 | 53.895 | -3863.4094
2022-07-15 01:00 | -13375.3 | 6.8587 | 31.9144 | 53.895 | -3919.9135
2022-07-16 02:00 | -13539.2 | 6.8587 | 31.6197 | 53.895 | -3967.9478
2022-07-17 03:00 | -13722.1 | 6.8587 | 31.3284 | 53.895 | -4021.5505
2022-07-18 04:00 | -13770.3 | 6.8587 | 31.146 | 53.895 | -4035.6766
2022-07-19 05:00 | -13747.6 | 6.8587 | 31.0401 | 53.895 | -4029.0238
2022-07-20 06:00 | -13746.4 | 6.8587 | 30.9514 | 53.895 | -4028.6722
2022-07-21 07:00 | -13707.1 | 6.8587 | 30.8853 | 53.895 | -4017.1545
2022-07-22 08:00 | -13544.9 | 6.8587 | 30.928 | 53.895 | -3969.6183
2022-07-23 09:00 | -13242.2 | 6.8587 | 31.1139 | 53.895 | -3880.9057
2022-07-24 10:00 | -12683.9 | 6.8587 | 31.5042 | 53.895 | -3717.2841
2022-07-25 11:00 | -11658.9 | 6.8587 | 32.2633 | 53.895 | -3416.8863
2022-07-26 12:00 | -10397.6 | 6.8587 | 33.2737 | 53.895 | -3047.2358
2022-07-27 13:00 | -10325.5 | 6.8587 | 33.5413 | 53.895 | -3026.1053
2022-07-28 14:00 | -9454.53 | 6.8587 | 34.263 | 53.895 | -2770.8492
2022-07-29 15:00 | -8905.92 | 6.8587 | 34.8228 | 53.895 | -2610.0675
2022-07-30 16:00 | -8695.78 | 6.8587 | 35.1538 | 53.895 | -2548.4815
2022-07-31 17:00 | -9978.74 | 6.8587 | 34.4071 | 53.895 | -2924.48
2022-08-01 18:00 | -10704.2 | 6.8587 | 33.8342 | 53.895 | -3137.0913
2022-08-02 19:00 | -11567.1 | 6.8587 | 33.1425 | 53.895 | -3389.9824
2022-08-03 20:00 | -12140.9 | 6.8587 | 32.5983 | 53.895 | -3558.1466
2022-08-04 21:00 | -12713.1 | 6.8587 | 32.0524 | 53.895 | -3725.8418
2022-08-05 22:00 | -13021.2 | 6.8587 | 31.6679 | 53.895 | -3816.137
2022-08-06 23:00 | -13408.3 | 6.8587 | 31.2619 | 53.895 | -3929.5848
2022-08-08 | -13928.1 | 6.8587 | 30.7562 | 53.895 | -4081.9232
2022-08-09 01:00 | -14086.1 | 6.8587 | 30.4843 | 53.895 | -4128.2284
2022-08-10 02:00 | -14255.5 | 6.8587 | 30.2308 | 53.895 | -4177.8746
2022-08-11 03:00 | -14320.3 | 6.8587 | 30.0414 | 53.895 | -4196.8656
2022-08-12 04:00 | 0 | 0 | 39.839 | 53.895 | 0
2022-08-13 05:00 | -12539.5 | 6.8587 | 32.8853 | 53.895 | -3674.9647
2022-08-14 06:00 | -14721 | 6.8587 | 30.789 | 53.895 | -4314.2992
2022-08-15 07:00 | -15716.6 | 6.8587 | 29.4151 | 53.895 | -4606.0808
2022-08-16 08:00 | 0 | 0 | 40.0405 | 53.895 | 0
2022-08-17 09:00 | -11950.6 | 6.8587 | 33.6242 | 53.895 | -3502.3751
2022-08-18 10:00 | -14621.8 | 6.8587 | 31.0346 | 53.895 | -4285.2266
2022-08-19 11:00 | -11058.5 | 6.8587 | 32.7866 | 53.895 | -3240.9264
2022-08-20 12:00 | -9161.05 | 6.8587 | 34.4185 | 53.895 | -2684.8387
2022-08-21 13:00 | -7913.32 | 6.8587 | 35.7435 | 53.895 | -2319.1652
2022-08-22 14:00 | -7506.06 | 6.8587 | 36.0981 | 53.895 | -2199.809
2022-08-23 15:00 | -7375.73 | 6.8587 | 36.4323 | 53.895 | -2161.6131
2022-08-24 16:00 | -7070.07 | 6.8587 | 36.7478 | 53.895 | -2072.033
2022-08-25 17:00 | -8806.79 | 6.8587 | 35.74 | 53.895 | -2581.0154
2022-08-26 18:00 | -9347.84 | 6.8587 | 35.3049 | 53.895 | -2739.5815
2022-08-27 19:00 | -9838.77 | 6.8587 | 34.9122 | 53.895 | -2883.4589
2022-08-28 20:00 | -10936.1 | 6.8587 | 33.9547 | 53.895 | -3205.0545
2022-08-29 21:00 | -11921.6 | 6.8587 | 33.1067 | 53.895 | -3493.8761
2022-08-30 22:00 | -12100.1 | 6.8587 | 32.7857 | 53.895 | -3546.1893
2022-08-31 23:00 | -12640.4 | 6.8587 | 32.2883 | 53.895 | -3704.5356
2022-09-02 | -13159 | 6.8587 | 31.7734 | 53.895 | -3856.5222
2022-09-03 01:00 | -13538.4 | 6.8587 | 31.3225 | 53.895 | -3967.7134
2022-09-04 02:00 | -13637.5 | 6.8587 | 31.0832 | 53.895 | -3996.7567
2022-09-05 03:00 | -13527.8 | 6.8587 | 31.0343 | 53.895 | -3964.6068
2022-09-06 04:00 | -13348.8 | 6.8587 | 30.9914 | 53.895 | -3912.1471
2022-09-07 05:00 | -13276.7 | 6.8587 | 30.9895 | 53.895 | -3891.0167
2022-09-08 06:00 | -13383.6 | 6.8587 | 30.8861 | 53.895 | -3922.346
2022-09-09 07:00 | -13355.5 | 6.8587 | 30.8705 | 53.895 | -3914.1107
2022-09-10 08:00 | -13225.1 | 6.8587 | 30.8639 | 53.895 | -3875.8942
2022-09-11 09:00 | -12997.5 | 6.8587 | 31.0136 | 53.895 | -3809.1912
2022-09-12 10:00 | -11924.6 | 6.8587 | 31.7794 | 53.895 | -3494.7553
2022-09-13 11:00 | -11021.8 | 6.8587 | 32.5304 | 53.895 | -3230.1707
2022-09-14 12:00 | -10503.3 | 6.8587 | 33.0569 | 53.895 | -3078.2134
2022-09-15 13:00 | -9860.19 | 6.8587 | 33.6469 | 53.895 | -2889.7364
2022-09-16 14:00 | -9204.26 | 6.8587 | 34.2655 | 53.895 | -2697.5023
2022-09-17 15:00 | -9868.8 | 6.8587 | 33.9951 | 53.895 | -2892.2598
2022-09-18 16:00 | -9405.47 | 6.8587 | 34.3334 | 53.895 | -2756.4712
2022-09-19 17:00 | -9131.35 | 6.8587 | 34.6096 | 53.895 | -2676.1345
2022-09-20 18:00 | -9290.84 | 6.8587 | 34.6128 | 53.895 | -2722.8764
2022-09-21 19:00 | -9555.98 | 6.8587 | 34.4859 | 53.895 | -2800.5813
2022-09-22 20:00 | -9600.42 | 6.8587 | 34.4703 | 53.895 | -2813.6054
2022-09-23 21:00 | -10367.6 | 6.8587 | 33.9904 | 53.895 | -3038.4436
2022-09-24 22:00 | -10651.5 | 6.8587 | 33.7376 | 53.895 | -3121.6465
2022-09-25 23:00 | -11418.3 | 6.8587 | 33.1492 | 53.895 | -3346.3734
2022-09-27 | -11774.1 | 6.8587 | 32.7848 | 53.895 | -3450.6481
2022-09-28 01:00 | -11664.3 | 6.8587 | 32.7522 | 53.895 | -3418.4689
2022-09-29 02:00 | -11685.2 | 6.8587 | 32.6834 | 53.895 | -3424.5941
2022-09-30 03:00 | -11755.1 | 6.8587 | 32.6056 | 53.895 | -3445.0797
2022-10-01 04:00 | -11895.7 | 6.8587 | 32.4302 | 53.895 | -3486.2855
2022-10-02 05:00 | -11923.7 | 6.8587 | 32.3641 | 53.895 | -3494.4915
2022-10-03 06:00 | -11976.9 | 6.8587 | 32.302 | 53.895 | -3510.0829
2022-10-04 07:00 | -11565.3 | 6.8587 | 32.5634 | 53.895 | -3389.4548
2022-10-05 08:00 | -10882.4 | 6.8587 | 33.0289 | 53.895 | -3189.3166
2022-10-06 09:00 | -11403.4 | 6.8587 | 32.7694 | 53.895 | -3342.0066
2022-10-07 10:00 | -11007.2 | 6.8587 | 33.0295 | 53.895 | -3225.8919
2022-10-08 11:00 | -10489.6 | 6.8587 | 33.4262 | 53.895 | -3074.1983
2022-10-09 12:00 | -9589.01 | 6.8587 | 34.1456 | 53.895 | -2810.2614
2022-10-10 13:00 | -9111.39 | 6.8587 | 34.6258 | 53.895 | -2670.2848
2022-10-11 14:00 | -8865.2 | 6.8587 | 34.9223 | 53.895 | -2598.1336
2022-10-12 15:00 | -8655.43 | 6.8587 | 35.1844 | 53.895 | -2536.6561
2022-10-13 16:00 | -8586.47 | 6.8587 | 35.336 | 53.895 | -2516.446
2022-10-14 17:00 | -7213.53 | 6.8587 | 36.3692 | 53.895 | -2114.077
2022-10-15 18:00 | -7584.29 | 6.8587 | 36.3516 | 53.895 | -2222.736
2022-10-16 19:00 | -7835.62 | 6.8587 | 36.2834 | 53.895 | -2296.3935
2022-10-17 20:00 | -8139.07 | 6.8587 | 36.1156 | 53.895 | -2385.326
2022-10-18 21:00 | -8197.46 | 6.8587 | 36.1137 | 53.895 | -2402.4384
2022-10-19 22:00 | -8144.8 | 6.8587 | 36.2028 | 53.895 | -2387.0053
2022-10-20 23:00 | -8286.89 | 6.8587 | 36.1503 | 53.895 | -2428.6477
2022-10-22 | -9489.27 | 6.8587 | 35.3511 | 53.895 | -2781.0305
2022-10-23 01:00 | -9698.95 | 6.8587 | 35.0891 | 53.895 | -2842.4817
2022-10-24 02:00 | -9779.82 | 6.8587 | 34.9643 | 53.895 | -2866.1823
2022-10-25 03:00 | -9644.36 | 6.8587 | 35.017 | 53.895 | -2826.4829
2022-10-26 04:00 | -9467.7 | 6.8587 | 35.134 | 53.895 | -2774.709
2022-10-27 05:00 | -9380.37 | 6.8587 | 35.1963 | 53.895 | -2749.1151
2022-10-28 06:00 | -9205.79 | 6.8587 | 35.3452 | 53.895 | -2697.9507
2022-10-29 07:00 | -8515.33 | 6.8587 | 35.8564 | 53.895 | -2495.5969
2022-10-30 08:00 | -8018.01 | 6.8587 | 36.3186 | 53.895 | -2349.8468
2022-10-31 09:00 | -8632.09 | 6.8587 | 36.0369 | 53.895 | -2529.8159
2022-11-01 10:00 | -8602.45 | 6.8587 | 36.062 | 53.895 | -2521.1292
2022-11-02 11:00 | -8027.68 | 6.8587 | 36.4753 | 53.895 | -2352.6808
2022-11-03 12:00 | -7794.7 | 6.8587 | 36.7441 | 53.895 | -2284.4011
2022-11-04 13:00 | -7429.42 | 6.8587 | 37.084 | 53.895 | -2177.3481
2022-11-05 14:00 | -7549.42 | 6.8587 | 37.0919 | 53.895 | -2212.5166
2022-11-06 15:00 | -7291.54 | 6.8587 | 37.3288 | 53.895 | -2136.9394
2022-11-07 16:00 | -7385.7 | 6.8587 | 37.3468 | 53.895 | -2164.535
2022-11-08 17:00 | -5921.91 | 6.8587 | 38.3954 | 53.895 | -1735.5405
2022-11-09 18:00 | -6339.07 | 6.8587 | 38.3299 | 53.895 | -1857.798
2022-11-10 19:00 | -7015.56 | 6.8587 | 37.9469 | 53.895 | -2056.0577
2022-11-11 20:00 | -7347.12 | 6.8587 | 37.6921 | 53.895 | -2153.2283
2022-11-12 21:00 | -7895.67 | 6.8587 | 37.2999 | 53.895 | -2313.9925
2022-11-13 22:00 | -8524.86 | 6.8587 | 36.8244 | 53.895 | -2498.3898
2022-11-14 23:00 | -8840.11 | 6.8587 | 36.4922 | 53.895 | -2590.7805
2022-11-16 | -10038.8 | 6.8587 | 35.5776 | 53.895 | -2942.0819
2022-11-17 01:00 | -10458.3 | 6.8587 | 35.0945 | 53.895 | -3065.0252
2022-11-18 02:00 | -10414.7 | 6.8587 | 34.9615 | 53.895 | -3052.2473
2022-11-19 03:00 | -10505.9 | 6.8587 | 34.8006 | 53.895 | -3078.9754
2022-11-20 04:00 | -10294.9 | 6.8587 | 34.8504 | 53.895 | -3017.1374
2022-11-21 05:00 | -10013 | 6.8587 | 34.9881 | 53.895 | -2934.5206
2022-11-22 06:00 | -9892.76 | 6.8587 | 35.0744 | 53.895 | -2899.2818
2022-11-23 07:00 | -9982.86 | 6.8587 | 35.0106 | 53.895 | -2925.6875
2022-11-24 08:00 | -10057.1 | 6.8587 | 34.9162 | 53.895 | -2947.4451
2022-11-25 09:00 | -10528.4 | 6.8587 | 34.5688 | 53.895 | -3085.5695
2022-11-26 10:00 | -9989.07 | 6.8587 | 34.8688 | 53.895 | -2927.5074
2022-11-27 11:00 | -9914.09 | 6.8587 | 34.9326 | 53.895 | -2905.533
2022-11-28 12:00 | -9630.56 | 6.8587 | 35.1377 | 53.895 | -2822.4385
2022-11-29 13:00 | -9689.39 | 6.8587 | 35.1228 | 53.895 | -2839.6799
2022-11-30 14:00 | -9906.77 | 6.8587 | 34.9733 | 53.895 | -2903.3877
2022-12-01 15:00 | -9873.34 | 6.8587 | 34.972 | 53.895 | -2893.5903
2022-12-02 16:00 | -9268.03 | 6.8587 | 35.3701 | 53.895 | -2716.1915
2022-12-03 17:00 | -9449.77 | 6.8587 | 35.294 | 53.895 | -2769.4542
2022-12-04 18:00 | -9557.54 | 6.8587 | 35.209 | 53.895 | -2801.0385
2022-12-05 19:00 | -10224.3 | 6.8587 | 34.7231 | 53.895 | -2996.4465
2022-12-06 20:00 | -10459.9 | 6.8587 | 34.4703 | 53.895 | -3065.4941
2022-12-07 21:00 | -11204.6 | 6.8587 | 33.8848 | 53.895 | -3283.7441
2022-12-08 22:00 | -11486.1 | 6.8587 | 33.5421 | 53.895 | -3366.2436
2022-12-09 23:00 | -11969.5 | 6.8587 | 33.0753 | 53.895 | -3507.9142
2022-12-11 | -12164.7 | 6.8587 | 32.7967 | 53.895 | -3565.1216
2022-12-12 01:00 | -12116.3 | 6.8587 | 32.7154 | 53.895 | -3550.937
2022-12-13 02:00 | -12278.3 | 6.8587 | 32.5288 | 53.895 | -3598.4145
2022-12-14 03:00 | -12243.8 | 6.8587 | 32.4755 | 53.895 | -3588.3036
2022-12-15 04:00 | -12147.2 | 6.8587 | 32.475 | 53.895 | -3559.9929
2022-12-16 05:00 | -12170.1 | 6.8587 | 32.4177 | 53.895 | -3566.7042
2022-12-17 06:00 | -12043.9 | 6.8587 | 32.4577 | 53.895 | -3529.7187
2022-12-18 07:00 | -12088.2 | 6.8587 | 32.399 | 53.895 | -3542.7017
2022-12-19 08:00 | -12140.5 | 6.8587 | 32.3268 | 53.895 | -3558.0293
2022-12-20 09:00 | -12198.2 | 6.8587 | 32.2534 | 53.895 | -3574.9395
2022-12-21 10:00 | -12201 | 6.8587 | 32.2107 | 53.895 | -3575.7601
2022-12-22 11:00 | -10882.8 | 6.8587 | 33.0872 | 53.895 | -3189.4338
2022-12-23 12:00 | -9286.16 | 6.8587 | 34.3237 | 53.895 | -2721.5048
2022-12-24 13:00 | -8306.69 | 6.8587 | 35.2628 | 53.895 | -2434.4505
2022-12-25 14:00 | -8001.18 | 6.8587 | 35.7335 | 53.895 | -2344.9144
2022-12-26 15:00 | -8773.87 | 6.8587 | 35.398 | 53.895 | -2571.3675
2022-12-27 16:00 | -8050.05 | 6.8587 | 35.9425 | 53.895 | -2359.2368
2022-12-28 17:00 | -8348.32 | 6.8587 | 35.877 | 53.895 | -2446.6511
2022-12-29 18:00 | -8601.05 | 6.8587 | 35.7575 | 53.895 | -2520.7189
2022-12-30 19:00 | -8904.78 | 6.8587 | 35.5504 | 53.895 | -2609.7334
2022-12-31 20:00 | -9306.61 | 6.8587 | 35.2568 | 53.895 | -2727.4982
2023-01-01 21:00 | -10330.5 | 6.8587 | 34.5313 | 53.895 | -3027.5707
2023-01-02 22:00 | -10326.9 | 6.8587 | 34.4029 | 53.895 | -3026.5156
2023-01-03 23:00 | -11010.8 | 6.8587 | 33.8674 | 53.895 | -3226.9469
2023-01-05 | -11086.8 | 6.8587 | 33.689 | 53.895 | -3249.2203
2023-01-06 01:00 | -11257.4 | 6.8587 | 33.4677 | 53.895 | -3299.2183
2023-01-07 02:00 | -11758.8 | 6.8587 | 33.03 | 53.895 | -3446.1641
2023-01-08 03:00 | -11681.8 | 6.8587 | 32.9683 | 53.895 | -3423.5976
2023-01-09 04:00 | -11334.6 | 6.8587 | 33.1287 | 53.895 | -3321.8434
2023-01-10 05:00 | -11593.6 | 6.8587 | 32.9437 | 53.895 | -3397.7488
2023-01-11 06:00 | -11360.7 | 6.8587 | 33.0456 | 53.895 | -3329.4925
2023-01-12 07:00 | -11467.3 | 6.8587 | 32.9538 | 53.895 | -3360.7339
2023-01-13 08:00 | -11307.6 | 6.8587 | 33.0413 | 53.895 | -3313.9304
2023-01-14 09:00 | -11577.6 | 6.8587 | 32.8629 | 53.895 | -3393.0596
2023-01-15 10:00 | -11513 | 6.8587 | 32.8646 | 53.895 | -3374.1272
2023-01-16 11:00 | -11298.8 | 6.8587 | 32.9923 | 53.895 | -3311.3514
2023-01-17 12:00 | -9776.27 | 6.8587 | 34.0416 | 53.895 | -2865.1419
2023-01-18 13:00 | -10196.9 | 6.8587 | 33.9304 | 53.895 | -2988.4164
2023-01-19 14:00 | -10325 | 6.8587 | 33.8739 | 53.895 | -3025.9588
2023-01-20 15:00 | -9849.07 | 6.8587 | 34.2012 | 53.895 | -2886.4775
2023-01-21 16:00 | -9402.45 | 6.8587 | 34.5787 | 53.895 | -2755.5861
2023-01-22 17:00 | -9872.96 | 6.8587 | 34.3577 | 53.895 | -2893.479
2023-01-23 18:00 | -9792.19 | 6.8587 | 34.386 | 53.895 | -2869.8076
2023-01-24 19:00 | -10442.1 | 6.8587 | 33.9471 | 53.895 | -3060.2774
2023-01-25 20:00 | -10946.7 | 6.8587 | 33.5395 | 53.895 | -3208.1611
2023-01-26 21:00 | -11849.9 | 6.8587 | 32.8236 | 53.895 | -3472.8629
2023-01-27 22:00 | -12029.8 | 6.8587 | 32.5317 | 53.895 | -3525.5864
2023-01-28 23:00 | -12484.7 | 6.8587 | 32.1067 | 53.895 | -3658.9044
2023-01-30 | -12905.9 | 6.8587 | 31.6697 | 53.895 | -3782.3459
2023-01-31 01:00 | -13024.8 | 6.8587 | 31.4373 | 53.895 | -3817.1921
2023-02-01 02:00 | -13212.8 | 6.8587 | 31.1955 | 53.895 | -3872.2894
2023-02-02 03:00 | -13401.4 | 6.8587 | 30.962 | 53.895 | -3927.5626
2023-02-03 04:00 | -13392.2 | 6.8587 | 30.852 | 53.895 | -3924.8664
2023-02-04 05:00 | -13325.9 | 6.8587 | 30.8153 | 53.895 | -3905.4358
2023-02-05 06:00 | -13343.2 | 6.8587 | 30.741 | 53.895 | -3910.5059
2023-02-06 07:00 | -13366.4 | 6.8587 | 30.6651 | 53.895 | -3917.3052
2023-02-07 08:00 | -13226.1 | 6.8587 | 30.7061 | 53.895 | -3876.1873
2023-02-08 09:00 | -12678.7 | 6.8587 | 31.0652 | 53.895 | -3715.7602
2023-02-09 10:00 | -11515 | 6.8587 | 31.9162 | 53.895 | -3374.7134
2023-02-10 11:00 | -10026 | 6.8587 | 33.1039 | 53.895 | -2938.3305
2023-02-11 12:00 | -8861.96 | 6.8587 | 34.1677 | 53.895 | -2597.1841
2023-02-12 13:00 | -8371.38 | 6.8587 | 34.793 | 53.895 | -2453.4093
2023-02-13 14:00 | -7825.07 | 6.8587 | 35.4068 | 53.895 | -2293.3016
2023-02-14 15:00 | -7643.82 | 6.8587 | 35.7646 | 53.895 | -2240.1825
2023-02-15 16:00 | -7374.14 | 6.8587 | 36.1325 | 53.895 | -2161.1471
2023-02-16 17:00 | -8003.05 | 6.8587 | 35.8595 | 53.895 | -2345.4624
2023-02-17 18:00 | -9393.71 | 6.8587 | 34.9388 | 53.895 | -2753.0246
2023-02-18 19:00 | -10268.3 | 6.8587 | 34.2165 | 53.895 | -3009.3417
2023-02-19 20:00 | -10929 | 6.8587 | 33.6169 | 53.895 | -3202.9737
2023-02-20 21:00 | -11342.9 | 6.8587 | 33.1908 | 53.895 | -3324.2758
2023-02-21 22:00 | -11973 | 6.8587 | 32.6123 | 53.895 | -3508.9399
2023-02-22 23:00 | -12521.2 | 6.8587 | 32.0547 | 53.895 | -3669.6015
2023-02-24 | -12883.8 | 6.8587 | 31.6241 | 53.895 | -3775.8691
2023-02-25 01:00 | -13023.3 | 6.8587 | 31.3664 | 53.895 | -3816.7525
2023-02-26 02:00 | -12993.9 | 6.8587 | 31.2562 | 53.895 | -3808.1362
2023-02-27 03:00 | -12856.9 | 6.8587 | 31.2518 | 53.895 | -3767.9854
2023-02-28 04:00 | -12652.6 | 6.8587 | 31.3144 | 53.895 | -3708.111
2023-03-01 05:00 | -12385.1 | 6.8587 | 31.4649 | 53.895 | -3629.7145
2023-03-02 06:00 | -12104 | 6.8587 | 31.6665 | 53.895 | -3547.3322
2023-03-03 07:00 | -11814.9 | 6.8587 | 31.9016 | 53.895 | -3462.6054
2023-03-04 08:00 | -11360.6 | 6.8587 | 32.2587 | 53.895 | -3329.4632
2023-03-05 09:00 | -11737.3 | 6.8587 | 32.0826 | 53.895 | -3439.8631
2023-03-06 10:00 | -9744.37 | 6.8587 | 33.4576 | 53.895 | -2855.7929
2023-03-07 11:00 | -7880.77 | 6.8587 | 34.9962 | 53.895 | -2309.6257
2023-03-08 12:00 | -6796.86 | 6.8587 | 36.1171 | 53.895 | -1991.963
2023-03-09 13:00 | -6228.14 | 6.8587 | 36.8493 | 53.895 | -1825.2877
2023-03-10 14:00 | -5741.72 | 6.8587 | 37.4676 | 53.895 | -1682.732
2023-03-11 15:00 | -5807.43 | 6.8587 | 37.7071 | 53.895 | -1701.9897
2023-03-12 16:00 | -6083.49 | 6.8587 | 37.7028 | 53.895 | -1782.8949
2023-03-13 17:00 | -6442.76 | 6.8587 | 37.5586 | 53.895 | -1888.1866
2023-03-14 18:00 | -6439.21 | 6.8587 | 37.6175 | 53.895 | -1887.1462
2023-03-15 19:00 | -6974.54 | 6.8587 | 37.3269 | 53.895 | -2044.0359
2023-03-16 20:00 | -7322.05 | 6.8587 | 37.0997 | 53.895 | -2145.881
2023-03-17 21:00 | -8033.42 | 6.8587 | 36.6185 | 53.895 | -2354.363
2023-03-18 22:00 | -8543.11 | 6.8587 | 36.2105 | 53.895 | -2503.7384
2023-03-19 23:00 | -9236.48 | 6.8587 | 35.6539 | 53.895 | -2706.9451
2023-03-21 | -9799.32 | 6.8587 | 35.1409 | 53.895 | -2871.8972
2023-03-22 01:00 | -10012.5 | 6.8587 | 34.8573 | 53.895 | -2934.3741
2023-03-23 02:00 | -10407.3 | 6.8587 | 34.4766 | 53.895 | -3050.0785
2023-03-24 03:00 | -10351.4 | 6.8587 | 34.4007 | 53.895 | -3033.6959
2023-03-25 04:00 | -10421.9 | 6.8587 | 34.2855 | 53.895 | -3054.3574
2023-03-26 05:00 | -10734.5 | 6.8587 | 34.0201 | 53.895 | -3145.9714
2023-03-27 06:00 | -11255.5 | 6.8587 | 33.5829 | 53.895 | -3298.6614
2023-03-28 07:00 | -10779.8 | 6.8587 | 33.7919 | 53.895 | -3159.2475
2023-03-29 08:00 | -9702.2 | 6.8587 | 34.5305 | 53.895 | -2843.4341
2023-03-30 09:00 | -9036.24 | 6.8587 | 35.1172 | 53.895 | -2648.2605
2023-03-31 10:00 | -8042.33 | 6.8587 | 35.9329 | 53.895 | -2356.9743
2023-04-01 11:00 | -6580.21 | 6.8587 | 37.1243 | 53.895 | -1928.4692
2023-04-02 12:00 | -5569.98 | 6.8587 | 38.1195 | 53.895 | -1632.4
2023-04-03 13:00 | -5015.07 | 6.8587 | 38.8055 | 53.895 | -1469.7719
2023-04-04 14:00 | -4957.88 | 6.8587 | 39.0964 | 53.895 | -1453.0112
2023-04-05 15:00 | -4665.54 | 6.8587 | 39.4818 | 53.895 | -1367.3348
2023-04-06 16:00 | -4879.71 | 6.8587 | 39.5149 | 53.895 | -1430.1018
2023-04-07 17:00 | -4253.02 | 6.8587 | 40.0579 | 53.895 | -1246.4371
2023-04-08 18:00 | -5570.1 | 6.8587 | 39.3357 | 53.895 | -1632.4352
2023-04-09 19:00 | -6426.76 | 6.8587 | 38.7265 | 53.895 | -1883.4974
2023-04-10 20:00 | -7316.24 | 6.8587 | 38.0281 | 53.895 | -2144.1783
2023-04-11 21:00 | -7578.62 | 6.8587 | 37.729 | 53.895 | -2221.0743
2023-04-12 22:00 | -8475.65 | 6.8587 | 37.0334 | 53.895 | -2483.9678
2023-04-13 23:00 | -8870.9 | 6.8587 | 36.5892 | 53.895 | -2599.8042
2023-04-15 | -10109 | 6.8587 | 35.5921 | 53.895 | -2962.6554
2023-04-16 01:00 | -10703.9 | 6.8587 | 34.9425 | 53.895 | -3137.0034
2023-04-17 02:00 | -10808 | 6.8587 | 34.6556 | 53.895 | -3167.5121
2023-04-18 03:00 | -10812.8 | 6.8587 | 34.4973 | 53.895 | -3168.9189
2023-04-19 04:00 | -10644.8 | 6.8587 | 34.5025 | 53.895 | -3119.6829
2023-04-20 05:00 | -10532.1 | 6.8587 | 34.4976 | 53.895 | -3086.6538
2023-04-21 06:00 | -10494.3 | 6.8587 | 34.4876 | 53.895 | -3075.5757
2023-04-22 07:00 | -9566.24 | 6.8587 | 35.1027 | 53.895 | -2803.5882
2023-04-23 08:00 | -8746.67 | 6.8587 | 35.7598 | 53.895 | -2563.3959
2023-04-24 09:00 | -8518.77 | 6.8587 | 36.0623 | 53.895 | -2496.605
2023-04-25 10:00 | -7488.38 | 6.8587 | 36.8674 | 53.895 | -2194.6275
2023-04-26 11:00 | -6067.36 | 6.8587 | 38.0217 | 53.895 | -1778.1677
2023-04-27 12:00 | -6480.7 | 6.8587 | 38.032 | 53.895 | -1899.3057
2023-04-28 13:00 | -6162.16 | 6.8587 | 38.3673 | 53.895 | -1805.9508
2023-04-29 14:00 | -6416.13 | 6.8587 | 38.3093 | 53.895 | -1880.3821
2023-04-30 15:00 | -6212.92 | 6.8587 | 38.5224 | 53.895 | -1820.8271
2023-05-01 16:00 | -6396.16 | 6.8587 | 38.4768 | 53.895 | -1874.5295
2023-05-02 17:00 | -5203.59 | 6.8587 | 39.318 | 53.895 | -1525.0217
2023-05-03 18:00 | -5752.94 | 6.8587 | 39.1313 | 53.895 | -1686.0203
2023-05-04 19:00 | -6373.8 | 6.8587 | 38.7594 | 53.895 | -1867.9764
2023-05-05 20:00 | -6653.78 | 6.8587 | 38.5385 | 53.895 | -1950.0304
2023-05-06 21:00 | -6952.03 | 6.8587 | 38.3181 | 53.895 | -2037.4389
2023-05-07 22:00 | -7035.33 | 6.8587 | 38.2417 | 53.895 | -2061.8517
2023-05-08 23:00 | -7495.52 | 6.8587 | 37.8856 | 53.895 | -2196.7201
2023-05-10 | -9118.61 | 6.8587 | 36.7102 | 53.895 | -2672.4008
2023-05-11 01:00 | -9507.67 | 6.8587 | 36.2175 | 53.895 | -2786.423
2023-05-12 02:00 | -10071.4 | 6.8587 | 35.6679 | 53.895 | -2951.636
2023-05-13 03:00 | -10301 | 6.8587 | 35.3477 | 53.895 | -3018.9251
2023-05-14 04:00 | -10457.5 | 6.8587 | 35.099 | 53.895 | -3064.7907
2023-05-15 05:00 | -10844.5 | 6.8587 | 34.6991 | 53.895 | -3178.2092
2023-05-16 06:00 | -11236.4 | 6.8587 | 34.3025 | 53.895 | -3293.0638
2023-05-17 07:00 | -10583.6 | 6.8587 | 34.6056 | 53.895 | -3101.747
2023-05-18 08:00 | -9542.84 | 6.8587 | 35.3048 | 53.895 | -2796.7303
2023-05-19 09:00 | -8760.63 | 6.8587 | 35.9398 | 53.895 | -2567.4872
2023-05-20 10:00 | -7747.32 | 6.8587 | 36.7505 | 53.895 | -2270.5154
2023-05-21 11:00 | -6535.18 | 6.8587 | 37.7492 | 53.895 | -1915.2722
2023-05-22 12:00 | -6008.34 | 6.8587 | 38.3724 | 53.895 | -1760.8706
2023-05-23 13:00 | -5012.63 | 6.8587 | 39.2735 | 53.895 | -1469.0568
2023-05-24 14:00 | -6240 | 6.8587 | 38.691 | 53.895 | -1828.7635
2023-05-25 15:00 | -6214.35 | 6.8587 | 38.7288 | 53.895 | -1821.2462
2023-05-26 16:00 | -6220.14 | 6.8587 | 38.7642 | 53.895 | -1822.9431
2023-05-27 17:00 | -5251.24 | 6.8587 | 39.477 | 53.895 | -1538.9865
2023-05-28 18:00 | -6228.29 | 6.8587 | 38.9765 | 53.895 | -1825.3316
2023-05-29 19:00 | -6779.25 | 6.8587 | 38.5737 | 53.895 | -1986.8021
2023-05-30 20:00 | -7331.42 | 6.8587 | 38.1417 | 53.895 | -2148.6271
2023-05-31 21:00 | -7474.48 | 6.8587 | 37.9758 | 53.895 | -2190.5539
2023-06-01 22:00 | -7550.94 | 6.8587 | 37.8783 | 53.895 | -2212.9621
2023-06-02 23:00 | -7826.76 | 6.8587 | 37.6308 | 53.895 | -2293.7969
2023-06-04 | -8980.33 | 6.8587 | 36.781 | 53.895 | -2631.8749
2023-06-05 01:00 | -9046.51 | 6.8587 | 36.555 | 53.895 | -2651.2704
2023-06-06 02:00 | -9164.37 | 6.8587 | 36.3837 | 53.895 | -2685.8117
2023-06-07 03:00 | -9531.9 | 6.8587 | 36.0644 | 53.895 | -2793.5241
2023-06-08 04:00 | -9401.5 | 6.8587 | 36.0552 | 53.895 | -2755.3077
2023-06-09 05:00 | -9344.58 | 6.8587 | 36.0333 | 53.895 | -2738.6261
2023-06-10 06:00 | -8997.42 | 6.8587 | 36.2591 | 53.895 | -2636.8835
2023-06-11 07:00 | -9158.3 | 6.8587 | 36.1678 | 53.895 | -2684.0328
2023-06-12 08:00 | -8378.49 | 6.8587 | 36.687 | 53.895 | -2455.493
2023-06-13 09:00 | -7514.02 | 6.8587 | 37.3674 | 53.895 | -2202.1419
2023-06-14 10:00 | -5858.36 | 6.8587 | 38.6512 | 53.895 | -1716.9158
2023-06-15 11:00 | -4261.85 | 6.8587 | 40.0195 | 53.895 | -1249.0249
2023-06-16 12:00 | -3208.83 | 6.8587 | 41.0998 | 53.895 | -940.4152
2023-06-17 13:00 | -2331.76 | 6.8587 | 42.0516 | 53.895 | -683.3714
2023-06-18 14:00 | -2193.61 | 6.8587 | 42.4922 | 53.895 | -642.8836
2023-06-19 15:00 | -2140.74 | 6.8587 | 42.7981 | 53.895 | -627.389
2023-06-20 16:00 | -1879.29 | 6.8214 | 43.1766 | 53.895 | -550.7655
2023-06-21 17:00 | -2600.04 | 6.8587 | 42.8802 | 53.895 | -761.9965
2023-06-22 18:00 | -3672.87 | 6.8587 | 42.2112 | 53.895 | -1076.4119
2023-06-23 19:00 | -4520.03 | 6.8587 | 41.5807 | 53.895 | -1324.69
2023-06-24 20:00 | -5497.19 | 6.8587 | 40.8267 | 53.895 | -1611.0674
2023-06-25 21:00 | -6621.47 | 6.8587 | 39.9194 | 53.895 | -1940.5613
2023-06-26 22:00 | -6768.11 | 6.8587 | 39.5985 | 53.895 | -1983.5372
2023-06-27 23:00 | -7583.72 | 6.8587 | 38.8923 | 53.895 | -2222.5689
2023-06-29 | -7818.55 | 6.8587 | 38.5476 | 53.895 | -2291.3908
2023-06-30 01:00 | -8114.05 | 6.8587 | 38.1899 | 53.895 | -2377.9933
2023-07-01 02:00 | -8275.3 | 6.8587 | 37.9469 | 53.895 | -2425.251
2023-07-02 03:00 | -8184.43 | 6.8587 | 37.9054 | 53.895 | -2398.6197
2023-07-03 04:00 | -8210.72 | 6.8587 | 37.8128 | 53.895 | -2406.3245
2023-07-04 05:00 | -7949.19 | 6.8587 | 37.9406 | 53.895 | -2329.6776
2023-07-05 06:00 | -7405.94 | 6.8587 | 38.3095 | 53.895 | -2170.4668
2023-07-06 07:00 | -7394.95 | 6.8587 | 38.3814 | 53.895 | -2167.2459
2023-07-07 08:00 | -7192.17 | 6.8587 | 38.5546 | 53.895 | -2107.817
2023-07-08 09:00 | -7160.16 | 6.8587 | 38.6209 | 53.895 | -2098.4358
2023-07-09 10:00 | -6364.1 | 6.8587 | 39.1944 | 53.895 | -1865.1336
2023-07-10 11:00 | -5529.67 | 6.8587 | 39.8748 | 53.895 | -1620.5863
2023-07-11 12:00 | -4963.15 | 6.8587 | 40.4143 | 53.895 | -1454.5557
2023-07-12 13:00 | -4982.77 | 6.8587 | 40.5474 | 53.895 | -1460.3057
2023-07-13 14:00 | -5067.84 | 6.8587 | 40.5766 | 53.895 | -1485.2373
2023-07-14 15:00 | -4843.8 | 6.8587 | 40.7889 | 53.895 | -1419.5776
2023-07-15 16:00 | -3814.5 | 6.8587 | 41.5691 | 53.895 | -1117.9196
2023-07-16 17:00 | -3583.09 | 6.8587 | 41.9021 | 53.895 | -1050.1
2023-07-17 18:00 | -3512.47 | 6.8587 | 42.0854 | 53.895 | -1029.4033
2023-07-18 19:00 | -3865.28 | 6.8587 | 41.9503 | 53.895 | -1132.8017
2023-07-19 20:00 | -4049.32 | 6.8587 | 41.8836 | 53.895 | -1186.7385
2023-07-20 21:00 | -4864.6 | 6.8587 | 41.3798 | 53.895 | -1425.6735
2023-07-21 22:00 | -4996.82 | 6.8587 | 41.2353 | 53.895 | -1464.4234
2023-07-22 23:00 | -5801.58 | 6.8587 | 40.6541 | 53.895 | -1700.2753
2023-07-24 | -6017.72 | 6.8587 | 40.4068 | 53.895 | -1763.6196
2023-07-25 01:00 | -6068.2 | 6.8587 | 40.3031 | 53.895 | -1778.4139
2023-07-26 02:00 | -6252.51 | 6.8587 | 40.1442 | 53.895 | -1832.4298
2023-07-27 03:00 | -6118.94 | 6.8587 | 40.2048 | 53.895 | -1793.2843
2023-07-28 04:00 | -5880.33 | 6.8587 | 40.3572 | 53.895 | -1723.3546
2023-07-29 05:00 | -5590.73 | 6.8587 | 40.5862 | 53.895 | -1638.4812
2023-07-30 06:00 | -4931.75 | 6.8587 | 41.088 | 53.895 | -1445.3532
2023-07-31 07:00 | -5083.89 | 6.8587 | 41.0969 | 53.895 | -1489.9411
2023-08-01 08:00 | -5084.33 | 6.8587 | 41.1484 | 53.895 | -1490.07
2023-08-02 09:00 | -5649.79 | 6.8587 | 40.8028 | 53.895 | -1655.79
2023-08-03 10:00 | -5297.69 | 6.8587 | 41.0065 | 53.895 | -1552.5997
2023-08-04 11:00 | -5101.26 | 6.8587 | 41.1692 | 53.895 | -1495.0317
2023-08-05 12:00 | -4799.46 | 6.8587 | 41.41 | 53.895 | -1406.5829
2023-08-06 13:00 | -4652.12 | 6.8587 | 41.5626 | 53.895 | -1363.4018
2023-08-07 14:00 | -4245.25 | 6.8587 | 41.8917 | 53.895 | -1244.16
2023-08-08 15:00 | -4150.58 | 6.8587 | 42.0491 | 53.895 | -1216.4149
2023-08-09 16:00 | -3362.75 | 6.8587 | 42.6517 | 53.895 | -985.5247
2023-08-10 17:00 | -3221.56 | 6.8587 | 42.8841 | 53.895 | -944.146
2023-08-11 18:00 | -2897.61 | 6.8587 | 43.2057 | 53.895 | -849.2057
2023-08-12 19:00 | -3298.39 | 6.8587 | 43.0432 | 53.895 | -966.6627
2023-08-13 20:00 | -3441.61 | 6.8587 | 42.9813 | 53.895 | -1008.6363
2023-08-14 21:00 | -4264.2 | 6.8587 | 42.4594 | 53.895 | -1249.7137
2023-08-15 22:00 | -4410.86 | 6.8587 | 42.299 | 53.895 | -1292.6955
2023-08-16 23:00 | -4978.64 | 6.8587 | 41.8816 | 53.895 | -1459.0954
2023-08-18 | -5329.17 | 6.8587 | 41.5699 | 53.895 | -1561.8256
2023-08-19 01:00 | -5192.77 | 6.8587 | 41.5911 | 53.895 | -1521.8507
2023-08-20 02:00 | -5402.89 | 6.8587 | 41.4291 | 53.895 | -1583.4308
2023-08-21 03:00 | -5243.25 | 6.8587 | 41.5138 | 53.895 | -1536.6449
2023-08-22 04:00 | -4808.73 | 6.8587 | 41.8079 | 53.895 | -1409.2996
2023-08-23 05:00 | -4366.93 | 6.8587 | 42.1682 | 53.895 | -1279.8208
2023-08-24 06:00 | -3662.16 | 6.8587 | 42.7359 | 53.895 | -1073.2731
2023-08-25 07:00 | -3614.47 | 6.8587 | 42.9057 | 53.895 | -1059.2966
2023-08-26 08:00 | -3431.24 | 6.8587 | 43.1273 | 53.895 | -1005.5972
2023-08-27 09:00 | -3703.88 | 6.8587 | 43.0414 | 53.895 | -1085.5001
2023-08-28 10:00 | -3196.64 | 6.8587 | 43.431 | 53.895 | -936.8427
2023-08-29 11:00 | -2566.22 | 6.8587 | 43.9674 | 53.895 | -752.0848
2023-08-30 12:00 | -1872.27 | 6.6736 | 44.5564 | 53.895 | -548.7082
2023-08-31 13:00 | -1477.37 | 5.2127 | 44.7237 | 53.895 | -432.9744
2023-09-01 14:00 | -1205.03 | 4.4022 | 44.9414 | 53.895 | -353.1594
2023-09-02 15:00 | -792.575 | 3.0272 | 45.1636 | 53.895 | -232.2808
2023-09-03 16:00 | -235.601 | 1.2296 | 45.6633 | 53.895 | -69.0478
2023-09-04 17:00 | -113.89 | 1.0095 | 46.2252 | 53.895 | -33.3779
2023-09-05 18:00 | -103.475 | 0.99579 | 46.4099 | 53.895 | -30.3255
2023-09-06 19:00 | -597.083 | 2.6903 | 45.9709 | 53.895 | -174.9878
2023-09-07 20:00 | -1096.77 | 4.2573 | 45.8496 | 53.895 | -321.4316
2023-09-08 21:00 | -2049.35 | 6.8587 | 45.6685 | 53.895 | -600.6052
2023-09-09 22:00 | -2514.45 | 6.8587 | 45.2675 | 53.895 | -736.9126
2023-09-10 23:00 | -3448.61 | 6.8587 | 44.5491 | 53.895 | -1010.6878
2023-09-12 | -3938.07 | 6.8587 | 44.0691 | 53.895 | -1154.1344
2023-09-13 01:00 | -4118.08 | 6.8587 | 43.8089 | 53.895 | -1206.8901
2023-09-14 02:00 | -4206.4 | 6.8587 | 43.6534 | 53.895 | -1232.7741
2023-09-15 03:00 | -4387.02 | 6.8587 | 43.463 | 53.895 | -1285.7086
2023-09-16 04:00 | -4407.58 | 6.8587 | 43.366 | 53.895 | -1291.7342
2023-09-17 05:00 | -4485.56 | 6.8587 | 43.2582 | 53.895 | -1314.5879
2023-09-18 06:00 | -4379.49 | 6.8587 | 43.2782 | 53.895 | -1283.5018
2023-09-19 07:00 | -3689.83 | 6.8587 | 43.7257 | 53.895 | -1081.3824
2023-09-20 08:00 | -3245.38 | 6.8587 | 44.0878 | 53.895 | -951.127
2023-09-21 09:00 | -3995.11 | 6.8587 | 43.6672 | 53.895 | -1170.8512
2023-09-22 10:00 | -3890.06 | 6.8587 | 43.6922 | 53.895 | -1140.064
2023-09-23 11:00 | -3412 | 6.8587 | 44.0143 | 53.895 | -999.9585
2023-09-24 12:00 | -3765.45 | 6.8587 | 43.8399 | 53.895 | -1103.5445
2023-09-25 13:00 | -4453.08 | 6.8587 | 43.3469 | 53.895 | -1305.0689
2023-09-26 14:00 | -4561.54 | 6.8587 | 43.1565 | 53.895 | -1336.8554
2023-09-27 15:00 | -4894.02 | 6.8587 | 42.8612 | 53.895 | -1434.2957
2023-09-28 16:00 | -5127.46 | 6.8587 | 42.612 | 53.895 | -1502.7102
2023-09-29 17:00 | -4097.54 | 6.8587 | 43.2124 | 53.895 | -1200.8704
2023-09-30 18:00 | -4702.12 | 6.8587 | 42.8512 | 53.895 | -1378.0553
2023-10-01 19:00 | -5134.84 | 6.8587 | 42.4974 | 53.895 | -1504.8731
2023-10-02 20:00 | -5603.2 | 6.8587 | 42.0668 | 53.895 | -1642.1358
2023-10-03 21:00 | -5818.14 | 6.8587 | 41.8169 | 53.895 | -1705.1285
2023-10-04 22:00 | -5880.14 | 6.8587 | 41.6904 | 53.895 | -1723.2989
2023-10-05 23:00 | -5969.96 | 6.8587 | 41.5449 | 53.895 | -1749.6226
2023-10-07 | -7365.03 | 6.8587 | 40.5229 | 53.895 | -2158.4772
2023-10-08 01:00 | -7534.85 | 6.8587 | 40.1894 | 53.895 | -2208.2466
2023-10-09 02:00 | -7464.34 | 6.8587 | 40.0892 | 53.895 | -2187.5821
2023-10-10 03:00 | -7545.03 | 6.8587 | 39.9553 | 53.895 | -2211.23
2023-10-11 04:00 | -7582.97 | 6.8587 | 39.8448 | 53.895 | -2222.3491
2023-10-12 05:00 | -7619.23 | 6.8587 | 39.7231 | 53.895 | -2232.9759
2023-10-13 06:00 | -7597.24 | 6.8587 | 39.6739 | 53.895 | -2226.5313
2023-10-14 07:00 | -6907.1 | 6.8587 | 40.0937 | 53.895 | -2024.2712
2023-10-15 08:00 | -6650.91 | 6.8587 | 40.3021 | 53.895 | -1949.1893
2023-10-16 09:00 | -7229.69 | 6.8587 | 39.9399 | 53.895 | -2118.813
2023-10-17 10:00 | -7057.22 | 6.8587 | 39.9825 | 53.895 | -2068.267
2023-10-18 11:00 | -6534.28 | 6.8587 | 40.3056 | 53.895 | -1915.0084
2023-10-19 12:00 | -5953.47 | 6.8587 | 40.7558 | 53.895 | -1744.7898
2023-10-20 13:00 | -5696.42 | 6.8587 | 41.0131 | 53.895 | -1669.4559
2023-10-21 14:00 | -5432.11 | 6.8587 | 41.254 | 53.895 | -1591.9943
2023-10-22 15:00 | -5336.6 | 6.8587 | 41.3936 | 53.895 | -1564.0031
2023-10-23 16:00 | -5238.23 | 6.8587 | 41.5202 | 53.895 | -1535.1737
2023-10-24 17:00 | -3894.12 | 6.8587 | 42.4837 | 53.895 | -1141.2539
2023-10-25 18:00 | -4597.7 | 6.8587 | 42.1947 | 53.895 | -1347.4529
2023-10-26 19:00 | -5451.97 | 6.8587 | 41.6324 | 53.895 | -1597.8147
2023-10-27 20:00 | -5756.45 | 6.8587 | 41.331 | 53.895 | -1687.049
2023-10-28 21:00 | -5871.1 | 6.8587 | 41.198 | 53.895 | -1720.6496
2023-10-29 22:00 | -5930.74 | 6.8587 | 41.1299 | 53.895 | -1738.1283
2023-10-30 23:00 | -6156.32 | 6.8587 | 40.9273 | 53.895 | -1804.2393
2023-11-01 | -7168.41 | 6.8587 | 40.1813 | 53.895 | -2100.8536
2023-11-02 01:00 | -7470.92 | 6.8587 | 39.8251 | 53.895 | -2189.5105
2023-11-03 02:00 | -7345.77 | 6.8587 | 39.7893 | 53.895 | -2152.8327
2023-11-04 03:00 | -7354.67 | 6.8587 | 39.7275 | 53.895 | -2155.441
2023-11-05 04:00 | -7110.21 | 6.8587 | 39.8414 | 53.895 | -2083.7969
2023-11-06 05:00 | -6905.74 | 6.8587 | 39.9459 | 53.895 | -2023.8726
2023-11-07 06:00 | -6420.29 | 6.8587 | 40.2835 | 53.895 | -1881.6013
2023-11-08 07:00 | -6415.93 | 6.8587 | 40.3426 | 53.895 | -1880.3235
2023-11-09 08:00 | -6102 | 6.8587 | 40.5797 | 53.895 | -1788.3197
2023-11-10 09:00 | -5549.5 | 6.8587 | 41.0119 | 53.895 | -1626.3979
2023-11-11 10:00 | -3939.61 | 6.8587 | 42.2154 | 53.895 | -1154.5857
2023-11-12 11:00 | -2358.16 | 6.8587 | 43.554 | 53.895 | -691.1085
2023-11-13 12:00 | -1147.74 | 4.0636 | 44.1873 | 53.895 | -336.3694
2023-11-14 13:00 | -605.727 | 2.4256 | 44.7084 | 53.895 | -177.5211
2023-11-15 14:00 | -296.218 | 1.5171 | 45.2789 | 53.895 | -86.8129
2023-11-16 15:00 | 419.104 | 1 | 46.4041 | 53.895 | 122.8273
2023-11-17 16:00 | 2682.8 | 1 | 46.3134 | 53.895 | 786.2511
2023-11-18 17:00 | -377.342 | 2.0325 | 46.3785 | 53.895 | -110.588
2023-11-19 18:00 | -1353.03 | 5.2145 | 45.9719 | 53.895 | -396.5339
2023-11-20 19:00 | -2448.07 | 6.8587 | 45.4152 | 53.895 | -717.4585
2023-11-21 20:00 | -2997.58 | 6.8587 | 44.9417 | 53.895 | -878.504
2023-11-22 21:00 | -4894.66 | 6.8587 | 43.5457 | 53.895 | -1434.4832
2023-11-23 22:00 | -6028.32 | 6.8587 | 42.4336 | 53.895 | -1766.7262
2023-11-24 23:00 | -7094.05 | 6.8587 | 41.3918 | 53.895 | -2079.0608
2023-11-26 | -7806.17 | 6.8587 | 40.5958 | 53.895 | -2287.7626
2023-11-27 01:00 | -8213.4 | 6.8587 | 40.0304 | 53.895 | -2407.1099
2023-11-28 02:00 | -8540.31 | 6.8587 | 39.5483 | 53.895 | -2502.9178
2023-11-29 03:00 | -8666.76 | 6.8587 | 39.2388 | 53.895 | -2539.9766
2023-11-30 04:00 | -8692.55 | 6.8587 | 39.0111 | 53.895 | -2547.5349
2023-12-01 05:00 | -8523.76 | 6.8587 | 38.9837 | 53.895 | -2498.0675
2023-12-02 06:00 | -8151.87 | 6.8587 | 39.1443 | 53.895 | -2389.0773
2023-12-03 07:00 | -8367.07 | 6.8587 | 38.9575 | 53.895 | -2452.1462
2023-12-04 08:00 | -8419.82 | 6.8587 | 38.8389 | 53.895 | -2467.6057
2023-12-05 09:00 | -8664.81 | 6.8587 | 38.6025 | 53.895 | -2539.4051
2023-12-06 10:00 | -8474.18 | 6.8587 | 38.6462 | 53.895 | -2483.537
2023-12-07 11:00 | -8169.67 | 6.8587 | 38.8034 | 53.895 | -2394.2939
2023-12-08 12:00 | -7800.87 | 6.8587 | 39.0314 | 53.895 | -2286.2093
2023-12-09 13:00 | -7625.74 | 6.8587 | 39.1545 | 53.895 | -2234.8838
2023-12-10 14:00 | -7435.58 | 6.8587 | 39.2834 | 53.895 | -2179.1534
2023-12-11 15:00 | -7472.14 | 6.8587 | 39.2614 | 53.895 | -2189.8681
2023-12-12 16:00 | -6682.95 | 6.8587 | 39.77 | 53.895 | -1958.5793
2023-12-13 17:00 | -6510.25 | 6.8587 | 39.9538 | 53.895 | -1907.9659
2023-12-14 18:00 | -6478.35 | 6.8587 | 40.0178 | 53.895 | -1898.617
2023-12-15 19:00 | -7032.54 | 6.8587 | 39.6572 | 53.895 | -2061.034
2023-12-16 20:00 | -7243.53 | 6.8587 | 39.4564 | 53.895 | -2122.8691
2023-12-17 21:00 | -8383.12 | 6.8587 | 38.6346 | 53.895 | -2456.8499
2023-12-18 22:00 | -8537.47 | 6.8587 | 38.3624 | 53.895 | -2502.0855
2023-12-19 23:00 | -9485.02 | 6.8587 | 37.594 | 53.895 | -2779.785
2023-12-21 | -9811.6 | 6.8587 | 37.1797 | 53.895 | -2875.4961
2023-12-22 01:00 | -9963.04 | 6.8587 | 36.9135 | 53.895 | -2919.8788
2023-12-23 02:00 | -10057.5 | 6.8587 | 36.7188 | 53.895 | -2947.5623
2023-12-24 03:00 | -10639.7 | 6.8587 | 36.2201 | 53.895 | -3118.1883
2023-12-25 04:00 | -10381.2 | 6.8587 | 36.23 | 53.895 | -3042.4294
2023-12-26 05:00 | -10253 | 6.8587 | 36.2348 | 53.895 | -3004.8577
2023-12-27 06:00 | -9815.05 | 6.8587 | 36.4763 | 53.895 | -2876.5072
2023-12-28 07:00 | -9703.3 | 6.8587 | 36.5432 | 53.895 | -2843.7565
2023-12-29 08:00 | -9107.5 | 6.8587 | 36.9322 | 53.895 | -2669.1448
2023-12-30 09:00 | -8659.5 | 6.8587 | 37.2998 | 53.895 | -2537.8489
2023-12-31 10:00 | -6937.98 | 6.8587 | 38.5539 | 53.895 | -2033.3212
2024-01-01 11:00 | -5020.35 | 6.8587 | 40.1159 | 53.895 | -1471.3193
2024-01-02 12:00 | -3598.69 | 6.8587 | 41.4597 | 53.895 | -1054.6719
2024-01-03 13:00 | -2878.49 | 6.8587 | 42.3414 | 53.895 | -843.6021
2024-01-04 14:00 | -2125.06 | 6.8587 | 43.1878 | 53.895 | -622.7936
2024-01-05 15:00 | -1659.86 | 5.9581 | 43.671 | 53.895 | -486.4569
2024-01-06 16:00 | -1168.37 | 4.244 | 43.9699 | 53.895 | -342.4154
2024-01-07 17:00 | -1631.37 | 6.1034 | 44.273 | 53.895 | -478.1074
2024-01-08 18:00 | -3109.59 | 6.8587 | 43.5353 | 53.895 | -911.3309
2024-01-09 19:00 | -4717.67 | 6.8587 | 42.3838 | 53.895 | -1382.6126
2024-01-10 20:00 | -5132.87 | 6.8587 | 41.9215 | 53.895 | -1504.2957
2024-01-11 21:00 | -6491 | 6.8587 | 40.8888 | 53.895 | -1902.3243
2024-01-12 22:00 | -7274.31 | 6.8587 | 40.127 | 53.895 | -2131.8898
2024-01-13 23:00 | -8629.62 | 6.8587 | 38.9565 | 53.895 | -2529.092
2024-01-15 | -9325.76 | 6.8587 | 38.1724 | 53.895 | -2733.1105
2024-01-16 01:00 | -9909.22 | 6.8587 | 37.5028 | 53.895 | -2904.1057
2024-01-17 02:00 | -10518.2 | 6.8587 | 36.8236 | 53.895 | -3082.5801
2024-01-18 03:00 | -11080.8 | 6.8587 | 36.1786 | 53.895 | -3247.4619
2024-01-19 04:00 | -11237.9 | 6.8587 | 35.8023 | 53.895 | -3293.5034
2024-01-20 05:00 | -11348.7 | 6.8587 | 35.5198 | 53.895 | -3325.9757
2024-01-21 06:00 | -10998.4 | 6.8587 | 35.5934 | 53.895 | -3223.3129
2024-01-22 07:00 | -10964.2 | 6.8587 | 35.5333 | 53.895 | -3213.2898
2024-01-23 08:00 | -10275.8 | 6.8587 | 35.926 | 53.895 | -3011.5397
2024-01-24 09:00 | -10453.4 | 6.8587 | 35.8221 | 53.895 | -3063.5891
2024-01-25 10:00 | -9885.18 | 6.8587 | 36.1716 | 53.895 | -2897.0603
2024-01-26 11:00 | -9254.35 | 6.8587 | 36.6286 | 53.895 | -2712.1823
2024-01-27 12:00 | -8718.78 | 6.8587 | 37.0646 | 53.895 | -2555.2222
2024-01-28 13:00 | -6604.4 | 6.8587 | 38.603 | 53.895 | -1935.5586
2024-01-29 14:00 | -6746.4 | 6.8587 | 38.7948 | 53.895 | -1977.1747
2024-01-30 15:00 | -5870.5 | 6.8587 | 39.5452 | 53.895 | -1720.4737
2024-01-31 16:00 | -5020.47 | 6.8587 | 40.3134 | 53.895 | -1471.3545
2024-02-01 17:00 | -5491.38 | 6.8587 | 40.2274 | 53.895 | -1609.3646
2024-02-02 18:00 | -5856.42 | 6.8587 | 40.076 | 53.895 | -1716.3473
2024-02-03 19:00 | -6742.38 | 6.8587 | 39.4862 | 53.895 | -1975.9965
2024-02-04 20:00 | -7151.81 | 6.8587 | 39.1449 | 53.895 | -2095.9886
2024-02-05 21:00 | -8280.44 | 6.8587 | 38.3109 | 53.895 | -2426.7574
2024-02-06 22:00 | -8758.73 | 6.8587 | 37.8112 | 53.895 | -2566.9304
2024-02-07 23:00 | -9778.78 | 6.8587 | 36.9652 | 53.895 | -2865.8775
2024-02-09 | -9972.41 | 6.8587 | 36.6269 | 53.895 | -2922.6249
2024-02-10 01:00 | -10302.5 | 6.8587 | 36.241 | 53.895 | -3019.3647
2024-02-11 02:00 | -10475.5 | 6.8587 | 35.9771 | 53.895 | -3070.066
2024-02-12 03:00 | -10340 | 6.8587 | 35.9465 | 53.895 | -3030.3549
2024-02-13 04:00 | -10397 | 6.8587 | 35.8213 | 53.895 | -3047.0599
2024-02-14 05:00 | -9981.99 | 6.8587 | 36.0379 | 53.895 | -2925.4325
2024-02-15 06:00 | -9635.21 | 6.8587 | 36.2632 | 53.895 | -2823.8013
2024-02-16 07:00 | -9294.23 | 6.8587 | 36.5235 | 53.895 | -2723.8699
2024-02-17 08:00 | -8919.87 | 6.8587 | 36.8206 | 53.895 | -2614.1558
2024-02-18 09:00 | -8940.29 | 6.8587 | 36.8725 | 53.895 | -2620.1404
2024-02-19 10:00 | -8580.69 | 6.8587 | 37.1486 | 53.895 | -2514.752
2024-02-20 11:00 | -7819.87 | 6.8587 | 37.7269 | 53.895 | -2291.7777
2024-02-21 12:00 | -5827.92 | 6.8587 | 39.2153 | 53.895 | -1707.9948
2024-02-22 13:00 | -5267.83 | 6.8587 | 39.9004 | 53.895 | -1543.8486
2024-02-23 14:00 | -5600.43 | 6.8587 | 39.9052 | 53.895 | -1641.324
2024-02-24 15:00 | -5537.67 | 6.8587 | 40.0394 | 53.895 | -1622.9309
2024-02-25 16:00 | -5589.52 | 6.8587 | 40.0866 | 53.895 | -1638.1266
2024-02-26 17:00 | -4692.37 | 6.8587 | 40.7737 | 53.895 | -1375.1979
2024-02-27 18:00 | -5037.62 | 6.8587 | 40.6832 | 53.895 | -1476.3807
2024-02-28 19:00 | -5824.04 | 6.8587 | 40.1963 | 53.895 | -1706.8576
2024-02-29 20:00 | -6411.7 | 6.8587 | 39.7439 | 53.895 | -1879.0838
2024-03-01 21:00 | -7331.35 | 6.8587 | 39.0535 | 53.895 | -2148.6066
2024-03-02 22:00 | -7631.43 | 6.8587 | 38.7316 | 53.895 | -2236.5514
2024-03-03 23:00 | -8579.79 | 6.8587 | 37.978 | 53.895 | -2514.4882
2024-03-05 | -8938.99 | 6.8587 | 37.5444 | 53.895 | -2619.7594
2024-03-06 01:00 | -9176.89 | 6.8587 | 37.2233 | 53.895 | -2689.481
2024-03-07 02:00 | -9211.64 | 6.8587 | 37.0798 | 53.895 | -2699.6652
2024-03-08 03:00 | -9260.83 | 6.8587 | 36.9655 | 53.895 | -2714.0814
2024-03-09 04:00 | -9228.29 | 6.8587 | 36.9177 | 53.895 | -2704.5448
2024-03-10 05:00 | -9256.52 | 6.8587 | 36.844 | 53.895 | -2712.8182
2024-03-11 06:00 | -9173.19 | 6.8587 | 36.8505 | 53.895 | -2688.3966
2024-03-12 07:00 | -8425.21 | 6.8587 | 37.3372 | 53.895 | -2469.1853
2024-03-13 08:00 | -8093.89 | 6.8587 | 37.6315 | 53.895 | -2372.085
2024-03-14 09:00 | -8479.69 | 6.8587 | 37.443 | 53.895 | -2485.1518
2024-03-15 10:00 | -8191.52 | 6.8587 | 37.6258 | 53.895 | -2400.6975
2024-03-16 11:00 | -7794.68 | 6.8587 | 37.9339 | 53.895 | -2284.3952
2024-03-17 12:00 | -7219.75 | 6.8587 | 38.4003 | 53.895 | -2115.8999
2024-03-18 13:00 | -6818.78 | 6.8587 | 38.7671 | 53.895 | -1998.3872
2024-03-19 14:00 | -7019.18 | 6.8587 | 38.7229 | 53.895 | -2057.1186
2024-03-20 15:00 | -6681.42 | 6.8587 | 38.9894 | 53.895 | -1958.1309
2024-03-21 16:00 | -6658.37 | 6.8587 | 39.0706 | 53.895 | -1951.3756
2024-03-22 17:00 | -5343.06 | 6.8587 | 40.0193 | 53.895 | -1565.8963
2024-03-23 18:00 | -6047.16 | 6.8587 | 39.725 | 53.895 | -1772.2477
2024-03-24 19:00 | -6444.97 | 6.8587 | 39.4733 | 53.895 | -1888.8343
2024-03-25 20:00 | -6764.72 | 6.8587 | 39.2268 | 53.895 | -1982.5437
2024-03-26 21:00 | -7127.45 | 6.8587 | 38.9606 | 53.895 | -2088.8494
2024-03-27 22:00 | -7098.06 | 6.8587 | 38.9477 | 53.895 | -2080.236
2024-03-28 23:00 | -7286.99 | 6.8587 | 38.7961 | 53.895 | -2135.606
2024-03-30 | -8716.45 | 6.8587 | 37.7895 | 53.895 | -2554.5393
2024-03-31 01:00 | -9006.15 | 6.8587 | 37.4002 | 53.895 | -2639.442
2024-04-01 02:00 | -9174.85 | 6.8587 | 37.1501 | 53.895 | -2688.8831
2024-04-02 03:00 | -9189.53 | 6.8587 | 37.0499 | 53.895 | -2693.1854
2024-04-03 04:00 | -9193.56 | 6.8587 | 36.9722 | 53.895 | -2694.3665
2024-04-04 05:00 | -9221.94 | 6.8587 | 36.8723 | 53.895 | -2702.6838
2024-04-05 06:00 | -9237.93 | 6.8587 | 36.813 | 53.895 | -2707.37
2024-04-06 07:00 | -8446.14 | 6.8587 | 37.3141 | 53.895 | -2475.3193
2024-04-07 08:00 | -8134.38 | 6.8587 | 37.59 | 53.895 | -2383.9515
2024-04-08 09:00 | -8583.79 | 6.8587 | 37.3457 | 53.895 | -2515.6605
2024-04-09 10:00 | -8035.4 | 6.8587 | 37.6831 | 53.895 | -2354.9433
2024-04-10 11:00 | -7630.56 | 6.8587 | 38.0011 | 53.895 | -2236.2964
2024-04-11 12:00 | -7202.04 | 6.8587 | 38.3761 | 53.895 | -2110.7096
2024-04-12 13:00 | -6907.98 | 6.8587 | 38.6561 | 53.895 | -2024.5291
2024-04-13 14:00 | -6815.97 | 6.8587 | 38.7949 | 53.895 | -1997.5636
2024-04-14 15:00 | -6451.14 | 6.8587 | 39.1109 | 53.895 | -1890.6425
2024-04-15 16:00 | -5988.54 | 6.8587 | 39.5141 | 53.895 | -1755.0678
2024-04-16 17:00 | -4441.64 | 6.8587 | 40.6807 | 53.895 | -1301.7162
2024-04-17 18:00 | -5324.93 | 6.8587 | 40.335 | 53.895 | -1560.5829
2024-04-18 19:00 | -6008.72 | 6.8587 | 39.9112 | 53.895 | -1760.982
2024-04-19 20:00 | -6312.5 | 6.8587 | 39.6592 | 53.895 | -1850.0111
2024-04-20 21:00 | -6881.46 | 6.8587 | 39.2545 | 53.895 | -2016.7568
2024-04-21 22:00 | -7355.95 | 6.8587 | 38.8669 | 53.895 | -2155.8161
2024-04-22 23:00 | -7505.97 | 6.8587 | 38.6514 | 53.895 | -2199.7827
2024-04-24 | -8826.59 | 6.8587 | 37.6798 | 53.895 | -2586.8182
2024-04-25 01:00 | -9279.69 | 6.8587 | 37.1735 | 53.895 | -2719.6087
2024-04-26 02:00 | -9400.25 | 6.8587 | 36.9218 | 53.895 | -2754.9413
2024-04-27 03:00 | -9474.91 | 6.8587 | 36.7615 | 53.895 | -2776.822
2024-04-28 04:00 | -9378.97 | 6.8587 | 36.7353 | 53.895 | -2748.7048
2024-04-29 05:00 | -9451.81 | 6.8587 | 36.6004 | 53.895 | -2770.0521
2024-04-30 06:00 | -9081.77 | 6.8587 | 36.7945 | 53.895 | -2661.6041
2024-05-01 07:00 | -8891 | 6.8587 | 36.9232 | 53.895 | -2605.6949
2024-05-02 08:00 | -8248.06 | 6.8587 | 37.3713 | 53.895 | -2417.2678
2024-05-03 09:00 | -7925.85 | 6.8587 | 37.6695 | 53.895 | -2322.8373
2024-05-04 10:00 | -6427.34 | 6.8587 | 38.7749 | 53.895 | -1883.6674
2024-05-05 11:00 | -5074.23 | 6.8587 | 39.9295 | 53.895 | -1487.11
2024-05-06 12:00 | -4109.32 | 6.8587 | 40.8978 | 53.895 | -1204.3228
2024-05-07 13:00 | -3205.3 | 6.8587 | 41.8214 | 53.895 | -939.3807
2024-05-08 14:00 | -3968.46 | 6.8587 | 41.6092 | 53.895 | -1163.0408
2024-05-09 15:00 | -3866.29 | 6.8587 | 41.8071 | 53.895 | -1133.0977
2024-05-10 16:00 | -3358.15 | 6.8587 | 42.2723 | 53.895 | -984.1766
2024-05-11 17:00 | -3665.4 | 6.8587 | 42.2212 | 53.895 | -1074.2227
2024-05-12 18:00 | -3777.78 | 6.8587 | 42.2193 | 53.895 | -1107.158
2024-05-13 19:00 | -4292.13 | 6.8587 | 41.9136 | 53.895 | -1257.8991
2024-05-14 20:00 | -4865.8 | 6.8587 | 41.5309 | 53.895 | -1426.0252
2024-05-15 21:00 | -5733.44 | 6.8587 | 40.9049 | 53.895 | -1680.3054
2024-05-16 22:00 | -6867.34 | 6.8587 | 40.0102 | 53.895 | -2012.6187
2024-05-17 23:00 | -8051.73 | 6.8587 | 38.9962 | 53.895 | -2359.7291
2024-05-19 | -8665.98 | 6.8587 | 38.316 | 53.895 | -2539.748
2024-05-20 01:00 | -8819.96 | 6.8587 | 37.9787 | 53.895 | -2584.8751
2024-05-21 02:00 | -9150.8 | 6.8587 | 37.5916 | 53.895 | -2681.8347
2024-05-22 03:00 | -9169.45 | 6.8587 | 37.422 | 53.895 | -2687.3005
2024-05-23 04:00 | -9113.64 | 6.8587 | 37.3418 | 53.895 | -2670.9442
2024-05-24 05:00 | -9144.76 | 6.8587 | 37.2478 | 53.895 | -2680.0646
2024-05-25 06:00 | -8645.27 | 6.8587 | 37.5239 | 53.895 | -2533.6785
2024-05-26 07:00 | -8937.65 | 6.8587 | 37.3233 | 53.895 | -2619.3666
2024-05-27 08:00 | -8824.21 | 6.8587 | 37.3463 | 53.895 | -2586.1207
2024-05-28 09:00 | -9258.49 | 6.8587 | 37.0155 | 53.895 | -2713.3956
2024-05-29 10:00 | -9112.17 | 6.8587 | 37.0314 | 53.895 | -2670.5134
2024-05-30 11:00 | -8629.11 | 6.8587 | 37.3201 | 53.895 | -2528.9425
2024-05-31 12:00 | -8333.38 | 6.8587 | 37.5335 | 53.895 | -2442.2726
2024-06-01 13:00 | -7956.29 | 6.8587 | 37.8106 | 53.895 | -2331.7584
2024-06-02 14:00 | -7847.9 | 6.8587 | 37.9245 | 53.895 | -2299.9925
2024-06-03 15:00 | -6963.93 | 6.8587 | 38.563 | 53.895 | -2040.9264
2024-06-04 16:00 | -6170.37 | 6.8587 | 39.2242 | 53.895 | -1808.3569
2024-06-05 17:00 | -6157.07 | 6.8587 | 39.3869 | 53.895 | -1804.4591
2024-06-06 18:00 | -6079.7 | 6.8587 | 39.5183 | 53.895 | -1781.7842
2024-06-07 19:00 | -6804.58 | 6.8587 | 39.0843 | 53.895 | -1994.2255
2024-06-08 20:00 | -6936.2 | 6.8587 | 38.9634 | 53.895 | -2032.7996
2024-06-09 21:00 | -8093.92 | 6.8587 | 38.1516 | 53.895 | -2372.0938
2024-06-10 22:00 | -8518.2 | 6.8587 | 37.7169 | 53.895 | -2496.438
2024-06-11 23:00 | -9410.16 | 6.8587 | 36.9763 | 53.895 | -2757.8457
2024-06-13 | -9777.72 | 6.8587 | 36.5454 | 53.895 | -2865.5669
2024-06-14 01:00 | -10156.5 | 6.8587 | 36.1355 | 53.895 | -2976.5763
2024-06-15 02:00 | -10598.9 | 6.8587 | 35.6856 | 53.895 | -3106.231
2024-06-16 03:00 | -10699.1 | 6.8587 | 35.46 | 53.895 | -3135.5967
2024-06-17 04:00 | -10921.6 | 6.8587 | 35.1757 | 53.895 | -3200.805
2024-06-18 05:00 | -11184.7 | 6.8587 | 34.8734 | 53.895 | -3277.912
2024-06-19 06:00 | -11263.1 | 6.8587 | 34.6828 | 53.895 | -3300.8888
2024-06-20 07:00 | -11594.8 | 6.8587 | 34.3421 | 53.895 | -3398.1004
2024-06-21 08:00 | -10665 | 6.8587 | 34.8511 | 53.895 | -3125.603
2024-06-22 09:00 | -10712.8 | 6.8587 | 34.8424 | 53.895 | -3139.6118
2024-06-23 10:00 | -10673.2 | 6.8587 | 34.8506 | 53.895 | -3128.0061
2024-06-24 11:00 | -9295.34 | 6.8587 | 35.7669 | 53.895 | -2724.1952
2024-06-25 12:00 | -9181.83 | 6.8587 | 35.987 | 53.895 | -2690.9287
2024-06-26 13:00 | -8631.71 | 6.8587 | 36.4509 | 53.895 | -2529.7045
2024-06-27 14:00 | -8519.14 | 6.8587 | 36.6213 | 53.895 | -2496.7135
2024-06-28 15:00 | -8582.42 | 6.8587 | 36.6481 | 53.895 | -2515.259
2024-06-29 16:00 | -8182.97 | 6.8587 | 36.9575 | 53.895 | -2398.1918
2024-06-30 17:00 | -8389.21 | 6.8587 | 36.8734 | 53.895 | -2458.6348
2024-07-01 18:00 | -8924.98 | 6.8587 | 36.5164 | 53.895 | -2615.6534
2024-07-02 19:00 | -9573.19 | 6.8587 | 36.0105 | 53.895 | -2805.625
2024-07-03 20:00 | -10147.3 | 6.8587 | 35.4991 | 53.895 | -2973.8801
2024-07-04 21:00 | -11413.2 | 6.8587 | 34.5009 | 53.895 | -3344.8787
2024-07-05 22:00 | -11767 | 6.8587 | 34.0167 | 53.895 | -3448.5673
2024-07-06 23:00 | -12091.6 | 6.8587 | 33.5938 | 53.895 | -3543.6982
2024-07-08 | -12266.7 | 6.8587 | 33.3046 | 53.895 | -3595.0149
2024-07-09 01:00 | -12429.9 | 6.8587 | 33.0438 | 53.895 | -3642.8441
2024-07-10 02:00 | -12621.5 | 6.8587 | 32.7767 | 53.895 | -3698.9965
2024-07-11 03:00 | -12694 | 6.8587 | 32.6075 | 53.895 | -3720.2442
2024-07-12 04:00 | -12679.3 | 6.8587 | 32.5113 | 53.895 | -3715.936
2024-07-13 05:00 | -12658.9 | 6.8587 | 32.4419 | 53.895 | -3709.9574
2024-07-14 06:00 | -12515.3 | 6.8587 | 32.4701 | 53.895 | -3667.8724
2024-07-15 07:00 | -12277.5 | 6.8587 | 32.5896 | 53.895 | -3598.1801
2024-07-16 08:00 | -11858.9 | 6.8587 | 32.862 | 53.895 | -3475.5005
2024-07-17 09:00 | -11240.5 | 6.8587 | 33.3254 | 53.895 | -3294.2654
2024-07-18 10:00 | -9574.41 | 6.8587 | 34.5635 | 53.895 | -2805.9826
2024-07-19 11:00 | -8009.94 | 6.8587 | 35.8841 | 53.895 | -2347.4817
2024-07-20 12:00 | -8386.45 | 6.8587 | 35.9505 | 53.895 | -2457.8259
2024-07-21 13:00 | -6924.93 | 6.8587 | 37.0888 | 53.895 | -2029.4966
2024-07-22 14:00 | -7433.96 | 6.8587 | 37.0188 | 53.895 | -2178.6786
2024-07-23 15:00 | -6541.5 | 6.8587 | 37.7669 | 53.895 | -1917.1244
2024-07-24 16:00 | -5303.13 | 6.8587 | 38.8071 | 53.895 | -1554.194
2024-07-25 17:00 | -5954.58 | 6.8587 | 38.6391 | 53.895 | -1745.1151
2024-07-26 18:00 | -6121.61 | 6.8587 | 38.6395 | 53.895 | -1794.0668
2024-07-27 19:00 | -6661.43 | 6.8587 | 38.3332 | 53.895 | -1952.2724
2024-07-28 20:00 | -6989.23 | 6.8587 | 38.1442 | 53.895 | -2048.3411
2024-07-29 21:00 | -7651.03 | 6.8587 | 37.7048 | 53.895 | -2242.2955
2024-07-30 22:00 | -7595.22 | 6.8587 | 37.6704 | 53.895 | -2225.9393
2024-07-31 23:00 | -8273.77 | 6.8587 | 37.1866 | 53.895 | -2424.8026
2024-08-02 | -8368.69 | 6.8587 | 37.0474 | 53.895 | -2452.6209
2024-08-03 01:00 | -8387.57 | 6.8587 | 36.9823 | 53.895 | -2458.1541
2024-08-04 02:00 | -8292.07 | 6.8587 | 37.035 | 53.895 | -2430.1658
2024-08-05 03:00 | -8196.68 | 6.8587 | 37.1092 | 53.895 | -2402.2098
2024-08-06 04:00 | -8065.43 | 6.8587 | 37.2021 | 53.895 | -2363.7442
2024-08-07 05:00 | -7157.42 | 6.8587 | 37.8594 | 53.895 | -2097.6327
2024-08-08 06:00 | -6510.74 | 6.8587 | 38.4439 | 53.895 | -1908.1095
2024-08-09 07:00 | -5956.88 | 6.8587 | 38.9985 | 53.895 | -1745.7892
2024-08-10 08:00 | -4766.56 | 6.8587 | 39.9924 | 53.895 | -1396.9408
2024-08-11 09:00 | -4133.21 | 6.8587 | 40.7048 | 53.895 | -1211.3243
2024-08-12 10:00 | -2447.51 | 6.8587 | 42.1234 | 53.895 | -717.2944
2024-08-13 11:00 | -1327.6 | 4.8198 | 42.88 | 53.895 | -389.0812
2024-08-14 12:00 | -338.957 | 1.415 | 43.441 | 53.895 | -99.3385
2024-08-15 13:00 | 2088.31 | 1 | 44.6016 | 53.895 | 612.0232
2024-08-16 14:00 | 2753.11 | 1 | 45.0659 | 53.895 | 806.8569
2024-08-17 15:00 | 2631.52 | 1 | 45.5708 | 53.895 | 771.2224
2024-08-18 16:00 | 2748.52 | 1 | 45.8644 | 53.895 | 805.5117
2024-08-19 17:00 | 2730.63 | 1 | 46.1529 | 53.895 | 800.2687
2024-08-20 18:00 | 0 | 0 | 46.8734 | 53.895 | 0
2024-08-21 19:00 | -847.307 | 3.2399 | 45.502 | 53.895 | -248.3212
2024-08-22 20:00 | -1068.3 | 4.1149 | 45.394 | 53.895 | -313.0878
2024-08-23 21:00 | -2107.39 | 6.8587 | 45.1578 | 53.895 | -617.615
2024-08-24 22:00 | -2595.27 | 6.8587 | 44.6997 | 53.895 | -760.5986
2024-08-25 23:00 | -3360.22 | 6.8587 | 44.0473 | 53.895 | -984.7833
2024-08-27 | -3870.72 | 6.8587 | 43.5797 | 53.895 | -1134.3961
2024-08-28 01:00 | -3950.16 | 6.8587 | 43.3922 | 53.895 | -1157.6776
2024-08-29 02:00 | -4021.24 | 6.8587 | 43.2495 | 53.895 | -1178.5091
2024-08-30 03:00 | -4082.59 | 6.8587 | 43.1472 | 53.895 | -1196.489
2024-08-31 04:00 | -4105.55 | 6.8587 | 43.0778 | 53.895 | -1203.2179
2024-09-01 05:00 | -4145.65 | 6.8587 | 43.0102 | 53.895 | -1214.9701
2024-09-02 06:00 | -4199.63 | 6.8587 | 42.9653 | 53.895 | -1230.7901
2024-09-03 07:00 | -3255.29 | 6.8587 | 43.608 | 53.895 | -954.0313
2024-09-04 08:00 | -2597.38 | 6.8587 | 44.1727 | 53.895 | -761.2169
2024-09-05 09:00 | -2918.8 | 6.8587 | 44.1088 | 53.895 | -855.4158
2024-09-06 10:00 | -3280.78 | 6.8587 | 43.9047 | 53.895 | -961.5017
2024-09-07 11:00 | -3472.06 | 6.8587 | 43.7659 | 53.895 | -1017.5603
2024-09-08 12:00 | -2012.32 | 6.8587 | 44.7638 | 53.895 | -589.7528
2024-09-09 13:00 | -1620.2 | 5.6858 | 44.9674 | 53.895 | -474.8337
2024-09-10 14:00 | -2615.04 | 6.8587 | 44.6449 | 53.895 | -766.3926
2024-09-11 15:00 | -2009.98 | 6.8587 | 45.002 | 53.895 | -589.067
2024-09-12 16:00 | -1546.75 | 5.4118 | 45.0949 | 53.895 | -453.3077
2024-09-13 17:00 | -791.037 | 2.8964 | 45.2756 | 53.895 | -231.8301
2024-09-14 18:00 | -2255.07 | 6.8587 | 45.1779 | 53.895 | -660.8958
2024-09-15 19:00 | -3736.93 | 6.8587 | 44.0762 | 53.895 | -1095.1861
2024-09-16 20:00 | -4499.96 | 6.8587 | 43.3496 | 53.895 | -1318.8081
2024-09-17 21:00 | -5249.61 | 6.8587 | 42.6603 | 53.895 | -1538.5088
2024-09-18 22:00 | -5899.67 | 6.8587 | 42.0288 | 53.895 | -1729.0226
2024-09-19 23:00 | -6136.11 | 6.8587 | 41.6567 | 53.895 | -1798.3163
2024-09-21 | -7835.03 | 6.8587 | 40.328 | 53.895 | -2296.2206
2024-09-22 01:00 | -8082.37 | 6.8587 | 39.841 | 53.895 | -2368.7088
2024-09-23 02:00 | -8294.68 | 6.8587 | 39.4722 | 53.895 | -2430.9307
2024-09-24 03:00 | -8354.38 | 6.8587 | 39.2575 | 53.895 | -2448.4271
2024-09-25 04:00 | -8509.93 | 6.8587 | 38.9971 | 53.895 | -2494.0143
2024-09-26 05:00 | -8644.09 | 6.8587 | 38.7366 | 53.895 | -2533.3327
2024-09-27 06:00 | -8585.98 | 6.8587 | 38.6506 | 53.895 | -2516.3023
2024-09-28 07:00 | -7717.74 | 6.8587 | 39.1552 | 53.895 | -2261.8463
2024-09-29 08:00 | -6886.5 | 6.8587 | 39.7495 | 53.895 | -2018.2339
2024-09-30 09:00 | -7321.83 | 6.8587 | 39.5396 | 53.895 | -2145.8166
2024-10-01 10:00 | -6850.77 | 6.8587 | 39.8325 | 53.895 | -2007.7625
2024-10-02 11:00 | -5916.85 | 6.8587 | 40.5009 | 53.895 | -1734.0576
2024-10-03 12:00 | -5329.36 | 6.8587 | 41.0426 | 53.895 | -1561.8812
2024-10-04 13:00 | -3392.32 | 6.8587 | 42.4948 | 53.895 | -994.1909
2024-10-05 14:00 | -2607.72 | 6.8587 | 43.326 | 53.895 | -764.2473
2024-10-06 15:00 | -2453.99 | 6.8587 | 43.7094 | 53.895 | -719.1935
2024-10-07 16:00 | -2473.99 | 6.8587 | 43.8795 | 53.895 | -725.0549
2024-10-08 17:00 | -1591.71 | 5.6641 | 44.3792 | 53.895 | -466.4842
2024-10-09 18:00 | -2889.56 | 6.8587 | 43.9572 | 53.895 | -846.8464
2024-10-10 19:00 | -3913.03 | 6.8587 | 43.2465 | 53.895 | -1146.7959
2024-10-11 20:00 | -4593.52 | 6.8587 | 42.6631 | 53.895 | -1346.2278
2024-10-12 21:00 | -4966.99 | 6.8587 | 42.3092 | 53.895 | -1455.6811
2024-10-13 22:00 | -5211.3 | 6.8587 | 42.0657 | 53.895 | -1527.2813
2024-10-14 23:00 | -5548.12 | 6.8587 | 41.7451 | 53.895 | -1625.9935
2024-10-16 | -7086.62 | 6.8587 | 40.6145 | 53.895 | -2076.8833
2024-10-17 01:00 | -7115.02 | 6.8587 | 40.3544 | 53.895 | -2085.2065
2024-10-18 02:00 | -7558.25 | 6.8587 | 39.9061 | 53.895 | -2215.1044
2024-10-19 03:00 | -7607.27 | 6.8587 | 39.7291 | 53.895 | -2229.4708
2024-10-20 04:00 | -7362.09 | 6.8587 | 39.7765 | 53.895 | -2157.6156
2024-10-21 05:00 | -7281.48 | 6.8587 | 39.7591 | 53.895 | -2133.9911
2024-10-22 06:00 | -7088.61 | 6.8587 | 39.863 | 53.895 | -2077.4665
2024-10-23 07:00 | -7071.02 | 6.8587 | 39.8621 | 53.895 | -2072.3114
2024-10-24 08:00 | -6687.24 | 6.8587 | 40.1089 | 53.895 | -1959.8366
2024-10-25 09:00 | -6743.54 | 6.8587 | 40.1046 | 53.895 | -1976.3365
2024-10-26 10:00 | -6762.26 | 6.8587 | 40.0919 | 53.895 | -1981.8228
2024-10-27 11:00 | -6304.49 | 6.8587 | 40.3893 | 53.895 | -1847.6636
2024-10-28 12:00 | -5439.14 | 6.8587 | 41.0323 | 53.895 | -1594.0546
2024-10-29 13:00 | -4914.41 | 6.8587 | 41.5131 | 53.895 | -1440.2714
2024-10-30 14:00 | -4717.01 | 6.8587 | 41.7709 | 53.895 | -1382.4192
2024-10-31 15:00 | -4322.31 | 6.8587 | 42.1319 | 53.895 | -1266.744
2024-11-01 16:00 | -3379.82 | 6.8587 | 42.886 | 53.895 | -990.5275
2024-11-02 17:00 | -3303.99 | 6.8587 | 43.1197 | 53.895 | -968.3039
2024-11-03 18:00 | -3143.07 | 6.8587 | 43.3511 | 53.895 | -921.1429
2024-11-04 19:00 | -3632.78 | 6.8587 | 43.1227 | 53.895 | -1064.6627
2024-11-05 20:00 | -3872.07 | 6.8587 | 42.9921 | 53.895 | -1134.7917
2024-11-06 21:00 | -4652.82 | 6.8587 | 42.4787 | 53.895 | -1363.6069
2024-11-07 22:00 | -4771.56 | 6.8587 | 42.3329 | 53.895 | -1398.4062
2024-11-08 23:00 | -5176.37 | 6.8587 | 42.0217 | 53.895 | -1517.0443
2024-11-10 | -5277.91 | 6.8587 | 41.9 | 53.895 | -1546.8027
2024-11-11 01:00 | -5248.7 | 6.8587 | 41.8863 | 53.895 | -1538.2421
2024-11-12 02:00 | -5227.94 | 6.8587 | 41.8943 | 53.895 | -1532.158
2024-11-13 03:00 | -5209.49 | 6.8587 | 41.9175 | 53.895 | -1526.7508
2024-11-14 04:00 | -4963.39 | 6.8587 | 42.0887 | 53.895 | -1454.626
2024-11-15 05:00 | -4781.04 | 6.8587 | 42.252 | 53.895 | -1401.1845
2024-11-16 06:00 | -4294.39 | 6.8587 | 42.6314 | 53.895 | -1258.5615
2024-11-17 07:00 | -4069.3 | 6.8587 | 42.8762 | 53.895 | -1192.5941
2024-11-18 08:00 | -3635.85 | 6.8587 | 43.2567 | 53.895 | -1065.5624
2024-11-19 09:00 | -3867.15 | 6.8587 | 43.2169 | 53.895 | -1133.3498
2024-11-20 10:00 | -3367.69 | 6.8587 | 43.6107 | 53.895 | -986.9725
2024-11-21 11:00 | -2825.5 | 6.8587 | 44.0878 | 53.895 | -828.0723
2024-11-22 12:00 | -2393.43 | 6.8587 | 44.5209 | 53.895 | -701.4451
2024-11-23 13:00 | -1550.17 | 5.4579 | 44.955 | 53.895 | -454.31
2024-11-24 14:00 | -1623.93 | 5.8461 | 45.168 | 53.895 | -475.9269
2024-11-25 15:00 | -1317.77 | 4.703 | 45.2746 | 53.895 | -386.2003
2024-11-26 16:00 | -570.161 | 2.1996 | 45.4872 | 53.895 | -167.0977
2024-11-27 17:00 | -286.218 | 1.4952 | 45.9861 | 53.895 | -83.8822
2024-11-28 18:00 | -521.652 | 2.3826 | 46.0165 | 53.895 | -152.8811
2024-11-29 19:00 | -1211.26 | 4.6866 | 45.9115 | 53.895 | -354.9853
2024-11-30 20:00 | -1700.82 | 6.1509 | 45.8253 | 53.895 | -498.4611
2024-12-01 21:00 | -2865.45 | 6.8587 | 45.1453 | 53.895 | -839.7805
2024-12-02 22:00 | -3248.57 | 6.8587 | 44.7488 | 53.895 | -952.0619
2024-12-03 23:00 | -4456.19 | 6.8587 | 43.809 | 53.895 | -1305.9804
2024-12-05 | -4559.78 | 6.8587 | 43.5368 | 53.895 | -1336.3396
2024-12-06 01:00 | -4856.29 | 6.8587 | 43.2006 | 53.895 | -1423.2381
2024-12-07 02:00 | -5016.18 | 6.8587 | 42.9764 | 53.895 | -1470.0972
2024-12-08 03:00 | -5458.59 | 6.8587 | 42.5784 | 53.895 | -1599.7548
2024-12-09 04:00 | -5302.25 | 6.8587 | 42.5513 | 53.895 | -1553.9361
2024-12-10 05:00 | -5226.72 | 6.8587 | 42.5378 | 53.895 | -1531.8004
2024-12-11 06:00 | -4665.25 | 6.8587 | 42.8738 | 53.895 | -1367.2498
2024-12-12 07:00 | -4728.92 | 6.8587 | 42.8538 | 53.895 | -1385.9096
2024-12-13 08:00 | -4603.26 | 6.8587 | 42.9276 | 53.895 | -1349.0823
2024-12-14 09:00 | -4769.88 | 6.8587 | 42.8258 | 53.895 | -1397.9138
2024-12-15 10:00 | -4142.25 | 6.8587 | 43.2409 | 53.895 | -1213.9736
2024-12-16 11:00 | -2513.5 | 6.8587 | 44.4319 | 53.895 | -736.6341
2024-12-17 12:00 | -972.925 | 3.3936 | 45.0358 | 53.895 | -285.1362
2024-12-18 13:00 | 256.284 | 1 | 46.66 | 53.895 | 75.1094
2024-12-19 14:00 | 2685.56 | 1 | 46.5865 | 53.895 | 787.0599
2024-12-20 15:00 | 2936.84 | 1 | 47.0775 | 53.895 | 860.7028
2024-12-21 16:00 | 2958.8 | 1 | 68.9272 | 53.895 | 867.1387
2024-12-22 17:00 | 2747.52 | 1 | 47.7341 | 53.895 | 805.2186
2024-12-23 18:00 | -544.691 | 2.564 | 47.3976 | 53.895 | -159.6332
2024-12-24 19:00 | -1644.98 | 6.0957 | 46.8995 | 53.895 | -482.096
2024-12-25 20:00 | -2583.3 | 6.8587 | 46.1604 | 53.895 | -757.0905
2024-12-26 21:00 | -3863.21 | 6.8587 | 45.0955 | 53.895 | -1132.1951
2024-12-27 22:00 | -4273.77 | 6.8587 | 44.5452 | 53.895 | -1252.5183
2024-12-28 23:00 | -5414.03 | 6.8587 | 43.5359 | 53.895 | -1586.6956
2024-12-30 | -6077.7 | 6.8587 | 42.8273 | 53.895 | -1781.198
2024-12-31 01:00 | -6488.19 | 6.8587 | 42.2939 | 53.895 | -1901.5008
2025-01-01 02:00 | -6790.88 | 6.8587 | 41.8492 | 53.895 | -1990.2105
2025-01-02 03:00 | -6946.66 | 6.8587 | 41.5362 | 53.895 | -2035.8651
2025-01-03 04:00 | -6855.18 | 6.8587 | 41.4093 | 53.895 | -2009.0549
2025-01-04 05:00 | -6843.85 | 6.8587 | 41.2821 | 53.895 | -2005.7344
2025-01-05 06:00 | -6562.17 | 6.8587 | 41.3856 | 53.895 | -1923.1822
2025-01-06 07:00 | -6290.57 | 6.8587 | 41.5329 | 53.895 | -1843.5841
2025-01-07 08:00 | -6034.28 | 6.8587 | 41.7012 | 53.895 | -1768.4729
2025-01-08 09:00 | -6379.73 | 6.8587 | 41.4843 | 53.895 | -1869.7143
2025-01-09 10:00 | -5947.33 | 6.8587 | 41.7326 | 53.895 | -1742.9904
2025-01-10 11:00 | -5685.4 | 6.8587 | 41.9281 | 53.895 | -1666.2263
2025-01-11 12:00 | -4994.5 | 6.8587 | 42.4296 | 53.895 | -1463.7435
2025-01-12 13:00 | -4865.77 | 6.8587 | 42.5919 | 53.895 | -1426.0164
2025-01-13 14:00 | -4912.18 | 6.8587 | 42.5898 | 53.895 | -1439.6178
2025-01-14 15:00 | -4742.64 | 6.8587 | 42.708 | 53.895 | -1389.9306
2025-01-15 16:00 | -4006.7 | 6.8587 | 43.2218 | 53.895 | -1174.2479
2025-01-16 17:00 | -4087.29 | 6.8587 | 43.254 | 53.895 | -1197.8665
2025-01-17 18:00 | -4152.25 | 6.8587 | 43.2453 | 53.895 | -1216.9044
2025-01-18 19:00 | -4629.56 | 6.8587 | 42.931 | 53.895 | -1356.7901
2025-01-19 20:00 | -4873.25 | 6.8587 | 42.7286 | 53.895 | -1428.2086
2025-01-20 21:00 | -5790.77 | 6.8587 | 42.0722 | 53.895 | -1697.1072
2025-01-21 22:00 | -6112.48 | 6.8587 | 41.7206 | 53.895 | -1791.3911
2025-01-22 23:00 | -6942.53 | 6.8587 | 41.0449 | 53.895 | -2034.6547
2025-01-24 | -7256.79 | 6.8587 | 40.6643 | 53.895 | -2126.7552
2025-01-25 01:00 | -7371.5 | 6.8587 | 40.4471 | 53.895 | -2160.3734
2025-01-26 02:00 | -7381.24 | 6.8587 | 40.3385 | 53.895 | -2163.2279
2025-01-27 03:00 | -7501.1 | 6.8587 | 40.1887 | 53.895 | -2198.3554
2025-01-28 04:00 | -7534.68 | 6.8587 | 40.0848 | 53.895 | -2208.1967
2025-01-29 05:00 | -7279.2 | 6.8587 | 40.1995 | 53.895 | -2133.3229
2025-01-30 06:00 | -6771.9 | 6.8587 | 40.5288 | 53.895 | -1984.648
2025-01-31 07:00 | -6714.82 | 6.8587 | 40.6062 | 53.895 | -1967.9195
2025-02-01 08:00 | -6398.4 | 6.8587 | 40.8339 | 53.895 | -1875.1859
2025-02-02 09:00 | -6503.12 | 6.8587 | 40.8074 | 53.895 | -1905.8763
2025-02-03 10:00 | -6073.91 | 6.8587 | 41.114 | 53.895 | -1780.0873
2025-02-04 11:00 | -5459.49 | 6.8587 | 41.5928 | 53.895 | -1600.0186
2025-02-05 12:00 | -4988.53 | 6.8587 | 42.0147 | 53.895 | -1461.9938
2025-02-06 13:00 | -4891.54 | 6.8587 | 42.1875 | 53.895 | -1433.5689
2025-02-07 14:00 | -4487.47 | 6.8587 | 42.5262 | 53.895 | -1315.1476
2025-02-08 15:00 | -4198.91 | 6.8587 | 42.8173 | 53.895 | -1230.579
2025-02-09 16:00 | -3507 | 6.8587 | 43.3818 | 53.895 | -1027.8002
2025-02-10 17:00 | -3453.87 | 6.8587 | 43.5534 | 53.895 | -1012.2294
2025-02-11 18:00 | -3840.02 | 6.8587 | 43.3794 | 53.895 | -1125.3988
2025-02-12 19:00 | -4676.87 | 6.8587 | 42.828 | 53.895 | -1370.6553
2025-02-13 20:00 | -4973.8 | 6.8587 | 42.5528 | 53.895 | -1457.6769
2025-02-14 21:00 | -5789.99 | 6.8587 | 41.9455 | 53.895 | -1696.8786
2025-02-15 22:00 | -6315.88 | 6.8587 | 41.4607 | 53.895 | -1851.0017
2025-02-16 23:00 | -7181.06 | 6.8587 | 40.7304 | 53.895 | -2104.5609
2025-02-18 | -7702.88 | 6.8587 | 40.1868 | 53.895 | -2257.4913
2025-02-19 01:00 | -7993.54 | 6.8587 | 39.8166 | 53.895 | -2342.6753
2025-02-20 02:00 | -8004.26 | 6.8587 | 39.66 | 53.895 | -2345.817
2025-02-21 03:00 | -7835.38 | 6.8587 | 39.6725 | 53.895 | -2296.3232
2025-02-22 04:00 | -8426.76 | 6.8587 | 39.1971 | 53.895 | -2469.6396
2025-02-23 05:00 | -8299.35 | 6.8587 | 39.1471 | 53.895 | -2432.2994
2025-02-24 06:00 | -8486.5 | 6.8587 | 38.9338 | 53.895 | -2487.1476
2025-02-25 07:00 | -7522.16 | 6.8587 | 39.5132 | 53.895 | -2204.5275
2025-02-26 08:00 | -6756.5 | 6.8587 | 40.0834 | 53.895 | -1980.1347
2025-02-27 09:00 | -6612.63 | 6.8587 | 40.2836 | 53.895 | -1937.9705
2025-02-28 10:00 | -5156.54 | 6.8587 | 41.3442 | 53.895 | -1511.2327
2025-03-01 11:00 | -3459.69 | 6.8587 | 42.7212 | 53.895 | -1013.9351
2025-03-02 12:00 | -2098.32 | 6.8587 | 44.0015 | 53.895 | -614.9569
2025-03-03 13:00 | -1476.17 | 5.2164 | 44.4689 | 53.895 | -432.6227
2025-03-04 14:00 | -1030.22 | 3.7876 | 44.8157 | 53.895 | -301.9277
2025-03-05 15:00 | -872.692 | 3.3828 | 45.1514 | 53.895 | -255.7608
2025-03-06 16:00 | -833.424 | 3.2809 | 45.386 | 53.895 | -244.2525
2025-03-07 17:00 | -383.573 | 1.7126 | 45.6884 | 53.895 | -112.4141
2025-03-08 18:00 | -1336.4 | 5.2056 | 45.7267 | 53.895 | -391.6602
2025-03-09 19:00 | -2221.07 | 6.8587 | 45.4436 | 53.895 | -650.9314
2025-03-10 20:00 | -2947.41 | 6.8587 | 44.8877 | 53.895 | -863.8006
2025-03-11 21:00 | -3438.3 | 6.8587 | 44.4825 | 53.895 | -1007.6663
2025-03-12 22:00 | -3966.46 | 6.8587 | 44.0445 | 53.895 | -1162.4547
2025-03-13 23:00 | -4494.24 | 6.8587 | 43.571 | 53.895 | -1317.1317
2025-03-15 | -6101.55 | 6.8587 | 42.344 | 53.895 | -1788.1878
2025-03-16 01:00 | -6473.59 | 6.8587 | 41.8197 | 53.895 | -1897.2219
2025-03-17 02:00 | -6929.02 | 6.8587 | 41.304 | 53.895 | -2030.6953
2025-03-18 03:00 | -7041.37 | 6.8587 | 41.0448 | 53.895 | -2063.6218
2025-03-19 04:00 | -7195.77 | 6.8587 | 40.7921 | 53.895 | -2108.872
2025-03-20 05:00 | -7418.72 | 6.8587 | 40.4979 | 53.895 | -2174.2122
2025-03-21 06:00 | -7482.28 | 6.8587 | 40.3387 | 53.895 | -2192.8398
2025-03-22 07:00 | -6432.9 | 6.8587 | 40.9638 | 53.895 | -1885.2969
2025-03-23 08:00 | -5519.71 | 6.8587 | 41.6493 | 53.895 | -1617.6673
2025-03-24 09:00 | -5935.27 | 6.8587 | 41.4915 | 53.895 | -1739.4559
2025-03-25 10:00 | -5386.66 | 6.8587 | 41.8608 | 53.895 | -1578.6742
2025-03-26 11:00 | -3682.07 | 6.8587 | 43.0829 | 53.895 | -1079.1082
2025-03-27 12:00 | -3194.3 | 6.8587 | 43.6735 | 53.895 | -936.1569
2025-03-28 13:00 | -2946.48 | 6.8587 | 44.0306 | 53.895 | -863.528
2025-03-29 14:00 | -2808.86 | 6.8587 | 44.2443 | 53.895 | -823.1956
2025-03-30 15:00 | -2999.34 | 6.8587 | 44.2295 | 53.895 | -879.0198
2025-03-31 16:00 | -3363.89 | 6.8587 | 44.0446 | 53.895 | -985.8588
2025-04-01 17:00 | -1940.44 | 6.8587 | 45.0086 | 53.895 | -568.6868
2025-04-02 18:00 | -2412.6 | 6.8587 | 44.8787 | 53.895 | -707.0633
2025-04-03 19:00 | -3027.42 | 6.8587 | 44.5229 | 53.895 | -887.2492
2025-04-04 20:00 | -3235.76 | 6.8587 | 44.3427 | 53.895 | -948.3076
2025-04-05 21:00 | -3136.31 | 6.8587 | 44.4098 | 53.895 | -919.1617
2025-04-06 22:00 | -3034.19 | 6.8587 | 44.5284 | 53.895 | -889.2333
2025-04-07 23:00 | -3015.25 | 6.8587 | 44.5639 | 53.895 | -883.6825
2025-04-09 | -3877.4 | 6.8587 | 44.0064 | 53.895 | -1136.3538
2025-04-10 01:00 | -4056.51 | 6.8587 | 43.8182 | 53.895 | -1188.8457
2025-04-11 02:00 | -4335.21 | 6.8587 | 43.5898 | 53.895 | -1270.5246
2025-04-12 03:00 | -4459.88 | 6.8587 | 43.4688 | 53.895 | -1307.0618
2025-04-13 04:00 | -4434.57 | 6.8587 | 43.4591 | 53.895 | -1299.6442
2025-04-14 05:00 | -4522.61 | 6.8587 | 43.376 | 53.895 | -1325.4462
2025-04-15 06:00 | -4254.83 | 6.8587 | 43.5515 | 53.895 | -1246.9676
2025-04-16 07:00 | -4271.08 | 6.8587 | 43.5707 | 53.895 | -1251.73
2025-04-17 08:00 | -4514.79 | 6.8587 | 43.4209 | 53.895 | -1323.1543
2025-04-18 09:00 | -5522.96 | 6.8587 | 42.713 | 53.895 | -1618.6198
2025-04-19 10:00 | -5391.62 | 6.8587 | 42.6633 | 53.895 | -1580.1278
2025-04-20 11:00 | -5715.6 | 6.8587 | 42.3658 | 53.895 | -1675.077
2025-04-21 12:00 | -5411.88 | 6.8587 | 42.4783 | 53.895 | -1586.0655
2025-04-22 13:00 | -5772.87 | 6.8587 | 42.1838 | 53.895 | -1691.8612
2025-04-23 14:00 | -5564.03 | 6.8587 | 42.2344 | 53.895 | -1630.6562
2025-04-24 15:00 | -5399.07 | 6.8587 | 42.3132 | 53.895 | -1582.3112
2025-04-25 16:00 | -4456.97 | 6.8587 | 42.9438 | 53.895 | -1306.209
2025-04-26 17:00 | -4234.11 | 6.8587 | 43.1823 | 53.895 | -1240.8951
2025-04-27 18:00 | -4610.18 | 6.8587 | 42.9807 | 53.895 | -1351.1104
2025-04-28 19:00 | -4928.17 | 6.8587 | 42.7451 | 53.895 | -1444.3041
2025-04-29 20:00 | -5286.29 | 6.8587 | 42.457 | 53.895 | -1549.2587
2025-04-30 21:00 | -6149.83 | 6.8587 | 41.8152 | 53.895 | -1802.3373
2025-05-01 22:00 | -6631.62 | 6.8587 | 41.3357 | 53.895 | -1943.536
2025-05-02 23:00 | -7775.92 | 6.8587 | 40.399 | 53.895 | -2278.8972
2025-05-04 | -8086.47 | 6.8587 | 39.9576 | 53.895 | -2369.9104
2025-05-05 01:00 | -8392.37 | 6.8587 | 39.5691 | 53.895 | -2459.5609
2025-05-06 02:00 | -8642.25 | 6.8587 | 39.2411 | 53.895 | -2532.7935
2025-05-07 03:00 | -9021.09 | 6.8587 | 38.8362 | 53.895 | -2643.8205
2025-05-08 04:00 | -9516.05 | 6.8587 | 38.3267 | 53.895 | -2788.879
2025-05-09 05:00 | -9822 | 6.8587 | 37.9344 | 53.895 | -2878.544
2025-05-10 06:00 | -9576.88 | 6.8587 | 37.9293 | 53.895 | -2806.7065
2025-05-11 07:00 | -9709.83 | 6.8587 | 37.7342 | 53.895 | -2845.6703
2025-05-12 08:00 | -9595.94 | 6.8587 | 37.6952 | 53.895 | -2812.2924
2025-05-13 09:00 | -9883.35 | 6.8587 | 37.4177 | 53.895 | -2896.524
2025-05-14 10:00 | -8778.21 | 6.8587 | 38.0719 | 53.895 | -2572.6394
2025-05-15 11:00 | -8744.21 | 6.8587 | 38.1558 | 53.895 | -2562.675
2025-05-16 12:00 | -8239.94 | 6.8587 | 38.5102 | 53.895 | -2414.888
2025-05-17 13:00 | -8386.7 | 6.8587 | 38.451 | 53.895 | -2457.8991
2025-05-18 14:00 | -8998.56 | 6.8587 | 38.0229 | 53.895 | -2637.2176
2025-05-19 15:00 | -9003.01 | 6.8587 | 37.9355 | 53.895 | -2638.5218
2025-05-20 16:00 | -8402.77 | 6.8587 | 38.2779 | 53.895 | -2462.6088
2025-05-21 17:00 | -8039.93 | 6.8587 | 38.5497 | 53.895 | -2356.2709
2025-05-22 18:00 | -8091.67 | 6.8587 | 38.5409 | 53.895 | -2371.4344
2025-05-23 19:00 | -8837.6 | 6.8587 | 38.0193 | 53.895 | -2590.0449
2025-05-24 20:00 | -9178.34 | 6.8587 | 37.6874 | 53.895 | -2689.9059
2025-05-25 21:00 | -10248.9 | 6.8587 | 36.861 | 53.895 | -3003.6561
2025-05-26 22:00 | -10565.2 | 6.8587 | 36.4377 | 53.895 | -3096.3545
2025-05-27 23:00 | -11383.2 | 6.8587 | 35.6971 | 53.895 | -3336.0866
2025-05-29 | -11787 | 6.8587 | 35.1885 | 53.895 | -3454.4287
2025-05-30 01:00 | -11915.5 | 6.8587 | 34.8925 | 53.895 | -3492.0883
2025-05-31 02:00 | -12026.1 | 6.8587 | 34.656 | 53.895 | -3524.502
2025-06-01 03:00 | -12056.8 | 6.8587 | 34.5047 | 53.895 | -3533.4993
2025-06-02 04:00 | -11985.7 | 6.8587 | 34.4333 | 53.895 | -3512.6619
2025-06-03 05:00 | -12002.2 | 6.8587 | 34.3307 | 53.895 | -3517.4976
2025-06-04 06:00 | -11392.1 | 6.8587 | 34.6622 | 53.895 | -3338.6949
2025-06-05 07:00 | -10947.6 | 6.8587 | 34.9662 | 53.895 | -3208.4248
2025-06-06 08:00 | -10218 | 6.8587 | 35.4947 | 53.895 | -2994.6002
2025-06-07 09:00 | -9407.72 | 6.8587 | 36.1439 | 53.895 | -2757.1306
2025-06-08 10:00 | -8027.7 | 6.8587 | 37.2272 | 53.895 | -2352.6866
2025-06-09 11:00 | -6060.56 | 6.8587 | 38.8278 | 53.895 | -1776.1748
2025-06-10 12:00 | -5123.28 | 6.8587 | 39.853 | 53.895 | -1501.4852
2025-06-11 13:00 | -4545.31 | 6.8587 | 40.5928 | 53.895 | -1332.0989
2025-06-12 14:00 | -4341.74 | 6.8587 | 41.0251 | 53.895 | -1272.4384
2025-06-13 15:00 | -4132.36 | 6.8587 | 41.4096 | 53.895 | -1211.0752
2025-06-14 16:00 | -3469.97 | 6.8587 | 42.0665 | 53.895 | -1016.9478
2025-06-15 17:00 | -3778.51 | 6.8587 | 42.0792 | 53.895 | -1107.372
2025-06-16 18:00 | -4971.91 | 6.8587 | 41.3821 | 53.895 | -1457.123
2025-06-17 19:00 | -5935.81 | 6.8587 | 40.6775 | 53.895 | -1739.6142
2025-06-18 20:00 | -6812.16 | 6.8587 | 39.9763 | 53.895 | -1996.447
2025-06-19 21:00 | -8123.38 | 6.8587 | 38.9508 | 53.895 | -2380.7277
2025-06-20 22:00 | -8591.86 | 6.8587 | 38.3909 | 53.895 | -2518.0256
2025-06-21 23:00 | -9593.63 | 6.8587 | 37.4978 | 53.895 | -2811.6154
2025-06-23 | -9922.14 | 6.8587 | 37.0268 | 53.895 | -2907.8922
2025-06-24 01:00 | -10233.7 | 6.8587 | 36.6111 | 53.895 | -2999.2014
2025-06-25 02:00 | -10457.1 | 6.8587 | 36.2837 | 53.895 | -3064.6735
2025-06-26 03:00 | -10521.9 | 6.8587 | 36.0911 | 53.895 | -3083.6645
2025-06-27 04:00 | -10678.6 | 6.8587 | 35.8528 | 53.895 | -3129.5887
2025-06-28 05:00 | -10624.1 | 6.8587 | 35.7756 | 53.895 | -3113.6164
2025-06-29 06:00 | -10163.8 | 6.8587 | 36.0107 | 53.895 | -2978.7157
2025-06-30 07:00 | -9800.1 | 6.8587 | 36.2533 | 53.895 | -2872.1258
2025-07-01 08:00 | -8679.56 | 6.8587 | 37.0447 | 53.895 | -2543.7279
2025-07-02 09:00 | -8078.46 | 6.8587 | 37.5987 | 53.895 | -2367.5629
2025-07-03 10:00 | -6302.97 | 6.8587 | 38.9608 | 53.895 | -1847.2182
2025-07-04 11:00 | -4853.48 | 6.8587 | 40.2495 | 53.895 | -1422.4146
2025-07-05 12:00 | -3779 | 6.8587 | 41.3345 | 53.895 | -1107.5156
2025-07-06 13:00 | -3084.1 | 6.8587 | 42.1527 | 53.895 | -903.8605
2025-07-07 14:00 | -2596.43 | 6.8587 | 42.7915 | 53.895 | -760.9385
2025-07-08 15:00 | -2431.81 | 6.8587 | 43.1865 | 53.895 | -712.6932
2025-07-09 16:00 | -1859.66 | 6.7045 | 43.7646 | 53.895 | -545.0125
2025-07-10 17:00 | -2602.47 | 6.8587 | 43.5165 | 53.895 | -762.7087
2025-07-11 18:00 | -3375.74 | 6.8587 | 43.0721 | 53.895 | -989.3317
2025-07-12 19:00 | -4502.4 | 6.8587 | 42.2999 | 53.895 | -1319.5232
2025-07-13 20:00 | -5130.05 | 6.8587 | 41.7765 | 53.895 | -1503.4692
2025-07-14 21:00 | -6223.96 | 6.8587 | 40.9389 | 53.895 | -1824.0626
2025-07-15 22:00 | -6672.15 | 6.8587 | 40.4479 | 53.895 | -1955.4141
2025-07-16 23:00 | -7671.58 | 6.8587 | 39.6082 | 53.895 | -2248.3182
2025-07-18 | -7948.12 | 6.8587 | 39.2062 | 53.895 | -2329.364
2025-07-19 01:00 | -7923.98 | 6.8587 | 39.0622 | 53.895 | -2322.2893
2025-07-20 02:00 | -7946.07 | 6.8587 | 38.946 | 53.895 | -2328.7632
2025-07-21 03:00 | -7778.46 | 6.8587 | 38.9866 | 53.895 | -2279.6416
2025-07-22 04:00 | -7564.95 | 6.8587 | 39.0845 | 53.895 | -2217.068
2025-07-23 05:00 | -7434.13 | 6.8587 | 39.1727 | 53.895 | -2178.7284
2025-07-24 06:00 | -7005.02 | 6.8587 | 39.4752 | 53.895 | -2052.9687
2025-07-25 07:00 | -6863.64 | 6.8587 | 39.6284 | 53.895 | -2011.5343
2025-07-26 08:00 | -6043.58 | 6.8587 | 40.2376 | 53.895 | -1771.1985
2025-07-27 09:00 | -5345.81 | 6.8587 | 40.8489 | 53.895 | -1566.7023
2025-07-28 10:00 | -3850.47 | 6.8587 | 42.0338 | 53.895 | -1128.4614
2025-07-29 11:00 | -2019.6 | 6.8587 | 43.5673 | 53.895 | -591.8863
2025-07-30 12:00 | -982.836 | 3.4659 | 44.0063 | 53.895 | -288.0408
2025-07-31 13:00 | -572.741 | 2.3847 | 44.5797 | 53.895 | -167.8538
2025-08-01 14:00 | 50.603 | 1 | 45.993 | 53.895 | 14.8303
2025-08-02 15:00 | 101.071 | 1 | 46.2802 | 53.895 | 29.621
2025-08-03 16:00 | 2336.77 | 1 | 46.1176 | 53.895 | 684.8397
2025-08-04 17:00 | -62.9744 | 0.96461 | 46.6454 | 53.895 | -18.456
2025-08-05 18:00 | -649.442 | 2.8759 | 45.8949 | 53.895 | -190.3327
2025-08-06 19:00 | -1524.5 | 5.7497 | 45.6974 | 53.895 | -446.7868
2025-08-07 20:00 | -2303.79 | 6.8587 | 45.3329 | 53.895 | -675.1742
2025-08-08 21:00 | -3706.13 | 6.8587 | 44.3087 | 53.895 | -1086.1595
2025-08-09 22:00 | -4320.52 | 6.8587 | 43.6587 | 53.895 | -1266.2194
2025-08-10 23:00 | -5398.71 | 6.8587 | 42.7521 | 53.895 | -1582.2057
2025-08-12 | -6400.4 | 6.8587 | 41.8428 | 53.895 | -1875.7721
2025-08-13 01:00 | -7128.96 | 6.8587 | 41.0856 | 53.895 | -2089.2919
2025-08-14 02:00 | -7607.09 | 6.8587 | 40.5059 | 53.895 | -2229.418
2025-08-15 03:00 | -8024.89 | 6.8587 | 40.0058 | 53.895 | -2351.8631
2025-08-16 04:00 | -8191.41 | 6.8587 | 39.6633 | 53.895 | -2400.6653
2025-08-17 05:00 | -8696.19 | 6.8587 | 39.1515 | 53.895 | -2548.6017
2025-08-18 06:00 | -8954.68 | 6.8587 | 38.7894 | 53.895 | -2624.3576
2025-08-19 07:00 | -7931.17 | 6.8587 | 39.331 | 53.895 | -2324.3965
2025-08-20 08:00 | -6496.56 | 6.8587 | 40.3246 | 53.895 | -1903.9538
2025-08-21 09:00 | -6030.95 | 6.8587 | 40.8046 | 53.895 | -1767.497
2025-08-22 10:00 | -4684.08 | 6.8587 | 41.8343 | 53.895 | -1372.7683
2025-08-23 11:00 | -3304.45 | 6.8587 | 42.9925 | 53.895 | -968.4387
2025-08-24 12:00 | -2110.06 | 6.8587 | 44.1167 | 53.895 | -618.3975
2025-08-25 13:00 | -1548.71 | 5.4713 | 44.5529 | 53.895 | -453.8821
2025-08-26 14:00 | -1015.83 | 3.7037 | 44.8504 | 53.895 | -297.7104
2025-08-27 15:00 | -740.43 | 2.9248 | 45.2005 | 53.895 | -216.9986
2025-08-28 16:00 | -758.2 | 3.0683 | 45.4285 | 53.895 | -222.2065
2025-08-29 17:00 | 0 | 1 | 46.7492 | 53.895 | 0
2025-08-30 18:00 | -941.651 | 3.9652 | 45.8594 | 53.895 | -275.9707
2025-08-31 19:00 | -1879.57 | 6.8587 | 45.7481 | 53.895 | -550.8476
2025-09-01 20:00 | -2774.21 | 6.8587 | 45.0827 | 53.895 | -813.0407
2025-09-02 21:00 | -3381.69 | 6.8587 | 44.5819 | 53.895 | -991.0755
2025-09-03 22:00 | -3860.61 | 6.8587 | 44.1605 | 53.895 | -1131.4331
2025-09-04 23:00 | -4175.69 | 6.8587 | 43.8312 | 53.895 | -1223.7739
2025-09-06 | -5676.71 | 6.8587 | 42.7077 | 53.895 | -1663.6795
2025-09-07 01:00 | -5970.89 | 6.8587 | 42.2716 | 53.895 | -1749.8951
2025-09-08 02:00 | -6280.35 | 6.8587 | 41.893 | 53.895 | -1840.5889
2025-09-09 03:00 | -6499.09 | 6.8587 | 41.6117 | 53.895 | -1904.6953
2025-09-10 04:00 | -6567.18 | 6.8587 | 41.4426 | 53.895 | -1924.6505
2025-09-11 05:00 | -6837.5 | 6.8587 | 41.1479 | 53.895 | -2003.8734
2025-09-12 06:00 | -6697.65 | 6.8587 | 41.1513 | 53.895 | -1962.8875
2025-09-13 07:00 | -5347.15 | 6.8587 | 42.0287 | 53.895 | -1567.095
2025-09-14 08:00 | -3642.67 | 6.8587 | 43.3236 | 53.895 | -1067.5612
2025-09-15 09:00 | -2790.82 | 6.8587 | 44.1762 | 53.895 | -817.9086
2025-09-16 10:00 | -1463.04 | 5.1636 | 44.9907 | 53.895 | -428.7747
2025-09-17 11:00 | -467.772 | 1.7895 | 45.3868 | 53.895 | -137.0904
2025-09-18 12:00 | 2706.28 | 1 | 46.4848 | 53.895 | 793.1324
2025-09-19 13:00 | 2884.72 | 1 | 47.0504 | 53.895 | 845.428
2025-09-20 14:00 | 2875.17 | 1 | 68.3081 | 53.895 | 842.6291
2025-09-21 15:00 | 2911.93 | 1 | 66.0907 | 53.895 | 853.4024
2025-09-22 16:00 | 2918.55 | 1 | 67.8173 | 53.895 | 855.3426
2025-09-23 17:00 | 3647.01 | 1.2268 | 62.544 | 53.895 | 1068.8331
2025-09-24 18:00 | 3085.79 | 1 | 48.328 | 53.895 | 904.3558
2025-09-25 19:00 | 591.755 | 1 | 48.8855 | 53.895 | 173.4263
2025-09-26 20:00 | -479.956 | 2.3265 | 47.8262 | 53.895 | -140.6612
2025-09-27 21:00 | -995.371 | 3.8548 | 47.4065 | 53.895 | -291.7144
2025-09-28 22:00 | -1489.12 | 5.3874 | 47.2066 | 53.895 | -436.418
2025-09-29 23:00 | -1993.28 | 6.8587 | 47.0054 | 53.895 | -584.1727
2025-10-01 | -3496.71 | 6.8587 | 45.8101 | 53.895 | -1024.7845
2025-10-02 01:00 | -3816.24 | 6.8587 | 45.3323 | 53.895 | -1118.4295
2025-10-03 02:00 | -3870.4 | 6.8587 | 45.1164 | 53.895 | -1134.3023
2025-10-04 03:00 | -3801.5 | 6.8587 | 45.0546 | 53.895 | -1114.1097
2025-10-05 04:00 | -3687.8 | 6.8587 | 45.0563 | 53.895 | -1080.7875
2025-10-06 05:00 | -3670.16 | 6.8587 | 45.0101 | 53.895 | -1075.6177
2025-10-07 06:00 | -3318.21 | 6.8587 | 45.2233 | 53.895 | -972.4714
2025-10-08 07:00 | -3008.29 | 6.8587 | 45.4686 | 53.895 | -881.6428
2025-10-09 08:00 | -1925.97 | 6.717 | 46.232 | 53.895 | -564.4461
2025-10-10 09:00 | -2171.35 | 6.8587 | 46.2483 | 53.895 | -636.3599
2025-10-11 10:00 | -1898.61 | 6.5422 | 46.421 | 53.895 | -556.4277
2025-10-12 11:00 | -1750.05 | 6.0414 | 46.4783 | 53.895 | -512.889
2025-10-13 12:00 | -2176.82 | 6.8587 | 46.4029 | 53.895 | -637.963
2025-10-14 13:00 | -2500.47 | 6.8587 | 46.159 | 53.895 | -732.8154
2025-10-15 14:00 | -2315.25 | 6.8587 | 46.2168 | 53.895 | -678.5328
2025-10-16 15:00 | -1944.52 | 6.7125 | 46.4289 | 53.895 | -569.8826
2025-10-17 16:00 | -1322.57 | 4.5342 | 46.444 | 53.895 | -387.607
2025-10-18 17:00 | -814.576 | 3.0248 | 46.6176 | 53.895 | -238.7287
2025-10-19 18:00 | -1077.09 | 4.0947 | 46.7498 | 53.895 | -315.6639
2025-10-20 19:00 | -2057.47 | 6.8587 | 46.6235 | 53.895 | -602.9849
2025-10-21 20:00 | -2732.53 | 6.8587 | 46.0755 | 53.895 | -800.8255
2025-10-22 21:00 | -3647.91 | 6.8587 | 45.3383 | 53.895 | -1069.0969
2025-10-23 22:00 | -4298.53 | 6.8587 | 44.7223 | 53.895 | -1259.7748
2025-10-24 23:00 | -5513.81 | 6.8587 | 43.6994 | 53.895 | -1615.9382
2025-10-26 | -6103.69 | 6.8587 | 43.038 | 53.895 | -1788.815
2025-10-27 01:00 | -6522.93 | 6.8587 | 42.5301 | 53.895 | -1911.6821
2025-10-28 02:00 | -7137.38 | 6.8587 | 41.9181 | 53.895 | -2091.7596
2025-10-29 03:00 | -7410.94 | 6.8587 | 41.5184 | 53.895 | -2171.9321
2025-10-30 04:00 | -7250.66 | 6.8587 | 41.434 | 53.895 | -2124.9587
2025-10-31 05:00 | -7264.22 | 6.8587 | 41.305 | 53.895 | -2128.9327
2025-11-01 06:00 | -7220.53 | 6.8587 | 41.2255 | 53.895 | -2116.1285
2025-11-02 07:00 | -6791.43 | 6.8587 | 41.4251 | 53.895 | -1990.3717
2025-11-03 08:00 | -5914.59 | 6.8587 | 41.9927 | 53.895 | -1733.3952
2025-11-04 09:00 | -5002.9 | 6.8587 | 42.6844 | 53.895 | -1466.2053
2025-11-05 10:00 | -3178.7 | 6.8587 | 44.0523 | 53.895 | -931.585
2025-11-06 11:00 | -1580.32 | 5.5928 | 45.1777 | 53.895 | -463.1461
2025-11-07 12:00 | -642.93 | 2.3446 | 45.5632 | 53.895 | -188.4242
2025-11-08 13:00 | -110.033 | 0.86634 | 46.5777 | 53.895 | -32.2475
2025-11-09 14:00 | 39.4485 | 1 | 47.4452 | 53.895 | 11.5612
2025-11-10 15:00 | 2384.52 | 1 | 47.2649 | 53.895 | 698.8338
2025-11-11 16:00 | 2747.04 | 1 | 47.6427 | 53.895 | 805.078
2025-11-12 17:00 | 2626.67 | 1 | 47.9872 | 53.895 | 769.801
2025-11-13 18:00 | -490.825 | 2.3735 | 47.6626 | 53.895 | -143.8466
2025-11-14 19:00 | -1599.6 | 5.9332 | 47.1762 | 53.895 | -468.7965
2025-11-15 20:00 | -2399.74 | 6.8587 | 46.6288 | 53.895 | -703.2944
2025-11-16 21:00 | -3929.24 | 6.8587 | 45.4162 | 53.895 | -1151.5466
2025-11-17 22:00 | -4746.85 | 6.8587 | 44.5545 | 53.895 | -1391.1644
2025-11-18 23:00 | -6130.88 | 6.8587 | 43.303 | 53.895 | -1796.7836
2025-11-20 | -6807.56 | 6.8587 | 42.5166 | 53.895 | -1995.0989
2025-11-21 01:00 | -6542.86 | 6.8587 | 42.4112 | 53.895 | -1917.523
2025-11-22 02:00 | -6928.94 | 6.8587 | 41.9915 | 53.895 | -2030.6719
2025-11-23 03:00 | -7193.91 | 6.8587 | 41.6227 | 53.895 | -2108.3269
2025-11-24 04:00 | -7266.14 | 6.8587 | 41.3775 | 53.895 | -2129.4954
2025-11-25 05:00 | -6966.65 | 6.8587 | 41.4355 | 53.895 | -2041.7236
2025-11-26 06:00 | -6597.48 | 6.8587 | 41.6366 | 53.895 | -1933.5305
2025-11-27 07:00 | -6054.29 | 6.8587 | 41.9917 | 53.895 | -1774.3372
2025-11-28 08:00 | -4723.06 | 6.8587 | 42.9334 | 53.895 | -1384.1922
2025-11-29 09:00 | -3768.81 | 6.8587 | 43.7599 | 53.895 | -1104.5292
2025-11-30 10:00 | -1948.99 | 6.8587 | 45.2087 | 53.895 | -571.1926
2025-12-01 11:00 | -509.765 | 1.7316 | 45.4898 | 53.895 | -149.3974
2025-12-02 12:00 | 2527.13 | 1 | 46.8305 | 53.895 | 740.6287
2025-12-03 13:00 | 2743.69 | 1 | 47.4053 | 53.895 | 804.0962
2025-12-04 14:00 | 2741.48 | 1 | 64.951 | 53.895 | 803.4485
2025-12-05 15:00 | 3057.14 | 1.0564 | 62.1214 | 53.895 | 895.9593
2025-12-06 16:00 | 3899.76 | 1.3746 | 62.1259 | 53.895 | 1142.9068
2025-12-07 17:00 | 3013.76 | 1.0539 | 62.5559 | 53.895 | 883.2459
2025-12-08 18:00 | 2856.46 | 1 | 48.7594 | 53.895 | 837.1458
2025-12-09 19:00 | 0 | 0 | 49.3611 | 53.895 | 0
2025-12-10 20:00 | -1056.4 | 3.9246 | 47.8773 | 53.895 | -309.6003
2025-12-11 21:00 | -2103.04 | 6.8587 | 47.5027 | 53.895 | -616.3402
2025-12-12 22:00 | -2785.35 | 6.8587 | 46.8183 | 53.895 | -816.3055
2025-12-13 23:00 | -3902.19 | 6.8587 | 45.8532 | 53.895 | -1143.619
2025-12-15 | -4231.03 | 6.8587 | 45.335 | 53.895 | -1239.9925
2025-12-16 01:00 | -4568.56 | 6.8587 | 44.9068 | 53.895 | -1338.9128
2025-12-17 02:00 | -5044.58 | 6.8587 | 44.4195 | 53.895 | -1478.4205
2025-12-18 03:00 | -5088.48 | 6.8587 | 44.2174 | 53.895 | -1491.2863
2025-12-19 04:00 | -5128.08 | 6.8587 | 44.0538 | 53.895 | -1502.8919
2025-12-20 05:00 | -4661.98 | 6.8587 | 44.2802 | 53.895 | -1366.2915
2025-12-21 06:00 | -4303.98 | 6.8587 | 44.5002 | 53.895 | -1261.372
2025-12-22 07:00 | -3696.99 | 6.8587 | 44.9429 | 53.895 | -1083.4808
2025-12-23 08:00 | -2355.88 | 6.8587 | 45.9396 | 53.895 | -690.4403
2025-12-24 09:00 | -1461.43 | 5.023 | 46.3901 | 53.895 | -428.3029
2025-12-25 10:00 | 0 | 1 | 47.9767 | 53.895 | 0
2025-12-26 11:00 | 2681.98 | 1 | 47.8199 | 53.895 | 786.0107
2025-12-27 12:00 | 3628.24 | 1.202 | 62.9843 | 53.895 | 1063.3322
2025-12-28 13:00 | 4836.44 | 1.5638 | 63.6978 | 53.895 | 1417.4206
2025-12-29 14:00 | 5397.31 | 1.7835 | 63.7998 | 53.895 | 1581.7954
2025-12-30 15:00 | 5737.79 | 1.855 | 64.4819 | 53.895 | 1681.5803
2025-12-31 16:00 | 6624.07 | 2.1761 | 64.5563 | 53.895 | 1941.3233
2026-01-01 17:00 | 5832.26 | 1.9068 | 64.9557 | 53.895 | 1709.2667
2026-01-02 18:00 | 4396.74 | 1.4442 | 65.054 | 53.895 | 1288.5573
2026-01-03 19:00 | 2980.56 | 1 | 69.336 | 53.895 | 873.5159
2026-01-04 20:00 | 2939.3 | 1 | 50.1571 | 53.895 | 861.4238
2026-01-05 21:00 | -410.17 | 2.0207 | 49.7134 | 53.895 | -120.209
2026-01-06 22:00 | -915.641 | 3.5321 | 49.053 | 53.895 | -268.3479
2026-01-07 23:00 | -2115.41 | 6.8587 | 48.5396 | 53.895 | -619.9655
2026-01-09 | -2709.12 | 6.8587 | 47.8551 | 53.895 | -793.9647
2026-01-10 01:00 | -2934.3 | 6.8587 | 47.445 | 53.895 | -859.9584
2026-01-11 02:00 | -2988.56 | 6.8587 | 47.191 | 53.895 | -875.8605
2026-01-12 03:00 | -3016.81 | 6.8587 | 47.0454 | 53.895 | -884.1397
2026-01-13 04:00 | -3004.82 | 6.8587 | 46.9352 | 53.895 | -880.6258
2026-01-14 05:00 | -3007.42 | 6.8587 | 46.8495 | 53.895 | -881.3878
2026-01-15 06:00 | -2442.76 | 6.8587 | 47.1754 | 53.895 | -715.9023
2026-01-16 07:00 | -2051.45 | 6.8587 | 47.467 | 53.895 | -601.2206
2026-01-17 08:00 | -1230.56 | 4.1337 | 47.503 | 53.895 | -360.6415
2026-01-18 09:00 | -466.686 | 1.848 | 47.8378 | 53.895 | -136.7722
2026-01-19 10:00 | 2751.99 | 1 | 48.714 | 53.895 | 806.5287
2026-01-20 11:00 | 3917.03 | 1.2682 | 64.1958 | 53.895 | 1147.9682
2026-01-21 12:00 | 5250.23 | 1.7082 | 64.4855 | 53.895 | 1538.6905
2026-01-22 13:00 | 6479.03 | 2.1379 | 64.6897 | 53.895 | 1898.8163
2026-01-23 14:00 | 6780.27 | 2.2467 | 65.0664 | 53.895 | 1987.101
2026-01-24 15:00 | 6426.68 | 2.1359 | 65.3766 | 53.895 | 1883.474
2026-01-25 16:00 | 7590.45 | 2.5322 | 65.4969 | 53.895 | 2224.5413
2026-01-26 17:00 | 6955.93 | 2.2424 | 66.3023 | 53.895 | 2038.5818
2026-01-27 18:00 | 5653.16 | 1.807 | 66.5923 | 53.895 | 1656.7777
2026-01-28 19:00 | 3749.28 | 1.2122 | 66.4177 | 53.895 | 1098.8055
2026-01-29 20:00 | 3045.65 | 1 | 71.0794 | 53.895 | 892.5919
2026-01-30 21:00 | 0 | 0 | 51.6517 | 53.895 | 0
2026-01-31 22:00 | -543.708 | 2.0717 | 49.9808 | 53.895 | -159.3451
2026-02-01 23:00 | -1737.46 | 6.2081 | 49.5916 | 53.895 | -509.1993
2026-02-03 | -2531.43 | 6.8587 | 48.8556 | 53.895 | -741.8889
2026-02-04 01:00 | -3012.34 | 6.8587 | 48.2177 | 53.895 | -882.8297
2026-02-05 02:00 | -3480.56 | 6.8587 | 47.6208 | 53.895 | -1020.0514
2026-02-06 03:00 | -3720.64 | 6.8587 | 47.2389 | 53.895 | -1090.4119
2026-02-07 04:00 | -3954.05 | 6.8587 | 46.8697 | 53.895 | -1158.8177
2026-02-08 05:00 | -4186.84 | 6.8587 | 46.5291 | 53.895 | -1227.0417
2026-02-09 06:00 | -4280.79 | 6.8587 | 46.2997 | 53.895 | -1254.5757
2026-02-10 07:00 | -2956.34 | 6.8587 | 47.0745 | 53.895 | -866.4177
2026-02-11 08:00 | -1267.13 | 4.2803 | 47.7588 | 53.895 | -371.3591
2026-02-12 09:00 | -620.784 | 2.3394 | 48.1281 | 53.895 | -181.9338
2026-02-13 10:00 | 2332.31 | 1 | 49.1445 | 53.895 | 683.5326
2026-02-14 11:00 | 4000.62 | 1.3255 | 64.1846 | 53.895 | 1172.466
2026-02-15 12:00 | 5361.91 | 1.815 | 64.307 | 53.895 | 1571.4207
2026-02-16 13:00 | 5265.98 | 1.7963 | 64.6386 | 53.895 | 1543.3064
2026-02-17 14:00 | 5698.13 | 1.9272 | 65.024 | 53.895 | 1669.9571
2026-02-18 15:00 | 5865.9 | 1.9137 | 65.8038 | 53.895 | 1719.1256
2026-02-19 16:00 | 5371.27 | 1.7665 | 65.8933 | 53.895 | 1574.1638
2026-02-20 17:00 | 7031.82 | 2.3215 | 65.9282 | 53.895 | 2060.823
2026-02-21 18:00 | 5187.89 | 1.6885 | 66.4487 | 53.895 | 1520.4205
2026-02-22 19:00 | 3149.07 | 1.0417 | 66.2376 | 53.895 | 922.9013
2026-02-23 20:00 | 2943.1 | 1 | 51.3471 | 53.895 | 862.5375
2026-02-24 21:00 | 0 | 1 | 51.7959 | 53.895 | 0
2026-02-25 22:00 | -565.845 | 2.5177 | 50.3712 | 53.895 | -165.8328
2026-02-26 23:00 | -1459.02 | 5.2291 | 49.7987 | 53.895 | -427.5966
2026-02-28 | -3677.13 | 6.8587 | 48.3167 | 53.895 | -1077.6604
2026-03-01 01:00 | -5005.46 | 6.8587 | 46.9631 | 53.895 | -1466.9555
2026-03-02 02:00 | -6132.83 | 6.8587 | 45.7265 | 53.895 | -1797.3551
2026-03-03 03:00 | -7181.1 | 6.8587 | 44.6025 | 53.895 | -2104.5727
2026-03-04 04:00 | -7642.18 | 6.8587 | 43.8679 | 53.895 | -2239.7019
2026-03-05 05:00 | -7969.12 | 6.8587 | 43.2603 | 53.895 | -2335.5185
2026-03-06 06:00 | -7492.88 | 6.8587 | 43.2834 | 53.895 | -2195.9464
2026-03-07 07:00 | -7014.6 | 6.8587 | 43.4395 | 53.895 | -2055.7763
2026-03-08 08:00 | -7295.38 | 6.8587 | 43.1321 | 53.895 | -2138.0648
2026-03-09 09:00 | -6255.3 | 6.8587 | 43.7002 | 53.895 | -1833.2475
2026-03-10 10:00 | -5747.36 | 6.8587 | 44.0222 | 53.895 | -1684.3849
2026-03-11 11:00 | -5048.11 | 6.8587 | 44.4938 | 53.895 | -1479.455
2026-03-12 12:00 | -4415.36 | 6.8587 | 44.9455 | 53.895 | -1294.0143
2026-03-13 13:00 | -3605.47 | 6.8587 | 45.5454 | 53.895 | -1056.659
2026-03-14 14:00 | -3489.15 | 6.8587 | 45.7304 | 53.895 | -1022.5689
2026-03-15 15:00 | -3348.68 | 6.8587 | 45.8728 | 53.895 | -981.4012
2026-03-16 16:00 | -2246.27 | 6.8587 | 46.6523 | 53.895 | -658.3168
2026-03-17 17:00 | -2531.2 | 6.8587 | 46.5913 | 53.895 | -741.8215
2026-03-18 18:00 | -3041.49 | 6.8587 | 46.2748 | 53.895 | -891.3727
2026-03-19 19:00 | -3749.62 | 6.8587 | 45.7379 | 53.895 | -1098.9051
2026-03-20 20:00 | -4591.95 | 6.8587 | 45.0614 | 53.895 | -1345.7677
2026-03-21 21:00 | -4901.71 | 6.8587 | 44.7085 | 53.895 | -1436.5494
2026-03-22 22:00 | -5326.17 | 6.8587 | 44.2824 | 53.895 | -1560.9463
2026-03-23 23:00 | -6896.22 | 6.8587 | 43.0689 | 53.895 | -2021.0826
2026-03-25 | -7339.52 | 6.8587 | 42.4812 | 53.895 | -2151.001
2026-03-26 01:00 | -7799.19 | 6.8587 | 41.9384 | 53.895 | -2285.717
2026-03-27 02:00 | -8046.78 | 6.8587 | 41.58 | 53.895 | -2358.2784
2026-03-28 03:00 | -8165.17 | 6.8587 | 41.3288 | 53.895 | -2392.9751
2026-03-29 04:00 | -8302.04 | 6.8587 | 41.0783 | 53.895 | -2433.0877
2026-03-30 05:00 | -7989.3 | 6.8587 | 41.1708 | 53.895 | -2341.4327
2026-03-31 06:00 | -8109.2 | 6.8587 | 41.0286 | 53.895 | -2376.5719
2026-04-01 07:00 | -8118.67 | 6.8587 | 40.9435 | 53.895 | -2379.3473
2026-04-02 08:00 | -7940.41 | 6.8587 | 40.9905 | 53.895 | -2327.1045
2026-04-03 09:00 | -6993.78 | 6.8587 | 41.5887 | 53.895 | -2049.6746
2026-04-04 10:00 | -6443.82 | 6.8587 | 42.0183 | 53.895 | -1888.4972
2026-04-05 11:00 | -5152.96 | 6.8587 | 42.9663 | 53.895 | -1510.1835
2026-04-06 12:00 | -5544.25 | 6.8587 | 42.8602 | 53.895 | -1624.8593
2026-04-07 13:00 | -5762.45 | 6.8587 | 42.7368 | 53.895 | -1688.8074
2026-04-08 14:00 | -5877.24 | 6.8587 | 42.6334 | 53.895 | -1722.449
2026-04-09 15:00 | -4477.78 | 6.8587 | 43.5574 | 53.895 | -1312.3078
2026-04-10 16:00 | -4347.92 | 6.8587 | 43.7837 | 53.895 | -1274.2496
2026-04-11 17:00 | -4525.31 | 6.8587 | 43.713 | 53.895 | -1326.2374
2026-04-12 18:00 | -5359.55 | 6.8587 | 43.1386 | 53.895 | -1570.7291
2026-04-13 19:00 | -6044.38 | 6.8587 | 42.5843 | 53.895 | -1771.4329
2026-04-14 20:00 | -7076.12 | 6.8587 | 41.7617 | 53.895 | -2073.8061
2026-04-15 21:00 | -7511.31 | 6.8587 | 41.2557 | 53.895 | -2201.3477
2026-04-16 22:00 | -8438.82 | 6.8587 | 40.4296 | 53.895 | -2473.174
2026-04-17 23:00 | -8990.08 | 6.8587 | 39.8025 | 53.895 | -2634.7324
2026-04-19 | -8994.13 | 6.8587 | 39.5767 | 53.895 | -2635.9193
2026-04-20 01:00 | -9389.32 | 6.8587 | 39.1635 | 53.895 | -2751.7381
2026-04-21 02:00 | -9475.33 | 6.8587 | 38.9572 | 53.895 | -2776.9451
2026-04-22 03:00 | -9247.4 | 6.8587 | 38.9752 | 53.895 | -2710.1454
2026-04-23 04:00 | -9204.89 | 6.8587 | 38.9316 | 53.895 | -2697.687
2026-04-24 05:00 | -9221.17 | 6.8587 | 38.8559 | 53.895 | -2702.4582
2026-04-25 06:00 | -9327.58 | 6.8587 | 38.7137 | 53.895 | -2733.6439
2026-04-26 07:00 | -8582.53 | 6.8587 | 39.1561 | 53.895 | -2515.2913
2026-04-27 08:00 | -7952.05 | 6.8587 | 39.6307 | 53.895 | -2330.5158
2026-04-28 09:00 | -7187.95 | 6.8587 | 40.2314 | 53.895 | -2106.5802
2026-04-29 10:00 | -6742.74 | 6.8587 | 40.6522 | 53.895 | -1976.102
2026-04-30 11:00 | -6248.08 | 6.8587 | 41.0976 | 53.895 | -1831.1315
2026-05-01 12:00 | -5940.88 | 6.8587 | 41.4295 | 53.895 | -1741.1001
2026-05-02 13:00 | -6054.34 | 6.8587 | 41.4572 | 53.895 | -1774.3519
2026-05-03 14:00 | -6005.48 | 6.8587 | 41.5377 | 53.895 | -1760.0324
2026-05-04 15:00 | -5263.14 | 6.8587 | 42.071 | 53.895 | -1542.4741
2026-05-05 16:00 | -4633.78 | 6.8587 | 42.6058 | 53.895 | -1358.0269
2026-05-06 17:00 | -4584.63 | 6.8587 | 42.7725 | 53.895 | -1343.6224
2026-05-07 18:00 | -5216.73 | 6.8587 | 42.4242 | 53.895 | -1528.8726
2026-05-08 19:00 | -5807.39 | 6.8587 | 42.0059 | 53.895 | -1701.978
2026-05-09 20:00 | -7045.36 | 6.8587 | 41.1023 | 53.895 | -2064.7912
2026-05-10 21:00 | -7843.04 | 6.8587 | 40.3797 | 53.895 | -2298.5681
2026-05-11 22:00 | -8803.67 | 6.8587 | 39.5177 | 53.895 | -2580.101
2026-05-12 23:00 | -9212.42 | 6.8587 | 38.9977 | 53.895 | -2699.8938
2026-05-14 | -9494.05 | 6.8587 | 38.6027 | 53.895 | -2782.4314
2026-05-15 01:00 | -9746.63 | 6.8587 | 38.2618 | 53.895 | -2856.4553
2026-05-16 02:00 | -9800.07 | 6.8587 | 38.0813 | 53.895 | -2872.117
2026-05-17 03:00 | -9795.76 | 6.8587 | 37.9648 | 53.895 | -2870.8539
2026-05-18 04:00 | -9789.08 | 6.8587 | 37.8751 | 53.895 | -2868.8961
2026-05-19 05:00 | -9088.75 | 6.8587 | 38.2725 | 53.895 | -2663.6497
2026-05-20 06:00 | -9081.43 | 6.8587 | 38.2951 | 53.895 | -2661.5044
2026-05-21 07:00 | -8849.87 | 6.8587 | 38.44 | 53.895 | -2593.6409
2026-05-22 08:00 | -9279.42 | 6.8587 | 38.1449 | 53.895 | -2719.5295
2026-05-23 09:00 | -8225.97 | 6.8587 | 38.803 | 53.895 | -2410.7938
2026-05-24 10:00 | -7572.7 | 6.8587 | 39.3364 | 53.895 | -2219.3393
2026-05-25 11:00 | -6040.74 | 6.8587 | 40.4932 | 53.895 | -1770.3661
2026-05-26 12:00 | -5551.12 | 6.8587 | 41.0583 | 53.895 | -1626.8727
2026-05-27 13:00 | -4638.91 | 6.8587 | 41.8717 | 53.895 | -1359.5303
2026-05-28 14:00 | -3859.3 | 6.8587 | 42.6433 | 53.895 | -1131.0492
2026-05-29 15:00 | -2371.58 | 6.8587 | 43.903 | 53.895 | -695.0415
2026-05-30 16:00 | -2497.34 | 6.8587 | 44.1559 | 53.895 | -731.8981
2026-05-31 17:00 | -2922.17 | 6.8587 | 44.045 | 53.895 | -856.4035
2026-06-01 18:00 | -4257.71 | 6.8587 | 43.2166 | 53.895 | -1247.8116
2026-06-02 19:00 | -5179.58 | 6.8587 | 42.517 | 53.895 | -1517.9851
2026-06-03 20:00 | -6430.18 | 6.8587 | 41.5576 | 53.895 | -1884.4997
2026-06-04 21:00 | -7036.32 | 6.8587 | 40.9414 | 53.895 | -2062.1418
2026-06-05 22:00 | -8046.04 | 6.8587 | 40.0715 | 53.895 | -2358.0616
2026-06-06 23:00 | -8198.4 | 6.8587 | 39.7328 | 53.895 | -2402.7139
2026-06-08 | -8155.97 | 6.8587 | 39.6096 | 53.895 | -2390.2789
2026-06-09 01:00 | -8441.08 | 6.8587 | 39.3205 | 53.895 | -2473.8363
2026-06-10 02:00 | -8325.63 | 6.8587 | 39.2931 | 53.895 | -2440.0013
2026-06-11 03:00 | -8223.45 | 6.8587 | 39.2835 | 53.895 | -2410.0553
2026-06-12 04:00 | -8113.05 | 6.8587 | 39.3183 | 53.895 | -2377.7002
2026-06-13 05:00 | -7350.93 | 6.8587 | 39.8101 | 53.895 | -2154.3449
2026-06-14 06:00 | -7223.6 | 6.8587 | 39.9652 | 53.895 | -2117.0282
2026-06-15 07:00 | -7097.66 | 6.8587 | 40.1025 | 53.895 | -2080.1188
2026-06-16 08:00 | -7269.82 | 6.8587 | 40.0308 | 53.895 | -2130.5739
2026-06-17 09:00 | -6908.68 | 6.8587 | 40.2878 | 53.895 | -2024.7342
2026-06-18 10:00 | -6197.92 | 6.8587 | 40.8369 | 53.895 | -1816.431
2026-06-19 11:00 | -5636.05 | 6.8587 | 41.3341 | 53.895 | -1651.7632
2026-06-20 12:00 | -5069.16 | 6.8587 | 41.8466 | 53.895 | -1485.6241
2026-06-21 13:00 | -4594.09 | 6.8587 | 42.31 | 53.895 | -1346.3949
2026-06-22 14:00 | -4101.42 | 6.8587 | 42.7956 | 53.895 | -1202.0075
2026-06-23 15:00 | -2491.21 | 6.8587 | 44.0474 | 53.895 | -730.1016
2026-06-24 16:00 | -2125.07 | 6.8587 | 44.5877 | 53.895 | -622.7965
2026-06-25 17:00 | -2158.32 | 6.8587 | 44.7836 | 53.895 | -632.5412
2026-06-26 18:00 | -2870.75 | 6.8587 | 44.4372 | 53.895 | -841.3338
2026-06-27 19:00 | -3603.79 | 6.8587 | 43.976 | 53.895 | -1056.1666
2026-06-28 20:00 | -4895.52 | 6.8587 | 43.0814 | 53.895 | -1434.7353
2026-06-29 21:00 | -5297.27 | 6.8587 | 42.6647 | 53.895 | -1552.4766
2026-06-30 22:00 | -6397.84 | 6.8587 | 41.8031 | 53.895 | -1875.0218
2026-07-01 23:00 | -6579.65 | 6.8587 | 41.4945 | 53.895 | -1928.3051
2026-07-03 | -6778.61 | 6.8587 | 41.2328 | 53.895 | -1986.6145
2026-07-04 01:00 | -6826.25 | 6.8587 | 41.1074 | 53.895 | -2000.5764
2026-07-05 02:00 | -6944.32 | 6.8587 | 40.966 | 53.895 | -2035.1793
2026-07-06 03:00 | -6639.02 | 6.8587 | 41.1004 | 53.895 | -1945.7047
2026-07-07 04:00 | -6278.16 | 6.8587 | 41.3379 | 53.895 | -1839.9471
2026-07-08 05:00 | -5949.11 | 6.8587 | 41.5841 | 53.895 | -1743.512
2026-07-09 06:00 | -5832.83 | 6.8587 | 41.7076 | 53.895 | -1709.4337
2026-07-10 07:00 | -5717.71 | 6.8587 | 41.8228 | 53.895 | -1675.6954
2026-07-11 08:00 | -6072.31 | 6.8587 | 41.6302 | 53.895 | -1779.6184
2026-07-12 09:00 | -5909.7 | 6.8587 | 41.7292 | 53.895 | -1731.9621
2026-07-13 10:00 | -5658.61 | 6.8587 | 41.9207 | 53.895 | -1658.3749
2026-07-14 11:00 | -5250.72 | 6.8587 | 42.2378 | 53.895 | -1538.8341
2026-07-15 12:00 | -4340.44 | 6.8587 | 42.927 | 53.895 | -1272.0574
2026-07-16 13:00 | -4398.75 | 6.8587 | 43.0291 | 53.895 | -1289.1464
2026-07-17 14:00 | -3496.93 | 6.8587 | 43.7252 | 53.895 | -1024.849
2026-07-18 15:00 | -2166.83 | 6.8587 | 44.781 | 53.895 | -635.0352
2026-07-19 16:00 | -1587.33 | 5.5586 | 45.1758 | 53.895 | -465.2005
2026-07-20 17:00 | -1529.2 | 5.4749 | 45.4236 | 53.895 | -448.1643
2026-07-21 18:00 | -2052.24 | 6.8587 | 45.4751 | 53.895 | -601.4522
2026-07-22 19:00 | -2732.21 | 6.8587 | 45.0752 | 53.895 | -800.7317
2026-07-23 20:00 | -3924.69 | 6.8587 | 44.2611 | 53.895 | -1150.2131
2026-07-24 21:00 | -4332.84 | 6.8587 | 43.8642 | 53.895 | -1269.8301
2026-07-25 22:00 | -5346.59 | 6.8587 | 43.0804 | 53.895 | -1566.9309
2026-07-26 23:00 | -5885.06 | 6.8587 | 42.5514 | 53.895 | -1724.7408
2026-07-28 | -6262.15 | 6.8587 | 42.1346 | 53.895 | -1835.255
2026-07-29 01:00 | -6572.81 | 6.8587 | 41.7926 | 53.895 | -1926.3005
2026-07-30 02:00 | -6640.51 | 6.8587 | 41.631 | 53.895 | -1946.1414
2026-07-31 03:00 | -6786.87 | 6.8587 | 41.4277 | 53.895 | -1989.0353
2026-08-01 04:00 | -6966.3 | 6.8587 | 41.2096 | 53.895 | -2041.621
2026-08-02 05:00 | -6651.78 | 6.8587 | 41.3246 | 53.895 | -1949.4443
2026-08-03 06:00 | -6024.61 | 6.8587 | 41.7199 | 53.895 | -1765.6389
2026-08-04 07:00 | -5317.99 | 6.8587 | 42.2488 | 53.895 | -1558.549
2026-08-05 08:00 | -5397.01 | 6.8587 | 42.2987 | 53.895 | -1581.7075
2026-08-06 09:00 | -4422.63 | 6.8587 | 43.0081 | 53.895 | -1296.1449
2026-08-07 10:00 | -2684.69 | 6.8587 | 44.3525 | 53.895 | -786.805
2026-08-08 11:00 | -1272.05 | 4.4598 | 45.1641 | 53.895 | -372.8011
2026-08-09 12:00 | -546.331 | 2.1399 | 45.6556 | 53.895 | -160.1138
2026-08-10 13:00 | -413.7 | 1.9369 | 46.1543 | 53.895 | -121.2435
2026-08-11 14:00 | 1993.63 | 1 | 47.0546 | 53.895 | 584.2753
2026-08-12 15:00 | 2765.14 | 1 | 47.3948 | 53.895 | 810.3825
2026-08-13 16:00 | 3453.61 | 1.251 | 61.2584 | 53.895 | 1012.1532
2026-08-14 17:00 | 2719.04 | 1 | 65.6285 | 53.895 | 796.872
2026-08-15 18:00 | 2686.41 | 1 | 48.3082 | 53.895 | 787.3091
2026-08-16 19:00 | -372.423 | 1.956 | 48.0593 | 53.895 | -109.1464
2026-08-17 20:00 | -1356.19 | 5.1144 | 47.4985 | 53.895 | -397.4601
2026-08-18 21:00 | -2277.63 | 6.8587 | 46.9916 | 53.895 | -667.5075
2026-08-19 22:00 | -2928.98 | 6.8587 | 46.3609 | 53.895 | -858.3993
2026-08-20 23:00 | -5184.11 | 6.8587 | 44.6347 | 53.895 | -1519.3127
2026-08-22 | -5947.57 | 6.8587 | 43.7055 | 53.895 | -1743.0607
2026-08-23 01:00 | -6224.15 | 6.8587 | 43.2176 | 53.895 | -1824.1183
2026-08-24 02:00 | -6904.78 | 6.8587 | 42.5255 | 53.895 | -2023.5913
2026-08-25 03:00 | -7290.35 | 6.8587 | 41.9986 | 53.895 | -2136.5907
2026-08-26 04:00 | -7817.5 | 6.8587 | 41.3779 | 53.895 | -2291.0831
2026-08-27 05:00 | -8130.21 | 6.8587 | 40.9309 | 53.895 | -2382.7293
2026-08-28 06:00 | -7450.26 | 6.8587 | 41.1788 | 53.895 | -2183.4557
2026-08-29 07:00 | -6609.55 | 6.8587 | 41.6877 | 53.895 | -1937.0679
2026-08-30 08:00 | -6210.5 | 6.8587 | 41.9984 | 53.895 | -1820.1179
2026-08-31 09:00 | -4615.03 | 6.8587 | 43.1242 | 53.895 | -1352.5318
2026-09-01 10:00 | -2893.23 | 6.8587 | 44.4934 | 53.895 | -847.922
2026-09-02 11:00 | -1522.59 | 5.344 | 45.4602 | 53.895 | -446.2271
2026-09-03 12:00 | -622.406 | 2.2933 | 45.8626 | 53.895 | -182.4092
2026-09-04 13:00 | 139.981 | 1 | 47.4297 | 53.895 | 41.0244
2026-09-05 14:00 | 2756.87 | 1 | 47.2842 | 53.895 | 807.9588
2026-09-06 15:00 | 2735.5 | 1 | 47.8075 | 53.895 | 801.6959
2026-09-07 16:00 | 3613.35 | 1.3008 | 61.668 | 53.895 | 1058.9684
2026-09-08 17:00 | 2718.94 | 1 | 66.9953 | 53.895 | 796.8427
2026-09-09 18:00 | 1914.65 | 1 | 48.7455 | 53.895 | 561.1285
2026-09-10 19:00 | -685.788 | 3.0079 | 48.0725 | 53.895 | -200.9846
2026-09-11 20:00 | -1576.8 | 5.749 | 47.6222 | 53.895 | -462.1145
2026-09-12 21:00 | -2828.59 | 6.8587 | 46.7817 | 53.895 | -828.9779
2026-09-13 22:00 | -3438.9 | 6.8587 | 46.1138 | 53.895 | -1007.8421
2026-09-14 23:00 | -5100.39 | 6.8587 | 44.7613 | 53.895 | -1494.7768
2026-09-16 | -5645.71 | 6.8587 | 44.0492 | 53.895 | -1654.5943
2026-09-17 01:00 | -6017.33 | 6.8587 | 43.5441 | 53.895 | -1763.5053
2026-09-18 02:00 | -6468.22 | 6.8587 | 43.0145 | 53.895 | -1895.6482
2026-09-19 03:00 | -6495.8 | 6.8587 | 42.7834 | 53.895 | -1903.7311
2026-09-20 04:00 | -6376.85 | 6.8587 | 42.6928 | 53.895 | -1868.8703
2026-09-21 05:00 | -6142.58 | 6.8587 | 42.756 | 53.895 | -1800.2125
2026-09-22 06:00 | -5931.47 | 6.8587 | 42.8417 | 53.895 | -1738.3423
2026-09-23 07:00 | -5132.14 | 6.8587 | 43.3677 | 53.895 | -1504.0818
2026-09-24 08:00 | -4310.52 | 6.8587 | 44.0083 | 53.895 | -1263.2887
2026-09-25 09:00 | -2572.27 | 6.8587 | 45.3323 | 53.895 | -753.8579
2026-09-26 10:00 | -901.894 | 3.098 | 45.9929 | 53.895 | -264.319
2026-09-27 11:00 | 2309.87 | 1 | 47.3325 | 53.895 | 676.9561
2026-09-28 12:00 | 2875.12 | 1 | 63.2347 | 53.895 | 842.6145
2026-09-29 13:00 | 3751.72 | 1.2908 | 62.409 | 53.895 | 1099.5206
2026-09-30 14:00 | 4748.39 | 1.6315 | 62.8197 | 53.895 | 1391.6157
2026-10-01 15:00 | 5945.27 | 2.0787 | 62.9918 | 53.895 | 1742.3866
2026-10-02 16:00 | 5730.79 | 2.0226 | 63.308 | 53.895 | 1679.5288
2026-10-03 17:00 | 4916.99 | 1.7297 | 63.6128 | 53.895 | 1441.0275
2026-10-04 18:00 | 3067.95 | 1.0864 | 63.6541 | 53.895 | 899.1274
2026-10-05 19:00 | 2666.86 | 1 | 49.8923 | 53.895 | 781.5795
2026-10-06 20:00 | -726.281 | 3.0681 | 49.231 | 53.895 | -212.8519
2026-10-07 21:00 | -1898.83 | 6.7424 | 48.6365 | 53.895 | -556.4921
2026-10-08 22:00 | -3122.21 | 6.8587 | 47.4712 | 53.895 | -915.0294
2026-10-09 23:00 | -3897.33 | 6.8587 | 46.6031 | 53.895 | -1142.1947
2026-10-11 | -4221.22 | 6.8587 | 46.0857 | 53.895 | -1237.1175
2026-10-12 01:00 | -4927.25 | 6.8587 | 45.3471 | 53.895 | -1444.0344
2026-10-13 02:00 | -4918.94 | 6.8587 | 45.115 | 53.895 | -1441.599
2026-10-14 03:00 | -5028.13 | 6.8587 | 44.8636 | 53.895 | -1473.5994
2026-10-15 04:00 | -5019.22 | 6.8587 | 44.7291 | 53.895 | -1470.9882
2026-10-16 05:00 | -4810.86 | 6.8587 | 44.7612 | 53.895 | -1409.9239
2026-10-17 06:00 | -5113.77 | 6.8587 | 44.495 | 53.895 | -1498.698
2026-10-18 07:00 | -4456.42 | 6.8587 | 44.8493 | 53.895 | -1306.0478
2026-10-19 08:00 | -3829.19 | 6.8587 | 45.3041 | 53.895 | -1122.2248
2026-10-20 09:00 | -2127.2 | 6.8587 | 46.5482 | 53.895 | -623.4208
2026-10-21 10:00 | -634.565 | 2.1303 | 46.8364 | 53.895 | -185.9726
2026-10-22 11:00 | 2134.75 | 1 | 48.171 | 53.895 | 625.6335
2026-10-23 12:00 | 2809.27 | 1 | 67.2854 | 53.895 | 823.3158
2026-10-24 13:00 | 3320.47 | 1.1614 | 62.8295 | 53.895 | 973.1337
2026-10-25 14:00 | 4240.65 | 1.48 | 63.1749 | 53.895 | 1242.8118
2026-10-26 15:00 | 5225.75 | 1.8321 | 63.4413 | 53.895 | 1531.5161
2026-10-27 16:00 | 4641.09 | 1.62 | 63.8592 | 53.895 | 1360.1692
2026-10-28 17:00 | 3706.39 | 1.3169 | 63.7782 | 53.895 | 1086.2357
2026-10-29 18:00 | 2845.74 | 1 | 71.1371 | 53.895 | 834.0041
2026-10-30 19:00 | 2937.13 | 1 | 50.105 | 53.895 | 860.7878
2026-10-31 20:00 | -740.805 | 3.1149 | 49.5714 | 53.895 | -217.1085
2026-11-01 21:00 | -1423.04 | 5.1076 | 48.9913 | 53.895 | -417.0519
2026-11-02 22:00 | -2728.28 | 6.8587 | 48.153 | 53.895 | -799.5799
2026-11-03 23:00 | -3488.99 | 6.8587 | 47.3395 | 53.895 | -1022.522
2026-11-05 | -4153.66 | 6.8587 | 46.6006 | 53.895 | -1217.3176
2026-11-06 01:00 | -4602.7 | 6.8587 | 46.0046 | 53.895 | -1348.9182
2026-11-07 02:00 | -4733.28 | 6.8587 | 45.6972 | 53.895 | -1387.1874
2026-11-08 03:00 | -5193.98 | 6.8587 | 45.1963 | 53.895 | -1522.2053
2026-11-09 04:00 | -5228.75 | 6.8587 | 44.9831 | 53.895 | -1532.3954
2026-11-10 05:00 | -4852.2 | 6.8587 | 45.0992 | 53.895 | -1422.0394
2026-11-11 06:00 | -4745.04 | 6.8587 | 45.1172 | 53.895 | -1390.6339
2026-11-12 07:00 | -4825.34 | 6.8587 | 45.0027 | 53.895 | -1414.1676
2026-11-13 08:00 | -4984.83 | 6.8587 | 44.8412 | 53.895 | -1460.9095
2026-11-14 09:00 | -3924.56 | 6.8587 | 45.4978 | 53.895 | -1150.175
2026-11-15 10:00 | -2574.12 | 6.8587 | 46.4961 | 53.895 | -754.4001
2026-11-16 11:00 | -1275.98 | 4.3412 | 47.0424 | 53.895 | -373.9528
2026-11-17 12:00 | -537.552 | 2.0735 | 47.4268 | 53.895 | -157.5409
2026-11-18 13:00 | -260.599 | 1.3876 | 47.97 | 53.895 | -76.374
2026-11-19 14:00 | -972.609 | 3.846 | 47.8228 | 53.895 | -285.0436
2026-11-20 15:00 | -475.494 | 1.9106 | 47.8434 | 53.895 | -139.3535
2026-11-21 16:00 | -212.133 | 1.2396 | 48.2773 | 53.895 | -62.17
2026-11-22 17:00 | -459.13 | 2.1318 | 48.1439 | 53.895 | -134.5577
2026-11-23 18:00 | -1355.58 | 5.0637 | 47.9082 | 53.895 | -397.2813
2026-11-24 19:00 | -2365.41 | 6.8587 | 47.4492 | 53.895 | -693.2332
2026-11-25 20:00 | -3548.73 | 6.8587 | 46.5159 | 53.895 | -1040.0301
2026-11-26 21:00 | -3738.28 | 6.8587 | 46.1823 | 53.895 | -1095.5817
2026-11-27 22:00 | -4500.93 | 6.8587 | 45.5184 | 53.895 | -1319.0924
2026-11-28 23:00 | -4778.56 | 6.8587 | 45.1391 | 53.895 | -1400.4577
2026-11-30 | -5214.81 | 6.8587 | 44.6792 | 53.895 | -1528.3099
2026-12-01 01:00 | -5614.26 | 6.8587 | 44.2511 | 53.895 | -1645.3772
2026-12-02 02:00 | -5890.15 | 6.8587 | 43.9229 | 53.895 | -1726.2326
2026-12-03 03:00 | -6081.49 | 6.8587 | 43.6547 | 53.895 | -1782.3088
2026-12-04 04:00 | -5861 | 6.8587 | 43.6857 | 53.895 | -1717.6895
2026-12-05 05:00 | -5537.17 | 6.8587 | 43.84 | 53.895 | -1622.7843
2026-12-06 06:00 | -5506.85 | 6.8587 | 43.8458 | 53.895 | -1613.8984
2026-12-07 07:00 | -5508.15 | 6.8587 | 43.8257 | 53.895 | -1614.2794
2026-12-08 08:00 | -5541.29 | 6.8587 | 43.7883 | 53.895 | -1623.9918
2026-12-09 09:00 | -4345.25 | 6.8587 | 44.5815 | 53.895 | -1273.4671
2026-12-10 10:00 | -3432.61 | 6.8587 | 45.321 | 53.895 | -1005.9987
2026-12-11 11:00 | -1879.79 | 6.5573 | 46.4703 | 53.895 | -550.9121
2026-12-12 12:00 | -2087.26 | 6.8587 | 46.6382 | 53.895 | -611.7155
2026-12-13 13:00 | -2021.87 | 6.8587 | 46.7975 | 53.895 | -592.5516
2026-12-14 14:00 | -1018.88 | 3.4435 | 46.8742 | 53.895 | -298.6043
2026-12-15 15:00 | 0 | 1 | 48.4501 | 53.895 | 0
2026-12-16 16:00 | 2970.4 | 1 | 48.1782 | 53.895 | 870.5383
2026-12-17 17:00 | 2905.49 | 1 | 48.6787 | 53.895 | 851.5151
2026-12-18 18:00 | -484.728 | 2.316 | 48.4995 | 53.895 | -142.0598
2026-12-19 19:00 | -1161.13 | 4.3786 | 48.0449 | 53.895 | -340.2936
2026-12-20 20:00 | -2502.13 | 6.8587 | 47.4771 | 53.895 | -733.3019
2026-12-21 21:00 | -2977.87 | 6.8587 | 46.9947 | 53.895 | -872.7275
2026-12-22 22:00 | -4464.85 | 6.8587 | 45.7893 | 53.895 | -1308.5184
2026-12-23 23:00 | -4766.86 | 6.8587 | 45.2666 | 53.895 | -1397.0288
2026-12-25 | -5187.89 | 6.8587 | 44.7951 | 53.895 | -1520.4205
2026-12-26 01:00 | -5429.61 | 6.8587 | 44.4733 | 53.895 | -1591.2616
2026-12-27 02:00 | -5514.15 | 6.8587 | 44.2803 | 53.895 | -1616.0378
2026-12-28 03:00 | -5598.14 | 6.8587 | 44.1046 | 53.895 | -1640.6529
2026-12-29 04:00 | -5451.65 | 6.8587 | 44.0861 | 53.895 | -1597.7209
2026-12-30 05:00 | -5162.32 | 6.8587 | 44.1953 | 53.895 | -1512.9266
2026-12-31 06:00 | -4932.58 | 6.8587 | 44.338 | 53.895 | -1445.5965
2027-01-01 07:00 | -4422.22 | 6.8587 | 44.693 | 53.895 | -1296.0247
2027-01-02 08:00 | -4342.23 | 6.8587 | 44.8097 | 53.895 | -1272.582
2027-01-03 09:00 | -3815.8 | 6.8587 | 45.2039 | 53.895 | -1118.3006
2027-01-04 10:00 | -3555.23 | 6.8587 | 45.4628 | 53.895 | -1041.9351
2027-01-05 11:00 | -2711.79 | 6.8587 | 46.1036 | 53.895 | -794.7472
2027-01-06 12:00 | -2632.95 | 6.8587 | 46.2926 | 53.895 | -771.6415
2027-01-07 13:00 | -2681.04 | 6.8587 | 46.3414 | 53.895 | -785.7353
2027-01-08 14:00 | -2856.95 | 6.8587 | 46.2604 | 53.895 | -837.2894
2027-01-09 15:00 | -1664.48 | 5.7231 | 46.8474 | 53.895 | -487.8109
2027-01-10 16:00 | -989.555 | 3.4682 | 47.0051 | 53.895 | -290.0099
2027-01-11 17:00 | -685.893 | 2.6809 | 47.2868 | 53.895 | -201.0154
2027-01-12 18:00 | -1280.5 | 4.79 | 47.3629 | 53.895 | -375.2775
2027-01-13 19:00 | -1780.21 | 6.2742 | 47.3084 | 53.895 | -521.728
2027-01-14 20:00 | -2676.91 | 6.8587 | 46.8076 | 53.895 | -784.5249
2027-01-15 21:00 | -2975.24 | 6.8587 | 46.5096 | 53.895 | -871.9568
2027-01-16 22:00 | -3752.53 | 6.8587 | 45.9043 | 53.895 | -1099.758
2027-01-17 23:00 | -4199.06 | 6.8587 | 45.4605 | 53.895 | -1230.623
2027-01-19 | -4629.1 | 6.8587 | 45.0375 | 53.895 | -1356.6553
2027-01-20 01:00 | -4872.97 | 6.8587 | 44.7501 | 53.895 | -1428.1265
2027-01-21 02:00 | -4782.72 | 6.8587 | 44.7194 | 53.895 | -1401.6769
2027-01-22 03:00 | -4664.58 | 6.8587 | 44.7401 | 53.895 | -1367.0535
2027-01-23 04:00 | -4802.34 | 6.8587 | 44.6108 | 53.895 | -1407.4269
2027-01-24 05:00 | -4708.2 | 6.8587 | 44.6172 | 53.895 | -1379.8372
2027-01-25 06:00 | -3764.67 | 6.8587 | 45.2347 | 53.895 | -1103.3159
2027-01-26 07:00 | -3105.4 | 6.8587 | 45.7814 | 53.895 | -910.1029
2027-01-27 08:00 | -3358.46 | 6.8587 | 45.7394 | 53.895 | -984.2675
2027-01-28 09:00 | -3144.03 | 6.8587 | 45.9139 | 53.895 | -921.4242
2027-01-29 10:00 | -2407.93 | 6.8587 | 46.4695 | 53.895 | -705.6946
2027-01-30 11:00 | -1490.38 | 5.089 | 46.8707 | 53.895 | -436.7873
2027-01-31 12:00 | -1028.56 | 3.6705 | 47.1108 | 53.895 | -301.4412
2027-02-01 13:00 | -2072.49 | 6.8587 | 47.1679 | 53.895 | -607.3869
2027-02-02 14:00 | -2199.35 | 6.8587 | 47.0558 | 53.895 | -644.5659
2027-02-03 15:00 | -2341.75 | 6.8587 | 46.94 | 53.895 | -686.2992
2027-02-04 16:00 | -1167.89 | 3.9531 | 47.1309 | 53.895 | -342.2748
2027-02-05 17:00 | -1523.57 | 5.4836 | 47.3309 | 53.895 | -446.5143
2027-02-06 18:00 | -1879.72 | 6.5385 | 47.2962 | 53.895 | -550.8916
2027-02-07 19:00 | -2400.11 | 6.8587 | 46.9704 | 53.895 | -703.4028
2027-02-08 20:00 | -2868.7 | 6.8587 | 46.6003 | 53.895 | -840.733
2027-02-09 21:00 | -2827.52 | 6.8587 | 46.5646 | 53.895 | -828.6643
2027-02-10 22:00 | -3218.84 | 6.8587 | 46.2574 | 53.895 | -943.3489
2027-02-11 23:00 | -4782 | 6.8587 | 45.1143 | 53.895 | -1401.4659
2027-02-13 | -5097.03 | 6.8587 | 44.6558 | 53.895 | -1493.792
2027-02-14 01:00 | -5225.46 | 6.8587 | 44.4045 | 53.895 | -1531.4312
2027-02-15 02:00 | -5250.36 | 6.8587 | 44.2847 | 53.895 | -1538.7286
2027-02-16 03:00 | -5251.27 | 6.8587 | 44.1959 | 53.895 | -1538.9953
2027-02-17 04:00 | -5191.8 | 6.8587 | 44.1502 | 53.895 | -1521.5664
2027-02-18 05:00 | -5106.44 | 6.8587 | 44.1647 | 53.895 | -1496.5498
2027-02-19 06:00 | -4317.35 | 6.8587 | 44.673 | 53.895 | -1265.2904
2027-02-20 07:00 | -3828.49 | 6.8587 | 45.0709 | 53.895 | -1122.0197
2027-02-21 08:00 | -4017.9 | 6.8587 | 45.0276 | 53.895 | -1177.5303
2027-02-22 09:00 | -3362.96 | 6.8587 | 45.4835 | 53.895 | -985.5863
2027-02-23 10:00 | -2785.79 | 6.8587 | 45.9569 | 53.895 | -816.4345
2027-02-24 11:00 | -1799.75 | 6.2143 | 46.6296 | 53.895 | -527.4547
2027-02-25 12:00 | -1953.01 | 6.755 | 46.8131 | 53.895 | -572.3707
2027-02-26 13:00 | -2097.08 | 6.8587 | 46.823 | 53.895 | -614.5935
2027-02-27 14:00 | -1673.17 | 5.7016 | 46.9306 | 53.895 | -490.3577
2027-02-28 15:00 | -1352.38 | 4.7141 | 47.0596 | 53.895 | -396.3435
2027-03-01 16:00 | -472.285 | 1.8136 | 47.2813 | 53.895 | -138.4131
2027-03-02 17:00 | -685.827 | 2.8533 | 47.5373 | 53.895 | -200.9961
2027-03-03 18:00 | -1219.49 | 4.5548 | 47.4889 | 53.895 | -357.3972
2027-03-04 19:00 | -1829.96 | 6.462 | 47.4201 | 53.895 | -536.3083
2027-03-05 20:00 | -2289.53 | 6.8587 | 47.1437 | 53.895 | -670.995
2027-03-06 21:00 | -2874.25 | 6.8587 | 46.6844 | 53.895 | -842.3595
2027-03-07 22:00 | -3186.19 | 6.8587 | 46.363 | 53.895 | -933.7801
2027-03-08 23:00 | -4470.79 | 6.8587 | 45.3875 | 53.895 | -1310.2592
2027-03-10 | -4784.36 | 6.8587 | 44.9671 | 53.895 | -1402.1575
2027-03-11 01:00 | -4969.81 | 6.8587 | 44.6887 | 53.895 | -1456.5075
2027-03-12 02:00 | -5029.13 | 6.8587 | 44.5363 | 53.895 | -1473.8925
2027-03-13 03:00 | -4993.89 | 6.8587 | 44.4699 | 53.895 | -1463.5647
2027-03-14 04:00 | -4589.85 | 6.8587 | 44.6671 | 53.895 | -1345.1523
2027-03-15 05:00 | -4255.18 | 6.8587 | 44.8956 | 53.895 | -1247.0702
2027-03-16 06:00 | -4218.43 | 6.8587 | 44.9445 | 53.895 | -1236.2998
2027-03-17 07:00 | -4239.69 | 6.8587 | 44.933 | 53.895 | -1242.5305
2027-03-18 08:00 | -4510.21 | 6.8587 | 44.7423 | 53.895 | -1321.8121
2027-03-19 09:00 | -4205.68 | 6.8587 | 44.9103 | 53.895 | -1232.5631
2027-03-20 10:00 | -3880.46 | 6.8587 | 45.1321 | 53.895 | -1137.2506
2027-03-21 11:00 | -3607.57 | 6.8587 | 45.3467 | 53.895 | -1057.2744
2027-03-22 12:00 | -3347.85 | 6.8587 | 45.5609 | 53.895 | -981.158
2027-03-23 13:00 | -3127.2 | 6.8587 | 45.7617 | 53.895 | -916.4919
2027-03-24 14:00 | -2472.01 | 6.8587 | 46.2665 | 53.895 | -724.4746
2027-03-25 15:00 | -1184.88 | 4.0437 | 46.689 | 53.895 | -347.254
2027-03-26 16:00 | -903.336 | 3.3678 | 47.0106 | 53.895 | -264.7416
2027-03-27 17:00 | -710.096 | 2.7774 | 47.2154 | 53.895 | -208.1086
2027-03-28 18:00 | -1226.42 | 4.6002 | 47.2847 | 53.895 | -359.4282
2027-03-29 19:00 | -1671.19 | 5.9252 | 47.2527 | 53.895 | -489.7774
2027-03-30 20:00 | -2778.43 | 6.8587 | 46.6761 | 53.895 | -814.2775
2027-03-31 21:00 | -3212.55 | 6.8587 | 46.2554 | 53.895 | -941.5055
2027-04-01 22:00 | -4136.29 | 6.8587 | 45.5126 | 53.895 | -1212.2269
2027-04-02 23:00 | -4421.17 | 6.8587 | 45.1545 | 53.895 | -1295.717
2027-04-04 | -4535.4 | 6.8587 | 44.9519 | 53.895 | -1329.1945
2027-04-05 01:00 | -4725.75 | 6.8587 | 44.7359 | 53.895 | -1384.9806
2027-04-06 02:00 | -4734.92 | 6.8587 | 44.6525 | 53.895 | -1387.6681
2027-04-07 03:00 | -4840.69 | 6.8587 | 44.5113 | 53.895 | -1418.6662
2027-04-08 04:00 | -4704.57 | 6.8587 | 44.5429 | 53.895 | -1378.7734
2027-04-09 05:00 | -4231.4 | 6.8587 | 44.8298 | 53.895 | -1240.1009
2027-04-10 06:00 | -4032.99 | 6.8587 | 44.9887 | 53.895 | -1181.9527
2027-04-11 07:00 | -3879.17 | 6.8587 | 45.1189 | 53.895 | -1136.8725
2027-04-12 08:00 | -4030.99 | 6.8587 | 45.0468 | 53.895 | -1181.3666
2027-04-13 09:00 | -3367.21 | 6.8587 | 45.5013 | 53.895 | -986.8318
2027-04-14 10:00 | -2546.32 | 6.8587 | 46.1515 | 53.895 | -746.2527
2027-04-15 11:00 | -1593.15 | 5.471 | 46.6721 | 53.895 | -466.9062
2027-04-16 12:00 | -864.132 | 3.0724 | 46.9133 | 53.895 | -253.2521
2027-04-17 13:00 | -734.077 | 2.8908 | 47.2515 | 53.895 | -215.1367
2027-04-18 14:00 | -444.883 | 1.9239 | 47.5141 | 53.895 | -130.3823
2027-04-19 15:00 | 2348.63 | 1 | 48.3434 | 53.895 | 688.3155
2027-04-20 16:00 | 2479.3 | 1 | 48.7667 | 53.895 | 726.6111
2027-04-21 17:00 | 2957.36 | 1 | 48.9683 | 53.895 | 866.7167
2027-04-22 18:00 | -153.975 | 1.2336 | 49.1231 | 53.895 | -45.1256
2027-04-23 19:00 | -841.393 | 3.3929 | 48.3678 | 53.895 | -246.5879
2027-04-24 20:00 | -1940.22 | 6.8587 | 48.0963 | 53.895 | -568.6224
2027-04-25 21:00 | -2650.02 | 6.8587 | 47.4366 | 53.895 | -776.6442
2027-04-26 22:00 | -4008.44 | 6.8587 | 46.319 | 53.895 | -1174.7578
2027-04-27 23:00 | -4495.1 | 6.8587 | 45.6856 | 53.895 | -1317.3838
2027-04-29 | -4728.48 | 6.8587 | 45.3175 | 53.895 | -1385.7807
2027-04-30 01:00 | -4978.19 | 6.8587 | 44.9924 | 53.895 | -1458.9635
2027-05-01 02:00 | -4971.92 | 6.8587 | 44.8588 | 53.895 | -1457.1259
2027-05-02 03:00 | -4923.94 | 6.8587 | 44.7612 | 53.895 | -1443.0644
2027-05-03 04:00 | -4803.13 | 6.8587 | 44.7524 | 53.895 | -1407.6584
2027-05-04 05:00 | -4478.04 | 6.8587 | 44.8974 | 53.895 | -1312.384
2027-05-05 06:00 | -4220.19 | 6.8587 | 45.0644 | 53.895 | -1236.8156
2027-05-06 07:00 | -3399.23 | 6.8587 | 45.6386 | 53.895 | -996.216
2027-05-07 08:00 | -2778.73 | 6.8587 | 46.1669 | 53.895 | -814.3654
2027-05-08 09:00 | -1446.43 | 4.9582 | 46.8278 | 53.895 | -423.9068
2027-05-09 10:00 | 0 | 1 | 48.4412 | 53.895 | 0
2027-05-10 11:00 | 2970.24 | 1 | 67.7313 | 53.895 | 870.4914
2027-05-11 12:00 | 3731.76 | 1.2082 | 63.7968 | 53.895 | 1093.6709
2027-05-12 13:00 | 4590.42 | 1.4897 | 64.2192 | 53.895 | 1345.3193
2027-05-13 14:00 | 5689.9 | 1.8107 | 64.906 | 53.895 | 1667.5451
2027-05-14 15:00 | 7061.58 | 2.3672 | 64.5801 | 53.895 | 2069.5448
2027-05-15 16:00 | 6993.45 | 2.2686 | 65.5296 | 53.895 | 2049.5779
2027-05-16 17:00 | 6455.69 | 2.093 | 65.8382 | 53.895 | 1891.976
2027-05-17 18:00 | 4703.72 | 1.4823 | 66.4557 | 53.895 | 1378.5243
2027-05-18 19:00 | 3058.74 | 1 | 69.6392 | 53.895 | 896.4282
2027-05-19 20:00 | 0 | 0 | 51.4496 | 53.895 | 0
2027-05-20 21:00 | -533.651 | 2.2415 | 49.9237 | 53.895 | -156.3977
2027-05-21 22:00 | -1618.68 | 5.8092 | 49.471 | 53.895 | -474.3883
2027-05-22 23:00 | -2203.67 | 6.8587 | 48.9814 | 53.895 | -645.8319
2027-05-24 | -2751.62 | 6.8587 | 48.347 | 53.895 | -806.4202
2027-05-25 01:00 | -3032.98 | 6.8587 | 47.9184 | 53.895 | -888.8787
2027-05-26 02:00 | -3428.34 | 6.8587 | 47.4757 | 53.895 | -1004.7473
2027-05-27 03:00 | -3348.21 | 6.8587 | 47.3379 | 53.895 | -981.2635
2027-05-28 04:00 | -3507.61 | 6.8587 | 47.0978 | 53.895 | -1027.979
2027-05-29 05:00 | -3031.35 | 6.8587 | 47.2955 | 53.895 | -888.401
2027-05-30 06:00 | -2952.56 | 6.8587 | 47.3133 | 53.895 | -865.3099
2027-05-31 07:00 | -2203.17 | 6.8587 | 47.7971 | 53.895 | -645.6854
2027-06-01 08:00 | -1702.88 | 5.7166 | 47.9881 | 53.895 | -499.0649
2027-06-02 09:00 | -345.098 | 1.2538 | 48.187 | 53.895 | -101.1382
2027-06-03 10:00 | 2219.92 | 1.0624 | 59.5375 | 53.895 | 650.5943
2027-06-04 11:00 | 4575.9 | 1.6174 | 63.4001 | 53.895 | 1341.0639
2027-06-05 12:00 | 5651.92 | 1.8954 | 64.6459 | 53.895 | 1656.4142
2027-06-06 13:00 | 6470.68 | 2.1605 | 65.1604 | 53.895 | 1896.3691
2027-06-07 14:00 | 7206.55 | 2.3955 | 65.6378 | 53.895 | 2112.0313
2027-06-08 15:00 | 8515.5 | 2.8715 | 65.8207 | 53.895 | 2495.6467
2027-06-09 16:00 | 8575.45 | 2.7879 | 66.7736 | 53.895 | 2513.2163
2027-06-10 17:00 | 7898.37 | 2.5689 | 67.0687 | 53.895 | 2314.7837
2027-06-11 18:00 | 5990.13 | 1.875 | 67.8062 | 53.895 | 1755.5338
2027-06-12 19:00 | 3999.98 | 1.2826 | 67.4073 | 53.895 | 1172.2784
2027-06-13 20:00 | 2986.96 | 1 | 52.1066 | 53.895 | 875.3916
2027-06-14 21:00 | 0 | 0 | 52.4497 | 53.895 | 0
2027-06-15 22:00 | -964.755 | 3.5859 | 50.7357 | 53.895 | -282.7418
2027-06-16 23:00 | -1480.91 | 5.1528 | 50.2627 | 53.895 | -434.0119
2027-06-18 | -1913.78 | 6.4345 | 49.9408 | 53.895 | -560.8736
2027-06-19 01:00 | -2301.39 | 6.8587 | 49.5247 | 53.895 | -674.4708
2027-06-20 02:00 | -2706.24 | 6.8587 | 49.0161 | 53.895 | -793.1207
2027-06-21 03:00 | -2969.3 | 6.8587 | 48.6355 | 53.895 | -870.2159
2027-06-22 04:00 | -2860.51 | 6.8587 | 48.5287 | 53.895 | -838.3327
2027-06-23 05:00 | -2523.43 | 6.8587 | 48.6316 | 53.895 | -739.5443
2027-06-24 06:00 | -2524.02 | 6.8587 | 48.5759 | 53.895 | -739.7172
2027-06-25 07:00 | -1583.23 | 5.2577 | 48.834 | 53.895 | -463.9989
2027-06-26 08:00 | -1063.41 | 3.6713 | 48.9545 | 53.895 | -311.6547
2027-06-27 09:00 | 1583.49 | 1 | 50.155 | 53.895 | 464.0751
2027-06-28 10:00 | 3279.2 | 1.1358 | 64.3742 | 53.895 | 961.0387
2027-06-29 11:00 | 5757.98 | 1.9781 | 64.8359 | 53.895 | 1687.4974
2027-06-30 12:00 | 7112.36 | 2.4181 | 65.5117 | 53.895 | 2084.427
2027-07-01 13:00 | 7978.52 | 2.6701 | 66.2314 | 53.895 | 2338.2734
2027-07-02 14:00 | 9125.26 | 2.9776 | 67.0341 | 53.895 | 2674.3497
2027-07-03 15:00 | 10247.2 | 3.4163 | 67.1632 | 53.895 | 3003.1579
2027-07-04 16:00 | 10415.2 | 3.4378 | 67.7579 | 53.895 | 3052.3938
2027-07-05 17:00 | 9989.53 | 3.252 | 68.2877 | 53.895 | 2927.6422
2027-07-06 18:00 | 8227.31 | 2.6081 | 68.905 | 53.895 | 2411.1865
2027-07-07 19:00 | 6167.05 | 1.9617 | 68.8713 | 53.895 | 1807.3839
2027-07-08 20:00 | 3099.08 | 1.006 | 68.4329 | 53.895 | 908.2507
2027-07-09 21:00 | 3053.09 | 1 | 53.0667 | 53.895 | 894.7724
2027-07-10 22:00 | 0 | 0 | 53.3961 | 53.895 | 0
2027-07-11 23:00 | -1117.02 | 3.8925 | 51.5542 | 53.895 | -327.3662
2027-07-13 | -1487.32 | 5.0807 | 51.0806 | 53.895 | -435.8905
2027-07-14 01:00 | -1902.57 | 6.3307 | 50.742 | 53.895 | -557.5882
2027-07-15 02:00 | -2384.11 | 6.8587 | 50.2759 | 53.895 | -698.7137
2027-07-16 03:00 | -2550.62 | 6.8587 | 49.8797 | 53.895 | -747.5129
2027-07-17 04:00 | -2961.88 | 6.8587 | 49.3946 | 53.895 | -868.0413
2027-07-18 05:00 | -3001.86 | 6.8587 | 49.1593 | 53.895 | -879.7583
2027-07-19 06:00 | -2129.65 | 6.8587 | 49.5947 | 53.895 | -624.1388
2027-07-20 07:00 | -1145.96 | 3.7322 | 49.5928 | 53.895 | -335.8477
2027-07-21 08:00 | -753.133 | 2.7784 | 49.8629 | 53.895 | -220.7215
2027-07-22 09:00 | 1632.35 | 1 | 50.9172 | 53.895 | 478.3946
2027-07-23 10:00 | 3332.96 | 1.2353 | 64.2086 | 53.895 | 976.7942
2027-07-24 11:00 | 5426.37 | 1.9282 | 65.0985 | 53.895 | 1590.3121
2027-07-25 12:00 | 6830.01 | 2.3513 | 65.9821 | 53.895 | 2001.6783
2027-07-26 13:00 | 7914.84 | 2.585 | 67.1688 | 53.895 | 2319.6106
2027-07-27 14:00 | 8670.42 | 2.8507 | 67.5107 | 53.895 | 2541.0493
2027-07-28 15:00 | 8972.6 | 2.8817 | 68.2217 | 53.895 | 2629.6095
2027-07-29 16:00 | 10419 | 3.4912 | 67.9155 | 53.895 | 3053.5075
2027-07-30 17:00 | 8823.19 | 2.8347 | 68.9302 | 53.895 | 2585.8217
2027-07-31 18:00 | 7122.17 | 2.2996 | 68.9674 | 53.895 | 2087.302
2027-08-01 19:00 | 5374.34 | 1.6962 | 69.2239 | 53.895 | 1575.0636
2027-08-02 20:00 | 4098.88 | 1.3058 | 68.9271 | 53.895 | 1201.2631
2027-08-03 21:00 | 3292.28 | 1 | 74.5371 | 53.895 | 964.872
2027-08-04 22:00 | 3069.69 | 1 | 53.2889 | 53.895 | 899.6373
2027-08-05 23:00 | -609.296 | 2.5547 | 52.5714 | 53.895 | -178.567
2027-08-07 | -1140.93 | 4.0607 | 51.8438 | 53.895 | -334.3736
2027-08-08 01:00 | -1589.52 | 5.3687 | 51.4047 | 53.895 | -465.8423
2027-08-09 02:00 | -1967.95 | 6.4782 | 51.1092 | 53.895 | -576.7492
2027-08-10 03:00 | -2277.39 | 6.8587 | 50.7242 | 53.895 | -667.4371
2027-08-11 04:00 | -2629.51 | 6.8587 | 50.217 | 53.895 | -770.6333
2027-08-12 05:00 | -2914.07 | 6.8587 | 49.8314 | 53.895 | -854.0296
2027-08-13 06:00 | -2360.16 | 6.8587 | 50.0346 | 53.895 | -691.6946
2027-08-14 07:00 | -1838.9 | 5.9916 | 50.1458 | 53.895 | -538.9284
2027-08-15 08:00 | -2079.55 | 6.8587 | 50.1641 | 53.895 | -609.4559
2027-08-16 09:00 | -1705.95 | 5.5456 | 50.0609 | 53.895 | -499.9646
2027-08-17 10:00 | -998.328 | 3.37 | 50.0673 | 53.895 | -292.5811
2027-08-18 11:00 | 0 | 0 | 51.513 | 53.895 | 0
2027-08-19 12:00 | -369.147 | 1.8319 | 50.6758 | 53.895 | -108.1863
2027-08-20 13:00 | -280.883 | 1.4345 | 50.6788 | 53.895 | -82.3187
2027-08-21 14:00 | 1653.61 | 1 | 51.2936 | 53.895 | 484.6253
2027-08-22 15:00 | 2823.75 | 1 | 51.3052 | 53.895 | 827.5594
2027-08-23 16:00 | 3056.07 | 1.0145 | 66.187 | 53.895 | 895.6457
2027-08-24 17:00 | 3065.32 | 1 | 51.6275 | 53.895 | 898.3566
2027-08-25 18:00 | 0 | 0 | 52.2657 | 53.895 | 0
2027-08-26 19:00 | -972.934 | 3.4434 | 50.6653 | 53.895 | -285.1388
2027-08-27 20:00 | -1346.69 | 4.719 | 50.3993 | 53.895 | -394.6759
2027-08-28 21:00 | -1861.97 | 6.2893 | 50.1738 | 53.895 | -545.6895
2027-08-29 22:00 | -2265.19 | 6.8587 | 49.8216 | 53.895 | -663.8617
2027-08-30 23:00 | -3568.83 | 6.8587 | 48.7395 | 53.895 | -1045.9208
2027-09-01 | -4115.46 | 6.8587 | 48.1211 | 53.895 | -1206.1223
2027-09-02 01:00 | -4621.57 | 6.8587 | 47.5659 | 53.895 | -1354.4485
2027-09-03 02:00 | -4883.19 | 6.8587 | 47.1755 | 53.895 | -1431.1217
2027-09-04 03:00 | -5035.13 | 6.8587 | 46.8715 | 53.895 | -1475.6509
2027-09-05 04:00 | -4880.89 | 6.8587 | 46.7967 | 53.895 | -1430.4477
2027-09-06 05:00 | -4373.73 | 6.8587 | 47.0268 | 53.895 | -1281.8137
2027-09-07 06:00 | -4293.14 | 6.8587 | 47.0623 | 53.895 | -1258.1951
2027-09-08 07:00 | -3785.68 | 6.8587 | 47.3823 | 53.895 | -1109.4733
2027-09-09 08:00 | -3415.83 | 6.8587 | 47.6603 | 53.895 | -1001.081
2027-09-10 09:00 | -2755.61 | 6.8587 | 48.1519 | 53.895 | -807.5896
2027-09-11 10:00 | -2220.66 | 6.8587 | 48.5932 | 53.895 | -650.8112
2027-09-12 11:00 | -1730.94 | 5.7436 | 48.7811 | 53.895 | -507.2884
2027-09-13 12:00 | -2024.2 | 6.8384 | 48.9046 | 53.895 | -593.2345
2027-09-14 13:00 | -1828.52 | 6.0562 | 48.8848 | 53.895 | -535.8863
2027-09-15 14:00 | -1059.7 | 3.5707 | 48.9202 | 53.895 | -310.5674
2027-09-16 15:00 | 0 | 1 | 50.4029 | 53.895 | 0
2027-09-17 16:00 | 2999.86 | 1 | 50.0452 | 53.895 | 879.1722
2027-09-18 17:00 | 3002.5 | 1 | 50.4842 | 53.895 | 879.9459
2027-09-19 18:00 | -297.866 | 1.6713 | 50.439 | 53.895 | -87.2959
2027-09-20 19:00 | -996.348 | 3.7913 | 49.8226 | 53.895 | -292.0008
2027-09-21 20:00 | -2333.87 | 6.8587 | 49.3129 | 53.895 | -683.9898
2027-09-22 21:00 | -3033.43 | 6.8587 | 48.6388 | 53.895 | -889.0106
2027-09-23 22:00 | -4160.77 | 6.8587 | 47.6123 | 53.895 | -1219.4013
2027-09-24 23:00 | -4697.09 | 6.8587 | 46.9406 | 53.895 | -1376.5812
2027-09-26 | -5253.15 | 6.8587 | 46.3459 | 53.895 | -1539.5463
2027-09-27 01:00 | -5383.31 | 6.8587 | 46.0535 | 53.895 | -1577.6924
2027-09-28 02:00 | -5541.14 | 6.8587 | 45.7948 | 53.895 | -1623.9478
2027-09-29 03:00 | -5612.92 | 6.8587 | 45.6051 | 53.895 | -1644.9845
2027-09-30 04:00 | -5515.34 | 6.8587 | 45.5269 | 53.895 | -1616.3866
2027-10-01 05:00 | -4834.95 | 6.8587 | 45.8775 | 53.895 | -1416.984
2027-10-02 06:00 | -4606.77 | 6.8587 | 46.0446 | 53.895 | -1350.111
2027-10-03 07:00 | -4410.38 | 6.8587 | 46.184 | 53.895 | -1292.5548
2027-10-04 08:00 | -4494.14 | 6.8587 | 46.138 | 53.895 | -1317.1024
2027-10-05 09:00 | -3923.37 | 6.8587 | 46.5121 | 53.895 | -1149.8262
2027-10-06 10:00 | -3375.93 | 6.8587 | 46.9416 | 53.895 | -989.3874
2027-10-07 11:00 | -2700.68 | 6.8587 | 47.4817 | 53.895 | -791.4912
2027-10-08 12:00 | -1570.11 | 5.2852 | 48.0505 | 53.895 | -460.1538
2027-10-09 13:00 | -751.902 | 2.6576 | 48.3142 | 53.895 | -220.3607
2027-10-10 14:00 | -535.561 | 2.2195 | 48.7233 | 53.895 | -156.9574
2027-10-11 15:00 | 2229.81 | 1 | 49.6195 | 53.895 | 653.4928
2027-10-12 16:00 | 2869.86 | 1 | 49.9282 | 53.895 | 841.0729
2027-10-13 17:00 | 2718.12 | 1 | 50.2825 | 53.895 | 796.6023
2027-10-14 18:00 | 0 | 0 | 50.9391 | 53.895 | 0
2027-10-15 19:00 | -1076.48 | 3.8921 | 49.4723 | 53.895 | -315.4851
2027-10-16 20:00 | -2279.08 | 6.8587 | 49.0676 | 53.895 | -667.9324
2027-10-17 21:00 | -3126.75 | 6.8587 | 48.275 | 53.895 | -916.36
2027-10-18 22:00 | -4373.84 | 6.8587 | 47.1918 | 53.895 | -1281.846
2027-10-19 23:00 | -4987.19 | 6.8587 | 46.4721 | 53.895 | -1461.6011
2027-10-21 | -5367.15 | 6.8587 | 45.9771 | 53.895 | -1572.9564
2027-10-22 01:00 | -5766.31 | 6.8587 | 45.5092 | 53.895 | -1689.9386
2027-10-23 02:00 | -5974.41 | 6.8587 | 45.1864 | 53.895 | -1750.9267
2027-10-24 03:00 | -6053.1 | 6.8587 | 44.949 | 53.895 | -1773.9885
2027-10-25 04:00 | -6112.54 | 6.8587 | 44.7572 | 53.895 | -1791.4086
2027-10-26 05:00 | -6031.08 | 6.8587 | 44.6744 | 53.895 | -1767.5351
2027-10-27 06:00 | -5972.28 | 6.8587 | 44.6254 | 53.895 | -1750.3025
2027-10-28 07:00 | -5286.35 | 6.8587 | 45.0264 | 53.895 | -1549.2763
2027-10-29 08:00 | -5076.28 | 6.8587 | 45.1971 | 53.895 | -1487.7108
2027-10-30 09:00 | -3638.92 | 6.8587 | 46.1984 | 53.895 | -1066.4622
2027-10-31 10:00 | -2044.8 | 6.8587 | 47.46 | 53.895 | -599.2717
2027-11-01 11:00 | -796.004 | 2.6474 | 47.7264 | 53.895 | -233.2857
2027-11-02 12:00 | 0 | 1 | 49.4466 | 53.895 | 0
2027-11-03 13:00 | 2743.77 | 1 | 49.2513 | 53.895 | 804.1196
2027-11-04 14:00 | 2745.34 | 1 | 69.7798 | 53.895 | 804.5797
2027-11-05 15:00 | 3965.44 | 1.3677 | 64.1319 | 53.895 | 1162.1557
2027-11-06 16:00 | 4048.51 | 1.452 | 63.9569 | 53.895 | 1186.5012
2027-11-07 17:00 | 3796.78 | 1.3341 | 64.4846 | 53.895 | 1112.7264
2027-11-08 18:00 | 2827.55 | 1 | 70.7717 | 53.895 | 828.6731
2027-11-09 19:00 | 2027.11 | 1 | 51.0156 | 53.895 | 594.0873
2027-11-10 20:00 | -947.128 | 3.7609 | 50.1835 | 53.895 | -277.5758
2027-11-11 21:00 | -1653.87 | 5.7507 | 49.6849 | 53.895 | -484.7015
2027-11-12 22:00 | -3092.05 | 6.8587 | 48.6719 | 53.895 | -906.1904
2027-11-13 23:00 | -3775.76 | 6.8587 | 47.9078 | 53.895 | -1106.566
2027-11-15 | -4395.12 | 6.8587 | 47.2156 | 53.895 | -1288.0825
2027-11-16 01:00 | -4790.65 | 6.8587 | 46.6711 | 53.895 | -1404.0009
2027-11-17 02:00 | -5113.92 | 6.8587 | 46.2441 | 53.895 | -1498.742
2027-11-18 03:00 | -5147.87 | 6.8587 | 46.0178 | 53.895 | -1508.6918
2027-11-19 04:00 | -5231.65 | 6.8587 | 45.812 | 53.895 | -1533.2453
2027-11-20 05:00 | -5004.7 | 6.8587 | 45.8352 | 53.895 | -1466.7328
2027-11-21 06:00 | -4855.13 | 6.8587 | 45.8605 | 53.895 | -1422.8981
2027-11-22 07:00 | -4139.17 | 6.8587 | 46.2939 | 53.895 | -1213.071
2027-11-23 08:00 | -3672.93 | 6.8587 | 46.6671 | 53.895 | -1076.4295
2027-11-24 09:00 | -2064.83 | 6.8587 | 47.8349 | 53.895 | -605.1419
2027-11-25 10:00 | -816.674 | 2.7052 | 48.052 | 53.895 | -239.3435
2027-11-26 11:00 | 2381.41 | 1 | 49.3391 | 53.895 | 697.9224
2027-11-27 12:00 | 2854.45 | 1 | 67.0387 | 53.895 | 836.5567
2027-11-28 13:00 | 3528.24 | 1.2057 | 64.3814 | 53.895 | 1034.0251
2027-11-29 14:00 | 4465.45 | 1.5152 | 64.8082 | 53.895 | 1308.6942
2027-11-30 15:00 | 5978.67 | 2.0436 | 65.045 | 53.895 | 1752.1752
2027-12-01 16:00 | 6034.19 | 2.0428 | 65.612 | 53.895 | 1768.4465
2027-12-02 17:00 | 5343.71 | 1.8375 | 65.6679 | 53.895 | 1566.0868
2027-12-03 18:00 | 3515.59 | 1.2128 | 65.7687 | 53.895 | 1030.3177
2027-12-04 19:00 | 2792.69 | 1 | 51.6362 | 53.895 | 818.4566
2027-12-05 20:00 | 0 | 0 | 52.0779 | 53.895 | 0
2027-12-06 21:00 | -1097.06 | 3.857 | 50.4054 | 53.895 | -321.5165
2027-12-07 22:00 | -2321.82 | 6.8587 | 49.8472 | 53.895 | -680.4583
2027-12-08 23:00 | -3274.83 | 6.8587 | 48.8682 | 53.895 | -959.7579
2027-12-10 | -3617.66 | 6.8587 | 48.3237 | 53.895 | -1060.2315
2027-12-11 01:00 | -3655.32 | 6.8587 | 48.0453 | 53.895 | -1071.2685
2027-12-12 02:00 | -3796.79 | 6.8587 | 47.79 | 53.895 | -1112.7293
2027-12-13 03:00 | -3912.67 | 6.8587 | 47.555 | 53.895 | -1146.6904
2027-12-14 04:00 | -3909.63 | 6.8587 | 47.4207 | 53.895 | -1145.7994
2027-12-15 05:00 | -3556.29 | 6.8587 | 47.5615 | 53.895 | -1042.2457
2027-12-16 06:00 | -3336.66 | 6.8587 | 47.6833 | 53.895 | -977.8785
2027-12-17 07:00 | -2809.06 | 6.8587 | 48.0264 | 53.895 | -823.2542
2027-12-18 08:00 | -2658.65 | 6.8587 | 48.1828 | 53.895 | -779.1734
2027-12-19 09:00 | -1411.37 | 4.6996 | 48.6277 | 53.895 | -413.6317
2027-12-20 10:00 | 76.2039 | 1 | 50.1934 | 53.895 | 22.3332
2027-12-21 11:00 | 2550.45 | 1 | 64.9392 | 53.895 | 747.4631
2027-12-22 12:00 | 3749.72 | 1.2022 | 65.5349 | 53.895 | 1098.9345
2027-12-23 13:00 | 4422.29 | 1.3992 | 66.128 | 53.895 | 1296.0453
2027-12-24 14:00 | 4069.29 | 1.2703 | 66.6683 | 53.895 | 1192.5912
2027-12-25 15:00 | 5048.73 | 1.7894 | 65.0579 | 53.895 | 1479.6367
2027-12-26 16:00 | 5199.83 | 1.7651 | 65.9128 | 53.895 | 1523.9197
2027-12-27 17:00 | 4527.16 | 1.6111 | 65.4735 | 53.895 | 1326.7796
2027-12-28 18:00 | 2770.17 | 1 | 67.2773 | 53.895 | 811.8567
2027-12-29 19:00 | 2881.62 | 1 | 51.7435 | 53.895 | 844.5195
2027-12-30 20:00 | -930.374 | 3.6489 | 51.0689 | 53.895 | -272.6657
2027-12-31 21:00 | -1889.1 | 6.4685 | 50.4722 | 53.895 | -553.6406
2028-01-01 22:00 | -3050.29 | 6.8587 | 49.3996 | 53.895 | -893.9518
2028-01-02 23:00 | -4059.96 | 6.8587 | 48.3723 | 53.895 | -1189.8568
2028-01-04 | -4750.61 | 6.8587 | 47.5556 | 53.895 | -1392.2664
2028-01-05 01:00 | -5161.95 | 6.8587 | 46.925 | 53.895 | -1512.8182
2028-01-06 02:00 | -5685.5 | 6.8587 | 46.3189 | 53.895 | -1666.2556
2028-01-07 03:00 | -5968.31 | 6.8587 | 45.8658 | 53.895 | -1749.139
2028-01-08 04:00 | -6288.9 | 6.8587 | 45.4142 | 53.895 | -1843.0947
2028-01-09 05:00 | -6512.81 | 6.8587 | 45.0441 | 53.895 | -1908.7162
2028-01-10 06:00 | -5437.6 | 6.8587 | 45.5924 | 53.895 | -1593.6033
2028-01-11 07:00 | -4325.02 | 6.8587 | 46.325 | 53.895 | -1267.5382
2028-01-12 08:00 | -4085.44 | 6.8587 | 46.5975 | 53.895 | -1197.3243
2028-01-13 09:00 | -2979.87 | 6.8587 | 47.4028 | 53.895 | -873.3137
2028-01-14 10:00 | -1794.94 | 6.0596 | 48.1953 | 53.895 | -526.045
2028-01-15 11:00 | -918.698 | 3.1228 | 48.4196 | 53.895 | -269.2438
2028-01-16 12:00 | 0 | 0 | 50.009 | 53.895 | 0
2028-01-17 13:00 | 2979.92 | 1 | 49.7117 | 53.895 | 873.3283
2028-01-18 14:00 | 2734.39 | 1 | 50.26 | 53.895 | 801.3706
2028-01-19 15:00 | 2737.66 | 1 | 50.5182 | 53.895 | 802.3289
2028-01-20 16:00 | 2928.13 | 1.0619 | 64.1099 | 53.895 | 858.1502
2028-01-21 17:00 | 2746.45 | 1 | 69.6315 | 53.895 | 804.905
2028-01-22 18:00 | 2718.28 | 1 | 50.9766 | 53.895 | 796.6492
2028-01-23 19:00 | -492.472 | 2.2763 | 50.4959 | 53.895 | -144.3293
2028-01-24 20:00 | -1376.01 | 4.9706 | 49.9193 | 53.895 | -403.2687
2028-01-25 21:00 | -2133 | 6.8587 | 49.5209 | 53.895 | -625.1206
2028-01-26 22:00 | -2959.88 | 6.8587 | 48.7647 | 53.895 | -867.4552
2028-01-27 23:00 | -4583.91 | 6.8587 | 47.4308 | 53.895 | -1343.4114
2028-01-29 | -5087.48 | 6.8587 | 46.7227 | 53.895 | -1490.9932
2028-01-30 01:00 | -5353.82 | 6.8587 | 46.2637 | 53.895 | -1569.0498
2028-01-31 02:00 | -5370.83 | 6.8587 | 46.0441 | 53.895 | -1574.0349
2028-02-01 03:00 | -5583.45 | 6.8587 | 45.7359 | 53.895 | -1636.3477
2028-02-02 04:00 | -5573.8 | 6.8587 | 45.5797 | 53.895 | -1633.5195
2028-02-03 05:00 | -5306.94 | 6.8587 | 45.6482 | 53.895 | -1555.3106
2028-02-04 06:00 | -4254.43 | 6.8587 | 46.2983 | 53.895 | -1246.8504
2028-02-05 07:00 | -3112.11 | 6.8587 | 47.157 | 53.895 | -912.0694
2028-02-06 08:00 | -2956.64 | 6.8587 | 47.4266 | 53.895 | -866.5056
2028-02-07 09:00 | -1897.33 | 6.4146 | 48.1505 | 53.895 | -556.0525
2028-02-08 10:00 | -783.203 | 2.6334 | 48.3114 | 53.895 | -229.5341
2028-02-09 11:00 | 2323.72 | 1 | 49.5627 | 53.895 | 681.0151
2028-02-10 12:00 | 3084.53 | 1 | 49.9491 | 53.895 | 903.9865
2028-02-11 13:00 | 3021.23 | 1 | 65.4042 | 53.895 | 885.4351
2028-02-12 14:00 | 4612.7 | 1.3438 | 67.1595 | 53.895 | 1351.8489
2028-02-13 15:00 | 5473.35 | 1.6598 | 66.8988 | 53.895 | 1604.0805
2028-02-14 16:00 | 8145.26 | 2.7164 | 65.8703 | 53.895 | 2387.1401
2028-02-15 17:00 | 7227.67 | 2.3492 | 66.799 | 53.895 | 2118.221
2028-02-16 18:00 | 5875.65 | 1.9128 | 67.0382 | 53.895 | 1721.983
2028-02-17 19:00 | 4082.01 | 1.3921 | 66.4538 | 53.895 | 1196.319
2028-02-18 20:00 | 3013.45 | 1 | 68.2216 | 53.895 | 883.155
2028-02-19 21:00 | 2770.06 | 1 | 52.066 | 53.895 | 811.8244
2028-02-20 22:00 | 287.75 | 1 | 52.4262 | 53.895 | 84.3312
2028-02-21 23:00 | -1094.57 | 4.1724 | 50.9105 | 53.895 | -320.7868
2028-02-23 | -1707.39 | 5.8209 | 50.4226 | 53.895 | -500.3866
2028-02-24 01:00 | -2274.86 | 6.8587 | 50.0144 | 53.895 | -666.6957
2028-02-25 02:00 | -2911.71 | 6.8587 | 49.3616 | 53.895 | -853.338
2028-02-26 03:00 | -3130.09 | 6.8587 | 48.962 | 53.895 | -917.3388
2028-02-27 04:00 | -3547.58 | 6.8587 | 48.4748 | 53.895 | -1039.6931
2028-02-28 05:00 | -3664.18 | 6.8587 | 48.2097 | 53.895 | -1073.8652
2028-02-29 06:00 | -3441.3 | 6.8587 | 48.2084 | 53.895 | -1008.5455
2028-03-01 07:00 | -3181.02 | 6.8587 | 48.2998 | 53.895 | -932.2649
2028-03-02 08:00 | -3087.32 | 6.8587 | 48.3241 | 53.895 | -904.8042
2028-03-03 09:00 | -2000.32 | 6.6917 | 48.9808 | 53.895 | -586.2359
2028-03-04 10:00 | -925.688 | 3.0472 | 49.0471 | 53.895 | -271.2924
2028-03-05 11:00 | 987.294 | 1 | 50.4677 | 53.895 | 289.3473
2028-03-06 12:00 | 2768.37 | 1 | 50.4664 | 53.895 | 811.3292
2028-03-07 13:00 | 2757.45 | 1 | 50.853 | 53.895 | 808.1288
2028-03-08 14:00 | 2742.54 | 1 | 64.5956 | 53.895 | 803.7591
2028-03-09 15:00 | 4543.9 | 1.6195 | 64.8374 | 53.895 | 1331.6856
2028-03-10 16:00 | 4626.31 | 1.6478 | 65.1781 | 53.895 | 1355.8376
2028-03-11 17:00 | 4503.83 | 1.5892 | 65.5213 | 53.895 | 1319.9423
2028-03-12 18:00 | 2922.51 | 1.0293 | 65.6666 | 53.895 | 856.5031
2028-03-13 19:00 | 2694.73 | 1 | 51.834 | 53.895 | 789.7474
2028-03-14 20:00 | -614.378 | 2.6286 | 51.2111 | 53.895 | -180.0564
2028-03-15 21:00 | -1351.68 | 4.8079 | 50.6049 | 53.895 | -396.1383
2028-03-16 22:00 | -2602.61 | 6.8587 | 49.8513 | 53.895 | -762.7497
2028-03-17 23:00 | -3235.89 | 6.8587 | 49.1062 | 53.895 | -948.3457
2028-03-19 | -3339.21 | 6.8587 | 48.7522 | 53.895 | -978.6258
2028-03-20 01:00 | -3571.58 | 6.8587 | 48.3781 | 53.895 | -1046.7268
2028-03-21 02:00 | -3780.84 | 6.8587 | 48.0885 | 53.895 | -1108.0548
2028-03-22 03:00 | -3816.84 | 6.8587 | 47.9052 | 53.895 | -1118.6054
2028-03-23 04:00 | -3549.31 | 6.8587 | 47.9703 | 53.895 | -1040.2001
2028-03-24 05:00 | -3376.84 | 6.8587 | 48.0259 | 53.895 | -989.6541
2028-03-25 06:00 | -3405.43 | 6.8587 | 47.9665 | 53.895 | -998.033
2028-03-26 07:00 | -2685.48 | 6.8587 | 48.3999 | 53.895 | -787.0365
2028-03-27 08:00 | -2164.24 | 6.8587 | 48.8206 | 53.895 | -634.2761
2028-03-28 09:00 | -617.79 | 2.0152 | 48.9475 | 53.895 | -181.0564
2028-03-29 10:00 | 1930.38 | 1 | 50.2902 | 53.895 | 565.7385
2028-03-30 11:00 | 2962.31 | 1 | 69.6811 | 53.895 | 868.1674
2028-03-31 12:00 | 3737.43 | 1.2136 | 65.8366 | 53.895 | 1095.3326
2028-04-01 13:00 | 3014.59 | 1 | 66.5869 | 53.895 | 883.4891
2028-04-02 14:00 | 3034.4 | 1 | 66.8026 | 53.895 | 889.2949
2028-04-03 15:00 | 4350.64 | 1.4211 | 66.3294 | 53.895 | 1275.0467
2028-04-04 16:00 | 5034.85 | 1.6416 | 66.5872 | 53.895 | 1475.5689
2028-04-05 17:00 | 4396.36 | 1.4369 | 66.7833 | 53.895 | 1288.4459
2028-04-06 18:00 | 3017.07 | 1 | 69.3101 | 53.895 | 884.2159
2028-04-07 19:00 | 2977.7 | 1 | 51.9397 | 53.895 | 872.6777
2028-04-08 20:00 | -354.454 | 1.7993 | 51.5663 | 53.895 | -103.8802
2028-04-09 21:00 | -918.428 | 3.4737 | 50.8803 | 53.895 | -269.1647
2028-04-10 22:00 | -1887.94 | 6.4829 | 50.4648 | 53.895 | -553.3006
2028-04-11 23:00 | -2413.8 | 6.8587 | 49.9126 | 53.895 | -707.4149
2028-04-13 | -2648.14 | 6.8587 | 49.5109 | 53.895 | -776.0932
2028-04-14 01:00 | -2934.19 | 6.8587 | 49.114 | 53.895 | -859.9262
2028-04-15 02:00 | -3391.41 | 6.8587 | 48.6654 | 53.895 | -993.9242
2028-04-16 03:00 | -3216.65 | 6.8587 | 48.6134 | 53.895 | -942.7071
2028-04-17 04:00 | -3098.8 | 6.8587 | 48.5902 | 53.895 | -908.1686
2028-04-18 05:00 | -2620.98 | 6.8587 | 48.8498 | 53.895 | -768.1334
2028-04-19 06:00 | -2463.09 | 6.8587 | 48.9558 | 53.895 | -721.8604
2028-04-20 07:00 | -2238.33 | 6.8587 | 49.0988 | 53.895 | -655.9898
2028-04-21 08:00 | -1830.77 | 6.039 | 49.2416 | 53.895 | -536.5457
2028-04-22 09:00 | -909.147 | 3.0551 | 49.3229 | 53.895 | -266.4447
2028-04-23 10:00 | 1990.8 | 1 | 50.5168 | 53.895 | 583.4459
2028-04-24 11:00 | 2898.21 | 1 | 66.4658 | 53.895 | 849.3815
2028-04-25 12:00 | 2947.34 | 1 | 66.9256 | 53.895 | 863.7801
2028-04-26 13:00 | 3018.22 | 1 | 66.6107 | 53.895 | 884.553
2028-04-27 14:00 | 3467.41 | 1.1342 | 66.3232 | 53.895 | 1016.1976
2028-04-28 15:00 | 5839.95 | 1.9228 | 66.4185 | 53.895 | 1711.5204
2028-04-29 16:00 | 6138.42 | 2.0383 | 66.6974 | 53.895 | 1798.9933
2028-04-30 17:00 | 6138.43 | 2.0397 | 66.9679 | 53.895 | 1798.9962
2028-05-01 18:00 | 4621.53 | 1.5127 | 67.389 | 53.895 | 1354.4367
2028-05-02 19:00 | 3039.58 | 1 | 68.0318 | 53.895 | 890.813
2028-05-03 20:00 | 2982.51 | 1 | 52.4721 | 53.895 | 874.0874
2028-05-04 21:00 | -10.708 | 0.72519 | 52.8934 | 53.895 | -3.1382
2028-05-05 22:00 | -926.283 | 3.5537 | 51.366 | 53.895 | -271.4667
2028-05-06 23:00 | -1526.98 | 5.2604 | 50.8954 | 53.895 | -447.5137
2028-05-08 | -1810.71 | 6.0216 | 50.6146 | 53.895 | -530.6667
2028-05-09 01:00 | -1933.6 | 6.3573 | 50.4256 | 53.895 | -566.6822
2028-05-10 02:00 | -2037.14 | 6.6762 | 50.2661 | 53.895 | -597.0268
2028-05-11 03:00 | -2045.71 | 6.6805 | 50.1454 | 53.895 | -599.5384
2028-05-12 04:00 | -2154.91 | 6.8587 | 50.0154 | 53.895 | -631.5418
2028-05-13 05:00 | -1928.4 | 6.2931 | 49.9574 | 53.895 | -565.1583
2028-05-14 06:00 | -1836.37 | 6.0507 | 49.9306 | 53.895 | -538.1869
2028-05-15 07:00 | -1381.73 | 4.5789 | 49.9139 | 53.895 | -404.9451
2028-05-16 08:00 | -834.879 | 2.9458 | 50.0189 | 53.895 | -244.6789
2028-05-17 09:00 | 604 | 1 | 51.3303 | 53.895 | 177.0149
2028-05-18 10:00 | 2908.75 | 1 | 68.9636 | 53.895 | 852.4705
2028-05-19 11:00 | 4407.73 | 1.4505 | 66.2557 | 53.895 | 1291.7781
2028-05-20 12:00 | 5846.57 | 1.9098 | 66.7714 | 53.895 | 1713.4605
2028-05-21 13:00 | 6698.93 | 2.1698 | 67.3187 | 53.895 | 1963.2626
2028-05-22 14:00 | 7157.7 | 2.3466 | 67.542 | 53.895 | 2097.7148
2028-05-23 15:00 | 8063.25 | 2.6582 | 67.7787 | 53.895 | 2363.1053
2028-05-24 16:00 | 8497.89 | 2.8037 | 68.0931 | 53.895 | 2490.4857
2028-05-25 17:00 | 8240.31 | 2.6661 | 68.6644 | 53.895 | 2414.9965
2028-05-26 18:00 | 6838.5 | 2.2053 | 68.9076 | 53.895 | 2004.1665
2028-05-27 19:00 | 4883.19 | 1.5763 | 68.9064 | 53.895 | 1431.1217
2028-05-28 20:00 | 3064.88 | 1 | 53.713 | 53.895 | 898.2277
2028-05-29 21:00 | 3017.93 | 1 | 53.4722 | 53.895 | 884.468
2028-05-30 22:00 | -825.57 | 3.2531 | 52.6706 | 53.895 | -241.9507
2028-05-31 23:00 | -1352.25 | 4.6557 | 51.9498 | 53.895 | -396.3054
2028-06-02 | -1907.25 | 6.3227 | 51.5015 | 53.895 | -558.9598
2028-06-03 01:00 | -2238.23 | 6.8587 | 51.1017 | 53.895 | -655.9605
2028-06-04 02:00 | -2393.13 | 6.8587 | 50.7508 | 53.895 | -701.3572
2028-06-05 03:00 | -2663.04 | 6.8587 | 50.328 | 53.895 | -780.46
2028-06-06 04:00 | -2821.96 | 6.8587 | 50.0419 | 53.895 | -827.0348
2028-06-07 05:00 | -2616.67 | 6.8587 | 50.0148 | 53.895 | -766.8703
2028-06-08 06:00 | -2458.38 | 6.8587 | 50.0227 | 53.895 | -720.4801
2028-06-09 07:00 | -1640.16 | 5.3362 | 50.1972 | 53.895 | -480.6834
2028-06-10 08:00 | -1195.16 | 4.0241 | 50.2862 | 53.895 | -350.2668
2028-06-11 09:00 | 0 | 1 | 51.7242 | 53.895 | 0
2028-06-12 10:00 | 2709.22 | 1 | 66.1869 | 53.895 | 793.994
2028-06-13 11:00 | 4969.17 | 1.6175 | 66.6862 | 53.895 | 1456.32
2028-06-14 12:00 | 6547.86 | 2.2192 | 66.6159 | 53.895 | 1918.9883
2028-06-15 13:00 | 7714.36 | 2.5496 | 67.4468 | 53.895 | 2260.8557
2028-06-16 14:00 | 8427.69 | 2.8335 | 67.6642 | 53.895 | 2469.9121
2028-06-17 15:00 | 9941.59 | 3.3752 | 67.9288 | 53.895 | 2913.5924
2028-06-18 16:00 | 10498.1 | 3.5269 | 68.5346 | 53.895 | 3076.6894
2028-06-19 17:00 | 10411.2 | 3.4969 | 68.9215 | 53.895 | 3051.2215
2028-06-20 18:00 | 8702.26 | 2.9064 | 69.2846 | 53.895 | 2550.3806
2028-06-21 19:00 | 6757.47 | 2.2235 | 69.5379 | 53.895 | 1980.419
2028-06-22 20:00 | 3958.5 | 1.2212 | 70.3779 | 53.895 | 1160.1218
2028-06-23 21:00 | 2975.44 | 1 | 54.338 | 53.895 | 872.0154
2028-06-24 22:00 | 0 | 0 | 54.5785 | 53.895 | 0
2028-06-25 23:00 | -1077.77 | 3.6798 | 52.6789 | 53.895 | -315.8632
2028-06-27 | -1629.61 | 5.4756 | 52.2076 | 53.895 | -477.5915
2028-06-28 01:00 | -2090.02 | 6.7939 | 51.8221 | 53.895 | -612.5244
2028-06-29 02:00 | -2590.06 | 6.8587 | 51.2114 | 53.895 | -759.0717
2028-06-30 03:00 | -2657.89 | 6.8587 | 50.8663 | 53.895 | -778.9507
2028-07-01 04:00 | -3243.73 | 6.8587 | 50.2566 | 53.895 | -950.6434
2028-07-02 05:00 | -3515.21 | 6.8587 | 49.8287 | 53.895 | -1030.2064
2028-07-03 06:00 | -2640 | 6.8587 | 50.2114 | 53.895 | -773.7076
2028-07-04 07:00 | -1586.21 | 5.1432 | 50.5164 | 53.895 | -464.8723
2028-07-05 08:00 | -887.408 | 3.0276 | 50.6638 | 53.895 | -260.0736
2028-07-06 09:00 | 1956.32 | 1 | 51.7884 | 53.895 | 573.3408
2028-07-07 10:00 | 2876.64 | 1 | 67.4495 | 53.895 | 843.06
2028-07-08 11:00 | 4850.42 | 1.6163 | 66.8839 | 53.895 | 1421.5178
2028-07-09 12:00 | 6141.98 | 2.0864 | 67.0222 | 53.895 | 1800.0367
2028-07-10 13:00 | 6763.44 | 2.3007 | 67.4144 | 53.895 | 1982.1686
2028-07-11 14:00 | 7426.55 | 2.5265 | 67.7583 | 53.895 | 2176.507
2028-07-12 15:00 | 7529.33 | 2.5808 | 67.9405 | 53.895 | 2206.6288
2028-07-13 16:00 | 9521.64 | 3.2575 | 68.1874 | 53.895 | 2790.5172
2028-07-14 17:00 | 8361.3 | 2.8571 | 68.621 | 53.895 | 2450.4551
2028-07-15 18:00 | 6867.71 | 2.3085 | 68.997 | 53.895 | 2012.7271
2028-07-16 19:00 | 4609.43 | 1.533 | 69.102 | 53.895 | 1350.8906
2028-07-17 20:00 | 3179.04 | 1.0563 | 68.9068 | 53.895 | 931.6847
2028-07-18 21:00 | 2969.48 | 1 | 75.7071 | 53.895 | 870.2687
2028-07-19 22:00 | 2958.32 | 1 | 53.8861 | 53.895 | 866.998
2028-07-20 23:00 | -571.616 | 2.4322 | 53.2078 | 53.895 | -167.5241
2028-07-22 | -1073.32 | 3.8239 | 52.4943 | 53.895 | -314.559
2028-07-23 01:00 | -1449.97 | 4.8971 | 52.0879 | 53.895 | -424.9443
2028-07-24 02:00 | -1821.05 | 5.9893 | 51.833 | 53.895 | -533.6971
2028-07-25 03:00 | -2188.08 | 6.8587 | 51.5377 | 53.895 | -641.2629
2028-07-26 04:00 | -2688.14 | 6.8587 | 50.9388 | 53.895 | -787.8161
2028-07-27 05:00 | -2787.29 | 6.8587 | 50.6675 | 53.895 | -816.8741
2028-07-28 06:00 | -1804.72 | 5.8319 | 50.9625 | 53.895 | -528.9112
2028-07-29 07:00 | -1373.45 | 4.5061 | 50.9896 | 53.895 | -402.5185
2028-07-30 08:00 | -1281.37 | 4.3492 | 51.0672 | 53.895 | -375.5325
2028-07-31 09:00 | -631.032 | 2.2743 | 51.1233 | 53.895 | -184.9372
2028-08-01 10:00 | 2393.4 | 1 | 52.0525 | 53.895 | 701.4363
2028-08-02 11:00 | 2882.25 | 1 | 68.0448 | 53.895 | 844.7041
2028-08-03 12:00 | 4023.09 | 1.3804 | 66.7534 | 53.895 | 1179.0513
2028-08-04 13:00 | 4682.88 | 1.6183 | 66.9151 | 53.895 | 1372.4167
2028-08-05 14:00 | 5146.8 | 1.8086 | 66.9505 | 53.895 | 1508.3782
2028-08-06 15:00 | 5390.5 | 1.8995 | 67.1444 | 53.895 | 1579.7996
2028-08-07 16:00 | 7671.44 | 2.7038 | 67.2813 | 53.895 | 2248.2771
2028-08-08 17:00 | 6428.25 | 2.2879 | 67.5578 | 53.895 | 1883.9341
2028-08-09 18:00 | 5124.02 | 1.7913 | 67.9039 | 53.895 | 1501.702
2028-08-10 19:00 | 3060.17 | 1.0547 | 68.0399 | 53.895 | 896.8473
2028-08-11 20:00 | 2799.51 | 1 | 53.7556 | 53.895 | 820.4554
2028-08-12 21:00 | 2747.17 | 1 | 53.6747 | 53.895 | 805.1161
2028-08-13 22:00 | 2730.77 | 1 | 53.5851 | 53.895 | 800.3097
2028-08-14 23:00 | -739.114 | 2.9815 | 52.8495 | 53.895 | -216.6129
2028-08-16 | -1210.47 | 4.2167 | 52.2175 | 53.895 | -354.7537
2028-08-17 01:00 | -1515.46 | 5.0791 | 51.8772 | 53.895 | -444.1375
2028-08-18 02:00 | -1778.09 | 5.8458 | 51.6619 | 53.895 | -521.1067
2028-08-19 03:00 | -2296.4 | 6.8587 | 51.3292 | 53.895 | -673.0084
2028-08-20 04:00 | -2761.36 | 6.8587 | 50.7607 | 53.895 | -809.2747
2028-08-21 05:00 | -2567.3 | 6.8587 | 50.7051 | 53.895 | -752.4014
2028-08-22 06:00 | -2644.32 | 6.8587 | 50.5438 | 53.895 | -774.9737
2028-08-23 07:00 | -2570.61 | 6.8587 | 50.5014 | 53.895 | -753.3714
2028-08-24 08:00 | -3019.13 | 6.8587 | 50.1141 | 53.895 | -884.8197
2028-08-25 09:00 | -2616.73 | 6.8587 | 50.2482 | 53.895 | -766.8879
2028-08-26 10:00 | -2398.38 | 6.8587 | 50.315 | 53.895 | -702.8958
2028-08-27 11:00 | -993.544 | 3.1992 | 50.4518 | 53.895 | -291.179
2028-08-28 12:00 | 164.573 | 1 | 51.9862 | 53.895 | 48.2316
2028-08-29 13:00 | 2725.04 | 1 | 51.7103 | 53.895 | 798.6304
2028-08-30 14:00 | 2746.97 | 1 | 52.0898 | 53.895 | 805.0574
2028-08-31 15:00 | 2856.68 | 1.0388 | 65.6988 | 53.895 | 837.2103
2028-09-01 16:00 | 2979.26 | 1.0713 | 65.9271 | 53.895 | 873.1349
2028-09-02 17:00 | 2869.69 | 1.032 | 66.0374 | 53.895 | 841.0231
2028-09-03 18:00 | 2737.05 | 1 | 52.6116 | 53.895 | 802.1502
2028-09-04 19:00 | 0 | 0 | 53.1183 | 53.895 | 0
2028-09-05 20:00 | -1543.91 | 5.2614 | 51.4564 | 53.895 | -452.4754
2028-09-06 21:00 | -2366.91 | 6.8587 | 50.8789 | 53.895 | -693.6728
2028-09-07 22:00 | -3791.05 | 6.8587 | 49.6336 | 53.895 | -1111.0471
2028-09-08 23:00 | -4444.44 | 6.8587 | 48.8452 | 53.895 | -1302.5368
2028-09-10 | -4642.81 | 6.8587 | 48.3822 | 53.895 | -1360.6733
2028-09-11 01:00 | -4816 | 6.8587 | 48.0242 | 53.895 | -1411.4303
2028-09-12 02:00 | -5069.19 | 6.8587 | 47.6555 | 53.895 | -1485.6329
2028-09-13 03:00 | -4964.99 | 6.8587 | 47.5351 | 53.895 | -1455.0949
2028-09-14 04:00 | -4806.92 | 6.8587 | 47.5159 | 53.895 | -1408.7692
2028-09-15 05:00 | -4475.21 | 6.8587 | 47.6517 | 53.895 | -1311.5546
2028-09-16 06:00 | -4196.62 | 6.8587 | 47.7838 | 53.895 | -1229.9079
2028-09-17 07:00 | -3768.28 | 6.8587 | 48.06 | 53.895 | -1104.3739
2028-09-18 08:00 | -3751.67 | 6.8587 | 48.106 | 53.895 | -1099.5059
2028-09-19 09:00 | -2835.57 | 6.8587 | 48.7385 | 53.895 | -831.0235
2028-09-20 10:00 | -1941.97 | 6.4385 | 49.3663 | 53.895 | -569.1352
2028-09-21 11:00 | -1514.67 | 5.0013 | 49.5126 | 53.895 | -443.906
2028-09-22 12:00 | -1114.89 | 3.8319 | 49.6831 | 53.895 | -326.742
2028-09-23 13:00 | -405.473 | 1.6328 | 49.9732 | 53.895 | -118.8324
2028-09-24 14:00 | -531.799 | 2.2718 | 50.1863 | 53.895 | -155.8549
2028-09-25 15:00 | 2308.38 | 1 | 50.9486 | 53.895 | 676.5194
2028-09-26 16:00 | 121.687 | 1 | 51.6875 | 53.895 | 35.6629
2028-09-27 17:00 | 2728.81 | 1 | 51.1838 | 53.895 | 799.7353
2028-09-28 18:00 | 0 | 0 | 51.9386 | 53.895 | 0
2028-09-29 19:00 | -1051.63 | 3.9828 | 50.5847 | 53.895 | -308.2023
2028-09-30 20:00 | -2688.8 | 6.8587 | 49.8184 | 53.895 | -788.0095
2028-10-01 21:00 | -3553.09 | 6.8587 | 48.9325 | 53.895 | -1041.3079
2028-10-02 22:00 | -4631.48 | 6.8587 | 47.9584 | 53.895 | -1357.3528
2028-10-03 23:00 | -5469.1 | 6.8587 | 47.066 | 53.895 | -1602.835
2028-10-05 | -5811.61 | 6.8587 | 46.5468 | 53.895 | -1703.2148
2028-10-06 01:00 | -5939.06 | 6.8587 | 46.2267 | 53.895 | -1740.5667
2028-10-07 02:00 | -5886.16 | 6.8587 | 46.0967 | 53.895 | -1725.0632
2028-10-08 03:00 | -5744.09 | 6.8587 | 46.0413 | 53.895 | -1683.4266
2028-10-09 04:00 | -5819.08 | 6.8587 | 45.9024 | 53.895 | -1705.404
2028-10-10 05:00 | -5382.51 | 6.8587 | 46.0834 | 53.895 | -1577.458
2028-10-11 06:00 | -4817.22 | 6.8587 | 46.4398 | 53.895 | -1411.7878
2028-10-12 07:00 | -4294.73 | 6.8587 | 46.8262 | 53.895 | -1258.6611
2028-10-13 08:00 | -3848.94 | 6.8587 | 47.1976 | 53.895 | -1128.013
2028-10-14 09:00 | -2420.03 | 6.8587 | 48.2476 | 53.895 | -709.2408
2028-10-15 10:00 | -1065.05 | 3.5205 | 48.6952 | 53.895 | -312.1353
2028-10-16 11:00 | 189.554 | 1 | 50.3709 | 53.895 | 55.5528
2028-10-17 12:00 | 2758.77 | 1 | 50.2433 | 53.895 | 808.5157
2028-10-18 13:00 | 2737.68 | 1 | 67.8316 | 53.895 | 802.3348
2028-10-19 14:00 | 2794.91 | 1 | 64.9055 | 53.895 | 819.1073
2028-10-20 15:00 | 4164.16 | 1.4932 | 64.8008 | 53.895 | 1220.3948
2028-10-21 16:00 | 4740.25 | 1.6804 | 65.295 | 53.895 | 1389.2301
2028-10-22 17:00 | 4722.98 | 1.6824 | 65.5336 | 53.895 | 1384.1688
2028-10-23 18:00 | 3298.15 | 1.1804 | 65.6639 | 53.895 | 966.5923
2028-10-24 19:00 | 2720.13 | 1 | 52.105 | 53.895 | 797.1914
2028-10-25 20:00 | -567.69 | 2.4604 | 51.5103 | 53.895 | -166.3735
2028-10-26 21:00 | -1574.57 | 5.5261 | 50.9063 | 53.895 | -461.4609
2028-10-27 22:00 | -2838.34 | 6.8587 | 49.9984 | 53.895 | -831.8353
2028-10-28 23:00 | -3577.06 | 6.8587 | 49.1845 | 53.895 | -1048.3328
2028-10-30 | -3897.49 | 6.8587 | 48.6676 | 53.895 | -1142.2416
2028-10-31 01:00 | -4549.54 | 6.8587 | 47.976 | 53.895 | -1333.3386
2028-11-01 02:00 | -4668.55 | 6.8587 | 47.6762 | 53.895 | -1368.2169
2028-11-02 03:00 | -4795.92 | 6.8587 | 47.4062 | 53.895 | -1405.5454
2028-11-03 04:00 | -4986.24 | 6.8587 | 47.124 | 53.895 | -1461.3227
2028-11-04 05:00 | -4532.5 | 6.8587 | 47.2817 | 53.895 | -1328.3446
2028-11-05 06:00 | -4255.6 | 6.8587 | 47.4057 | 53.895 | -1247.1932
2028-11-06 07:00 | -3440.51 | 6.8587 | 47.9297 | 53.895 | -1008.3139
2028-11-07 08:00 | -3141.03 | 6.8587 | 48.2071 | 53.895 | -920.545
2028-11-08 09:00 | -1823.17 | 6.0898 | 49.0108 | 53.895 | -534.3184
2028-11-09 10:00 | -794.651 | 2.6758 | 49.2039 | 53.895 | -232.8892
2028-11-10 11:00 | -144.395 | 0.91248 | 50.08 | 53.895 | -42.318
2028-11-11 12:00 | -87.3013 | 0.91205 | 50.5665 | 53.895 | -25.5855
2028-11-12 13:00 | 60.8795 | 1 | 51.1268 | 53.895 | 17.842
2028-11-13 14:00 | 2800.84 | 1 | 50.767 | 53.895 | 820.8452
2028-11-14 15:00 | 2890.07 | 1 | 67.7384 | 53.895 | 846.9959
2028-11-15 16:00 | 3493.11 | 1.2081 | 65.4279 | 53.895 | 1023.7295
2028-11-16 17:00 | 3772.43 | 1.2855 | 65.8379 | 53.895 | 1105.5901
2028-11-17 18:00 | 2990.03 | 1 | 66.9196 | 53.895 | 876.2913
2028-11-18 19:00 | 2943.73 | 1 | 51.8826 | 53.895 | 862.7221
2028-11-19 20:00 | 0 | 0 | 52.4683 | 53.895 | 0
2028-11-20 21:00 | -553.108 | 1.9349 | 50.8534 | 53.895 | -162.1
2028-11-21 22:00 | -1241.15 | 4.5095 | 50.7078 | 53.895 | -363.7452
2028-11-22 23:00 | -1398.6 | 4.7693 | 50.4592 | 53.895 | -409.8892
2028-11-24 | -1645.67 | 5.5581 | 50.3349 | 53.895 | -482.2983
2028-11-25 01:00 | -1660.81 | 5.5309 | 50.2063 | 53.895 | -486.7354
2028-11-26 02:00 | -1618.94 | 5.4006 | 50.1491 | 53.895 | -474.4645
2028-11-27 03:00 | -1473.63 | 4.9396 | 50.1211 | 53.895 | -431.8783
2028-11-28 04:00 | -1403.99 | 4.7615 | 50.1294 | 53.895 | -411.4689
2028-11-29 05:00 | -1101.86 | 3.7917 | 50.1367 | 53.895 | -322.9233
2028-11-30 06:00 | -827.598 | 3 | 50.2334 | 53.895 | -242.545
2028-12-01 07:00 | -353.879 | 1.547 | 50.4926 | 53.895 | -103.7117
2028-12-02 08:00 | 21.0954 | 1 | 51.6668 | 53.895 | 6.1825
2028-12-03 09:00 | 2032.41 | 1 | 51.4277 | 53.895 | 595.6406
2028-12-04 10:00 | 2799.51 | 1 | 51.6112 | 53.895 | 820.4554
2028-12-05 11:00 | 3035.79 | 1 | 68.9029 | 53.895 | 889.7022
2028-12-06 12:00 | 3077.38 | 1 | 68.2472 | 53.895 | 901.891
2028-12-07 13:00 | 4760.23 | 1.4949 | 67.6196 | 53.895 | 1395.0857
2028-12-08 14:00 | 5933.08 | 1.9316 | 67.4126 | 53.895 | 1738.8141
2028-12-09 15:00 | 7582.51 | 2.5679 | 67.1839 | 53.895 | 2222.2143
2028-12-10 16:00 | 8008.41 | 2.6475 | 67.9238 | 53.895 | 2347.0333
2028-12-11 17:00 | 7562.87 | 2.4613 | 68.4734 | 53.895 | 2216.4584
2028-12-12 18:00 | 6060.29 | 1.8363 | 69.7458 | 53.895 | 1776.0957
2028-12-13 19:00 | 4874.38 | 1.4308 | 70.238 | 53.895 | 1428.5398
2028-12-14 20:00 | 3128.06 | 1 | 76.1352 | 53.895 | 916.7439
2028-12-15 21:00 | 3130.68 | 1 | 53.4602 | 53.895 | 917.5117
2028-12-16 22:00 | -142.503 | 1.1134 | 53.3069 | 53.895 | -41.7635
2028-12-17 23:00 | -589.42 | 2.4364 | 52.3323 | 53.895 | -172.742
2028-12-19 | -1062.53 | 3.8216 | 51.871 | 53.895 | -311.3968
2028-12-20 01:00 | -1150.72 | 3.9726 | 51.6001 | 53.895 | -337.2427
2028-12-21 02:00 | -1248.5 | 4.2794 | 51.4265 | 53.895 | -365.8992
2028-12-22 03:00 | -1223.63 | 4.1772 | 51.2462 | 53.895 | -358.6106
2028-12-23 04:00 | -1334.28 | 4.5507 | 51.1453 | 53.895 | -391.0389
2028-12-24 05:00 | -1503.88 | 5.0667 | 51.0272 | 53.895 | -440.7437
2028-12-25 06:00 | -1042.13 | 3.5236 | 50.9354 | 53.895 | -305.4182
2028-12-26 07:00 | -768.883 | 2.8085 | 51.0208 | 53.895 | -225.3374
2028-12-27 08:00 | -1706.95 | 5.9142 | 50.9693 | 53.895 | -500.2577
2028-12-28 09:00 | -1456.55 | 4.7836 | 50.7459 | 53.895 | -426.8727
2028-12-29 10:00 | 0 | 0 | 52.1247 | 53.895 | 0
2028-12-30 11:00 | 1923.79 | 1.0468 | 60.9163 | 53.895 | 563.8072
2028-12-31 12:00 | 2876.58 | 1.0727 | 65.151 | 53.895 | 843.0424
2029-01-01 13:00 | 3433.84 | 1.1507 | 66.8108 | 53.895 | 1006.3592
2029-01-02 14:00 | 3112.82 | 1.0011 | 67.6164 | 53.895 | 912.2775
2029-01-03 15:00 | 2951.36 | 1 | 69.9603 | 53.895 | 864.9582
2029-01-04 16:00 | 5265.87 | 1.7009 | 67.695 | 53.895 | 1543.2742
2029-01-05 17:00 | 3816.73 | 1.2057 | 68.3521 | 53.895 | 1118.5731
2029-01-06 18:00 | 3094.81 | 1 | 71.596 | 53.895 | 906.9993
2029-01-07 19:00 | 3090.11 | 1 | 52.9268 | 53.895 | 905.6218
2029-01-08 20:00 | 3083.96 | 1 | 52.9798 | 53.895 | 903.8195
2029-01-09 21:00 | 2973.12 | 1 | 53.069 | 53.895 | 871.3355
2029-01-10 22:00 | 0 | 0 | 53.595 | 53.895 | 0
2029-01-11 23:00 | -1190.95 | 4.2718 | 51.9538 | 53.895 | -349.033
2029-01-13 | -1530.49 | 5.1452 | 51.5524 | 53.895 | -448.5423
2029-01-14 01:00 | -1622.87 | 5.3652 | 51.3223 | 53.895 | -475.6162
2029-01-15 02:00 | -1710.94 | 5.639 | 51.1589 | 53.895 | -501.427
2029-01-16 03:00 | -1736.44 | 5.7044 | 51.0029 | 53.895 | -508.9003
2029-01-17 04:00 | -1784.02 | 5.8611 | 50.8946 | 53.895 | -522.8447
2029-01-18 05:00 | -1822.91 | 5.9768 | 50.8208 | 53.895 | -534.2422
2029-01-19 06:00 | -994.774 | 3.2788 | 50.7626 | 53.895 | -291.5395
2029-01-20 07:00 | -193.305 | 0.99175 | 51.3125 | 53.895 | -56.6521
2029-01-21 08:00 | -154.901 | 1.1056 | 51.6751 | 53.895 | -45.397
2029-01-22 09:00 | 1864.7 | 1 | 52.0486 | 53.895 | 546.4896
2029-01-23 10:00 | 2824.3 | 1 | 66.7003 | 53.895 | 827.7206
2029-01-24 11:00 | 4638.84 | 1.5664 | 66.8014 | 53.895 | 1359.5098
2029-01-25 12:00 | 5987.57 | 1.9867 | 67.4199 | 53.895 | 1754.7835
2029-01-26 13:00 | 6512.03 | 2.2146 | 67.4714 | 53.895 | 1908.4876
2029-01-27 14:00 | 6788.35 | 2.2127 | 68.4037 | 53.895 | 1989.469
2029-01-28 15:00 | 6814.39 | 2.2284 | 68.6091 | 53.895 | 1997.1006
2029-01-29 16:00 | 8256.18 | 2.9675 | 67.5032 | 53.895 | 2419.6475
2029-01-30 17:00 | 7297.44 | 2.4662 | 68.6713 | 53.895 | 2138.6685
2029-01-31 18:00 | 4906.53 | 1.5527 | 69.7327 | 53.895 | 1437.962
2029-02-01 19:00 | 2870.99 | 1 | 74.1232 | 53.895 | 841.4041
2029-02-02 20:00 | 2735.77 | 1 | 53.9816 | 53.895 | 801.775
2029-02-03 21:00 | -253.622 | 1.4729 | 53.5054 | 53.895 | -74.3293
2029-02-04 22:00 | -806.584 | 3.0725 | 52.6233 | 53.895 | -236.3864
2029-02-05 23:00 | -2288.72 | 6.8587 | 51.9363 | 53.895 | -670.7576
2029-02-07 | -2968.19 | 6.8587 | 51.0924 | 53.895 | -869.8906
2029-02-08 01:00 | -3344.3 | 6.8587 | 50.5037 | 53.895 | -980.1176
2029-02-09 02:00 | -3476.48 | 6.8587 | 50.1177 | 53.895 | -1018.8557
2029-02-10 03:00 | -3538.04 | 6.8587 | 49.8667 | 53.895 | -1036.8972
2029-02-11 04:00 | -3483.84 | 6.8587 | 49.7036 | 53.895 | -1021.0127
2029-02-12 05:00 | -3103.22 | 6.8587 | 49.8186 | 53.895 | -909.464
2029-02-13 06:00 | -3038.52 | 6.8587 | 49.7964 | 53.895 | -890.5023
2029-02-14 07:00 | -2936.02 | 6.8587 | 49.8089 | 53.895 | -860.4625
2029-02-15 08:00 | -2965.25 | 6.8587 | 49.7346 | 53.895 | -869.029
2029-02-16 09:00 | -1949.64 | 6.3832 | 50.2823 | 53.895 | -571.3831
2029-02-17 10:00 | -888.515 | 2.9067 | 50.3476 | 53.895 | -260.398
2029-02-18 11:00 | 1709.81 | 1 | 51.6344 | 53.895 | 501.0958
2029-02-19 12:00 | 2859.73 | 1 | 51.8108 | 53.895 | 838.1041
2029-02-20 13:00 | 2887.22 | 1 | 68.6821 | 53.895 | 846.1607
2029-02-21 14:00 | 3516.93 | 1.185 | 66.7492 | 53.895 | 1030.7104
2029-02-22 15:00 | 4597.82 | 1.526 | 67.1866 | 53.895 | 1347.488
2029-02-23 16:00 | 5269.72 | 1.7733 | 67.2777 | 53.895 | 1544.4025
2029-02-24 17:00 | 4956.55 | 1.6865 | 67.3722 | 53.895 | 1452.6214
2029-02-25 18:00 | 3664.85 | 1.2369 | 67.6213 | 53.895 | 1074.0615
2029-02-26 19:00 | 2903.63 | 1 | 53.2175 | 53.895 | 850.97
2029-02-27 20:00 | -308.047 | 1.6099 | 52.7743 | 53.895 | -90.2797
2029-02-28 21:00 | -1057.86 | 3.8779 | 52.0095 | 53.895 | -310.0282
2029-03-01 22:00 | -2357.09 | 6.8587 | 51.38 | 53.895 | -690.7949
2029-03-02 23:00 | -3327.6 | 6.8587 | 50.3873 | 53.895 | -975.2233
2029-03-04 | -3789.52 | 6.8587 | 49.7316 | 53.895 | -1110.5987
2029-03-05 01:00 | -4092.49 | 6.8587 | 49.2361 | 53.895 | -1199.3904
2029-03-06 02:00 | -4365.86 | 6.8587 | 48.8387 | 53.895 | -1279.5073
2029-03-07 03:00 | -4397.37 | 6.8587 | 48.6077 | 53.895 | -1288.7419
2029-03-08 04:00 | -4340.58 | 6.8587 | 48.477 | 53.895 | -1272.0984
2029-03-09 05:00 | -3698.09 | 6.8587 | 48.7852 | 53.895 | -1083.8032
2029-03-10 06:00 | -3500.71 | 6.8587 | 48.8871 | 53.895 | -1025.9568
2029-03-11 07:00 | -2593.76 | 6.8587 | 49.474 | 53.895 | -760.156
2029-03-12 08:00 | -2006.93 | 6.587 | 49.9067 | 53.895 | -588.1731
2029-03-13 09:00 | -878.503 | 2.8654 | 49.9964 | 53.895 | -257.4638
2029-03-14 10:00 | 2329.17 | 1 | 51.2272 | 53.895 | 682.6123
2029-03-15 11:00 | 2957.72 | 1 | 69.7648 | 53.895 | 866.8222
2029-03-16 12:00 | 3838.93 | 1.2712 | 66.602 | 53.895 | 1125.0793
2029-03-17 13:00 | 4696.44 | 1.5306 | 67.1422 | 53.895 | 1376.3907
2029-03-18 14:00 | 5620.97 | 1.8527 | 67.3109 | 53.895 | 1647.3437
2029-03-19 15:00 | 7428.86 | 2.4764 | 67.4907 | 53.895 | 2177.1839
2029-03-20 16:00 | 7883.56 | 2.6239 | 67.9312 | 53.895 | 2310.4434
2029-03-21 17:00 | 7413.97 | 2.472 | 68.2472 | 53.895 | 2172.8201
2029-03-22 18:00 | 5646.1 | 1.8514 | 68.6869 | 53.895 | 1654.7086
2029-03-23 19:00 | 3593.76 | 1.2198 | 68.1821 | 53.895 | 1053.2271
2029-03-24 20:00 | 2820.59 | 1 | 53.7149 | 53.895 | 826.6333
2029-03-25 21:00 | -140.217 | 1.1189 | 53.463 | 53.895 | -41.0935
2029-03-26 22:00 | -1423.93 | 5.05 | 52.2849 | 53.895 | -417.3127
2029-03-27 23:00 | -2054.03 | 6.7309 | 51.7633 | 53.895 | -601.9768
2029-03-29 | -2386.21 | 6.8587 | 51.2623 | 53.895 | -699.3291
2029-03-30 01:00 | -2668.77 | 6.8587 | 50.8364 | 53.895 | -782.1393
2029-03-31 02:00 | -2871.26 | 6.8587 | 50.4755 | 53.895 | -841.4832
2029-04-01 03:00 | -2927.57 | 6.8587 | 50.2573 | 53.895 | -857.9861
2029-04-02 04:00 | -2928.62 | 6.8587 | 50.1109 | 53.895 | -858.2938
2029-04-03 05:00 | -2587.18 | 6.8587 | 50.2215 | 53.895 | -758.2276
2029-04-04 06:00 | -2453.82 | 6.8587 | 50.2572 | 53.895 | -719.1437
2029-04-05 07:00 | -1926.63 | 6.2585 | 50.4555 | 53.895 | -564.6395
2029-04-06 08:00 | -1878.43 | 6.1431 | 50.4885 | 53.895 | -550.5135
2029-04-07 09:00 | -1336.68 | 4.3829 | 50.5104 | 53.895 | -391.7422
2029-04-08 10:00 | -906.919 | 3.1744 | 50.6591 | 53.895 | -265.7917
2029-04-09 11:00 | -633.451 | 2.4176 | 50.8391 | 53.895 | -185.6462
2029-04-10 12:00 | -847.959 | 3.1851 | 50.8751 | 53.895 | -248.5123
2029-04-11 13:00 | -968.966 | 3.4973 | 50.8117 | 53.895 | -283.9759
2029-04-12 14:00 | -770.686 | 2.8255 | 50.8011 | 53.895 | -225.8658
2029-04-13 15:00 | -188.739 | 1.0272 | 51.2009 | 53.895 | -55.3139
2029-04-14 16:00 | -69.3825 | 0.83397 | 51.7078 | 53.895 | -20.334
2029-04-15 17:00 | -117.639 | 1.0059 | 51.5555 | 53.895 | -34.4766
2029-04-16 18:00 | -558.051 | 2.3877 | 51.002 | 53.895 | -163.5486
2029-04-17 19:00 | -963.837 | 3.5662 | 50.7805 | 53.895 | -282.4727
2029-04-18 20:00 | -1874.8 | 6.4153 | 50.6134 | 53.895 | -549.4496
2029-04-19 21:00 | -2236.5 | 6.8587 | 50.3104 | 53.895 | -655.4534
2029-04-20 22:00 | -2944.24 | 6.8587 | 49.7047 | 53.895 | -862.8716
2029-04-21 23:00 | -3155.39 | 6.8587 | 49.4038 | 53.895 | -924.7535
2029-04-23 | -3066.13 | 6.8587 | 49.3451 | 53.895 | -898.594
2029-04-24 01:00 | -3050.93 | 6.8587 | 49.2925 | 53.895 | -894.1393
2029-04-25 02:00 | -3009.24 | 6.8587 | 49.2806 | 53.895 | -881.9212
2029-04-26 03:00 | -2620.22 | 6.8587 | 49.5096 | 53.895 | -767.9107
2029-04-27 04:00 | -2291.63 | 6.8587 | 49.7565 | 53.895 | -671.6105
2029-04-28 05:00 | -1726.29 | 5.6339 | 49.928 | 53.895 | -505.9257
2029-04-29 06:00 | -1444.93 | 4.8243 | 50.0435 | 53.895 | -423.4672
2029-04-30 07:00 | -1170.86 | 4.0091 | 50.1542 | 53.895 | -343.1452
2029-05-01 08:00 | -1281.72 | 4.4546 | 50.2598 | 53.895 | -375.6351
2029-05-02 09:00 | -1197.97 | 4.131 | 50.2826 | 53.895 | -351.0903
2029-05-03 10:00 | -963.011 | 3.3982 | 50.341 | 53.895 | -282.2307
2029-05-04 11:00 | -680.954 | 2.559 | 50.4616 | 53.895 | -199.5679
2029-05-05 12:00 | -607.096 | 2.407 | 50.5756 | 53.895 | -177.9223
2029-05-06 13:00 | -547.371 | 2.2292 | 50.6349 | 53.895 | -160.4186
2029-05-07 14:00 | -324.127 | 1.5284 | 50.8125 | 53.895 | -94.9922
2029-05-08 15:00 | 1941.85 | 1 | 51.5069 | 53.895 | 569.1001
2029-05-09 16:00 | 2809.65 | 1 | 51.6419 | 53.895 | 823.4271
2029-05-10 17:00 | 3005.53 | 1 | 51.8675 | 53.895 | 880.8339
2029-05-11 18:00 | 2899.43 | 1 | 52.0608 | 53.895 | 849.7391
2029-05-12 19:00 | 0 | 0 | 52.6884 | 53.895 | 0
2029-05-13 20:00 | -788.031 | 2.7876 | 51.1361 | 53.895 | -230.9491
2029-05-14 21:00 | -1010.11 | 3.664 | 50.9679 | 53.895 | -296.034
2029-05-15 22:00 | -1725.69 | 5.9025 | 50.7824 | 53.895 | -505.7498
2029-05-16 23:00 | -1961.27 | 6.4487 | 50.5639 | 53.895 | -574.7915
2029-05-18 | -2054.87 | 6.7105 | 50.4082 | 53.895 | -602.2229
2029-05-19 01:00 | -2081.88 | 6.7766 | 50.3416 | 53.895 | -610.1388
2029-05-20 02:00 | -2071.11 | 6.7375 | 50.3024 | 53.895 | -606.9824
2029-05-21 03:00 | -1874.15 | 6.0974 | 50.2485 | 53.895 | -549.2591
2029-05-22 04:00 | -1642.43 | 5.4074 | 50.2403 | 53.895 | -481.3487
2029-05-23 05:00 | -1179.3 | 3.9662 | 50.2607 | 53.895 | -345.6187
2029-05-24 06:00 | -971.669 | 3.4432 | 50.3637 | 53.895 | -284.7681
2029-05-25 07:00 | -628.991 | 2.385 | 50.5035 | 53.895 | -184.3391
2029-05-26 08:00 | -659.216 | 2.5913 | 50.6273 | 53.895 | -193.1971
2029-05-27 09:00 | -199.889 | 1.0902 | 51.0059 | 53.895 | -58.5817
2029-05-28 10:00 | 1875.63 | 1 | 51.6391 | 53.895 | 549.6929
2029-05-29 11:00 | 2889.31 | 1 | 71.2147 | 53.895 | 846.7732
2029-05-30 12:00 | 2884.3 | 1 | 69.9776 | 53.895 | 845.3049
2029-05-31 13:00 | 3097.01 | 1 | 72.6645 | 53.895 | 907.644
2029-06-01 14:00 | 3451.62 | 1.094 | 67.7154 | 53.895 | 1011.57
2029-06-02 15:00 | 5025.79 | 1.6491 | 67.4032 | 53.895 | 1472.9137
2029-06-03 16:00 | 4384.78 | 1.4232 | 67.8663 | 53.895 | 1285.0522
2029-06-04 17:00 | 4215.87 | 1.3629 | 68.0281 | 53.895 | 1235.5495
2029-06-05 18:00 | 3082.12 | 1 | 69.1243 | 53.895 | 903.2802
2029-06-06 19:00 | 3112.82 | 1 | 53.0395 | 53.895 | 912.2775
2029-06-07 20:00 | 0 | 0 | 53.6215 | 53.895 | 0
2029-06-08 21:00 | -438.108 | 1.804 | 52.1339 | 53.895 | -128.3968
2029-06-09 22:00 | -1383.33 | 4.9111 | 51.7143 | 53.895 | -405.414
2029-06-10 23:00 | -1886.78 | 6.2403 | 51.3772 | 53.895 | -552.9606
2029-06-12 | -2048.09 | 6.6409 | 51.1325 | 53.895 | -600.2359
2029-06-13 01:00 | -2159.16 | 6.8587 | 50.9192 | 53.895 | -632.7873
2029-06-14 02:00 | -2309.2 | 6.8587 | 50.7046 | 53.895 | -676.7597
2029-06-15 03:00 | -2428.03 | 6.8587 | 50.4941 | 53.895 | -711.5854
2029-06-16 04:00 | -2513.88 | 6.8587 | 50.3266 | 53.895 | -736.7455
2029-06-17 05:00 | -2486.67 | 6.8587 | 50.2438 | 53.895 | -728.771
2029-06-18 06:00 | -1495.03 | 4.8435 | 50.4171 | 53.895 | -438.15
2029-06-19 07:00 | -775.998 | 2.7046 | 50.5626 | 53.895 | -227.4226
2029-06-20 08:00 | -609.36 | 2.3907 | 50.8306 | 53.895 | -178.5858
2029-06-21 09:00 | 151.763 | 1 | 52.0744 | 53.895 | 44.4773
2029-06-22 10:00 | 2187.6 | 1 | 51.8554 | 53.895 | 641.1223
2029-06-23 11:00 | 2807.38 | 1 | 52.0841 | 53.895 | 822.7619
2029-06-24 12:00 | 2972.75 | 1 | 52.318 | 53.895 | 871.227
2029-06-25 13:00 | 3047.96 | 1 | 52.4746 | 53.895 | 893.2689
2029-06-26 14:00 | 3095.07 | 1 | 52.611 | 53.895 | 907.0755
2029-06-27 15:00 | 3041.9 | 1 | 52.7287 | 53.895 | 891.4929
2029-06-28 16:00 | 4721.33 | 1.5576 | 67.5468 | 53.895 | 1383.6852
2029-06-29 17:00 | 4146.39 | 1.3528 | 67.9137 | 53.895 | 1215.187
2029-06-30 18:00 | 3315.34 | 1.071 | 68.1528 | 53.895 | 971.6302
2029-07-01 19:00 | 3105.46 | 1 | 53.0854 | 53.895 | 910.1205
2029-07-02 20:00 | 3089.89 | 1 | 53.119 | 53.895 | 905.5574
2029-07-03 21:00 | 1556.07 | 1 | 53.4412 | 53.895 | 456.0391
2029-07-04 22:00 | -4.6459 | 0.72034 | 53.5087 | 53.895 | -1.3616
2029-07-05 23:00 | -1397.8 | 5.002 | 51.9556 | 53.895 | -409.6547
2029-07-07 | -1813.34 | 5.9797 | 51.5444 | 53.895 | -531.4375
2029-07-08 01:00 | -2049.16 | 6.6572 | 51.2976 | 53.895 | -600.5495
2029-07-09 02:00 | -2270.49 | 6.8587 | 50.9996 | 53.895 | -665.4149
2029-07-10 03:00 | -2476.76 | 6.8587 | 50.6994 | 53.895 | -725.8667
2029-07-11 04:00 | -2528.84 | 6.8587 | 50.5127 | 53.895 | -741.1298
2029-07-12 05:00 | -2520.76 | 6.8587 | 50.4113 | 53.895 | -738.7618
2029-07-13 06:00 | -1640.93 | 5.3104 | 50.5982 | 53.895 | -480.9091
2029-07-14 07:00 | -1155.54 | 3.8765 | 50.6741 | 53.895 | -338.6553
2029-07-15 08:00 | -1575.82 | 5.3938 | 50.7487 | 53.895 | -461.8273
2029-07-16 09:00 | -1180.48 | 3.9489 | 50.6689 | 53.895 | -345.9645
2029-07-17 10:00 | 0 | 0 | 52.0809 | 53.895 | 0
2029-07-18 11:00 | 2181.04 | 1 | 67.0188 | 53.895 | 639.1997
2029-07-19 12:00 | 3280.78 | 1.1645 | 65.7671 | 53.895 | 961.5017
2029-07-20 13:00 | 3983.94 | 1.2954 | 67.2906 | 53.895 | 1167.5776
2029-07-21 14:00 | 4441.44 | 1.4234 | 67.78 | 53.895 | 1301.6576
2029-07-22 15:00 | 5257.07 | 1.6874 | 68.0132 | 53.895 | 1540.6951
2029-07-23 16:00 | 7245.97 | 2.4729 | 67.4196 | 53.895 | 2123.5842
2029-07-24 17:00 | 6131.68 | 2.0019 | 68.4803 | 53.895 | 1797.018
2029-07-25 18:00 | 4708.8 | 1.4945 | 69.0384 | 53.895 | 1380.0131
2029-07-26 19:00 | 3033.44 | 1 | 69.4225 | 53.895 | 889.0135
2029-07-27 20:00 | 3042.05 | 1 | 53.5527 | 53.895 | 891.5368
2029-07-28 21:00 | 2976.98 | 1 | 53.5424 | 53.895 | 872.4667
2029-07-29 22:00 | -118.621 | 1.0641 | 53.505 | 53.895 | -34.7644
2029-07-30 23:00 | -1416.6 | 5.0274 | 52.3125 | 53.895 | -415.1645
2029-08-01 | -1980.4 | 6.4895 | 51.8303 | 53.895 | -580.3979
2029-08-02 01:00 | -2357.13 | 6.8587 | 51.3996 | 53.895 | -690.8066
2029-08-03 02:00 | -2605.4 | 6.8587 | 50.999 | 53.895 | -763.5674
2029-08-04 03:00 | -2651.06 | 6.8587 | 50.7368 | 53.895 | -776.949
2029-08-05 04:00 | -2688.24 | 6.8587 | 50.5433 | 53.895 | -787.8454
2029-08-06 05:00 | -2282.57 | 6.8587 | 50.6958 | 53.895 | -668.9552
2029-08-07 06:00 | -2159.26 | 6.8587 | 50.7274 | 53.895 | -632.8166
2029-08-08 07:00 | -1496.63 | 4.8132 | 50.7055 | 53.895 | -438.619
2029-08-09 08:00 | -1085.81 | 3.698 | 50.8178 | 53.895 | -318.2195
2029-08-10 09:00 | 13.9701 | 1 | 52.235 | 53.895 | 4.0942
2029-08-11 10:00 | 2249.97 | 1 | 64.4599 | 53.895 | 659.4011
2029-08-12 11:00 | 4200.93 | 1.4679 | 66.1548 | 53.895 | 1231.1711
2029-08-13 12:00 | 5225.07 | 1.7408 | 67.2423 | 53.895 | 1531.3169
2029-08-14 13:00 | 5299.22 | 1.7286 | 67.9228 | 53.895 | 1553.0481
2029-08-15 14:00 | 6247.26 | 2.053 | 68.0806 | 53.895 | 1830.8912
2029-08-16 15:00 | 8229.44 | 2.7726 | 68.0446 | 53.895 | 2411.8108
2029-08-17 16:00 | 8135.53 | 2.6455 | 69.0004 | 53.895 | 2384.2885
2029-08-18 17:00 | 8195.71 | 2.7008 | 69.0813 | 53.895 | 2401.9255
2029-08-19 18:00 | 6853.29 | 2.1813 | 69.802 | 53.895 | 2008.501
2029-08-20 19:00 | 5298.96 | 1.6379 | 70.2963 | 53.895 | 1552.9719
2029-08-21 20:00 | 3069.48 | 1 | 72.8589 | 53.895 | 899.5758
2029-08-22 21:00 | 3022.6 | 1 | 54.2379 | 53.895 | 885.8366
2029-08-23 22:00 | -354.407 | 1.7482 | 53.6745 | 53.895 | -103.8664
2029-08-24 23:00 | -957.05 | 3.5071 | 52.8521 | 53.895 | -280.4837
2029-08-26 | -1283.81 | 4.3836 | 52.388 | 53.895 | -376.2476
2029-08-27 01:00 | -1500.99 | 4.9982 | 52.1134 | 53.895 | -439.8967
2029-08-28 02:00 | -1649.31 | 5.4216 | 51.9025 | 53.895 | -483.365
2029-08-29 03:00 | -1698.93 | 5.5519 | 51.6854 | 53.895 | -497.9072
2029-08-30 04:00 | -1667.12 | 5.4454 | 51.5552 | 53.895 | -488.5846
2029-08-31 05:00 | -1412.31 | 4.6443 | 51.4546 | 53.895 | -413.9072
2029-09-01 06:00 | -1079.17 | 3.6635 | 51.4377 | 53.895 | -316.2735
2029-09-02 07:00 | -411.097 | 1.6361 | 51.6212 | 53.895 | -120.4806
2029-09-03 08:00 | -86.7516 | 0.82096 | 52.3708 | 53.895 | -25.4244
2029-09-04 09:00 | 2083.77 | 1 | 65.4866 | 53.895 | 610.6927
2029-09-05 10:00 | 4048.88 | 1.4642 | 66.1762 | 53.895 | 1186.6096
2029-09-06 11:00 | 5733.08 | 1.9925 | 67.0984 | 53.895 | 1680.1999
2029-09-07 12:00 | 6337.27 | 2.1553 | 67.8209 | 53.895 | 1857.2705
2029-09-08 13:00 | 6904.35 | 2.2748 | 68.6048 | 53.895 | 2023.4652
2029-09-09 14:00 | 7691.68 | 2.5404 | 68.8833 | 53.895 | 2254.2089
2029-09-10 15:00 | 9472.55 | 3.1699 | 68.9995 | 53.895 | 2776.1304
2029-09-11 16:00 | 9529.47 | 3.1518 | 69.5885 | 53.895 | 2792.812
2029-09-12 17:00 | 9774.68 | 3.1833 | 70.088 | 53.895 | 2864.6759
2029-09-13 18:00 | 8376.79 | 2.6868 | 70.5636 | 53.895 | 2454.9948
2029-09-14 19:00 | 6763.8 | 2.1085 | 71.0485 | 53.895 | 1982.2741
2029-09-15 20:00 | 4270.36 | 1.3279 | 71.0136 | 53.895 | 1251.519
2029-09-16 21:00 | 3148.83 | 1.0005 | 70.3762 | 53.895 | 922.831
2029-09-17 22:00 | 2999.59 | 1 | 54.8446 | 53.895 | 879.0931
2029-09-18 23:00 | 2878.17 | 1 | 54.7014 | 53.895 | 843.5084
2029-09-20 | -1.1856 | 0.70163 | 55.0712 | 53.895 | -0.34746
2029-09-21 01:00 | -277.584 | 1.4772 | 53.7623 | 53.895 | -81.3518
2029-09-22 02:00 | -348.614 | 1.6332 | 53.3721 | 53.895 | -102.1687
2029-09-23 03:00 | -340.403 | 1.5958 | 53.2038 | 53.895 | -99.7623
2029-09-24 04:00 | -266.665 | 1.3735 | 53.1411 | 53.895 | -78.1518
2029-09-25 05:00 | 220.629 | 1 | 53.8718 | 53.895 | 64.66
2029-09-26 06:00 | 364.042 | 1 | 53.8299 | 53.895 | 106.6902
2029-09-27 07:00 | 169.745 | 1 | 53.8517 | 53.895 | 49.7473
2029-09-28 08:00 | 0 | 0 | 53.8465 | 53.895 | 0
2029-09-29 09:00 | 60.3985 | 1 | 53.7814 | 53.895 | 17.7011
2029-09-30 10:00 | 1923.96 | 1 | 53.4087 | 53.895 | 563.857
2029-10-01 11:00 | 2661.26 | 1 | 73.1135 | 53.895 | 779.9383
2029-10-02 12:00 | 3385.5 | 1.1544 | 67.7871 | 53.895 | 992.1921
2029-10-03 13:00 | 5382.05 | 1.7772 | 68.4064 | 53.895 | 1577.3232
2029-10-04 14:00 | 6376.9 | 2.1652 | 68.3604 | 53.895 | 1868.8849
2029-10-05 15:00 | 8011.54 | 2.754 | 68.5163 | 53.895 | 2347.9506
2029-10-06 16:00 | 8734.26 | 2.9315 | 69.2215 | 53.895 | 2559.7589
2029-10-07 17:00 | 8764.77 | 2.9066 | 69.7208 | 53.895 | 2568.7005
2029-10-08 18:00 | 7236.03 | 2.2719 | 70.7633 | 53.895 | 2120.6711
2029-10-09 19:00 | 4853.69 | 1.5507 | 70.5177 | 53.895 | 1422.4761
2029-10-10 20:00 | 3143.7 | 1 | 55.1116 | 53.895 | 921.3275
2029-10-11 21:00 | 3048.62 | 1 | 54.8571 | 53.895 | 893.4623
2029-10-12 22:00 | -324.102 | 1.6611 | 54.3156 | 53.895 | -94.9849
2029-10-13 23:00 | -890.162 | 3.2805 | 53.4461 | 53.895 | -260.8807
2029-10-15 | -1272.77 | 4.3368 | 52.9783 | 53.895 | -373.0121
2029-10-16 01:00 | -1494.08 | 4.9412 | 52.6909 | 53.895 | -437.8716
2029-10-17 02:00 | -1552.95 | 5.079 | 52.4653 | 53.895 | -455.1247
2029-10-18 03:00 | -1468.88 | 4.8116 | 52.2589 | 53.895 | -430.4862
2029-10-19 04:00 | -1408.68 | 4.6562 | 52.1458 | 53.895 | -412.8434
2029-10-20 05:00 | -955.554 | 3.2392 | 52.0668 | 53.895 | -280.0452
2029-10-21 06:00 | -819.374 | 2.9573 | 52.1093 | 53.895 | -240.1348
2029-10-22 07:00 | -300.301 | 1.35 | 52.3421 | 53.895 | -88.0095
2029-10-23 08:00 | -332.053 | 1.6115 | 52.46 | 53.895 | -97.3151
2029-10-24 09:00 | 351.874 | 1 | 53.3664 | 53.895 | 103.1241
2029-10-25 10:00 | 1802.65 | 1 | 53.2024 | 53.895 | 528.3046
2029-10-26 11:00 | 2709.41 | 1 | 53.2623 | 53.895 | 794.0497
2029-10-27 12:00 | 3027.79 | 1 | 68.3227 | 53.895 | 887.3577
2029-10-28 13:00 | 3306.66 | 1.0772 | 68.4836 | 53.895 | 969.0864
2029-10-29 14:00 | 5045.6 | 1.6016 | 68.9894 | 53.895 | 1478.7194
2029-10-30 15:00 | 7514.33 | 2.6425 | 67.8387 | 53.895 | 2202.2327
2029-10-31 16:00 | 8512.81 | 2.8771 | 68.8456 | 53.895 | 2494.8583
2029-11-01 17:00 | 8273.3 | 2.7143 | 69.6497 | 53.895 | 2424.6649
2029-11-02 18:00 | 7118.69 | 2.2281 | 70.5759 | 53.895 | 2086.2821
2029-11-03 19:00 | 5485.62 | 1.6651 | 71.1277 | 53.895 | 1607.6765
2029-11-04 20:00 | 3194.08 | 1 | 75.987 | 53.895 | 936.0924
2029-11-05 21:00 | 3032.27 | 1 | 54.8159 | 53.895 | 888.6706
2029-11-06 22:00 | -293.701 | 1.5495 | 54.2984 | 53.895 | -86.0753
2029-11-07 23:00 | -778.363 | 2.9452 | 53.4594 | 53.895 | -228.1157
2029-11-09 | -1094.08 | 3.81 | 53.0114 | 53.895 | -320.6432
2029-11-10 01:00 | -1372.22 | 4.6085 | 52.7446 | 53.895 | -402.158
2029-11-11 02:00 | -1555.78 | 5.1191 | 52.5256 | 53.895 | -455.9541
2029-11-12 03:00 | -1548.45 | 5.0572 | 52.3027 | 53.895 | -453.8059
2029-11-13 04:00 | -1431.15 | 4.6995 | 52.175 | 53.895 | -419.4287
2029-11-14 05:00 | -1016.84 | 3.427 | 52.103 | 53.895 | -298.0064
2029-11-15 06:00 | -818.98 | 2.9352 | 52.1405 | 53.895 | -240.0193
2029-11-16 07:00 | -194.623 | 1.0198 | 52.5271 | 53.895 | -57.0384
2029-11-17 08:00 | 1593.94 | 1 | 53.2078 | 53.895 | 467.1377
2029-11-18 09:00 | 2789.29 | 1 | 67.4161 | 53.895 | 817.4602
2029-11-19 10:00 | 5310.67 | 1.7897 | 67.897 | 53.895 | 1556.4037
2029-11-20 11:00 | 7094.02 | 2.4102 | 68.2468 | 53.895 | 2079.052
2029-11-21 12:00 | 8192.42 | 2.798 | 68.6882 | 53.895 | 2400.9613
2029-11-22 13:00 | 8793.09 | 2.9639 | 69.3337 | 53.895 | 2577.0003
2029-11-23 14:00 | 9548.05 | 3.2468 | 69.5888 | 53.895 | 2798.2572
2029-11-24 15:00 | 11247.6 | 3.7627 | 70.172 | 53.895 | 3296.3462
2029-11-25 16:00 | 11753.9 | 3.8475 | 70.9315 | 53.895 | 3444.728
2029-11-26 17:00 | 11549.1 | 3.7405 | 71.4493 | 53.895 | 3384.7071
2029-11-27 18:00 | 9935.5 | 3.1332 | 72.0944 | 53.895 | 2911.8076
2029-11-28 19:00 | 8293.6 | 2.5626 | 72.4485 | 53.895 | 2430.6142
2029-11-29 20:00 | 5679.12 | 1.6845 | 73.0053 | 53.895 | 1664.3858
2029-11-30 21:00 | 4231.91 | 1.3219 | 71.8932 | 53.895 | 1240.2504
2029-12-01 22:00 | 3069.47 | 1 | 56.06 | 53.895 | 899.5729
2029-12-02 23:00 | 0 | 0 | 56.2783 | 53.895 | 0
2029-12-04 | -310.17 | 1.4595 | 54.7121 | 53.895 | -90.9019
2029-12-05 01:00 | -668.144 | 2.5914 | 54.1194 | 53.895 | -195.8137
2029-12-06 02:00 | -1214.27 | 4.1815 | 53.7026 | 53.895 | -355.8674
2029-12-07 03:00 | -1670.56 | 5.4657 | 53.3394 | 53.895 | -489.5928
2029-12-08 04:00 | -2234.12 | 6.8587 | 52.9544 | 53.895 | -654.7559
2029-12-09 05:00 | -2607.3 | 6.8587 | 52.4391 | 53.895 | -764.1242
2029-12-10 06:00 | -1837.69 | 5.798 | 52.4915 | 53.895 | -538.5738
2029-12-11 07:00 | -1156.27 | 3.7334 | 52.4322 | 53.895 | -338.8693
2029-12-12 08:00 | -1108.18 | 3.7978 | 52.5107 | 53.895 | -324.7755
2029-12-13 09:00 | -225.161 | 1.0208 | 52.7968 | 53.895 | -65.9882
2029-12-14 10:00 | 2565.94 | 1 | 53.4374 | 53.895 | 752.0028
2029-12-15 11:00 | 3329.13 | 1.1053 | 68.3959 | 53.895 | 975.6717
2029-12-16 12:00 | 4608.47 | 1.5051 | 68.8498 | 53.895 | 1350.6092
2029-12-17 13:00 | 5450.58 | 1.7796 | 69.1372 | 53.895 | 1597.4073
2029-12-18 14:00 | 6195.78 | 2.0594 | 69.1762 | 53.895 | 1815.8039
2029-12-19 15:00 | 6808.43 | 2.2464 | 69.5509 | 53.895 | 1995.3539
2029-12-20 16:00 | 9198.7 | 3.0988 | 69.4761 | 53.895 | 2695.8729
2029-12-21 17:00 | 7965.52 | 2.6819 | 69.9469 | 53.895 | 2334.4635
2029-12-22 18:00 | 6478.9 | 2.155 | 70.2648 | 53.895 | 1898.7782
2029-12-23 19:00 | 4632.89 | 1.521 | 70.3938 | 53.895 | 1357.766
2029-12-24 20:00 | 2968.74 | 1 | 70.1224 | 53.895 | 870.0518
2029-12-25 21:00 | 2965.38 | 1 | 55.2106 | 53.895 | 869.0671
2029-12-26 22:00 | 2907.91 | 1 | 55.0636 | 53.895 | 852.2243
2029-12-27 23:00 | -1021.69 | 3.7673 | 54.2081 | 53.895 | -299.4278
2029-12-29 | -1667.9 | 5.4886 | 53.5115 | 53.895 | -488.8132
2029-12-30 01:00 | -2160.35 | 6.8587 | 53.0735 | 53.895 | -633.1361
2029-12-31 02:00 | -2758.73 | 6.8587 | 52.4027 | 53.895 | -808.504
2030-01-01 03:00 | -3162.61 | 6.8587 | 51.8318 | 53.895 | -926.8695
2030-01-02 04:00 | -3374.03 | 6.8587 | 51.3674 | 53.895 | -988.8306
2030-01-03 05:00 | -3550.04 | 6.8587 | 51.035 | 53.895 | -1040.414
2030-01-04 06:00 | -2463.18 | 6.8587 | 51.5907 | 53.895 | -721.8868
2030-01-05 07:00 | -1569.41 | 4.9861 | 51.7847 | 53.895 | -459.9487
2030-01-06 08:00 | -1356.98 | 4.4869 | 51.9152 | 53.895 | -397.6916
2030-01-07 09:00 | -511.238 | 1.8546 | 52.0568 | 53.895 | -149.8291
2030-01-08 10:00 | 2637.98 | 1 | 52.9659 | 53.895 | 773.1156
2030-01-09 11:00 | 2887.09 | 1 | 67.6516 | 53.895 | 846.1226
2030-01-10 12:00 | 4362.89 | 1.4928 | 67.7989 | 53.895 | 1278.6368
2030-01-11 13:00 | 5267.02 | 1.774 | 68.317 | 53.895 | 1543.6112
2030-01-12 14:00 | 6543.13 | 2.1754 | 68.8198 | 53.895 | 1917.6021
2030-01-13 15:00 | 7181.64 | 2.4353 | 68.9103 | 53.895 | 2104.7309
2030-01-14 16:00 | 9650.65 | 3.2871 | 69.1156 | 53.895 | 2828.3263
2030-01-15 17:00 | 8730.74 | 2.9499 | 69.7429 | 53.895 | 2558.7273
2030-01-16 18:00 | 7281.41 | 2.4202 | 70.2019 | 53.895 | 2133.9706
2030-01-17 19:00 | 5133.48 | 1.7418 | 69.9262 | 53.895 | 1504.4745
2030-01-18 20:00 | 3458.53 | 1.1625 | 69.8946 | 53.895 | 1013.5951
2030-01-19 21:00 | 3081.21 | 1 | 55.1914 | 53.895 | 903.0135
2030-01-20 22:00 | 2925.89 | 1 | 55.0197 | 53.895 | 857.4937
2030-01-21 23:00 | -1082.23 | 3.9619 | 54.1352 | 53.895 | -317.1703
2030-01-23 | -1821.05 | 5.9557 | 53.4192 | 53.895 | -533.6971
2030-01-24 01:00 | -2303.86 | 6.8587 | 52.8735 | 53.895 | -675.1947
2030-01-25 02:00 | -2632.24 | 6.8587 | 52.3736 | 53.895 | -771.4334
2030-01-26 03:00 | -2933.41 | 6.8587 | 51.9038 | 53.895 | -859.6976
2030-01-27 04:00 | -3188.82 | 6.8587 | 51.44 | 53.895 | -934.5509
2030-01-28 05:00 | -3234.29 | 6.8587 | 51.2078 | 53.895 | -947.8768
2030-01-29 06:00 | -2120.73 | 6.8148 | 51.797 | 53.895 | -621.5246
2030-01-30 07:00 | -1009.93 | 3.19 | 51.7792 | 53.895 | -295.9813
2030-01-31 08:00 | -472.329 | 1.8672 | 52.194 | 53.895 | -138.426
2030-02-01 09:00 | 2186.45 | 1 | 53.1028 | 53.895 | 640.7852
2030-02-02 10:00 | 3135.16 | 1.0692 | 67.5984 | 53.895 | 918.8247
2030-02-03 11:00 | 5178.94 | 1.6828 | 68.5685 | 53.895 | 1517.7975
2030-02-04 12:00 | 6652.95 | 2.2442 | 68.4653 | 53.895 | 1949.7872
2030-02-05 13:00 | 7624.84 | 2.5249 | 69.1781 | 53.895 | 2234.62
2030-02-06 14:00 | 8346.66 | 2.7581 | 69.6227 | 53.895 | 2446.1646
2030-02-07 15:00 | 8951.43 | 2.9054 | 70.2273 | 53.895 | 2623.4052
2030-02-08 16:00 | 11471.3 | 3.7595 | 70.3973 | 53.895 | 3361.9062
2030-02-09 17:00 | 10248.5 | 3.3832 | 70.8445 | 53.895 | 3003.5389
2030-02-10 18:00 | 8597.35 | 2.7698 | 71.4185 | 53.895 | 2519.6346
2030-02-11 19:00 | 6653.28 | 2.0737 | 71.8984 | 53.895 | 1949.8839
2030-02-12 20:00 | 5416.73 | 1.6706 | 71.9228 | 53.895 | 1587.4869
2030-02-13 21:00 | 4230.81 | 1.3444 | 71.3039 | 53.895 | 1239.928
2030-02-14 22:00 | 3122.56 | 1 | 71.9821 | 53.895 | 915.132
2030-02-15 23:00 | 572.631 | 1 | 55.969 | 53.895 | 167.8216
2030-02-17 | -253.098 | 1.4505 | 54.7969 | 53.895 | -74.1757
2030-02-18 01:00 | -621.694 | 2.4527 | 54.0729 | 53.895 | -182.2005
2030-02-19 02:00 | -838.785 | 3.0352 | 53.7109 | 53.895 | -245.8236
2030-02-20 03:00 | -884.851 | 3.1286 | 53.4645 | 53.895 | -259.3242
2030-02-21 04:00 | -910.204 | 3.2062 | 53.2592 | 53.895 | -266.7545
2030-02-22 05:00 | -551.525 | 2.0872 | 53.2214 | 53.895 | -161.636
2030-02-23 06:00 | -185.002 | 1.0667 | 53.5911 | 53.895 | -54.2187
2030-02-24 07:00 | 2022.28 | 1 | 54.0498 | 53.895 | 592.6718
2030-02-25 08:00 | 2803.6 | 1 | 54.1606 | 53.895 | 821.6541
2030-02-26 09:00 | 3160.09 | 1.0553 | 68.9208 | 53.895 | 926.131
2030-02-27 10:00 | 5636.79 | 1.8451 | 69.2914 | 53.895 | 1651.9801
2030-02-28 11:00 | 7412.59 | 2.5357 | 69.0742 | 53.895 | 2172.4157
2030-03-01 12:00 | 8733.28 | 2.8877 | 70.0199 | 53.895 | 2559.4717
2030-03-02 13:00 | 9428.09 | 3.0271 | 70.8593 | 53.895 | 2763.1004
2030-03-03 14:00 | 10129.4 | 3.2972 | 71.018 | 53.895 | 2968.6341
2030-03-04 15:00 | 11669.8 | 3.8852 | 71.0475 | 53.895 | 3420.0808
2030-03-05 16:00 | 11908.8 | 3.8957 | 71.7144 | 53.895 | 3490.1248
2030-03-06 17:00 | 11680.8 | 3.7407 | 72.3367 | 53.895 | 3423.3046
2030-03-07 18:00 | 9911.9 | 3.1123 | 72.8442 | 53.895 | 2904.8911
2030-03-08 19:00 | 8395.41 | 2.5981 | 73.0453 | 53.895 | 2460.4518
2030-03-09 20:00 | 5769.81 | 1.7337 | 73.3885 | 53.895 | 1690.9644
2030-03-10 21:00 | 4071.43 | 1.2829 | 72.334 | 53.895 | 1193.2183
2030-03-11 22:00 | 3098.66 | 1 | 56.5593 | 53.895 | 908.1276
2030-03-12 23:00 | 3022.98 | 1 | 56.2572 | 53.895 | 885.948
2030-03-14 | 0 | 0 | 56.5794 | 53.895 | 0
2030-03-15 01:00 | -129.317 | 0.9426 | 55.4231 | 53.895 | -37.8991
2030-03-16 02:00 | -239.832 | 1.3266 | 54.8997 | 53.895 | -70.2878
2030-03-17 03:00 | -256.129 | 1.3443 | 54.6437 | 53.895 | -75.064
2030-03-18 04:00 | -219.437 | 1.2338 | 54.52 | 53.895 | -64.3106
2030-03-19 05:00 | 559.755 | 1 | 55.0884 | 53.895 | 164.048
2030-03-20 06:00 | 1950.75 | 1 | 54.8481 | 53.895 | 571.7084
2030-03-21 07:00 | 2763.85 | 1 | 54.841 | 53.895 | 810.0045
2030-03-22 08:00 | 3019.06 | 1 | 54.9584 | 53.895 | 884.7991
2030-03-23 09:00 | 3194.48 | 1 | 71.4357 | 53.895 | 936.2097
2030-03-24 10:00 | 5767.84 | 1.8229 | 70.479 | 53.895 | 1690.387
2030-03-25 11:00 | 6753.18 | 2.21 | 70.3245 | 53.895 | 1979.1617
2030-03-26 12:00 | 6561.04 | 2.1142 | 70.8768 | 53.895 | 1922.851
2030-03-27 13:00 | 6725.76 | 2.2481 | 70.5024 | 53.895 | 1971.1257
2030-03-28 14:00 | 7572.72 | 2.4247 | 71.2537 | 53.895 | 2219.3452
2030-03-29 15:00 | 9650.57 | 3.2688 | 70.6694 | 53.895 | 2828.3029
2030-03-30 16:00 | 10409 | 3.4549 | 71.3212 | 53.895 | 3050.5768
2030-03-31 17:00 | 10499.3 | 3.4813 | 71.6417 | 53.895 | 3077.0411
2030-04-01 18:00 | 9157.61 | 2.9649 | 72.2087 | 53.895 | 2683.8306
2030-04-02 19:00 | 7414.99 | 2.3271 | 72.703 | 53.895 | 2173.1191
2030-04-03 20:00 | 5005.3 | 1.5102 | 73.1928 | 53.895 | 1466.9086
2030-04-04 21:00 | 3663 | 1.1797 | 71.9001 | 53.895 | 1073.5193
2030-04-05 22:00 | 3097.8 | 1 | 56.4919 | 53.895 | 907.8756
2030-04-06 23:00 | 3147.61 | 1 | 56.2266 | 53.895 | 922.4734
2030-04-08 | 2345.98 | 1 | 56.2296 | 53.895 | 687.5389
2030-04-09 01:00 | 0 | 0 | 56.4499 | 53.895 | 0
2030-04-10 02:00 | -123.059 | 0.97263 | 55.4634 | 53.895 | -36.065
2030-04-11 03:00 | -132.252 | 0.99965 | 55.1826 | 53.895 | -38.7592
2030-04-12 04:00 | -98.8483 | 0.89816 | 55.1161 | 53.895 | -28.9696
2030-04-13 05:00 | 1629.33 | 1 | 55.1843 | 53.895 | 477.5095
2030-04-14 06:00 | 2782.97 | 1 | 55.0503 | 53.895 | 815.608
2030-04-15 07:00 | 3057.04 | 1 | 77.8725 | 53.895 | 895.93
2030-04-16 08:00 | 3049.33 | 1 | 72.4615 | 53.895 | 893.6704
2030-04-17 09:00 | 4200.25 | 1.4116 | 69.818 | 53.895 | 1230.9718
2030-04-18 10:00 | 6010.11 | 2.0827 | 69.5861 | 53.895 | 1761.3894
2030-04-19 11:00 | 7452.14 | 2.6064 | 69.7654 | 53.895 | 2184.0066
2030-04-20 12:00 | 8142.24 | 2.7194 | 70.732 | 53.895 | 2386.255
2030-04-21 13:00 | 8709.01 | 2.8391 | 71.3766 | 53.895 | 2552.3589
2030-04-22 14:00 | 9386.95 | 3.0619 | 71.6519 | 53.895 | 2751.0435
2030-04-23 15:00 | 10885.8 | 3.6759 | 71.4367 | 53.895 | 3190.3131
2030-04-24 16:00 | 11705.6 | 3.8051 | 72.3386 | 53.895 | 3430.5727
2030-04-25 17:00 | 11403.7 | 3.7301 | 72.5722 | 53.895 | 3342.0946
2030-04-26 18:00 | 9722.48 | 3.1073 | 73.1001 | 53.895 | 2849.3776
2030-04-27 19:00 | 7976.94 | 2.5269 | 73.2064 | 53.895 | 2337.8103
2030-04-28 20:00 | 5325.58 | 1.5829 | 74.0473 | 53.895 | 1560.7734
2030-04-29 21:00 | 3782.96 | 1.1966 | 72.7414 | 53.895 | 1108.6761
2030-04-30 22:00 | 3075.86 | 1 | 57.0286 | 53.895 | 901.4456
2030-05-01 23:00 | 3014.1 | 1 | 56.732 | 53.895 | 883.3455
2030-05-03 | 785.613 | 1 | 56.9202 | 53.895 | 230.2404
2030-05-04 01:00 | -4.9812 | 0.70102 | 56.6179 | 53.895 | -1.4598
2030-05-05 02:00 | -199.585 | 1.2179 | 55.5457 | 53.895 | -58.4926
2030-05-06 03:00 | -244.368 | 1.3108 | 55.2074 | 53.895 | -71.6172
2030-05-07 04:00 | -218.96 | 1.2284 | 55.049 | 53.895 | -64.1708
2030-05-08 05:00 | 1641.75 | 1 | 55.4132 | 53.895 | 481.1494
2030-05-09 06:00 | 2767.5 | 1 | 55.3114 | 53.895 | 811.0742
2030-05-10 07:00 | 3059.82 | 1 | 72.2152 | 53.895 | 896.7447
2030-05-11 08:00 | 3498.69 | 1.1285 | 70.5758 | 53.895 | 1025.3648
2030-05-12 09:00 | 5702.79 | 1.8073 | 70.9542 | 53.895 | 1671.3228
2030-05-13 10:00 | 7472.31 | 2.5627 | 70.1795 | 53.895 | 2189.9179
2030-05-14 11:00 | 8997.81 | 3.0675 | 70.6535 | 53.895 | 2636.9978
2030-05-15 12:00 | 9900.4 | 3.3046 | 71.3622 | 53.895 | 2901.5208
2030-05-16 13:00 | 10634.7 | 3.5383 | 71.7983 | 53.895 | 3116.7229
2030-05-17 14:00 | 11187.7 | 3.6461 | 72.4662 | 53.895 | 3278.7912
2030-05-18 15:00 | 12731.4 | 4.1631 | 72.73 | 53.895 | 3731.205
2030-05-19 16:00 | 13217.2 | 4.3264 | 73.1246 | 53.895 | 3873.5789
2030-05-20 17:00 | 12975.6 | 4.255 | 73.4264 | 53.895 | 3802.773
2030-05-21 18:00 | 12005.2 | 3.6858 | 74.6106 | 53.895 | 3518.3768
2030-05-22 19:00 | 9857.42 | 3.0661 | 74.5032 | 53.895 | 2888.9246
2030-05-23 20:00 | 7398.9 | 2.1597 | 75.3831 | 53.895 | 2168.4035
2030-05-24 21:00 | 5054.76 | 1.6141 | 73.6904 | 53.895 | 1481.4039
2030-05-25 22:00 | 2867.78 | 1 | 58.1065 | 53.895 | 840.4634
2030-05-26 23:00 | 0 | 0 | 58.086 | 53.895 | 0
2030-05-28 | -713.803 | 2.6965 | 56.1786 | 53.895 | -209.195
2030-05-29 01:00 | -1159.61 | 3.9056 | 55.5388 | 53.895 | -339.8481
2030-05-30 02:00 | -1340.91 | 4.357 | 55.1169 | 53.895 | -392.9819
2030-05-31 03:00 | -1553.74 | 4.9817 | 54.7824 | 53.895 | -455.3562
2030-06-01 04:00 | -1771.9 | 5.6096 | 54.4855 | 53.895 | -519.2926
2030-06-02 05:00 | -2083.24 | 6.5301 | 54.2291 | 53.895 | -610.5374
2030-06-03 06:00 | -1719.36 | 5.3238 | 53.9612 | 53.895 | -503.8947
2030-06-04 07:00 | -1071.18 | 3.4492 | 53.8631 | 53.895 | -313.9319
2030-06-05 08:00 | -1400.79 | 4.6636 | 53.8546 | 53.895 | -410.531
2030-06-06 09:00 | -914.066 | 3.0395 | 53.7202 | 53.895 | -267.8863
2030-06-07 10:00 | 0 | 1 | 55.0668 | 53.895 | 0
2030-06-08 11:00 | 2753.93 | 1 | 54.6478 | 53.895 | 807.0972
2030-06-09 12:00 | 2984.11 | 1 | 76.9729 | 53.895 | 874.5563
2030-06-10 13:00 | 3037.91 | 1 | 69.8698 | 53.895 | 890.3235
2030-06-11 14:00 | 3577.98 | 1.1801 | 69.8871 | 53.895 | 1048.6024
2030-06-12 15:00 | 4301.31 | 1.4192 | 69.9911 | 53.895 | 1260.5895
2030-06-13 16:00 | 6829.09 | 2.3155 | 69.7495 | 53.895 | 2001.4087
2030-06-14 17:00 | 6007.43 | 2.0172 | 70.2466 | 53.895 | 1760.6039
2030-06-15 18:00 | 4732.48 | 1.5992 | 70.2698 | 53.895 | 1386.953
2030-06-16 19:00 | 2852.68 | 1 | 70.3305 | 53.895 | 836.038
2030-06-17 20:00 | 2855.26 | 1 | 55.6479 | 53.895 | 836.7941
2030-06-18 21:00 | 2679.13 | 1 | 55.6211 | 53.895 | 785.1755
2030-06-19 22:00 | -103.703 | 0.99228 | 55.5175 | 53.895 | -30.3923
2030-06-20 23:00 | -1708.04 | 5.7909 | 54.223 | 53.895 | -500.5771
2030-06-22 | -2406.22 | 6.8587 | 53.5453 | 53.895 | -705.1935
2030-06-23 01:00 | -2818.52 | 6.8587 | 52.9732 | 53.895 | -826.0267
2030-06-24 02:00 | -3308.62 | 6.8587 | 52.3793 | 53.895 | -969.6608
2030-06-25 03:00 | -3458.63 | 6.8587 | 51.9973 | 53.895 | -1013.6244
2030-06-26 04:00 | -3758.74 | 6.8587 | 51.5652 | 53.895 | -1101.578
2030-06-27 05:00 | -3815.71 | 6.8587 | 51.3226 | 53.895 | -1118.2742
2030-06-28 06:00 | -2575.78 | 6.8587 | 51.9999 | 53.895 | -754.8866
2030-06-29 07:00 | -1594.9 | 5.0364 | 52.2931 | 53.895 | -467.419
2030-06-30 08:00 | -1336.98 | 4.3857 | 52.4371 | 53.895 | -391.8302
2030-07-01 09:00 | -571.856 | 2.0429 | 52.5789 | 53.895 | -167.5944
2030-07-02 10:00 | 2471.95 | 1 | 53.5691 | 53.895 | 724.457
2030-07-03 11:00 | 3024.56 | 1 | 72.9583 | 53.895 | 886.411
2030-07-04 12:00 | 3844.26 | 1.2455 | 69.1524 | 53.895 | 1126.6414
2030-07-05 13:00 | 4793.52 | 1.5574 | 69.3673 | 53.895 | 1404.842
2030-07-06 14:00 | 5722.66 | 1.8823 | 69.4891 | 53.895 | 1677.1461
2030-07-07 15:00 | 6489.51 | 2.138 | 69.78 | 53.895 | 1901.8876
2030-07-08 16:00 | 8963.96 | 3.0516 | 69.5703 | 53.895 | 2627.0773
2030-07-09 17:00 | 8358.98 | 2.7356 | 70.6175 | 53.895 | 2449.7752
2030-07-10 18:00 | 7190.17 | 2.3757 | 70.7311 | 53.895 | 2107.2308
2030-07-11 19:00 | 5405.02 | 1.7088 | 71.4225 | 53.895 | 1584.055
2030-07-12 20:00 | 3731.87 | 1.185 | 71.2539 | 53.895 | 1093.7031
2030-07-13 21:00 | 3154.15 | 1 | 77.9044 | 53.895 | 924.3901
2030-07-14 22:00 | 3072.29 | 1 | 55.5819 | 53.895 | 900.3993
2030-07-15 23:00 | -235.655 | 1.3546 | 55.2059 | 53.895 | -69.0637
2030-07-17 | -771.497 | 2.908 | 54.316 | 53.895 | -226.1035
2030-07-18 01:00 | -1014.24 | 3.5227 | 53.889 | 53.895 | -297.2444
2030-07-19 02:00 | -1178.04 | 3.9776 | 53.6594 | 53.895 | -345.2494
2030-07-20 03:00 | -1025.17 | 3.4653 | 53.4837 | 53.895 | -300.4477
2030-07-21 04:00 | -955.497 | 3.308 | 53.3532 | 53.895 | -280.0285
2030-07-22 05:00 | -301.717 | 1.2995 | 53.5341 | 53.895 | -88.4245
2030-07-23 06:00 | -71.5265 | 0.79447 | 54.2054 | 53.895 | -20.9623
2030-07-24 07:00 | 2011.11 | 1 | 54.2951 | 53.895 | 589.3982
2030-07-25 08:00 | 2930.2 | 1 | 54.3947 | 53.895 | 858.7568
2030-07-26 09:00 | 3537.36 | 1.1494 | 69.6068 | 53.895 | 1036.6979
2030-07-27 10:00 | 5740.32 | 1.9007 | 69.4736 | 53.895 | 1682.3217
2030-07-28 11:00 | 7840.7 | 2.6054 | 69.829 | 53.895 | 2297.8823
2030-07-29 12:00 | 9092.41 | 3.0065 | 70.4285 | 53.895 | 2664.7223
2030-07-30 13:00 | 7445.96 | 2.2944 | 71.9345 | 53.895 | 2182.1955
2030-07-31 14:00 | 6669.79 | 2.0169 | 72.329 | 53.895 | 1954.7225
2030-08-01 15:00 | 8261.58 | 2.676 | 71.3267 | 53.895 | 2421.2301
2030-08-02 16:00 | 8448.85 | 2.7033 | 71.7594 | 53.895 | 2476.1135
2030-08-03 17:00 | 8531.72 | 2.7427 | 71.8643 | 53.895 | 2500.4003
2030-08-04 18:00 | 7293.51 | 2.3193 | 72.1376 | 53.895 | 2137.5168
2030-08-05 19:00 | 6306.31 | 1.9412 | 72.6043 | 53.895 | 1848.197
2030-08-06 20:00 | 3972.7 | 1.1859 | 73.0209 | 53.895 | 1164.2834
2030-08-07 21:00 | 3104.91 | 1 | 72.498 | 53.895 | 909.9593
2030-08-08 22:00 | 3046.6 | 1 | 56.2441 | 53.895 | 892.8703
2030-08-09 23:00 | 1463.98 | 1 | 56.3635 | 53.895 | 429.0502
2030-08-11 | 351.219 | 1 | 56.2488 | 53.895 | 102.9321
2030-08-12 01:00 | 33.9099 | 1 | 55.9839 | 53.895 | 9.938
2030-08-13 02:00 | 30.0895 | 1 | 55.7919 | 53.895 | 8.8184
2030-08-14 03:00 | 1295.14 | 1 | 55.4344 | 53.895 | 379.5681
2030-08-15 04:00 | 1696.2 | 1 | 55.3926 | 53.895 | 497.1071
2030-08-16 05:00 | 2488.3 | 1 | 55.2944 | 53.895 | 729.2487
2030-08-17 06:00 | 2830.06 | 1 | 76.1441 | 53.895 | 829.4087
2030-08-18 07:00 | 3033.42 | 1 | 71.7196 | 53.895 | 889.0076
2030-08-19 08:00 | 3152.07 | 1 | 78.0609 | 53.895 | 923.7805
2030-08-20 09:00 | 3355.5 | 1.0384 | 71.195 | 53.895 | 983.4
2030-08-21 10:00 | 4730.36 | 1.5052 | 70.8365 | 53.895 | 1386.3317
2030-08-22 11:00 | 5684.38 | 1.8237 | 70.8989 | 53.895 | 1665.9273
2030-08-23 12:00 | 6602.75 | 2.1767 | 70.7238 | 53.895 | 1935.075
2030-08-24 13:00 | 7119.95 | 2.3062 | 71.2197 | 53.895 | 2086.6514
2030-08-25 14:00 | 7431.39 | 2.4142 | 71.4051 | 53.895 | 2177.9254
2030-08-26 15:00 | 8717.02 | 2.9247 | 71.1248 | 53.895 | 2554.7064
2030-08-27 16:00 | 9169.65 | 3.0686 | 71.4273 | 53.895 | 2687.3591
2030-08-28 17:00 | 9465.94 | 3.0483 | 72.196 | 53.895 | 2774.1932
2030-08-29 18:00 | 8312.7 | 2.6606 | 72.4726 | 53.895 | 2436.2119
2030-08-30 19:00 | 7358.73 | 2.2662 | 73.065 | 53.895 | 2156.6309
2030-08-31 20:00 | 5228.49 | 1.5219 | 73.9118 | 53.895 | 1532.3192
2030-09-01 21:00 | 4131.02 | 1.2489 | 73.0763 | 53.895 | 1210.6825
2030-09-02 22:00 | 3123.04 | 1 | 56.8031 | 53.895 | 915.2727
2030-09-03 23:00 | 3178.36 | 1 | 56.5511 | 53.895 | 931.4854
2030-09-05 | 2889.78 | 1 | 56.4681 | 53.895 | 846.9109
2030-09-06 01:00 | 651.334 | 1 | 56.7311 | 53.895 | 190.8872
2030-09-07 02:00 | 558.568 | 1 | 56.4013 | 53.895 | 163.7001
2030-09-08 03:00 | 3145.36 | 1 | 55.7263 | 53.895 | 921.814
2030-09-09 04:00 | 3176.8 | 1 | 55.9024 | 53.895 | 931.0282
2030-09-10 05:00 | 3204.78 | 1 | 55.9422 | 53.895 | 939.2283
2030-09-11 06:00 | 3185.91 | 1 | 55.9257 | 53.895 | 933.6981
2030-09-12 07:00 | 3268.43 | 1 | 74.3258 | 53.895 | 957.8823
2030-09-13 08:00 | 3296.81 | 1 | 73.1218 | 53.895 | 966.1996
2030-09-14 09:00 | 4604.52 | 1.4585 | 71.326 | 53.895 | 1349.4516
2030-09-15 10:00 | 5001.88 | 1.5861 | 71.471 | 53.895 | 1465.9063
2030-09-16 11:00 | 6255.13 | 2.0689 | 70.9798 | 53.895 | 1833.1976
2030-09-17 12:00 | 7025.15 | 2.2719 | 71.5102 | 53.895 | 2058.8682
2030-09-18 13:00 | 7204.38 | 2.3228 | 71.8042 | 53.895 | 2111.3954
2030-09-19 14:00 | 7877.42 | 2.4686 | 72.4143 | 53.895 | 2308.6439
2030-09-20 15:00 | 9725.08 | 3.3934 | 71.0606 | 53.895 | 2850.1396
2030-09-21 16:00 | 10671.5 | 3.6124 | 71.825 | 53.895 | 3127.5079
2030-09-22 17:00 | 10931.9 | 3.6278 | 72.4259 | 53.895 | 3203.8236
2030-09-23 18:00 | 9602.14 | 3.0096 | 73.5075 | 53.895 | 2814.1094
2030-09-24 19:00 | 8170.68 | 2.5354 | 73.7084 | 53.895 | 2394.5899
2030-09-25 20:00 | 6036.91 | 1.751 | 74.7055 | 53.895 | 1769.2437
2030-09-26 21:00 | 4756.23 | 1.4331 | 73.8475 | 53.895 | 1393.9134
2030-09-27 22:00 | 3150.7 | 1 | 78.6176 | 53.895 | 923.379
2030-09-28 23:00 | 3082.65 | 1 | 57.1586 | 53.895 | 903.4355
2030-09-30 | 3094.53 | 1 | 56.9539 | 53.895 | 906.9172
2030-10-01 01:00 | 3124.07 | 1 | 56.8341 | 53.895 | 915.5745
2030-10-02 02:00 | 3233.91 | 1 | 56.7442 | 53.895 | 947.7655
2030-10-03 03:00 | 3160.55 | 1 | 56.6887 | 53.895 | 926.2658
2030-10-04 04:00 | 3139.35 | 1 | 56.6311 | 53.895 | 920.0527
2030-10-05 05:00 | 3160.53 | 1 | 56.56 | 53.895 | 926.2599
2030-10-06 06:00 | 3317.54 | 1 | 76.6687 | 53.895 | 972.275
2030-10-07 07:00 | 3743.31 | 1.1581 | 72.1479 | 53.895 | 1097.0559
2030-10-08 08:00 | 3184.4 | 1 | 72.3185 | 53.895 | 933.2555
2030-10-09 09:00 | 4229.98 | 1.3023 | 72.2221 | 53.895 | 1239.6848
2030-10-10 10:00 | 6067.79 | 1.9751 | 71.4933 | 53.895 | 1778.2937
2030-10-11 11:00 | 7686.05 | 2.6912 | 70.7588 | 53.895 | 2252.5589
2030-10-12 12:00 | 7421.99 | 2.3863 | 72.2969 | 53.895 | 2175.1706
2030-10-13 13:00 | 8769.99 | 2.9385 | 71.858 | 53.895 | 2570.2304
2030-10-14 14:00 | 8911.01 | 2.8541 | 72.7954 | 53.895 | 2611.5592
2030-10-15 15:00 | 9544.3 | 3.2217 | 72.2553 | 53.895 | 2797.1582
2030-10-16 16:00 | 10835.9 | 3.5501 | 72.8655 | 53.895 | 3175.6888
2030-10-17 17:00 | 10139.7 | 3.2364 | 73.5261 | 53.895 | 2971.6527
2030-10-18 18:00 | 8515.63 | 2.6627 | 73.9608 | 53.895 | 2495.6848
2030-10-19 19:00 | 7378.39 | 2.268 | 74.1234 | 53.895 | 2162.3927
2030-10-20 20:00 | 4887.7 | 1.457 | 74.4949 | 53.895 | 1432.4435
2030-10-21 21:00 | 3738.2 | 1.1647 | 73.4969 | 53.895 | 1095.5583
2030-10-22 22:00 | 3146.38 | 1 | 57.5949 | 53.895 | 922.113
2030-10-23 23:00 | 3057.19 | 1 | 57.3466 | 53.895 | 895.9739
2030-10-25 | 2254.51 | 1 | 57.3094 | 53.895 | 660.7317
2030-10-26 01:00 | 532.481 | 1 | 57.3706 | 53.895 | 156.0548
2030-10-27 02:00 | -4.5894 | 0.67713 | 57.11 | 53.895 | -1.345
2030-10-28 03:00 | 116.556 | 1 | 56.7901 | 53.895 | 34.1592
2030-10-29 04:00 | 83.0783 | 1 | 56.5945 | 53.895 | 24.3478
2030-10-30 05:00 | 1746.76 | 1 | 56.1203 | 53.895 | 511.9248
2030-10-31 06:00 | 2669.44 | 1 | 56.0098 | 53.895 | 782.3356
2030-11-01 07:00 | 3013.36 | 1 | 72.5043 | 53.895 | 883.1286
2030-11-02 08:00 | 3374.35 | 1.084 | 71.2604 | 53.895 | 988.9244
2030-11-03 09:00 | 5918.29 | 1.9239 | 71.1815 | 53.895 | 1734.4796
2030-11-04 10:00 | 7976.33 | 2.7295 | 70.8308 | 53.895 | 2337.6316
2030-11-05 11:00 | 9630.12 | 3.3096 | 71.2088 | 53.895 | 2822.3096
2030-11-06 12:00 | 9729.21 | 3.3485 | 71.6356 | 53.895 | 2851.35
2030-11-07 13:00 | 10784 | 3.5945 | 72.388 | 53.895 | 3160.4784
2030-11-08 14:00 | 11320.9 | 3.7259 | 72.9479 | 53.895 | 3317.8283
2030-11-09 15:00 | 13444 | 4.436 | 73.2303 | 53.895 | 3940.0475
2030-11-10 16:00 | 13630.2 | 4.532 | 73.5993 | 53.895 | 3994.6173
2030-11-11 17:00 | 13594.2 | 4.398 | 74.3165 | 53.895 | 3984.0667
2030-11-12 18:00 | 12151.5 | 3.819 | 74.9955 | 53.895 | 3561.2531
2030-11-13 19:00 | 10521.8 | 3.2556 | 75.2887 | 53.895 | 3083.6352
2030-11-14 20:00 | 7531.03 | 2.298 | 75.4474 | 53.895 | 2207.127
2030-11-15 21:00 | 6249.15 | 1.8606 | 75.4683 | 53.895 | 1831.4451
2030-11-16 22:00 | 3649.97 | 1.1272 | 74.5781 | 53.895 | 1069.7006
2030-11-17 23:00 | 3019.68 | 1 | 58.3914 | 53.895 | 884.9808
2030-11-19 | 3024.88 | 1 | 58.0167 | 53.895 | 886.5048
2030-11-20 01:00 | 2743.33 | 1 | 57.8324 | 53.895 | 803.9907
2030-11-21 02:00 | 766.75 | 1 | 57.9838 | 53.895 | 224.7122
2030-11-22 03:00 | 187.644 | 1 | 57.6648 | 53.895 | 54.993
2030-11-23 04:00 | -63.5843 | 0.83092 | 57.0094 | 53.895 | -18.6347
2030-11-24 05:00 | -95.9071 | 0.89258 | 56.5989 | 53.895 | -28.1076
2030-11-25 06:00 | 1969.44 | 1 | 56.5358 | 53.895 | 577.1859
2030-11-26 07:00 | 2743.12 | 1 | 71.9509 | 53.895 | 803.9291
2030-11-27 08:00 | 2913.58 | 1 | 56.5406 | 53.895 | 853.886
2030-11-28 09:00 | 3028.64 | 1 | 56.5686 | 53.895 | 887.6068
2030-11-29 10:00 | 3141.76 | 1 | 72.5715 | 53.895 | 920.759
2030-11-30 11:00 | 3932.97 | 1.2171 | 72.2783 | 53.895 | 1152.6397
2030-12-01 12:00 | 4739.95 | 1.4929 | 72.087 | 53.895 | 1389.1422
2030-12-02 13:00 | 5175.85 | 1.6106 | 72.374 | 53.895 | 1516.8919
2030-12-03 14:00 | 5960.58 | 1.9171 | 71.9897 | 53.895 | 1746.8736
2030-12-04 15:00 | 6769.95 | 2.1862 | 72.0734 | 53.895 | 1984.0765
2030-12-05 16:00 | 9766.37 | 3.4105 | 71.1574 | 53.895 | 2862.2405
2030-12-06 17:00 | 9077.78 | 2.9178 | 72.7985 | 53.895 | 2660.4347
2030-12-07 18:00 | 8189.61 | 2.671 | 72.7766 | 53.895 | 2400.1378
2030-12-08 19:00 | 7034.54 | 2.2248 | 73.2472 | 53.895 | 2061.6202
2030-12-09 20:00 | 6054.15 | 1.8419 | 73.7857 | 53.895 | 1774.2962
2030-12-10 21:00 | 5154.09 | 1.6499 | 72.9364 | 53.895 | 1510.5147
2030-12-11 22:00 | 4420.49 | 1.4051 | 72.8866 | 53.895 | 1295.5177
2030-12-12 23:00 | 3020.91 | 1 | 57.4798 | 53.895 | 885.3413
2030-12-14 | 3062.29 | 1 | 57.2235 | 53.895 | 897.4686
2030-12-15 01:00 | 47.6809 | 1 | 57.616 | 53.895 | 13.9739
2030-12-16 02:00 | 260.131 | 1 | 57.1438 | 53.895 | 76.2369
2030-12-17 03:00 | -25.6423 | 0.72751 | 56.7775 | 53.895 | -7.515
2030-12-18 04:00 | -134.597 | 1.0188 | 56.1106 | 53.895 | -39.4465
2030-12-19 05:00 | -142.066 | 1.0171 | 55.8898 | 53.895 | -41.6354
2030-12-20 06:00 | 1767.05 | 1 | 56.0663 | 53.895 | 517.8712
2030-12-21 07:00 | 2676.44 | 1 | 74.1535 | 53.895 | 784.3871
2030-12-22 08:00 | 2891.87 | 1 | 56.1503 | 53.895 | 847.5234
2030-12-23 09:00 | 3232.23 | 1 | 74.3945 | 53.895 | 947.2731
2030-12-24 10:00 | 4342.53 | 1.3471 | 71.8929 | 53.895 | 1272.6699
2030-12-25 11:00 | 6066.68 | 1.9425 | 71.6188 | 53.895 | 1777.9684
2030-12-26 12:00 | 6298.02 | 1.9276 | 72.5909 | 53.895 | 1845.7675
2030-12-27 13:00 | 6864.57 | 2.1955 | 72.1371 | 53.895 | 2011.8069
2030-12-28 14:00 | 7880.47 | 2.6343 | 71.7018 | 53.895 | 2309.5378
2030-12-29 15:00 | 8832.25 | 3.0188 | 71.6639 | 53.895 | 2588.477
2030-12-30 16:00 | 12205.9 | 4.186 | 71.8849 | 53.895 | 3577.1962
2030-12-31 17:00 | 11088.8 | 3.7536 | 72.6538 | 53.895 | 3249.8065
2031-01-01 18:00 | 10158.9 | 3.2264 | 73.7979 | 53.895 | 2977.2797
2031-01-02 19:00 | 8745.58 | 2.7078 | 74.2403 | 53.895 | 2563.0765
2031-01-03 20:00 | 7512.72 | 2.3222 | 74.2302 | 53.895 | 2201.7609
2031-01-04 21:00 | 6413.41 | 1.9751 | 74.187 | 53.895 | 1879.5849
2031-01-05 22:00 | 5845.82 | 1.7617 | 74.3235 | 53.895 | 1713.2407
2031-01-06 23:00 | 3280.24 | 1 | 77.2565 | 53.895 | 961.3434
2031-01-08 | 3181.66 | 1 | 57.6979 | 53.895 | 932.4525
2031-01-09 01:00 | 3159.4 | 1 | 57.4926 | 53.895 | 925.9287
2031-01-10 02:00 | 3205.04 | 1 | 57.3699 | 53.895 | 939.3045
2031-01-11 03:00 | 3095 | 1 | 57.3004 | 53.895 | 907.055
2031-01-12 04:00 | 3190.27 | 1 | 57.1584 | 53.895 | 934.9758
2031-01-13 05:00 | 3168.16 | 1 | 73.3171 | 53.895 | 928.496
2031-01-14 06:00 | 3654.01 | 1.1509 | 72.4667 | 53.895 | 1070.8846
2031-01-15 07:00 | 3909.67 | 1.2151 | 72.6792 | 53.895 | 1145.8112
2031-01-16 08:00 | 3179.45 | 1 | 74.2332 | 53.895 | 931.8048
2031-01-17 09:00 | 4178.59 | 1.2934 | 72.6845 | 53.895 | 1224.6238
2031-01-18 10:00 | 5405.45 | 1.7585 | 72.016 | 53.895 | 1584.181
2031-01-19 11:00 | 6418.83 | 2.1485 | 71.8127 | 53.895 | 1881.1734
2031-01-20 12:00 | 7175.32 | 2.3418 | 72.3902 | 53.895 | 2102.8787
2031-01-21 13:00 | 8146.56 | 2.5996 | 72.9249 | 53.895 | 2387.5211
2031-01-22 14:00 | 9758.41 | 3.225 | 72.6818 | 53.895 | 2859.9077
2031-01-23 15:00 | 11564 | 3.9154 | 72.7044 | 53.895 | 3389.0739
2031-01-24 16:00 | 11613.1 | 3.8171 | 73.543 | 53.895 | 3403.4636
2031-01-25 17:00 | 10666.8 | 3.5524 | 73.6323 | 53.895 | 3126.1305
2031-01-26 18:00 | 8410.88 | 2.7054 | 74.2249 | 53.895 | 2464.9856
2031-01-27 19:00 | 7387.02 | 2.2582 | 74.8318 | 53.895 | 2164.9219
2031-01-28 20:00 | 5115.35 | 1.5508 | 74.8173 | 53.895 | 1499.1611
2031-01-29 21:00 | 3874.62 | 1.1781 | 74.4323 | 53.895 | 1135.539
2031-01-30 22:00 | 3065.78 | 1 | 58.1527 | 53.895 | 898.4914
2031-01-31 23:00 | 2906.4 | 1 | 57.8926 | 53.895 | 851.7818
2031-02-02 | 332.469 | 1 | 58.1438 | 53.895 | 97.437
2031-02-03 01:00 | -40.1353 | 0.76868 | 57.4982 | 53.895 | -11.7625
2031-02-04 02:00 | -158.762 | 1.0796 | 56.7173 | 53.895 | -46.5285
2031-02-05 03:00 | -47.6379 | 0.72665 | 56.8582 | 53.895 | -13.9613
2031-02-06 04:00 | 0 | 0 | 56.9721 | 53.895 | 0
2031-02-07 05:00 | 0 | 1 | 56.7925 | 53.895 | 0
2031-02-08 06:00 | 2573.73 | 1 | 56.2318 | 53.895 | 754.2858
2031-02-09 07:00 | 2886.61 | 1 | 56.3912 | 53.895 | 845.9819
2031-02-10 08:00 | 3079.68 | 1 | 56.505 | 53.895 | 902.5651
2031-02-11 09:00 | 3141.58 | 1 | 56.5689 | 53.895 | 920.7062
2031-02-12 10:00 | 3085.81 | 1 | 56.6338 | 53.895 | 904.3616
2031-02-13 11:00 | 3164.77 | 1 | 56.6473 | 53.895 | 927.5025
2031-02-14 12:00 | 3110.94 | 1 | 79.407 | 53.895 | 911.7265
2031-02-15 13:00 | 3158.4 | 1 | 77.8698 | 53.895 | 925.6357
2031-02-16 14:00 | 3174.38 | 1 | 74.1241 | 53.895 | 930.3189
2031-02-17 15:00 | 4395.47 | 1.4109 | 71.6949 | 53.895 | 1288.1851
2031-02-18 16:00 | 5533 | 1.7765 | 71.7926 | 53.895 | 1621.5622
2031-02-19 17:00 | 5295.62 | 1.7562 | 71.5138 | 53.895 | 1551.993
2031-02-20 18:00 | 4158.75 | 1.3499 | 71.8752 | 53.895 | 1218.8093
2031-02-21 19:00 | 3103.28 | 1 | 72.0972 | 53.895 | 909.4816
2031-02-22 20:00 | 2947 | 1 | 56.686 | 53.895 | 863.6804
2031-02-23 21:00 | 101.068 | 1 | 57.0863 | 53.895 | 29.6201
2031-02-24 22:00 | -638.224 | 2.5683 | 55.5153 | 53.895 | -187.045
2031-02-25 23:00 | -1003.36 | 3.4733 | 54.979 | 53.895 | -294.0558
2031-02-27 | -1252.64 | 4.1555 | 54.6942 | 53.895 | -367.1125
2031-02-28 01:00 | -1369.22 | 4.4558 | 54.4757 | 53.895 | -401.2788
2031-03-01 02:00 | -1399.4 | 4.5288 | 54.2925 | 53.895 | -410.1237
2031-03-02 03:00 | -1300.25 | 4.2225 | 54.178 | 53.895 | -381.0657
2031-03-03 04:00 | -1134.65 | 3.7481 | 54.1037 | 53.895 | -332.5331
2031-03-04 05:00 | -574.101 | 2.0761 | 54.1527 | 53.895 | -168.2524
2031-03-05 06:00 | 36.4695 | 1 | 55.4308 | 53.895 | 10.6882
2031-03-06 07:00 | 2010.5 | 1 | 55.1282 | 53.895 | 589.2194
2031-03-07 08:00 | 2772.4 | 1 | 55.2327 | 53.895 | 812.5102
2031-03-08 09:00 | 3022.49 | 1 | 70.4608 | 53.895 | 885.8044
2031-03-09 10:00 | 5259.36 | 1.6817 | 70.7392 | 53.895 | 1541.3663
2031-03-10 11:00 | 6722.32 | 2.177 | 70.9368 | 53.895 | 1970.1175
2031-03-11 12:00 | 7558.95 | 2.4891 | 71.129 | 53.895 | 2215.3096
2031-03-12 13:00 | 8046.74 | 2.6299 | 71.5835 | 53.895 | 2358.2667
2031-03-13 14:00 | 8976.37 | 2.9546 | 71.7773 | 53.895 | 2630.7144
2031-03-14 15:00 | 11290.9 | 3.7255 | 72.0781 | 53.895 | 3309.0361
2031-03-15 16:00 | 11744.4 | 3.7949 | 72.8854 | 53.895 | 3441.9439
2031-03-16 17:00 | 11756.4 | 3.8582 | 73.0471 | 53.895 | 3445.4607
2031-03-17 18:00 | 10495.5 | 3.3245 | 73.8491 | 53.895 | 3075.9274
2031-03-18 19:00 | 8805.01 | 2.6908 | 74.4846 | 53.895 | 2580.4937
2031-03-19 20:00 | 6075.99 | 1.7245 | 75.5967 | 53.895 | 1780.6969
2031-03-20 21:00 | 4372.81 | 1.3367 | 74.1078 | 53.895 | 1281.5441
2031-03-21 22:00 | 3084.64 | 1 | 57.9128 | 53.895 | 904.0187
2031-03-22 23:00 | 3050.2 | 1 | 57.5718 | 53.895 | 893.9254
2031-03-24 | 110.936 | 1 | 57.8659 | 53.895 | 32.5121
2031-03-25 01:00 | -73.3243 | 0.89487 | 57.0013 | 53.895 | -21.4892
2031-03-26 02:00 | -279.45 | 1.429 | 56.1462 | 53.895 | -81.8987
2031-03-27 03:00 | -325.156 | 1.5214 | 55.8245 | 53.895 | -95.2938
2031-03-28 04:00 | -283.782 | 1.3926 | 55.6668 | 53.895 | -83.1683
2031-03-29 05:00 | 905.112 | 1 | 56.2764 | 53.895 | 265.2621
2031-03-30 06:00 | 1902.77 | 1 | 56.1207 | 53.895 | 557.6468
2031-03-31 07:00 | 2717 | 1 | 56.0661 | 53.895 | 796.2741
2031-04-01 08:00 | 2983.62 | 1 | 56.1459 | 53.895 | 874.4127
2031-04-02 09:00 | 3812.74 | 1.227 | 71.3489 | 53.895 | 1117.4038
2031-04-03 10:00 | 5844.07 | 1.8993 | 71.3174 | 53.895 | 1712.7278
2031-04-04 11:00 | 7387 | 2.4747 | 71.21 | 53.895 | 2164.916
2031-04-05 12:00 | 8652.42 | 2.8733 | 71.7225 | 53.895 | 2535.774
2031-04-06 13:00 | 9251.73 | 3.0497 | 72.2129 | 53.895 | 2711.4144
2031-04-07 14:00 | 10019.6 | 3.2611 | 72.7306 | 53.895 | 2936.4549
2031-04-08 15:00 | 11432.8 | 3.7689 | 72.8718 | 53.895 | 3350.6229
2031-04-09 16:00 | 11568.9 | 3.7298 | 73.5851 | 53.895 | 3390.5099
2031-04-10 17:00 | 11895.9 | 3.8414 | 73.8311 | 53.895 | 3486.3441
2031-04-11 18:00 | 10498.7 | 3.2956 | 74.4892 | 53.895 | 3076.8652
2031-04-12 19:00 | 8718.54 | 2.7612 | 74.3997 | 53.895 | 2555.1518
2031-04-13 20:00 | 6294.22 | 1.8771 | 75.2014 | 53.895 | 1844.6538
2031-04-14 21:00 | 4880.86 | 1.4676 | 74.7694 | 53.895 | 1430.4389
2031-04-15 22:00 | 3103.16 | 1 | 78.7034 | 53.895 | 909.4464
2031-04-16 23:00 | 3151.36 | 1 | 57.9427 | 53.895 | 923.5724
2031-04-18 | 3002.89 | 1 | 57.7458 | 53.895 | 880.0602
2031-04-19 01:00 | 120.081 | 1 | 58.0784 | 53.895 | 35.1923
2031-04-20 02:00 | -16.2414 | 0.68458 | 57.6362 | 53.895 | -4.7599
2031-04-21 03:00 | 0 | 1 | 57.3042 | 53.895 | 0
2031-04-22 04:00 | 40.8488 | 1 | 57.1096 | 53.895 | 11.9716
2031-04-23 05:00 | 1733.11 | 1 | 56.6272 | 53.895 | 507.9244
2031-04-24 06:00 | 2691.69 | 1 | 56.4882 | 53.895 | 788.8565
2031-04-25 07:00 | 3033.3 | 1 | 77.4281 | 53.895 | 888.9725
2031-04-26 08:00 | 3105.33 | 1 | 78.616 | 53.895 | 910.0824
2031-04-27 09:00 | 3093.94 | 1 | 71.697 | 53.895 | 906.7443
2031-04-28 10:00 | 3971.06 | 1.292 | 71.6508 | 53.895 | 1163.8028
2031-04-29 11:00 | 5213.4 | 1.6853 | 71.8364 | 53.895 | 1527.8967
2031-04-30 12:00 | 6461.5 | 2.1124 | 71.8483 | 53.895 | 1893.6787
2031-05-01 13:00 | 6879.27 | 2.3595 | 71.4345 | 53.895 | 2016.115
2031-05-02 14:00 | 8195.9 | 2.6089 | 72.6873 | 53.895 | 2401.9812
2031-05-03 15:00 | 9802.82 | 3.3 | 72.1628 | 53.895 | 2872.9229
2031-05-04 16:00 | 10474.3 | 3.4322 | 72.9235 | 53.895 | 3069.7143
2031-05-05 17:00 | 10904.4 | 3.5197 | 73.4347 | 53.895 | 3195.7642
2031-05-06 18:00 | 9877.24 | 3.1229 | 73.9864 | 53.895 | 2894.7333
2031-05-07 19:00 | 8161.89 | 2.5624 | 74.1752 | 53.895 | 2392.0138
2031-05-08 20:00 | 6010.35 | 1.7106 | 75.6224 | 53.895 | 1761.4597
2031-05-09 21:00 | 4815.84 | 1.4529 | 74.4289 | 53.895 | 1411.3834
2031-05-10 22:00 | 3156.47 | 1 | 80.0808 | 53.895 | 925.07
2031-05-11 23:00 | 3010.9 | 1 | 57.792 | 53.895 | 882.4077
2031-05-13 | 1669.58 | 1 | 57.8035 | 53.895 | 489.3056
2031-05-14 01:00 | 147.182 | 1 | 57.7787 | 53.895 | 43.1348
2031-05-15 02:00 | -124.627 | 1.0036 | 56.8512 | 53.895 | -36.5246
2031-05-16 03:00 | -333.268 | 1.5766 | 56.167 | 53.895 | -97.6712
2031-05-17 04:00 | -420.966 | 1.7914 | 55.8442 | 53.895 | -123.373
2031-05-18 05:00 | -451.363 | 1.8669 | 55.5939 | 53.895 | -132.2814
2031-05-19 06:00 | 1609.45 | 1 | 56.2688 | 53.895 | 471.6832
2031-05-20 07:00 | 3164.94 | 1.2395 | 68.6546 | 53.895 | 927.5524
2031-05-21 08:00 | 3537.01 | 1.1924 | 70.7915 | 53.895 | 1036.5953
2031-05-22 09:00 | 5132.62 | 1.6703 | 71.4284 | 53.895 | 1504.2224
2031-05-23 10:00 | 6593.72 | 2.2002 | 71.3514 | 53.895 | 1932.4286
2031-05-24 11:00 | 8033.25 | 2.6716 | 71.7571 | 53.895 | 2354.3132
2031-05-25 12:00 | 9157.87 | 2.9682 | 72.4975 | 53.895 | 2683.9068
2031-05-26 13:00 | 9597.61 | 3.1944 | 72.4929 | 53.895 | 2812.7818
2031-05-27 14:00 | 10221.7 | 3.3216 | 73.1459 | 53.895 | 2995.6846
2031-05-28 15:00 | 10557.9 | 3.4009 | 73.5574 | 53.895 | 3094.215
2031-05-29 16:00 | 12798.8 | 4.2707 | 73.2927 | 53.895 | 3750.958
2031-05-30 17:00 | 11214.6 | 3.5308 | 74.5957 | 53.895 | 3286.6748
2031-05-31 18:00 | 8255.05 | 2.6584 | 74.3738 | 53.895 | 2419.3163
2031-06-01 19:00 | 6992.65 | 2.2122 | 74.3771 | 53.895 | 2049.3434
2031-06-02 20:00 | 5943.14 | 1.8245 | 74.6182 | 53.895 | 1741.7624
2031-06-03 21:00 | 4965.69 | 1.484 | 74.8419 | 53.895 | 1455.3001
2031-06-04 22:00 | 4001.73 | 1.2907 | 73.4261 | 53.895 | 1172.7913
2031-06-05 23:00 | 2618.27 | 1 | 58.1816 | 53.895 | 767.3392
2031-06-07 | 0 | 0 | 58.3192 | 53.895 | 0
2031-06-08 01:00 | -312.233 | 1.584 | 56.8884 | 53.895 | -91.5065
2031-06-09 02:00 | -812.688 | 2.9429 | 56.1711 | 53.895 | -238.1753
2031-06-10 03:00 | -1030.45 | 3.4808 | 55.7851 | 53.895 | -301.9951
2031-06-11 04:00 | -1365.58 | 4.4546 | 55.4492 | 53.895 | -400.212
2031-06-12 05:00 | -1119.59 | 3.6259 | 55.175 | 53.895 | -328.1194
2031-06-13 06:00 | -308.665 | 1.262 | 55.3354 | 53.895 | -90.4608
2031-06-14 07:00 | 2272.3 | 1 | 56.0621 | 53.895 | 665.9454
2031-06-15 08:00 | 1927.82 | 1 | 56.3779 | 53.895 | 564.9883
2031-06-16 09:00 | 3085.87 | 1 | 56.2388 | 53.895 | 904.3792
2031-06-17 10:00 | 3068.3 | 1 | 76.3245 | 53.895 | 899.23
2031-06-18 11:00 | 3643.3 | 1.1808 | 71.4347 | 53.895 | 1067.7458
2031-06-19 12:00 | 4385.64 | 1.4318 | 71.4625 | 53.895 | 1285.3042
2031-06-20 13:00 | 4818.83 | 1.548 | 71.828 | 53.895 | 1412.2597
2031-06-21 14:00 | 5518.8 | 1.8022 | 71.7212 | 53.895 | 1617.4006
2031-06-22 15:00 | 6326.17 | 2.0906 | 71.6935 | 53.895 | 1854.0174
2031-06-23 16:00 | 8852.51 | 2.9694 | 71.6576 | 53.895 | 2594.4146
2031-06-24 17:00 | 7984.3 | 2.6373 | 72.3033 | 53.895 | 2339.9673
2031-06-25 18:00 | 6927.59 | 2.2462 | 72.7308 | 53.895 | 2030.2762
2031-06-26 19:00 | 5346.44 | 1.701 | 72.9854 | 53.895 | 1566.8869
2031-06-27 20:00 | 3682.96 | 1.1884 | 72.6481 | 53.895 | 1079.369
2031-06-28 21:00 | 3127.26 | 1 | 78.8005 | 53.895 | 916.5094
2031-06-29 22:00 | 3064.02 | 1 | 57.1439 | 53.895 | 897.9756
2031-06-30 23:00 | -670.21 | 2.6261 | 56.3567 | 53.895 | -196.4192
2031-07-02 | -1317.94 | 4.3856 | 55.6115 | 53.895 | -386.2501
2031-07-03 01:00 | -1618.31 | 5.15 | 55.1643 | 53.895 | -474.2798
2031-07-04 02:00 | -1927.64 | 6.0382 | 54.9019 | 53.895 | -564.9355
2031-07-05 03:00 | -2088.69 | 6.4642 | 54.6468 | 53.895 | -612.1346
2031-07-06 04:00 | -2040.9 | 6.2946 | 54.3863 | 53.895 | -598.1287
2031-07-07 05:00 | -1662.32 | 5.1513 | 54.2448 | 53.895 | -487.1779
2031-07-08 06:00 | -851.296 | 2.7759 | 54.2318 | 53.895 | -249.4902
2031-07-09 07:00 | 0 | 0 | 55.6697 | 53.895 | 0
2031-07-10 08:00 | 2202.91 | 1 | 55.3655 | 53.895 | 645.6092
2031-07-11 09:00 | 2936.43 | 1 | 77.3983 | 53.895 | 860.5827
2031-07-12 10:00 | 3878.3 | 1.2921 | 70.2749 | 53.895 | 1136.6175
2031-07-13 11:00 | 5713.93 | 1.8797 | 70.7129 | 53.895 | 1674.5876
2031-07-14 12:00 | 6802.73 | 2.2382 | 71.0927 | 53.895 | 1993.6834
2031-07-15 13:00 | 7358.98 | 2.3952 | 71.6245 | 53.895 | 2156.7041
2031-07-16 14:00 | 8156.68 | 2.6375 | 72.0012 | 53.895 | 2390.4869
2031-07-17 15:00 | 10107 | 3.392 | 71.7648 | 53.895 | 2962.0693
2031-07-18 16:00 | 11151 | 3.6864 | 72.4157 | 53.895 | 3268.0355
2031-07-19 17:00 | 11360.7 | 3.6552 | 73.2168 | 53.895 | 3329.4925
2031-07-20 18:00 | 9788.25 | 3.1491 | 73.5314 | 53.895 | 2868.6529
2031-07-21 19:00 | 8258.97 | 2.5351 | 74.3032 | 53.895 | 2420.4652
2031-07-22 20:00 | 5381.13 | 1.555 | 75.1877 | 53.895 | 1577.0535
2031-07-23 21:00 | 3688.79 | 1.1604 | 73.5308 | 53.895 | 1081.0776
2031-07-24 22:00 | 3017.98 | 1 | 57.751 | 53.895 | 884.4826
2031-07-25 23:00 | 0 | 0 | 57.9907 | 53.895 | 0
2031-07-27 | -358.588 | 1.5963 | 56.3931 | 53.895 | -105.0918
2031-07-28 01:00 | -647.604 | 2.4626 | 55.8359 | 53.895 | -189.794
2031-07-29 02:00 | -885.269 | 3.1045 | 55.4861 | 53.895 | -259.4467
2031-07-30 03:00 | -856.881 | 2.9656 | 55.235 | 53.895 | -251.127
2031-07-31 04:00 | -840.927 | 2.9385 | 55.0432 | 53.895 | -246.4514
2031-08-01 05:00 | -514.383 | 1.9563 | 55.0102 | 53.895 | -150.7508
2031-08-02 06:00 | 326.9 | 1 | 56.1028 | 53.895 | 95.8049
2031-08-03 07:00 | 2196.73 | 1 | 55.7917 | 53.895 | 643.798
2031-08-04 08:00 | 2843.3 | 1 | 76.9232 | 53.895 | 833.289
2031-08-05 09:00 | 4126.33 | 1.3664 | 70.6839 | 53.895 | 1209.3079
2031-08-06 10:00 | 5748.54 | 1.8953 | 71.001 | 53.895 | 1684.7308
2031-08-07 11:00 | 7113.18 | 2.3777 | 71.1742 | 53.895 | 2084.6673
2031-08-08 12:00 | 8548.06 | 2.7728 | 71.9907 | 53.895 | 2505.1891
2031-08-09 13:00 | 9475.47 | 3.0491 | 72.5126 | 53.895 | 2776.9861
2031-08-10 14:00 | 10048.4 | 3.2658 | 72.7553 | 53.895 | 2944.8953
2031-08-11 15:00 | 12172.1 | 3.9839 | 72.9715 | 53.895 | 3567.2904
2031-08-12 16:00 | 12958.1 | 4.237 | 73.4655 | 53.895 | 3797.6442
2031-08-13 17:00 | 13087.6 | 4.2317 | 74.0484 | 53.895 | 3835.5969
2031-08-14 18:00 | 11629.9 | 3.7338 | 74.4641 | 53.895 | 3408.3872
2031-08-15 19:00 | 9834 | 3.0702 | 74.9559 | 53.895 | 2882.0609
2031-08-16 20:00 | 6898.86 | 2.073 | 75.4767 | 53.895 | 2021.8563
2031-08-17 21:00 | 5711.01 | 1.7009 | 75.2735 | 53.895 | 1673.7318
2031-08-18 22:00 | 3216.36 | 1 | 75.5568 | 53.895 | 942.6221
2031-08-19 23:00 | 3179.71 | 1 | 58.249 | 53.895 | 931.881
2031-08-21 | 3108.43 | 1 | 57.9936 | 53.895 | 910.9909
2031-08-22 01:00 | 3000.21 | 1 | 57.8409 | 53.895 | 879.2748
2031-08-23 02:00 | 3096.77 | 1 | 57.7017 | 53.895 | 907.5737
2031-08-24 03:00 | 3102.87 | 1 | 57.601 | 53.895 | 909.3614
2031-08-25 04:00 | 3117.5 | 1 | 57.5414 | 53.895 | 913.6491
2031-08-26 05:00 | 3103.24 | 1 | 57.4818 | 53.895 | 909.4699
2031-08-27 06:00 | 3196.11 | 1 | 74.5933 | 53.895 | 936.6874
2031-08-28 07:00 | 4489.42 | 1.3617 | 73.3367 | 53.895 | 1315.7191
2031-08-29 08:00 | 5623.29 | 1.6511 | 73.9789 | 53.895 | 1648.0236
2031-08-30 09:00 | 7310.35 | 2.4165 | 72.3954 | 53.895 | 2142.4521
2031-08-31 10:00 | 9329.67 | 3.0578 | 72.8414 | 53.895 | 2734.2564
2031-09-01 11:00 | 10405.8 | 3.5257 | 72.8127 | 53.895 | 3049.6389
2031-09-02 12:00 | 11253.1 | 3.7112 | 73.5946 | 53.895 | 3297.9581
2031-09-03 13:00 | 11645.6 | 3.7943 | 74.126 | 53.895 | 3412.9885
2031-09-04 14:00 | 12492.9 | 4.019 | 74.6078 | 53.895 | 3661.3076
2031-09-05 15:00 | 14142.5 | 4.7108 | 74.4111 | 53.895 | 4144.7576
2031-09-06 16:00 | 14578.9 | 4.8408 | 74.8589 | 53.895 | 4272.6538
2031-09-07 17:00 | 14787 | 4.8217 | 75.4412 | 53.895 | 4333.6419
2031-09-08 18:00 | 13423.7 | 4.3091 | 75.9476 | 53.895 | 3934.0981
2031-09-09 19:00 | 11762.3 | 3.7032 | 76.3154 | 53.895 | 3447.1898
2031-09-10 20:00 | 8701.05 | 2.6943 | 76.5042 | 53.895 | 2550.026
2031-09-11 21:00 | 7092.29 | 2.2268 | 75.9416 | 53.895 | 2078.545
2031-09-12 22:00 | 4199.65 | 1.3735 | 74.9936 | 53.895 | 1230.7959
2031-09-13 23:00 | 3045.78 | 1 | 75.461 | 53.895 | 892.63
2031-09-15 | 3106.44 | 1 | 59.1331 | 53.895 | 910.4077
2031-09-16 01:00 | 3052.59 | 1 | 58.8704 | 53.895 | 894.6258
2031-09-17 02:00 | 2419.22 | 1 | 58.7832 | 53.895 | 709.0034
2031-09-18 03:00 | 438.703 | 1 | 58.8661 | 53.895 | 128.5712
2031-09-19 04:00 | 837.288 | 1 | 58.3824 | 53.895 | 245.3849
2031-09-20 05:00 | 2339.32 | 1 | 57.9003 | 53.895 | 685.587
2031-09-21 06:00 | 2958.71 | 1 | 57.807 | 53.895 | 867.1123
2031-09-22 07:00 | 3107.23 | 1 | 77.7283 | 53.895 | 910.6392
2031-09-23 08:00 | 3150.97 | 1 | 74.6562 | 53.895 | 923.4581
2031-09-24 09:00 | 4939.8 | 1.5295 | 73.4045 | 53.895 | 1447.7125
2031-09-25 10:00 | 6957.04 | 2.2401 | 73.041 | 53.895 | 2038.9072
2031-09-26 11:00 | 8932.87 | 2.8932 | 73.2978 | 53.895 | 2617.9658
2031-09-27 12:00 | 10557.6 | 3.4241 | 73.6817 | 53.895 | 3094.1271
2031-09-28 13:00 | 11564 | 3.7949 | 73.9472 | 53.895 | 3389.0739
2031-09-29 14:00 | 12658.1 | 4.147 | 74.383 | 53.895 | 3709.7229
2031-09-30 15:00 | 14465.5 | 4.856 | 74.4476 | 53.895 | 4239.4196
2031-10-01 16:00 | 15082.4 | 4.9599 | 75.2336 | 53.895 | 4420.2151
2031-10-02 17:00 | 15245.1 | 4.8906 | 75.9798 | 53.895 | 4467.8978
2031-10-03 18:00 | 13779 | 4.3517 | 76.5101 | 53.895 | 4038.2263
2031-10-04 19:00 | 11870.1 | 3.6975 | 76.8032 | 53.895 | 3478.7829
2031-10-05 20:00 | 9211.63 | 2.6934 | 77.7128 | 53.895 | 2699.6623
2031-10-06 21:00 | 7754.31 | 2.2903 | 77.2465 | 53.895 | 2272.5639
2031-10-07 22:00 | 5297.96 | 1.5345 | 77.2656 | 53.895 | 1552.6788
2031-10-08 23:00 | 4109.75 | 1.2667 | 75.8319 | 53.895 | 1204.4488
2031-10-10 | 3161.74 | 1 | 75.3912 | 53.895 | 926.6145
2031-10-11 01:00 | 3155.14 | 1 | 78.7284 | 53.895 | 924.6803
2031-10-12 02:00 | 3100.99 | 1 | 80.2888 | 53.895 | 908.8105
2031-10-13 03:00 | 3096.39 | 1 | 81.3909 | 53.895 | 907.4623
2031-10-14 04:00 | 3146.9 | 1 | 81.2319 | 53.895 | 922.2654
2031-10-15 05:00 | 3130.96 | 1 | 73.9925 | 53.895 | 917.5938
2031-10-16 06:00 | 4446.6 | 1.3702 | 74.2346 | 53.895 | 1303.1698
2031-10-17 07:00 | 5920.19 | 1.8425 | 74.1523 | 53.895 | 1735.0364
2031-10-18 08:00 | 6216.35 | 2.0248 | 73.6948 | 53.895 | 1821.8323
2031-10-19 09:00 | 8038.7 | 2.6998 | 73.388 | 53.895 | 2355.9104
2031-10-20 10:00 | 9131.96 | 3.141 | 73.3588 | 53.895 | 2676.3133
2031-10-21 11:00 | 11068.9 | 3.6775 | 74.1623 | 53.895 | 3243.9744
2031-10-22 12:00 | 11824.3 | 3.8968 | 74.6992 | 53.895 | 3465.3603
2031-10-23 13:00 | 12164.9 | 3.9892 | 75.1168 | 53.895 | 3565.1803
2031-10-24 14:00 | 12962.6 | 4.2881 | 75.2653 | 53.895 | 3798.9631
2031-10-25 15:00 | 14657.1 | 4.8429 | 75.5541 | 53.895 | 4295.572
2031-10-26 16:00 | 15077.5 | 4.8982 | 76.2016 | 53.895 | 4418.7791
2031-10-27 17:00 | 14536 | 4.7403 | 76.4539 | 53.895 | 4260.0811
2031-10-28 18:00 | 11408.7 | 3.5432 | 77.3325 | 53.895 | 3343.5599
2031-10-29 19:00 | 9744.19 | 3.0112 | 77.1838 | 53.895 | 2855.7402
2031-10-30 20:00 | 7319.19 | 2.2035 | 77.3444 | 53.895 | 2145.0428
2031-10-31 21:00 | 6137.29 | 1.819 | 77.1885 | 53.895 | 1798.6621
2031-11-01 22:00 | 3575.39 | 1.0899 | 76.3885 | 53.895 | 1047.8434
2031-11-02 23:00 | 3165.15 | 1 | 59.9443 | 53.895 | 927.6139
2031-11-04 | 3071.84 | 1 | 59.5984 | 53.895 | 900.2674
2031-11-05 01:00 | 3061.85 | 1 | 59.355 | 53.895 | 897.3397
2031-11-06 02:00 | 535.788 | 1 | 59.6065 | 53.895 | 157.024
2031-11-07 03:00 | 190.874 | 1 | 59.1826 | 53.895 | 55.9396
2031-11-08 04:00 | -82.7391 | 0.87348 | 58.4225 | 53.895 | -24.2484
2031-11-09 05:00 | -120.951 | 0.94847 | 57.992 | 53.895 | -35.4472
2031-11-10 06:00 | 1603.16 | 1 | 66.3 | 53.895 | 469.8398
2031-11-11 07:00 | 3568.4 | 1.4046 | 70.2604 | 53.895 | 1045.7948
2031-11-12 08:00 | 3864.72 | 1.3457 | 72.0338 | 53.895 | 1132.6376
2031-11-13 09:00 | 5324.57 | 1.8299 | 72.3172 | 53.895 | 1560.4774
2031-11-14 10:00 | 6607.62 | 2.3643 | 72.0112 | 53.895 | 1936.5023
2031-11-15 11:00 | 7459.65 | 2.5507 | 72.9153 | 53.895 | 2186.2076
2031-11-16 12:00 | 7925.72 | 2.6825 | 73.2996 | 53.895 | 2322.7992
2031-11-17 13:00 | 8286.01 | 2.7949 | 73.519 | 53.895 | 2428.3898
2031-11-18 14:00 | 9254.44 | 2.9755 | 74.3759 | 53.895 | 2712.2086
2031-11-19 15:00 | 9667.43 | 3.1232 | 74.5249 | 53.895 | 2833.2441
2031-11-20 16:00 | 12071.4 | 4.0053 | 74.3174 | 53.895 | 3537.7781
2031-11-21 17:00 | 11227.5 | 3.5555 | 75.4095 | 53.895 | 3290.4554
2031-11-22 18:00 | 9720.39 | 3.099 | 75.4828 | 53.895 | 2848.7651
2031-11-23 19:00 | 8033.21 | 2.5446 | 75.5242 | 53.895 | 2354.3015
2031-11-24 20:00 | 6830.75 | 2.1373 | 75.5483 | 53.895 | 2001.8952
2031-11-25 21:00 | 5856.77 | 1.78 | 75.8043 | 53.895 | 1716.4499
2031-11-26 22:00 | 4682.08 | 1.4944 | 74.8383 | 53.895 | 1372.1822
2031-11-27 23:00 | 3042.93 | 1 | 59.3775 | 53.895 | 891.7948
2031-11-29 | 0 | 0 | 59.5484 | 53.895 | 0
2031-11-30 01:00 | -202.744 | 1.1156 | 58.1105 | 53.895 | -59.4184
2031-12-01 02:00 | -399.336 | 1.7337 | 57.5103 | 53.895 | -117.0338
2031-12-02 03:00 | -700.596 | 2.569 | 57.0386 | 53.895 | -205.3244
2031-12-03 04:00 | -844.222 | 2.9262 | 56.6712 | 53.895 | -247.417
2031-12-04 05:00 | -961.605 | 3.2504 | 56.3897 | 53.895 | -281.8186
2031-12-05 06:00 | 263.267 | 1 | 57.5521 | 53.895 | 77.1559
2031-12-06 07:00 | 2003.52 | 1 | 57.24 | 53.895 | 587.1738
2031-12-07 08:00 | 2750.27 | 1 | 57.2679 | 53.895 | 806.0246
2031-12-08 09:00 | 3006.93 | 1 | 78.273 | 53.895 | 881.2442
2031-12-09 10:00 | 3794.68 | 1.1972 | 72.7434 | 53.895 | 1112.1109
2031-12-10 11:00 | 4793.73 | 1.5542 | 72.4825 | 53.895 | 1404.9036
2031-12-11 12:00 | 5651.9 | 1.8595 | 72.4736 | 53.895 | 1656.4084
2031-12-12 13:00 | 5865 | 1.9059 | 72.8469 | 53.895 | 1718.8618
2031-12-13 14:00 | 6059.29 | 2.0464 | 72.4262 | 53.895 | 1775.8026
2031-12-14 15:00 | 6472.54 | 2.1826 | 72.5465 | 53.895 | 1896.9142
2031-12-15 16:00 | 8844.43 | 3.006 | 72.5318 | 53.895 | 2592.0466
2031-12-16 17:00 | 7830.71 | 2.5997 | 73.2204 | 53.895 | 2294.9546
2031-12-17 18:00 | 6430.99 | 2.0763 | 73.71 | 53.895 | 1884.7371
2031-12-18 19:00 | 4345.24 | 1.4099 | 73.53 | 53.895 | 1273.4641
2031-12-19 20:00 | 3024.14 | 1 | 77.0584 | 53.895 | 886.2879
2031-12-20 21:00 | 2999.33 | 1 | 58.0485 | 53.895 | 879.0169
2031-12-21 22:00 | 0 | 0 | 58.3878 | 53.895 | 0
2031-12-22 23:00 | -1363.79 | 4.5915 | 56.5039 | 53.895 | -399.6874
2031-12-24 | -2062.96 | 6.4225 | 55.924 | 53.895 | -604.5939
2031-12-25 01:00 | -2562.64 | 6.8587 | 55.3308 | 53.895 | -751.0356
2031-12-26 02:00 | -2919.08 | 6.8587 | 54.7904 | 53.895 | -855.4979
2031-12-27 03:00 | -2934.57 | 6.8587 | 54.4876 | 53.895 | -860.0376
2031-12-28 04:00 | -2911.26 | 6.8587 | 54.2824 | 53.895 | -853.2061
2031-12-29 05:00 | -2423.28 | 6.8587 | 54.4467 | 53.895 | -710.1933
2031-12-30 06:00 | -1757 | 5.3765 | 54.4767 | 53.895 | -514.9259
2031-12-31 07:00 | -998.384 | 3.191 | 54.5195 | 53.895 | -292.5975
2032-01-01 08:00 | -642.866 | 2.3264 | 54.7315 | 53.895 | -188.4054
2032-01-02 09:00 | 1994.21 | 1 | 55.705 | 53.895 | 584.4453
2032-01-03 10:00 | 3027.03 | 1 | 74.2333 | 53.895 | 887.1349
2032-01-04 11:00 | 4320.12 | 1.4037 | 71.066 | 53.895 | 1266.1022
2032-01-05 12:00 | 5820.69 | 1.9416 | 71.0028 | 53.895 | 1705.8758
2032-01-06 13:00 | 6670.58 | 2.203 | 71.5223 | 53.895 | 1954.954
2032-01-07 14:00 | 7540.77 | 2.5354 | 71.6255 | 53.895 | 2209.9815
2032-01-08 15:00 | 9728.44 | 3.1956 | 72.2616 | 53.895 | 2851.1243
2032-01-09 16:00 | 10300.1 | 3.404 | 72.6442 | 53.895 | 3018.6613
2032-01-10 17:00 | 10719.4 | 3.4601 | 73.3591 | 53.895 | 3141.546
2032-01-11 18:00 | 9208.71 | 2.9934 | 73.5718 | 53.895 | 2698.8065
2032-01-12 19:00 | 7699.92 | 2.4314 | 74.0776 | 53.895 | 2256.6238
2032-01-13 20:00 | 4712.43 | 1.4467 | 74.459 | 53.895 | 1381.0769
2032-01-14 21:00 | 3165.47 | 1 | 74.1666 | 53.895 | 927.7077
2032-01-15 22:00 | 2842.46 | 1 | 58.002 | 53.895 | 833.0428
2032-01-16 23:00 | -352.991 | 1.697 | 57.2903 | 53.895 | -103.4515
2032-01-18 | -833.546 | 2.9851 | 56.4227 | 53.895 | -244.2882
2032-01-19 01:00 | -1008.57 | 3.4037 | 55.9509 | 53.895 | -295.5827
2032-01-20 02:00 | -1187.77 | 3.9125 | 55.6841 | 53.895 | -348.101
2032-01-21 03:00 | -1246.44 | 4.0512 | 55.4441 | 53.895 | -365.2955
2032-01-22 04:00 | -1251.03 | 4.0626 | 55.2303 | 53.895 | -366.6407
2032-01-23 05:00 | -752.112 | 2.5554 | 55.1474 | 53.895 | -220.4223
2032-01-24 06:00 | -273.991 | 1.265 | 55.4467 | 53.895 | -80.2988
2032-01-25 07:00 | 1975.01 | 1 | 56.1026 | 53.895 | 578.8183
2032-01-26 08:00 | 2837.26 | 1 | 56.1992 | 53.895 | 831.5188
2032-01-27 09:00 | 3224.07 | 1.0648 | 71.1264 | 53.895 | 944.8816
2032-01-28 10:00 | 5243.22 | 1.7491 | 71.0813 | 53.895 | 1536.6361
2032-01-29 11:00 | 6852.61 | 2.2619 | 71.5854 | 53.895 | 2008.3017
2032-01-30 12:00 | 7956.96 | 2.5937 | 72.1864 | 53.895 | 2331.9548
2032-01-31 13:00 | 8761.46 | 2.8396 | 72.6327 | 53.895 | 2567.7305
2032-02-01 14:00 | 9496.57 | 3.0793 | 72.9596 | 53.895 | 2783.1699
2032-02-02 15:00 | 11840.6 | 3.8539 | 73.2245 | 53.895 | 3470.1373
2032-02-03 16:00 | 12738.7 | 4.0633 | 74.0171 | 53.895 | 3733.3444
2032-02-04 17:00 | 12614.4 | 4.0231 | 74.4521 | 53.895 | 3696.9157
2032-02-05 18:00 | 11391.6 | 3.5751 | 74.9826 | 53.895 | 3338.5484
2032-02-06 19:00 | 9629.45 | 3.0289 | 75.0467 | 53.895 | 2822.1132
2032-02-07 20:00 | 6977.52 | 2.0863 | 75.7701 | 53.895 | 2044.9093
2032-02-08 21:00 | 5611.86 | 1.6754 | 75.4964 | 53.895 | 1644.6738
2032-02-09 22:00 | 3214.01 | 1 | 75.7441 | 53.895 | 941.9333
2032-02-10 23:00 | 3093.64 | 1 | 58.549 | 53.895 | 906.6564
2032-02-12 | 3070.62 | 1 | 58.2898 | 53.895 | 899.9099
2032-02-13 01:00 | 3106.47 | 1 | 58.1229 | 53.895 | 910.4165
2032-02-14 02:00 | 3129.97 | 1 | 58.0202 | 53.895 | 917.3037
2032-02-15 03:00 | 3122.73 | 1 | 57.9296 | 53.895 | 915.1818
2032-02-16 04:00 | 3209.93 | 1 | 57.8601 | 53.895 | 940.7376
2032-02-17 05:00 | 3199.06 | 1 | 57.8179 | 53.895 | 937.5519
2032-02-18 06:00 | 3268.68 | 1 | 77.8087 | 53.895 | 957.9555
2032-02-19 07:00 | 4160.44 | 1.2001 | 74.4973 | 53.895 | 1219.3046
2032-02-20 08:00 | 4491.94 | 1.3686 | 73.7313 | 53.895 | 1316.4577
2032-02-21 09:00 | 6102.88 | 2.0367 | 72.4763 | 53.895 | 1788.5776
2032-02-22 10:00 | 7958.08 | 2.7153 | 72.413 | 53.895 | 2332.283
2032-02-23 11:00 | 9529.91 | 3.2343 | 72.8529 | 53.895 | 2792.9409
2032-02-24 12:00 | 10682.3 | 3.5197 | 73.6709 | 53.895 | 3130.6731
2032-02-25 13:00 | 11560.6 | 3.7572 | 74.2485 | 53.895 | 3388.0774
2032-02-26 14:00 | 12114.8 | 4.02 | 74.3204 | 53.895 | 3550.4974
2032-02-27 15:00 | 14035.8 | 4.6764 | 74.5612 | 53.895 | 4113.4869
2032-02-28 16:00 | 14640.7 | 4.8315 | 75.1315 | 53.895 | 4290.7656
2032-02-29 17:00 | 14569.5 | 4.6589 | 75.9501 | 53.895 | 4269.899
2032-03-01 18:00 | 12897.4 | 4.1159 | 76.239 | 53.895 | 3779.8548
2032-03-02 19:00 | 10286.7 | 3.1606 | 76.8364 | 53.895 | 3014.7342
2032-03-03 20:00 | 7326.9 | 2.1945 | 77.0361 | 53.895 | 2147.3024
2032-03-04 21:00 | 6221.77 | 1.855 | 76.6837 | 53.895 | 1823.4208
2032-03-05 22:00 | 3739.43 | 1.1598 | 75.7407 | 53.895 | 1095.9188
2032-03-06 23:00 | 3157.54 | 1 | 77.3635 | 53.895 | 925.3836
2032-03-08 | 3302.85 | 1 | 59.1873 | 53.895 | 967.9698
2032-03-09 01:00 | 3036.66 | 1 | 59.0242 | 53.895 | 889.9572
2032-03-10 02:00 | 3218.33 | 1 | 58.8101 | 53.895 | 943.1994
2032-03-11 03:00 | 3204.48 | 1 | 58.6653 | 53.895 | 939.1404
2032-03-12 04:00 | 3166.66 | 1 | 58.5668 | 53.895 | 928.0564
2032-03-13 05:00 | 2800.3 | 1 | 74.1969 | 53.895 | 820.6869
2032-03-14 06:00 | 4038.82 | 1.213 | 74.4514 | 53.895 | 1183.6613
2032-03-15 07:00 | 4357.97 | 1.2805 | 74.8511 | 53.895 | 1277.1949
2032-03-16 08:00 | 3667.84 | 1.1656 | 73.7166 | 53.895 | 1074.9378
2032-03-17 09:00 | 5796.72 | 1.8822 | 73.3224 | 53.895 | 1698.8509
2032-03-18 10:00 | 7794.36 | 2.6258 | 73.018 | 53.895 | 2284.3014
2032-03-19 11:00 | 8330.52 | 2.8409 | 73.2306 | 53.895 | 2441.4344
2032-03-20 12:00 | 9497.15 | 3.1518 | 73.8471 | 53.895 | 2783.3399
2032-03-21 13:00 | 10447.1 | 3.361 | 74.5728 | 53.895 | 3061.7428
2032-03-22 14:00 | 11676.3 | 3.8322 | 74.6125 | 53.895 | 3421.9857
2032-03-23 15:00 | 13592 | 4.4951 | 74.8357 | 53.895 | 3983.422
2032-03-24 16:00 | 13476.9 | 4.483 | 75.1865 | 53.895 | 3949.6895
2032-03-25 17:00 | 13857.5 | 4.4269 | 76.0413 | 53.895 | 4061.2324
2032-03-26 18:00 | 12389.3 | 3.9502 | 76.3209 | 53.895 | 3630.9454
2032-03-27 19:00 | 10646.5 | 3.3052 | 76.7723 | 53.895 | 3120.1811
2032-03-28 20:00 | 7840.38 | 2.4288 | 76.7177 | 53.895 | 2297.7886
2032-03-29 21:00 | 6716.26 | 2.0456 | 76.6207 | 53.895 | 1968.3415
2032-03-30 22:00 | 4245.86 | 1.2535 | 76.8235 | 53.895 | 1244.3387
2032-03-31 23:00 | 3219.3 | 1 | 76.7222 | 53.895 | 943.4837
2032-04-02 | 3075.7 | 1 | 59.576 | 53.895 | 901.3987
2032-04-03 01:00 | 3040.17 | 1 | 59.3219 | 53.895 | 890.9859
2032-04-04 02:00 | 3086.32 | 1 | 59.1277 | 53.895 | 904.5111
2032-04-05 03:00 | 3093.42 | 1 | 58.9572 | 53.895 | 906.5919
2032-04-06 04:00 | 3124.49 | 1 | 58.8343 | 53.895 | 915.6976
2032-04-07 05:00 | 3142.19 | 1 | 58.7332 | 53.895 | 920.885
2032-04-08 06:00 | 3211.51 | 1 | 76.9112 | 53.895 | 941.2007
2032-04-09 07:00 | 4240.98 | 1.3507 | 73.801 | 53.895 | 1242.9085
2032-04-10 08:00 | 4870.44 | 1.5699 | 73.716 | 53.895 | 1427.3851
2032-04-11 09:00 | 6777.67 | 2.3469 | 72.8052 | 53.895 | 1986.339
2032-04-12 10:00 | 8561.47 | 2.8459 | 73.6422 | 53.895 | 2509.1192
2032-04-13 11:00 | 10393.9 | 3.403 | 74.2305 | 53.895 | 3046.1514
2032-04-14 12:00 | 10701.8 | 3.451 | 74.8919 | 53.895 | 3136.388
2032-04-15 13:00 | 10892.1 | 3.4445 | 75.4789 | 53.895 | 3192.1594
2032-04-16 14:00 | 10734.8 | 3.4562 | 75.4446 | 53.895 | 3146.0593
2032-04-17 15:00 | 12678.2 | 4.1248 | 75.4177 | 53.895 | 3715.6136
2032-04-18 16:00 | 13211.6 | 4.3361 | 75.6251 | 53.895 | 3871.9377
2032-04-19 17:00 | 13481.8 | 4.3247 | 76.2194 | 53.895 | 3951.1256
2032-04-20 18:00 | 11605.2 | 3.819 | 76.0764 | 53.895 | 3401.1484
2032-04-21 19:00 | 10305.6 | 3.1944 | 76.919 | 53.895 | 3020.2732
2032-04-22 20:00 | 7445.89 | 2.2931 | 76.9386 | 53.895 | 2182.1749
2032-04-23 21:00 | 6287.98 | 1.8787 | 77.0465 | 53.895 | 1842.825
2032-04-24 22:00 | 3732.77 | 1.1529 | 76.2169 | 53.895 | 1093.9669
2032-04-25 23:00 | 3060.9 | 1 | 60.0313 | 53.895 | 897.0612
2032-04-27 | 3011.4 | 1 | 59.6605 | 53.895 | 882.5542
2032-04-28 01:00 | 3173.41 | 1 | 59.3818 | 53.895 | 930.0347
2032-04-29 02:00 | 2576.88 | 1 | 59.3385 | 53.895 | 755.209
2032-04-30 03:00 | 1106.81 | 1 | 59.3688 | 53.895 | 324.374
2032-05-01 04:00 | 247.035 | 1 | 59.1835 | 53.895 | 72.3988
2032-05-02 05:00 | 26.0793 | 1 | 58.8866 | 53.895 | 7.6431
2032-05-03 06:00 | 1924.34 | 1 | 58.3029 | 53.895 | 563.9684
2032-05-04 07:00 | 2702.3 | 1 | 74.358 | 53.895 | 791.966
2032-05-05 08:00 | 3005.92 | 1 | 58.1889 | 53.895 | 880.9482
2032-05-06 09:00 | 3118.64 | 1 | 58.2007 | 53.895 | 913.9832
2032-05-07 10:00 | 3086.51 | 1 | 76.8273 | 53.895 | 904.5668
2032-05-08 11:00 | 3850.95 | 1.1899 | 73.8994 | 53.895 | 1128.602
2032-05-09 12:00 | 4613.7 | 1.4615 | 73.5788 | 53.895 | 1352.142
2032-05-10 13:00 | 5178.16 | 1.6013 | 74.0191 | 53.895 | 1517.5689
2032-05-11 14:00 | 6148.92 | 2.0002 | 73.3519 | 53.895 | 1802.0706
2032-05-12 15:00 | 6607.23 | 2.1821 | 73.2803 | 53.895 | 1936.388
2032-05-13 16:00 | 8826.86 | 3.0155 | 72.9408 | 53.895 | 2586.8973
2032-05-14 17:00 | 8090.77 | 2.5306 | 74.5541 | 53.895 | 2371.1706
2032-05-15 18:00 | 7057.13 | 2.2799 | 74.1869 | 53.895 | 2068.2406
2032-05-16 19:00 | 6141.4 | 1.8991 | 74.7834 | 53.895 | 1799.8667
2032-05-17 20:00 | 4767.02 | 1.4653 | 74.7899 | 53.895 | 1397.0757
2032-05-18 21:00 | 3640.87 | 1.1665 | 73.9981 | 53.895 | 1067.0337
2032-05-19 22:00 | 2981.63 | 1 | 75.109 | 53.895 | 873.8295
2032-05-20 23:00 | 0 | 0 | 58.9525 | 53.895 | 0
2032-05-22 | -461.115 | 1.5891 | 57.0973 | 53.895 | -135.1395
2032-05-23 01:00 | -655.72 | 2.456 | 56.8454 | 53.895 | -192.1726
2032-05-24 02:00 | -944.483 | 3.2409 | 56.4859 | 53.895 | -276.8006
2032-05-25 03:00 | -1179.7 | 3.8783 | 56.1961 | 53.895 | -345.7359
2032-05-26 04:00 | -1287.45 | 4.1521 | 55.9251 | 53.895 | -377.3143
2032-05-27 05:00 | -1520.82 | 4.8385 | 55.7401 | 53.895 | -445.7083
2032-05-28 06:00 | -663.324 | 2.1951 | 55.6205 | 53.895 | -194.4011
2032-05-29 07:00 | 1923.06 | 1 | 56.662 | 53.895 | 563.5933
2032-05-30 08:00 | 3060.51 | 1 | 56.7196 | 53.895 | 896.9469
2032-05-31 09:00 | 3017.84 | 1 | 56.9699 | 53.895 | 884.4416
2032-06-01 10:00 | 3778.68 | 1.2325 | 71.9791 | 53.895 | 1107.4218
2032-06-02 11:00 | 5504.38 | 1.785 | 72.1968 | 53.895 | 1613.1745
2032-06-03 12:00 | 5810.64 | 1.935 | 72.1569 | 53.895 | 1702.9305
2032-06-04 13:00 | 5553.24 | 1.7626 | 73.0582 | 53.895 | 1627.494
2032-06-05 14:00 | 6292.75 | 2.0906 | 72.4749 | 53.895 | 1844.223
2032-06-06 15:00 | 6913.52 | 2.2794 | 72.7494 | 53.895 | 2026.1527
2032-06-07 16:00 | 9589.93 | 3.2564 | 72.511 | 53.895 | 2810.531
2032-06-08 17:00 | 8819.93 | 2.8844 | 73.4749 | 53.895 | 2584.8663
2032-06-09 18:00 | 7484.73 | 2.3917 | 73.9913 | 53.895 | 2193.5578
2032-06-10 19:00 | 5726.28 | 1.7718 | 74.4364 | 53.895 | 1678.207
2032-06-11 20:00 | 4036.36 | 1.2796 | 73.9062 | 53.895 | 1182.9403
2032-06-12 21:00 | 3084.64 | 1 | 76.5364 | 53.895 | 904.0187
2032-06-13 22:00 | 3002.89 | 1 | 58.0975 | 53.895 | 880.0602
2032-06-14 23:00 | 0 | 0 | 58.455 | 53.895 | 0
2032-06-16 | -720.943 | 2.6521 | 56.7022 | 53.895 | -211.2875
2032-06-17 01:00 | -1036.29 | 3.5065 | 56.2237 | 53.895 | -303.7066
2032-06-18 02:00 | -1239.24 | 4.0443 | 55.9277 | 53.895 | -363.1854
2032-06-19 03:00 | -1418.56 | 4.544 | 55.6879 | 53.895 | -415.7389
2032-06-20 04:00 | -1503.61 | 4.7666 | 55.4344 | 53.895 | -440.6646
2032-06-21 05:00 | -1258.85 | 4.0107 | 55.2799 | 53.895 | -368.9325
2032-06-22 06:00 | -650.422 | 2.2499 | 55.29 | 53.895 | -190.6199
2032-06-23 07:00 | 0 | 0 | 56.6163 | 53.895 | 0
2032-06-24 08:00 | 713.972 | 1 | 56.5196 | 53.895 | 209.2445
2032-06-25 09:00 | 2638.03 | 1 | 56.2602 | 53.895 | 773.1303
2032-06-26 10:00 | 3052.96 | 1 | 73.3602 | 53.895 | 894.7343
2032-06-27 11:00 | 4174.81 | 1.362 | 71.4948 | 53.895 | 1223.516
2032-06-28 12:00 | 5374.31 | 1.7379 | 71.8596 | 53.895 | 1575.0548
2032-06-29 13:00 | 6053.13 | 1.9785 | 72.0064 | 53.895 | 1773.9973
2032-06-30 14:00 | 6810.04 | 2.2355 | 72.213 | 53.895 | 1995.8257
2032-07-01 15:00 | 8853.57 | 2.9282 | 72.3446 | 53.895 | 2594.7252
2032-07-02 16:00 | 9427.77 | 3.1098 | 72.7908 | 53.895 | 2763.0066
2032-07-03 17:00 | 9627.98 | 3.182 | 73.0953 | 53.895 | 2821.6824
2032-07-04 18:00 | 8488.59 | 2.7434 | 73.667 | 53.895 | 2487.7602
2032-07-05 19:00 | 6680.82 | 2.1134 | 74.0592 | 53.895 | 1957.9551
2032-07-06 20:00 | 3716.31 | 1.2162 | 73.47 | 53.895 | 1089.1429
2032-07-07 21:00 | 3061.47 | 1 | 80.1079 | 53.895 | 897.2283
2032-07-08 22:00 | 0 | 0 | 58.4991 | 53.895 | 0
2032-07-09 23:00 | -389.574 | 1.5766 | 56.8169 | 53.895 | -114.1729
2032-07-11 | -749.74 | 2.7508 | 56.3251 | 53.895 | -219.7271
2032-07-12 01:00 | -1115.35 | 3.7466 | 55.939 | 53.895 | -326.8768
2032-07-13 02:00 | -1269.43 | 4.1254 | 55.6646 | 53.895 | -372.0332
2032-07-14 03:00 | -1420.94 | 4.5591 | 55.4237 | 53.895 | -416.4364
2032-07-15 04:00 | -1516.34 | 4.8159 | 55.2451 | 53.895 | -444.3954
2032-07-16 05:00 | -1091.38 | 3.5067 | 55.1021 | 53.895 | -319.8519
2032-07-17 06:00 | -598.254 | 2.1474 | 55.1709 | 53.895 | -175.3309
2032-07-18 07:00 | -115.101 | 0.82855 | 55.7993 | 53.895 | -33.7328
2032-07-19 08:00 | 574.778 | 1 | 56.3744 | 53.895 | 168.4508
2032-07-20 09:00 | 3012.89 | 1 | 56.0158 | 53.895 | 882.9909
2032-07-21 10:00 | 3615.82 | 1.1691 | 71.3949 | 53.895 | 1059.6922
2032-07-22 11:00 | 5388.74 | 1.7575 | 71.4673 | 53.895 | 1579.2838
2032-07-23 12:00 | 6244.82 | 2.077 | 71.5317 | 53.895 | 1830.1761
2032-07-24 13:00 | 7275.67 | 2.3576 | 72.232 | 53.895 | 2132.2884
2032-07-25 14:00 | 8104.49 | 2.6078 | 72.6705 | 53.895 | 2375.1916
2032-07-26 15:00 | 10033.7 | 3.2578 | 72.8309 | 53.895 | 2940.5872
2032-07-27 16:00 | 10165.3 | 3.3228 | 73.1739 | 53.895 | 2979.1553
2032-07-28 17:00 | 10568.2 | 3.4022 | 73.6824 | 53.895 | 3097.2337
2032-07-29 18:00 | 9325.8 | 2.9091 | 74.4157 | 53.895 | 2733.1222
2032-07-30 19:00 | 7818.59 | 2.4321 | 74.5378 | 53.895 | 2291.4025
2032-07-31 20:00 | 5638.4 | 1.6721 | 75.2236 | 53.895 | 1652.4519
2032-08-01 21:00 | 4708.4 | 1.4496 | 74.3769 | 53.895 | 1379.8958
2032-08-02 22:00 | 3041.34 | 1 | 78.7294 | 53.895 | 891.3288
2032-08-03 23:00 | 3077.11 | 1 | 58.1174 | 53.895 | 901.8119
2032-08-05 | 2946.9 | 1 | 57.9718 | 53.895 | 863.6511
2032-08-06 01:00 | 0 | 0 | 58.3609 | 53.895 | 0
2032-08-07 02:00 | 249.612 | 1 | 57.8774 | 53.895 | 73.1541
2032-08-08 03:00 | -63.9024 | 0.84177 | 57.3128 | 53.895 | -18.7279
2032-08-09 04:00 | -268.039 | 1.3931 | 56.5904 | 53.895 | -78.5545
2032-08-10 05:00 | -331.574 | 1.5357 | 56.2796 | 53.895 | -97.1747
2032-08-11 06:00 | 1843.52 | 1 | 56.7978 | 53.895 | 540.2824
2032-08-12 07:00 | 2978.86 | 1 | 56.7725 | 53.895 | 873.0177
2032-08-13 08:00 | 3015.29 | 1 | 56.978 | 53.895 | 883.6943
2032-08-14 09:00 | 3153.26 | 1 | 57.0416 | 53.895 | 924.1293
2032-08-15 10:00 | 3222.58 | 1 | 57.1121 | 53.895 | 944.445
2032-08-16 11:00 | 3289.5 | 1 | 78.6178 | 53.895 | 964.0573
2032-08-17 12:00 | 3251.6 | 1 | 73.8941 | 53.895 | 952.9499
2032-08-18 13:00 | 3621.09 | 1.0991 | 73.169 | 53.895 | 1061.2367
2032-08-19 14:00 | 5965.52 | 1.8648 | 72.753 | 53.895 | 1748.3213
2032-08-20 15:00 | 6618.22 | 2.155 | 72.4458 | 53.895 | 1939.6088
2032-08-21 16:00 | 10752.1 | 3.8849 | 71.2474 | 53.895 | 3151.1295
2032-08-22 17:00 | 9983.68 | 3.3424 | 72.9205 | 53.895 | 2925.9278
2032-08-23 18:00 | 8952.56 | 2.895 | 73.7172 | 53.895 | 2623.7363
2032-08-24 19:00 | 7857.92 | 2.4823 | 74.1431 | 53.895 | 2302.929
2032-08-25 20:00 | 6693.55 | 2.0722 | 74.4457 | 53.895 | 1961.6859
2032-08-26 21:00 | 5909.26 | 1.8033 | 74.6014 | 53.895 | 1731.8332
2032-08-27 22:00 | 5523.84 | 1.7122 | 74.2308 | 53.895 | 1618.8777
2032-08-28 23:00 | 2978.7 | 1 | 76.4755 | 53.895 | 872.9708
2032-08-30 | 3041.88 | 1 | 58.1956 | 53.895 | 891.487
2032-08-31 01:00 | 3068.58 | 1 | 58.0525 | 53.895 | 899.312
2032-09-01 02:00 | 3145.04 | 1 | 57.9729 | 53.895 | 921.7202
2032-09-02 03:00 | 3139.01 | 1 | 57.9256 | 53.895 | 919.953
2032-09-03 04:00 | 3188.83 | 1 | 57.8296 | 53.895 | 934.5538
2032-09-04 05:00 | 3231.34 | 1 | 57.7992 | 53.895 | 947.0123
2032-09-05 06:00 | 3268.48 | 1 | 80.219 | 53.895 | 957.8969
2032-09-06 07:00 | 3216.24 | 1 | 75.0726 | 53.895 | 942.5869
2032-09-07 08:00 | 3247.1 | 1 | 57.7104 | 53.895 | 951.6311
2032-09-08 09:00 | 3242.59 | 1 | 80.9909 | 53.895 | 950.3093
2032-09-09 10:00 | 5042.89 | 1.5258 | 73.6711 | 53.895 | 1477.9252
2032-09-10 11:00 | 6897.76 | 2.4601 | 71.5475 | 53.895 | 2021.5339
2032-09-11 12:00 | 8156.64 | 2.8386 | 72.2194 | 53.895 | 2390.4752
2032-09-12 13:00 | 8970.05 | 3.0779 | 72.7525 | 53.895 | 2628.8622
2032-09-13 14:00 | 9717.2 | 3.2518 | 73.4018 | 53.895 | 2847.8302
2032-09-14 15:00 | 11725.5 | 3.9493 | 73.6105 | 53.895 | 3436.4048
2032-09-15 16:00 | 12051.2 | 4.0221 | 74.165 | 53.895 | 3531.8581
2032-09-16 17:00 | 12330.3 | 3.9782 | 74.9536 | 53.895 | 3613.6542
2032-09-17 18:00 | 10935.4 | 3.4819 | 75.3977 | 53.895 | 3204.8494
2032-09-18 19:00 | 9632.79 | 2.9856 | 75.8517 | 53.895 | 2823.0921
2032-09-19 20:00 | 7320.6 | 2.1599 | 76.5725 | 53.895 | 2145.4561
2032-09-20 21:00 | 6239.27 | 1.9231 | 75.6384 | 53.895 | 1828.5495
2032-09-21 22:00 | 3835.46 | 1.2132 | 75.0121 | 53.895 | 1124.0624
2032-09-22 23:00 | 3176.56 | 1 | 75.6971 | 53.895 | 930.9578
2032-09-24 | 3147 | 1 | 79.7105 | 53.895 | 922.2947
2032-09-25 01:00 | 3124.84 | 1 | 58.7134 | 53.895 | 915.8002
2032-09-26 02:00 | 3136.52 | 1 | 58.5761 | 53.895 | 919.2233
2032-09-27 03:00 | 3151.46 | 1 | 58.4364 | 53.895 | 923.6018
2032-09-28 04:00 | 3161.72 | 1 | 58.3463 | 53.895 | 926.6087
2032-09-29 05:00 | 3186.92 | 1 | 77.6105 | 53.895 | 933.9941
2032-09-30 06:00 | 3329.33 | 1.0435 | 73.6668 | 53.895 | 975.7303
2032-10-01 07:00 | 3431.33 | 1.0867 | 73.4789 | 53.895 | 1005.6236
2032-10-02 08:00 | 3092.92 | 1 | 78.1708 | 53.895 | 906.4454
2032-10-03 09:00 | 3119.33 | 1 | 74.4372 | 53.895 | 914.1854
2032-10-04 10:00 | 4967.38 | 1.5988 | 73.1259 | 53.895 | 1455.7954
2032-10-05 11:00 | 6342.49 | 2.1029 | 72.8993 | 53.895 | 1858.8003
2032-10-06 12:00 | 7285.34 | 2.4463 | 72.983 | 53.895 | 2135.1224
2032-10-07 13:00 | 8554.21 | 2.7953 | 73.607 | 53.895 | 2506.9915
2032-10-08 14:00 | 8822.36 | 3.0774 | 73.0045 | 53.895 | 2585.5785
2032-10-09 15:00 | 11032 | 3.6554 | 73.9318 | 53.895 | 3233.16
2032-10-10 16:00 | 11807.8 | 3.9623 | 74.1449 | 53.895 | 3460.5246
2032-10-11 17:00 | 11769.9 | 3.9427 | 74.5098 | 53.895 | 3449.4172
2032-10-12 18:00 | 10758.1 | 3.4697 | 75.2722 | 53.895 | 3152.8879
2032-10-13 19:00 | 9087.7 | 2.8777 | 75.603 | 53.895 | 2663.342
2032-10-14 20:00 | 6517.61 | 2.0086 | 75.941 | 53.895 | 1910.1229
2032-10-15 21:00 | 5045.23 | 1.5628 | 75.5538 | 53.895 | 1478.611
2032-10-16 22:00 | 3176.82 | 1 | 80.6232 | 53.895 | 931.034
2032-10-17 23:00 | 2921.88 | 1 | 59.2132 | 53.895 | 856.3185
2032-10-19 | 0 | 0 | 59.4418 | 53.895 | 0
2032-10-20 01:00 | -486.659 | 2.0074 | 57.7513 | 53.895 | -142.6257
2032-10-21 02:00 | -789.021 | 2.7996 | 57.163 | 53.895 | -231.2392
2032-10-22 03:00 | -964.966 | 3.2564 | 56.7789 | 53.895 | -282.8036
2032-10-23 04:00 | -1225.26 | 3.9992 | 56.4554 | 53.895 | -359.0883
2032-10-24 05:00 | -1164.31 | 3.7592 | 56.1527 | 53.895 | -341.2256
2032-10-25 06:00 | 0 | 1 | 57.4146 | 53.895 | 0
2032-10-26 07:00 | 2268.01 | 1 | 57.009 | 53.895 | 664.6881
2032-10-27 08:00 | 2913.63 | 1 | 57.1358 | 53.895 | 853.9007
2032-10-28 09:00 | 3062.67 | 1.0034 | 72.1455 | 53.895 | 897.58
2032-10-29 10:00 | 4716.93 | 1.5292 | 72.3482 | 53.895 | 1382.3957
2032-10-30 11:00 | 5654.79 | 1.9305 | 71.8793 | 53.895 | 1657.2554
2032-10-31 12:00 | 6529.97 | 2.1567 | 72.6243 | 53.895 | 1913.7453
2032-11-01 13:00 | 7107.13 | 2.3065 | 73.1129 | 53.895 | 2082.8942
2032-11-02 14:00 | 7643.84 | 2.5435 | 72.9772 | 53.895 | 2240.1884
2032-11-03 15:00 | 8292.53 | 2.7458 | 73.2554 | 53.895 | 2430.3006
2032-11-04 16:00 | 11070.3 | 3.7003 | 73.3201 | 53.895 | 3244.3847
2032-11-05 17:00 | 10351.6 | 3.3669 | 74.1919 | 53.895 | 3033.7545
2032-11-06 18:00 | 9415.47 | 3.001 | 74.6994 | 53.895 | 2759.4019
2032-11-07 19:00 | 7550.28 | 2.4028 | 74.7533 | 53.895 | 2212.7686
2032-11-08 20:00 | 6044.42 | 1.8755 | 75.0079 | 53.895 | 1771.4446
2032-11-09 21:00 | 4803.53 | 1.5265 | 74.464 | 53.895 | 1407.7757
2032-11-10 22:00 | 3839.72 | 1.1974 | 74.4856 | 53.895 | 1125.3108
2032-11-11 23:00 | 2803.57 | 1 | 58.7303 | 53.895 | 821.6453
2032-11-13 | -155.122 | 1.1156 | 58.2884 | 53.895 | -45.4618
2032-11-14 01:00 | -597.737 | 2.3156 | 57.2071 | 53.895 | -175.1794
2032-11-15 02:00 | -1029.44 | 3.4978 | 56.6729 | 53.895 | -301.6991
2032-11-16 03:00 | -1299.56 | 4.2044 | 56.3215 | 53.895 | -380.8634
2032-11-17 04:00 | -1582.36 | 5.0018 | 56.0014 | 53.895 | -463.7439
2032-11-18 05:00 | -1575.46 | 4.9192 | 55.7172 | 53.895 | -461.7217
2032-11-19 06:00 | -351.362 | 1.2525 | 55.718 | 53.895 | -102.974
2032-11-20 07:00 | 2047.16 | 1 | 56.6779 | 53.895 | 599.9634
2032-11-21 08:00 | 2844.8 | 1 | 56.79 | 53.895 | 833.7286
2032-11-22 09:00 | 3007.34 | 1 | 74.494 | 53.895 | 881.3644
2032-11-23 10:00 | 4515.33 | 1.4368 | 72.2913 | 53.895 | 1323.3126
2032-11-24 11:00 | 5983.87 | 1.9669 | 72.0843 | 53.895 | 1753.6992
2032-11-25 12:00 | 7083.45 | 2.4 | 72.0167 | 53.895 | 2075.9543
2032-11-26 13:00 | 7775 | 2.5702 | 72.6812 | 53.895 | 2278.6276
2032-11-27 14:00 | 8624.88 | 2.843 | 73.003 | 53.895 | 2527.7028
2032-11-28 15:00 | 9605.14 | 3.1044 | 73.5909 | 53.895 | 2814.9887
2032-11-29 16:00 | 11912.4 | 3.9628 | 73.4834 | 53.895 | 3491.1798
2032-11-30 17:00 | 11195.7 | 3.6587 | 74.2376 | 53.895 | 3281.1358
2032-12-01 18:00 | 10333.5 | 3.3088 | 74.7701 | 53.895 | 3028.4499
2032-12-02 19:00 | 8606.47 | 2.6563 | 75.3936 | 53.895 | 2522.3074
2032-12-03 20:00 | 7009.68 | 2.1845 | 75.1679 | 53.895 | 2054.3344
2032-12-04 21:00 | 5807.56 | 1.8194 | 74.9171 | 53.895 | 1702.0278
2032-12-05 22:00 | 4687.85 | 1.4866 | 74.4994 | 53.895 | 1373.8732
2032-12-06 23:00 | 3131.24 | 1 | 58.9476 | 53.895 | 917.6759
2032-12-08 | 3085.78 | 1 | 58.6359 | 53.895 | 904.3528
2032-12-09 01:00 | 3101.19 | 1 | 58.4496 | 53.895 | 908.8691
2032-12-10 02:00 | 670.596 | 1 | 58.7663 | 53.895 | 196.5323
2032-12-11 03:00 | 0 | 0 | 58.4942 | 53.895 | 0
2032-12-12 04:00 | -57.797 | 0.78823 | 57.8055 | 53.895 | -16.9386
2032-12-13 05:00 | 1749.59 | 1 | 57.6479 | 53.895 | 512.7542
2032-12-14 06:00 | 2951.79 | 1 | 57.4878 | 53.895 | 865.0843
2032-12-15 07:00 | 3013.27 | 1 | 75.329 | 53.895 | 883.1023
2032-12-16 08:00 | 3131.82 | 1.0148 | 72.5877 | 53.895 | 917.8458
2032-12-17 09:00 | 4794.77 | 1.5738 | 72.4527 | 53.895 | 1405.2084
2032-12-18 10:00 | 6206.94 | 2.0671 | 72.4874 | 53.895 | 1819.0745
2032-12-19 11:00 | 7782.11 | 2.5939 | 72.7651 | 53.895 | 2280.7113
2032-12-20 12:00 | 8739.99 | 2.8855 | 73.2285 | 53.895 | 2561.4382
2032-12-21 13:00 | 10029.4 | 3.2887 | 73.638 | 53.895 | 2939.327
2032-12-22 14:00 | 11446.7 | 3.7227 | 74.145 | 53.895 | 3354.6966
2032-12-23 15:00 | 13275.6 | 4.3549 | 74.4505 | 53.895 | 3890.6943
2032-12-24 16:00 | 13370.2 | 4.3786 | 74.9735 | 53.895 | 3918.4188
2032-12-25 17:00 | 13266.3 | 4.2318 | 75.6819 | 53.895 | 3887.9687
2032-12-26 18:00 | 11853.2 | 3.7567 | 76.0116 | 53.895 | 3473.83
2032-12-27 19:00 | 10187.1 | 3.2138 | 76.1332 | 53.895 | 2985.5443
2032-12-28 20:00 | 7709.38 | 2.132 | 78.1331 | 53.895 | 2259.3962
2032-12-29 21:00 | 6206.03 | 1.8275 | 76.7867 | 53.895 | 1818.8079
2032-12-30 22:00 | 3259.18 | 1 | 75.8541 | 53.895 | 955.1714
2032-12-31 23:00 | 3144.94 | 1 | 81.6931 | 53.895 | 921.6909
2033-01-02 | 3147.56 | 1 | 59.1676 | 53.895 | 922.4588
2033-01-03 01:00 | 3102.45 | 1 | 58.9783 | 53.895 | 909.2383
2033-01-04 02:00 | 3028.06 | 1 | 58.8343 | 53.895 | 887.4368
2033-01-05 03:00 | 3119.77 | 1 | 58.6712 | 53.895 | 914.3143
2033-01-06 04:00 | 3117.27 | 1 | 58.6023 | 53.895 | 913.5817
2033-01-07 05:00 | 3141.84 | 1 | 58.5196 | 53.895 | 920.7824
2033-01-08 06:00 | 3216.69 | 1 | 80.6574 | 53.895 | 942.7188
2033-01-09 07:00 | 3657.7 | 1.1573 | 73.7051 | 53.895 | 1071.9661
2033-01-10 08:00 | 3922.44 | 1.2488 | 73.6462 | 53.895 | 1149.5537
2033-01-11 09:00 | 6076.72 | 1.9942 | 73.229 | 53.895 | 1780.9108
2033-01-12 10:00 | 7831.48 | 2.5804 | 73.4523 | 53.895 | 2295.1802
2033-01-13 11:00 | 9332.85 | 3.2164 | 73.1921 | 53.895 | 2735.1883
2033-01-14 12:00 | 9978.08 | 3.4828 | 73.4061 | 53.895 | 2924.2866
2033-01-15 13:00 | 10522.6 | 3.5779 | 74.0753 | 53.895 | 3083.8696
2033-01-16 14:00 | 11370.8 | 3.8307 | 74.4864 | 53.895 | 3332.4525
2033-01-17 15:00 | 13080.3 | 4.3465 | 74.9536 | 53.895 | 3833.4575
2033-01-18 16:00 | 13790 | 4.4879 | 75.6357 | 53.895 | 4041.4501
2033-01-19 17:00 | 13416.3 | 4.4199 | 75.7952 | 53.895 | 3931.9294
2033-01-20 18:00 | 12062.3 | 3.8463 | 76.4666 | 53.895 | 3535.1112
2033-01-21 19:00 | 10292.9 | 3.2111 | 76.8224 | 53.895 | 3016.5512
2033-01-22 20:00 | 7581.33 | 2.2586 | 77.4294 | 53.895 | 2221.8685
2033-01-23 21:00 | 6462.43 | 1.9307 | 77.0314 | 53.895 | 1893.9513
2033-01-24 22:00 | 3983.02 | 1.2208 | 76.336 | 53.895 | 1167.3079
2033-01-25 23:00 | 3055.5 | 1 | 75.7113 | 53.895 | 895.4787
2033-01-27 | 3135.23 | 1 | 59.648 | 53.895 | 918.8452
2033-01-28 01:00 | 3120.71 | 1 | 59.4202 | 53.895 | 914.5898
2033-01-29 02:00 | 3112.26 | 1 | 59.2633 | 53.895 | 912.1134
2033-01-30 03:00 | 3194.53 | 1 | 59.0951 | 53.895 | 936.2243
2033-01-31 04:00 | 3119.79 | 1 | 59.0098 | 53.895 | 914.3202
2033-02-01 05:00 | 3161.29 | 1 | 58.9089 | 53.895 | 926.4826
2033-02-02 06:00 | 3226.58 | 1 | 78.2392 | 53.895 | 945.6173
2033-02-03 07:00 | 4086.53 | 1.3236 | 73.7483 | 53.895 | 1197.6437
2033-02-04 08:00 | 4958.8 | 1.6136 | 73.755 | 53.895 | 1453.2808
2033-02-05 09:00 | 6598.73 | 2.1372 | 73.9377 | 53.895 | 1933.8969
2033-02-06 10:00 | 8606.17 | 2.7919 | 74.1707 | 53.895 | 2522.2195
2033-02-07 11:00 | 10082.4 | 3.3407 | 74.2592 | 53.895 | 2954.8598
2033-02-08 12:00 | 11159.2 | 3.6365 | 74.907 | 53.895 | 3270.4387
2033-02-09 13:00 | 11722.7 | 3.8684 | 75.1084 | 53.895 | 3435.5842
2033-02-10 14:00 | 12849.8 | 4.1484 | 75.7431 | 53.895 | 3765.9046
2033-02-11 15:00 | 15103.8 | 4.9176 | 75.9616 | 53.895 | 4426.4868
2033-02-12 16:00 | 15329 | 5.0136 | 76.4011 | 53.895 | 4492.4864
2033-02-13 17:00 | 14835.4 | 4.8038 | 76.9002 | 53.895 | 4347.8266
2033-02-14 18:00 | 13377.2 | 4.2846 | 77.2646 | 53.895 | 3920.4703
2033-02-15 19:00 | 11784.4 | 3.7178 | 77.5272 | 53.895 | 3453.6667
2033-02-16 20:00 | 9511.29 | 2.8134 | 78.4429 | 53.895 | 2787.4839
2033-02-17 21:00 | 8067.66 | 2.4573 | 77.7039 | 53.895 | 2364.3977
2033-02-18 22:00 | 5792.48 | 1.695 | 78.0419 | 53.895 | 1697.6083
2033-02-19 23:00 | 4782.38 | 1.4654 | 76.8897 | 53.895 | 1401.5772
2033-02-21 | 3919.49 | 1.255 | 75.8633 | 53.895 | 1148.6891
2033-02-22 01:00 | 3308.31 | 1.0778 | 75.2879 | 53.895 | 969.57
2033-02-23 02:00 | 3166.21 | 1 | 76.5604 | 53.895 | 927.9246
2033-02-24 03:00 | 3151 | 1 | 76.2303 | 53.895 | 923.4669
2033-02-25 04:00 | 3186.29 | 1 | 76.3546 | 53.895 | 933.8094
2033-02-26 05:00 | 3850.59 | 1.2061 | 75.0073 | 53.895 | 1128.4965
2033-02-27 06:00 | 4901.79 | 1.4842 | 75.4922 | 53.895 | 1436.5728
2033-02-28 07:00 | 5958.62 | 2.0218 | 73.9085 | 53.895 | 1746.2991
2033-03-01 08:00 | 6581.08 | 2.1458 | 74.6312 | 53.895 | 1928.7242
2033-03-02 09:00 | 8418.02 | 2.8215 | 74.3842 | 53.895 | 2467.0781
2033-03-03 10:00 | 10132.9 | 3.3674 | 74.8179 | 53.895 | 2969.6598
2033-03-04 11:00 | 11394.5 | 3.7502 | 75.3503 | 53.895 | 3339.3983
2033-03-05 12:00 | 12134.4 | 4.0105 | 75.6771 | 53.895 | 3556.2416
2033-03-06 13:00 | 13064.6 | 4.2196 | 76.3451 | 53.895 | 3828.8563
2033-03-07 14:00 | 13736.9 | 4.5295 | 76.4021 | 53.895 | 4025.888
2033-03-08 15:00 | 15528.6 | 5.1622 | 76.5933 | 53.895 | 4550.9834
2033-03-09 16:00 | 16324.7 | 5.345 | 77.2322 | 53.895 | 4784.2973
2033-03-10 17:00 | 16665.4 | 5.2701 | 78.1192 | 53.895 | 4884.1466
2033-03-11 18:00 | 14758 | 4.7553 | 78.1666 | 53.895 | 4325.1429
2033-03-12 19:00 | 13265.1 | 4.1131 | 78.7646 | 53.895 | 3887.6171
2033-03-13 20:00 | 10251.9 | 3.1748 | 78.7215 | 53.895 | 3004.5353
2033-03-14 21:00 | 8643.85 | 2.6693 | 78.4171 | 53.895 | 2533.2624
2033-03-15 22:00 | 6482.31 | 1.9077 | 78.8084 | 53.895 | 1899.7775
2033-03-16 23:00 | 5798.22 | 1.6783 | 78.6119 | 53.895 | 1699.2905
2033-03-18 | 4766.72 | 1.5031 | 76.9384 | 53.895 | 1396.9877
2033-03-19 01:00 | 4199.22 | 1.3049 | 76.8115 | 53.895 | 1230.6699
2033-03-20 02:00 | 3834.09 | 1.2095 | 76.2992 | 53.895 | 1123.6609
2033-03-21 03:00 | 3803.04 | 1.2259 | 75.7274 | 53.895 | 1114.561
2033-03-22 04:00 | 3793.64 | 1.1964 | 75.8621 | 53.895 | 1111.8061
2033-03-23 05:00 | 4946.87 | 1.5662 | 75.6284 | 53.895 | 1449.7845
2033-03-24 06:00 | 6013.18 | 1.9947 | 74.9596 | 53.895 | 1762.2891
2033-03-25 07:00 | 7586 | 2.4165 | 75.6389 | 53.895 | 2223.2371
2033-03-26 08:00 | 8153.36 | 2.5836 | 75.9503 | 53.895 | 2389.5139
2033-03-27 09:00 | 9881.99 | 3.2239 | 75.7144 | 53.895 | 2896.1254
2033-03-28 10:00 | 11647.9 | 3.8356 | 75.911 | 53.895 | 3413.6625
2033-03-29 11:00 | 12572.3 | 4.2652 | 75.9073 | 53.895 | 3684.5774
2033-03-30 12:00 | 13455.8 | 4.4907 | 76.4989 | 53.895 | 3943.5057
2033-03-31 13:00 | 14264.6 | 4.6093 | 77.2927 | 53.895 | 4180.5416
2033-04-01 14:00 | 14985.8 | 4.874 | 77.5407 | 53.895 | 4391.9044
2033-04-02 15:00 | 17122.3 | 5.5929 | 77.7823 | 53.895 | 5018.0508
2033-04-03 16:00 | 17893.5 | 5.7739 | 78.4277 | 53.895 | 5244.0672
2033-04-04 17:00 | 18252 | 5.8031 | 79.0455 | 53.895 | 5349.1332
2033-04-05 18:00 | 16640.2 | 5.2825 | 79.4033 | 53.895 | 4876.7612
2033-04-06 19:00 | 14688.5 | 4.6325 | 79.577 | 53.895 | 4304.7744
2033-04-07 20:00 | 11783.7 | 3.5882 | 80.0232 | 53.895 | 3453.4616
2033-04-08 21:00 | 9971.33 | 3.1083 | 79.323 | 53.895 | 2922.3084
2033-04-09 22:00 | 7637.22 | 2.2786 | 79.6291 | 53.895 | 2238.2482
2033-04-10 23:00 | 6018.29 | 1.7935 | 79.1605 | 53.895 | 1763.7867
2033-04-12 | 5933.1 | 1.7029 | 79.279 | 53.895 | 1738.82
2033-04-13 01:00 | 5169.67 | 1.6322 | 77.4978 | 53.895 | 1515.0807
2033-04-14 02:00 | 4298.91 | 1.397 | 76.7978 | 53.895 | 1259.8862
2033-04-15 03:00 | 4021.8 | 1.281 | 76.7551 | 53.895 | 1178.6732
2033-04-16 04:00 | 3357.79 | 1.0938 | 76.1695 | 53.895 | 984.0711
2033-04-17 05:00 | 3170.35 | 1.0355 | 75.852 | 53.895 | 929.1379
2033-04-18 06:00 | 5989.34 | 1.8726 | 76.23 | 53.895 | 1755.3023
2033-04-19 07:00 | 7940.23 | 2.6335 | 75.5174 | 53.895 | 2327.0517
2033-04-20 08:00 | 8101.32 | 2.5883 | 76.3559 | 53.895 | 2374.2625
2033-04-21 09:00 | 9510.37 | 3.1216 | 76.0979 | 53.895 | 2787.2143
2033-04-22 10:00 | 11357.8 | 3.7678 | 76.2053 | 53.895 | 3328.6426
2033-04-23 11:00 | 13179.2 | 4.3402 | 76.7278 | 53.895 | 3862.4422
2033-04-24 12:00 | 14089.6 | 4.6626 | 77.1018 | 53.895 | 4129.2541
2033-04-25 13:00 | 14452.2 | 4.7879 | 77.4519 | 53.895 | 4235.5217
2033-04-26 14:00 | 15759.1 | 5.021 | 78.3162 | 53.895 | 4618.5363
2033-04-27 15:00 | 16326.1 | 5.266 | 78.5088 | 53.895 | 4784.7076
2033-04-28 16:00 | 19082.1 | 6.1439 | 78.8532 | 53.895 | 5592.4115
2033-04-29 17:00 | 18056 | 5.8384 | 79.357 | 53.895 | 5291.6912
2033-04-30 18:00 | 17017.9 | 5.3274 | 80.0803 | 53.895 | 4987.4542
2033-05-01 19:00 | 14744.8 | 4.6602 | 80.0171 | 53.895 | 4321.2743
2033-05-02 20:00 | 12924.1 | 4.0556 | 80.0057 | 53.895 | 3787.6798
2033-05-03 21:00 | 11394.3 | 3.5693 | 79.8264 | 53.895 | 3339.3397
2033-05-04 22:00 | 10159.3 | 3.1907 | 79.5031 | 53.895 | 2977.3969
2033-05-05 23:00 | 6976.32 | 2.0544 | 80.2134 | 53.895 | 2044.5576
2033-05-07 | 5927.68 | 1.7856 | 79.2996 | 53.895 | 1737.2315
2033-05-08 01:00 | 5103.5 | 1.5548 | 78.692 | 53.895 | 1495.6882
2033-05-09 02:00 | 4600.2 | 1.4358 | 77.9706 | 53.895 | 1348.1855
2033-05-10 03:00 | 4014.08 | 1.3041 | 77.0686 | 53.895 | 1176.4107
2033-05-11 04:00 | 3495.66 | 1.1351 | 76.7421 | 53.895 | 1024.4768
2033-05-12 05:00 | 3266.28 | 1.029 | 76.9053 | 53.895 | 957.2522
2033-05-13 06:00 | 5762.78 | 1.8253 | 76.5653 | 53.895 | 1688.9041
2033-05-14 07:00 | 6998.84 | 2.385 | 75.6309 | 53.895 | 2051.1575
2033-05-15 08:00 | 7345.94 | 2.3018 | 77.0017 | 53.895 | 2152.8825
2033-05-16 09:00 | 9169.95 | 3.1286 | 75.8569 | 53.895 | 2687.4471
2033-05-17 10:00 | 11246.2 | 3.8389 | 76.1027 | 53.895 | 3295.9359
2033-05-18 11:00 | 13379.9 | 4.418 | 76.9909 | 53.895 | 3921.2616
2033-05-19 12:00 | 14228.1 | 4.7293 | 77.377 | 53.895 | 4169.8445
2033-05-20 13:00 | 12020.3 | 3.939 | 77.979 | 53.895 | 3522.8022
2033-05-21 14:00 | 11836.9 | 3.8165 | 78.2076 | 53.895 | 3469.0529
2033-05-22 15:00 | 11922.6 | 3.7563 | 78.5611 | 53.895 | 3494.1691
2033-05-23 16:00 | 12908.8 | 4.31 | 77.7673 | 53.895 | 3783.1958
2033-05-24 17:00 | 11317.4 | 3.6888 | 78.2513 | 53.895 | 3316.8025
2033-05-25 18:00 | 10298.3 | 3.2249 | 78.6938 | 53.895 | 3018.1338
2033-05-26 19:00 | 9244.94 | 2.8655 | 78.6823 | 53.895 | 2709.4245
2033-05-27 20:00 | 8063.97 | 2.5718 | 78.0876 | 53.895 | 2363.3163
2033-05-28 21:00 | 7270.7 | 2.2324 | 78.4198 | 53.895 | 2130.8318
2033-05-29 22:00 | 6411.26 | 2.0021 | 77.8968 | 53.895 | 1878.9548
2033-05-30 23:00 | 3731.25 | 1.1059 | 78.4459 | 53.895 | 1093.5214
2033-06-01 | 3235.71 | 1 | 79.0533 | 53.895 | 948.293
2033-06-02 01:00 | 3179.02 | 1 | 80.5894 | 53.895 | 931.6788
2033-06-03 02:00 | 3333.08 | 1 | 81.9186 | 53.895 | 976.8293
2033-06-04 03:00 | 3194.01 | 1 | 77.5202 | 53.895 | 936.0719
2033-06-05 04:00 | 3128.28 | 1 | 76.5585 | 53.895 | 916.8084
2033-06-06 05:00 | 4097.33 | 1.3153 | 75.7282 | 53.895 | 1200.8089
2033-06-07 06:00 | 4517.94 | 1.4326 | 75.9306 | 53.895 | 1324.0775
2033-06-08 07:00 | 5900.28 | 1.8469 | 76.1412 | 53.895 | 1729.2014
2033-06-09 08:00 | 6312.62 | 2.0081 | 76.049 | 53.895 | 1850.0463
2033-06-10 09:00 | 7781.27 | 2.6745 | 75.0593 | 53.895 | 2280.4651
2033-06-11 10:00 | 9807.14 | 3.2879 | 75.6176 | 53.895 | 2874.189
2033-06-12 11:00 | 11731.4 | 3.9373 | 75.9666 | 53.895 | 3438.134
2033-06-13 12:00 | 13454.3 | 4.4379 | 76.6523 | 53.895 | 3943.0661
2033-06-14 13:00 | 14267.4 | 4.7581 | 76.9737 | 53.895 | 4181.3622
2033-06-15 14:00 | 14413.6 | 4.6903 | 77.7396 | 53.895 | 4224.2092
2033-06-16 15:00 | 14937.5 | 5.1965 | 77.114 | 53.895 | 4377.7491
2033-06-17 16:00 | 16228.6 | 5.2701 | 78.3505 | 53.895 | 4756.1332
2033-06-18 17:00 | 14780 | 4.7285 | 78.9414 | 53.895 | 4331.5904
2033-06-19 18:00 | 14708.7 | 4.4866 | 79.735 | 53.895 | 4310.6944
2033-06-20 19:00 | 12524.8 | 3.9278 | 79.4118 | 53.895 | 3670.6565
2033-06-21 20:00 | 9340.54 | 2.9078 | 79.4105 | 53.895 | 2737.4421
2033-06-22 21:00 | 8315.91 | 2.4836 | 79.632 | 53.895 | 2437.1526
2033-06-23 22:00 | 6197.57 | 1.8307 | 79.4616 | 53.895 | 1816.3285
2033-06-24 23:00 | 5102 | 1.5873 | 78.2402 | 53.895 | 1495.2486
2033-06-26 | 4485.65 | 1.3542 | 78.2738 | 53.895 | 1314.6142
2033-06-27 01:00 | 3985.77 | 1.2565 | 77.2757 | 53.895 | 1168.1139
2033-06-28 02:00 | 3771.22 | 1.174 | 77.1941 | 53.895 | 1105.2355
2033-06-29 03:00 | 3998.56 | 1.2937 | 76.3894 | 53.895 | 1171.8623
2033-06-30 04:00 | 4106.48 | 1.3196 | 76.3418 | 53.895 | 1203.4905
2033-07-01 05:00 | 5018.82 | 1.5787 | 76.5435 | 53.895 | 1470.8709
2033-07-02 06:00 | 5381.07 | 1.7355 | 76.1678 | 53.895 | 1577.0359
2033-07-03 07:00 | 6527.15 | 2.1436 | 75.9127 | 53.895 | 1912.9188
2033-07-04 08:00 | 6953.95 | 2.2758 | 76.0978 | 53.895 | 2038.0016
2033-07-05 09:00 | 7972.24 | 2.8301 | 75.0862 | 53.895 | 2336.4329
2033-07-06 10:00 | 8985.66 | 3.1108 | 75.5984 | 53.895 | 2633.437
2033-07-07 11:00 | 10706.3 | 3.6763 | 75.914 | 53.895 | 3137.7068
2033-07-08 12:00 | 11906.3 | 3.9061 | 76.8727 | 53.895 | 3489.3921
2033-07-09 13:00 | 12325.5 | 3.9885 | 77.4038 | 53.895 | 3612.2475
2033-07-10 14:00 | 12973 | 4.2166 | 77.6012 | 53.895 | 3802.011
2033-07-11 15:00 | 14482 | 4.8084 | 77.547 | 53.895 | 4244.2552
2033-07-12 16:00 | 15139.7 | 4.9126 | 78.2347 | 53.895 | 4437.0081
2033-07-13 17:00 | 14552.6 | 4.7522 | 78.457 | 53.895 | 4264.9461
2033-07-14 18:00 | 13226 | 4.2763 | 78.7413 | 53.895 | 3876.158
2033-07-15 19:00 | 11065.8 | 3.6442 | 78.4645 | 53.895 | 3243.0658
2033-07-16 20:00 | 8235.05 | 2.5824 | 78.9939 | 53.895 | 2413.4549
2033-07-17 21:00 | 6845.57 | 2.1134 | 78.8094 | 53.895 | 2006.2385
2033-07-18 22:00 | 4088.07 | 1.3121 | 77.8526 | 53.895 | 1198.095
2033-07-19 23:00 | 3095.23 | 1 | 77.4476 | 53.895 | 907.1224
2033-07-21 | 3080.22 | 1 | 61.7085 | 53.895 | 902.7234
2033-07-22 01:00 | 3056.37 | 1 | 61.42 | 53.895 | 895.7336
2033-07-23 02:00 | 3085.8 | 1 | 61.1994 | 53.895 | 904.3587
2033-07-24 03:00 | 3110.9 | 1 | 60.9976 | 53.895 | 911.7148
2033-07-25 04:00 | 3122.19 | 1 | 60.8515 | 53.895 | 915.0236
2033-07-26 05:00 | 3136.37 | 1 | 60.7236 | 53.895 | 919.1793
2033-07-27 06:00 | 3195.49 | 1 | 60.5951 | 53.895 | 936.5057
2033-07-28 07:00 | 3367.1 | 1.0492 | 76.0991 | 53.895 | 986.7996
2033-07-29 08:00 | 4091.63 | 1.2978 | 75.7303 | 53.895 | 1199.1384
2033-07-30 09:00 | 5629.2 | 1.7978 | 75.645 | 53.895 | 1649.7557
2033-07-31 10:00 | 7040.3 | 2.385 | 74.9837 | 53.895 | 2063.3083
2033-08-01 11:00 | 7933.19 | 2.7043 | 75.1442 | 53.895 | 2324.9885
2033-08-02 12:00 | 9434.35 | 3.0932 | 75.9077 | 53.895 | 2764.935
2033-08-03 13:00 | 9434.4 | 3.0682 | 76.334 | 53.895 | 2764.9497
2033-08-04 14:00 | 10130.7 | 3.3133 | 76.4346 | 53.895 | 2969.0151
2033-08-05 15:00 | 12134.2 | 3.993 | 76.52 | 53.895 | 3556.183
2033-08-06 16:00 | 12723.3 | 4.2031 | 76.8152 | 53.895 | 3728.8311
2033-08-07 17:00 | 12860.6 | 4.1985 | 77.2738 | 53.895 | 3769.0698
2033-08-08 18:00 | 11447.2 | 3.7496 | 77.4238 | 53.895 | 3354.8432
2033-08-09 19:00 | 9728.65 | 3.1296 | 77.7026 | 53.895 | 2851.1859
2033-08-10 20:00 | 7099.22 | 2.201 | 78.1324 | 53.895 | 2080.576
2033-08-11 21:00 | 5612.06 | 1.6371 | 78.72 | 53.895 | 1644.7324
2033-08-12 22:00 | 3174.8 | 1 | 79.6157 | 53.895 | 930.442
2033-08-13 23:00 | 3143.9 | 1 | 61.2772 | 53.895 | 921.3861
2033-08-15 | 3078.46 | 1 | 60.9751 | 53.895 | 902.2076
2033-08-16 01:00 | 2272.36 | 1 | 60.9024 | 53.895 | 665.963
2033-08-17 02:00 | 0 | 0 | 61.035 | 53.895 | 0
2033-08-18 03:00 | 701.76 | 1 | 60.4254 | 53.895 | 205.6656
2033-08-19 04:00 | 294.975 | 1 | 60.2818 | 53.895 | 86.4486
2033-08-20 05:00 | 2141.09 | 1 | 59.7307 | 53.895 | 627.4915
2033-08-21 06:00 | 2915.11 | 1 | 59.6044 | 53.895 | 854.3344
2033-08-22 07:00 | 3097.33 | 1.0057 | 74.6074 | 53.895 | 907.7378
2033-08-23 08:00 | 4332.61 | 1.3845 | 74.836 | 53.895 | 1269.7626
2033-08-24 09:00 | 6166.68 | 2.0907 | 74.135 | 53.895 | 1807.2755
2033-08-25 10:00 | 7890.76 | 2.7582 | 74.0408 | 53.895 | 2312.5535
2033-08-26 11:00 | 9614.94 | 3.2838 | 74.7049 | 53.895 | 2817.8608
2033-08-27 12:00 | 10752.3 | 3.5988 | 75.3741 | 53.895 | 3151.1881
2033-08-28 13:00 | 11011.3 | 3.5714 | 76.2178 | 53.895 | 3227.0935
2033-08-29 14:00 | 11341.4 | 3.6993 | 76.4439 | 53.895 | 3323.8362
2033-08-30 15:00 | 13143.7 | 4.3283 | 76.5414 | 53.895 | 3852.0382
2033-08-31 16:00 | 13615.3 | 4.446 | 77.0609 | 53.895 | 3990.2505
2033-09-01 17:00 | 13709.9 | 4.4141 | 77.5684 | 53.895 | 4017.9751
2033-09-02 18:00 | 12283.5 | 3.9231 | 77.9086 | 53.895 | 3599.9385
2033-09-03 19:00 | 10622.3 | 3.351 | 78.1274 | 53.895 | 3113.0888
2033-09-04 20:00 | 7692.62 | 2.4015 | 78.1951 | 53.895 | 2254.4844
2033-09-05 21:00 | 6293.7 | 1.8966 | 78.3635 | 53.895 | 1844.5014
2033-09-06 22:00 | 3853.11 | 1.1501 | 78.17 | 53.895 | 1129.2351
2033-09-07 23:00 | 3148.71 | 1 | 80.541 | 53.895 | 922.7958
2033-09-09 | 3094.05 | 1 | 61.0584 | 53.895 | 906.7765
2033-09-10 01:00 | 3038.37 | 1 | 60.8172 | 53.895 | 890.4583
2033-09-11 02:00 | 3141.08 | 1 | 60.6283 | 53.895 | 920.5597
2033-09-12 03:00 | 3153.73 | 1 | 60.4795 | 53.895 | 924.267
2033-09-13 04:00 | 3138.98 | 1 | 60.3812 | 53.895 | 919.9442
2033-09-14 05:00 | 3154.52 | 1 | 60.2742 | 53.895 | 924.4986
2033-09-15 06:00 | 3141.41 | 1 | 79.9485 | 53.895 | 920.6564
2033-09-16 07:00 | 3437.09 | 1.0482 | 75.9766 | 53.895 | 1007.3116
2033-09-17 08:00 | 3145.92 | 1 | 76.9822 | 53.895 | 921.9781
2033-09-18 09:00 | 4389.94 | 1.3882 | 75.3289 | 53.895 | 1286.5644
2033-09-19 10:00 | 6199.29 | 2.0637 | 74.6765 | 53.895 | 1816.8326
2033-09-20 11:00 | 6783.09 | 2.2214 | 75.1601 | 53.895 | 1987.9274
2033-09-21 12:00 | 8820.11 | 2.9437 | 75.0652 | 53.895 | 2584.9191
2033-09-22 13:00 | 8876.23 | 2.905 | 75.6816 | 53.895 | 2601.3662
2033-09-23 14:00 | 9176.19 | 2.9307 | 76.2557 | 53.895 | 2689.2758
2033-09-24 15:00 | 10282.6 | 3.3602 | 76.0691 | 53.895 | 3013.5326
2033-09-25 16:00 | 10660.9 | 3.336 | 76.9279 | 53.895 | 3124.4014
2033-09-26 17:00 | 10439.7 | 3.3137 | 76.9102 | 53.895 | 3059.574
2033-09-27 18:00 | 9194.65 | 2.7708 | 77.7846 | 53.895 | 2694.6859
2033-09-28 19:00 | 8106.07 | 2.4769 | 77.5152 | 53.895 | 2375.6546
2033-09-29 20:00 | 5920.78 | 1.771 | 77.7577 | 53.895 | 1735.2093
2033-09-30 21:00 | 4909.04 | 1.4881 | 77.2602 | 53.895 | 1438.6976
2033-10-01 22:00 | 3124.43 | 1 | 81.0192 | 53.895 | 915.68
2033-10-02 23:00 | 3002.61 | 1 | 60.6627 | 53.895 | 879.9781
2033-10-04 | 2814.3 | 1 | 60.4454 | 53.895 | 824.7899
2033-10-05 01:00 | 0 | 0 | 60.7383 | 53.895 | 0
2033-10-06 02:00 | 391.697 | 1 | 60.1893 | 53.895 | 114.7951
2033-10-07 03:00 | 264.277 | 1 | 59.9372 | 53.895 | 77.4519
2033-10-08 04:00 | 259.249 | 1 | 59.75 | 53.895 | 75.9784
2033-10-09 05:00 | 384.745 | 1 | 59.532 | 53.895 | 112.7576
2033-10-10 06:00 | 1671.6 | 1.0161 | 67.1569 | 53.895 | 489.8976
2033-10-11 07:00 | 2689.99 | 1.0505 | 71.4884 | 53.895 | 788.3582
2033-10-12 08:00 | 2835.07 | 1 | 59.121 | 53.895 | 830.877
2033-10-13 09:00 | 3010.08 | 1 | 59.1436 | 53.895 | 882.1674
2033-10-14 10:00 | 3057.3 | 1 | 74.4925 | 53.895 | 896.0062
2033-10-15 11:00 | 4337.09 | 1.3535 | 74.6944 | 53.895 | 1271.0756
2033-10-16 12:00 | 5110.09 | 1.6402 | 74.3975 | 53.895 | 1497.6195
2033-10-17 13:00 | 6488.89 | 2.2108 | 73.7038 | 53.895 | 1901.7059
2033-10-18 14:00 | 7709.89 | 2.6366 | 73.8859 | 53.895 | 2259.5457
2033-10-19 15:00 | 9418.48 | 3.1172 | 74.6099 | 53.895 | 2760.284
2033-10-20 16:00 | 12579.9 | 4.3147 | 74.4774 | 53.895 | 3686.8048
2033-10-21 17:00 | 11772.5 | 3.9216 | 75.5013 | 53.895 | 3450.1792
2033-10-22 18:00 | 10677.8 | 3.4859 | 76.0739 | 53.895 | 3129.3543
2033-10-23 19:00 | 9189.96 | 2.8959 | 76.6606 | 53.895 | 2693.3114
2033-10-24 20:00 | 7697.46 | 2.4593 | 76.4232 | 53.895 | 2255.9028
2033-10-25 21:00 | 6943.65 | 2.0895 | 77.1929 | 53.895 | 2034.9829
2033-10-26 22:00 | 5873.73 | 1.8069 | 76.7047 | 53.895 | 1721.4203
2033-10-27 23:00 | 3270.44 | 1 | 83.7643 | 53.895 | 958.4714
2033-10-29 | 3119.44 | 1 | 60.3524 | 53.895 | 914.2176
2033-10-30 01:00 | 3090.92 | 1 | 60.127 | 53.895 | 905.8592
2033-10-31 02:00 | 3134.14 | 1 | 59.9831 | 53.895 | 918.5258
2033-11-01 03:00 | 3100.75 | 1 | 59.8627 | 53.895 | 908.7401
2033-11-02 04:00 | 0 | 0 | 60.2559 | 53.895 | 0
2033-11-03 05:00 | 506.185 | 1 | 59.7032 | 53.895 | 148.3482
2033-11-04 06:00 | 2391.86 | 1.3589 | 67.8143 | 53.895 | 700.985
2033-11-05 07:00 | 4369.37 | 1.6769 | 71.8333 | 53.895 | 1280.5359
2033-11-06 08:00 | 4767.88 | 1.5692 | 74.0742 | 53.895 | 1397.3277
2033-11-07 09:00 | 6716.87 | 2.2193 | 74.1203 | 53.895 | 1968.5203
2033-11-08 10:00 | 8770.82 | 2.8769 | 74.5565 | 53.895 | 2570.4736
2033-11-09 11:00 | 10006.7 | 3.3642 | 74.6913 | 53.895 | 2932.6743
2033-11-10 12:00 | 10045.2 | 3.3171 | 75.3681 | 53.895 | 2943.9575
2033-11-11 13:00 | 10142.1 | 3.3358 | 75.6765 | 53.895 | 2972.3561
2033-11-12 14:00 | 9979.8 | 3.2759 | 75.9111 | 53.895 | 2924.7907
2033-11-13 15:00 | 9729.88 | 3.1032 | 76.4526 | 53.895 | 2851.5463
2033-11-14 16:00 | 10792.8 | 3.5339 | 76.1344 | 53.895 | 3163.0574
2033-11-15 17:00 | 10058.1 | 3.2567 | 76.4908 | 53.895 | 2947.7381
2033-11-16 18:00 | 8586.18 | 2.7489 | 76.7052 | 53.895 | 2516.361
2033-11-17 19:00 | 7330.82 | 2.3326 | 76.6598 | 53.895 | 2148.4513
2033-11-18 20:00 | 6323.61 | 1.91 | 77.2709 | 53.895 | 1853.2671
2033-11-19 21:00 | 5341.21 | 1.6369 | 76.8514 | 53.895 | 1565.3541
2033-11-20 22:00 | 4518.75 | 1.4193 | 76.2284 | 53.895 | 1324.3149
2033-11-21 23:00 | 3121.44 | 1 | 60.5376 | 53.895 | 914.8038
2033-11-23 | 3059.02 | 1 | 60.2287 | 53.895 | 896.5103
2033-11-24 01:00 | 3154.91 | 1 | 60.0109 | 53.895 | 924.6128
2033-11-25 02:00 | 3331.06 | 1 | 59.8628 | 53.895 | 976.2373
2033-11-26 03:00 | 3202.81 | 1 | 59.8097 | 53.895 | 938.651
2033-11-27 04:00 | 3269.64 | 1 | 59.7178 | 53.895 | 958.2369
2033-11-28 05:00 | 3166.47 | 1 | 76.1937 | 53.895 | 928.0008
2033-11-29 06:00 | 3541.97 | 1.1 | 75.2517 | 53.895 | 1038.0489
2033-11-30 07:00 | 3995.14 | 1.2307 | 75.3694 | 53.895 | 1170.86
2033-12-01 08:00 | 3225.18 | 1 | 76.3831 | 53.895 | 945.207
2033-12-02 09:00 | 5580.48 | 1.7206 | 75.2891 | 53.895 | 1635.4772
2033-12-03 10:00 | 7009.56 | 2.4409 | 73.7612 | 53.895 | 2054.2992
2033-12-04 11:00 | 8563.1 | 2.8963 | 74.4535 | 53.895 | 2509.5969
2033-12-05 12:00 | 8629.97 | 2.8147 | 75.295 | 53.895 | 2529.1945
2033-12-06 13:00 | 7154.72 | 2.4239 | 74.965 | 53.895 | 2096.8414
2033-12-07 14:00 | 8085.44 | 2.6836 | 75.2254 | 53.895 | 2369.6086
2033-12-08 15:00 | 9344.25 | 2.9948 | 75.8344 | 53.895 | 2738.5293
2033-12-09 16:00 | 8785.07 | 2.8416 | 75.9224 | 53.895 | 2574.6499
2033-12-10 17:00 | 9436.7 | 2.968 | 76.3642 | 53.895 | 2765.6238
2033-12-11 18:00 | 8022.71 | 2.589 | 76.1028 | 53.895 | 2351.2242
2033-12-12 19:00 | 7252.66 | 2.2268 | 76.8066 | 53.895 | 2125.5448
2033-12-13 20:00 | 4700.08 | 1.4309 | 76.8648 | 53.895 | 1377.4575
2033-12-14 21:00 | 3536.39 | 1.105 | 76.1212 | 53.895 | 1036.4136
2033-12-15 22:00 | 3079.9 | 1 | 60.2803 | 53.895 | 902.6296
2033-12-16 23:00 | 3138.11 | 1 | 60.013 | 53.895 | 919.6893
2033-12-18 | 3208.29 | 1 | 59.8358 | 53.895 | 940.257
2033-12-19 01:00 | 3139.58 | 1 | 59.7338 | 53.895 | 920.1201
2033-12-20 02:00 | 3150.51 | 1 | 59.6462 | 53.895 | 923.3233
2033-12-21 03:00 | 3138.13 | 1 | 59.5773 | 53.895 | 919.6951
2033-12-22 04:00 | 3163.09 | 1 | 59.5251 | 53.895 | 927.0102
2033-12-23 05:00 | 3184.02 | 1 | 80.405 | 53.895 | 933.1441
2033-12-24 06:00 | 3243.66 | 1 | 79.1934 | 53.895 | 950.6229
2033-12-25 07:00 | 3235.63 | 1 | 76.4411 | 53.895 | 948.2695
2033-12-26 08:00 | 3189.16 | 1 | 59.3541 | 53.895 | 934.6505
2033-12-27 09:00 | 3162.56 | 1 | 82.2022 | 53.895 | 926.8548
2033-12-28 10:00 | 3641.54 | 1.1496 | 74.6359 | 53.895 | 1067.23
2033-12-29 11:00 | 5578.73 | 1.7087 | 75.1007 | 53.895 | 1634.9644
2033-12-30 12:00 | 7559.61 | 2.641 | 73.4197 | 53.895 | 2215.503
2033-12-31 13:00 | 8980.95 | 3.0469 | 74.1664 | 53.895 | 2632.0566
2034-01-01 14:00 | 10547.8 | 3.4632 | 74.9773 | 53.895 | 3091.255
2034-01-02 15:00 | 12712.1 | 4.3113 | 74.9243 | 53.895 | 3725.5487
2034-01-03 16:00 | 13357.8 | 4.5231 | 75.4868 | 53.895 | 3914.7847
2034-01-04 17:00 | 13168.6 | 4.3321 | 76.3134 | 53.895 | 3859.3357
2034-01-05 18:00 | 12149.1 | 3.8148 | 77.2636 | 53.895 | 3560.5497
2034-01-06 19:00 | 10444.3 | 3.3145 | 77.2244 | 53.895 | 3060.9222
2034-01-07 20:00 | 7359.45 | 2.4315 | 76.6041 | 53.895 | 2156.8419
2034-01-08 21:00 | 6547.11 | 2.0243 | 77.233 | 53.895 | 1918.7685
2034-01-09 22:00 | 4645.57 | 1.4132 | 77.2417 | 53.895 | 1361.4822
2034-01-10 23:00 | 4273.26 | 1.2233 | 77.8528 | 53.895 | 1252.3689
2034-01-12 | 3663.92 | 1.0961 | 76.8732 | 53.895 | 1073.789
2034-01-13 01:00 | 3111.46 | 1.0138 | 75.3495 | 53.895 | 911.8789
2034-01-14 02:00 | 3149.93 | 1.0009 | 75.4919 | 53.895 | 923.1534
2034-01-15 03:00 | 3577.36 | 1.0912 | 75.9258 | 53.895 | 1048.4207
2034-01-16 04:00 | 3423.55 | 1.1221 | 74.7846 | 53.895 | 1003.3435
2034-01-17 05:00 | 4147.67 | 1.3234 | 75.0621 | 53.895 | 1215.5621
2034-01-18 06:00 | 4392.07 | 1.3828 | 75.2508 | 53.895 | 1287.1887
2034-01-19 07:00 | 4635.63 | 1.4779 | 75.08 | 53.895 | 1358.569
2034-01-20 08:00 | 3470.88 | 1.0866 | 75.3986 | 53.895 | 1017.2145
2034-01-21 09:00 | 3924.79 | 1.2458 | 75.0618 | 53.895 | 1150.2424
2034-01-22 10:00 | 3862.21 | 1.2478 | 74.7992 | 53.895 | 1131.902
2034-01-23 11:00 | 5026.34 | 1.62 | 74.8016 | 53.895 | 1473.0748
2034-01-24 12:00 | 5684.41 | 1.8976 | 74.3917 | 53.895 | 1665.9361
2034-01-25 13:00 | 7744.63 | 2.6638 | 74.084 | 53.895 | 2269.727
2034-01-26 14:00 | 8815.85 | 2.9828 | 74.6143 | 53.895 | 2583.6706
2034-01-27 15:00 | 11076.6 | 3.8697 | 74.4511 | 53.895 | 3246.231
2034-01-28 16:00 | 12417.8 | 4.1548 | 75.4775 | 53.895 | 3639.2979
2034-01-29 17:00 | 13227.4 | 4.2905 | 76.339 | 53.895 | 3876.5683
2034-01-30 18:00 | 12102.7 | 3.8553 | 76.9868 | 53.895 | 3546.9512
2034-01-31 19:00 | 10471.3 | 3.2605 | 77.4586 | 53.895 | 3068.8351
2034-02-01 20:00 | 7999.06 | 2.3977 | 78.025 | 53.895 | 2344.2931
2034-02-02 21:00 | 6707.73 | 2.0275 | 77.6447 | 53.895 | 1965.8416
2034-02-03 22:00 | 4556.19 | 1.312 | 78.1746 | 53.895 | 1335.2875
2034-02-04 23:00 | 3438.42 | 1.0628 | 76.6724 | 53.895 | 1007.7014
2034-02-06 | 3144.59 | 1 | 79.3363 | 53.895 | 921.5884
2034-02-07 01:00 | 3054.51 | 1 | 60.3903 | 53.895 | 895.1885
2034-02-08 02:00 | 3085.41 | 1 | 60.2136 | 53.895 | 904.2444
2034-02-09 03:00 | 3286.29 | 1 | 84.4855 | 53.895 | 963.1165
2034-02-10 04:00 | 3163.4 | 1 | 80.291 | 53.895 | 927.101
2034-02-11 05:00 | 3434.59 | 1.107 | 74.8796 | 53.895 | 1006.579
2034-02-12 06:00 | 4154.18 | 1.2787 | 75.5053 | 53.895 | 1217.47
2034-02-13 07:00 | 4899.25 | 1.5158 | 75.4493 | 53.895 | 1435.8284
2034-02-14 08:00 | 3963.23 | 1.2518 | 75.2473 | 53.895 | 1161.5081
2034-02-15 09:00 | 5321.76 | 1.9103 | 73.3934 | 53.895 | 1559.6539
2034-02-16 10:00 | 7502.06 | 2.6159 | 73.916 | 53.895 | 2198.6368
2034-02-17 11:00 | 9056.64 | 3.004 | 74.9623 | 53.895 | 2654.2392
2034-02-18 12:00 | 9783.2 | 3.3539 | 74.8803 | 53.895 | 2867.1729
2034-02-19 13:00 | 10665.4 | 3.4576 | 75.9563 | 53.895 | 3125.7202
2034-02-20 14:00 | 11173.7 | 3.6144 | 76.3106 | 53.895 | 3274.6882
2034-02-21 15:00 | 13498.9 | 4.4837 | 76.1952 | 53.895 | 3956.1371
2034-02-22 16:00 | 13900 | 4.6076 | 76.675 | 53.895 | 4073.6879
2034-02-23 17:00 | 14101.7 | 4.5489 | 77.3917 | 53.895 | 4132.8003
2034-02-24 18:00 | 13093.2 | 4.0718 | 78.1847 | 53.895 | 3837.2381
2034-02-25 19:00 | 11122.2 | 3.4688 | 78.2394 | 53.895 | 3259.5951
2034-02-26 20:00 | 8414.43 | 2.5432 | 78.6448 | 53.895 | 2466.026
2034-02-27 21:00 | 6883.17 | 2.166 | 77.7007 | 53.895 | 2017.258
2034-02-28 22:00 | 4693.67 | 1.4271 | 77.8937 | 53.895 | 1375.5789
2034-03-01 23:00 | 3674.93 | 1.1343 | 77.2106 | 53.895 | 1077.0157
2034-03-03 | 3258.13 | 1 | 77.7238 | 53.895 | 954.8636
2034-03-04 01:00 | 3177.02 | 1 | 81.8036 | 53.895 | 931.0927
2034-03-05 02:00 | 3184.91 | 1 | 83.586 | 53.895 | 933.405
2034-03-06 03:00 | 3031.74 | 1 | 80.7101 | 53.895 | 888.5153
2034-03-07 04:00 | 3111.53 | 1 | 80.2118 | 53.895 | 911.8994
2034-03-08 05:00 | 3378.35 | 1.0773 | 75.3378 | 53.895 | 990.0966
2034-03-09 06:00 | 4084.03 | 1.2566 | 75.8018 | 53.895 | 1196.911
2034-03-10 07:00 | 5265.19 | 1.5834 | 76.1573 | 53.895 | 1543.0749
2034-03-11 08:00 | 5275.88 | 1.601 | 76.1633 | 53.895 | 1546.2078
2034-03-12 09:00 | 7067.08 | 2.3229 | 75.0443 | 53.895 | 2071.1567
2034-03-13 10:00 | 8244.01 | 2.8681 | 74.5185 | 53.895 | 2416.0808
2034-03-14 11:00 | 9476.87 | 3.3176 | 74.7378 | 53.895 | 2777.3964
2034-03-15 12:00 | 10605.6 | 3.661 | 75.2475 | 53.895 | 3108.1945
2034-03-16 13:00 | 11805.3 | 3.9169 | 76.123 | 53.895 | 3459.7919
2034-03-17 14:00 | 13248.3 | 4.2674 | 76.9173 | 53.895 | 3882.6935
2034-03-18 15:00 | 15123.8 | 4.9291 | 77.1415 | 53.895 | 4432.3482
2034-03-19 16:00 | 15319.1 | 5.0158 | 77.5673 | 53.895 | 4489.585
2034-03-20 17:00 | 15666.6 | 4.987 | 78.3172 | 53.895 | 4591.4272
2034-03-21 18:00 | 13656.7 | 4.3225 | 78.7055 | 53.895 | 4002.3837
2034-03-22 19:00 | 11748.8 | 3.6863 | 78.8468 | 53.895 | 3443.2334
2034-03-23 20:00 | 8916.68 | 2.7375 | 79.0423 | 53.895 | 2613.2209
2034-03-24 21:00 | 7588.27 | 2.3214 | 78.7247 | 53.895 | 2223.9024
2034-03-25 22:00 | 5518.25 | 1.5505 | 79.7582 | 53.895 | 1617.2394
2034-03-26 23:00 | 3724.15 | 1.1711 | 77.5471 | 53.895 | 1091.4406
2034-03-28 | 3052.82 | 1 | 77.5999 | 53.895 | 894.6932
2034-03-29 01:00 | 3163.69 | 1 | 81.7179 | 53.895 | 927.186
2034-03-30 02:00 | 3267.6 | 1 | 84.7298 | 53.895 | 957.639
2034-03-31 03:00 | 3215.44 | 1 | 60.819 | 53.895 | 942.3524
2034-04-01 04:00 | 3098.98 | 1 | 60.6761 | 53.895 | 908.2214
2034-04-02 05:00 | 3003.43 | 1 | 60.5371 | 53.895 | 880.2184
2034-04-03 06:00 | 3458.8 | 1.064 | 76.1734 | 53.895 | 1013.6742
2034-04-04 07:00 | 5517.64 | 1.6951 | 76.0856 | 53.895 | 1617.0607
2034-04-05 08:00 | 3980.41 | 1.2715 | 75.7151 | 53.895 | 1166.543
2034-04-06 09:00 | 4283.42 | 1.3321 | 76.0101 | 53.895 | 1255.3465
2034-04-07 10:00 | 5158.98 | 1.6457 | 75.5861 | 53.895 | 1511.9478
2034-04-08 11:00 | 6480.63 | 2.1061 | 75.4178 | 53.895 | 1899.2852
2034-04-09 12:00 | 7289.88 | 2.3916 | 75.4802 | 53.895 | 2136.4529
2034-04-10 13:00 | 8358.26 | 2.8769 | 74.9592 | 53.895 | 2449.5642
2034-04-11 14:00 | 9863.03 | 3.4552 | 74.9377 | 53.895 | 2890.5688
2034-04-12 15:00 | 11494.4 | 3.8436 | 75.869 | 53.895 | 3368.6761
2034-04-13 16:00 | 14211.3 | 4.9118 | 75.7743 | 53.895 | 4164.9209
2034-04-14 17:00 | 14096.4 | 4.5035 | 77.4334 | 53.895 | 4131.247
2034-04-15 18:00 | 12164.9 | 4.0176 | 77.2985 | 53.895 | 3565.1803
2034-04-16 19:00 | 10369.3 | 3.3339 | 77.6872 | 53.895 | 3038.9418
2034-04-17 20:00 | 8912.88 | 2.7982 | 77.931 | 53.895 | 2612.1073
2034-04-18 21:00 | 7757.66 | 2.3884 | 78.0662 | 53.895 | 2273.5457
2034-04-19 22:00 | 6876.12 | 2.1202 | 77.8271 | 53.895 | 2015.1918
2034-04-20 23:00 | 3433.04 | 1.0177 | 78.2265 | 53.895 | 1006.1247
2034-04-22 | 3211.31 | 1 | 84.7034 | 53.895 | 941.1421
2034-04-23 01:00 | 3122.3 | 1 | 61.0479 | 53.895 | 915.0558
2034-04-24 02:00 | 3007.9 | 1 | 60.8733 | 53.895 | 881.5285
2034-04-25 03:00 | 3126.33 | 1 | 60.6547 | 53.895 | 916.2369
2034-04-26 04:00 | 2546.9 | 1 | 60.5711 | 53.895 | 746.4227
2034-04-27 05:00 | 2048.88 | 1 | 60.4697 | 53.895 | 600.4675
2034-04-28 06:00 | 3269.39 | 1 | 81.687 | 53.895 | 958.1636
2034-04-29 07:00 | 4729.39 | 1.4771 | 75.5753 | 53.895 | 1386.0474
2034-04-30 08:00 | 5418.47 | 1.6326 | 76.2902 | 53.895 | 1587.9968
2034-05-01 09:00 | 6726.49 | 2.2589 | 74.8186 | 53.895 | 1971.3396
2034-05-02 10:00 | 7976.26 | 2.8817 | 74.0598 | 53.895 | 2337.6111
2034-05-03 11:00 | 10350.3 | 3.4703 | 75.3812 | 53.895 | 3033.3735
2034-05-04 12:00 | 12030.2 | 3.8813 | 76.4013 | 53.895 | 3525.7036
2034-05-05 13:00 | 12012.2 | 3.9486 | 76.6178 | 53.895 | 3520.4283
2034-05-06 14:00 | 13110.1 | 4.169 | 77.3901 | 53.895 | 3842.191
2034-05-07 15:00 | 13442.3 | 4.332 | 77.5271 | 53.895 | 3939.5492
2034-05-08 16:00 | 15725.5 | 5.2703 | 77.242 | 53.895 | 4608.6891
2034-05-09 17:00 | 15039.2 | 4.8581 | 78.2371 | 53.895 | 4407.5544
2034-05-10 18:00 | 13901.2 | 4.4338 | 78.6504 | 53.895 | 4074.0396
2034-05-11 19:00 | 12007.8 | 3.7517 | 79.0145 | 53.895 | 3519.1388
2034-05-12 20:00 | 10449.2 | 3.2994 | 78.75 | 53.895 | 3062.3582
2034-05-13 21:00 | 9174.28 | 2.8595 | 78.7674 | 53.895 | 2688.7161
2034-05-14 22:00 | 7964.16 | 2.551 | 78.1221 | 53.895 | 2334.0649
2034-05-15 23:00 | 5640.03 | 1.6079 | 79.6714 | 53.895 | 1652.9296
2034-05-17 | 4665.9 | 1.4288 | 78.0963 | 53.895 | 1367.4403
2034-05-18 01:00 | 4060.06 | 1.2488 | 77.6693 | 53.895 | 1189.8861
2034-05-19 02:00 | 3864.04 | 1.2062 | 77.1512 | 53.895 | 1132.4383
2034-05-20 03:00 | 3729.22 | 1.1752 | 76.7742 | 53.895 | 1092.9265
2034-05-21 04:00 | 3806.43 | 1.2143 | 76.3761 | 53.895 | 1115.5545
2034-05-22 05:00 | 4670.47 | 1.4846 | 76.2903 | 53.895 | 1368.7796
2034-05-23 06:00 | 5631.59 | 1.8178 | 76.0542 | 53.895 | 1650.4561
2034-05-24 07:00 | 6711.83 | 2.2645 | 75.5036 | 53.895 | 1967.0432
2034-05-25 08:00 | 7484.44 | 2.5196 | 75.6928 | 53.895 | 2193.4728
2034-05-26 09:00 | 9430.57 | 3.0949 | 76.2188 | 53.895 | 2763.8272
2034-05-27 10:00 | 10827.2 | 3.6415 | 76.2069 | 53.895 | 3173.1391
2034-05-28 11:00 | 12458.5 | 4.046 | 77.0727 | 53.895 | 3651.2259
2034-05-29 12:00 | 12987.6 | 4.3133 | 77.1737 | 53.895 | 3806.2898
2034-05-30 13:00 | 14025.7 | 4.5104 | 77.9725 | 53.895 | 4110.5269
2034-05-31 14:00 | 14339.4 | 4.7442 | 77.9295 | 53.895 | 4202.4633
2034-06-01 15:00 | 15762.5 | 5.2343 | 78.1603 | 53.895 | 4619.5327
2034-06-02 16:00 | 16178 | 5.323 | 78.6536 | 53.895 | 4741.3038
2034-06-03 17:00 | 16294.8 | 5.239 | 79.2799 | 53.895 | 4775.5345
2034-06-04 18:00 | 14836.7 | 4.7069 | 79.7165 | 53.895 | 4348.2075
2034-06-05 19:00 | 12793.2 | 4.0499 | 79.7777 | 53.895 | 3749.3168
2034-06-06 20:00 | 9979.45 | 3.1404 | 79.719 | 53.895 | 2924.6881
2034-06-07 21:00 | 8538.1 | 2.6389 | 79.6018 | 53.895 | 2502.2701
2034-06-08 22:00 | 6524.93 | 1.9755 | 79.5514 | 53.895 | 1912.2682
2034-06-09 23:00 | 5429.88 | 1.6248 | 79.2814 | 53.895 | 1591.3407
2034-06-11 | 4518.79 | 1.4084 | 78.25 | 53.895 | 1324.3266
2034-06-12 01:00 | 4046.63 | 1.2272 | 78.2995 | 53.895 | 1185.9502
2034-06-13 02:00 | 3735.69 | 1.2059 | 77.0761 | 53.895 | 1094.8227
2034-06-14 03:00 | 3617.33 | 1.1313 | 77.2837 | 53.895 | 1060.1348
2034-06-15 04:00 | 3693.62 | 1.155 | 77.0793 | 53.895 | 1082.4932
2034-06-16 05:00 | 4542 | 1.4527 | 76.5793 | 53.895 | 1331.1288
2034-06-17 06:00 | 5630.45 | 1.8489 | 76.1623 | 53.895 | 1650.122
2034-06-18 07:00 | 6875.25 | 2.2102 | 76.5397 | 53.895 | 2014.9369
2034-06-19 08:00 | 7337.74 | 2.3958 | 76.4895 | 53.895 | 2150.4793
2034-06-20 09:00 | 8901.94 | 2.9951 | 76.1949 | 53.895 | 2608.9011
2034-06-21 10:00 | 10397.8 | 3.5335 | 76.3236 | 53.895 | 3047.2944
2034-06-22 11:00 | 12298.2 | 4.1971 | 76.5962 | 53.895 | 3604.2466
2034-06-23 12:00 | 13334 | 4.4086 | 77.4596 | 53.895 | 3907.8096
2034-06-24 13:00 | 13911.2 | 4.4814 | 78.2126 | 53.895 | 4076.9703
2034-06-25 14:00 | 14499.1 | 4.7574 | 78.2743 | 53.895 | 4249.2668
2034-06-26 15:00 | 16408.3 | 5.3635 | 78.6188 | 53.895 | 4808.798
2034-06-27 16:00 | 16673.5 | 5.3747 | 79.264 | 53.895 | 4886.5205
2034-06-28 17:00 | 16654.5 | 5.3549 | 79.6148 | 53.895 | 4880.9521
2034-06-29 18:00 | 15303.5 | 4.7657 | 80.313 | 53.895 | 4485.0131
2034-06-30 19:00 | 13099.4 | 4.1019 | 80.2769 | 53.895 | 3839.0552
2034-07-01 20:00 | 10298.8 | 3.1605 | 80.4364 | 53.895 | 3018.2803
2034-07-02 21:00 | 8880.93 | 2.7698 | 79.8065 | 53.895 | 2602.7437
2034-07-03 22:00 | 6728.8 | 1.9954 | 80.2343 | 53.895 | 1972.0166
2034-07-04 23:00 | 5703.81 | 1.7319 | 79.4012 | 53.895 | 1671.6217
2034-07-06 | 5146.85 | 1.6099 | 78.5399 | 53.895 | 1508.3928
2034-07-07 01:00 | 4547.33 | 1.4343 | 78.0993 | 53.895 | 1332.6909
2034-07-08 02:00 | 4031.68 | 1.283 | 77.6916 | 53.895 | 1181.5688
2034-07-09 03:00 | 3909.97 | 1.2581 | 77.2474 | 53.895 | 1145.8991
2034-07-10 04:00 | 3993.16 | 1.2975 | 76.8944 | 53.895 | 1170.2797
2034-07-11 05:00 | 4672.57 | 1.5015 | 76.8881 | 53.895 | 1369.3951
2034-07-12 06:00 | 5512.75 | 1.7456 | 77.0364 | 53.895 | 1615.6275
2034-07-13 07:00 | 6127.38 | 1.9844 | 76.7298 | 53.895 | 1795.7578
2034-07-14 08:00 | 6550.47 | 2.0711 | 77.153 | 53.895 | 1919.7533
2034-07-15 09:00 | 8177.73 | 2.7508 | 76.3295 | 53.895 | 2396.6561
2034-07-16 10:00 | 9259.74 | 2.9836 | 77.1784 | 53.895 | 2713.7619
2034-07-17 11:00 | 10078.1 | 3.275 | 77.3064 | 53.895 | 2953.5996
2034-07-18 12:00 | 10850.9 | 3.6251 | 77.1396 | 53.895 | 3180.0849
2034-07-19 13:00 | 10805.3 | 3.4872 | 77.8672 | 53.895 | 3166.7208
2034-07-20 14:00 | 11541.9 | 3.7214 | 78.0293 | 53.895 | 3382.597
2034-07-21 15:00 | 12778.4 | 4.147 | 78.1027 | 53.895 | 3744.9794
2034-07-22 16:00 | 12739.2 | 4.1152 | 78.4285 | 53.895 | 3733.491
2034-07-23 17:00 | 12298.5 | 3.9767 | 78.5596 | 53.895 | 3604.3346
2034-07-24 18:00 | 11294.9 | 3.6113 | 78.7692 | 53.895 | 3310.2084
2034-07-25 19:00 | 9888.42 | 3.1572 | 78.7515 | 53.895 | 2898.0098
2034-07-26 20:00 | 7629.61 | 2.3208 | 79.3419 | 53.895 | 2236.018
2034-07-27 21:00 | 6406.85 | 2.0094 | 78.5319 | 53.895 | 1877.6624
2034-07-28 22:00 | 4394.89 | 1.3236 | 78.8256 | 53.895 | 1288.0151
2034-07-29 23:00 | 3423.92 | 1.0775 | 77.7252 | 53.895 | 1003.4519
2034-07-31 | 3075.33 | 1 | 78.2637 | 53.895 | 901.2903
2034-08-01 01:00 | 3153.54 | 1 | 83.2222 | 53.895 | 924.2113
2034-08-02 02:00 | 3087.51 | 1 | 61.4527 | 53.895 | 904.8599
2034-08-03 03:00 | 3110.22 | 1 | 83.3035 | 53.895 | 911.5155
2034-08-04 04:00 | 3208.68 | 1 | 80.2936 | 53.895 | 940.3713
2034-08-05 05:00 | 3423.12 | 1.1016 | 76.113 | 53.895 | 1003.2174
2034-08-06 06:00 | 4262.93 | 1.3276 | 76.5341 | 53.895 | 1249.3415
2034-08-07 07:00 | 5603.78 | 1.7837 | 76.2271 | 53.895 | 1642.3058
2034-08-08 08:00 | 6674.75 | 2.0737 | 76.7465 | 53.895 | 1956.1761
2034-08-09 09:00 | 8940.58 | 2.8287 | 76.6621 | 53.895 | 2620.2253
2034-08-10 10:00 | 10699.3 | 3.5933 | 76.1876 | 53.895 | 3135.6553
2034-08-11 11:00 | 12611.2 | 4.1406 | 76.9489 | 53.895 | 3695.9779
2034-08-12 12:00 | 13843.6 | 4.5337 | 77.48 | 53.895 | 4057.1587
2034-08-13 13:00 | 14923 | 4.7329 | 78.4101 | 53.895 | 4373.4996
2034-08-14 14:00 | 15292.1 | 5.0625 | 78.2386 | 53.895 | 4481.6721
2034-08-15 15:00 | 17462 | 5.6038 | 79.0188 | 53.895 | 5117.607
2034-08-16 16:00 | 17248.6 | 5.8075 | 78.8502 | 53.895 | 5055.0657
2034-08-17 17:00 | 17596.4 | 5.6784 | 79.7788 | 53.895 | 5156.9958
2034-08-18 18:00 | 15660.2 | 5.0425 | 80.1065 | 53.895 | 4589.5516
2034-08-19 19:00 | 13665 | 4.3277 | 80.3762 | 53.895 | 4004.8162
2034-08-20 20:00 | 10878.4 | 3.342 | 80.7077 | 53.895 | 3188.1443
2034-08-21 21:00 | 9632.89 | 2.981 | 80.2287 | 53.895 | 2823.1214
2034-08-22 22:00 | 7673.94 | 2.2984 | 80.424 | 53.895 | 2249.0098
2034-08-23 23:00 | 7479.75 | 2.2348 | 80.0408 | 53.895 | 2192.0983
2034-08-25 | 6365.73 | 2.001 | 78.9971 | 53.895 | 1865.6113
2034-08-26 01:00 | 6323.24 | 1.8982 | 79.3919 | 53.895 | 1853.1587
2034-08-27 02:00 | 5801.27 | 1.8731 | 78.1037 | 53.895 | 1700.1844
2034-08-28 03:00 | 5151.66 | 1.8101 | 76.7158 | 53.895 | 1509.8025
2034-08-29 04:00 | 4947.78 | 1.6594 | 77.1244 | 53.895 | 1450.0512
2034-08-30 05:00 | 5376.6 | 1.797 | 76.9622 | 53.895 | 1575.7259
2034-08-31 06:00 | 5713.88 | 1.865 | 77.2075 | 53.895 | 1674.5729
2034-09-01 07:00 | 6743.55 | 2.1789 | 77.2968 | 53.895 | 1976.3394
2034-09-02 08:00 | 6934.9 | 2.2201 | 77.5076 | 53.895 | 2032.4186
2034-09-03 09:00 | 7932.02 | 2.6378 | 77.0014 | 53.895 | 2324.6456
2034-09-04 10:00 | 9796.37 | 3.2141 | 77.3207 | 53.895 | 2871.0326
2034-09-05 11:00 | 11709.4 | 3.8335 | 77.6293 | 53.895 | 3431.6864
2034-09-06 12:00 | 13470.9 | 4.385 | 78.095 | 53.895 | 3947.9311
2034-09-07 13:00 | 14584.6 | 4.6717 | 78.7475 | 53.895 | 4274.3243
2034-09-08 14:00 | 15633.2 | 5.1118 | 78.8527 | 53.895 | 4581.6387
2034-09-09 15:00 | 17129.7 | 5.7374 | 78.9007 | 53.895 | 5020.2195
2034-09-10 16:00 | 17546.7 | 5.6512 | 79.9111 | 53.895 | 5142.4301
2034-09-11 17:00 | 17145.4 | 5.3849 | 80.6309 | 53.895 | 5024.8207
2034-09-12 18:00 | 15317.6 | 4.825 | 80.8009 | 53.895 | 4489.1454
2034-09-13 19:00 | 12543.2 | 4.1357 | 80.1224 | 53.895 | 3676.049
2034-09-14 20:00 | 10026.8 | 3.1354 | 80.6438 | 53.895 | 2938.565
2034-09-15 21:00 | 8549.66 | 2.6737 | 80.2456 | 53.895 | 2505.658
2034-09-16 22:00 | 6645.44 | 1.9687 | 80.7092 | 53.895 | 1947.5862
2034-09-17 23:00 | 4900.85 | 1.4752 | 80.001 | 53.895 | 1436.2974
2034-09-19 | 4180.2 | 1.3289 | 78.6722 | 53.895 | 1225.0957
2034-09-20 01:00 | 3358.79 | 1.0857 | 78.0331 | 53.895 | 984.3642
2034-09-21 02:00 | 3067.51 | 1 | 79.3585 | 53.895 | 898.9984
2034-09-22 03:00 | 3154.78 | 1 | 82.1931 | 53.895 | 924.5748
2034-09-23 04:00 | 3116.25 | 1 | 83.293 | 53.895 | 913.2827
2034-09-24 05:00 | 3312.38 | 1 | 84.3511 | 53.895 | 970.7628
2034-09-25 06:00 | 4695.31 | 1.4906 | 77.0246 | 53.895 | 1376.0595
2034-09-26 07:00 | 6145.08 | 2.0371 | 76.4621 | 53.895 | 1800.9452
2034-09-27 08:00 | 5997.68 | 1.9623 | 76.8337 | 53.895 | 1757.7465
2034-09-28 09:00 | 6364.07 | 2.141 | 76.4838 | 53.895 | 1865.1248
2034-09-29 10:00 | 7744.54 | 2.6325 | 76.3913 | 53.895 | 2269.7006
2034-09-30 11:00 | 8830.84 | 2.8614 | 77.2704 | 53.895 | 2588.0637
2034-10-01 12:00 | 9206.28 | 2.8834 | 77.9896 | 53.895 | 2698.0943
2034-10-02 13:00 | 9109.67 | 2.974 | 77.5208 | 53.895 | 2669.7807
2034-10-03 14:00 | 9743.17 | 3.1132 | 77.9027 | 53.895 | 2855.4413
2034-10-04 15:00 | 9713.89 | 3.1602 | 77.7575 | 53.895 | 2846.8601
2034-10-05 16:00 | 11841.8 | 4.0082 | 77.2445 | 53.895 | 3470.489
2034-10-06 17:00 | 11101.9 | 3.5555 | 78.3103 | 53.895 | 3253.6457
2034-10-07 18:00 | 9774.67 | 3.1779 | 78.166 | 53.895 | 2864.673
2034-10-08 19:00 | 8910.88 | 2.7813 | 78.6581 | 53.895 | 2611.5211
2034-10-09 20:00 | 7728.36 | 2.4329 | 78.4227 | 53.895 | 2264.9587
2034-10-10 21:00 | 6783.46 | 2.1635 | 78.0736 | 53.895 | 1988.0359
2034-10-11 22:00 | 5879.65 | 1.891 | 77.7267 | 53.895 | 1723.1553
2034-10-12 23:00 | 3076 | 1 | 80.5449 | 53.895 | 901.4866
2034-10-14 | 3092.65 | 1 | 61.9366 | 53.895 | 906.3662
2034-10-15 01:00 | 3062.35 | 1 | 61.6688 | 53.895 | 897.4862
2034-10-16 02:00 | 2473.71 | 1 | 61.5955 | 53.895 | 724.9728
2034-10-17 03:00 | 882.613 | 1 | 61.6443 | 53.895 | 258.6683
2034-10-18 04:00 | -65.0982 | 0.82734 | 61.0318 | 53.895 | -19.0784
2034-10-19 05:00 | -259.626 | 1.3177 | 60.1267 | 53.895 | -76.0889
2034-10-20 06:00 | 2027.62 | 1 | 60.4304 | 53.895 | 594.2368
2034-10-21 07:00 | 2939.82 | 1 | 81.6036 | 53.895 | 861.5762
2034-10-22 08:00 | 3074.88 | 1 | 60.3676 | 53.895 | 901.1584
2034-10-23 09:00 | 3123.56 | 1 | 60.3769 | 53.895 | 915.4251
2034-10-24 10:00 | 3691.05 | 1.1782 | 75.6063 | 53.895 | 1081.74
2034-10-25 11:00 | 4872.12 | 1.5281 | 75.8992 | 53.895 | 1427.8774
2034-10-26 12:00 | 5763.56 | 1.8837 | 75.4323 | 53.895 | 1689.1327
2034-10-27 13:00 | 6403.18 | 2.1443 | 75.236 | 53.895 | 1876.5868
2034-10-28 14:00 | 7622.79 | 2.5049 | 75.6391 | 53.895 | 2234.0192
2034-10-29 15:00 | 8654.13 | 2.892 | 75.637 | 53.895 | 2536.2751
2034-10-30 16:00 | 11905.6 | 3.9894 | 75.8554 | 53.895 | 3489.1869
2034-10-31 17:00 | 11033.4 | 3.5878 | 76.8483 | 53.895 | 3233.5703
2034-11-01 18:00 | 9910.61 | 3.1955 | 77.2019 | 53.895 | 2904.5131
2034-11-02 19:00 | 8267.1 | 2.6092 | 77.5467 | 53.895 | 2422.8478
2034-11-03 20:00 | 7017.26 | 2.2051 | 77.5115 | 53.895 | 2056.5559
2034-11-04 21:00 | 6145.46 | 1.8908 | 77.6834 | 53.895 | 1801.0565
2034-11-05 22:00 | 5107.38 | 1.6238 | 76.9951 | 53.895 | 1496.8253
2034-11-06 23:00 | 3106.11 | 1 | 81.6841 | 53.895 | 910.311
2034-11-08 | 3086.53 | 1 | 61.165 | 53.895 | 904.5726
2034-11-09 01:00 | 3067.21 | 1 | 60.9708 | 53.895 | 898.9105
2034-11-10 02:00 | 3048.18 | 1 | 60.8477 | 53.895 | 893.3334
2034-11-11 03:00 | 3086.08 | 1 | 60.7294 | 53.895 | 904.4408
2034-11-12 04:00 | 3171.82 | 1 | 60.6022 | 53.895 | 929.5687
2034-11-13 05:00 | 3121.43 | 1 | 60.5589 | 53.895 | 914.8008
2034-11-14 06:00 | 3137.32 | 1 | 60.4864 | 53.895 | 919.4577
2034-11-15 07:00 | 3193.62 | 1 | 78.3104 | 53.895 | 935.9576
2034-11-16 08:00 | 3381.64 | 1.0851 | 75.4959 | 53.895 | 991.0609
2034-11-17 09:00 | 5291.65 | 1.7028 | 75.4336 | 53.895 | 1550.8295
2034-11-18 10:00 | 7047.43 | 2.3834 | 74.9267 | 53.895 | 2065.3979
2034-11-19 11:00 | 8653.36 | 2.8761 | 75.4916 | 53.895 | 2536.0495
2034-11-20 12:00 | 10297.3 | 3.3641 | 76.0962 | 53.895 | 3017.8407
2034-11-21 13:00 | 11298.9 | 3.6337 | 76.7464 | 53.895 | 3311.3807
2034-11-22 14:00 | 11561.8 | 3.7805 | 76.9083 | 53.895 | 3388.4291
2034-11-23 15:00 | 13539.5 | 4.4982 | 76.9594 | 53.895 | 3968.0358
2034-11-24 16:00 | 13891.5 | 4.5614 | 77.547 | 53.895 | 4071.1968
2034-11-25 17:00 | 13736.5 | 4.419 | 78.1724 | 53.895 | 4025.7708
2034-11-26 18:00 | 12252.3 | 3.9026 | 78.5322 | 53.895 | 3590.7947
2034-11-27 19:00 | 10267.2 | 3.2613 | 78.5959 | 53.895 | 3009.0193
2034-11-28 20:00 | 7883.56 | 2.4032 | 79.0821 | 53.895 | 2310.4434
2034-11-29 21:00 | 6640.39 | 2.0116 | 78.8429 | 53.895 | 1946.1062
2034-11-30 22:00 | 4236.29 | 1.3089 | 78.2274 | 53.895 | 1241.534
2034-12-01 23:00 | 3212.5 | 1.0054 | 77.5634 | 53.895 | 941.4908
2034-12-03 | 3164.42 | 1 | 82.1396 | 53.895 | 927.4
2034-12-04 01:00 | 3087.01 | 1 | 61.3855 | 53.895 | 904.7133
2034-12-05 02:00 | 2982.9 | 1 | 61.2143 | 53.895 | 874.2017
2034-12-06 03:00 | 3127.83 | 1 | 60.9954 | 53.895 | 916.6765
2034-12-07 04:00 | 3099.89 | 1 | 60.8817 | 53.895 | 908.4881
2034-12-08 05:00 | 3135.64 | 1 | 60.7715 | 53.895 | 918.9654
2034-12-09 06:00 | 3166.63 | 1 | 83.5187 | 53.895 | 928.0476
2034-12-10 07:00 | 4016.63 | 1.2156 | 76.5821 | 53.895 | 1177.1581
2034-12-11 08:00 | 5014.28 | 1.567 | 76.1586 | 53.895 | 1469.5404
2034-12-12 09:00 | 7170.57 | 2.3328 | 75.6907 | 53.895 | 2101.4866
2034-12-13 10:00 | 8917.96 | 3.1908 | 74.7094 | 53.895 | 2613.5961
2034-12-14 11:00 | 10932.3 | 3.727 | 75.7504 | 53.895 | 3203.9409
2034-12-15 12:00 | 11934.8 | 4.0092 | 76.4263 | 53.895 | 3497.7446
2034-12-16 13:00 | 12533.1 | 4.1489 | 77.0464 | 53.895 | 3673.089
2034-12-17 14:00 | 13440.5 | 4.3081 | 77.8568 | 53.895 | 3939.0217
2034-12-18 15:00 | 15040.1 | 4.8442 | 78.1188 | 53.895 | 4407.8182
2034-12-19 16:00 | 15346.6 | 5.0026 | 78.3699 | 53.895 | 4497.6445
2034-12-20 17:00 | 15500.8 | 4.9285 | 79.0455 | 53.895 | 4542.836
2034-12-21 18:00 | 13894.9 | 4.3404 | 79.5745 | 53.895 | 4072.1932
2034-12-22 19:00 | 11503.4 | 3.6728 | 79.302 | 53.895 | 3371.3137
2034-12-23 20:00 | 8772.81 | 2.7505 | 79.3979 | 53.895 | 2571.0568
2034-12-24 21:00 | 7401.75 | 2.2514 | 79.4685 | 53.895 | 2169.2388
2034-12-25 22:00 | 5171.12 | 1.5164 | 79.697 | 53.895 | 1515.5057
2034-12-26 23:00 | 3831.11 | 1.16 | 78.7144 | 53.895 | 1122.7875
2034-12-28 | 3091.76 | 1 | 77.7698 | 53.895 | 906.1054
2034-12-29 01:00 | 3088.09 | 1 | 83.2208 | 53.895 | 905.0298
2034-12-30 02:00 | 3083.41 | 1 | 82.96 | 53.895 | 903.6583
2034-12-31 03:00 | 3108.85 | 1 | 81.1956 | 53.895 | 911.114
2035-01-01 04:00 | 3081.21 | 1 | 80.3228 | 53.895 | 903.0135
2035-01-02 05:00 | 3328.93 | 1.033 | 76.7248 | 53.895 | 975.6131
2035-01-03 06:00 | 3727.92 | 1.1649 | 76.5412 | 53.895 | 1092.5455
2035-01-04 07:00 | 4599.82 | 1.4319 | 76.5641 | 53.895 | 1348.0742
2035-01-05 08:00 | 4995.65 | 1.5662 | 76.5276 | 53.895 | 1464.0805
2035-01-06 09:00 | 6189.38 | 2.0157 | 76.0257 | 53.895 | 1813.9282
2035-01-07 10:00 | 7328.81 | 2.36 | 76.3517 | 53.895 | 2147.8622
2035-01-08 11:00 | 8752.97 | 2.8017 | 76.6582 | 53.895 | 2565.2423
2035-01-09 12:00 | 9132.75 | 2.9837 | 76.6541 | 53.895 | 2676.5448
2035-01-10 13:00 | 10074.9 | 3.3662 | 76.5413 | 53.895 | 2952.6617
2035-01-11 14:00 | 10439.3 | 3.3985 | 77.1552 | 53.895 | 3059.4568
2035-01-12 15:00 | 11480.6 | 3.906 | 76.7213 | 53.895 | 3364.6317
2035-01-13 16:00 | 12748.8 | 4.2849 | 77.1294 | 53.895 | 3736.3045
2035-01-14 17:00 | 13080.8 | 4.2027 | 78.0731 | 53.895 | 3833.6041
2035-01-15 18:00 | 11729 | 3.6666 | 78.7308 | 53.895 | 3437.4306
2035-01-16 19:00 | 10641.7 | 3.3045 | 78.8523 | 53.895 | 3118.7744
2035-01-17 20:00 | 8678.27 | 2.5958 | 79.3894 | 53.895 | 2543.3499
2035-01-18 21:00 | 7861.06 | 2.3979 | 78.8767 | 53.895 | 2303.8493
2035-01-19 22:00 | 6094.67 | 1.7686 | 79.4736 | 53.895 | 1786.1715
2035-01-20 23:00 | 5059.12 | 1.5766 | 78.049 | 53.895 | 1482.6817
2035-01-22 | 4565.3 | 1.4301 | 77.674 | 53.895 | 1337.9574
2035-01-23 01:00 | 4007.26 | 1.2962 | 76.965 | 53.895 | 1174.412
2035-01-24 02:00 | 3765.01 | 1.2053 | 76.9045 | 53.895 | 1103.4155
2035-01-25 03:00 | 3787.63 | 1.2323 | 76.4781 | 53.895 | 1110.0448
2035-01-26 04:00 | 3932.09 | 1.2608 | 76.5552 | 53.895 | 1152.3818
2035-01-27 05:00 | 5115.73 | 1.5696 | 77.1144 | 53.895 | 1499.2725
2035-01-28 06:00 | 5378.05 | 1.6606 | 77.0788 | 53.895 | 1576.1509
2035-01-29 07:00 | 5840.99 | 1.8438 | 76.7919 | 53.895 | 1711.8252
2035-01-30 08:00 | 4881.58 | 1.5225 | 77.0474 | 53.895 | 1430.6499
2035-01-31 09:00 | 5624 | 1.7745 | 76.7877 | 53.895 | 1648.2317
2035-02-01 10:00 | 6478.45 | 2.2388 | 75.5413 | 53.895 | 1898.6463
2035-02-02 11:00 | 7839.78 | 2.6126 | 76.1544 | 53.895 | 2297.6127
2035-02-03 12:00 | 8495.42 | 2.8153 | 76.4387 | 53.895 | 2489.7618
2035-02-04 13:00 | 9516.84 | 3.1726 | 76.5329 | 53.895 | 2789.1105
2035-02-05 14:00 | 11042.8 | 3.7191 | 76.6326 | 53.895 | 3236.3252
2035-02-06 15:00 | 13258 | 4.4555 | 76.9906 | 53.895 | 3885.5362
2035-02-07 16:00 | 13702.3 | 4.5878 | 77.5095 | 53.895 | 4015.7477
2035-02-08 17:00 | 13325.7 | 4.4813 | 77.7711 | 53.895 | 3905.3772
2035-02-09 18:00 | 11767.7 | 3.6985 | 78.9302 | 53.895 | 3448.7724
2035-02-10 19:00 | 9254.86 | 3.0522 | 78.2195 | 53.895 | 2712.3317
2035-02-11 20:00 | 6744.08 | 1.9972 | 79.6042 | 53.895 | 1976.4947
2035-02-12 21:00 | 5432 | 1.6388 | 78.8999 | 53.895 | 1591.9621
2035-02-13 22:00 | 3181.9 | 1 | 80.1825 | 53.895 | 932.5228
2035-02-14 23:00 | 3132.19 | 1 | 61.9935 | 53.895 | 917.9543
2035-02-16 | 3093.59 | 1 | 61.6908 | 53.895 | 906.6417
2035-02-17 01:00 | 3062.45 | 1 | 61.4929 | 53.895 | 897.5155
2035-02-18 02:00 | 3129.22 | 1 | 61.3158 | 53.895 | 917.0839
2035-02-19 03:00 | 3217.88 | 1 | 61.1499 | 53.895 | 943.0675
2035-02-20 04:00 | 3145.67 | 1 | 61.0617 | 53.895 | 921.9049
2035-02-21 05:00 | 3164.99 | 1 | 82.0355 | 53.895 | 927.567
2035-02-22 06:00 | 3198.05 | 1 | 79.4396 | 53.895 | 937.2559
2035-02-23 07:00 | 3143.4 | 1 | 76.7392 | 53.895 | 921.2396
2035-02-24 08:00 | 3161.08 | 1 | 80.08 | 53.895 | 926.4211
2035-02-25 09:00 | 3859.96 | 1.2139 | 76.0643 | 53.895 | 1131.2426
2035-02-26 10:00 | 4865.21 | 1.6021 | 75.4485 | 53.895 | 1425.8523
2035-02-27 11:00 | 5917.28 | 1.9494 | 75.5624 | 53.895 | 1734.1836
2035-02-28 12:00 | 6522.6 | 2.1849 | 75.4975 | 53.895 | 1911.5854
2035-03-01 13:00 | 7424.32 | 2.424 | 76.0094 | 53.895 | 2175.8534
2035-03-02 14:00 | 8867.45 | 2.9888 | 75.7431 | 53.895 | 2598.7931
2035-03-03 15:00 | 10674.6 | 3.6014 | 75.9919 | 53.895 | 3128.4164
2035-03-04 16:00 | 11548.3 | 3.8229 | 76.6183 | 53.895 | 3384.4726
2035-03-05 17:00 | 11026.1 | 3.6688 | 76.8594 | 53.895 | 3231.4309
2035-03-06 18:00 | 9845.19 | 3.1078 | 77.7733 | 53.895 | 2885.3404
2035-03-07 19:00 | 8410.68 | 2.6206 | 77.9751 | 53.895 | 2464.927
2035-03-08 20:00 | 6102.41 | 1.7923 | 78.7948 | 53.895 | 1788.4398
2035-03-09 21:00 | 4728.61 | 1.4638 | 77.6705 | 53.895 | 1385.8188
2035-03-10 22:00 | 3060.73 | 1 | 82.2104 | 53.895 | 897.0114
2035-03-11 23:00 | 2943.74 | 1 | 61.3457 | 53.895 | 862.725
2035-03-13 | 1193.54 | 1 | 61.4063 | 53.895 | 349.792
2035-03-14 01:00 | -23.2083 | 0.72467 | 61.0753 | 53.895 | -6.8017
2035-03-15 02:00 | -274.975 | 1.3711 | 59.8742 | 53.895 | -80.5872
2035-03-16 03:00 | -473.13 | 1.8852 | 59.3233 | 53.895 | -138.6607
2035-03-17 04:00 | -640.408 | 2.3243 | 58.9462 | 53.895 | -187.6851
2035-03-18 05:00 | -797.77 | 2.7448 | 58.6148 | 53.895 | -233.8033
2035-03-19 06:00 | 16.7918 | 1 | 59.7569 | 53.895 | 4.9212
2035-03-20 07:00 | 2179.56 | 1 | 59.3174 | 53.895 | 638.766
2035-03-21 08:00 | 2824.67 | 1 | 59.4019 | 53.895 | 827.8291
2035-03-22 09:00 | 3102.74 | 1 | 77.6872 | 53.895 | 909.3233
2035-03-23 10:00 | 4832.09 | 1.5386 | 74.8075 | 53.895 | 1416.1458
2035-03-24 11:00 | 6623.31 | 2.2181 | 74.3445 | 53.895 | 1941.1005
2035-03-25 12:00 | 8049.75 | 2.6526 | 74.9473 | 53.895 | 2359.1488
2035-03-26 13:00 | 8687.55 | 2.9313 | 74.9802 | 53.895 | 2546.0696
2035-03-27 14:00 | 9425.41 | 3.0998 | 75.6316 | 53.895 | 2762.315
2035-03-28 15:00 | 9679.95 | 3.1528 | 76.0528 | 53.895 | 2836.9133
2035-03-29 16:00 | 11904.9 | 3.991 | 75.8532 | 53.895 | 3488.9818
2035-03-30 17:00 | 11048.4 | 3.5955 | 76.7038 | 53.895 | 3237.9664
2035-03-31 18:00 | 9790.02 | 3.1662 | 76.9704 | 53.895 | 2869.1716
2035-04-01 19:00 | 8183.35 | 2.5557 | 77.4658 | 53.895 | 2398.3031
2035-04-02 20:00 | 6710.79 | 2.1086 | 77.2499 | 53.895 | 1966.7384
2035-04-03 21:00 | 5722.31 | 1.7741 | 77.2704 | 53.895 | 1677.0435
2035-04-04 22:00 | 4732.22 | 1.5113 | 76.6081 | 53.895 | 1386.8768
2035-04-05 23:00 | 3028.95 | 1 | 61.1918 | 53.895 | 887.6976
2035-04-07 | 3050.66 | 1 | 60.8381 | 53.895 | 894.0602
2035-04-08 01:00 | -50.7144 | 0.78982 | 60.8633 | 53.895 | -14.8629
2035-04-09 02:00 | -288.724 | 1.4079 | 59.6925 | 53.895 | -84.6167
2035-04-10 03:00 | -492.267 | 1.9411 | 59.1037 | 53.895 | -144.2692
2035-04-11 04:00 | -637.252 | 2.3165 | 58.7246 | 53.895 | -186.7601
2035-04-12 05:00 | -737.281 | 2.5774 | 58.4392 | 53.895 | -216.0757
2035-04-13 06:00 | 442.283 | 1 | 59.4789 | 53.895 | 129.6204
2035-04-14 07:00 | 2145.71 | 1 | 73.2435 | 53.895 | 628.8455
2035-04-15 08:00 | 2750.86 | 1 | 76.4869 | 53.895 | 806.1975
2035-04-16 09:00 | 4607.26 | 1.5346 | 73.8845 | 53.895 | 1350.2546
2035-04-17 10:00 | 6962.06 | 2.4444 | 73.4321 | 53.895 | 2040.3784
2035-04-18 11:00 | 8968.93 | 3.0888 | 74.1395 | 53.895 | 2628.5339
2035-04-19 12:00 | 10314.6 | 3.5278 | 74.7167 | 53.895 | 3022.9109
2035-04-20 13:00 | 10935.1 | 3.5802 | 75.7929 | 53.895 | 3204.7615
2035-04-21 14:00 | 11264 | 3.6641 | 76.277 | 53.895 | 3301.1525
2035-04-22 15:00 | 11719.2 | 3.8458 | 76.4649 | 53.895 | 3434.5585
2035-04-23 16:00 | 14360.1 | 4.7268 | 76.684 | 53.895 | 4208.5299
2035-04-24 17:00 | 13108.4 | 4.2248 | 77.5229 | 53.895 | 3841.6928
2035-04-25 18:00 | 11825.5 | 3.7243 | 78.0644 | 53.895 | 3465.7119
2035-04-26 19:00 | 9832.77 | 3.0962 | 78.0797 | 53.895 | 2881.7004
2035-04-27 20:00 | 8416.26 | 2.6539 | 77.9327 | 53.895 | 2466.5623
2035-04-28 21:00 | 7354.35 | 2.2456 | 78.2397 | 53.895 | 2155.3472
2035-04-29 22:00 | 6430.15 | 2.0202 | 77.5678 | 53.895 | 1884.4909
2035-04-30 23:00 | 3311.65 | 1.0157 | 77.7012 | 53.895 | 970.5488
2035-05-02 | 3178.58 | 1 | 61.3663 | 53.895 | 931.5498
2035-05-03 01:00 | 3112.51 | 1 | 61.0817 | 53.895 | 912.1866
2035-05-04 02:00 | 3129.32 | 1 | 60.9014 | 53.895 | 917.1132
2035-05-05 03:00 | 3175.42 | 1 | 60.7456 | 53.895 | 930.6237
2035-05-06 04:00 | 3085.83 | 1 | 60.6137 | 53.895 | 904.3675
2035-05-07 05:00 | 3176.82 | 1 | 83.1487 | 53.895 | 931.034
2035-05-08 06:00 | 3284.85 | 1 | 78.9708 | 53.895 | 962.6945
2035-05-09 07:00 | 4152.26 | 1.2868 | 76.0358 | 53.895 | 1216.9073
2035-05-10 08:00 | 4096.9 | 1.2945 | 75.8156 | 53.895 | 1200.6829
2035-05-11 09:00 | 5738.02 | 1.7424 | 76.4169 | 53.895 | 1681.6477
2035-05-12 10:00 | 8125.45 | 2.6342 | 75.6091 | 53.895 | 2381.3343
2035-05-13 11:00 | 9267.91 | 3.0215 | 75.9306 | 53.895 | 2716.1563
2035-05-14 12:00 | 10032.8 | 3.1975 | 76.6154 | 53.895 | 2940.3234
2035-05-15 13:00 | 10987.7 | 3.5135 | 76.858 | 53.895 | 3220.177
2035-05-16 14:00 | 11633.5 | 3.8446 | 76.7146 | 53.895 | 3409.4423
2035-05-17 15:00 | 13467.8 | 4.515 | 76.8055 | 53.895 | 3947.0226
2035-05-18 16:00 | 14087.1 | 4.5858 | 77.6109 | 53.895 | 4128.5215
2035-05-19 17:00 | 13856.3 | 4.4795 | 78.0492 | 53.895 | 4060.8807
2035-05-20 18:00 | 12255.8 | 3.9323 | 78.3815 | 53.895 | 3591.8204
2035-05-21 19:00 | 10697.9 | 3.4209 | 78.4379 | 53.895 | 3135.245
2035-05-22 20:00 | 8631.35 | 2.6183 | 79.1394 | 53.895 | 2529.599
2035-05-23 21:00 | 7657.9 | 2.3551 | 78.662 | 53.895 | 2244.3089
2035-05-24 22:00 | 5821.52 | 1.7206 | 79.026 | 53.895 | 1706.1191
2035-05-25 23:00 | 4982.13 | 1.5186 | 78.1897 | 53.895 | 1460.1182
2035-05-27 | 4201.93 | 1.3052 | 77.5965 | 53.895 | 1231.4641
2035-05-28 01:00 | 3592.97 | 1.1487 | 76.8962 | 53.895 | 1052.9956
2035-05-29 02:00 | 3335.82 | 1.0864 | 76.382 | 53.895 | 977.6323
2035-05-30 03:00 | 3532.08 | 1.1344 | 76.36 | 53.895 | 1035.1505
2035-05-31 04:00 | 3669.05 | 1.1825 | 76.1754 | 53.895 | 1075.2924
2035-06-01 05:00 | 4483.96 | 1.4249 | 76.2796 | 53.895 | 1314.119
2035-06-02 06:00 | 4772.54 | 1.5271 | 76.1947 | 53.895 | 1398.6934
2035-06-03 07:00 | 5832.67 | 1.8674 | 76.2081 | 53.895 | 1709.3868
2035-06-04 08:00 | 6442.96 | 2.0114 | 76.7219 | 53.895 | 1888.2452
2035-06-05 09:00 | 7520.73 | 2.6029 | 75.3923 | 53.895 | 2204.1084
2035-06-06 10:00 | 9420.14 | 3.1915 | 75.8876 | 53.895 | 2760.7705
2035-06-07 11:00 | 11421.5 | 3.8459 | 76.3111 | 53.895 | 3347.3112
2035-06-08 12:00 | 12649.1 | 4.1893 | 76.994 | 53.895 | 3707.0853
2035-06-09 13:00 | 13088 | 4.3285 | 77.4332 | 53.895 | 3835.7142
2035-06-10 14:00 | 14065.7 | 4.5372 | 78.12 | 53.895 | 4122.2497
2035-06-11 15:00 | 14916.1 | 4.9899 | 77.9519 | 53.895 | 4371.4774
2035-06-12 16:00 | 14772.7 | 4.7828 | 78.7613 | 53.895 | 4329.451
2035-06-13 17:00 | 15088.5 | 4.8344 | 79.1166 | 53.895 | 4422.0028
2035-06-14 18:00 | 13591.1 | 4.2806 | 79.5867 | 53.895 | 3983.1582
2035-06-15 19:00 | 11498.7 | 3.6505 | 79.4884 | 53.895 | 3369.9363
2035-06-16 20:00 | 9123.95 | 2.7718 | 79.9735 | 53.895 | 2673.9658
2035-06-17 21:00 | 7525.35 | 2.3258 | 79.3708 | 53.895 | 2205.4624
2035-06-18 22:00 | 5810.65 | 1.6732 | 80.1318 | 53.895 | 1702.9334
2035-06-19 23:00 | 4688.26 | 1.4885 | 78.1977 | 53.895 | 1373.9934
2035-06-21 | 3881.48 | 1.2607 | 77.4712 | 53.895 | 1137.5495
2035-06-22 01:00 | 3076.38 | 1 | 77.3015 | 53.895 | 901.598
2035-06-23 02:00 | 3121.13 | 1 | 80.1274 | 53.895 | 914.7129
2035-06-24 03:00 | 3150.61 | 1 | 79.1936 | 53.895 | 923.3526
2035-06-25 04:00 | 3114.3 | 1 | 78.4706 | 53.895 | 912.7112
2035-06-26 05:00 | 3605.94 | 1.1452 | 76.563 | 53.895 | 1056.7967
2035-06-27 06:00 | 3929.84 | 1.2389 | 76.6046 | 53.895 | 1151.7224
2035-06-28 07:00 | 5032.23 | 1.5986 | 76.4598 | 53.895 | 1474.801
2035-06-29 08:00 | 5472.16 | 1.7127 | 76.7747 | 53.895 | 1603.7318
2035-06-30 09:00 | 7344.09 | 2.4129 | 76.1465 | 53.895 | 2152.3403
2035-07-01 10:00 | 9542.36 | 3.1481 | 76.3429 | 53.895 | 2796.5897
2035-07-02 11:00 | 11548.8 | 3.8851 | 76.4691 | 53.895 | 3384.6192
2035-07-03 12:00 | 13245.1 | 4.3186 | 77.3805 | 53.895 | 3881.7556
2035-07-04 13:00 | 13919.5 | 4.5272 | 77.906 | 53.895 | 4079.4028
2035-07-05 14:00 | 14607.7 | 4.7621 | 78.2786 | 53.895 | 4281.0943
2035-07-06 15:00 | 15940.9 | 5.2557 | 78.4688 | 53.895 | 4671.8166
2035-07-07 16:00 | 16138.9 | 5.271 | 79.0183 | 53.895 | 4729.8447
2035-07-08 17:00 | 15609.7 | 5.1098 | 79.2905 | 53.895 | 4574.7515
2035-07-09 18:00 | 13797.4 | 4.4484 | 79.6787 | 53.895 | 4043.6188
2035-07-10 19:00 | 11871.9 | 3.7016 | 80.1319 | 53.895 | 3479.3104
2035-07-11 20:00 | 9168.37 | 2.8422 | 80.0549 | 53.895 | 2686.984
2035-07-12 21:00 | 8287.76 | 2.4863 | 80.1754 | 53.895 | 2428.9027
2035-07-13 22:00 | 5701.64 | 1.7227 | 79.7679 | 53.895 | 1670.9857
2035-07-14 23:00 | 4712.58 | 1.4257 | 79.2573 | 53.895 | 1381.1209
2035-07-16 | 3613.92 | 1.1682 | 77.8414 | 53.895 | 1059.1354
2035-07-17 01:00 | 3356.63 | 1.0676 | 77.6901 | 53.895 | 983.7311
2035-07-18 02:00 | 3132.97 | 1 | 78.5072 | 53.895 | 918.1829
2035-07-19 03:00 | 3117.34 | 1 | 77.1075 | 53.895 | 913.6022
2035-07-20 04:00 | 3242.2 | 1.0306 | 76.9587 | 53.895 | 950.195
2035-07-21 05:00 | 4388.07 | 1.3961 | 76.7932 | 53.895 | 1286.0164
2035-07-22 06:00 | 4816.52 | 1.5525 | 76.6264 | 53.895 | 1411.5827
2035-07-23 07:00 | 6020.19 | 1.9411 | 76.6453 | 53.895 | 1764.3435
2035-07-24 08:00 | 5858.78 | 1.8996 | 76.7129 | 53.895 | 1717.0389
2035-07-25 09:00 | 7515.95 | 2.5001 | 76.3871 | 53.895 | 2202.7075
2035-07-26 10:00 | 9436.97 | 3.1443 | 76.5821 | 53.895 | 2765.7029
2035-07-27 11:00 | 11671.5 | 3.7809 | 77.3237 | 53.895 | 3420.579
2035-07-28 12:00 | 12728.4 | 4.2219 | 77.4453 | 53.895 | 3730.3258
2035-07-29 13:00 | 13823.1 | 4.4317 | 78.3218 | 53.895 | 4051.1507
2035-07-30 14:00 | 14649.9 | 4.7651 | 78.5103 | 53.895 | 4293.4619
2035-07-31 15:00 | 15891.7 | 5.2569 | 78.6356 | 53.895 | 4657.3975
2035-08-01 16:00 | 15982.8 | 5.2142 | 79.2343 | 53.895 | 4684.0963
2035-08-02 17:00 | 15893.8 | 5.1718 | 79.5391 | 53.895 | 4658.013
2035-08-03 18:00 | 14178.6 | 4.517 | 80.0562 | 53.895 | 4155.3375
2035-08-04 19:00 | 12080.2 | 3.8412 | 80.0679 | 53.895 | 3540.3571
2035-08-05 20:00 | 9477.31 | 2.9608 | 80.1561 | 53.895 | 2777.5254
2035-08-06 21:00 | 8194.69 | 2.5408 | 79.8974 | 53.895 | 2401.6266
2035-08-07 22:00 | 5965.84 | 1.8362 | 79.6797 | 53.895 | 1748.4151
2035-08-08 23:00 | 5228.98 | 1.5838 | 79.4534 | 53.895 | 1532.4628
2035-08-10 | 4644.9 | 1.4192 | 78.9449 | 53.895 | 1361.2858
2035-08-11 01:00 | 3863.02 | 1.2382 | 77.926 | 53.895 | 1132.1394
2035-08-12 02:00 | 4011.78 | 1.2426 | 78.1328 | 53.895 | 1175.7367
2035-08-13 03:00 | 4001.53 | 1.2148 | 78.2253 | 53.895 | 1172.7327
2035-08-14 04:00 | 4259.71 | 1.3105 | 77.8671 | 53.895 | 1248.3978
2035-08-15 05:00 | 5116.81 | 1.6357 | 77.1761 | 53.895 | 1499.589
2035-08-16 06:00 | 5207.05 | 1.6698 | 77.1343 | 53.895 | 1526.0357
2035-08-17 07:00 | 5969.74 | 1.8914 | 77.2971 | 53.895 | 1749.5581
2035-08-18 08:00 | 5835.29 | 1.8038 | 77.7411 | 53.895 | 1710.1547
2035-08-19 09:00 | 6210.45 | 2.0572 | 76.7419 | 53.895 | 1820.1032
2035-08-20 10:00 | 8726.47 | 2.919 | 76.6386 | 53.895 | 2557.4759
2035-08-21 11:00 | 10820.7 | 3.7522 | 76.4451 | 53.895 | 3171.2341
2035-08-22 12:00 | 11685 | 4.0557 | 76.8496 | 53.895 | 3424.5355
2035-08-23 13:00 | 12591.8 | 4.2828 | 77.4449 | 53.895 | 3690.2923
2035-08-24 14:00 | 13015.5 | 4.3749 | 77.9248 | 53.895 | 3814.4665
2035-08-25 15:00 | 13836.4 | 4.8363 | 77.6632 | 53.895 | 4055.0486
2035-08-26 16:00 | 14095.6 | 4.7009 | 78.577 | 53.895 | 4131.0126
2035-08-27 17:00 | 13584.2 | 4.5339 | 78.7639 | 53.895 | 3981.136
2035-08-28 18:00 | 11913.3 | 3.8708 | 79.245 | 53.895 | 3491.4436
2035-08-29 19:00 | 9889.03 | 3.0651 | 79.8443 | 53.895 | 2898.1886
2035-08-30 20:00 | 7173.2 | 2.1587 | 80.0715 | 53.895 | 2102.2574
2035-08-31 21:00 | 5662.07 | 1.7185 | 79.5217 | 53.895 | 1659.3889
2035-09-01 22:00 | 3226.03 | 1 | 80.8007 | 53.895 | 945.4561
2035-09-02 23:00 | 3082.02 | 1 | 62.6113 | 53.895 | 903.2509
2035-09-04 | 2951.63 | 1 | 62.2691 | 53.895 | 865.0374
2035-09-05 01:00 | 127.468 | 1 | 62.4922 | 53.895 | 37.3572
2035-09-06 02:00 | -148.756 | 1.0241 | 61.279 | 53.895 | -43.5961
2035-09-07 03:00 | -368.336 | 1.5973 | 60.4632 | 53.895 | -107.9486
2035-09-08 04:00 | -434.192 | 1.7402 | 60.0805 | 53.895 | -127.2491
2035-09-09 05:00 | -599.822 | 2.2018 | 59.6907 | 53.895 | -175.7905
2035-09-10 06:00 | 1289.27 | 1 | 60.4711 | 53.895 | 377.8477
2035-09-11 07:00 | 2170.32 | 1 | 70.9742 | 53.895 | 636.058
2035-09-12 08:00 | 2771.79 | 1 | 74.4704 | 53.895 | 812.3315
2035-09-13 09:00 | 4684.3 | 1.5433 | 75.0949 | 53.895 | 1372.8328
2035-09-14 10:00 | 6644.55 | 2.2945 | 74.6915 | 53.895 | 1947.3254
2035-09-15 11:00 | 8241.44 | 2.829 | 75.1346 | 53.895 | 2415.3276
2035-09-16 12:00 | 9652.95 | 3.2234 | 75.8672 | 53.895 | 2829.0004
2035-09-17 13:00 | 10475 | 3.4409 | 76.4859 | 53.895 | 3069.9195
2035-09-18 14:00 | 11527 | 3.7676 | 76.9059 | 53.895 | 3378.2302
2035-09-19 15:00 | 11583.8 | 3.8169 | 77.1393 | 53.895 | 3394.8767
2035-09-20 16:00 | 14214.9 | 4.6444 | 77.4852 | 53.895 | 4165.976
2035-09-21 17:00 | 13286.8 | 4.2631 | 78.2474 | 53.895 | 3893.9767
2035-09-22 18:00 | 11881.8 | 3.7732 | 78.6151 | 53.895 | 3482.2118
2035-09-23 19:00 | 9683.71 | 3.0542 | 78.7215 | 53.895 | 2838.0153
2035-09-24 20:00 | 8187.35 | 2.5018 | 79.0287 | 53.895 | 2399.4754
2035-09-25 21:00 | 6950.5 | 2.1003 | 78.9942 | 53.895 | 2036.9905
2035-09-26 22:00 | 6047.07 | 1.8496 | 78.5413 | 53.895 | 1772.2213
2035-09-27 23:00 | 3190.88 | 1 | 82.2465 | 53.895 | 935.1546
2035-09-29 | 3106.98 | 1 | 61.9405 | 53.895 | 910.566
2035-09-30 01:00 | 3029.06 | 1 | 61.6673 | 53.895 | 887.7299
2035-10-01 02:00 | 1188.94 | 1 | 61.7973 | 53.895 | 348.4439
2035-10-02 03:00 | 530.603 | 1 | 61.5267 | 53.895 | 155.5044
2035-10-03 04:00 | -53.6204 | 0.78924 | 60.9219 | 53.895 | -15.7146
2035-10-04 05:00 | -225.27 | 1.2258 | 60.0867 | 53.895 | -66.0201
2035-10-05 06:00 | 1961.48 | 1 | 60.3541 | 53.895 | 574.853
2035-10-06 07:00 | 2888.75 | 1 | 76.3165 | 53.895 | 846.6091
2035-10-07 08:00 | 2980.47 | 1 | 75.8282 | 53.895 | 873.4895
2035-10-08 09:00 | 4288.2 | 1.4918 | 74.3274 | 53.895 | 1256.7474
2035-10-09 10:00 | 6410 | 2.3139 | 73.9848 | 53.895 | 1878.5856
2035-10-10 11:00 | 8310.77 | 2.8697 | 74.9263 | 53.895 | 2435.6463
2035-10-11 12:00 | 9319.48 | 3.1801 | 75.4689 | 53.895 | 2731.27
2035-10-12 13:00 | 9782.73 | 3.2484 | 76.1661 | 53.895 | 2867.0351
2035-10-13 14:00 | 10399.2 | 3.4226 | 76.5638 | 53.895 | 3047.7047
2035-10-14 15:00 | 10647.7 | 3.4966 | 76.8649 | 53.895 | 3120.5328
2035-10-15 16:00 | 12759.5 | 4.1821 | 77.0857 | 53.895 | 3739.4403
2035-10-16 17:00 | 11452.9 | 3.734 | 77.5676 | 53.895 | 3356.5137
2035-10-17 18:00 | 9869.51 | 3.1295 | 78.0729 | 53.895 | 2892.4679
2035-10-18 19:00 | 7827.36 | 2.4476 | 78.1883 | 53.895 | 2293.9728
2035-10-19 20:00 | 6440.36 | 2.0248 | 77.8896 | 53.895 | 1887.4832
2035-10-20 21:00 | 5157.11 | 1.6026 | 77.8231 | 53.895 | 1511.3997
2035-10-21 22:00 | 4167.46 | 1.3309 | 77.1018 | 53.895 | 1221.362
2035-10-22 23:00 | 3106.37 | 1 | 61.6098 | 53.895 | 910.3872
2035-10-24 | 2758.7 | 1 | 61.3523 | 53.895 | 808.4952
2035-10-25 01:00 | 307.196 | 1 | 61.543 | 53.895 | 90.0303
2035-10-26 02:00 | 262.951 | 1 | 61.0973 | 53.895 | 77.0633
2035-10-27 03:00 | 167.616 | 1 | 60.8205 | 53.895 | 49.1234
2035-10-28 04:00 | 2627.12 | 1 | 60.1718 | 53.895 | 769.9329
2035-10-29 05:00 | 2935.98 | 1 | 60.2417 | 53.895 | 860.4508
2035-10-30 06:00 | 3038.76 | 1 | 60.2671 | 53.895 | 890.5726
2035-10-31 07:00 | 3048.46 | 1 | 60.2899 | 53.895 | 893.4154
2035-11-01 08:00 | 3021.32 | 1 | 79.2946 | 53.895 | 885.4615
2035-11-02 09:00 | 4577.85 | 1.447 | 75.6434 | 53.895 | 1341.6354
2035-11-03 10:00 | 6763.21 | 2.2438 | 75.0927 | 53.895 | 1982.1012
2035-11-04 11:00 | 8778.18 | 2.9896 | 75.0486 | 53.895 | 2572.6306
2035-11-05 12:00 | 10581.3 | 3.4922 | 75.8875 | 53.895 | 3101.0729
2035-11-06 13:00 | 11401.8 | 3.7396 | 76.4482 | 53.895 | 3341.5377
2035-11-07 14:00 | 12404.7 | 4.0528 | 76.9154 | 53.895 | 3635.4587
2035-11-08 15:00 | 14077.7 | 4.6007 | 77.3116 | 53.895 | 4125.7666
2035-11-09 16:00 | 14239.7 | 4.6095 | 77.8941 | 53.895 | 4173.2441
2035-11-10 17:00 | 13909.3 | 4.4834 | 78.2704 | 53.895 | 4076.4134
2035-11-11 18:00 | 11776.3 | 3.6894 | 78.8868 | 53.895 | 3451.2928
2035-11-12 19:00 | 9876.23 | 3.1295 | 78.6642 | 53.895 | 2894.4373
2035-11-13 20:00 | 7582.35 | 2.3647 | 78.7303 | 53.895 | 2222.1674
2035-11-14 21:00 | 6359.84 | 1.9776 | 78.4408 | 53.895 | 1863.8851
2035-11-15 22:00 | 3973.18 | 1.2094 | 78.448 | 53.895 | 1164.4241
2035-11-16 23:00 | 3151.72 | 1 | 77.7264 | 53.895 | 923.678
2035-11-18 | 3108.95 | 1 | 82.3738 | 53.895 | 911.1433
2035-11-19 01:00 | 3119.7 | 1 | 61.4163 | 53.895 | 914.2938
2035-11-20 02:00 | 3084.14 | 1 | 61.2604 | 53.895 | 903.8722
2035-11-21 03:00 | 3053.06 | 1 | 61.1034 | 53.895 | 894.7636
2035-11-22 04:00 | 3127.84 | 1 | 60.9622 | 53.895 | 916.6794
2035-11-23 05:00 | 3133.42 | 1 | 79.0109 | 53.895 | 918.3148
2035-11-24 06:00 | 3258.31 | 1 | 77.5721 | 53.895 | 954.9164
2035-11-25 07:00 | 3610.02 | 1.103 | 76.5686 | 53.895 | 1057.9924
2035-11-26 08:00 | 3403.56 | 1 | 83.4944 | 53.895 | 997.485
2035-11-27 09:00 | 3259.48 | 1 | 79.5995 | 53.895 | 955.2593
2035-11-28 10:00 | 3754.48 | 1.1977 | 75.8204 | 53.895 | 1100.3295
2035-11-29 11:00 | 5473.07 | 1.6878 | 76.332 | 53.895 | 1603.9985
2035-11-30 12:00 | 5313.22 | 1.6409 | 76.4895 | 53.895 | 1557.1511
2035-12-01 13:00 | 6424.46 | 2.1922 | 75.0884 | 53.895 | 1882.8234
2035-12-02 14:00 | 8667.95 | 3.0875 | 74.6373 | 53.895 | 2540.3254
2035-12-03 15:00 | 11419 | 3.9069 | 75.516 | 53.895 | 3346.5785
2035-12-04 16:00 | 12529.9 | 4.1001 | 76.654 | 53.895 | 3672.1512
2035-12-05 17:00 | 12911.1 | 4.1741 | 77.2414 | 53.895 | 3783.8699
2035-12-06 18:00 | 11461.9 | 3.6207 | 77.9274 | 53.895 | 3359.1513
2035-12-07 19:00 | 9735.67 | 3.0716 | 78.0513 | 53.895 | 2853.2432
2035-12-08 20:00 | 7857.84 | 2.3237 | 78.9762 | 53.895 | 2302.9056
2035-12-09 21:00 | 6565.95 | 2.0214 | 78.1386 | 53.895 | 1924.29
2035-12-10 22:00 | 4166.33 | 1.2448 | 78.3776 | 53.895 | 1221.0308
2035-12-11 23:00 | 4123.54 | 1.2825 | 77.3363 | 53.895 | 1208.4903
2035-12-13 | 4214.87 | 1.2754 | 77.5251 | 53.895 | 1235.2565
2035-12-14 01:00 | 4267.39 | 1.3398 | 76.8569 | 53.895 | 1250.6486
2035-12-15 02:00 | 4142.88 | 1.2992 | 76.7875 | 53.895 | 1214.1583
2035-12-16 03:00 | 4561.75 | 1.4381 | 76.5984 | 53.895 | 1336.917
2035-12-17 04:00 | 4969.26 | 1.5307 | 76.9222 | 53.895 | 1456.3463
2035-12-18 05:00 | 5992.83 | 1.9406 | 76.184 | 53.895 | 1756.3251
2035-12-19 06:00 | 6331.06 | 2.0295 | 76.4404 | 53.895 | 1855.4505
2035-12-20 07:00 | 6945.08 | 2.3063 | 76.0302 | 53.895 | 2035.402
2035-12-21 08:00 | 7664.34 | 2.4306 | 76.8394 | 53.895 | 2246.1963
2035-12-22 09:00 | 9360.34 | 3.1972 | 75.9682 | 53.895 | 2743.2449
2035-12-23 10:00 | 10081.1 | 3.416 | 76.4274 | 53.895 | 2954.4788
2035-12-24 11:00 | 10656.3 | 3.4813 | 77.229 | 53.895 | 3123.0532
2035-12-25 12:00 | 10153 | 3.3423 | 77.3773 | 53.895 | 2975.5506
2035-12-26 13:00 | 9833.84 | 3.0568 | 78.3363 | 53.895 | 2882.014
2035-12-27 14:00 | 9301.05 | 3.0312 | 77.6979 | 53.895 | 2725.8687
2035-12-28 15:00 | 10426.2 | 3.6028 | 76.8414 | 53.895 | 3055.6176
2035-12-29 16:00 | 11061.7 | 3.6245 | 77.691 | 53.895 | 3241.8643
2035-12-30 17:00 | 10819 | 3.5349 | 77.8569 | 53.895 | 3170.7359
2035-12-31 18:00 | 8916.45 | 2.9551 | 77.7123 | 53.895 | 2613.1535
2036-01-01 19:00 | 6434.28 | 2.2222 | 76.9787 | 53.895 | 1885.7013
2036-01-02 20:00 | 3774.98 | 1.2225 | 77.5381 | 53.895 | 1106.3374
2036-01-03 21:00 | 3090.26 | 1 | 80.5205 | 53.895 | 905.6658
2036-01-04 22:00 | 2962 | 1 | 61.664 | 53.895 | 868.0765
2036-01-05 23:00 | 919.62 | 1 | 61.7413 | 53.895 | 269.514
2036-01-07 | 0 | 0 | 61.4363 | 53.895 | 0
2036-01-08 01:00 | -258.03 | 1.3398 | 60.1191 | 53.895 | -75.6211
2036-01-09 02:00 | -527.599 | 2.0366 | 59.5372 | 53.895 | -154.624
2036-01-10 03:00 | -832.524 | 2.8528 | 59.1237 | 53.895 | -243.9887
2036-01-11 04:00 | -1023.02 | 3.3369 | 58.7736 | 53.895 | -299.8176
2036-01-12 05:00 | -808.253 | 2.6811 | 58.5553 | 53.895 | -236.8756
2036-01-13 06:00 | -560.225 | 2.032 | 58.5134 | 53.895 | -164.1857
2036-01-14 07:00 | 562.457 | 1 | 59.5988 | 53.895 | 164.8399
2036-01-15 08:00 | 2217.77 | 1 | 59.3506 | 53.895 | 649.9642
2036-01-16 09:00 | 3010.89 | 1 | 77.7769 | 53.895 | 882.4048
2036-01-17 10:00 | 5010.41 | 1.6893 | 73.9269 | 53.895 | 1468.4062
2036-01-18 11:00 | 6824.5 | 2.3263 | 74.0889 | 53.895 | 2000.0635
2036-01-19 12:00 | 7443.1 | 2.4864 | 74.7807 | 53.895 | 2181.3573
2036-01-20 13:00 | 8063.89 | 2.6708 | 75.2101 | 53.895 | 2363.2929
2036-01-21 14:00 | 9307.83 | 3.0614 | 75.5674 | 53.895 | 2727.8557
2036-01-22 15:00 | 10957.3 | 3.6168 | 75.8496 | 53.895 | 3211.2676
2036-01-23 16:00 | 11096.5 | 3.6522 | 76.3016 | 53.895 | 3252.0631
2036-01-24 17:00 | 10762.3 | 3.5192 | 76.6628 | 53.895 | 3154.1188
2036-01-25 18:00 | 8937.37 | 2.8541 | 77.1815 | 53.895 | 2619.2846
2036-01-26 19:00 | 6768.99 | 2.1524 | 77.205 | 53.895 | 1983.7951
2036-01-27 20:00 | 3548.54 | 1.1837 | 76.2979 | 53.895 | 1039.9744
2036-01-28 21:00 | 3016.13 | 1 | 82.5436 | 53.895 | 883.9404
2036-01-29 22:00 | 0 | 0 | 61.4432 | 53.895 | 0
2036-01-30 23:00 | -377.392 | 1.6943 | 59.8128 | 53.895 | -110.6027
2036-02-01 | -926.114 | 3.1525 | 59.0582 | 53.895 | -271.4172
2036-02-02 01:00 | -1303.71 | 4.1254 | 58.6211 | 53.895 | -382.0797
2036-02-03 02:00 | -1641.01 | 5.0313 | 58.2898 | 53.895 | -480.9326
2036-02-04 03:00 | -1743.2 | 5.263 | 57.9711 | 53.895 | -510.8815
2036-02-05 04:00 | -1869.37 | 5.6271 | 57.7458 | 53.895 | -547.8583
2036-02-06 05:00 | -1605.96 | 4.8294 | 57.5286 | 53.895 | -470.6604
2036-02-07 06:00 | -1413.61 | 4.3487 | 57.4184 | 53.895 | -414.2882
2036-02-08 07:00 | -650.234 | 2.1576 | 57.4183 | 53.895 | -190.5648
2036-02-09 08:00 | -234.517 | 1.1562 | 57.8784 | 53.895 | -68.7301
2036-02-10 09:00 | 2623.67 | 1 | 58.379 | 53.895 | 768.9218
2036-02-11 10:00 | 3081.52 | 1.0425 | 73.0303 | 53.895 | 903.1044
2036-02-12 11:00 | 5208.75 | 1.6878 | 73.7988 | 53.895 | 1526.5339
2036-02-13 12:00 | 6547.94 | 2.1611 | 73.8821 | 53.895 | 1919.0118
2036-02-14 13:00 | 7432.32 | 2.4504 | 74.273 | 53.895 | 2178.198
2036-02-15 14:00 | 8160.78 | 2.6642 | 74.752 | 53.895 | 2391.6885
2036-02-16 15:00 | 9255.79 | 3.0691 | 74.7968 | 53.895 | 2712.6043
2036-02-17 16:00 | 9507.67 | 3.0903 | 75.4112 | 53.895 | 2786.423
2036-02-18 17:00 | 8782.6 | 2.8527 | 75.6613 | 53.895 | 2573.926
2036-02-19 18:00 | 6884.97 | 2.2439 | 75.7099 | 53.895 | 2017.7855
2036-02-20 19:00 | 5772.24 | 1.8378 | 75.9336 | 53.895 | 1691.6766
2036-02-21 20:00 | 3620.01 | 1.1564 | 75.7639 | 53.895 | 1060.9202
2036-02-22 21:00 | 3115.53 | 1 | 77.7833 | 53.895 | 913.0717
2036-02-23 22:00 | 3033.69 | 1 | 60.0398 | 53.895 | 889.0868
2036-02-24 23:00 | 0 | 0 | 60.4268 | 53.895 | 0
2036-02-26 | -215.504 | 1.1322 | 59.0635 | 53.895 | -63.158
2036-02-27 01:00 | -357.504 | 1.5918 | 58.5834 | 53.895 | -104.7741
2036-02-28 02:00 | -506.24 | 1.9846 | 58.2488 | 53.895 | -148.3643
2036-02-29 03:00 | -686.635 | 2.4771 | 57.9499 | 53.895 | -201.2329
2036-03-01 04:00 | -741.918 | 2.5992 | 57.7053 | 53.895 | -217.4347
2036-03-02 05:00 | -772.608 | 2.6815 | 57.5615 | 53.895 | -226.4291
2036-03-03 06:00 | -146.843 | 0.85112 | 57.9983 | 53.895 | -43.0354
2036-03-04 07:00 | 352.328 | 1 | 58.7315 | 53.895 | 103.2571
2036-03-05 08:00 | -308.901 | 1.5578 | 57.8946 | 53.895 | -90.5299
2036-03-06 09:00 | -197.911 | 1.1079 | 57.8838 | 53.895 | -58.002
2036-03-07 10:00 | 2039.09 | 1 | 58.2934 | 53.895 | 597.5983
2036-03-08 11:00 | 2960.98 | 1 | 58.3607 | 53.895 | 867.7776
2036-03-09 12:00 | 3023.21 | 1 | 58.552 | 53.895 | 886.0154
2036-03-10 13:00 | 3064.48 | 1 | 58.6193 | 53.895 | 898.1104
2036-03-11 14:00 | 3156.04 | 1 | 58.6552 | 53.895 | 924.944
2036-03-12 15:00 | 3134.09 | 1 | 58.7023 | 53.895 | 918.5111
2036-03-13 16:00 | 4489.58 | 1.4644 | 73.6106 | 53.895 | 1315.766
2036-03-14 17:00 | 3536.57 | 1.1302 | 74.0073 | 53.895 | 1036.4664
2036-03-15 18:00 | 3044.76 | 1 | 77.8765 | 53.895 | 892.3311
2036-03-16 19:00 | 3056.9 | 1 | 58.7087 | 53.895 | 895.889
2036-03-17 20:00 | 3095.13 | 1 | 58.7129 | 53.895 | 907.0931
2036-03-18 21:00 | 436.696 | 1 | 59.201 | 53.895 | 127.983
2036-03-19 22:00 | 0 | 0 | 58.9353 | 53.895 | 0
2036-03-20 23:00 | -1162.51 | 3.9767 | 57.3337 | 53.895 | -340.698
2036-03-22 | -1518.51 | 4.7732 | 56.9547 | 53.895 | -445.0314
2036-03-23 01:00 | -1607.94 | 4.9744 | 56.7049 | 53.895 | -471.2407
2036-03-24 02:00 | -1652.27 | 5.099 | 56.5194 | 53.895 | -484.2325
2036-03-25 03:00 | -1586.82 | 4.8981 | 56.4039 | 53.895 | -465.051
2036-03-26 04:00 | -1592.13 | 4.9408 | 56.3049 | 53.895 | -466.6072
2036-03-27 05:00 | -1593.12 | 4.9445 | 56.2275 | 53.895 | -466.8974
2036-03-28 06:00 | -887.642 | 2.8362 | 56.1956 | 53.895 | -260.1422
2036-03-29 07:00 | -199.922 | 1.0019 | 56.7378 | 53.895 | -58.5914
2036-03-30 08:00 | -166.088 | 1.0763 | 57.0124 | 53.895 | -48.6756
2036-03-31 09:00 | 2119.57 | 1 | 57.3957 | 53.895 | 621.1846
2036-04-01 10:00 | 3544.97 | 1.1915 | 71.9986 | 53.895 | 1038.9282
2036-04-02 11:00 | 6163.96 | 2.2039 | 71.4438 | 53.895 | 1806.4784
2036-04-03 12:00 | 8176.37 | 2.7022 | 73.0055 | 53.895 | 2396.2575
2036-04-04 13:00 | 9739.4 | 3.2285 | 73.5035 | 53.895 | 2854.3364
2036-04-05 14:00 | 10304.7 | 3.4856 | 73.7727 | 53.895 | 3020.0095
2036-04-06 15:00 | 11029 | 3.6448 | 74.5242 | 53.895 | 3232.2808
2036-04-07 16:00 | 13662.3 | 4.5829 | 74.703 | 53.895 | 4004.0249
2036-04-08 17:00 | 12784.2 | 4.186 | 75.6727 | 53.895 | 3746.6792
2036-04-09 18:00 | 11304.2 | 3.6272 | 76.2896 | 53.895 | 3312.934
2036-04-10 19:00 | 9613.98 | 3.0465 | 76.5469 | 53.895 | 2817.5794
2036-04-11 20:00 | 7962.14 | 2.3255 | 77.768 | 53.895 | 2333.4729
2036-04-12 21:00 | 6843.26 | 2.0603 | 77.1581 | 53.895 | 2005.5615
2036-04-13 22:00 | 5805.19 | 1.8067 | 76.458 | 53.895 | 1701.3332
2036-04-14 23:00 | 3258.44 | 1 | 77.489 | 53.895 | 954.9545
2036-04-16 | 3201.23 | 1 | 82.4298 | 53.895 | 938.1879
2036-04-17 01:00 | 3119.3 | 1 | 60.0173 | 53.895 | 914.1766
2036-04-18 02:00 | 3067.2 | 1 | 59.8929 | 53.895 | 898.9076
2036-04-19 03:00 | 3163.43 | 1 | 59.751 | 53.895 | 927.1098
2036-04-20 04:00 | 3155.49 | 1 | 59.6395 | 53.895 | 924.7828
2036-04-21 05:00 | 3229.15 | 1 | 76.8763 | 53.895 | 946.3704
2036-04-22 06:00 | 3211.74 | 1 | 76.1742 | 53.895 | 941.2681
2036-04-23 07:00 | 3655.04 | 1.1301 | 75.1825 | 53.895 | 1071.1865
2036-04-24 08:00 | 3191.32 | 1 | 78.2455 | 53.895 | 935.2836
2036-04-25 09:00 | 3917.17 | 1.238 | 74.8373 | 53.895 | 1148.0092
2036-04-26 10:00 | 4129.96 | 1.3012 | 74.9349 | 53.895 | 1210.3718
2036-04-27 11:00 | 4741.28 | 1.5277 | 74.6559 | 53.895 | 1389.532
2036-04-28 12:00 | 5591.55 | 1.7772 | 74.937 | 53.895 | 1638.7215
2036-04-29 13:00 | 5376.96 | 1.6799 | 75.3252 | 53.895 | 1575.8314
2036-04-30 14:00 | 5791.53 | 1.8251 | 75.2419 | 53.895 | 1697.3299
2036-05-01 15:00 | 7872.44 | 2.8724 | 73.2713 | 53.895 | 2307.1844
2036-05-02 16:00 | 8478.8 | 2.9568 | 74.148 | 53.895 | 2484.891
2036-05-03 17:00 | 8686.53 | 2.8934 | 75.0075 | 53.895 | 2545.7706
2036-05-04 18:00 | 7349.93 | 2.2986 | 76.0815 | 53.895 | 2154.0518
2036-05-05 19:00 | 6381.68 | 1.9504 | 76.4061 | 53.895 | 1870.2858
2036-05-06 20:00 | 4102.43 | 1.2926 | 75.881 | 53.895 | 1202.3035
2036-05-07 21:00 | 3127.21 | 1 | 76.5398 | 53.895 | 916.4948
2036-05-08 22:00 | 3036.71 | 1 | 59.9318 | 53.895 | 889.9718
2036-05-09 23:00 | 2118.35 | 1 | 59.9386 | 53.895 | 620.8271
2036-05-11 | 688.941 | 1 | 59.9692 | 53.895 | 201.9087
2036-05-12 01:00 | 96.3319 | 1 | 59.7536 | 53.895 | 28.2321
2036-05-13 02:00 | -9.5407 | 0.65327 | 59.5321 | 53.895 | -2.7961
2036-05-14 03:00 | 161.262 | 1 | 59.3133 | 53.895 | 47.2612
2036-05-15 04:00 | 1592.32 | 1 | 58.9219 | 53.895 | 466.6629
2036-05-16 05:00 | 1928.59 | 1 | 58.9077 | 53.895 | 565.2139
2036-05-17 06:00 | 2652.79 | 1 | 58.8298 | 53.895 | 777.456
2036-05-18 07:00 | 2946.4 | 1 | 58.8705 | 53.895 | 863.5046
2036-05-19 08:00 | 3069.89 | 1 | 58.9566 | 53.895 | 899.6959
2036-05-20 09:00 | 3105.55 | 1 | 59.0265 | 53.895 | 910.1469
2036-05-21 10:00 | 3096.13 | 1 | 74.6591 | 53.895 | 907.3861
2036-05-22 11:00 | 3930.52 | 1.2512 | 74.2942 | 53.895 | 1151.9217
2036-05-23 12:00 | 4547.14 | 1.4443 | 74.4241 | 53.895 | 1332.6352
2036-05-24 13:00 | 5271.92 | 1.693 | 74.3874 | 53.895 | 1545.0472
2036-05-25 14:00 | 6240 | 1.9978 | 74.5808 | 53.895 | 1828.7635
2036-05-26 15:00 | 7256.24 | 2.4457 | 74.042 | 53.895 | 2126.594
2036-05-27 16:00 | 7735.92 | 2.5698 | 74.4707 | 53.895 | 2267.1744
2036-05-28 17:00 | 8192.4 | 2.7535 | 74.4884 | 53.895 | 2400.9554
2036-05-29 18:00 | 7138.35 | 2.2597 | 75.5322 | 53.895 | 2092.0439
2036-05-30 19:00 | 5524.4 | 1.6806 | 76.1413 | 53.895 | 1619.0418
2036-05-31 20:00 | 3126.78 | 1 | 78.1668 | 53.895 | 916.3688
2036-06-01 21:00 | 3058.44 | 1 | 59.7333 | 53.895 | 896.3403
2036-06-02 22:00 | -191.771 | 1.1753 | 59.3149 | 53.895 | -56.2025
2036-06-03 23:00 | -643.269 | 2.4104 | 58.3153 | 53.895 | -188.5235
2036-06-05 | -1144.52 | 3.7757 | 57.7703 | 53.895 | -335.4257
2036-06-06 01:00 | -1310.49 | 4.149 | 57.427 | 53.895 | -384.0667
2036-06-07 02:00 | -1612.12 | 5.0174 | 57.1784 | 53.895 | -472.4657
2036-06-08 03:00 | -1535.7 | 4.7215 | 56.9122 | 53.895 | -450.0692
2036-06-09 04:00 | -1440.33 | 4.4764 | 56.7664 | 53.895 | -422.1191
2036-06-10 05:00 | -1220.41 | 3.8538 | 56.6477 | 53.895 | -357.6669
2036-06-11 06:00 | -819.751 | 2.7294 | 56.6178 | 53.895 | -240.2453
2036-06-12 07:00 | -490.292 | 1.8654 | 56.7391 | 53.895 | -143.6904
2036-06-13 08:00 | 2317.64 | 1 | 57.5671 | 53.895 | 679.2332
2036-06-14 09:00 | 2182.78 | 1.0709 | 67.8444 | 53.895 | 639.7097
2036-06-15 10:00 | 4823.54 | 1.8115 | 70.9042 | 53.895 | 1413.64
2036-06-16 11:00 | 6901.48 | 2.5052 | 71.7228 | 53.895 | 2022.6241
2036-06-17 12:00 | 8373.1 | 2.8953 | 72.877 | 53.895 | 2453.9134
2036-06-18 13:00 | 9341.61 | 3.1267 | 73.822 | 53.895 | 2737.7556
2036-06-19 14:00 | 9811.15 | 3.2063 | 74.5761 | 53.895 | 2875.3642
2036-06-20 15:00 | 10955.6 | 3.64 | 74.7054 | 53.895 | 3210.7694
2036-06-21 16:00 | 11348.9 | 3.7184 | 75.2964 | 53.895 | 3326.0343
2036-06-22 17:00 | 11302.9 | 3.6636 | 75.7732 | 53.895 | 3312.553
2036-06-23 18:00 | 9769.52 | 3.0572 | 76.5324 | 53.895 | 2863.1637
2036-06-24 19:00 | 7564.85 | 2.3027 | 76.9845 | 53.895 | 2217.0387
2036-06-25 20:00 | 4593.14 | 1.4186 | 76.5881 | 53.895 | 1346.1165
2036-06-26 21:00 | 3421.39 | 1.0862 | 75.7741 | 53.895 | 1002.7104
2036-06-27 22:00 | 2955.56 | 1 | 60.1784 | 53.895 | 866.1891
2036-06-28 23:00 | 0 | 0 | 60.4298 | 53.895 | 0
2036-06-30 | -316.592 | 1.471 | 58.8714 | 53.895 | -92.784
2036-07-01 01:00 | -515.558 | 2.0207 | 58.3027 | 53.895 | -151.0951
2036-07-02 02:00 | -671.332 | 2.4291 | 57.9647 | 53.895 | -196.748
2036-07-03 03:00 | -609.673 | 2.2185 | 57.7451 | 53.895 | -178.6775
2036-07-04 04:00 | -632.471 | 2.31 | 57.5464 | 53.895 | -185.359
2036-07-05 05:00 | -266.843 | 1.2377 | 57.6729 | 53.895 | -78.204
2036-07-06 06:00 | -214.073 | 1.1852 | 57.7532 | 53.895 | -62.7386
2036-07-07 07:00 | 1735.15 | 1 | 58.23 | 53.895 | 508.5223
2036-07-08 08:00 | 2975.35 | 1 | 58.1896 | 53.895 | 871.989
2036-07-09 09:00 | 3152.27 | 1.0162 | 73.4934 | 53.895 | 923.8391
2036-07-10 10:00 | 5675.09 | 1.8594 | 73.326 | 53.895 | 1663.2047
2036-07-11 11:00 | 6999.14 | 2.3938 | 73.1094 | 53.895 | 2051.2454
2036-07-12 12:00 | 7847.27 | 2.744 | 73.2141 | 53.895 | 2299.8078
2036-07-13 13:00 | 8859.6 | 2.8543 | 74.6717 | 53.895 | 2596.4925
2036-07-14 14:00 | 9679.44 | 3.1963 | 74.6406 | 53.895 | 2836.7638
2036-07-15 15:00 | 11203.6 | 3.6967 | 74.9835 | 53.895 | 3283.451
2036-07-16 16:00 | 11351 | 3.6947 | 75.5699 | 53.895 | 3326.6497
2036-07-17 17:00 | 11033.7 | 3.5974 | 75.8221 | 53.895 | 3233.6583
2036-07-18 18:00 | 9435.84 | 2.985 | 76.4457 | 53.895 | 2765.3717
2036-07-19 19:00 | 7286.24 | 2.23 | 76.9198 | 53.895 | 2135.3862
2036-07-20 20:00 | 4690.16 | 1.4506 | 76.5611 | 53.895 | 1374.5502
2036-07-21 21:00 | 3344.75 | 1.062 | 75.7814 | 53.895 | 980.2495
2036-07-22 22:00 | 3013.08 | 1 | 60.1478 | 53.895 | 883.0466
2036-07-23 23:00 | 0 | 0 | 60.4218 | 53.895 | 0
2036-07-25 | 246.379 | 1 | 59.8403 | 53.895 | 72.2066
2036-07-26 01:00 | -21.3311 | 0.70546 | 59.4345 | 53.895 | -6.2515
2036-07-27 02:00 | -16.9033 | 0.65849 | 59.3775 | 53.895 | -4.9539
2036-07-28 03:00 | 114.105 | 1 | 59.1538 | 53.895 | 33.4409
2036-07-29 04:00 | 2741.65 | 1 | 58.5382 | 53.895 | 803.4983
2036-07-30 05:00 | 2092.02 | 1 | 58.8709 | 53.895 | 613.1105
2036-07-31 06:00 | 2813.1 | 1 | 58.7555 | 53.895 | 824.4382
2036-08-01 07:00 | 3086.24 | 1 | 58.7736 | 53.895 | 904.4877
2036-08-02 08:00 | 2968.67 | 1 | 58.8886 | 53.895 | 870.0313
2036-08-03 09:00 | 3041.74 | 1 | 77.4406 | 53.895 | 891.446
2036-08-04 10:00 | 4852.43 | 1.6409 | 73.2607 | 53.895 | 1422.1069
2036-08-05 11:00 | 6877.54 | 2.4418 | 72.8423 | 53.895 | 2015.608
2036-08-06 12:00 | 8331.76 | 2.8719 | 73.6006 | 53.895 | 2441.7978
2036-08-07 13:00 | 8569.88 | 2.8241 | 74.5981 | 53.895 | 2511.5839
2036-08-08 14:00 | 9030.74 | 2.9737 | 74.8672 | 53.895 | 2646.6486
2036-08-09 15:00 | 10069.8 | 3.386 | 74.812 | 53.895 | 2951.1671
2036-08-10 16:00 | 10186.2 | 3.3792 | 75.2741 | 53.895 | 2985.2805
2036-08-11 17:00 | 9845.51 | 3.2614 | 75.4822 | 53.895 | 2885.4342
2036-08-12 18:00 | 8000.8 | 2.5944 | 75.8773 | 53.895 | 2344.803
2036-08-13 19:00 | 5718.15 | 1.8351 | 75.9168 | 53.895 | 1675.8243
2036-08-14 20:00 | 3056.24 | 1 | 78.5316 | 53.895 | 895.6955
2036-08-15 21:00 | 3075.49 | 1 | 60.0916 | 53.895 | 901.3371
2036-08-16 22:00 | -195.514 | 1.1858 | 59.609 | 53.895 | -57.2995
2036-08-17 23:00 | -812.237 | 2.8871 | 58.5043 | 53.895 | -238.0432
2036-08-19 | -1136.69 | 3.7004 | 57.9412 | 53.895 | -333.131
2036-08-20 01:00 | -1285.33 | 4.0731 | 57.6018 | 53.895 | -376.693
2036-08-21 02:00 | -1399.73 | 4.3865 | 57.3539 | 53.895 | -410.2204
2036-08-22 03:00 | -1482.79 | 4.6157 | 57.1039 | 53.895 | -434.5629
2036-08-23 04:00 | -1572.71 | 4.8719 | 56.9081 | 53.895 | -460.9158
2036-08-24 05:00 | -1662.82 | 5.1266 | 56.7269 | 53.895 | -487.3244
2036-08-25 06:00 | -1014.42 | 3.1795 | 56.5917 | 53.895 | -297.2972
2036-08-26 07:00 | -302.788 | 1.2674 | 56.9153 | 53.895 | -88.7384
2036-08-27 08:00 | -280.626 | 1.3839 | 57.1192 | 53.895 | -82.2434
2036-08-28 09:00 | 1969.26 | 1 | 57.7106 | 53.895 | 577.1331
2036-08-29 10:00 | 2902.8 | 1 | 72.3708 | 53.895 | 850.7267
2036-08-30 11:00 | 5005.35 | 1.6144 | 73.0495 | 53.895 | 1466.9233
2036-08-31 12:00 | 6314.73 | 2.1783 | 72.4628 | 53.895 | 1850.6647
2036-09-01 13:00 | 7090.37 | 2.4103 | 73.031 | 53.895 | 2077.9823
2036-09-02 14:00 | 7891.18 | 2.6699 | 73.4186 | 53.895 | 2312.6766
2036-09-03 15:00 | 8606.69 | 2.8836 | 73.8386 | 53.895 | 2522.3718
2036-09-04 16:00 | 10918.2 | 3.6046 | 74.3264 | 53.895 | 3199.8086
2036-09-05 17:00 | 10012.9 | 3.2011 | 75.2675 | 53.895 | 2934.4913
2036-09-06 18:00 | 8302.17 | 2.6372 | 75.5712 | 53.895 | 2433.1258
2036-09-07 19:00 | 6752.81 | 2.0141 | 76.4977 | 53.895 | 1979.0533
2036-09-08 20:00 | 5486.18 | 1.6702 | 76.0802 | 53.895 | 1607.8406
2036-09-09 21:00 | 4302.21 | 1.3864 | 75.0756 | 53.895 | 1260.8533
2036-09-10 22:00 | 3452.08 | 1.0829 | 75.2496 | 53.895 | 1011.7048
2036-09-11 23:00 | 492.104 | 1 | 60.0286 | 53.895 | 144.2214
2036-09-13 | -65.827 | 0.85545 | 59.268 | 53.895 | -19.292
2036-09-14 01:00 | -355.199 | 1.6149 | 58.2482 | 53.895 | -104.0986
2036-09-15 02:00 | -516.244 | 2.0213 | 57.838 | 53.895 | -151.2962
2036-09-16 03:00 | -768.449 | 2.7257 | 57.4999 | 53.895 | -225.2102
2036-09-17 04:00 | -1069.58 | 3.5546 | 57.1706 | 53.895 | -313.463
2036-09-18 05:00 | -1121.11 | 3.6365 | 56.9478 | 53.895 | -328.5649
2036-09-19 06:00 | -435.195 | 1.6092 | 56.9749 | 53.895 | -127.5431
2036-09-20 07:00 | 1849.05 | 1 | 57.8929 | 53.895 | 541.9031
2036-09-21 08:00 | 2846.2 | 1 | 57.9501 | 53.895 | 834.1389
2036-09-22 09:00 | 3062.97 | 1 | 73.0659 | 53.895 | 897.6679
2036-09-23 10:00 | 5620.18 | 1.8986 | 72.627 | 53.895 | 1647.1122
2036-09-24 11:00 | 7447.38 | 2.6454 | 72.3526 | 53.895 | 2182.6116
2036-09-25 12:00 | 8711.26 | 2.996 | 73.2581 | 53.895 | 2553.0183
2036-09-26 13:00 | 9514.58 | 3.1264 | 74.2979 | 53.895 | 2788.4481
2036-09-27 14:00 | 10417.8 | 3.4451 | 74.5632 | 53.895 | 3053.1558
2036-09-28 15:00 | 10831.6 | 3.4739 | 75.3839 | 53.895 | 3174.4286
2036-09-29 16:00 | 12532.5 | 4.134 | 75.2701 | 53.895 | 3672.9132
2036-09-30 17:00 | 11016.4 | 3.539 | 76.0855 | 53.895 | 3228.5881
2036-10-01 18:00 | 9313.87 | 2.9493 | 76.4254 | 53.895 | 2729.6258
2036-10-02 19:00 | 7588.14 | 2.3668 | 76.5701 | 53.895 | 2223.8643
2036-10-03 20:00 | 6438.94 | 1.94 | 76.9276 | 53.895 | 1887.067
2036-10-04 21:00 | 5128.83 | 1.5618 | 76.5899 | 53.895 | 1503.1117
2036-10-05 22:00 | 4188.56 | 1.3252 | 75.7444 | 53.895 | 1227.5458
2036-10-06 23:00 | 2926.01 | 1 | 60.2009 | 53.895 | 857.5289
2036-10-08 | 0 | 0 | 60.4187 | 53.895 | 0
2036-10-09 01:00 | -18.3712 | 0.69528 | 59.7628 | 53.895 | -5.3841
2036-10-10 02:00 | -181.822 | 1.1266 | 58.8016 | 53.895 | -53.2868
2036-10-11 03:00 | -251.898 | 1.2947 | 58.4149 | 53.895 | -73.824
2036-10-12 04:00 | -331.37 | 1.5126 | 58.073 | 53.895 | -97.115
2036-10-13 05:00 | -486.693 | 1.9472 | 57.7422 | 53.895 | -142.6356
2036-10-14 06:00 | 1296.33 | 1 | 58.5653 | 53.895 | 379.9168
2036-10-15 07:00 | 2824.34 | 1 | 58.4075 | 53.895 | 827.7323
2036-10-16 08:00 | 3091.45 | 1 | 58.5781 | 53.895 | 906.0146
2036-10-17 09:00 | 4639.39 | 1.502 | 73.7226 | 53.895 | 1359.671
2036-10-18 10:00 | 7471.28 | 2.4342 | 73.8206 | 53.895 | 2189.616
2036-10-19 11:00 | 8764.01 | 3.0567 | 73.372 | 53.895 | 2568.4778
2036-10-20 12:00 | 10256.2 | 3.5116 | 74.0673 | 53.895 | 3005.7955
2036-10-21 13:00 | 11463.9 | 3.7233 | 75.2419 | 53.895 | 3359.7374
2036-10-22 14:00 | 12242.4 | 3.9386 | 75.8336 | 53.895 | 3587.8933
2036-10-23 15:00 | 12435.2 | 4.0744 | 75.9774 | 53.895 | 3644.3974
2036-10-24 16:00 | 14017.1 | 4.6242 | 76.154 | 53.895 | 4108.0065
2036-10-25 17:00 | 12956.1 | 4.1102 | 77.1512 | 53.895 | 3797.0581
2036-10-26 18:00 | 10910.1 | 3.4856 | 77.23 | 53.895 | 3197.4347
2036-10-27 19:00 | 9108.76 | 2.8263 | 77.575 | 53.895 | 2669.514
2036-10-28 20:00 | 7827.1 | 2.4705 | 77.1387 | 53.895 | 2293.8966
2036-10-29 21:00 | 6881.42 | 2.1116 | 77.3722 | 53.895 | 2016.7451
2036-10-30 22:00 | 5900.18 | 1.7299 | 77.8432 | 53.895 | 1729.1721
2036-10-31 23:00 | 3289.87 | 1 | 78.57 | 53.895 | 964.1657
2036-11-02 | 3205.9 | 1 | 81.6999 | 53.895 | 939.5565
2036-11-03 01:00 | 3128.23 | 1 | 60.3917 | 53.895 | 916.7937
2036-11-04 02:00 | 3065.95 | 1 | 60.2409 | 53.895 | 898.5412
2036-11-05 03:00 | 3135.24 | 1 | 60.0771 | 53.895 | 918.8481
2036-11-06 04:00 | 3132.64 | 1 | 59.9421 | 53.895 | 918.0862
2036-11-07 05:00 | 3169.92 | 1 | 80.4168 | 53.895 | 929.0118
2036-11-08 06:00 | 3199.81 | 1 | 75.9931 | 53.895 | 937.7717
2036-11-09 07:00 | 4573.63 | 1.4262 | 75.3004 | 53.895 | 1340.3986
2036-11-10 08:00 | 5569.21 | 1.7 | 75.7495 | 53.895 | 1632.1743
2036-11-11 09:00 | 7290.75 | 2.5924 | 73.7509 | 53.895 | 2136.7079
2036-11-12 10:00 | 9594.84 | 3.3484 | 74.2794 | 53.895 | 2811.97
2036-11-13 11:00 | 12117.5 | 4.0127 | 75.4524 | 53.895 | 3551.2887
2036-11-14 12:00 | 12736.7 | 4.0898 | 76.4781 | 53.895 | 3732.7583
2036-11-15 13:00 | 11766.1 | 3.7043 | 77.1966 | 53.895 | 3448.3035
2036-11-16 14:00 | 12538.1 | 4.302 | 76.135 | 53.895 | 3674.5544
2036-11-17 15:00 | 14325.7 | 4.8269 | 76.6327 | 53.895 | 4198.4482
2036-11-18 16:00 | 14515.6 | 4.7537 | 77.435 | 53.895 | 4254.1024
2036-11-19 17:00 | 13350.3 | 4.437 | 77.4969 | 53.895 | 3912.5867
2036-11-20 18:00 | 11362.3 | 3.6784 | 77.9423 | 53.895 | 3329.9614
2036-11-21 19:00 | 9286.59 | 2.9665 | 78.0385 | 53.895 | 2721.6309
2036-11-22 20:00 | 6624.76 | 2.0773 | 78.0874 | 53.895 | 1941.5255
2036-11-23 21:00 | 5162.41 | 1.5997 | 77.8291 | 53.895 | 1512.953
2036-11-24 22:00 | 3132.76 | 1 | 79.8168 | 53.895 | 918.1213
2036-11-25 23:00 | 3120.62 | 1 | 61.2475 | 53.895 | 914.5634
2036-11-27 | 3099.83 | 1 | 60.938 | 53.895 | 908.4705
2036-11-28 01:00 | 1812.92 | 1 | 60.9575 | 53.895 | 531.3144
2036-11-29 02:00 | 790.341 | 1 | 60.8204 | 53.895 | 231.6261
2036-11-30 03:00 | 1056.9 | 1 | 60.4122 | 53.895 | 309.7468
2036-12-01 04:00 | 586.573 | 1 | 60.2962 | 53.895 | 171.9076
2036-12-02 05:00 | 2980.63 | 1 | 59.6576 | 53.895 | 873.5364
2036-12-03 06:00 | 3102.37 | 1 | 59.74 | 53.895 | 909.2149
2036-12-04 07:00 | 3146.5 | 1 | 59.7778 | 53.895 | 922.1481
2036-12-05 08:00 | 3133.42 | 1 | 59.7924 | 53.895 | 918.3148
2036-12-06 09:00 | 4350.95 | 1.3713 | 75.2136 | 53.895 | 1275.1376
2036-12-07 10:00 | 7045.52 | 2.363 | 74.4236 | 53.895 | 2064.8381
2036-12-08 11:00 | 9183.72 | 3.0633 | 74.8538 | 53.895 | 2691.4826
2036-12-09 12:00 | 10396.2 | 3.4556 | 75.3346 | 53.895 | 3046.8255
2036-12-10 13:00 | 11083.6 | 3.671 | 75.7869 | 53.895 | 3248.2825
2036-12-11 14:00 | 11824.2 | 3.8953 | 76.2238 | 53.895 | 3465.3309
2036-12-12 15:00 | 13345.8 | 4.3871 | 76.5907 | 53.895 | 3911.2679
2036-12-13 16:00 | 13166.3 | 4.3208 | 77.0272 | 53.895 | 3858.6616
2036-12-14 17:00 | 12668.2 | 4.0466 | 77.6475 | 53.895 | 3712.6829
2036-12-15 18:00 | 10734.7 | 3.4232 | 77.7999 | 53.895 | 3146.03
2036-12-16 19:00 | 9168.86 | 2.8468 | 78.1204 | 53.895 | 2687.1276
2036-12-17 20:00 | 6746.56 | 2.0364 | 78.4047 | 53.895 | 1977.2216
2036-12-18 21:00 | 5632.56 | 1.6969 | 78.0897 | 53.895 | 1650.7404
2036-12-19 22:00 | 3111.06 | 1 | 78.4029 | 53.895 | 911.7617
2036-12-20 23:00 | 3054.11 | 1 | 61.2236 | 53.895 | 895.0713
2036-12-22 | 3011.79 | 1 | 60.9246 | 53.895 | 882.6685
2036-12-23 01:00 | 1751.82 | 1 | 60.9395 | 53.895 | 513.4078
2036-12-24 02:00 | 133.33 | 1 | 60.9112 | 53.895 | 39.0752
2036-12-25 03:00 | 43.2231 | 1 | 60.4906 | 53.895 | 12.6674
2036-12-26 04:00 | 45.4791 | 1 | 60.223 | 53.895 | 13.3286
2036-12-27 05:00 | 2024.59 | 1 | 59.6639 | 53.895 | 593.3488
2036-12-28 06:00 | 2691.75 | 1 | 59.5984 | 53.895 | 788.8741
2036-12-29 07:00 | 3055.57 | 1 | 59.6011 | 53.895 | 895.4992
2036-12-30 08:00 | 3171.55 | 1 | 59.6485 | 53.895 | 929.4896
2036-12-31 09:00 | 5009.85 | 1.548 | 75.4185 | 53.895 | 1468.2421
2037-01-01 10:00 | 7784.33 | 2.5884 | 74.5496 | 53.895 | 2281.3619
2037-01-02 11:00 | 9597.56 | 3.3195 | 74.4414 | 53.895 | 2812.7672
2037-01-03 12:00 | 11192.8 | 3.7624 | 75.2691 | 53.895 | 3280.2859
2037-01-04 13:00 | 12424.1 | 4.001 | 76.3346 | 53.895 | 3641.1443
2037-01-05 14:00 | 13359.5 | 4.303 | 76.8081 | 53.895 | 3915.283
2037-01-06 15:00 | 15079.6 | 4.8312 | 77.3115 | 53.895 | 4419.3945
2037-01-07 16:00 | 15014.7 | 4.7703 | 77.9321 | 53.895 | 4400.3742
2037-01-08 17:00 | 13973.5 | 4.4774 | 78.1328 | 53.895 | 4095.2286
2037-01-09 18:00 | 11942.2 | 3.7392 | 78.6027 | 53.895 | 3499.9133
2037-01-10 19:00 | 10496.4 | 3.2342 | 78.7624 | 53.895 | 3076.1912
2037-01-11 20:00 | 8429.13 | 2.4939 | 79.2725 | 53.895 | 2470.3341
2037-01-12 21:00 | 7191.97 | 2.2185 | 78.344 | 53.895 | 2107.7583
2037-01-13 22:00 | 5607.74 | 1.6045 | 79.2405 | 53.895 | 1643.4664
2037-01-14 23:00 | 4822.22 | 1.4634 | 77.9504 | 53.895 | 1413.2532
2037-01-16 | 4049.4 | 1.2576 | 77.3002 | 53.895 | 1186.762
2037-01-17 01:00 | 3614.52 | 1.1311 | 76.9061 | 53.895 | 1059.3112
2037-01-18 02:00 | 3453.59 | 1.0875 | 76.5869 | 53.895 | 1012.1473
2037-01-19 03:00 | 3543.95 | 1.1218 | 76.3163 | 53.895 | 1038.6292
2037-01-20 04:00 | 3600 | 1.1591 | 75.9414 | 53.895 | 1055.0559
2037-01-21 05:00 | 4473.44 | 1.4361 | 75.8739 | 53.895 | 1311.0358
2037-01-22 06:00 | 4439.62 | 1.4204 | 75.9485 | 53.895 | 1301.1242
2037-01-23 07:00 | 5772.04 | 1.7636 | 76.626 | 53.895 | 1691.6179
2037-01-24 08:00 | 6291.08 | 1.9968 | 76.2063 | 53.895 | 1843.7335
2037-01-25 09:00 | 6664.19 | 2.2238 | 75.6336 | 53.895 | 1953.0813
2037-01-26 10:00 | 8523.48 | 2.8218 | 75.8538 | 53.895 | 2497.9854
2037-01-27 11:00 | 9810.81 | 3.3393 | 75.7433 | 53.895 | 2875.2646
2037-01-28 12:00 | 11415.8 | 3.9359 | 75.8903 | 53.895 | 3345.6407
2037-01-29 13:00 | 11350.8 | 3.6708 | 77.1575 | 53.895 | 3326.5911
2037-01-30 14:00 | 12305.1 | 3.9765 | 77.3835 | 53.895 | 3606.2688
2037-01-31 15:00 | 13956.2 | 4.5815 | 77.4208 | 53.895 | 4090.1585
2037-02-01 16:00 | 12075.2 | 3.8569 | 78.2102 | 53.895 | 3538.8918
2037-02-02 17:00 | 10135.9 | 3.2742 | 78.0622 | 53.895 | 2970.5391
2037-02-03 18:00 | 8713.31 | 2.7096 | 78.4314 | 53.895 | 2553.6191
2037-02-04 19:00 | 7678.07 | 2.3235 | 78.6376 | 53.895 | 2250.2202
2037-02-05 20:00 | 5664.28 | 1.6125 | 79.4079 | 53.895 | 1660.0366
2037-02-06 21:00 | 4493.34 | 1.4246 | 77.3452 | 53.895 | 1316.868
2037-02-07 22:00 | 3102.65 | 1 | 82.8476 | 53.895 | 909.297
2037-02-08 23:00 | 3059.34 | 1 | 61.3307 | 53.895 | 896.604
2037-02-10 | 2964.24 | 1 | 61.1015 | 53.895 | 868.733
2037-02-11 01:00 | 0 | 0 | 61.4223 | 53.895 | 0
2037-02-12 02:00 | 764.503 | 1 | 60.7738 | 53.895 | 224.0537
2037-02-13 03:00 | 286.627 | 1 | 60.5975 | 53.895 | 84.0021
2037-02-14 04:00 | 1614.57 | 1 | 60.1502 | 53.895 | 473.1838
2037-02-15 05:00 | 1761.31 | 1 | 60.0843 | 53.895 | 516.189
2037-02-16 06:00 | 2609.59 | 1 | 75.6171 | 53.895 | 764.7953
2037-02-17 07:00 | 3753.92 | 1.2524 | 74.4032 | 53.895 | 1100.1654
2037-02-18 08:00 | 3108.15 | 1 | 80.8159 | 53.895 | 910.9088
2037-02-19 09:00 | 4214.74 | 1.2802 | 75.9175 | 53.895 | 1235.2184
2037-02-20 10:00 | 6556.26 | 2.2387 | 74.3155 | 53.895 | 1921.4501
2037-02-21 11:00 | 6772.5 | 2.205 | 75.3188 | 53.895 | 1984.8238
2037-02-22 12:00 | 9007.37 | 3.057 | 74.8958 | 53.895 | 2639.7996
2037-02-23 13:00 | 9742.88 | 3.2662 | 75.435 | 53.895 | 2855.3563
2037-02-24 14:00 | 9558.53 | 3.2433 | 75.6034 | 53.895 | 2801.3286
2037-02-25 15:00 | 10548.1 | 3.4697 | 76.205 | 53.895 | 3091.343
2037-02-26 16:00 | 12742.1 | 4.3609 | 75.8697 | 53.895 | 3734.3409
2037-02-27 17:00 | 10888.3 | 3.6708 | 76.5473 | 53.895 | 3191.0457
2037-02-28 18:00 | 9941.3 | 3.1252 | 77.6058 | 53.895 | 2913.5074
2037-03-01 19:00 | 8524.22 | 2.6283 | 77.8472 | 53.895 | 2498.2023
2037-03-02 20:00 | 7525.46 | 2.3104 | 77.8265 | 53.895 | 2205.4946
2037-03-03 21:00 | 6753.47 | 2.0618 | 77.7844 | 53.895 | 1979.2467
2037-03-04 22:00 | 6472.06 | 1.9386 | 77.8971 | 53.895 | 1896.7735
2037-03-05 23:00 | 3224.03 | 1 | 78.1899 | 53.895 | 944.8699
2037-03-07 | 3130.42 | 1 | 81.3228 | 53.895 | 917.4355
2037-03-08 01:00 | 3143.73 | 1 | 60.8953 | 53.895 | 921.3363
2037-03-09 02:00 | 3090.31 | 1 | 60.7726 | 53.895 | 905.6805
2037-03-10 03:00 | 3125.36 | 1 | 60.6305 | 53.895 | 915.9526
2037-03-11 04:00 | 3217.25 | 1 | 60.462 | 53.895 | 942.8829
2037-03-12 05:00 | 3082.93 | 1 | 60.4244 | 53.895 | 903.5176
2037-03-13 06:00 | 3109.53 | 1 | 81.6878 | 53.895 | 911.3133
2037-03-14 07:00 | 3908.38 | 1.2083 | 75.9311 | 53.895 | 1145.4331
2037-03-15 08:00 | 3233.9 | 1 | 60.2994 | 53.895 | 947.7625
2037-03-16 09:00 | 3200.26 | 1 | 60.2318 | 53.895 | 937.9036
2037-03-17 10:00 | 3231.52 | 1 | 60.1317 | 53.895 | 947.065
2037-03-18 11:00 | 3351.97 | 1 | 76.506 | 53.895 | 982.3654
2037-03-19 12:00 | 4361.19 | 1.3589 | 75.6113 | 53.895 | 1278.1386
2037-03-20 13:00 | 5337.39 | 1.6228 | 76.033 | 53.895 | 1564.2346
2037-03-21 14:00 | 5928.54 | 1.9931 | 74.6863 | 53.895 | 1737.4836
2037-03-22 15:00 | 4501.99 | 1.5351 | 74.6064 | 53.895 | 1319.403
2037-03-23 16:00 | 7621.3 | 2.6128 | 74.3802 | 53.895 | 2233.5825
2037-03-24 17:00 | 6141.94 | 2.0055 | 75.3838 | 53.895 | 1800.0249
2037-03-25 18:00 | 4970.07 | 1.5977 | 75.6205 | 53.895 | 1456.5837
2037-03-26 19:00 | 3559.79 | 1.2706 | 74.0053 | 53.895 | 1043.2715
2037-03-27 20:00 | 3061.9 | 1 | 79.0917 | 53.895 | 897.3543
2037-03-28 21:00 | 2956.07 | 1 | 60.0073 | 53.895 | 866.3386
2037-03-29 22:00 | 2901.22 | 1 | 59.88 | 53.895 | 850.2636
2037-03-30 23:00 | -562.793 | 2.2436 | 59.1243 | 53.895 | -164.9383
2037-04-01 | -1057.79 | 3.5102 | 58.399 | 53.895 | -310.0076
2037-04-02 01:00 | -1237.28 | 3.9308 | 57.9949 | 53.895 | -362.611
2037-04-03 02:00 | -1416.7 | 4.4277 | 57.7461 | 53.895 | -415.1938
2037-04-04 03:00 | -1507.15 | 4.6578 | 57.5252 | 53.895 | -441.7021
2037-04-05 04:00 | -1499.45 | 4.6269 | 57.2873 | 53.895 | -439.4454
2037-04-06 05:00 | -1236.86 | 3.8615 | 57.1646 | 53.895 | -362.4879
2037-04-07 06:00 | -1174.77 | 3.7566 | 57.1142 | 53.895 | -344.2911
2037-04-08 07:00 | -837.407 | 2.775 | 57.0814 | 53.895 | -245.4198
2037-04-09 08:00 | -623.511 | 2.2415 | 57.1528 | 53.895 | -182.733
2037-04-10 09:00 | 2323.12 | 1 | 58.0249 | 53.895 | 680.8393
2037-04-11 10:00 | 4566.88 | 1.5297 | 72.7308 | 53.895 | 1338.4204
2037-04-12 11:00 | 7003.86 | 2.4451 | 72.5592 | 53.895 | 2052.6287
2037-04-13 12:00 | 8067.58 | 2.8115 | 73.1081 | 53.895 | 2364.3743
2037-04-14 13:00 | 8886.71 | 2.955 | 74.2003 | 53.895 | 2604.4376
2037-04-15 14:00 | 9420.2 | 3.1542 | 74.5132 | 53.895 | 2760.7881
2037-04-16 15:00 | 10964 | 3.6131 | 75.0784 | 53.895 | 3213.2312
2037-04-17 16:00 | 10886.9 | 3.5426 | 75.6734 | 53.895 | 3190.6354
2037-04-18 17:00 | 10096 | 3.2289 | 76.1976 | 53.895 | 2958.8455
2037-04-19 18:00 | 7845.24 | 2.3835 | 77.0943 | 53.895 | 2299.2129
2037-04-20 19:00 | 6105.43 | 1.8423 | 77.0806 | 53.895 | 1789.3249
2037-04-21 20:00 | 3158.09 | 1.0125 | 75.9754 | 53.895 | 925.5448
2037-04-22 21:00 | 3123.97 | 1 | 60.3752 | 53.895 | 915.5452
2037-04-23 22:00 | 0 | 0 | 60.6391 | 53.895 | 0
2037-04-24 23:00 | -426.65 | 1.8562 | 59.0043 | 53.895 | -125.0388
2037-04-26 | -945.1 | 3.2234 | 58.3026 | 53.895 | -276.9815
2037-04-27 01:00 | -965.678 | 3.1707 | 57.9282 | 53.895 | -283.0123
2037-04-28 02:00 | -1298.21 | 4.1583 | 57.6673 | 53.895 | -380.4678
2037-04-29 03:00 | -1137.77 | 3.6057 | 57.3856 | 53.895 | -333.4475
2037-04-30 04:00 | -936.5 | 3.0738 | 57.2739 | 53.895 | -274.4611
2037-05-01 05:00 | -575.84 | 2.0697 | 57.2768 | 53.895 | -168.762
2037-05-02 06:00 | -521.88 | 2.0083 | 57.3046 | 53.895 | -152.9479
2037-05-03 07:00 | 0 | 1 | 58.4597 | 53.895 | 0
2037-05-04 08:00 | 2096.67 | 1 | 58.1217 | 53.895 | 614.4733
2037-05-05 09:00 | 3416.51 | 1.2148 | 71.916 | 53.895 | 1001.2802
2037-05-06 10:00 | 5865.72 | 2.0615 | 72.3118 | 53.895 | 1719.0728
2037-05-07 11:00 | 7986.74 | 2.7905 | 72.8186 | 53.895 | 2340.6824
2037-05-08 12:00 | 9406.31 | 3.1929 | 73.7306 | 53.895 | 2756.7173
2037-05-09 13:00 | 10191.4 | 3.3687 | 74.5942 | 53.895 | 2986.8045
2037-05-10 14:00 | 10813.2 | 3.5602 | 75.0545 | 53.895 | 3169.0361
2037-05-11 15:00 | 12255.2 | 4.0505 | 75.3586 | 53.895 | 3591.6446
2037-05-12 16:00 | 12212.4 | 3.9408 | 76.1285 | 53.895 | 3579.1011
2037-05-13 17:00 | 11355.8 | 3.683 | 76.3486 | 53.895 | 3328.0565
2037-05-14 18:00 | 9536.96 | 3.0362 | 76.7563 | 53.895 | 2795.0071
2037-05-15 19:00 | 7782.4 | 2.4386 | 76.942 | 53.895 | 2280.7963
2037-05-16 20:00 | 5547.01 | 1.6878 | 77.2291 | 53.895 | 1625.6682
2037-05-17 21:00 | 4116.48 | 1.3072 | 76.253 | 53.895 | 1206.4212
2037-05-18 22:00 | 3098.53 | 1 | 60.6367 | 53.895 | 908.0895
2037-05-19 23:00 | 3022.32 | 1 | 60.3328 | 53.895 | 885.7546
2037-05-21 | 1402.58 | 1 | 60.405 | 53.895 | 411.0556
2037-05-22 01:00 | -19.0612 | 0.71923 | 60.1817 | 53.895 | -5.5863
2037-05-23 02:00 | -302.862 | 1.4638 | 58.9447 | 53.895 | -88.7601
2037-05-24 03:00 | -401.605 | 1.6908 | 58.5142 | 53.895 | -117.6988
2037-05-25 04:00 | -171.25 | 1.0109 | 58.6125 | 53.895 | -50.1884
2037-05-26 05:00 | 71.4127 | 1 | 59.2252 | 53.895 | 20.929
2037-05-27 06:01 | -96.1404 | 0.90447 | 58.6397 | 53.895 | -28.176
2037-05-28 07:01 | 2192.84 | 1 | 58.6632 | 53.895 | 642.658
2037-05-29 08:01 | 3031.43 | 1 | 58.724 | 53.895 | 888.4244
2037-05-30 09:01 | 3464.13 | 1.12 | 73.957 | 53.895 | 1015.2363
2037-05-31 10:01 | 6384.71 | 2.0921 | 73.8291 | 53.895 | 1871.1738
2037-06-01 11:01 | 8467.3 | 2.8919 | 73.6498 | 53.895 | 2481.5207
2037-06-02 12:01 | 10076.8 | 3.383 | 74.3906 | 53.895 | 2953.2186
2037-06-03 13:01 | 10907.8 | 3.5741 | 75.2002 | 53.895 | 3196.7606
2037-06-04 14:01 | 11772.6 | 3.8885 | 75.4876 | 53.895 | 3450.2085
2037-06-05 15:01 | 13229.8 | 4.3704 | 75.8781 | 53.895 | 3877.2716
2037-06-06 16:01 | 13176.1 | 4.3168 | 76.4374 | 53.895 | 3861.5337
2037-06-07 17:01 | 12546.5 | 4.0273 | 77.0316 | 53.895 | 3677.0162
2037-06-08 18:01 | 10519 | 3.2702 | 77.6751 | 53.895 | 3082.8146
2037-06-09 19:01 | 8584.02 | 2.706 | 77.3954 | 53.895 | 2515.7279
2037-06-10 20:01 | 6247.19 | 1.8264 | 78.3687 | 53.895 | 1830.8707
2037-06-11 21:01 | 4534.45 | 1.42 | 76.9602 | 53.895 | 1328.9161
2037-06-12 22:01 | 3136.06 | 1 | 61.0889 | 53.895 | 919.0885
2037-06-13 23:01 | 3052.93 | 1 | 60.6996 | 53.895 | 894.7255
2037-06-15 00:01 | 2938.03 | 1 | 60.4611 | 53.895 | 861.0516
2037-06-16 01:01 | 251.976 | 1 | 60.7408 | 53.895 | 73.8469
2037-06-17 02:01 | -59.4081 | 0.80036 | 59.9683 | 53.895 | -17.4108
2037-06-18 03:01 | -87.3326 | 0.84664 | 59.489 | 53.895 | -25.5947
2037-06-19 04:01 | -22.0472 | 0.65879 | 59.7695 | 53.895 | -6.4614
2037-06-20 05:01 | 1756.77 | 1 | 59.2563 | 53.895 | 514.8585
2037-06-21 06:01 | 0 | 0 | 59.6062 | 53.895 | 0
2037-06-22 07:01 | 3433.85 | 1 | 58.8099 | 53.895 | 1006.3621
2037-06-23 08:01 | 3265.37 | 1 | 81.3557 | 53.895 | 956.9855
2037-06-24 09:01 | 5824.48 | 1.7958 | 74.9803 | 53.895 | 1706.9866
2037-06-25 10:01 | 8250.64 | 2.8897 | 73.5247 | 53.895 | 2418.0239
2037-06-26 11:01 | 10520.5 | 3.5717 | 74.4192 | 53.895 | 3083.2542
2037-06-27 12:01 | 11655.6 | 3.9537 | 75.0016 | 53.895 | 3415.9192
2037-06-28 13:01 | 12537.1 | 4.1424 | 75.8381 | 53.895 | 3674.2613
2037-06-29 14:01 | 12981 | 4.2215 | 76.5135 | 53.895 | 3804.3556
2037-06-30 15:01 | 14191.9 | 4.3127 | 77.8798 | 53.895 | 4159.2353
2037-07-01 16:01 | 12421.4 | 3.8428 | 78.0178 | 53.895 | 3640.353
2037-07-02 17:01 | 10079.4 | 3.2012 | 77.6882 | 53.895 | 2953.9805
2037-07-03 18:01 | 6759.47 | 2.2737 | 76.7074 | 53.895 | 1981.0051
2037-07-04 19:01 | 5322.07 | 1.7281 | 76.7718 | 53.895 | 1559.7447
2037-07-05 20:01 | 2913.32 | 1 | 78.0376 | 53.895 | 853.8098
2037-07-06 21:01 | 3072.79 | 1 | 60.9493 | 53.895 | 900.5459
2037-07-07 22:01 | -188.829 | 1.1564 | 60.4104 | 53.895 | -55.3403
2037-07-08 23:01 | -712.296 | 2.5794 | 59.2646 | 53.895 | -208.7534
2037-07-10 00:01 | -1232.36 | 3.9714 | 58.6495 | 53.895 | -361.1691
2037-07-11 01:01 | -1543.3 | 4.7649 | 58.2345 | 53.895 | -452.2966
2037-07-12 02:01 | -1666.95 | 5.0695 | 57.9133 | 53.895 | -488.5348
2037-07-13 03:01 | -1708.06 | 5.1805 | 57.6124 | 53.895 | -500.583
2037-07-14 04:01 | -1744.97 | 5.2922 | 57.4117 | 53.895 | -511.4002
2037-07-15 05:01 | -1554.15 | 4.7281 | 57.2398 | 53.895 | -455.4764
2037-07-16 06:01 | -1708.47 | 5.2467 | 57.1599 | 53.895 | -500.7031
2037-07-17 07:01 | -1519.77 | 4.644 | 57.0253 | 53.895 | -445.4006
2037-07-18 08:01 | -1347.91 | 4.1977 | 56.9778 | 53.895 | -395.0334
2037-07-19 09:01 | -470.471 | 1.6548 | 57.0679 | 53.895 | -137.8814
2037-07-20 10:01 | 2723.84 | 1 | 57.9572 | 53.895 | 798.2787
2037-07-21 11:01 | 3100.93 | 1.0514 | 72.6178 | 53.895 | 908.7929
2037-07-22 12:01 | 4616.04 | 1.4992 | 73.3783 | 53.895 | 1352.8278
2037-07-23 13:01 | 5521.91 | 1.7967 | 73.6044 | 53.895 | 1618.3121
2037-07-24 14:01 | 6425.77 | 2.0783 | 73.9592 | 53.895 | 1883.2073
2037-07-25 15:01 | 7767.25 | 2.5899 | 73.7776 | 53.895 | 2276.3563
2037-07-26 16:01 | 7479.11 | 2.4917 | 74.0848 | 53.895 | 2191.9108
2037-07-27 17:01 | 6294.31 | 2.0581 | 74.5202 | 53.895 | 1844.6802
2037-07-28 18:01 | 4621.65 | 1.477 | 74.8458 | 53.895 | 1354.4719
2037-07-29 19:01 | 3092.77 | 1.0263 | 74.157 | 53.895 | 906.4014
2037-07-30 20:01 | 2919.41 | 1 | 59.3335 | 53.895 | 855.5946
2037-07-31 21:01 | 0 | 0 | 59.7057 | 53.895 | 0
2037-08-01 22:01 | -961.37 | 3.4081 | 57.939 | 53.895 | -281.7497
2037-08-02 23:01 | -1698.76 | 5.3328 | 57.3881 | 53.895 | -497.8574
2037-08-04 00:01 | -2123.86 | 6.4335 | 57.0261 | 53.895 | -622.4419
2037-08-05 01:01 | -2410.57 | 6.8587 | 56.6644 | 53.895 | -706.4683
2037-08-06 02:01 | -2698.83 | 6.8587 | 56.2112 | 53.895 | -790.949
2037-08-07 03:01 | -2943.99 | 6.8587 | 55.826 | 53.895 | -862.7983
2037-08-08 04:01 | -3151.39 | 6.8587 | 55.4827 | 53.895 | -923.5812
2037-08-09 05:01 | -3164.39 | 6.8587 | 55.2885 | 53.895 | -927.3912
2037-08-10 06:01 | -2560.35 | 6.8587 | 55.5635 | 53.895 | -750.3645
2037-08-11 07:01 | -1825.82 | 5.5005 | 55.7103 | 53.895 | -535.095
2037-08-12 08:01 | -1566.32 | 4.8366 | 55.7665 | 53.895 | -459.0431
2037-08-13 09:01 | -626.077 | 2.0769 | 55.8847 | 53.895 | -183.4851
2037-08-14 10:01 | 2359.02 | 1 | 56.9775 | 53.895 | 691.3605
2037-08-15 11:01 | 3092.84 | 1 | 73.1153 | 53.895 | 906.4219
2037-08-16 12:01 | 4545.94 | 1.4819 | 72.4054 | 53.895 | 1332.2835
2037-08-17 13:01 | 5249.86 | 1.743 | 72.4506 | 53.895 | 1538.5821
2037-08-18 14:01 | 6159.49 | 2.0059 | 73.0083 | 53.895 | 1805.1683
2037-08-19 15:01 | 6456.8 | 2.1109 | 73.2372 | 53.895 | 1892.3013
2037-08-20 16:01 | 8269.45 | 2.763 | 73.1246 | 53.895 | 2423.5366
2037-08-21 17:01 | 6616.31 | 2.1939 | 73.6209 | 53.895 | 1939.0491
2037-08-22 18:01 | 4915.79 | 1.5703 | 74.2234 | 53.895 | 1440.6758
2037-08-23 19:01 | 3116.5 | 1.0069 | 73.9349 | 53.895 | 913.356
2037-08-24 20:01 | 3068.67 | 1 | 81.2303 | 53.895 | 899.3384
2037-08-25 21:01 | 3017.81 | 1 | 58.6212 | 53.895 | 884.4328
2037-08-26 22:01 | 2892.79 | 1 | 58.5714 | 53.895 | 847.7931
2037-08-27 23:01 | -966.186 | 3.45 | 57.6993 | 53.895 | -283.1612
2037-08-29 00:01 | -1481.15 | 4.7085 | 57.0346 | 53.895 | -434.0822
2037-08-30 01:01 | -1824.51 | 5.6309 | 56.6629 | 53.895 | -534.7111
2037-08-31 02:01 | -2034.31 | 6.1872 | 56.4109 | 53.895 | -596.1974
2037-09-01 03:01 | -2479.7 | 6.8587 | 56.0356 | 53.895 | -726.7283
2037-09-02 04:01 | -2708.35 | 6.8587 | 55.6059 | 53.895 | -793.739
2037-09-03 05:01 | -2803.7 | 6.8587 | 55.3647 | 53.895 | -821.6834
2037-09-04 06:01 | -2069.64 | 6.2672 | 55.5942 | 53.895 | -606.5516
2037-09-05 07:01 | -1492.38 | 4.5456 | 55.5847 | 53.895 | -437.3734
2037-09-06 08:01 | -1411.69 | 4.4735 | 55.667 | 53.895 | -413.7255
2037-09-07 09:01 | -391.24 | 1.415 | 55.8279 | 53.895 | -114.6611
2037-09-08 10:01 | 2461.86 | 1 | 56.7655 | 53.895 | 721.4999
2037-09-09 11:01 | 3767.6 | 1.2627 | 71.5895 | 53.895 | 1104.1746
2037-09-10 12:01 | 5668.65 | 1.8529 | 72.2466 | 53.895 | 1661.3173
2037-09-11 13:01 | 6809.23 | 2.2164 | 72.7165 | 53.895 | 1995.5883
2037-09-12 14:01 | 7496.18 | 2.488 | 72.8459 | 53.895 | 2196.9135
2037-09-13 15:01 | 8057.49 | 2.6492 | 73.3299 | 53.895 | 2361.4172
2037-09-14 16:01 | 10070.2 | 3.3041 | 73.6354 | 53.895 | 2951.2843
2037-09-15 17:01 | 8425.21 | 2.7676 | 74.096 | 53.895 | 2469.1853
2037-09-16 18:01 | 6750.44 | 2.1759 | 74.4898 | 53.895 | 1978.3587
2037-09-17 19:01 | 5290.43 | 1.6621 | 74.7907 | 53.895 | 1550.472
2037-09-18 20:01 | 3884.21 | 1.2485 | 74.3241 | 53.895 | 1138.3496
2037-09-19 21:01 | 3129.76 | 1 | 78.3107 | 53.895 | 917.2421
2037-09-20 22:01 | 3082.36 | 1 | 58.8041 | 53.895 | 903.3505
2037-09-21 23:01 | -270.564 | 1.4042 | 58.3272 | 53.895 | -79.2945
2037-09-23 00:01 | -529.561 | 2.0853 | 57.557 | 53.895 | -155.199
2037-09-24 01:01 | -807.261 | 2.8473 | 57.103 | 53.895 | -236.5848
2037-09-25 02:01 | -1096.61 | 3.6393 | 56.8127 | 53.895 | -321.3847
2037-09-26 03:01 | -1075.44 | 3.51 | 56.5805 | 53.895 | -315.1804
2037-09-27 04:01 | -1071 | 3.5182 | 56.3895 | 53.895 | -313.8791
2037-09-28 05:01 | -866.218 | 2.9115 | 56.3142 | 53.895 | -253.8634
2037-09-29 06:01 | -857.528 | 2.9467 | 56.2816 | 53.895 | -251.3166
2037-09-30 07:01 | -598.317 | 2.1738 | 56.2925 | 53.895 | -175.3494
2037-10-01 08:01 | -330.702 | 1.4549 | 56.5001 | 53.895 | -96.9192
2037-10-02 09:01 | 2204.38 | 1 | 57.1871 | 53.895 | 646.04
2037-10-03 10:01 | 4235.2 | 1.4702 | 71.3507 | 53.895 | 1241.2146
2037-10-04 11:01 | 6847.86 | 2.3793 | 71.6872 | 53.895 | 2006.9097
2037-10-05 12:01 | 7446.58 | 2.5041 | 72.6548 | 53.895 | 2182.3772
2037-10-06 13:01 | 7594.38 | 2.4585 | 73.5794 | 53.895 | 2225.6931
2037-10-07 14:01 | 7352.54 | 2.2737 | 74.5385 | 53.895 | 2154.8168
2037-10-08 15:01 | 8826.13 | 2.8635 | 73.9907 | 53.895 | 2586.6834
2037-10-09 16:01 | 8525.34 | 2.7651 | 74.2994 | 53.895 | 2498.5305
2037-10-10 17:01 | 8273.04 | 2.6258 | 74.7722 | 53.895 | 2424.5887
2037-10-11 18:01 | 6986.27 | 2.1521 | 75.3252 | 53.895 | 2047.4736
2037-10-12 19:01 | 6162.23 | 1.9081 | 75.2227 | 53.895 | 1805.9713
2037-10-13 20:01 | 3696.74 | 1.1447 | 75.1913 | 53.895 | 1083.4075
2037-10-14 21:01 | 3092.52 | 1 | 78.0024 | 53.895 | 906.3281
2037-10-15 22:01 | 3125.79 | 1 | 58.9748 | 53.895 | 916.0786
2037-10-16 23:01 | 1703.5 | 1 | 59.1027 | 53.895 | 499.2466
2037-10-18 00:01 | 275.117 | 1 | 59.0884 | 53.895 | 80.6288
2037-10-19 01:01 | 173.04 | 1 | 58.7589 | 53.895 | 50.713
2037-10-20 02:01 | 0 | 0 | 58.6032 | 53.895 | 0
2037-10-21 03:01 | 302.569 | 1 | 58.3927 | 53.895 | 88.6742
2037-10-22 04:01 | 1741.25 | 1 | 58.0395 | 53.895 | 510.31
2037-10-23 05:01 | 2613.98 | 1 | 57.983 | 53.895 | 766.0819
2037-10-24 06:01 | 2988.28 | 1 | 58.078 | 53.895 | 875.7784
2037-10-25 07:01 | 3103.13 | 1 | 58.1806 | 53.895 | 909.4376
2037-10-26 08:01 | 3041.56 | 1 | 58.308 | 53.895 | 891.3932
2037-10-27 09:01 | 3169.77 | 1 | 58.3583 | 53.895 | 928.9679
2037-10-28 10:01 | 3201.02 | 1 | 58.3858 | 53.895 | 938.1264
2037-10-29 11:01 | 3183.64 | 1 | 79.0382 | 53.895 | 933.0328
2037-10-30 12:01 | 3202.84 | 1 | 74.4687 | 53.895 | 938.6597
2037-10-31 13:01 | 4716.34 | 1.4235 | 74.4315 | 53.895 | 1382.2228
2037-11-01 14:01 | 5972.94 | 1.9975 | 73.0945 | 53.895 | 1750.4959
2037-11-02 15:01 | 7928.35 | 2.7217 | 72.9683 | 53.895 | 2323.57
2037-11-03 16:01 | 8333.46 | 2.7454 | 73.8912 | 53.895 | 2442.296
2037-11-04 17:01 | 8366.33 | 2.6822 | 74.5422 | 53.895 | 2451.9293
2037-11-05 18:01 | 7146.08 | 2.1521 | 75.6814 | 53.895 | 2094.3093
2037-11-06 19:01 | 6205.73 | 1.8583 | 75.7783 | 53.895 | 1818.7199
2037-11-07 20:01 | 3993.49 | 1.2277 | 75.3275 | 53.895 | 1170.3764
2037-11-08 21:01 | 3186.75 | 1.0014 | 74.7282 | 53.895 | 933.9442
2037-11-09 22:01 | 3066.92 | 1 | 59.0693 | 53.895 | 898.8255
2037-11-10 23:01 | 2973.35 | 1 | 58.9697 | 53.895 | 871.4029
2037-11-12 00:01 | 0 | 0 | 59.4154 | 53.895 | 0
2037-11-13 01:01 | 0 | 1 | 58.9928 | 53.895 | 0
2037-11-14 02:01 | -50.8558 | 0.78308 | 58.4569 | 53.895 | -14.9044
2037-11-15 03:01 | 607.427 | 1 | 58.5086 | 53.895 | 178.0193
2037-11-16 04:01 | 1814.91 | 1 | 58.2272 | 53.895 | 531.8976
2037-11-17 05:01 | 2655.11 | 1 | 58.1231 | 53.895 | 778.1359
2037-11-18 06:01 | 3029.93 | 1 | 58.1913 | 53.895 | 887.9848
2037-11-19 07:01 | 3142.22 | 1 | 58.2767 | 53.895 | 920.8938
2037-11-20 08:01 | 3021.18 | 1 | 58.3924 | 53.895 | 885.4205
2037-11-21 09:01 | 2908.69 | 1 | 58.4584 | 53.895 | 852.4529
2037-11-22 10:01 | 3017.63 | 1 | 58.4389 | 53.895 | 884.3801
2037-11-23 11:01 | 2964.31 | 1 | 58.4442 | 53.895 | 868.7535
2037-11-24 12:01 | 3081.63 | 1 | 58.4291 | 53.895 | 903.1366
2037-11-25 13:01 | 3072.37 | 1 | 58.4372 | 53.895 | 900.4228
2037-11-26 14:01 | 3186.97 | 1 | 58.4134 | 53.895 | 934.0087
2037-11-27 15:01 | 4219.75 | 1.3568 | 73.5421 | 53.895 | 1236.6866
2037-11-28 16:01 | 4556.93 | 1.4869 | 73.3774 | 53.895 | 1335.5044
2037-11-29 17:01 | 4740.08 | 1.5452 | 73.4616 | 53.895 | 1389.1803
2037-11-30 18:01 | 3621.55 | 1.1557 | 73.8278 | 53.895 | 1061.3715
2037-12-01 19:01 | 3091.98 | 1 | 77.1407 | 53.895 | 906.1699
2037-12-02 20:01 | 2990.56 | 1 | 58.4554 | 53.895 | 876.4466
2037-12-03 21:01 | 0 | 0 | 58.9241 | 53.895 | 0
2037-12-04 22:01 | -606.831 | 2.3841 | 57.3197 | 53.895 | -177.8446
2037-12-05 23:01 | -872.177 | 3.0208 | 56.8388 | 53.895 | -255.6098
2037-12-07 00:01 | -1154.84 | 3.8061 | 56.5849 | 53.895 | -338.4502
2037-12-08 01:01 | -1331.08 | 4.2652 | 56.3693 | 53.895 | -390.101
2037-12-09 02:01 | -1265.55 | 4.0333 | 56.189 | 53.895 | -370.8961
2037-12-10 03:01 | -1196.41 | 3.8539 | 56.1064 | 53.895 | -350.6332
2037-12-11 04:01 | -1219.23 | 3.9444 | 56.0248 | 53.895 | -357.321
2037-12-12 05:01 | -1105.49 | 3.599 | 55.934 | 53.895 | -323.9871
2037-12-13 06:01 | -1130.66 | 3.7119 | 55.8731 | 53.895 | -331.3637
2037-12-14 07:01 | -744.132 | 2.5443 | 55.8529 | 53.895 | -218.0836
2037-12-15 08:01 | -646.898 | 2.3683 | 55.9129 | 53.895 | -189.5871
2037-12-16 09:01 | 1953.82 | 1 | 56.8494 | 53.895 | 572.6081
2037-12-17 10:01 | 3572.26 | 1.2277 | 71.1389 | 53.895 | 1046.9261
2037-12-18 11:01 | 5795.3 | 2.0256 | 71.2199 | 53.895 | 1698.4348
2037-12-19 12:01 | 6822.18 | 2.2676 | 72.3725 | 53.895 | 1999.3836
2037-12-20 13:01 | 7576.16 | 2.5015 | 72.8773 | 53.895 | 2220.3533
2037-12-21 14:01 | 7766.04 | 2.5486 | 73.3419 | 53.895 | 2276.0017
2037-12-22 15:01 | 9484.77 | 3.15 | 73.4295 | 53.895 | 2779.7117
2037-12-23 16:01 | 9404.18 | 3.0947 | 73.9648 | 53.895 | 2756.0931
2037-12-24 17:01 | 8644.51 | 2.765 | 74.6327 | 53.895 | 2533.4558
2037-12-25 18:01 | 6784.84 | 2.0655 | 75.4835 | 53.895 | 1988.4403
2037-12-26 19:01 | 5508.32 | 1.6612 | 75.5356 | 53.895 | 1614.3292
2037-12-27 20:01 | 3138.38 | 1 | 77.0271 | 53.895 | 919.7684
2037-12-28 21:01 | 3133.52 | 1 | 59.0133 | 53.895 | 918.3441
2037-12-29 22:01 | 0 | 0 | 59.3711 | 53.895 | 0
2037-12-30 23:01 | -430.968 | 1.7071 | 57.6794 | 53.895 | -126.3043
2038-01-01 00:01 | -481.876 | 1.9251 | 57.3295 | 53.895 | -141.2239
2038-01-02 01:01 | -618.721 | 2.3122 | 57.0251 | 53.895 | -181.3292
2038-01-03 02:01 | -466.44 | 1.8324 | 56.9094 | 53.895 | -136.7001
2038-01-04 03:01 | -336.688 | 1.499 | 56.881 | 53.895 | -98.6735
2038-01-05 04:01 | -281.239 | 1.3684 | 56.8769 | 53.895 | -82.423
2038-01-06 05:01 | 13.2572 | 1 | 57.7537 | 53.895 | 3.8853
2038-01-07 06:01 | 296.724 | 1 | 57.6687 | 53.895 | 86.9612
2038-01-08 07:01 | 3197.66 | 1 | 57.1619 | 53.895 | 937.1416
2038-01-09 08:01 | -313.466 | 1.593 | 57.1399 | 53.895 | -91.8678
2038-01-10 09:01 | -207.448 | 1.1435 | 56.9454 | 53.895 | -60.797
2038-01-11 10:01 | 2371.94 | 1.0996 | 67.7821 | 53.895 | 695.147
2038-01-12 11:01 | 3772.9 | 1.37 | 70.8103 | 53.895 | 1105.7278
2038-01-13 12:01 | 6204.48 | 2.1794 | 71.5157 | 53.895 | 1818.3536
2038-01-14 13:01 | 7366.76 | 2.5639 | 72.0042 | 53.895 | 2158.9842
2038-01-15 14:01 | 7514.6 | 2.531 | 72.8665 | 53.895 | 2202.3119
2038-01-16 15:01 | 9259.58 | 3.187 | 72.8401 | 53.895 | 2713.715
2038-01-17 16:01 | 9245.02 | 3.1139 | 73.5371 | 53.895 | 2709.4479
2038-01-18 17:01 | 8603.74 | 2.7597 | 74.5101 | 53.895 | 2521.5073
2038-01-19 18:01 | 6604.22 | 2.0785 | 74.902 | 53.895 | 1935.5058
2038-01-20 19:01 | 5283.1 | 1.6397 | 74.9634 | 53.895 | 1548.3238
2038-01-21 20:01 | 3067.19 | 1 | 78.0291 | 53.895 | 898.9047
2038-01-22 21:01 | 3071 | 1 | 58.9054 | 53.895 | 900.0213
2038-01-23 22:01 | -203.002 | 1.2189 | 58.4977 | 53.895 | -59.494
2038-01-24 23:01 | -881.905 | 3.1249 | 57.4596 | 53.895 | -258.4608
2038-01-26 00:01 | -1467.23 | 4.7045 | 56.9294 | 53.895 | -430.0027
2038-01-27 01:01 | -1750.46 | 5.4169 | 56.5667 | 53.895 | -513.0092
2038-01-28 02:01 | -2010.83 | 6.1477 | 56.2991 | 53.895 | -589.3161
2038-01-29 03:01 | -2070.56 | 6.2772 | 56.0176 | 53.895 | -606.8212
2038-01-30 04:01 | -2264.7 | 6.8587 | 55.8288 | 53.895 | -663.7181
2038-01-31 05:01 | -2381.2 | 6.8587 | 55.5656 | 53.895 | -697.8608
2038-02-01 06:01 | -1744.29 | 5.2609 | 55.4811 | 53.895 | -511.2009
2038-02-02 07:01 | -855.372 | 2.7318 | 55.5035 | 53.895 | -250.6848
2038-02-03 08:01 | -255.133 | 1.1834 | 56.0267 | 53.895 | -74.7721
2038-02-04 09:01 | 2048.24 | 1 | 71.4107 | 53.895 | 600.2799
2038-02-05 10:01 | 4342.84 | 1.557 | 70.4718 | 53.895 | 1272.7608
2038-02-06 11:01 | 5803 | 2.0393 | 71.1888 | 53.895 | 1700.6914
2038-02-07 12:01 | 7169.23 | 2.4631 | 71.9094 | 53.895 | 2101.0939
2038-02-08 13:01 | 7837.84 | 2.626 | 72.6708 | 53.895 | 2297.0442
2038-02-09 14:01 | 8671.01 | 2.8941 | 73.0913 | 53.895 | 2541.2222
2038-02-10 15:01 | 9195.22 | 3.0754 | 73.3927 | 53.895 | 2694.853
2038-02-11 16:01 | 11452.1 | 3.8027 | 73.7735 | 53.895 | 3356.2792
2038-02-12 17:01 | 9567.55 | 3.055 | 74.8353 | 53.895 | 2803.9721
2038-02-13 18:01 | 7266.17 | 2.3112 | 75.0083 | 53.895 | 2129.5042
2038-02-14 19:01 | 5889.15 | 1.8101 | 75.3669 | 53.895 | 1725.9395
2038-02-15 20:01 | 4254.31 | 1.314 | 75.1429 | 53.895 | 1246.8152
2038-02-16 21:01 | 3349.58 | 1.0796 | 74.2686 | 53.895 | 981.665
2038-02-17 22:01 | 3152.28 | 1 | 82.4088 | 53.895 | 923.8421
2038-02-18 23:01 | 0 | 0 | 59.306 | 53.895 | 0
2038-02-20 00:01 | -683.902 | 2.5065 | 57.541 | 53.895 | -200.4319
2038-02-21 01:01 | -985.467 | 3.3331 | 57.0578 | 53.895 | -288.8119
2038-02-22 02:01 | -1265.88 | 4.0972 | 56.7424 | 53.895 | -370.9928
2038-02-23 03:01 | -1306.84 | 4.1579 | 56.4782 | 53.895 | -382.997
2038-02-24 04:01 | -1589.26 | 5.012 | 56.2258 | 53.895 | -465.7661
2038-02-25 05:01 | -1720.73 | 5.3358 | 56.0196 | 53.895 | -504.2962
2038-02-26 06:01 | -1020.96 | 3.2067 | 55.8875 | 53.895 | -299.2138
2038-02-27 07:01 | -280.858 | 1.2091 | 56.2509 | 53.895 | -82.3114
2038-02-28 08:01 | 0 | 1 | 57.392 | 53.895 | 0
2038-03-01 09:01 | 2237.78 | 1 | 69.8405 | 53.895 | 655.8286
2038-03-02 10:01 | 4709.18 | 1.6425 | 71.0808 | 53.895 | 1380.1244
2038-03-03 11:01 | 6424.92 | 2.1886 | 71.8473 | 53.895 | 1882.9582
2038-03-04 12:01 | 7800.86 | 2.538 | 72.9353 | 53.895 | 2286.2064
2038-03-05 13:01 | 7752.65 | 2.5672 | 73.1155 | 53.895 | 2272.0774
2038-03-06 14:01 | 7697.88 | 2.4882 | 73.7565 | 53.895 | 2256.0259
2038-03-07 15:01 | 6900.14 | 2.2066 | 74.1063 | 53.895 | 2022.2314
2038-03-08 16:01 | 8165.24 | 2.661 | 73.8625 | 53.895 | 2392.9956
2038-03-09 17:01 | 6973.87 | 2.111 | 75.1823 | 53.895 | 2043.8395
2038-03-10 18:01 | 5901.55 | 1.8186 | 74.92 | 53.895 | 1729.5736
2038-03-11 19:01 | 4759.52 | 1.4895 | 74.5988 | 53.895 | 1394.8776
2038-03-12 20:01 | 3877.11 | 1.2521 | 74.011 | 53.895 | 1136.2688
2038-03-13 21:01 | 3185.33 | 1.0496 | 73.5808 | 53.895 | 933.5281
2038-03-14 22:01 | 3059.95 | 1 | 78.4881 | 53.895 | 896.7828
2038-03-15 23:01 | 0 | 0 | 59.0769 | 53.895 | 0
2038-03-17 00:01 | -518.943 | 1.9571 | 57.3796 | 53.895 | -152.0872
2038-03-18 01:01 | -802.392 | 2.8491 | 56.9761 | 53.895 | -235.1579
2038-03-19 02:01 | -1104.81 | 3.6703 | 56.6672 | 53.895 | -323.7878
2038-03-20 03:01 | -1175.53 | 3.8116 | 56.4305 | 53.895 | -344.5138
2038-03-21 04:01 | -1174.81 | 3.8052 | 56.2338 | 53.895 | -344.3028
2038-03-22 05:01 | -901.339 | 2.9931 | 56.1634 | 53.895 | -264.1564
2038-03-23 06:01 | -976.21 | 3.2978 | 56.1345 | 53.895 | -286.0989
2038-03-24 07:01 | -790.602 | 2.7164 | 56.0904 | 53.895 | -231.7026
2038-03-25 08:01 | -724.318 | 2.5761 | 56.1004 | 53.895 | -212.2767
2038-03-26 09:01 | 499.771 | 1 | 57.2856 | 53.895 | 146.4684
2038-03-27 10:01 | 3083.6 | 1 | 56.912 | 53.895 | 903.714
2038-03-28 11:01 | 2785.23 | 1 | 77.6941 | 53.895 | 816.2703
2038-03-29 12:01 | 2901.08 | 1 | 57.3936 | 53.895 | 850.2226
2038-03-30 13:01 | 2961.1 | 1 | 75.5035 | 53.895 | 867.8127
2038-03-31 14:01 | 2887.47 | 1 | 57.5369 | 53.895 | 846.2339
2038-04-01 15:01 | 2886.82 | 1 | 72.7544 | 53.895 | 846.0434
2038-04-02 16:01 | 3286.31 | 1.1485 | 71.4342 | 53.895 | 963.1224
2038-04-03 17:01 | 2866.7 | 1 | 76.5721 | 53.895 | 840.1468
2038-04-04 18:01 | 2873.79 | 1 | 57.5562 | 53.895 | 842.2247
2038-04-05 19:01 | -241.071 | 1.3694 | 57.2295 | 53.895 | -70.6509
2038-04-06 20:01 | -1543.34 | 5.124 | 56.2836 | 53.895 | -452.3083
2038-04-07 21:01 | -2153.63 | 6.6536 | 55.8106 | 53.895 | -631.1666
2038-04-08 22:01 | -3150.92 | 6.8587 | 54.866 | 53.895 | -923.4435
2038-04-09 23:01 | -3535.45 | 6.8587 | 54.2817 | 53.895 | -1036.1381
2038-04-11 00:01 | -3985.19 | 6.8587 | 53.6793 | 53.895 | -1167.9439
2038-04-12 01:01 | -4099.54 | 6.8587 | 53.3675 | 53.895 | -1201.4566
2038-04-13 02:01 | -4303.4 | 6.8587 | 53.046 | 53.895 | -1261.202
2038-04-14 03:01 | -4310.42 | 6.8587 | 52.8665 | 53.895 | -1263.2594
2038-04-15 04:01 | -4304.46 | 6.8587 | 52.7264 | 53.895 | -1261.5127
2038-04-16 05:01 | -3815.35 | 6.8587 | 52.9346 | 53.895 | -1118.1687
2038-04-17 06:01 | -3867.54 | 6.8587 | 52.8415 | 53.895 | -1133.4641
2038-04-18 07:01 | -3308.99 | 6.8587 | 53.1606 | 53.895 | -969.7692
2038-04-19 08:01 | -3287 | 6.8587 | 53.1918 | 53.895 | -963.3246
2038-04-20 09:01 | -2681.92 | 6.8587 | 53.5882 | 53.895 | -785.9932
2038-04-21 10:01 | -2639.43 | 6.8587 | 53.6428 | 53.895 | -773.5406
2038-04-22 11:01 | -1453.35 | 4.4838 | 53.9098 | 53.895 | -425.9348
2038-04-23 12:01 | -1822.39 | 5.8485 | 54.0799 | 53.895 | -534.0898
2038-04-24 13:01 | -1239.63 | 3.9052 | 54.0387 | 53.895 | -363.2997
2038-04-25 14:01 | -1512.98 | 4.9456 | 54.1385 | 53.895 | -443.4107
2038-04-26 15:01 | -356.599 | 1.2864 | 54.2478 | 53.895 | -104.5089
2038-04-27 16:01 | 2524.13 | 1 | 55.229 | 53.895 | 739.7495
2038-04-28 17:01 | 2876.76 | 1 | 55.5635 | 53.895 | 843.0951
2038-04-29 18:01 | -62.5191 | 0.8536 | 55.9833 | 53.895 | -18.3225
2038-04-30 19:01 | -404.84 | 1.823 | 55.084 | 53.895 | -118.6469
2038-05-01 20:01 | -1524.3 | 5.1455 | 54.6566 | 53.895 | -446.7282
2038-05-02 21:01 | -1956.08 | 6.1672 | 54.4229 | 53.895 | -573.2705
2038-05-03 22:01 | -3500.49 | 6.8587 | 53.347 | 53.895 | -1025.8923
2038-05-04 23:01 | -4247 | 6.8587 | 52.5231 | 53.895 | -1244.6728
2038-05-06 00:01 | -4638.72 | 6.8587 | 52.0124 | 53.895 | -1359.4746
2038-05-07 01:01 | -5016.63 | 6.8587 | 51.5523 | 53.895 | -1470.2291
2038-05-08 02:01 | -5360.45 | 6.8587 | 51.1406 | 53.895 | -1570.9928
2038-05-09 03:01 | -4844.56 | 6.8587 | 51.3024 | 53.895 | -1419.8004
2038-05-10 04:01 | -4634.38 | 6.8587 | 51.3514 | 53.895 | -1358.2027
2038-05-11 05:01 | -4136.4 | 6.8587 | 51.6151 | 53.895 | -1212.2592
2038-05-12 06:01 | -3985.54 | 6.8587 | 51.7148 | 53.895 | -1168.0465
2038-05-13 07:01 | -3689.78 | 6.8587 | 51.9062 | 53.895 | -1081.3678
2038-05-14 08:01 | -3939.5 | 6.8587 | 51.7561 | 53.895 | -1154.5535
2038-05-15 09:01 | -3227.65 | 6.8587 | 52.1949 | 53.895 | -945.9308
2038-05-16 10:01 | -1157.54 | 3.6319 | 52.9485 | 53.895 | -339.2415
2038-05-17 11:01 | 1323.45 | 1 | 54.4814 | 53.895 | 387.8649
2038-05-18 12:01 | 2821.11 | 1 | 54.6668 | 53.895 | 826.7857
2038-05-19 13:01 | 2944.75 | 1.0511 | 68.7405 | 53.895 | 863.021
2038-05-20 14:01 | 3763.19 | 1.2892 | 69.5448 | 53.895 | 1102.8821
2038-05-21 15:01 | 5502.74 | 1.8844 | 69.8585 | 53.895 | 1612.6939
2038-05-22 16:01 | 5352.85 | 1.8214 | 70.3682 | 53.895 | 1568.7655
2038-05-23 17:01 | 4550.34 | 1.5474 | 70.6128 | 53.895 | 1333.573
2038-05-24 18:01 | 2901.62 | 1 | 73.3905 | 53.895 | 850.3809
2038-05-25 19:01 | 2976.25 | 1 | 56.3291 | 53.895 | 872.2528
2038-05-26 20:01 | -466.77 | 2.0352 | 55.8132 | 53.895 | -136.7968
2038-05-27 21:01 | -1141.21 | 3.932 | 55.1531 | 53.895 | -334.4556
2038-05-28 22:01 | -2221.33 | 6.8587 | 54.7083 | 53.895 | -651.0076
2038-05-29 23:01 | -2931.81 | 6.8587 | 53.9413 | 53.895 | -859.2287
2038-05-31 00:01 | -3516.86 | 6.8587 | 53.2731 | 53.895 | -1030.6899
2038-06-01 01:01 | -3697.64 | 6.8587 | 52.8784 | 53.895 | -1083.6713
2038-06-02 02:01 | -3991.8 | 6.8587 | 52.5022 | 53.895 | -1169.8811
2038-06-03 03:01 | -3680.23 | 6.8587 | 52.5236 | 53.895 | -1078.5689
2038-06-04 04:01 | -3570.37 | 6.8587 | 52.4896 | 53.895 | -1046.3722
2038-06-05 05:01 | -3250.9 | 6.8587 | 52.6242 | 53.895 | -952.7447
2038-06-06 06:01 | -3262.72 | 6.8587 | 52.5841 | 53.895 | -956.2088
2038-06-07 07:01 | -2554.82 | 6.8587 | 53.0127 | 53.895 | -748.7438
2038-06-08 08:01 | -2141.48 | 6.6857 | 53.3232 | 53.895 | -627.6058
2038-06-09 09:01 | -750.634 | 2.3322 | 53.3837 | 53.895 | -219.9891
2038-06-10 10:01 | 2551.06 | 1 | 54.6547 | 53.895 | 747.6419
2038-06-11 11:01 | 3124.97 | 1.0292 | 69.8575 | 53.895 | 915.8383
2038-06-12 12:01 | 4095.98 | 1.3401 | 70.2606 | 53.895 | 1200.4132
2038-06-13 13:01 | 4743.19 | 1.5248 | 70.842 | 53.895 | 1390.0918
2038-06-14 14:01 | 5040.1 | 1.6236 | 71.142 | 53.895 | 1477.1075
2038-06-15 15:01 | 5503.92 | 1.753 | 71.5669 | 53.895 | 1613.0397
2038-06-16 16:01 | 5936.73 | 1.9218 | 71.5321 | 53.895 | 1739.8838
2038-06-17 17:01 | 4746.61 | 1.5679 | 71.4626 | 53.895 | 1391.0941
2038-06-18 18:01 | 2959.44 | 1 | 78.2914 | 53.895 | 867.3262
2038-06-19 19:01 | 3046.9 | 1 | 56.631 | 53.895 | 892.9582
2038-06-20 20:01 | -474.968 | 2.068 | 56.076 | 53.895 | -139.1994
2038-06-21 21:01 | -988.493 | 3.4563 | 55.4007 | 53.895 | -289.6987
2038-06-22 22:01 | -1901.2 | 6.1246 | 54.96 | 53.895 | -557.1867
2038-06-23 23:01 | -2233.32 | 6.8587 | 54.613 | 53.895 | -654.5215
2038-06-25 00:01 | -2573.45 | 6.8587 | 54.1585 | 53.895 | -754.2037
2038-06-26 01:01 | -2652.75 | 6.8587 | 53.8796 | 53.895 | -777.4443
2038-06-27 02:01 | -2746.76 | 6.8587 | 53.6818 | 53.895 | -804.9959
2038-06-28 03:01 | -2550.04 | 6.8587 | 53.6884 | 53.895 | -747.343
2038-06-29 04:01 | -2591.39 | 6.8587 | 53.5777 | 53.895 | -759.4614
2038-06-30 05:01 | -2415.16 | 6.8587 | 53.6189 | 53.895 | -707.8135
2038-07-01 06:01 | -2454.69 | 6.8587 | 53.5562 | 53.895 | -719.3986
2038-07-02 07:01 | -2115.62 | 6.5647 | 53.669 | 53.895 | -620.027
2038-07-03 08:01 | -1694.86 | 5.2632 | 53.6904 | 53.895 | -496.7144
2038-07-04 09:01 | -1522.29 | 4.8577 | 53.7768 | 53.895 | -446.1392
2038-07-05 10:01 | -1026.75 | 3.3622 | 53.8303 | 53.895 | -300.9107
2038-07-06 11:01 | -230.897 | 1.0674 | 54.2923 | 53.895 | -67.6692
2038-07-07 12:01 | -118.999 | 0.95449 | 54.8308 | 53.895 | -34.8752
2038-07-08 13:01 | -324.416 | 1.5852 | 54.5092 | 53.895 | -95.0769
2038-07-09 14:01 | -431.252 | 1.8538 | 54.3637 | 53.895 | -126.3875
2038-07-10 15:01 | 2508.16 | 1 | 54.9916 | 53.895 | 735.0691
2038-07-11 16:01 | 3388.02 | 1.105 | 70.1528 | 53.895 | 992.9306
2038-07-12 17:01 | 3328.21 | 1.0803 | 70.4596 | 53.895 | 975.4021
2038-07-13 18:01 | 3034.25 | 1 | 55.6585 | 53.895 | 889.2509
2038-07-14 19:01 | 1144.27 | 1 | 56.0866 | 53.895 | 335.3524
2038-07-15 20:01 | -696.015 | 2.7631 | 55.0086 | 53.895 | -203.9819
2038-07-16 21:01 | -1241.62 | 4.2025 | 54.5343 | 53.895 | -363.8829
2038-07-17 22:01 | -2216.95 | 6.8587 | 54.2106 | 53.895 | -649.7239
2038-07-18 23:01 | -2954.73 | 6.8587 | 53.4725 | 53.895 | -865.9459
2038-07-20 00:01 | -3170.26 | 6.8587 | 53.0755 | 53.895 | -929.1115
2038-07-21 01:01 | -3459.45 | 6.8587 | 52.7135 | 53.895 | -1013.8647
2038-07-22 02:01 | -3601.9 | 6.8587 | 52.4909 | 53.895 | -1055.6127
2038-07-23 03:01 | -3680.08 | 6.8587 | 52.2951 | 53.895 | -1078.525
2038-07-24 04:01 | -3767.78 | 6.8587 | 52.1103 | 53.895 | -1104.2273
2038-07-25 05:01 | -3891.46 | 6.8587 | 51.9112 | 53.895 | -1140.4743
2038-07-26 06:01 | -3144.74 | 6.8587 | 52.3064 | 53.895 | -921.6323
2038-07-27 07:01 | -2317.52 | 6.8587 | 52.877 | 53.895 | -679.1981
2038-07-28 08:01 | -2053.03 | 6.4162 | 53.0554 | 53.895 | -601.6837
2038-07-29 09:01 | -1007.56 | 3.1685 | 53.1233 | 53.895 | -295.2867
2038-07-30 10:01 | 1995.9 | 1 | 54.4257 | 53.895 | 584.9405
2038-07-31 11:01 | 2988.65 | 1 | 54.7183 | 53.895 | 875.8869
2038-08-01 12:01 | 3633.55 | 1.1931 | 69.9163 | 53.895 | 1064.8884
2038-08-02 13:01 | 4589.61 | 1.5104 | 70.135 | 53.895 | 1345.0819
2038-08-03 14:01 | 5659.66 | 1.8282 | 70.7474 | 53.895 | 1658.6826
2038-08-04 15:01 | 5897.77 | 1.9344 | 70.8983 | 53.895 | 1728.4658
2038-08-05 16:01 | 7360.44 | 2.4724 | 70.8028 | 53.895 | 2157.132
2038-08-06 17:01 | 5582.33 | 1.8009 | 71.7519 | 53.895 | 1636.0194
2038-08-07 18:01 | 3461.33 | 1.1322 | 71.6129 | 53.895 | 1014.4157
2038-08-08 19:01 | 3058.85 | 1 | 56.5914 | 53.895 | 896.4604
2038-08-09 20:01 | 2972.15 | 1 | 56.5462 | 53.895 | 871.0512
2038-08-10 21:01 | 0 | 0 | 57.0565 | 53.895 | 0
2038-08-11 22:01 | -324.233 | 1.4728 | 55.62 | 53.895 | -95.0233
2038-08-12 23:01 | -1820.45 | 6.0491 | 54.9924 | 53.895 | -533.5212
2038-08-14 00:01 | -2393.66 | 6.8587 | 54.4792 | 53.895 | -701.5125
2038-08-15 01:01 | -2787.55 | 6.8587 | 53.9384 | 53.895 | -816.9503
2038-08-16 02:01 | -3089.47 | 6.8587 | 53.4802 | 53.895 | -905.4343
2038-08-17 03:01 | -3476.67 | 6.8587 | 53.0229 | 53.895 | -1018.9114
2038-08-18 04:01 | -3707.66 | 6.8587 | 52.6438 | 53.895 | -1086.6079
2038-08-19 05:01 | -3893.16 | 6.8587 | 52.3456 | 53.895 | -1140.9726
2038-08-20 06:01 | -3248.52 | 6.8587 | 52.645 | 53.895 | -952.0472
2038-08-21 07:01 | -2150.79 | 6.7588 | 53.3352 | 53.895 | -630.3343
2038-08-22 08:01 | -1894.48 | 5.8892 | 53.3937 | 53.895 | -555.2173
2038-08-23 09:01 | -703.327 | 2.2668 | 53.5038 | 53.895 | -206.1248
2038-08-24 10:01 | 2307.54 | 1 | 54.713 | 53.895 | 676.2732
2038-08-25 11:01 | 3076.55 | 1.0125 | 69.8413 | 53.895 | 901.6478
2038-08-26 12:01 | 4349.11 | 1.4371 | 70.0811 | 53.895 | 1274.5983
2038-08-27 13:01 | 5447.38 | 1.7338 | 70.9656 | 53.895 | 1596.4695
2038-08-28 14:01 | 6014.92 | 2.015 | 70.6118 | 53.895 | 1762.799
2038-08-29 15:01 | 6399.79 | 2.1209 | 71.0894 | 53.895 | 1875.5933
2038-08-30 16:01 | 8398.6 | 2.8156 | 71.1581 | 53.895 | 2461.3867
2038-08-31 17:01 | 6682.69 | 2.1675 | 72.0811 | 53.895 | 1958.5031
2038-09-01 18:01 | 4527.51 | 1.4836 | 72.0433 | 53.895 | 1326.8822
2038-09-02 19:01 | 3065.67 | 1 | 73.8895 | 53.895 | 898.4592
2038-09-03 20:01 | 3061.12 | 1 | 56.8805 | 53.895 | 897.1257
2038-09-04 21:01 | 3069.49 | 1 | 56.8429 | 53.895 | 899.5787
2038-09-05 22:01 | 2975.19 | 1 | 56.7965 | 53.895 | 871.9421
2038-09-06 23:01 | -574.966 | 2.378 | 56.1401 | 53.895 | -168.5059
2038-09-08 00:01 | -876.437 | 3.0858 | 55.508 | 53.895 | -256.8583
2038-09-09 01:01 | -768.56 | 2.701 | 55.2421 | 53.895 | -225.2427
2038-09-10 02:01 | -521.441 | 1.9963 | 55.225 | 53.895 | -152.8193
2038-09-11 03:01 | -94.5018 | 0.78252 | 55.7907 | 53.895 | -27.6957
2038-09-12 04:01 | 784.169 | 1 | 56.1503 | 53.895 | 229.8172
2038-09-13 05:01 | 2818.62 | 1 | 55.8984 | 53.895 | 826.056
2038-09-14 06:01 | 3069.79 | 1 | 56.1702 | 53.895 | 899.6666
2038-09-15 07:01 | 2990.64 | 1 | 56.4006 | 53.895 | 876.4701
2038-09-16 08:01 | -84.9596 | 0.91449 | 56.6005 | 53.895 | -24.8992
2038-09-17 09:01 | 2368.01 | 1 | 56.3441 | 53.895 | 693.9952
2038-09-18 10:01 | 2840.13 | 1 | 76.8715 | 53.895 | 832.3599
2038-09-19 11:01 | 4269.25 | 1.422 | 71.0688 | 53.895 | 1251.1937
2038-09-20 12:01 | 5032.57 | 1.6872 | 71.1972 | 53.895 | 1474.9007
2038-09-21 13:01 | 6048.4 | 1.9968 | 71.6167 | 53.895 | 1772.6111
2038-09-22 14:01 | 6382.41 | 2.1412 | 71.6923 | 53.895 | 1870.4997
2038-09-23 15:01 | 7503.1 | 2.4657 | 72.1905 | 53.895 | 2198.9415
2038-09-24 16:01 | 7152.97 | 2.4016 | 72.1546 | 53.895 | 2096.3286
2038-09-25 17:01 | 5892.95 | 1.9865 | 72.2236 | 53.895 | 1727.0532
2038-09-26 18:01 | 3405.44 | 1.1302 | 72.4001 | 53.895 | 998.0359
2038-09-27 19:01 | 2971.65 | 1 | 57.4845 | 53.895 | 870.9046
2038-09-28 20:01 | 0 | 0 | 57.852 | 53.895 | 0
2038-09-29 21:01 | -958.169 | 3.3868 | 56.0656 | 53.895 | -280.8116
2038-09-30 22:01 | -2242.65 | 6.8587 | 55.4566 | 53.895 | -657.2558
2038-10-01 23:01 | -3261.86 | 6.8587 | 54.3754 | 53.895 | -955.9568
2038-10-03 00:01 | -3805.57 | 6.8587 | 53.6353 | 53.895 | -1115.3025
2038-10-04 01:01 | -4248.22 | 6.8587 | 52.9889 | 53.895 | -1245.0304
2038-10-05 02:01 | -4483.12 | 6.8587 | 52.5473 | 53.895 | -1313.8728
2038-10-06 03:01 | -4673.09 | 6.8587 | 52.1542 | 53.895 | -1369.5475
2038-10-07 04:01 | -4819.22 | 6.8587 | 51.8194 | 53.895 | -1412.374
2038-10-08 05:01 | -4399.65 | 6.8587 | 51.894 | 53.895 | -1289.4101
2038-10-09 06:01 | -4249.75 | 6.8587 | 51.8842 | 53.895 | -1245.4788
2038-10-10 07:01 | -4226.14 | 6.8587 | 51.7999 | 53.895 | -1238.5594
2038-10-11 08:01 | -4438.02 | 6.8587 | 51.5871 | 53.895 | -1300.6553
2038-10-12 09:01 | -3392.17 | 6.8587 | 52.1975 | 53.895 | -994.1469
2038-10-13 10:01 | -1770.25 | 5.5781 | 53.0658 | 53.895 | -518.8091
2038-10-14 11:01 | -913.925 | 2.9589 | 53.2872 | 53.895 | -267.845
2038-10-15 12:01 | 0 | 0 | 54.9061 | 53.895 | 0
2038-10-16 13:01 | 2645.01 | 1 | 54.6346 | 53.895 | 775.1759
2038-10-17 14:01 | 439.963 | 1 | 55.4547 | 53.895 | 128.9404
2038-10-18 15:01 | 2731.94 | 1 | 55.0314 | 53.895 | 800.6526
2038-10-19 16:01 | 2770.6 | 1 | 55.2743 | 53.895 | 811.9827
2038-10-20 17:01 | 2688.6 | 1 | 55.4829 | 53.895 | 787.9509
2038-10-21 18:01 | -617.419 | 2.513 | 54.9013 | 53.895 | -180.9476
2038-10-22 19:01 | -1478.39 | 4.9667 | 54.3175 | 53.895 | -433.2733
2038-10-23 20:01 | -2816.7 | 6.8587 | 53.5823 | 53.895 | -825.4933
2038-10-24 21:01 | -3584.54 | 6.8587 | 52.779 | 53.895 | -1050.525
2038-10-25 22:01 | -4814.63 | 6.8587 | 51.6522 | 53.895 | -1411.0288
2038-10-26 23:01 | -5576.83 | 6.8587 | 50.7823 | 53.895 | -1634.4075
2038-10-28 00:01 | -5752.05 | 6.8587 | 50.3699 | 53.895 | -1685.7594
2038-10-29 01:01 | -6215.87 | 6.8587 | 49.81 | 53.895 | -1821.6917
2038-10-30 02:01 | -6210.29 | 6.8587 | 49.5976 | 53.895 | -1820.0563
2038-10-31 03:01 | -6294.34 | 6.8587 | 49.3467 | 53.895 | -1844.689
2038-11-01 04:01 | -5860.1 | 6.8587 | 49.4777 | 53.895 | -1717.4258
2038-11-02 05:01 | -5534.2 | 6.8587 | 49.6024 | 53.895 | -1621.9139
2038-11-03 06:01 | -5853.51 | 6.8587 | 49.3418 | 53.895 | -1715.4944
2038-11-04 07:01 | -5220.02 | 6.8587 | 49.6789 | 53.895 | -1529.8368
2038-11-05 08:01 | -3871.18 | 6.8587 | 50.6135 | 53.895 | -1134.5309
2038-11-06 09:01 | -2300.77 | 6.8587 | 51.8394 | 53.895 | -674.2891
2038-11-07 10:01 | -827.082 | 2.5949 | 52.1604 | 53.895 | -242.3938
2038-11-08 11:01 | 2459.36 | 1 | 53.5339 | 53.895 | 720.7673
2038-11-09 12:01 | 2755 | 1 | 69.1079 | 53.895 | 807.4108
2038-11-10 13:01 | 3778.83 | 1.3427 | 68.0881 | 53.895 | 1107.4658
2038-11-11 14:01 | 4695.78 | 1.646 | 68.633 | 53.895 | 1376.1973
2038-11-12 15:01 | 5637.2 | 1.9853 | 68.935 | 53.895 | 1652.1002
2038-11-13 16:01 | 4461.37 | 1.5813 | 69.2224 | 53.895 | 1307.4985
2038-11-14 17:01 | 3467.83 | 1.2286 | 69.3108 | 53.895 | 1016.3206
2038-11-15 18:01 | 2828.79 | 1 | 55.6157 | 53.895 | 829.0365
2038-11-16 19:01 | -224.27 | 1.3259 | 55.3135 | 53.895 | -65.727
2038-11-17 20:01 | -1369.57 | 4.7262 | 54.4188 | 53.895 | -401.3813
2038-11-18 21:01 | -1801.32 | 5.7669 | 53.9932 | 53.895 | -527.9148
2038-11-19 22:01 | -2916.49 | 6.8587 | 53.2668 | 53.895 | -854.7388
2038-11-20 23:01 | -3451.9 | 6.8587 | 52.6176 | 53.895 | -1011.652
2038-11-22 00:01 | -3697.22 | 6.8587 | 52.1852 | 53.895 | -1083.5482
2038-11-23 01:01 | -3659.53 | 6.8587 | 52.0354 | 53.895 | -1072.5024
2038-11-24 02:01 | -3680.55 | 6.8587 | 51.8954 | 53.895 | -1078.6627
2038-11-25 03:01 | -3457.18 | 6.8587 | 51.9257 | 53.895 | -1013.1994
2038-11-26 04:01 | -3210.36 | 6.8587 | 52.0331 | 53.895 | -940.8636
2038-11-27 05:01 | -2754.9 | 6.8587 | 52.3211 | 53.895 | -807.3815
2038-11-28 06:01 | -3079.21 | 6.8587 | 52.1252 | 53.895 | -902.4274
2038-11-29 07:01 | -2895.93 | 6.8587 | 52.2295 | 53.895 | -848.7133
2038-11-30 08:01 | -3086.28 | 6.8587 | 52.1097 | 53.895 | -904.4994
2038-12-01 09:01 | -2432.13 | 6.8587 | 52.5304 | 53.895 | -712.7869
2038-12-02 10:01 | -1659.32 | 5.2013 | 52.7436 | 53.895 | -486.2987
2038-12-03 11:01 | -859.428 | 2.8442 | 52.9106 | 53.895 | -251.8735
2038-12-04 12:01 | -419.787 | 1.7153 | 53.3115 | 53.895 | -123.0274
2038-12-05 13:01 | -81.6162 | 0.78434 | 54.0752 | 53.895 | -23.9193
2038-12-06 14:01 | 2604.1 | 1 | 54.2181 | 53.895 | 763.1864
2038-12-07 15:01 | 3007.91 | 1 | 72.6908 | 53.895 | 881.5314
2038-12-08 16:01 | 3760.01 | 1.1851 | 70.1451 | 53.895 | 1101.9502
2038-12-09 17:01 | 3715.69 | 1.2224 | 69.7638 | 53.895 | 1088.9612
2038-12-10 18:01 | 3050.91 | 1 | 71.9387 | 53.895 | 894.1335
2038-12-11 19:01 | 3054.37 | 1 | 55.2867 | 53.895 | 895.1475
2038-12-12 20:01 | 2824.94 | 1 | 55.4252 | 53.895 | 827.9082
2038-12-13 21:01 | 0 | 0 | 55.9846 | 53.895 | 0
2038-12-14 22:01 | -568.083 | 2.0903 | 54.4285 | 53.895 | -166.4887
2038-12-15 23:01 | -661.786 | 2.508 | 54.2719 | 53.895 | -193.9503
2038-12-17 00:01 | -730.715 | 2.6812 | 54.1567 | 53.895 | -214.1514
2038-12-18 01:01 | -772.275 | 2.7939 | 54.0753 | 53.895 | -226.3315
2038-12-19 02:01 | -832.877 | 2.9722 | 53.9726 | 53.895 | -244.0922
2038-12-20 03:01 | -677.989 | 2.4792 | 53.968 | 53.895 | -198.699
2038-12-21 04:01 | -525.113 | 2.0591 | 54.0423 | 53.895 | -153.8954
2038-12-22 05:01 | -225.148 | 1.1829 | 54.3427 | 53.895 | -65.9844
2038-12-23 06:01 | -492.605 | 2.0806 | 54.1569 | 53.895 | -144.3683
2038-12-24 07:01 | -258.568 | 1.2828 | 54.2971 | 53.895 | -75.7788
2038-12-25 08:01 | 547.762 | 1 | 55.1649 | 53.895 | 160.5332
2038-12-26 09:01 | 2435.66 | 1.0038 | 66.7826 | 53.895 | 713.8215
2038-12-27 10:01 | 4409.89 | 1.4464 | 69.9653 | 53.895 | 1292.4112
2038-12-28 11:01 | 7758.09 | 2.5457 | 70.3425 | 53.895 | 2273.6717
2038-12-29 12:01 | 9296.16 | 3.0182 | 71.1486 | 53.895 | 2724.4356
2038-12-30 13:01 | 9987.81 | 3.2393 | 71.7667 | 53.895 | 2927.1382
2038-12-31 14:01 | 10868.4 | 3.5346 | 72.1984 | 53.895 | 3185.2136
2039-01-01 15:01 | 12291.9 | 4.0592 | 72.4273 | 53.895 | 3602.4003
2039-01-02 16:01 | 11563.1 | 3.7018 | 73.396 | 53.895 | 3388.8101
2039-01-03 17:01 | 10204.4 | 3.2529 | 73.7228 | 53.895 | 2990.6144
2039-01-04 18:01 | 8460 | 2.5886 | 74.409 | 53.895 | 2479.3813
2039-01-05 19:01 | 7591.65 | 2.3347 | 74.268 | 53.895 | 2224.893
2039-01-06 20:01 | 5523.6 | 1.677 | 74.4162 | 53.895 | 1618.8074
2039-01-07 21:01 | 4708.1 | 1.4681 | 73.7677 | 53.895 | 1379.8079
2039-01-08 22:01 | 3155.96 | 1 | 77.5897 | 53.895 | 924.9206
2039-01-09 23:01 | 3131.76 | 1 | 57.7124 | 53.895 | 917.8283
2039-01-11 00:01 | 2714.26 | 1 | 57.6193 | 53.895 | 795.4711
2039-01-12 01:01 | 343.011 | 1 | 57.8642 | 53.895 | 100.5266
2039-01-13 02:01 | -90.7611 | 0.91788 | 57.0568 | 53.895 | -26.5995
2039-01-14 03:01 | -251.218 | 1.3416 | 56.3223 | 53.895 | -73.6247
2039-01-15 04:01 | -318.835 | 1.5076 | 56.0045 | 53.895 | -93.4413
2039-01-16 05:01 | -270.011 | 1.3499 | 55.8787 | 53.895 | -79.1324
2039-01-17 06:01 | 1474.81 | 1 | 56.4293 | 53.895 | 432.2241
2039-01-18 07:01 | 1196.11 | 1 | 56.6135 | 53.895 | 350.5452
2039-01-19 08:01 | -422.291 | 1.93 | 55.8279 | 53.895 | -123.7613
2039-01-20 09:01 | -684.161 | 2.5556 | 55.391 | 53.895 | -200.5078
2039-01-21 10:01 | 2186.69 | 1 | 56.1264 | 53.895 | 640.8556
2039-01-22 11:01 | 2843.81 | 1 | 56.2652 | 53.895 | 833.4384
2039-01-23 12:01 | 2914.28 | 1 | 56.4042 | 53.895 | 854.0912
2039-01-24 13:01 | 1997.41 | 1 | 56.6207 | 53.895 | 585.3831
2039-01-25 14:01 | 2935.9 | 1 | 56.4083 | 53.895 | 860.4274
2039-01-26 15:01 | 2944.38 | 1 | 73.4432 | 53.895 | 862.9126
2039-01-27 16:01 | 4544.08 | 1.5175 | 71.0531 | 53.895 | 1331.7384
2039-01-28 17:01 | 3319.89 | 1.1238 | 71.0651 | 53.895 | 972.9637
2039-01-29 18:01 | 2942.91 | 1 | 56.6754 | 53.895 | 862.4818
2039-01-30 19:01 | 0 | 0 | 57.1357 | 53.895 | 0
2039-01-31 20:01 | -420.182 | 1.744 | 55.6564 | 53.895 | -123.1432
2039-02-01 21:01 | -896.374 | 3.214 | 55.2595 | 53.895 | -262.7013
2039-02-02 22:01 | -1201.84 | 4.0129 | 54.9484 | 53.895 | -352.2245
2039-02-03 23:01 | -2885.18 | 6.8587 | 54.1896 | 53.895 | -845.5628
2039-02-05 00:01 | -3652.52 | 6.8587 | 53.3018 | 53.895 | -1070.4479
2039-02-06 01:01 | -4035.19 | 6.8587 | 52.7616 | 53.895 | -1182.5975
2039-02-07 02:01 | -4451.6 | 6.8587 | 52.2448 | 53.895 | -1304.6352
2039-02-08 03:01 | -4836.71 | 6.8587 | 51.7515 | 53.895 | -1417.4998
2039-02-09 04:01 | -5085.14 | 6.8587 | 51.3264 | 53.895 | -1490.3074
2039-02-10 05:01 | -5190.51 | 6.8587 | 51.0469 | 53.895 | -1521.1883
2039-02-11 06:01 | -4479.73 | 6.8587 | 51.3482 | 53.895 | -1312.8793
2039-02-12 07:01 | -3754.09 | 6.8587 | 51.7989 | 53.895 | -1100.2152
2039-02-13 08:01 | -3569.82 | 6.8587 | 51.9549 | 53.895 | -1046.211
2039-02-14 09:01 | -2228.78 | 6.8587 | 52.8704 | 53.895 | -653.1909
2039-02-15 10:01 | -1416.51 | 4.4085 | 53.002 | 53.895 | -415.1381
2039-02-16 11:01 | 0 | 0 | 54.6543 | 53.895 | 0
2039-02-17 12:01 | 2752.86 | 1 | 54.406 | 53.895 | 806.7836
2039-02-18 13:01 | 2791.71 | 1 | 54.8565 | 53.895 | 818.1694
2039-02-19 14:01 | 2795.65 | 1 | 69.7628 | 53.895 | 819.3241
2039-02-20 15:01 | 2867.27 | 1 | 69.8926 | 53.895 | 840.3139
2039-02-21 16:01 | 4259.45 | 1.4862 | 69.3045 | 53.895 | 1248.3216
2039-02-22 17:01 | 2840.63 | 1 | 74.2753 | 53.895 | 832.5065
2039-02-23 18:01 | 0 | 0 | 56.164 | 53.895 | 0
2039-02-24 19:01 | -749.694 | 2.7986 | 54.5816 | 53.895 | -219.7136
2039-02-25 20:01 | -1459.08 | 4.8853 | 54.2207 | 53.895 | -427.6141
2039-02-26 21:01 | -1982.45 | 6.316 | 53.9639 | 53.895 | -580.9987
2039-02-27 22:01 | -2761.28 | 6.8587 | 53.3285 | 53.895 | -809.2513
2039-02-28 23:01 | -4538.98 | 6.8587 | 51.8716 | 53.895 | -1330.2437
2039-03-02 00:01 | -5096.13 | 6.8587 | 51.1186 | 53.895 | -1493.5283
2039-03-03 01:01 | -5348.05 | 6.8587 | 50.6455 | 53.895 | -1567.3587
2039-03-04 02:01 | -5561.99 | 6.8587 | 50.2704 | 53.895 | -1630.0584
2039-03-05 03:01 | -5790.65 | 6.8587 | 49.9018 | 53.895 | -1697.072
2039-03-06 04:01 | -5943.67 | 6.8587 | 49.5784 | 53.895 | -1741.9177
2039-03-07 05:01 | -5958.81 | 6.8587 | 49.4001 | 53.895 | -1746.3548
2039-03-08 06:01 | -5312.55 | 6.8587 | 49.7198 | 53.895 | -1556.9547
2039-03-09 07:01 | -4404.6 | 6.8587 | 50.3137 | 53.895 | -1290.8608
2039-03-10 08:01 | -4036.1 | 6.8587 | 50.6338 | 53.895 | -1182.8641
2039-03-11 09:01 | -2518.33 | 6.8587 | 51.7187 | 53.895 | -738.0497
2039-03-12 10:01 | -664.438 | 2.0862 | 52.126 | 53.895 | -194.7276
2039-03-13 11:01 | 2344.43 | 1 | 53.554 | 53.895 | 687.0846
2039-03-14 12:01 | 2757.51 | 1 | 54.0215 | 53.895 | 808.1464
2039-03-15 13:01 | 2782.81 | 1 | 68.0373 | 53.895 | 815.5611
2039-03-16 14:01 | 3656.33 | 1.2876 | 68.391 | 53.895 | 1071.5645
2039-03-17 15:01 | 4150.64 | 1.4465 | 68.8277 | 53.895 | 1216.4325
2039-03-18 16:01 | 5799.42 | 2.0072 | 69.1775 | 53.895 | 1699.6422
2039-03-19 17:01 | 3468.37 | 1.2324 | 69.201 | 53.895 | 1016.4789
2039-03-20 18:01 | 2718.15 | 1 | 55.5307 | 53.895 | 796.6111
2039-03-21 19:01 | -127.285 | 1.049 | 55.3916 | 53.895 | -37.3036
2039-03-22 20:01 | -854.732 | 3.1794 | 54.4008 | 53.895 | -250.4972
2039-03-23 21:01 | -1331.81 | 4.4678 | 54.0273 | 53.895 | -390.315
2039-03-24 22:01 | -1791.26 | 5.7806 | 53.7562 | 53.895 | -524.9665
2039-03-25 23:01 | -3054.43 | 6.8587 | 52.9305 | 53.895 | -895.1651
2039-03-27 00:01 | -3397.61 | 6.8587 | 52.4014 | 53.895 | -995.7412
2039-03-28 01:01 | -3810.11 | 6.8587 | 51.9232 | 53.895 | -1116.633
2039-03-29 02:01 | -4073.51 | 6.8587 | 51.5611 | 53.895 | -1193.8279
2039-03-30 03:01 | -4146.93 | 6.8587 | 51.3345 | 53.895 | -1215.3452
2039-03-31 04:01 | -4218.57 | 6.8587 | 51.1198 | 53.895 | -1236.3408
2039-04-01 05:01 | -3806.59 | 6.8587 | 51.2877 | 53.895 | -1115.6014
2039-04-02 06:01 | -3721.11 | 6.8587 | 51.2998 | 53.895 | -1090.5497
2039-04-03 07:01 | -3563.82 | 6.8587 | 51.3831 | 53.895 | -1044.4525
2039-04-04 08:01 | -3210.75 | 6.8587 | 51.6139 | 53.895 | -940.9779
2039-04-05 09:01 | -1907.76 | 6.07 | 52.3466 | 53.895 | -559.1093
2039-04-06 10:01 | -426.123 | 1.4083 | 52.5387 | 53.895 | -124.8843
2039-04-07 11:01 | 2658.61 | 1 | 53.7333 | 53.895 | 779.1617
2039-04-08 12:01 | 3300.15 | 1.1193 | 68.524 | 53.895 | 967.1785
2039-04-09 13:01 | 4459.5 | 1.5083 | 68.8706 | 53.895 | 1306.9504
2039-04-10 14:01 | 4993.2 | 1.6927 | 69.1955 | 53.895 | 1463.3625
2039-04-11 15:01 | 6068.6 | 2.079 | 69.3605 | 53.895 | 1778.5311
2039-04-12 16:01 | 4540.11 | 1.5441 | 69.809 | 53.895 | 1330.5749
2039-04-13 17:01 | 3432.9 | 1.1759 | 69.7456 | 53.895 | 1006.0837
2039-04-14 18:01 | 2953.62 | 1 | 55.5046 | 53.895 | 865.6206
2039-04-15 19:01 | 2773.69 | 1 | 55.5211 | 53.895 | 812.8883
2039-04-16 20:01 | -450.462 | 2.0258 | 54.9661 | 53.895 | -132.0174
2039-04-17 21:01 | -894.269 | 3.2223 | 54.314 | 53.895 | -262.0844
2039-04-18 22:01 | -1862.77 | 6.1156 | 53.9372 | 53.895 | -545.924
2039-04-19 23:01 | -2259 | 6.8587 | 53.5765 | 53.895 | -662.0475
2039-04-21 00:01 | -2538.68 | 6.8587 | 53.1621 | 53.895 | -744.0137
2039-04-22 01:01 | -2529.52 | 6.8587 | 52.9594 | 53.895 | -741.3291
2039-04-23 02:01 | -2498.77 | 6.8587 | 52.8635 | 53.895 | -732.3172
2039-04-24 03:01 | -2337.32 | 6.8587 | 52.8684 | 53.895 | -685.0009
2039-04-25 04:01 | -2172.62 | 6.8099 | 52.9199 | 53.895 | -636.7321
2039-04-26 05:01 | -1856.97 | 5.8078 | 52.8934 | 53.895 | -544.2242
2039-04-27 06:01 | -1774.21 | 5.6511 | 52.9302 | 53.895 | -519.9696
2039-04-28 07:01 | -1611.35 | 5.1539 | 52.933 | 53.895 | -472.2401
2039-04-29 08:01 | -1997.26 | 6.422 | 52.9777 | 53.895 | -585.3391
2039-04-30 09:01 | -1570.43 | 4.944 | 52.9108 | 53.895 | -460.2476
2039-05-01 10:01 | -984.394 | 3.2581 | 53.0036 | 53.895 | -288.4974
2039-05-02 11:01 | -223.479 | 1.0646 | 53.4921 | 53.895 | -65.4952
2039-05-03 12:01 | 2393.84 | 1 | 54.1726 | 53.895 | 701.5653
2039-05-04 13:01 | 270.441 | 1 | 54.8983 | 53.895 | 79.2584
2039-05-05 14:01 | 2517.23 | 1 | 54.4534 | 53.895 | 737.7273
2039-05-06 15:01 | 3020.57 | 1 | 75.2712 | 53.895 | 885.2417
2039-05-07 16:01 | 3067 | 1 | 72.6937 | 53.895 | 898.849
2039-05-08 17:01 | 3046.36 | 1 | 73.5411 | 53.895 | 892.8
2039-05-09 18:01 | 3016.68 | 1 | 55.0166 | 53.895 | 884.1016
2039-05-10 19:01 | 2961.54 | 1 | 55.1513 | 53.895 | 867.9417
2039-05-11 20:01 | -375.86 | 1.8121 | 54.7766 | 53.895 | -110.1537
2039-05-12 21:01 | -719.831 | 2.7152 | 54.1759 | 53.895 | -210.9616
2039-05-13 22:01 | -1534.75 | 5.1545 | 53.8272 | 53.895 | -449.7908
2039-05-14 23:01 | -1886.27 | 6.0203 | 53.5793 | 53.895 | -552.8112
2039-05-16 00:01 | -2040.99 | 6.4323 | 53.3716 | 53.895 | -598.1551
2039-05-17 01:01 | -2248.08 | 6.8587 | 53.1831 | 53.895 | -658.8472
2039-05-18 02:01 | -2402.4 | 6.8587 | 52.978 | 53.895 | -704.0739
2039-05-19 03:01 | -2518.33 | 6.8587 | 52.7972 | 53.895 | -738.0497
2039-05-20 04:01 | -2534.24 | 6.8587 | 52.7006 | 53.895 | -742.7124
2039-05-21 05:01 | -2038.58 | 6.4011 | 52.8667 | 53.895 | -597.4488
2039-05-22 06:01 | -2187.79 | 6.8587 | 52.8608 | 53.895 | -641.178
2039-05-23 07:01 | -1908.06 | 5.972 | 52.8114 | 53.895 | -559.1972
2039-05-24 08:01 | -1437.36 | 4.5768 | 52.8543 | 53.895 | -421.2486
2039-05-25 09:01 | 0 | 0 | 54.3927 | 53.895 | 0
2039-05-26 10:01 | 2604.52 | 1 | 54.1565 | 53.895 | 763.3095
2039-05-27 11:01 | 3795.56 | 1.2509 | 69.2777 | 53.895 | 1112.3688
2039-05-28 12:01 | 5513.23 | 1.8352 | 69.4619 | 53.895 | 1615.7682
2039-05-29 13:01 | 6384.37 | 2.1215 | 69.9332 | 53.895 | 1871.0741
2039-05-30 14:01 | 7156.56 | 2.3956 | 70.2374 | 53.895 | 2097.3807
2039-05-31 15:01 | 8148.2 | 2.7399 | 70.5434 | 53.895 | 2388.0017
2039-06-01 16:01 | 7718.23 | 2.5579 | 71.1247 | 53.895 | 2261.9899
2039-06-02 17:01 | 5995.03 | 2.009 | 71.1979 | 53.895 | 1756.9699
2039-06-03 18:01 | 2912.02 | 1 | 71.5441 | 53.895 | 853.4288
2039-06-04 19:01 | 2919.87 | 1 | 56.3792 | 53.895 | 855.7294
2039-06-05 20:01 | -340.865 | 1.6558 | 55.817 | 53.895 | -99.8977
2039-06-06 21:01 | -945.02 | 3.3789 | 55.0272 | 53.895 | -276.958
2039-06-07 22:01 | -2044.64 | 6.6121 | 54.5317 | 53.895 | -599.2248
2039-06-08 23:01 | -2657.39 | 6.8587 | 53.8316 | 53.895 | -778.8041
2039-06-10 00:01 | -2819.34 | 6.8587 | 53.435 | 53.895 | -826.267
2039-06-11 01:01 | -3071.48 | 6.8587 | 53.0152 | 53.895 | -900.1619
2039-06-12 02:01 | -3275.81 | 6.8587 | 52.685 | 53.895 | -960.0451
2039-06-13 03:01 | -3337.17 | 6.8587 | 52.4475 | 53.895 | -978.028
2039-06-14 04:01 | -3308.9 | 6.8587 | 52.3091 | 53.895 | -969.7429
2039-06-15 05:01 | -2952.61 | 6.8587 | 52.4344 | 53.895 | -865.3246
2039-06-16 06:01 | -2939.66 | 6.8587 | 52.4054 | 53.895 | -861.5293
2039-06-17 07:01 | -2647.89 | 6.8587 | 52.5507 | 53.895 | -776.02
2039-06-18 08:01 | -3045.33 | 6.8587 | 52.2862 | 53.895 | -892.4981
2039-06-19 09:01 | -2341.78 | 6.8587 | 52.7042 | 53.895 | -686.308
2039-06-20 10:01 | -707.402 | 2.1987 | 52.8196 | 53.895 | -207.3191
2039-06-21 11:01 | 2596.54 | 1 | 67.419 | 53.895 | 760.9708
2039-06-22 12:01 | 3888.92 | 1.3125 | 68.8829 | 53.895 | 1139.7299
2039-06-23 13:01 | 5424.84 | 1.7849 | 69.6491 | 53.895 | 1589.8637
2039-06-24 14:01 | 6402.76 | 2.1215 | 69.9798 | 53.895 | 1876.4637
2039-06-25 15:01 | 7908.65 | 2.6393 | 70.2886 | 53.895 | 2317.7965
2039-06-26 16:01 | 7423.2 | 2.4733 | 70.7815 | 53.895 | 2175.5252
2039-06-27 17:01 | 6020.89 | 1.9923 | 71.1239 | 53.895 | 1764.5487
2039-06-28 18:01 | 3530.8 | 1.1712 | 71.1336 | 53.895 | 1034.7753
2039-06-29 19:01 | 2942.96 | 1 | 56.2932 | 53.895 | 862.4964
2039-06-30 20:01 | 0 | 0 | 56.7002 | 53.895 | 0
2039-07-01 21:01 | -668.052 | 2.4346 | 55.0168 | 53.895 | -195.7867
2039-07-02 22:01 | -1474.25 | 4.9409 | 54.6023 | 53.895 | -432.06
2039-07-03 23:01 | -2098.92 | 6.6475 | 54.2455 | 53.895 | -615.1327
2039-07-05 00:01 | -2474.27 | 6.8587 | 53.7829 | 53.895 | -725.137
2039-07-06 01:01 | -2795.96 | 6.8587 | 53.3206 | 53.895 | -819.415
2039-07-07 02:01 | -3023.05 | 6.8587 | 52.9746 | 53.895 | -885.9685
2039-07-08 03:01 | -3203.54 | 6.8587 | 52.6594 | 53.895 | -938.8649
2039-07-09 04:01 | -3390.41 | 6.8587 | 52.3607 | 53.895 | -993.6311
2039-07-10 05:01 | -3580.07 | 6.8587 | 52.0767 | 53.895 | -1049.2149
2039-07-11 06:01 | -2857.46 | 6.8587 | 52.4416 | 53.895 | -837.4389
2039-07-12 07:01 | -2378.22 | 6.8587 | 52.7559 | 53.895 | -696.9875
2039-07-13 08:01 | -2470.79 | 6.8587 | 52.7425 | 53.895 | -724.1171
2039-07-14 09:01 | -1388.82 | 4.3363 | 52.917 | 53.895 | -407.023
2039-07-15 10:01 | 0 | 1 | 54.5268 | 53.895 | 0
2039-07-16 11:01 | 2617.89 | 1 | 72.6772 | 53.895 | 767.2278
2039-07-17 12:01 | 3573.94 | 1.1572 | 69.5953 | 53.895 | 1047.4184
2039-07-18 13:01 | 3035.83 | 1 | 70.8475 | 53.895 | 889.7139
2039-07-19 14:01 | 4914.83 | 1.6002 | 69.9653 | 53.895 | 1440.3945
2039-07-20 15:01 | 4947.52 | 1.5788 | 70.5817 | 53.895 | 1449.975
2039-07-21 16:01 | 6847.64 | 2.2252 | 70.5337 | 53.895 | 2006.8452
2039-07-22 17:01 | 4652.17 | 1.5224 | 70.8037 | 53.895 | 1363.4164
2039-07-23 18:01 | 3070.38 | 1 | 71.6058 | 53.895 | 899.8396
2039-07-24 19:01 | 3024.75 | 1 | 55.817 | 53.895 | 886.4667
2039-07-25 20:01 | 2992.14 | 1 | 55.8213 | 53.895 | 876.9097
2039-07-26 21:01 | 2715.21 | 1 | 55.9037 | 53.895 | 795.7495
2039-07-27 22:01 | -58.0393 | 0.86286 | 56.0136 | 53.895 | -17.0096
2039-07-28 23:01 | -1421.69 | 4.8967 | 54.6226 | 53.895 | -416.6562
2039-07-30 00:01 | -2019.39 | 6.4129 | 54.171 | 53.895 | -591.8248
2039-07-31 01:01 | -2497.19 | 6.8587 | 53.697 | 53.895 | -731.8541
2039-08-01 02:01 | -2675.38 | 6.8587 | 53.3284 | 53.895 | -784.0765
2039-08-02 03:01 | -2868.31 | 6.8587 | 52.9774 | 53.895 | -840.6187
2039-08-03 04:01 | -2982.33 | 6.8587 | 52.719 | 53.895 | -874.0346
2039-08-04 05:01 | -3323.87 | 6.8587 | 52.3571 | 53.895 | -974.1301
2039-08-05 06:01 | -2566.03 | 6.8587 | 52.7392 | 53.895 | -752.0292
2039-08-06 07:01 | -2118.42 | 6.646 | 52.9852 | 53.895 | -620.8476
2039-08-07 08:01 | -2381.23 | 6.8587 | 52.873 | 53.895 | -697.8696
2039-08-08 09:01 | -2048.66 | 6.4171 | 52.9431 | 53.895 | -600.403
2039-08-09 10:01 | -1538.22 | 4.8405 | 52.9453 | 53.895 | -450.8078
2039-08-10 11:01 | -972.779 | 3.2299 | 53.0699 | 53.895 | -285.0934
2039-08-11 12:01 | -799.17 | 2.8519 | 53.2284 | 53.895 | -234.2136
2039-08-12 13:01 | -836.97 | 3.0064 | 53.2717 | 53.895 | -245.2917
2039-08-13 14:01 | -899.139 | 3.1846 | 53.248 | 53.895 | -263.5116
2039-08-14 15:01 | -731.165 | 2.645 | 53.2477 | 53.895 | -214.2833
2039-08-15 16:01 | 2277.08 | 1 | 54.1345 | 53.895 | 667.3463
2039-08-16 17:01 | 0 | 0 | 54.8785 | 53.895 | 0
2039-08-17 18:01 | -384.69 | 1.6431 | 53.6917 | 53.895 | -112.7415
2039-08-18 19:01 | -622.256 | 2.4544 | 53.4915 | 53.895 | -182.3652
2039-08-19 20:01 | -797.298 | 2.92 | 53.3696 | 53.895 | -233.665
2039-08-20 21:01 | -1013.48 | 3.5473 | 53.2804 | 53.895 | -297.0217
2039-08-21 22:01 | -1088.71 | 3.7232 | 53.1588 | 53.895 | -319.0694
2039-08-22 23:01 | -1991.02 | 6.5432 | 53.0754 | 53.895 | -583.5104
2039-08-24 00:01 | -2242.22 | 6.8587 | 52.8483 | 53.895 | -657.1298
2039-08-25 01:01 | -2311.14 | 6.8587 | 52.7073 | 53.895 | -677.3283
2039-08-26 02:01 | -2235.71 | 6.8587 | 52.704 | 53.895 | -655.2219
2039-08-27 03:01 | -2056.21 | 6.4536 | 52.7087 | 53.895 | -602.6157
2039-08-28 04:01 | -1909.47 | 6.0305 | 52.6805 | 53.895 | -559.6104
2039-08-29 05:01 | -1440.07 | 4.5885 | 52.7052 | 53.895 | -422.0429
2039-08-30 06:01 | -1376.36 | 4.5346 | 52.8152 | 53.895 | -403.3713
2039-08-31 07:01 | -1394.12 | 4.5938 | 52.8547 | 53.895 | -408.5762
2039-09-01 08:01 | -1727.75 | 5.6389 | 52.8622 | 53.895 | -506.3535
2039-09-02 09:01 | -1400.69 | 4.5001 | 52.8058 | 53.895 | -410.5017
2039-09-03 10:01 | -789.641 | 2.701 | 52.9048 | 53.895 | -231.4209
2039-09-04 11:01 | -282.512 | 1.3065 | 53.3297 | 53.895 | -82.7961
2039-09-05 12:01 | -320.544 | 1.5611 | 53.4643 | 53.895 | -93.9422
2039-09-06 13:01 | 157.117 | 1 | 54.4367 | 53.895 | 46.0464
2039-09-07 14:01 | 2394.64 | 1 | 54.1323 | 53.895 | 701.7997
2039-09-08 15:01 | 4419.15 | 1.4642 | 69.0404 | 53.895 | 1295.125
2039-09-09 16:01 | 3539.38 | 1.1779 | 69.3456 | 53.895 | 1037.2899
2039-09-10 17:01 | 3305.81 | 1.0815 | 69.721 | 53.895 | 968.8373
2039-09-11 18:01 | 3061.94 | 1 | 77.281 | 53.895 | 897.366
2039-09-12 19:01 | 3079.8 | 1 | 55.0663 | 53.895 | 902.6003
2039-09-13 20:01 | 0 | 0 | 55.6898 | 53.895 | 0
2039-09-14 21:01 | -161.426 | 1.0288 | 54.6192 | 53.895 | -47.3093
2039-09-15 22:01 | -952.537 | 3.499 | 53.9074 | 53.895 | -279.161
2039-09-16 23:01 | -1239.72 | 4.1732 | 53.6361 | 53.895 | -363.3261
2039-09-18 00:01 | -1726.86 | 5.6334 | 53.4574 | 53.895 | -506.0927
2039-09-19 01:01 | -1868.08 | 5.939 | 53.2603 | 53.895 | -547.4802
2039-09-20 02:01 | -1941.11 | 6.1455 | 53.1524 | 53.895 | -568.8832
2039-09-21 03:01 | -1868.37 | 5.9032 | 53.0428 | 53.895 | -547.5652
2039-09-22 04:01 | -1931.79 | 6.1342 | 52.9867 | 53.895 | -566.1518
2039-09-23 05:01 | -1942.8 | 6.1505 | 52.9154 | 53.895 | -569.3785
2039-09-24 06:01 | -2112.98 | 6.6934 | 52.8595 | 53.895 | -619.2533
2039-09-25 07:01 | -2056.55 | 6.4638 | 52.7717 | 53.895 | -602.7153
2039-09-26 08:01 | -1665.41 | 5.2505 | 52.7511 | 53.895 | -488.0835
2039-09-27 09:01 | -426.322 | 1.49 | 52.9154 | 53.895 | -124.9426
2039-09-28 10:01 | 2693.75 | 1 | 53.9538 | 53.895 | 789.4602
2039-09-29 11:01 | 3304.3 | 1.1481 | 68.3958 | 53.895 | 968.3947
2039-09-30 12:01 | 4924.44 | 1.6702 | 69.0177 | 53.895 | 1443.2109
2039-10-01 13:01 | 6414.91 | 2.1471 | 69.6035 | 53.895 | 1880.0245
2039-10-02 14:01 | 6918.29 | 2.3312 | 69.976 | 53.895 | 2027.5507
2039-10-03 15:01 | 8057.63 | 2.7191 | 70.3158 | 53.895 | 2361.4582
2039-10-04 16:01 | 7443.31 | 2.5179 | 70.6488 | 53.895 | 2181.4188
2039-10-05 17:01 | 5250.37 | 1.7717 | 70.9036 | 53.895 | 1538.7316
2039-10-06 18:01 | 2848.15 | 1.0012 | 70.2685 | 53.895 | 834.7104
2039-10-07 19:01 | 2849.34 | 1 | 56.1713 | 53.895 | 835.0591
2039-10-08 20:01 | -290.977 | 1.5179 | 55.6833 | 53.895 | -85.2769
2039-10-09 21:01 | -803.598 | 2.9699 | 54.8819 | 53.895 | -235.5113
2039-10-10 22:01 | -1728.43 | 5.688 | 54.3813 | 53.895 | -506.5528
2039-10-11 23:01 | -2225.44 | 6.8587 | 53.9946 | 53.895 | -652.2121
2039-10-13 00:01 | -2791.22 | 6.8587 | 53.356 | 53.895 | -818.0258
2039-10-14 01:01 | -2989.55 | 6.8587 | 52.9384 | 53.895 | -876.1506
2039-10-15 02:01 | -3053.61 | 6.8587 | 52.6933 | 53.895 | -894.9248
2039-10-16 03:01 | -3276.98 | 6.8587 | 52.3575 | 53.895 | -960.388
2039-10-17 04:01 | -3353.69 | 6.8587 | 52.1291 | 53.895 | -982.8695
2039-10-18 05:01 | -2757.36 | 6.8587 | 52.3956 | 53.895 | -808.1024
2039-10-19 06:01 | -2622.96 | 6.8587 | 52.4684 | 53.895 | -768.7137
2039-10-20 07:01 | -2455.92 | 6.8587 | 52.5545 | 53.895 | -719.7591
2039-10-21 08:01 | -2868.77 | 6.8587 | 52.2732 | 53.895 | -840.7535
2039-10-22 09:01 | -2508.96 | 6.8587 | 52.4545 | 53.895 | -735.3036
2039-10-23 10:01 | -1897.07 | 5.9673 | 52.6644 | 53.895 | -555.9763
2039-10-24 11:01 | -1632.97 | 5.2032 | 52.7218 | 53.895 | -478.5763
2039-10-25 12:01 | -1131.19 | 3.7008 | 52.78 | 53.895 | -331.5191
2039-10-26 13:01 | -511.589 | 1.9171 | 53.0009 | 53.895 | -149.9319
2039-10-27 14:01 | 2246.73 | 1 | 53.951 | 53.895 | 658.4516
2039-10-28 15:01 | 2521.72 | 1 | 67.4398 | 53.895 | 739.0432
2039-10-29 16:01 | 3071.87 | 1 | 76.5662 | 53.895 | 900.2762
2039-10-30 17:01 | 3141.18 | 1 | 54.5649 | 53.895 | 920.589
2039-10-31 18:01 | 3078.81 | 1 | 54.7569 | 53.895 | 902.3101
2039-11-01 19:01 | 3192.23 | 1 | 54.8669 | 53.895 | 935.5503
2039-11-02 20:01 | -87.5078 | 0.9391 | 55.0967 | 53.895 | -25.646
2039-11-03 21:01 | -110.258 | 0.94221 | 54.6868 | 53.895 | -32.3134
2039-11-04 22:01 | -733.418 | 2.8397 | 53.8836 | 53.895 | -214.9436
2039-11-05 23:01 | -770.377 | 2.7868 | 53.6857 | 53.895 | -225.7752
2039-11-07 00:01 | -1109.58 | 3.8459 | 53.5477 | 53.895 | -325.1858
2039-11-08 01:01 | -1339.41 | 4.4619 | 53.3839 | 53.895 | -392.5423
2039-11-09 02:01 | -1827.74 | 5.9351 | 53.2699 | 53.895 | -535.6577
2039-11-10 03:01 | -2004.72 | 6.3502 | 53.1154 | 53.895 | -587.5254
2039-11-11 04:01 | -2075.46 | 6.5392 | 53.0074 | 53.895 | -608.2573
2039-11-12 05:01 | -1976.05 | 6.2123 | 52.916 | 53.895 | -579.1231
2039-11-13 06:01 | -2299.33 | 6.8587 | 52.7765 | 53.895 | -673.8671
2039-11-14 07:01 | -2443.08 | 6.8587 | 52.5768 | 53.895 | -715.9961
2039-11-15 08:01 | -2925.86 | 6.8587 | 52.1871 | 53.895 | -857.4849
2039-11-16 09:01 | -2817.84 | 6.8587 | 52.1556 | 53.895 | -825.8274
2039-11-17 10:01 | -2694.98 | 6.8587 | 52.1718 | 53.895 | -789.8207
2039-11-18 11:01 | -1174.88 | 3.6936 | 52.4692 | 53.895 | -344.3233
2039-11-19 12:01 | -1948.49 | 6.4473 | 52.6777 | 53.895 | -571.046
2039-11-20 13:01 | -2637.82 | 6.8587 | 52.2429 | 53.895 | -773.0687
2039-11-21 14:01 | -2005.05 | 6.3428 | 52.4186 | 53.895 | -587.6221
2039-11-22 15:01 | -1892.12 | 6.0098 | 52.4124 | 53.895 | -554.5256
2039-11-23 16:01 | -1748.06 | 5.5882 | 52.405 | 53.895 | -512.3058
2039-11-24 17:01 | -1757.06 | 5.6651 | 52.3696 | 53.895 | -514.9435
2039-11-25 18:01 | -2251.31 | 6.8587 | 52.2541 | 53.895 | -659.7938
2039-11-26 19:01 | -2675.06 | 6.8587 | 51.8831 | 53.895 | -783.9827
2039-11-27 20:01 | -3542.52 | 6.8587 | 51.2024 | 53.895 | -1038.2101
2039-11-28 21:01 | -3790.93 | 6.8587 | 50.8726 | 53.895 | -1111.0119
2039-11-29 22:01 | -4551.98 | 6.8587 | 50.2226 | 53.895 | -1334.0536
2039-11-30 23:01 | -5140.87 | 6.8587 | 49.623 | 53.895 | -1506.6403
2039-12-02 00:01 | -5308.38 | 6.8587 | 49.3075 | 53.895 | -1555.7326
2039-12-03 01:01 | -5302.14 | 6.8587 | 49.1627 | 53.895 | -1553.9038
2039-12-04 02:01 | -5538.9 | 6.8587 | 48.894 | 53.895 | -1623.2913
2039-12-05 03:01 | -5518.46 | 6.8587 | 48.7817 | 53.895 | -1617.301
2039-12-06 04:01 | -5441.45 | 6.8587 | 48.7375 | 53.895 | -1594.7316
2039-12-07 05:01 | -5323.04 | 6.8587 | 48.7467 | 53.895 | -1560.029
2039-12-08 06:01 | -5464.91 | 6.8587 | 48.5981 | 53.895 | -1601.607
2039-12-09 07:01 | -5214.25 | 6.8587 | 48.6957 | 53.895 | -1528.1458
2039-12-10 08:01 | -4663.09 | 6.8587 | 49.0511 | 53.895 | -1366.6168
2039-12-11 09:01 | -3106.53 | 6.8587 | 50.1526 | 53.895 | -910.4341
2039-12-12 10:01 | -1569.6 | 5.0739 | 51.0191 | 53.895 | -460.0044
2039-12-13 11:01 | -446.511 | 1.5994 | 51.4377 | 53.895 | -130.8595
2039-12-14 12:01 | 2397.68 | 1 | 52.6383 | 53.895 | 702.6906
2039-12-15 13:01 | 2745.59 | 1 | 53.1188 | 53.895 | 804.653
2039-12-16 14:01 | 2744.19 | 1 | 73.0391 | 53.895 | 804.2427
2039-12-17 15:01 | 3401.11 | 1.1964 | 67.5041 | 53.895 | 996.7669
2039-12-18 16:01 | 2767.26 | 1 | 70.6014 | 53.895 | 811.0038
2039-12-19 17:01 | 2687.12 | 1 | 54.1415 | 53.895 | 787.5171
2039-12-20 18:01 | -936.206 | 3.5516 | 53.4581 | 53.895 | -274.3749
2039-12-21 19:01 | -1994.25 | 6.5866 | 52.9298 | 53.895 | -584.457
2039-12-22 20:01 | -3422.82 | 6.8587 | 51.7357 | 53.895 | -1003.1295
2039-12-23 21:01 | -4208.94 | 6.8587 | 50.8857 | 53.895 | -1233.5185
2039-12-24 22:01 | -5160.3 | 6.8587 | 49.9369 | 53.895 | -1512.3346
2039-12-25 23:01 | -5918.81 | 6.8587 | 49.0806 | 53.895 | -1734.632
2039-12-27 00:01 | -6315.83 | 6.8587 | 48.4993 | 53.895 | -1850.9871
2039-12-28 01:01 | -6542.19 | 6.8587 | 48.0741 | 53.895 | -1917.3266
2039-12-29 02:01 | -6709.05 | 6.8587 | 47.7382 | 53.895 | -1966.2285
2039-12-30 03:01 | -6687.98 | 6.8587 | 47.5441 | 53.895 | -1960.0535
2039-12-31 04:01 | -6602.29 | 6.8587 | 47.4386 | 53.895 | -1934.9402
2040-01-01 05:01 | -6513.04 | 6.8587 | 47.3657 | 53.895 | -1908.7836
2040-01-02 06:01 | -5716.84 | 6.8587 | 47.8303 | 53.895 | -1675.4404
2040-01-03 07:01 | -5020.1 | 6.8587 | 48.3337 | 53.895 | -1471.2461
2040-01-04 08:01 | -4510.27 | 6.8587 | 48.7683 | 53.895 | -1321.8297
2040-01-05 09:01 | -3105.01 | 6.8587 | 49.8144 | 53.895 | -909.9886
2040-01-06 10:01 | -1314.03 | 4.2583 | 50.6936 | 53.895 | -385.1042
2040-01-07 11:01 | 0 | 1 | 52.4758 | 53.895 | 0
2040-01-08 12:01 | 2878.58 | 1 | 52.3141 | 53.895 | 843.6285
2040-01-09 13:01 | 2907.25 | 1 | 69.6197 | 53.895 | 852.0309
2040-01-10 14:01 | 3382.98 | 1.1352 | 67.662 | 53.895 | 991.4536
2040-01-11 15:01 | 3473.44 | 1.192 | 67.6393 | 53.895 | 1017.9648
2040-01-12 16:01 | 5069.18 | 1.7231 | 67.9978 | 53.895 | 1485.63
2040-01-13 17:01 | 2825.31 | 1 | 68.4673 | 53.895 | 828.0166
2040-01-14 18:01 | 2816.56 | 1 | 54.106 | 53.895 | 825.4523
2040-01-15 19:01 | 0 | 0 | 54.6415 | 53.895 | 0
2040-01-16 20:01 | -318.261 | 1.5798 | 53.4619 | 53.895 | -93.2731
2040-01-17 21:01 | -684.458 | 2.6665 | 53.0673 | 53.895 | -200.5948
2040-01-18 22:01 | -1066.55 | 3.7613 | 52.8227 | 53.895 | -312.5749
2040-01-19 23:01 | -2559.07 | 6.8587 | 52.308 | 53.895 | -749.9894
2040-01-21 00:01 | -3126.53 | 6.8587 | 51.6414 | 53.895 | -916.2955
2040-01-22 01:01 | -3420.82 | 6.8587 | 51.2397 | 53.895 | -1002.5434
2040-01-23 02:01 | -3445.8 | 6.8587 | 51.0651 | 53.895 | -1009.8643
2040-01-24 03:01 | -3426.58 | 6.8587 | 50.9574 | 53.895 | -1004.2315
2040-01-25 04:01 | -3458.14 | 6.8587 | 50.8187 | 53.895 | -1013.4808
2040-01-26 05:01 | -3842.48 | 6.8587 | 50.4875 | 53.895 | -1126.1197
2040-01-27 06:01 | -3093.78 | 6.8587 | 50.8908 | 53.895 | -906.6974
2040-01-28 07:01 | -2835.26 | 6.8587 | 51.1041 | 53.895 | -830.9327
2040-01-29 08:01 | -2849.03 | 6.8587 | 51.1366 | 53.895 | -834.9683
2040-01-30 09:01 | -1947.58 | 6.2436 | 51.6142 | 53.895 | -570.7794
2040-01-31 10:01 | -423.819 | 1.3956 | 51.7347 | 53.895 | -124.2091
2040-02-01 11:01 | 2739.37 | 1 | 52.9352 | 53.895 | 802.8301
2040-02-02 12:01 | 3112.04 | 1.0432 | 67.9168 | 53.895 | 912.0489
2040-02-03 13:01 | 4182.63 | 1.4085 | 68.1281 | 53.895 | 1225.8078
2040-02-04 14:01 | 4975.17 | 1.6359 | 68.7937 | 53.895 | 1458.0784
2040-02-05 15:01 | 3179 | 1.0759 | 68.7359 | 53.895 | 931.6729
2040-02-06 16:01 | 5546.09 | 1.8217 | 69.1528 | 53.895 | 1625.3985
2040-02-07 17:01 | 3338.96 | 1.1093 | 69.3163 | 53.895 | 978.5526
2040-02-08 18:01 | 2950.74 | 1 | 54.6834 | 53.895 | 864.7765
2040-02-09 19:01 | 0 | 0 | 55.1553 | 53.895 | 0
2040-02-10 20:01 | -657.812 | 2.5657 | 53.6259 | 53.895 | -192.7857
2040-02-11 21:01 | -1207.93 | 4.1889 | 53.2679 | 53.895 | -354.0093
2040-02-12 22:01 | -1681.78 | 5.5272 | 52.986 | 53.895 | -492.8811
2040-02-13 23:01 | -2864.05 | 6.8587 | 52.262 | 53.895 | -839.3702
2040-02-15 00:01 | -3302.79 | 6.8587 | 51.6709 | 53.895 | -967.9522
2040-02-16 01:01 | -3415.92 | 6.8587 | 51.3773 | 53.895 | -1001.1073
2040-02-17 02:01 | -3464.74 | 6.8587 | 51.1804 | 53.895 | -1015.4151
2040-02-18 03:01 | -3465.04 | 6.8587 | 51.0606 | 53.895 | -1015.503
2040-02-19 04:01 | -3487.58 | 6.8587 | 50.917 | 53.895 | -1022.1088
2040-02-20 05:01 | -3092.55 | 6.8587 | 51.1069 | 53.895 | -906.3369
2040-02-21 06:01 | -3236.54 | 6.8587 | 50.9853 | 53.895 | -948.5362
2040-02-22 07:01 | -3430.8 | 6.8587 | 50.8211 | 53.895 | -1005.4682
2040-02-23 08:01 | -4009.61 | 6.8587 | 50.3729 | 53.895 | -1175.1007
2040-02-24 09:01 | -4022.63 | 6.8587 | 50.25 | 53.895 | -1178.9165
2040-02-25 10:01 | -3790.5 | 6.8587 | 50.3204 | 53.895 | -1110.8859
2040-02-26 11:01 | -3453.4 | 6.8587 | 50.4916 | 53.895 | -1012.0916
2040-02-27 12:01 | -3298.12 | 6.8587 | 50.5676 | 53.895 | -966.5836
2040-02-28 13:01 | -3159.47 | 6.8587 | 50.6276 | 53.895 | -925.9493
2040-02-29 14:01 | -3019.52 | 6.8587 | 50.693 | 53.895 | -884.934
2040-03-01 15:01 | -2240.3 | 6.8587 | 51.2095 | 53.895 | -656.5671
2040-03-02 16:01 | -1973.94 | 6.3193 | 51.3215 | 53.895 | -578.5047
2040-03-03 17:01 | -2013.05 | 6.4944 | 51.3753 | 53.895 | -589.9667
2040-03-04 18:01 | -2443.8 | 6.8587 | 51.1596 | 53.895 | -716.2071
2040-03-05 19:01 | -2806.87 | 6.8587 | 50.8763 | 53.895 | -822.6124
2040-03-06 20:01 | -3834.81 | 6.8587 | 50.1262 | 53.895 | -1123.8719
2040-03-07 21:01 | -3938.87 | 6.8587 | 49.8997 | 53.895 | -1154.3688
2040-03-08 22:01 | -4492.15 | 6.8587 | 49.4154 | 53.895 | -1316.5192
2040-03-09 23:01 | -5101.46 | 6.8587 | 48.8704 | 53.895 | -1495.0903
2040-03-11 00:01 | -5368.36 | 6.8587 | 48.527 | 53.895 | -1573.311
2040-03-12 01:01 | -5594.45 | 6.8587 | 48.2353 | 53.895 | -1639.5714
2040-03-13 02:01 | -5896.46 | 6.8587 | 47.9169 | 53.895 | -1728.0818
2040-03-14 03:01 | -6029.43 | 6.8587 | 47.6904 | 53.895 | -1767.0515
2040-03-15 04:01 | -6197.45 | 6.8587 | 47.4549 | 53.895 | -1816.2933
2040-03-16 05:01 | -5979.71 | 6.8587 | 47.4903 | 53.895 | -1752.48
2040-03-17 06:01 | -6175.22 | 6.8587 | 47.292 | 53.895 | -1809.7783
2040-03-18 07:01 | -6059.57 | 6.8587 | 47.2836 | 53.895 | -1775.8847
2040-03-19 08:01 | -5689.69 | 6.8587 | 47.4872 | 53.895 | -1667.4835
2040-03-20 09:01 | -4459.34 | 6.8587 | 48.325 | 53.895 | -1306.9035
2040-03-21 10:01 | -3590.39 | 6.8587 | 49.0471 | 53.895 | -1052.2394
2040-03-22 11:01 | -2934.97 | 6.8587 | 49.6447 | 53.895 | -860.1548
2040-03-23 12:01 | -3234.02 | 6.8587 | 49.5875 | 53.895 | -947.7977
2040-03-24 13:01 | -4225.42 | 6.8587 | 48.9535 | 53.895 | -1238.3484
2040-03-25 14:01 | -4469.25 | 6.8587 | 48.6925 | 53.895 | -1309.8079
2040-03-26 15:01 | -3977.91 | 6.8587 | 48.9388 | 53.895 | -1165.8103
2040-03-27 16:01 | -3937.17 | 6.8587 | 48.9593 | 53.895 | -1153.8706
2040-03-28 17:01 | -4105.23 | 6.8587 | 48.815 | 53.895 | -1203.1241
2040-03-29 18:01 | -4757.75 | 6.8587 | 48.3186 | 53.895 | -1394.3589
2040-03-30 19:01 | -5201.67 | 6.8587 | 47.9214 | 53.895 | -1524.459
2040-03-31 20:01 | -6219.22 | 6.8587 | 47.1284 | 53.895 | -1822.6735
2040-04-01 21:01 | -6385.11 | 6.8587 | 46.8144 | 53.895 | -1871.291
2040-04-02 22:01 | -7821.64 | 6.8587 | 45.6742 | 53.895 | -2292.2964
2040-04-03 23:01 | -8431.43 | 6.8587 | 44.964 | 53.895 | -2471.0082
2040-04-05 00:01 | -8204.23 | 6.8587 | 44.8522 | 53.895 | -2404.4225
2040-04-06 01:01 | -8542.73 | 6.8587 | 44.4806 | 53.895 | -2503.627
2040-04-07 02:01 | -8598.62 | 6.8587 | 44.2927 | 53.895 | -2520.0068
2040-04-08 03:01 | -8590.1 | 6.8587 | 44.1519 | 53.895 | -2517.5098
2040-04-09 04:01 | -8469.55 | 6.8587 | 44.133 | 53.895 | -2482.1801
2040-04-10 05:01 | -8167.95 | 6.8587 | 44.2669 | 53.895 | -2393.7898
2040-04-11 06:01 | -8119.67 | 6.8587 | 44.2607 | 53.895 | -2379.6404
2040-04-12 07:01 | -7829.01 | 6.8587 | 44.4171 | 53.895 | -2294.4563
2040-04-13 08:01 | -7297.73 | 6.8587 | 44.7732 | 53.895 | -2138.7535
2040-04-14 09:01 | -5486.21 | 6.8587 | 46.0482 | 53.895 | -1607.8494
2040-04-15 10:01 | -4002.14 | 6.8587 | 47.2902 | 53.895 | -1172.9115
2040-04-16 11:01 | -2677.18 | 6.8587 | 48.4886 | 53.895 | -784.604
2040-04-17 12:01 | -1684.39 | 5.5754 | 49.2163 | 53.895 | -493.646
2040-04-18 13:01 | -1229.06 | 4.1498 | 49.5672 | 53.895 | -360.2019
2040-04-19 14:01 | -757.072 | 2.7424 | 49.9374 | 53.895 | -221.8759
2040-04-20 15:01 | 437.374 | 1 | 51.3986 | 53.895 | 128.1817
2040-04-21 16:01 | -200.589 | 1.3386 | 51.08 | 53.895 | -58.7868
2040-04-22 17:01 | -1336.81 | 4.8749 | 50.6297 | 53.895 | -391.7803
2040-04-23 18:01 | -2833.45 | 6.8587 | 49.952 | 53.895 | -830.4022
2040-04-24 19:01 | -3549.69 | 6.8587 | 49.3216 | 53.895 | -1040.3114
2040-04-25 20:01 | -4851.68 | 6.8587 | 48.3101 | 53.895 | -1421.887
2040-04-26 21:01 | -5561.36 | 6.8587 | 47.5832 | 53.895 | -1629.8737
2040-04-27 22:01 | -6816.63 | 6.8587 | 46.4926 | 53.895 | -1997.757
2040-04-28 23:01 | -7519.32 | 6.8587 | 45.718 | 53.895 | -2203.6952
2040-04-30 00:01 | -7434.22 | 6.8587 | 45.5046 | 53.895 | -2178.7548
2040-05-01 01:01 | -7485.54 | 6.8587 | 45.2984 | 53.895 | -2193.7952
2040-05-02 02:01 | -7392.81 | 6.8587 | 45.2254 | 53.895 | -2166.6187
2040-05-03 03:01 | -7198.96 | 6.8587 | 45.2363 | 53.895 | -2109.8069
2040-05-04 04:01 | -7650.23 | 6.8587 | 44.8589 | 53.895 | -2242.0611
2040-05-05 05:01 | -7082.58 | 6.8587 | 45.1337 | 53.895 | -2075.6993
2040-05-06 06:01 | -7037.47 | 6.8587 | 45.1528 | 53.895 | -2062.4789
2040-05-07 07:01 | -7081.4 | 6.8587 | 45.1066 | 53.895 | -2075.3535
2040-05-08 08:01 | -6563.9 | 6.8587 | 45.4272 | 53.895 | -1923.6892
2040-05-09 09:01 | -4405.17 | 6.8587 | 46.9264 | 53.895 | -1291.0279
2040-05-10 10:01 | -2446.51 | 6.8587 | 48.541 | 53.895 | -717.0013
2040-05-11 11:01 | -728.703 | 2.3818 | 49.1446 | 53.895 | -213.5618
2040-05-12 12:01 | -228.716 | 1.2166 | 50.1061 | 53.895 | -67.03
2040-05-13 13:01 | 2461.76 | 1 | 50.8893 | 53.895 | 721.4706
2040-05-14 14:01 | 2249.51 | 1 | 51.4828 | 53.895 | 659.2663
2040-05-15 15:01 | 2742.82 | 1 | 51.7219 | 53.895 | 803.8412
2040-05-16 16:01 | 2775.81 | 1 | 51.9921 | 53.895 | 813.5096
2040-05-17 17:01 | 2420.57 | 1 | 52.2823 | 53.895 | 709.399
2040-05-18 18:01 | -385.991 | 1.9193 | 51.9188 | 53.895 | -113.1228
2040-05-19 19:01 | -886.309 | 3.335 | 51.4055 | 53.895 | -259.7515
2040-05-20 20:01 | -2118.71 | 6.8587 | 51.1029 | 53.895 | -620.9326
2040-05-21 21:01 | -2459.08 | 6.8587 | 50.6994 | 53.895 | -720.6852
2040-05-22 22:01 | -3469.91 | 6.8587 | 49.8654 | 53.895 | -1016.9302
2040-05-23 23:01 | -3784.29 | 6.8587 | 49.4342 | 53.895 | -1109.0659
2040-05-25 00:01 | -3981.34 | 6.8587 | 49.1604 | 53.895 | -1166.8156
2040-05-26 01:01 | -4150.46 | 6.8587 | 48.9131 | 53.895 | -1216.3798
2040-05-27 02:01 | -4108.09 | 6.8587 | 48.8373 | 53.895 | -1203.9623
2040-05-28 03:01 | -3938.95 | 6.8587 | 48.8696 | 53.895 | -1154.3923
2040-05-29 04:01 | -3789.99 | 6.8587 | 48.9351 | 53.895 | -1110.7364
2040-05-30 05:01 | -3176.64 | 6.8587 | 49.3323 | 53.895 | -930.9813
2040-05-31 06:01 | -3173.76 | 6.8587 | 49.4089 | 53.895 | -930.1372
2040-06-01 07:01 | -3098.21 | 6.8587 | 49.5071 | 53.895 | -907.9957
2040-06-02 08:01 | -3480.38 | 6.8587 | 49.2913 | 53.895 | -1019.9987
2040-06-03 09:01 | -2990.67 | 6.8587 | 49.6035 | 53.895 | -876.4789
2040-06-04 10:01 | -2807.32 | 6.8587 | 49.7771 | 53.895 | -822.7443
2040-06-05 11:01 | -2135.35 | 6.8587 | 50.2704 | 53.895 | -625.8093
2040-06-06 12:01 | -1873.16 | 6.0709 | 50.3717 | 53.895 | -548.969
2040-06-07 13:01 | -1522.54 | 5.001 | 50.4567 | 53.895 | -446.2124
2040-06-08 14:01 | -1072.09 | 3.6449 | 50.5856 | 53.895 | -314.1986
2040-06-09 15:01 | -202.716 | 0.98435 | 51.0907 | 53.895 | -59.4102
2040-06-10 16:01 | -129.92 | 1.0286 | 51.6279 | 53.895 | -38.0758
2040-06-11 17:01 | -250.362 | 1.4041 | 51.4802 | 53.895 | -73.3739
2040-06-12 18:01 | -734.432 | 2.9079 | 51.1971 | 53.895 | -215.2408
2040-06-13 19:01 | -1005.63 | 3.6312 | 51.0897 | 53.895 | -294.7211
2040-06-14 20:01 | -1771.75 | 6.0349 | 51.0235 | 53.895 | -519.2487
2040-06-15 21:01 | -2047.84 | 6.6863 | 50.8891 | 53.895 | -600.1627
2040-06-16 22:01 | -2993.56 | 6.8587 | 50.2243 | 53.895 | -877.3258
2040-06-17 23:01 | -3396.85 | 6.8587 | 49.8143 | 53.895 | -995.5185
2040-06-19 00:01 | -3522.71 | 6.8587 | 49.6102 | 53.895 | -1032.4044
2040-06-20 01:01 | -3770.33 | 6.8587 | 49.3612 | 53.895 | -1104.9746
2040-06-21 02:01 | -4069.87 | 6.8587 | 49.0764 | 53.895 | -1192.7612
2040-06-22 03:01 | -4204.27 | 6.8587 | 48.8793 | 53.895 | -1232.1499
2040-06-23 04:01 | -4402.21 | 6.8587 | 48.6649 | 53.895 | -1290.1604
2040-06-24 05:01 | -4321.77 | 6.8587 | 48.6368 | 53.895 | -1266.5858
2040-06-25 06:01 | -3470.96 | 6.8587 | 49.1682 | 53.895 | -1017.238
2040-06-26 07:01 | -3039.7 | 6.8587 | 49.528 | 53.895 | -890.8481
2040-06-27 08:01 | -3730.52 | 6.8587 | 49.1415 | 53.895 | -1093.3075
2040-06-28 09:01 | -3770.02 | 6.8587 | 49.0587 | 53.895 | -1104.8838
2040-06-29 10:01 | -3522.49 | 6.8587 | 49.1947 | 53.895 | -1032.3399
2040-06-30 11:01 | -3309.76 | 6.8587 | 49.3538 | 53.895 | -969.9949
2040-07-01 12:01 | -3309.66 | 6.8587 | 49.3613 | 53.895 | -969.9656
2040-07-02 13:01 | -2848.41 | 6.8587 | 49.6506 | 53.895 | -834.7866
2040-07-03 14:01 | -2572 | 6.8587 | 49.8801 | 53.895 | -753.7788
2040-07-04 15:01 | -2109.78 | 6.8587 | 50.2418 | 53.895 | -618.3155
2040-07-05 16:01 | -808.927 | 2.5982 | 50.2904 | 53.895 | -237.0731
2040-07-06 17:01 | -1034.84 | 3.7786 | 50.6652 | 53.895 | -303.2817
2040-07-07 18:01 | -1771.26 | 6.0483 | 50.6717 | 53.895 | -519.1051
2040-07-08 19:01 | -2467.66 | 6.8587 | 50.3216 | 53.895 | -723.1998
2040-07-09 20:01 | -2925.78 | 6.8587 | 49.9418 | 53.895 | -857.4615
2040-07-10 21:01 | -3506.18 | 6.8587 | 49.4745 | 53.895 | -1027.5599
2040-07-11 22:01 | -3589.91 | 6.8587 | 49.3009 | 53.895 | -1052.0988
2040-07-12 23:01 | -5376.1 | 6.8587 | 48.0047 | 53.895 | -1575.5794
2040-07-14 00:01 | -5984.06 | 6.8587 | 47.3288 | 53.895 | -1753.7549
2040-07-15 01:01 | -6363.61 | 6.8587 | 46.8414 | 53.895 | -1864.99
2040-07-16 02:01 | -6671.68 | 6.8587 | 46.4517 | 53.895 | -1955.2764
2040-07-17 03:01 | -6837.81 | 6.8587 | 46.167 | 53.895 | -2003.9643
2040-07-18 04:01 | -7108.41 | 6.8587 | 45.8066 | 53.895 | -2083.2693
2040-07-19 05:01 | -6894.82 | 6.8587 | 45.799 | 53.895 | -2020.6723
2040-07-20 06:01 | -7150.38 | 6.8587 | 45.5317 | 53.895 | -2095.5695
2040-07-21 07:01 | -5882.84 | 6.8587 | 46.2843 | 53.895 | -1724.0902
2040-07-22 08:01 | -4007.52 | 6.8587 | 47.6338 | 53.895 | -1174.4882
2040-07-23 09:01 | -3070.23 | 6.8587 | 48.5213 | 53.895 | -899.7956
2040-07-24 10:01 | -1168.62 | 3.8509 | 49.4201 | 53.895 | -342.4887
2040-07-25 11:01 | 0 | 1 | 51.2084 | 53.895 | 0
2040-07-26 12:01 | 2990.55 | 1 | 70.9338 | 53.895 | 876.4437
2040-07-27 13:01 | 2985.04 | 1 | 66.4712 | 53.895 | 874.8289
2040-07-28 14:01 | 2988.12 | 1 | 71.6251 | 53.895 | 875.7315
2040-07-29 15:01 | 3060.32 | 1 | 72.804 | 53.895 | 896.8913
2040-07-30 16:01 | 2997.89 | 1 | 52.5566 | 53.895 | 878.5948
2040-07-31 17:01 | 2973.89 | 1 | 74.0846 | 53.895 | 871.5611
2040-08-01 18:01 | 2903 | 1 | 52.9099 | 53.895 | 850.7853
2040-08-02 19:01 | -108.498 | 1.0282 | 53.0504 | 53.895 | -31.7976
2040-08-03 20:01 | -871.163 | 3.332 | 52.0675 | 53.895 | -255.3127
2040-08-04 21:01 | -1396.27 | 4.8016 | 51.7366 | 53.895 | -409.2063
2040-08-05 22:01 | -1669.63 | 5.5356 | 51.5474 | 53.895 | -489.3203
2040-08-06 23:01 | -1934.17 | 6.3223 | 51.407 | 53.895 | -566.8493
2040-08-08 00:01 | -3121.92 | 6.8587 | 50.5592 | 53.895 | -914.9444
2040-08-09 01:01 | -3509.56 | 6.8587 | 50.0847 | 53.895 | -1028.5505
2040-08-10 02:01 | -3636.48 | 6.8587 | 49.8282 | 53.895 | -1065.7471
2040-08-11 03:01 | -3903.67 | 6.8587 | 49.5286 | 53.895 | -1144.0527
2040-08-12 04:01 | -3875.66 | 6.8587 | 49.4249 | 53.895 | -1135.8438
2040-08-13 05:01 | -3921.51 | 6.8587 | 49.2962 | 53.895 | -1149.2811
2040-08-14 06:01 | -3449.18 | 6.8587 | 49.5466 | 53.895 | -1010.8549
2040-08-15 07:01 | -3465.58 | 6.8587 | 49.5546 | 53.895 | -1015.6612
2040-08-16 08:01 | -2526.94 | 6.8587 | 50.1921 | 53.895 | -740.573
2040-08-17 09:01 | -1587.92 | 5.139 | 50.5699 | 53.895 | -465.3734
2040-08-18 10:01 | 0 | 0 | 52.1768 | 53.895 | 0
2040-08-19 11:01 | 2679.57 | 1 | 51.9862 | 53.895 | 785.3044
2040-08-20 12:01 | 3033.59 | 1 | 68.7927 | 53.895 | 889.0575
2040-08-21 13:01 | 3872.37 | 1.2835 | 67.3778 | 53.895 | 1134.8796
2040-08-22 14:01 | 4146.74 | 1.357 | 67.8741 | 53.895 | 1215.2895
2040-08-23 15:01 | 4384.98 | 1.442 | 68.0771 | 53.895 | 1285.1108
2040-08-24 16:01 | 4920.94 | 1.5903 | 68.5499 | 53.895 | 1442.1852
2040-08-25 17:01 | 3059.16 | 1.0215 | 68.3081 | 53.895 | 896.5513
2040-08-26 18:01 | 2970.53 | 1 | 75.5985 | 53.895 | 870.5764
2040-08-27 19:01 | 3000.87 | 1 | 53.724 | 53.895 | 879.4682
2040-08-28 20:01 | 0 | 0 | 54.3256 | 53.895 | 0
2040-08-29 21:01 | -1215.03 | 4.2469 | 52.6792 | 53.895 | -356.0901
2040-08-30 22:01 | -1595.45 | 5.3011 | 52.2864 | 53.895 | -467.5802
2040-08-31 23:01 | -2859.14 | 6.8587 | 51.5491 | 53.895 | -837.9312
2040-09-02 00:01 | -3214.43 | 6.8587 | 51.0171 | 53.895 | -942.0564
2040-09-03 01:01 | -3305.48 | 6.8587 | 50.6929 | 53.895 | -968.7406
2040-09-04 02:01 | -3541.72 | 6.8587 | 50.3772 | 53.895 | -1037.9757
2040-09-05 03:01 | -3528.85 | 6.8587 | 50.2424 | 53.895 | -1034.2038
2040-09-06 04:01 | -3580.28 | 6.8587 | 50.0832 | 53.895 | -1049.2765
2040-09-07 05:01 | -3484.79 | 6.8587 | 50.069 | 53.895 | -1021.2911
2040-09-08 06:01 | -2789.58 | 6.8587 | 50.4853 | 53.895 | -817.5452
2040-09-09 07:01 | -2689.49 | 6.8587 | 50.5764 | 53.895 | -788.2117
2040-09-10 08:01 | -1553.13 | 5.0025 | 50.9802 | 53.895 | -455.1775
2040-09-11 09:01 | -434.909 | 1.5735 | 51.2786 | 53.895 | -127.4592
2040-09-12 10:01 | 2690.49 | 1 | 70.2141 | 53.895 | 788.5048
2040-09-13 11:01 | 5156.39 | 1.6235 | 68.1498 | 53.895 | 1511.1887
2040-09-14 12:01 | 6458.34 | 2.1118 | 68.187 | 53.895 | 1892.7526
2040-09-15 13:01 | 7354.76 | 2.3846 | 68.824 | 53.895 | 2155.4674
2040-09-16 14:01 | 7589.6 | 2.4602 | 69.2876 | 53.895 | 2224.2922
2040-09-17 15:01 | 7170.82 | 2.34 | 69.5694 | 53.895 | 2101.5599
2040-09-18 16:01 | 7600.98 | 2.4348 | 70.0531 | 53.895 | 2227.6273
2040-09-19 17:01 | 5726.66 | 1.8526 | 70.1582 | 53.895 | 1678.3184
2040-09-20 18:01 | 4427.81 | 1.4257 | 70.2005 | 53.895 | 1297.663
2040-09-21 19:01 | 3245.95 | 1.0396 | 70.1618 | 53.895 | 951.294
2040-09-22 20:01 | 3041.7 | 1 | 54.8746 | 53.895 | 891.4343
2040-09-23 21:01 | 0 | 0 | 55.3467 | 53.895 | 0
2040-09-24 22:01 | -607.579 | 2.1428 | 53.5895 | 53.895 | -178.0638
2040-09-25 23:01 | -1500.32 | 5.1429 | 53.2394 | 53.895 | -439.7004
2040-09-27 00:01 | -2060.97 | 6.6358 | 52.872 | 53.895 | -604.0107
2040-09-28 01:01 | -2309.45 | 6.8587 | 52.482 | 53.895 | -676.833
2040-09-29 02:01 | -2585.73 | 6.8587 | 52.0554 | 53.895 | -757.8027
2040-09-30 03:01 | -2522.27 | 6.8587 | 51.9251 | 53.895 | -739.2044
2040-10-01 04:01 | -2562.04 | 6.8587 | 51.763 | 53.895 | -750.8598
2040-10-02 05:01 | -2365.8 | 6.8587 | 51.7996 | 53.895 | -693.3475
2040-10-03 06:01 | -2162.61 | 6.8587 | 51.8846 | 53.895 | -633.7984
2040-10-04 07:01 | -2146.49 | 6.82 | 51.866 | 53.895 | -629.0741
2040-10-05 08:01 | -1660.99 | 5.2664 | 51.8254 | 53.895 | -486.7881
2040-10-06 09:01 | -597.916 | 2.0462 | 51.9692 | 53.895 | -175.2319
2040-10-07 10:01 | 2369.46 | 1 | 69.6546 | 53.895 | 694.4202
2040-10-08 11:01 | 3874.15 | 1.2645 | 68.2299 | 53.895 | 1135.4013
2040-10-09 12:01 | 3654.41 | 1.1736 | 68.8778 | 53.895 | 1071.0018
2040-10-10 13:01 | 5133.86 | 1.6661 | 68.9248 | 53.895 | 1504.5858
2040-10-11 14:01 | 5052.82 | 1.6114 | 69.522 | 53.895 | 1480.8354
2040-10-12 15:01 | 5214.16 | 1.6903 | 69.5229 | 53.895 | 1528.1195
2040-10-13 16:01 | 5569.22 | 1.787 | 69.8228 | 53.895 | 1632.1773
2040-10-14 17:01 | 5034.76 | 1.6037 | 70.1047 | 53.895 | 1475.5425
2040-10-15 18:01 | 4387.11 | 1.4424 | 69.7421 | 53.895 | 1285.735
2040-10-16 19:01 | 3559.16 | 1.1602 | 69.8758 | 53.895 | 1043.0868
2040-10-17 20:01 | 3094.04 | 1 | 72.8987 | 53.895 | 906.7736
2040-10-18 21:01 | 2702.75 | 1 | 54.9767 | 53.895 | 792.0978
2040-10-19 22:01 | -271.367 | 1.5106 | 54.5456 | 53.895 | -79.5298
2040-10-20 23:01 | -1555.19 | 5.3385 | 53.6378 | 53.895 | -455.7812
2040-10-22 00:01 | -2792.34 | 6.8587 | 52.7366 | 53.895 | -818.3541
2040-10-23 01:01 | -3808.93 | 6.8587 | 51.6913 | 53.895 | -1116.2872
2040-10-24 02:01 | -4631.04 | 6.8587 | 50.7689 | 53.895 | -1357.2238
2040-10-25 03:01 | -5493.05 | 6.8587 | 49.8141 | 53.895 | -1609.854
2040-10-26 04:01 | -5788.57 | 6.8587 | 49.2719 | 53.895 | -1696.4624
2040-10-27 05:01 | -5837.1 | 6.8587 | 48.9632 | 53.895 | -1710.6851
2040-10-28 06:01 | -5748.05 | 6.8587 | 48.8148 | 53.895 | -1684.5872
2040-10-29 07:01 | -5332.13 | 6.8587 | 48.9403 | 53.895 | -1562.693
2040-10-30 08:01 | -3946.53 | 6.8587 | 49.7912 | 53.895 | -1156.6138
2040-10-31 09:01 | -2690.39 | 6.8587 | 50.7125 | 53.895 | -788.4755
2040-11-01 10:01 | -1451.15 | 4.6534 | 51.2291 | 53.895 | -425.2901
2040-11-02 11:01 | -283.935 | 1.1261 | 51.6912 | 53.895 | -83.2131
2040-11-03 12:01 | 2608.75 | 1 | 52.6611 | 53.895 | 764.5492
2040-11-04 13:01 | -94.1846 | 0.98418 | 53.1395 | 53.895 | -27.6028
2040-11-05 14:01 | 2879.22 | 1 | 53.0344 | 53.895 | 843.8161
2040-11-06 15:01 | 979.265 | 1 | 53.6996 | 53.895 | 286.9942
2040-11-07 16:01 | -253.422 | 1.4698 | 53.0649 | 53.895 | -74.2707
2040-11-08 17:01 | -719.399 | 2.805 | 52.5164 | 53.895 | -210.835
2040-11-09 18:01 | -1156.82 | 4.0625 | 52.2437 | 53.895 | -339.0305
2040-11-10 19:01 | -1895.52 | 6.2934 | 52.1003 | 53.895 | -555.5221
2040-11-11 20:01 | -2607.9 | 6.8587 | 51.5372 | 53.895 | -764.3
2040-11-12 21:01 | -3704.09 | 6.8587 | 50.5955 | 53.895 | -1085.5616
2040-11-13 22:01 | -4102.94 | 6.8587 | 50.0845 | 53.895 | -1202.453
2040-11-14 23:01 | -4819.48 | 6.8587 | 49.3942 | 53.895 | -1412.4502
2040-11-16 00:01 | -5195.76 | 6.8587 | 48.8905 | 53.895 | -1522.7269
2040-11-17 01:01 | -5351.62 | 6.8587 | 48.5904 | 53.895 | -1568.405
2040-11-18 02:01 | -5501.36 | 6.8587 | 48.3062 | 53.895 | -1612.2895
2040-11-19 03:01 | -5488.15 | 6.8587 | 48.1817 | 53.895 | -1608.418
2040-11-20 04:01 | -5440.93 | 6.8587 | 48.1178 | 53.895 | -1594.5792
2040-11-21 05:01 | -5266.75 | 6.8587 | 48.1693 | 53.895 | -1543.5321
2040-11-22 06:01 | -4674.64 | 6.8587 | 48.5363 | 53.895 | -1370.0017
2040-11-23 07:01 | -4572.49 | 6.8587 | 48.6402 | 53.895 | -1340.0645
2040-11-24 08:01 | -4590.37 | 6.8587 | 48.6393 | 53.895 | -1345.3046
2040-11-25 09:01 | -4551.32 | 6.8587 | 48.6498 | 53.895 | -1333.8602
2040-11-26 10:01 | -4507.74 | 6.8587 | 48.6512 | 53.895 | -1321.0882
2040-11-27 11:01 | -4319.58 | 6.8587 | 48.7441 | 53.895 | -1265.9439
2040-11-28 12:01 | -4130.44 | 6.8587 | 48.8338 | 53.895 | -1210.5125
2040-11-29 13:01 | -4226.44 | 6.8587 | 48.7472 | 53.895 | -1238.6473
2040-11-30 14:01 | -4217.67 | 6.8587 | 48.6899 | 53.895 | -1236.0771
2040-12-01 15:01 | -3986.81 | 6.8587 | 48.7921 | 53.895 | -1168.4187
2040-12-02 16:01 | -3403.62 | 6.8587 | 49.1699 | 53.895 | -997.5026
2040-12-03 17:01 | -3503.36 | 6.8587 | 49.1422 | 53.895 | -1026.7335
2040-12-04 18:01 | -3383.24 | 6.8587 | 49.2111 | 53.895 | -991.5298
2040-12-05 19:01 | -4033.47 | 6.8587 | 48.7627 | 53.895 | -1182.0934
2040-12-06 20:01 | -4657.88 | 6.8587 | 48.2588 | 53.895 | -1365.0899
2040-12-07 21:01 | -5592.25 | 6.8587 | 47.4983 | 53.895 | -1638.9267
2040-12-08 22:01 | -6022.63 | 6.8587 | 47.0172 | 53.895 | -1765.0586
2040-12-09 23:01 | -6790.36 | 6.8587 | 46.3292 | 53.895 | -1990.0581
2040-12-11 00:01 | -7545.94 | 6.8587 | 45.6062 | 53.895 | -2211.4967
2040-12-12 01:01 | -7743.62 | 6.8587 | 45.2425 | 53.895 | -2269.431
2040-12-13 02:01 | -8141.92 | 6.8587 | 44.797 | 53.895 | -2386.1612
2040-12-14 03:01 | -8538.69 | 6.8587 | 44.3554 | 53.895 | -2502.443
2040-12-15 04:01 | -8851.66 | 6.8587 | 43.9518 | 53.895 | -2594.1655
2040-12-16 05:01 | -9207.75 | 6.8587 | 43.5282 | 53.895 | -2698.5251
2040-12-17 06:01 | -9353.55 | 6.8587 | 43.2432 | 53.895 | -2741.2549
2040-12-18 07:01 | -8089.24 | 6.8587 | 43.9449 | 53.895 | -2370.7222
2040-12-19 08:01 | -6388.4 | 6.8587 | 45.1345 | 53.895 | -1872.2552
2040-12-20 09:01 | -5566.55 | 6.8587 | 45.8848 | 53.895 | -1631.3948
2040-12-21 10:01 | -4539.61 | 6.8587 | 46.7517 | 53.895 | -1330.4284
2040-12-22 11:01 | -3187.77 | 6.8587 | 47.8794 | 53.895 | -934.2432
2040-12-23 12:01 | -2617.72 | 6.8587 | 48.5618 | 53.895 | -767.178
2040-12-24 13:01 | -1927.62 | 6.3942 | 49.18 | 53.895 | -564.9297
2040-12-25 14:01 | -1852.51 | 6.14 | 49.3956 | 53.895 | -542.9171
2040-12-26 15:01 | -2468.62 | 6.8587 | 49.2865 | 53.895 | -723.4811
2040-12-27 16:01 | -2469.99 | 6.8587 | 49.3275 | 53.895 | -723.8826
2040-12-28 17:01 | -2307.32 | 6.8587 | 49.4902 | 53.895 | -676.2087
2040-12-29 18:01 | -3349.44 | 6.8587 | 48.8619 | 53.895 | -981.624
2040-12-30 19:01 | -4116.51 | 6.8587 | 48.2628 | 53.895 | -1206.43
2040-12-31 20:01 | -4888.96 | 6.8587 | 47.6004 | 53.895 | -1432.8127
2041-01-01 21:01 | -5166.35 | 6.8587 | 47.2689 | 53.895 | -1514.1077
2041-01-02 22:01 | -5678.61 | 6.8587 | 46.8012 | 53.895 | -1664.2363
2041-01-03 23:01 | -5738.39 | 6.8587 | 46.608 | 53.895 | -1681.7561
2041-01-05 00:01 | -7200.68 | 6.8587 | 45.5042 | 53.895 | -2110.311
2041-01-06 01:01 | -7644.56 | 6.8587 | 44.9432 | 53.895 | -2240.3994
2041-01-07 02:01 | -7822.49 | 6.8587 | 44.6063 | 53.895 | -2292.5455
2041-01-08 03:01 | -7943.09 | 6.8587 | 44.3699 | 53.895 | -2327.8899
2041-01-09 04:01 | -7991.18 | 6.8587 | 44.2038 | 53.895 | -2341.9837
2041-01-10 05:01 | -8208.92 | 6.8587 | 43.9279 | 53.895 | -2405.797
2041-01-11 06:01 | -8068.48 | 6.8587 | 43.9159 | 53.895 | -2364.6381
2041-01-12 07:01 | -7363.86 | 6.8587 | 44.3314 | 53.895 | -2158.1343
2041-01-13 08:01 | -6448.25 | 6.8587 | 44.9821 | 53.895 | -1889.7955
2041-01-14 09:01 | -6916.05 | 6.8587 | 44.7568 | 53.895 | -2026.8942
2041-01-15 10:01 | -6354.64 | 6.8587 | 45.1031 | 53.895 | -1862.3611
2041-01-16 11:01 | -5744.42 | 6.8587 | 45.544 | 53.895 | -1683.5233
2041-01-17 12:01 | -4938.36 | 6.8587 | 46.1885 | 53.895 | -1447.2904
2041-01-18 13:01 | -4283.97 | 6.8587 | 46.7644 | 53.895 | -1255.5077
2041-01-19 14:01 | -2959.1 | 6.8587 | 47.8016 | 53.895 | -867.2266
2041-01-20 15:01 | -2689.87 | 6.8587 | 48.2348 | 53.895 | -788.3231
2041-01-21 16:01 | -2939.78 | 6.8587 | 48.243 | 53.895 | -861.5645
2041-01-22 17:01 | -1892.65 | 6.3207 | 48.9309 | 53.895 | -554.681
2041-01-23 18:01 | -2722.43 | 6.8587 | 48.6818 | 53.895 | -797.8655
2041-01-24 19:01 | -3314.08 | 6.8587 | 48.3217 | 53.895 | -971.261
2041-01-25 20:01 | -3833.29 | 6.8587 | 47.9178 | 53.895 | -1123.4264
2041-01-26 21:01 | -4253.99 | 6.8587 | 47.5776 | 53.895 | -1246.7214
2041-01-27 22:01 | -4477.72 | 6.8587 | 47.3728 | 53.895 | -1312.2902
2041-01-28 23:01 | -4565 | 6.8587 | 47.2493 | 53.895 | -1337.8694
2041-01-30 00:01 | -5510.11 | 6.8587 | 46.5733 | 53.895 | -1614.8538
2041-01-31 01:01 | -5560.15 | 6.8587 | 46.4128 | 53.895 | -1629.5191
2041-02-01 02:01 | -5442.8 | 6.8587 | 46.4134 | 53.895 | -1595.1272
2041-02-02 03:01 | -5468.23 | 6.8587 | 46.3721 | 53.895 | -1602.58
2041-02-03 04:01 | -5373.08 | 6.8587 | 46.4144 | 53.895 | -1574.6943
2041-02-04 05:01 | -5371.41 | 6.8587 | 46.3951 | 53.895 | -1574.2049
2041-02-05 06:01 | -4840.39 | 6.8587 | 46.7619 | 53.895 | -1418.5783
2041-02-06 07:01 | -4604.35 | 6.8587 | 46.9888 | 53.895 | -1349.4018
2041-02-07 08:01 | -4007.51 | 6.8587 | 47.4548 | 53.895 | -1174.4852
2041-02-08 09:01 | -4237.75 | 6.8587 | 47.4027 | 53.895 | -1241.9619
2041-02-09 10:01 | -3484.46 | 6.8587 | 47.9471 | 53.895 | -1021.1944
2041-02-10 11:01 | -2835.96 | 6.8587 | 48.4985 | 53.895 | -831.1378
2041-02-11 12:01 | -2410.61 | 6.8587 | 48.9323 | 53.895 | -706.4801
2041-02-12 13:01 | -2101.71 | 6.8587 | 49.2758 | 53.895 | -615.9504
2041-02-13 14:01 | -1947.87 | 6.4087 | 49.3901 | 53.895 | -570.8643
2041-02-14 15:01 | -1762.41 | 5.8299 | 49.4976 | 53.895 | -516.5114
2041-02-15 16:01 | -946.489 | 3.1891 | 49.6121 | 53.895 | -277.3885
2041-02-16 17:01 | -539.568 | 2.1385 | 49.981 | 53.895 | -158.1318
2041-02-17 18:01 | -135.49 | 0.9369 | 50.6441 | 53.895 | -39.7082
2041-02-18 19:01 | -297.105 | 1.5761 | 50.599 | 53.895 | -87.0729
2041-02-19 20:01 | -238.762 | 1.3254 | 50.7424 | 53.895 | -69.9742
2041-02-20 21:01 | -1215.04 | 4.4945 | 50.4322 | 53.895 | -356.0931
2041-02-21 22:01 | -1597.64 | 5.4347 | 50.2926 | 53.895 | -468.2221
2041-02-22 23:01 | -2481.98 | 6.8587 | 49.9345 | 53.895 | -727.3965
2041-02-24 00:01 | -2969.38 | 6.8587 | 49.4976 | 53.895 | -870.2394
2041-02-25 01:01 | -3447.32 | 6.8587 | 49.0662 | 53.895 | -1010.3098
2041-02-26 02:01 | -3906.94 | 6.8587 | 48.6379 | 53.895 | -1145.0111
2041-02-27 03:01 | -3928.28 | 6.8587 | 48.5109 | 53.895 | -1151.2652
2041-02-28 04:01 | -4069.55 | 6.8587 | 48.3373 | 53.895 | -1192.6674
2041-03-01 05:01 | -4024.67 | 6.8587 | 48.3035 | 53.895 | -1179.5143
2041-03-02 06:01 | -3824.3 | 6.8587 | 48.3911 | 53.895 | -1120.7917
2041-03-03 07:01 | -3776.14 | 6.8587 | 48.4099 | 53.895 | -1106.6774
2041-03-04 08:01 | -3777.97 | 6.8587 | 48.3913 | 53.895 | -1107.2137
2041-03-05 09:01 | -4132.64 | 6.8587 | 48.1339 | 53.895 | -1211.1572
2041-03-06 10:01 | -3810.7 | 6.8587 | 48.2928 | 53.895 | -1116.8059
2041-03-07 11:01 | -3302.26 | 6.8587 | 48.6378 | 53.895 | -967.7969
2041-03-08 12:01 | -2811.75 | 6.8587 | 49.024 | 53.895 | -824.0426
2041-03-09 13:01 | 0 | 0 | 51.0213 | 53.895 | 0
2041-03-10 14:01 | 2571.97 | 1 | 50.9652 | 53.895 | 753.77
2041-03-11 15:01 | 2899.13 | 1 | 51.4572 | 53.895 | 849.6511
2041-03-12 16:01 | 2953.98 | 1 | 51.8052 | 53.895 | 865.7261
2041-03-13 17:01 | -439.251 | 2.0672 | 51.5653 | 53.895 | -128.7318
2041-03-14 18:01 | -917.401 | 3.4332 | 51.1154 | 53.895 | -268.8637
2041-03-15 19:01 | -1751.7 | 6.0044 | 50.8691 | 53.895 | -513.3726
2041-03-16 20:01 | -2485.15 | 6.8587 | 50.3836 | 53.895 | -728.3256
2041-03-17 21:01 | -3591.73 | 6.8587 | 49.4438 | 53.895 | -1052.6322
2041-03-18 22:01 | -3894.66 | 6.8587 | 48.9785 | 53.895 | -1141.4122
2041-03-19 23:01 | -4916.87 | 6.8587 | 48.1365 | 53.895 | -1440.9924
2041-03-21 00:01 | -4882.26 | 6.8587 | 47.9509 | 53.895 | -1430.8492
2041-03-22 01:01 | -5133.33 | 6.8587 | 47.6288 | 53.895 | -1504.4305
2041-03-23 02:01 | -5211.96 | 6.8587 | 47.4148 | 53.895 | -1527.4747
2041-03-24 03:01 | -4824.63 | 6.8587 | 47.5423 | 53.895 | -1413.9595
2041-03-25 04:01 | -4997.72 | 6.8587 | 47.3535 | 53.895 | -1464.6871
2041-03-26 05:01 | -4862.73 | 6.8587 | 47.3924 | 53.895 | -1425.1255
2041-03-27 06:01 | -4003.21 | 6.8587 | 47.9423 | 53.895 | -1173.225
2041-03-28 07:01 | -3778.3 | 6.8587 | 48.1752 | 53.895 | -1107.3104
2041-03-29 08:01 | -3653.92 | 6.8587 | 48.3233 | 53.895 | -1070.8582
2041-03-30 09:01 | -3675.45 | 6.8587 | 48.3523 | 53.895 | -1077.1681
2041-03-31 10:01 | -3413.48 | 6.8587 | 48.5581 | 53.895 | -1000.3922
2041-04-01 11:01 | -3167.53 | 6.8587 | 48.7826 | 53.895 | -928.3114
2041-04-02 12:01 | -2786.23 | 6.8587 | 49.0937 | 53.895 | -816.5634
2041-04-03 13:01 | -2670.75 | 6.8587 | 49.2309 | 53.895 | -782.7196
2041-04-04 14:01 | -2724.04 | 6.8587 | 49.2235 | 53.895 | -798.3373
2041-04-05 15:01 | -2732.95 | 6.8587 | 49.2166 | 53.895 | -800.9486
2041-04-06 16:01 | -2260.94 | 6.8587 | 49.5299 | 53.895 | -662.6161
2041-04-07 17:01 | -2082.58 | 6.8371 | 49.7103 | 53.895 | -610.3439
2041-04-08 18:01 | -2065.34 | 6.7657 | 49.7552 | 53.895 | -605.2914
2041-04-09 19:01 | -2581.52 | 6.8587 | 49.4507 | 53.895 | -756.5688
2041-04-10 20:01 | -2820.48 | 6.8587 | 49.2504 | 53.895 | -826.6011
2041-04-11 21:01 | -3834.95 | 6.8587 | 48.5277 | 53.895 | -1123.9129
2041-04-12 22:01 | -4109.15 | 6.8587 | 48.2042 | 53.895 | -1204.273
2041-04-13 23:01 | -4948.72 | 6.8587 | 47.5226 | 53.895 | -1450.3267
2041-04-15 00:01 | -5283.39 | 6.8587 | 47.1265 | 53.895 | -1548.4088
2041-04-16 01:01 | -5471.13 | 6.8587 | 46.8546 | 53.895 | -1603.4299
2041-04-17 02:01 | -5716.32 | 6.8587 | 46.5716 | 53.895 | -1675.288
2041-04-18 03:01 | -5540.95 | 6.8587 | 46.5855 | 53.895 | -1623.8921
2041-04-19 04:01 | -5168.71 | 6.8587 | 46.7772 | 53.895 | -1514.7994
2041-04-20 05:01 | -5245.79 | 6.8587 | 46.7213 | 53.895 | -1537.3893
2041-04-21 06:01 | -4508.67 | 6.8587 | 47.1892 | 53.895 | -1321.3607
2041-04-22 07:01 | -4421.24 | 6.8587 | 47.3042 | 53.895 | -1295.7375
2041-04-23 08:01 | -4129.79 | 6.8587 | 47.5387 | 53.895 | -1210.322
2041-04-24 09:01 | -4246.83 | 6.8587 | 47.5096 | 53.895 | -1244.623
2041-04-25 10:01 | -3767.42 | 6.8587 | 47.8455 | 53.895 | -1104.1218
2041-04-26 11:01 | -2853.5 | 6.8587 | 48.541 | 53.895 | -836.2783
2041-04-27 12:01 | -2816.73 | 6.8587 | 48.7128 | 53.895 | -825.5021
2041-04-28 13:01 | -2274.6 | 6.8587 | 49.1627 | 53.895 | -666.6195
2041-04-29 14:01 | -2392.35 | 6.8587 | 49.1868 | 53.895 | -701.1286
2041-04-30 15:01 | -2409.32 | 6.8587 | 49.2348 | 53.895 | -706.102
2041-05-01 16:01 | -1856.44 | 6.1129 | 49.4872 | 53.895 | -544.0689
2041-05-02 17:01 | -1761.33 | 5.8514 | 49.5921 | 53.895 | -516.1949
2041-05-03 18:01 | -1847.95 | 6.1623 | 49.6691 | 53.895 | -541.5807
2041-05-04 19:01 | -2199.45 | 6.8587 | 49.6052 | 53.895 | -644.5952
2041-05-05 20:01 | -2512.71 | 6.8587 | 49.3858 | 53.895 | -736.4026
2041-05-06 21:01 | -3762.3 | 6.8587 | 48.5189 | 53.895 | -1102.6213
2041-05-07 22:01 | -4194.58 | 6.8587 | 48.0703 | 53.895 | -1229.31
2041-05-08 23:01 | -4911.12 | 6.8587 | 47.4452 | 53.895 | -1439.3072
2041-05-10 00:01 | -5385.93 | 6.8587 | 46.9624 | 53.895 | -1578.4603
2041-05-11 01:01 | -5862.54 | 6.8587 | 46.4741 | 53.895 | -1718.1409
2041-05-12 02:01 | -6233.1 | 6.8587 | 46.0557 | 53.895 | -1826.7413
2041-05-13 03:01 | -6343.25 | 6.8587 | 45.8338 | 53.895 | -1859.0231
2041-05-14 04:01 | -6383.75 | 6.8587 | 45.6821 | 53.895 | -1870.8924
2041-05-15 05:01 | -6439.78 | 6.8587 | 45.5459 | 53.895 | -1887.3132
2041-05-16 06:01 | -6340.87 | 6.8587 | 45.5182 | 53.895 | -1858.3256
2041-05-17 07:01 | -6188.6 | 6.8587 | 45.5553 | 53.895 | -1813.6996
2041-05-18 08:01 | -5244.49 | 6.8587 | 46.1578 | 53.895 | -1537.0083
2041-05-19 09:01 | -4488.5 | 6.8587 | 46.753 | 53.895 | -1315.4495
2041-05-20 10:01 | -3078.75 | 6.8587 | 47.8351 | 53.895 | -902.2926
2041-05-21 11:01 | -1974.26 | 6.6244 | 48.7673 | 53.895 | -578.5985
2041-05-22 12:01 | -1492.71 | 4.9431 | 49.011 | 53.895 | -437.4701
2041-05-23 13:01 | -1575.59 | 5.3908 | 49.2792 | 53.895 | -461.7598
2041-05-24 14:01 | -2897.13 | 6.8587 | 48.8053 | 53.895 | -849.065
2041-05-25 15:01 | -2010.28 | 6.681 | 49.3198 | 53.895 | -589.1549
2041-05-26 16:01 | -1778.02 | 5.8585 | 49.4003 | 53.895 | -521.0862
2041-05-27 17:01 | -2218.28 | 6.8587 | 49.403 | 53.895 | -650.1137
2041-05-28 18:01 | -2421.89 | 6.8587 | 49.2542 | 53.895 | -709.7859
2041-05-29 19:01 | -3356.31 | 6.8587 | 48.6007 | 53.895 | -983.6374
2041-05-30 20:01 | -3563.51 | 6.8587 | 48.3729 | 53.895 | -1044.3617
2041-05-31 21:01 | -4284.4 | 6.8587 | 47.8083 | 53.895 | -1255.6337
2041-06-01 22:01 | -5083.47 | 6.8587 | 47.1247 | 53.895 | -1489.818
2041-06-02 23:01 | -5623.85 | 6.8587 | 46.5677 | 53.895 | -1648.1877
2041-06-04 00:01 | -6160.87 | 6.8587 | 46.0132 | 53.895 | -1805.5728
2041-06-05 01:01 | -6379.44 | 6.8587 | 45.6868 | 53.895 | -1869.6293
2041-06-06 02:01 | -6748.25 | 6.8587 | 45.2967 | 53.895 | -1977.7168
2041-06-07 03:01 | -6986.17 | 6.8587 | 44.9839 | 53.895 | -2047.4443
2041-06-08 04:01 | -6979.03 | 6.8587 | 44.8493 | 53.895 | -2045.3518
2041-06-09 05:01 | -7021.59 | 6.8587 | 44.7215 | 53.895 | -2057.8249
2041-06-10 06:01 | -7141.66 | 6.8587 | 44.5525 | 53.895 | -2093.0139
2041-06-11 07:01 | -6401.29 | 6.8587 | 44.9729 | 53.895 | -1876.0329
2041-06-12 08:01 | -5937.13 | 6.8587 | 45.3088 | 53.895 | -1740.001
2041-06-13 09:01 | -6167.61 | 6.8587 | 45.2001 | 53.895 | -1807.5481
2041-06-14 10:01 | -5922.48 | 6.8587 | 45.3384 | 53.895 | -1735.7076
2041-06-15 11:01 | -4538.79 | 6.8587 | 46.2813 | 53.895 | -1330.188
2041-06-16 12:01 | -5050.8 | 6.8587 | 46.0982 | 53.895 | -1480.2434
2041-06-17 13:01 | -5251.36 | 6.8587 | 45.9647 | 53.895 | -1539.0217
2041-06-18 14:01 | -5466.37 | 6.8587 | 45.7776 | 53.895 | -1602.0349
2041-06-19 15:01 | -4628.96 | 6.8587 | 46.3126 | 53.895 | -1356.6143
2041-06-20 16:01 | -4501.92 | 6.8587 | 46.4757 | 53.895 | -1319.3825
2041-06-21 17:01 | -3282.49 | 6.8587 | 47.3439 | 53.895 | -962.0029
2041-06-22 18:01 | -4373.88 | 6.8587 | 46.7651 | 53.895 | -1281.8577
2041-06-23 19:01 | -4911.8 | 6.8587 | 46.3644 | 53.895 | -1439.5065
2041-06-24 20:01 | -5475.3 | 6.8587 | 45.9016 | 53.895 | -1604.652
2041-06-25 21:01 | -5915.39 | 6.8587 | 45.5093 | 53.895 | -1733.6297
2041-06-26 22:01 | -6069.19 | 6.8587 | 45.3057 | 53.895 | -1778.704
2041-06-27 23:01 | -6248.23 | 6.8587 | 45.0735 | 53.895 | -1831.1755
2041-06-29 00:01 | -7782.35 | 6.8587 | 43.9447 | 53.895 | -2280.7816
2041-06-30 01:01 | -7966.28 | 6.8587 | 43.5779 | 53.895 | -2334.6862
2041-07-01 02:01 | -8089.59 | 6.8587 | 43.334 | 53.895 | -2370.8248
2041-07-02 03:01 | -8166.45 | 6.8587 | 43.1661 | 53.895 | -2393.3502
2041-07-03 04:01 | -8206.39 | 6.8587 | 43.0283 | 53.895 | -2405.0555
2041-07-04 05:01 | -8039.63 | 6.8587 | 43.0264 | 53.895 | -2356.183
2041-07-05 06:01 | -8047.79 | 6.8587 | 42.9727 | 53.895 | -2358.5744
2041-07-06 07:01 | -6922.88 | 6.8587 | 43.6913 | 53.895 | -2028.8958
2041-07-07 08:01 | -5735.51 | 6.8587 | 44.5919 | 53.895 | -1680.9121
2041-07-08 09:01 | -4919.67 | 6.8587 | 45.3317 | 53.895 | -1441.813
2041-07-09 10:01 | -3481.84 | 6.8587 | 46.4977 | 53.895 | -1020.4266
2041-07-10 11:01 | -2025.75 | 6.8587 | 47.762 | 53.895 | -593.6887
2041-07-11 12:01 | -903.851 | 2.9957 | 48.0925 | 53.895 | -264.8926
2041-07-12 13:01 | 0 | 1 | 49.8746 | 53.895 | 0
2041-07-13 14:01 | 0 | 0 | 50.2269 | 53.895 | 0
2041-07-14 15:01 | 0 | 1 | 50.4745 | 53.895 | 0
2041-07-15 16:01 | -209.532 | 1.395 | 49.9553 | 53.895 | -61.4078
2041-07-16 17:01 | 0 | 1 | 50.7867 | 53.895 | 0
2041-07-17 18:01 | -433.637 | 2.1093 | 49.9651 | 53.895 | -127.0865
2041-07-18 19:01 | -1136.04 | 4.2121 | 49.7285 | 53.895 | -332.9405
2041-07-19 20:01 | -1684.97 | 5.8085 | 49.619 | 53.895 | -493.816
2041-07-20 21:01 | -2124.41 | 6.8587 | 49.4916 | 53.895 | -622.6031
2041-07-21 22:01 | -2398.94 | 6.8587 | 49.2567 | 53.895 | -703.0599
2041-07-22 23:01 | -2861.13 | 6.8587 | 48.8837 | 53.895 | -838.5144
2041-07-24 00:01 | -4321.45 | 6.8587 | 47.8064 | 53.895 | -1266.492
2041-07-25 01:01 | -4661.24 | 6.8587 | 47.3524 | 53.895 | -1366.0746
2041-07-26 02:01 | -4850.63 | 6.8587 | 47.0633 | 53.895 | -1421.5793
2041-07-27 03:01 | -5202.09 | 6.8587 | 46.7132 | 53.895 | -1524.5821
2041-07-28 04:01 | -5652.33 | 6.8587 | 46.2795 | 53.895 | -1656.5344
2041-07-29 05:01 | -6044.66 | 6.8587 | 45.8601 | 53.895 | -1771.515
2041-07-30 06:01 | -6381.97 | 6.8587 | 45.4976 | 53.895 | -1870.3708
2041-07-31 07:01 | -5429.05 | 6.8587 | 46.017 | 53.895 | -1591.0975
2041-08-01 08:01 | -4067.37 | 6.8587 | 46.9675 | 53.895 | -1192.0285
2041-08-02 09:01 | -3500.29 | 6.8587 | 47.513 | 53.895 | -1025.8337
2041-08-03 10:01 | -2172.03 | 6.8587 | 48.5514 | 53.895 | -636.5592
2041-08-04 11:01 | -1094.71 | 3.6042 | 48.8315 | 53.895 | -320.8278
2041-08-05 12:01 | 0 | 0 | 50.5462 | 53.895 | 0
2041-08-06 13:01 | 2704.22 | 1 | 50.388 | 53.895 | 792.5286
2041-08-07 14:01 | 2739.94 | 1 | 50.9052 | 53.895 | 802.9971
2041-08-08 15:01 | 2699.94 | 1 | 51.255 | 53.895 | 791.2743
2041-08-09 16:01 | -191.242 | 1.3088 | 51.2574 | 53.895 | -56.0475
2041-08-10 17:01 | 36.1251 | 1 | 51.7854 | 53.895 | 10.5872
2041-08-11 18:01 | -839.159 | 3.3243 | 50.6186 | 53.895 | -245.9332
2041-08-12 19:01 | -1614.78 | 5.6116 | 50.3776 | 53.895 | -473.2453
2041-08-13 20:01 | -2225.37 | 6.8587 | 50.0624 | 53.895 | -652.1916
2041-08-14 21:01 | -2779.68 | 6.8587 | 49.5311 | 53.895 | -814.6438
2041-08-15 22:01 | -2997.28 | 6.8587 | 49.2657 | 53.895 | -878.4161
2041-08-16 23:01 | -3018.85 | 6.8587 | 49.144 | 53.895 | -884.7376
2041-08-18 00:01 | -4359.24 | 6.8587 | 48.1663 | 53.895 | -1277.5671
2041-08-19 01:01 | -4647.41 | 6.8587 | 47.7392 | 53.895 | -1362.0214
2041-08-20 02:01 | -5044.95 | 6.8587 | 47.2862 | 53.895 | -1478.5289
2041-08-21 03:01 | -4801.37 | 6.8587 | 47.2934 | 53.895 | -1407.1426
2041-08-22 04:01 | -4642.99 | 6.8587 | 47.3398 | 53.895 | -1360.726
2041-08-23 05:01 | -4267.71 | 6.8587 | 47.5537 | 53.895 | -1250.7423
2041-08-24 06:01 | -3691.6 | 6.8587 | 47.9744 | 53.895 | -1081.9012
2041-08-25 07:01 | -3430.26 | 6.8587 | 48.2325 | 53.895 | -1005.31
2041-08-26 08:01 | -1942.46 | 6.4908 | 49.2466 | 53.895 | -569.2788
2041-08-27 09:01 | -1106.45 | 3.6486 | 49.4452 | 53.895 | -324.2685
2041-08-28 10:01 | 2306.86 | 1 | 50.7004 | 53.895 | 676.0739
2041-08-29 11:01 | 2994.64 | 1 | 66.8135 | 53.895 | 877.6423
2041-08-30 12:01 | 4310.69 | 1.4443 | 66.0247 | 53.895 | 1263.3385
2041-08-31 13:01 | 5120.67 | 1.6648 | 66.8661 | 53.895 | 1500.7202
2041-09-01 14:01 | 5140.35 | 1.7081 | 66.9531 | 53.895 | 1506.4879
2041-09-02 15:01 | 4930.46 | 1.6438 | 67.2064 | 53.895 | 1444.9752
2041-09-03 16:01 | 5043.44 | 1.644 | 67.7145 | 53.895 | 1478.0864
2041-09-04 17:01 | 3017.04 | 1 | 68.11 | 53.895 | 884.2071
2041-09-05 18:01 | 3036.23 | 1 | 52.9317 | 53.895 | 889.8312
2041-09-06 19:01 | 2879.23 | 1 | 52.9736 | 53.895 | 843.819
2041-09-07 20:01 | 77.0361 | 1 | 53.4947 | 53.895 | 22.5771
2041-09-08 21:01 | -802.409 | 3.1431 | 52.0102 | 53.895 | -235.1629
2041-09-09 22:01 | -1405.3 | 4.8632 | 51.5605 | 53.895 | -411.8528
2041-09-10 23:01 | -2291.82 | 6.8587 | 51.1541 | 53.895 | -671.6661
2041-09-12 00:01 | -2763.86 | 6.8587 | 50.5811 | 53.895 | -810.0074
2041-09-13 01:01 | -2759.13 | 6.8587 | 50.3378 | 53.895 | -808.6212
2041-09-14 02:01 | -2717.15 | 6.8587 | 50.2343 | 53.895 | -796.3181
2041-09-15 03:01 | -2553.8 | 6.8587 | 50.2541 | 53.895 | -748.4449
2041-09-16 04:01 | -2103.43 | 6.845 | 50.4969 | 53.895 | -616.4545
2041-09-17 05:01 | -1844.04 | 5.9629 | 50.5097 | 53.895 | -540.4348
2041-09-18 06:01 | -1337.41 | 4.4018 | 50.5672 | 53.895 | -391.9562
2041-09-19 07:01 | -1235.36 | 4.2344 | 50.6898 | 53.895 | -362.0483
2041-09-20 08:01 | -1061.12 | 3.684 | 50.7669 | 53.895 | -310.9836
2041-09-21 09:01 | -1475.46 | 5.0828 | 50.8185 | 53.895 | -432.4146
2041-09-22 10:01 | -1514 | 5.0616 | 50.7481 | 53.895 | -443.7096
2041-09-23 11:01 | -1466.93 | 4.9123 | 50.7262 | 53.895 | -429.9147
2041-09-24 12:01 | -1147.81 | 3.8929 | 50.7243 | 53.895 | -336.3899
2041-09-25 13:01 | -1189.1 | 4.1354 | 50.7637 | 53.895 | -348.4908
2041-09-26 14:01 | -1341.17 | 4.6049 | 50.7223 | 53.895 | -393.0581
2041-09-27 15:01 | -1272.61 | 4.3347 | 50.6664 | 53.895 | -372.9652
2041-09-28 16:01 | -535.838 | 1.9811 | 50.7479 | 53.895 | -157.0386
2041-09-29 17:01 | -127.066 | 0.91938 | 51.4459 | 53.895 | -37.2394
2041-09-30 18:01 | 43.3508 | 1 | 52.1685 | 53.895 | 12.7049
2041-10-01 19:01 | -334.058 | 1.7095 | 51.3174 | 53.895 | -97.9027
2041-10-02 20:01 | -528.872 | 2.2279 | 51.1319 | 53.895 | -154.9971
2041-10-03 21:01 | -1282.01 | 4.598 | 50.9519 | 53.895 | -375.72
2041-10-04 22:01 | -1532.17 | 5.1702 | 50.8007 | 53.895 | -449.0347
2041-10-05 23:01 | -2179.26 | 6.8587 | 50.6439 | 53.895 | -638.6781
2041-10-07 00:01 | -2351.29 | 6.8587 | 50.4254 | 53.895 | -689.0951
2041-10-08 01:01 | -2428.67 | 6.8587 | 50.3009 | 53.895 | -711.7729
2041-10-09 02:01 | -2323.77 | 6.8587 | 50.3274 | 53.895 | -681.0298
2041-10-10 03:01 | -2176.3 | 6.8587 | 50.4188 | 53.895 | -637.8106
2041-10-11 04:01 | -1849.61 | 5.9882 | 50.4583 | 53.895 | -542.0672
2041-10-12 05:01 | -1648.73 | 5.4185 | 50.5164 | 53.895 | -483.1951
2041-10-13 06:01 | -1206.41 | 4.0354 | 50.5774 | 53.895 | -353.5639
2041-10-14 07:01 | -1115.22 | 3.8838 | 50.7071 | 53.895 | -326.8387
2041-10-15 08:01 | -994.485 | 3.5065 | 50.7729 | 53.895 | -291.4548
2041-10-16 09:01 | -1073.08 | 3.7982 | 50.8276 | 53.895 | -314.4887
2041-10-17 10:01 | -1570.38 | 5.3808 | 50.7996 | 53.895 | -460.2329
2041-10-18 11:01 | -1577.28 | 5.2382 | 50.7058 | 53.895 | -462.2551
2041-10-19 12:01 | -1509.54 | 5.0354 | 50.6742 | 53.895 | -442.4025
2041-10-20 13:01 | -1642.68 | 5.493 | 50.6602 | 53.895 | -481.422
2041-10-21 14:01 | -1727.77 | 5.7249 | 50.6069 | 53.895 | -506.3594
2041-10-22 15:01 | -2417.98 | 6.8587 | 50.3239 | 53.895 | -708.64
2041-10-23 16:01 | -2106.64 | 6.8575 | 50.4147 | 53.895 | -617.3952
2041-10-24 17:01 | -2210.38 | 6.8587 | 50.3016 | 53.895 | -647.7984
2041-10-25 18:01 | -2794.21 | 6.8587 | 49.8468 | 53.895 | -818.9021
2041-10-26 19:01 | -3440.23 | 6.8587 | 49.2782 | 53.895 | -1008.2319
2041-10-27 20:01 | -3881.85 | 6.8587 | 48.8121 | 53.895 | -1137.6579
2041-10-28 21:01 | -5065.46 | 6.8587 | 47.8589 | 53.895 | -1484.5398
2041-10-29 22:01 | -5594.53 | 6.8587 | 47.2506 | 53.895 | -1639.5949
2041-10-30 23:01 | -6570.44 | 6.8587 | 46.3554 | 53.895 | -1925.6059
2041-11-01 00:01 | -6979.79 | 6.8587 | 45.8059 | 53.895 | -2045.5745
2041-11-02 01:01 | -7068.95 | 6.8587 | 45.5084 | 53.895 | -2071.7047
2041-11-03 02:01 | -7249.45 | 6.8587 | 45.1994 | 53.895 | -2124.6041
2041-11-04 03:01 | -7340.37 | 6.8587 | 44.9773 | 53.895 | -2151.2501
2041-11-05 04:01 | -7099.24 | 6.8587 | 44.989 | 53.895 | -2080.5819
2041-11-06 05:01 | -7117.1 | 6.8587 | 44.884 | 53.895 | -2085.8161
2041-11-07 06:01 | -6937.23 | 6.8587 | 44.9132 | 53.895 | -2033.1014
2041-11-08 07:01 | -6932.03 | 6.8587 | 44.845 | 53.895 | -2031.5774
2041-11-09 08:01 | -6541.72 | 6.8587 | 45.0377 | 53.895 | -1917.1889
2041-11-10 09:01 | -7249.02 | 6.8587 | 44.5359 | 53.895 | -2124.478
2041-11-11 10:01 | -7253.11 | 6.8587 | 44.4056 | 53.895 | -2125.6767
2041-11-12 11:01 | -6853.58 | 6.8587 | 44.5844 | 53.895 | -2008.586
2041-11-13 12:01 | -6943.68 | 6.8587 | 44.4983 | 53.895 | -2034.9917
2041-11-14 13:01 | -7287.91 | 6.8587 | 44.2027 | 53.895 | -2135.8756
2041-11-15 14:01 | -7552.54 | 6.8587 | 43.9046 | 53.895 | -2213.431
2041-11-16 15:01 | -7710.24 | 6.8587 | 43.6861 | 53.895 | -2259.6483
2041-11-17 16:01 | -7152.73 | 6.8587 | 43.9605 | 53.895 | -2096.2582
2041-11-18 17:01 | -7148.72 | 6.8587 | 43.934 | 53.895 | -2095.083
2041-11-19 18:01 | -7095.92 | 6.8587 | 43.921 | 53.895 | -2079.6089
2041-11-20 19:01 | -7821.37 | 6.8587 | 43.3765 | 53.895 | -2292.2173
2041-11-21 20:01 | -8237.32 | 6.8587 | 42.9557 | 53.895 | -2414.1202
2041-11-22 21:01 | -9002.46 | 6.8587 | 42.3002 | 53.895 | -2638.3606
2041-11-23 22:01 | -9363.86 | 6.8587 | 41.8634 | 53.895 | -2744.2765
2041-11-24 23:01 | -10180.5 | 6.8587 | 41.1259 | 53.895 | -2983.61
2041-11-26 00:01 | -10549.8 | 6.8587 | 40.6399 | 53.895 | -3091.8412
2041-11-27 01:01 | -10773.4 | 6.8587 | 40.2829 | 53.895 | -3157.3719
2041-11-28 02:01 | -10978.7 | 6.8587 | 39.9689 | 53.895 | -3217.5394
2041-11-29 03:01 | -11143.9 | 6.8587 | 39.6976 | 53.895 | -3265.9547
2041-11-30 04:01 | -11304.2 | 6.8587 | 39.4264 | 53.895 | -3312.934
2041-12-01 05:01 | -11272.3 | 6.8587 | 39.2984 | 53.895 | -3303.585
2041-12-02 06:01 | -11232.2 | 6.8587 | 39.1982 | 53.895 | -3291.8329
2041-12-03 07:01 | -10393.3 | 6.8587 | 39.667 | 53.895 | -3045.9756
2041-12-04 08:01 | -9291.53 | 6.8587 | 40.4232 | 53.895 | -2723.0786
2041-12-05 09:01 | -8696.2 | 6.8587 | 40.9371 | 53.895 | -2548.6046
2041-12-06 10:01 | -8276.97 | 6.8587 | 41.3215 | 53.895 | -2425.7405
2041-12-07 11:01 | -8632.06 | 6.8587 | 41.1642 | 53.895 | -2529.8071
2041-12-08 12:01 | -8304.32 | 6.8587 | 41.3893 | 53.895 | -2433.7559
2041-12-09 13:01 | -8290.16 | 6.8587 | 41.4332 | 53.895 | -2429.6061
2041-12-10 14:01 | -8349.81 | 6.8587 | 41.4022 | 53.895 | -2447.0878
2041-12-11 15:01 | -7979.45 | 6.8587 | 41.6399 | 53.895 | -2338.5459
2041-12-12 16:01 | -7561.9 | 6.8587 | 41.9488 | 53.895 | -2216.1741
2041-12-13 17:01 | -6244.45 | 6.8587 | 42.9207 | 53.895 | -1830.0676
2041-12-14 18:01 | -6540.3 | 6.8587 | 42.9128 | 53.895 | -1916.7727
2041-12-15 19:01 | -6858.1 | 6.8587 | 42.7671 | 53.895 | -2009.9107
2041-12-16 20:01 | -6947.19 | 6.8587 | 42.7102 | 53.895 | -2036.0204
2041-12-17 21:01 | -6939.81 | 6.8587 | 42.73 | 53.895 | -2033.8575
2041-12-18 22:01 | -7488.89 | 6.8587 | 42.3756 | 53.895 | -2194.777
2041-12-19 23:01 | -7292.81 | 6.8587 | 42.4505 | 53.895 | -2137.3116
2041-12-21 00:01 | -8817.88 | 6.8587 | 41.4053 | 53.895 | -2584.2655
2041-12-22 01:01 | -9404.26 | 6.8587 | 40.8253 | 53.895 | -2756.1165
2041-12-23 02:01 | -9704.35 | 6.8587 | 40.4476 | 53.895 | -2844.0642
2041-12-24 03:01 | -10454.2 | 6.8587 | 39.7992 | 53.895 | -3063.8236
2041-12-25 04:01 | -10590.1 | 6.8587 | 39.5184 | 53.895 | -3103.6519
2041-12-26 05:01 | -10949 | 6.8587 | 39.0989 | 53.895 | -3208.8351
2041-12-27 06:01 | -11157.6 | 6.8587 | 38.8009 | 53.895 | -3269.9698
2041-12-28 07:01 | -10459.4 | 6.8587 | 39.1342 | 53.895 | -3065.3475
2041-12-29 08:01 | -9779.07 | 6.8587 | 39.5668 | 53.895 | -2865.9625
2041-12-30 09:01 | -9768.72 | 6.8587 | 39.6087 | 53.895 | -2862.9292
2041-12-31 10:01 | -9241.76 | 6.8587 | 39.9539 | 53.895 | -2708.4925
2042-01-01 11:01 | -7937.71 | 6.8587 | 40.8829 | 53.895 | -2326.3132
2042-01-02 12:01 | -7166.6 | 6.8587 | 41.6002 | 53.895 | -2100.3231
2042-01-03 13:01 | -6370.62 | 6.8587 | 42.3375 | 53.895 | -1867.0444
2042-01-04 14:01 | -6007.73 | 6.8587 | 42.7855 | 53.895 | -1760.6919
2042-01-05 15:01 | -6084.27 | 6.8587 | 42.9166 | 53.895 | -1783.1235
2042-01-06 16:01 | -6719.96 | 6.8587 | 42.5957 | 53.895 | -1969.4259
2042-01-07 17:01 | -6111.95 | 6.8587 | 43.0089 | 53.895 | -1791.2357
2042-01-08 18:01 | -6868.24 | 6.8587 | 42.5874 | 53.895 | -2012.8824
2042-01-09 19:01 | -7449.1 | 6.8587 | 42.1594 | 53.895 | -2183.1157
2042-01-10 20:01 | -7980.61 | 6.8587 | 41.7012 | 53.895 | -2338.8859
2042-01-11 21:01 | -8267.05 | 6.8587 | 41.4037 | 53.895 | -2422.8332
2042-01-12 22:01 | -8422.82 | 6.8587 | 41.2186 | 53.895 | -2468.4849
2042-01-13 23:01 | -8448.07 | 6.8587 | 41.1119 | 53.895 | -2475.8849
2042-01-15 00:01 | -9458.97 | 6.8587 | 40.3607 | 53.895 | -2772.1505
2042-01-16 01:01 | -9543.16 | 6.8587 | 40.1314 | 53.895 | -2796.8241
2042-01-17 02:01 | -9758.2 | 6.8587 | 39.8664 | 53.895 | -2859.8461
2042-01-18 03:01 | -9658.54 | 6.8587 | 39.8379 | 53.895 | -2830.6387
2042-01-19 04:01 | -9535.69 | 6.8587 | 39.8628 | 53.895 | -2794.6349
2042-01-20 05:01 | -9273.5 | 6.8587 | 39.9962 | 53.895 | -2717.7946
2042-01-21 06:01 | -8667.44 | 6.8587 | 40.4187 | 53.895 | -2540.1759
2042-01-22 07:01 | -8513.94 | 6.8587 | 40.5899 | 53.895 | -2495.1895
2042-01-23 08:01 | -8326.02 | 6.8587 | 40.7654 | 53.895 | -2440.1156
2042-01-24 09:01 | -8275.2 | 6.8587 | 40.8417 | 53.895 | -2425.2217
2042-01-25 10:01 | -7520.46 | 6.8587 | 41.3871 | 53.895 | -2204.0293
2042-01-26 11:01 | -4557.88 | 6.8587 | 43.5213 | 53.895 | -1335.7828
2042-01-27 12:01 | -4792.68 | 6.8587 | 43.7836 | 53.895 | -1404.5959
2042-01-28 13:01 | -2862.65 | 6.8587 | 45.3128 | 53.895 | -838.9599
2042-01-29 14:01 | -2119.99 | 6.8587 | 46.1854 | 53.895 | -621.3077
2042-01-30 15:01 | -1723.87 | 5.9066 | 46.6269 | 53.895 | -505.2164
2042-01-31 16:01 | -1611.94 | 5.5948 | 46.9408 | 53.895 | -472.413
2042-02-01 17:01 | -2549.5 | 6.8587 | 46.7459 | 53.895 | -747.1847
2042-02-02 18:01 | -2676.44 | 6.8587 | 46.7249 | 53.895 | -784.3871
2042-02-03 19:01 | -3229.47 | 6.8587 | 46.4057 | 53.895 | -946.4642
2042-02-04 20:01 | -3541.77 | 6.8587 | 46.2051 | 53.895 | -1037.9903
2042-02-05 21:01 | -4100.88 | 6.8587 | 45.8241 | 53.895 | -1201.8493
2042-02-06 22:01 | -4258.41 | 6.8587 | 45.675 | 53.895 | -1248.0168
2042-02-07 23:01 | -5059.63 | 6.8587 | 45.0947 | 53.895 | -1482.8312
2042-02-09 00:01 | -5182.15 | 6.8587 | 44.9206 | 53.895 | -1518.7382
2042-02-10 01:01 | -5371.77 | 6.8587 | 44.7262 | 53.895 | -1574.3104
2042-02-11 02:01 | -5394.45 | 6.8587 | 44.6551 | 53.895 | -1580.9572
2042-02-12 03:01 | -5392.07 | 6.8587 | 44.6215 | 53.895 | -1580.2597
2042-02-13 04:01 | -5229.43 | 6.8587 | 44.7069 | 53.895 | -1532.5946
2042-02-14 05:01 | -5045.55 | 6.8587 | 44.8541 | 53.895 | -1478.7047
2042-02-15 06:01 | -4652.6 | 6.8587 | 45.1603 | 53.895 | -1363.5425
2042-02-16 07:01 | -4443.63 | 6.8587 | 45.381 | 53.895 | -1302.2994
2042-02-17 08:01 | -3508.89 | 6.8587 | 46.0976 | 53.895 | -1028.3541
2042-02-18 09:01 | -2763.57 | 6.8587 | 46.7838 | 53.895 | -809.9224
2042-02-19 10:01 | -1323.28 | 4.4827 | 47.4921 | 53.895 | -387.8151
2042-02-20 11:01 | -652.019 | 2.4282 | 47.9159 | 53.895 | -191.0879
2042-02-21 12:01 | 159.159 | 1 | 49.4296 | 53.895 | 46.6449
2042-02-22 13:01 | -201.796 | 1.3887 | 49.0544 | 53.895 | -59.1406
2042-02-23 14:01 | 381.101 | 1 | 49.8237 | 53.895 | 111.6897
2042-02-24 15:01 | 2638.57 | 1 | 49.6361 | 53.895 | 773.2885
2042-02-25 16:01 | -51.3362 | 0.88863 | 50.2457 | 53.895 | -15.0452
2042-02-26 17:01 | -640.641 | 2.7189 | 49.3581 | 53.895 | -187.7533
2042-02-27 18:01 | -968.946 | 3.6311 | 49.1384 | 53.895 | -283.97
2042-02-28 19:01 | -1730.75 | 6.073 | 49.0676 | 53.895 | -507.2328
2042-03-01 20:01 | -2534.6 | 6.8587 | 48.6073 | 53.895 | -742.8179
2042-03-02 21:01 | -3927.66 | 6.8587 | 47.4901 | 53.895 | -1151.0835
2042-03-03 22:01 | -4723.46 | 6.8587 | 46.7152 | 53.895 | -1384.3095
2042-03-04 23:01 | -5745.65 | 6.8587 | 45.7942 | 53.895 | -1683.8838
2042-03-06 00:01 | -6229.27 | 6.8587 | 45.2023 | 53.895 | -1825.6188
2042-03-07 01:01 | -6738.76 | 6.8587 | 44.6319 | 53.895 | -1974.9356
2042-03-08 02:01 | -7228.59 | 6.8587 | 44.0801 | 53.895 | -2118.4906
2042-03-09 03:01 | -7490.42 | 6.8587 | 43.6702 | 53.895 | -2195.2254
2042-03-10 04:01 | -7597.45 | 6.8587 | 43.4186 | 53.895 | -2226.5928
2042-03-11 05:01 | -7617.06 | 6.8587 | 43.2681 | 53.895 | -2232.3399
2042-03-12 06:01 | -7252.83 | 6.8587 | 43.4014 | 53.895 | -2125.5946
2042-03-13 07:01 | -7245.68 | 6.8587 | 43.3558 | 53.895 | -2123.4992
2042-03-14 08:01 | -6327.11 | 6.8587 | 43.9277 | 53.895 | -1854.2929
2042-03-15 09:01 | -6477.93 | 6.8587 | 43.8847 | 53.895 | -1898.4939
2042-03-16 10:01 | -6134.95 | 6.8587 | 44.1099 | 53.895 | -1797.9764
2042-03-17 11:01 | -3947.63 | 6.8587 | 45.6208 | 53.895 | -1156.9361
2042-03-18 12:01 | -4534.98 | 6.8587 | 45.4832 | 53.895 | -1329.0714
2042-03-19 13:01 | -4141.87 | 6.8587 | 45.8191 | 53.895 | -1213.8623
2042-03-20 14:01 | -3306.91 | 6.8587 | 46.4499 | 53.895 | -969.1597
2042-03-21 15:01 | -3579.7 | 6.8587 | 46.4171 | 53.895 | -1049.1065
2042-03-22 16:01 | -2653.55 | 6.8587 | 47.1212 | 53.895 | -777.6787
2042-03-23 17:01 | -3714.53 | 6.8587 | 46.5294 | 53.895 | -1088.6213
2042-03-24 18:01 | -4467.82 | 6.8587 | 45.9863 | 53.895 | -1309.3888
2042-03-25 19:01 | -5155.09 | 6.8587 | 45.4186 | 53.895 | -1510.8077
2042-03-26 20:01 | -5556.04 | 6.8587 | 45.0137 | 53.895 | -1628.3146
2042-03-27 21:01 | -6531.51 | 6.8587 | 44.2416 | 53.895 | -1914.1966
2042-03-28 22:01 | -6768.74 | 6.8587 | 43.878 | 53.895 | -1983.7219
2042-03-29 23:01 | -7593.25 | 6.8587 | 43.1539 | 53.895 | -2225.3619
2042-03-31 00:01 | -8233.47 | 6.8587 | 42.5222 | 53.895 | -2412.9919
2042-04-01 01:01 | -8594.08 | 6.8587 | 42.067 | 53.895 | -2518.6762
2042-04-02 02:01 | -8788.02 | 6.8587 | 41.7434 | 53.895 | -2575.5144
2042-04-03 03:01 | -8845.76 | 6.8587 | 41.5534 | 53.895 | -2592.4363
2042-04-04 04:01 | -8891.11 | 6.8587 | 41.3817 | 53.895 | -2605.7271
2042-04-05 05:01 | -8861.95 | 6.8587 | 41.2927 | 53.895 | -2597.1812
2042-04-06 06:01 | -8716.23 | 6.8587 | 41.3096 | 53.895 | -2554.4749
2042-04-07 07:01 | -8103.15 | 6.8587 | 41.6786 | 53.895 | -2374.7988
2042-04-08 08:01 | -7675.81 | 6.8587 | 41.9889 | 53.895 | -2249.5578
2042-04-09 09:01 | -7896.47 | 6.8587 | 41.8815 | 53.895 | -2314.2269
2042-04-10 10:01 | -8216.04 | 6.8587 | 41.6328 | 53.895 | -2407.8836
2042-04-11 11:01 | -7447.05 | 6.8587 | 42.0816 | 53.895 | -2182.5149
2042-04-12 12:01 | -7136.54 | 6.8587 | 42.34 | 53.895 | -2091.5134
2042-04-13 13:01 | -7026.82 | 6.8587 | 42.4566 | 53.895 | -2059.3577
2042-04-14 14:01 | -7234.97 | 6.8587 | 42.3141 | 53.895 | -2120.3604
2042-04-15 15:01 | -7256.81 | 6.8587 | 42.2583 | 53.895 | -2126.7611
2042-04-16 16:01 | -7451.32 | 6.8587 | 42.0982 | 53.895 | -2183.7663
2042-04-17 17:01 | -6256.51 | 6.8587 | 42.8655 | 53.895 | -1833.6021
2042-04-18 18:01 | -6838.29 | 6.8587 | 42.5739 | 53.895 | -2004.105
2042-04-19 19:01 | -7144.85 | 6.8587 | 42.339 | 53.895 | -2093.9488
2042-04-20 20:01 | -7453.41 | 6.8587 | 42.0628 | 53.895 | -2184.3788
2042-04-21 21:01 | -7725.92 | 6.8587 | 41.82 | 53.895 | -2264.2436
2042-04-22 22:01 | -8062.57 | 6.8587 | 41.5361 | 53.895 | -2362.906
2042-04-23 23:01 | -8500.27 | 6.8587 | 41.1396 | 53.895 | -2491.1832
2042-04-25 00:01 | -9502.73 | 6.8587 | 40.3413 | 53.895 | -2784.9752
2042-04-26 01:01 | -9690.98 | 6.8587 | 40.0173 | 53.895 | -2840.1459
2042-04-27 02:01 | -10191.3 | 6.8587 | 39.534 | 53.895 | -2986.7752
2042-04-28 03:01 | -10009.3 | 6.8587 | 39.5041 | 53.895 | -2933.4363
2042-04-29 04:01 | -10058.6 | 6.8587 | 39.3808 | 53.895 | -2947.8847
2042-04-30 05:01 | -9470.62 | 6.8587 | 39.6911 | 53.895 | -2775.5647
2042-05-01 06:01 | -8888.06 | 6.8587 | 40.0931 | 53.895 | -2604.8333
2042-05-02 07:01 | -8747.59 | 6.8587 | 40.2386 | 53.895 | -2563.6656
2042-05-03 08:01 | -8499.54 | 6.8587 | 40.4346 | 53.895 | -2490.9693
2042-05-04 09:01 | -8792.5 | 6.8587 | 40.2648 | 53.895 | -2576.8274
2042-05-05 10:01 | -7288.36 | 6.8587 | 41.2787 | 53.895 | -2136.0075
2042-05-06 11:01 | -7640.04 | 6.8587 | 41.1948 | 53.895 | -2239.0747
2042-05-07 12:01 | -7742.57 | 6.8587 | 41.1643 | 53.895 | -2269.1233
2042-05-08 13:01 | -7800 | 6.8587 | 41.1182 | 53.895 | -2285.9543
2042-05-09 14:01 | -7755.05 | 6.8587 | 41.1497 | 53.895 | -2272.7808
2042-05-10 15:01 | -7941.64 | 6.8587 | 41.0389 | 53.895 | -2327.4649
2042-05-11 16:01 | -6360.06 | 6.8587 | 42.085 | 53.895 | -1863.9496
2042-05-12 17:01 | -6847.44 | 6.8587 | 41.9181 | 53.895 | -2006.7866
2042-05-13 18:01 | -7155.06 | 6.8587 | 41.7366 | 53.895 | -2096.9411
2042-05-14 19:01 | -7589.86 | 6.8587 | 41.4099 | 53.895 | -2224.3684
2042-05-15 20:01 | -8291.58 | 6.8587 | 40.877 | 53.895 | -2430.0222
2042-05-16 21:01 | -9223.95 | 6.8587 | 40.1422 | 53.895 | -2703.2729
2042-05-17 22:01 | -9447.11 | 6.8587 | 39.782 | 53.895 | -2768.6746
2042-05-18 23:01 | -10343.6 | 6.8587 | 39.0235 | 53.895 | -3031.4099
2042-05-20 00:01 | -10639.5 | 6.8587 | 38.6197 | 53.895 | -3118.1296
2042-05-21 01:01 | -10855 | 6.8587 | 38.301 | 53.895 | -3181.2865
2042-05-22 02:01 | -11037.5 | 6.8587 | 38.0393 | 53.895 | -3234.7719
2042-05-23 03:01 | -11112.9 | 6.8587 | 37.8697 | 53.895 | -3256.8695
2042-05-24 04:01 | -11005 | 6.8587 | 37.8215 | 53.895 | -3225.2471
2042-05-25 05:01 | -10838.7 | 6.8587 | 37.8575 | 53.895 | -3176.5094
2042-05-26 06:01 | -10878.3 | 6.8587 | 37.7746 | 53.895 | -3188.115
2042-05-27 07:01 | -9927.31 | 6.8587 | 38.362 | 53.895 | -2909.4074
2042-05-28 08:01 | -8420.73 | 6.8587 | 39.4566 | 53.895 | -2467.8724
2042-05-29 09:01 | -7922.13 | 6.8587 | 40.0112 | 53.895 | -2321.7471
2042-05-30 10:01 | -6347.07 | 6.8587 | 41.2475 | 53.895 | -1860.1426
2042-05-31 11:01 | -4866.27 | 6.8587 | 42.5468 | 53.895 | -1426.163
2042-06-01 12:01 | -4032.38 | 6.8587 | 43.4907 | 53.895 | -1181.7739
2042-06-02 13:01 | -3457.06 | 6.8587 | 44.2172 | 53.895 | -1013.1643
2042-06-03 14:01 | -3149.06 | 6.8587 | 44.7126 | 53.895 | -922.8984
2042-06-04 15:01 | -3243.72 | 6.8587 | 44.9028 | 53.895 | -950.6405
2042-06-05 16:01 | -3859.08 | 6.8587 | 44.6518 | 53.895 | -1130.9847
2042-06-06 17:01 | -3553.28 | 6.8587 | 44.9176 | 53.895 | -1041.3636
2042-06-07 18:01 | -4577.29 | 6.8587 | 44.3331 | 53.895 | -1341.4713
2042-06-08 19:01 | -5115.83 | 6.8587 | 43.9387 | 53.895 | -1499.3018
2042-06-09 20:01 | -5509.69 | 6.8587 | 43.6042 | 53.895 | -1614.7307
2042-06-10 21:01 | -5745.73 | 6.8587 | 43.3939 | 53.895 | -1683.9072
2042-06-11 22:01 | -6038.97 | 6.8587 | 43.1528 | 53.895 | -1769.8474
2042-06-12 23:01 | -6129.79 | 6.8587 | 43.0247 | 53.895 | -1796.4641
2042-06-14 00:01 | -7501.38 | 6.8587 | 42.0476 | 53.895 | -2198.4375
2042-06-15 01:01 | -7802.12 | 6.8587 | 41.6532 | 53.895 | -2286.5757
2042-06-16 02:01 | -7588.04 | 6.8587 | 41.6584 | 53.895 | -2223.835
2042-06-17 03:01 | -7321.14 | 6.8587 | 41.7924 | 53.895 | -2145.6143
2042-06-18 04:01 | -7427.34 | 6.8587 | 41.7144 | 53.895 | -2176.7385
2042-06-19 05:01 | -7084.65 | 6.8587 | 41.9063 | 53.895 | -2076.306
2042-06-20 06:01 | -7084.54 | 6.8587 | 41.941 | 53.895 | -2076.2737
2042-06-21 07:01 | -6039.68 | 6.8587 | 42.6833 | 53.895 | -1770.0555
2042-06-22 08:01 | -5153.53 | 6.8587 | 43.4261 | 53.895 | -1510.3506
2042-06-23 09:01 | -5714.97 | 6.8587 | 43.2264 | 53.895 | -1674.8924
2042-06-24 10:01 | -5529.52 | 6.8587 | 43.3799 | 53.895 | -1620.5423
2042-06-25 11:01 | -5201.12 | 6.8587 | 43.6404 | 53.895 | -1524.2978
2042-06-26 12:01 | -4579.93 | 6.8587 | 44.1608 | 53.895 | -1342.245
2042-06-27 13:01 | -4441.11 | 6.8587 | 44.3832 | 53.895 | -1301.5609
2042-06-28 14:01 | -4467.48 | 6.8587 | 44.4437 | 53.895 | -1309.2891
2042-06-29 15:01 | -4394.38 | 6.8587 | 44.5517 | 53.895 | -1287.8656
2042-06-30 16:01 | -4215.27 | 6.8587 | 44.7332 | 53.895 | -1235.3737
2042-07-01 17:01 | -2834.27 | 6.8587 | 45.7476 | 53.895 | -830.6425
2042-07-02 18:01 | -3255.46 | 6.8587 | 45.6837 | 53.895 | -954.0811
2042-07-03 19:01 | -3646 | 6.8587 | 45.5022 | 53.895 | -1068.5371
2042-07-04 20:01 | -3832.25 | 6.8587 | 45.3866 | 53.895 | -1123.1216
2042-07-05 21:01 | -3877.04 | 6.8587 | 45.388 | 53.895 | -1136.2483
2042-07-06 22:01 | -3940.23 | 6.8587 | 45.3908 | 53.895 | -1154.7674
2042-07-07 23:01 | -3899.27 | 6.8587 | 45.4375 | 53.895 | -1142.7632
2042-07-09 00:01 | -5078.05 | 6.8587 | 44.6709 | 53.895 | -1488.2295
2042-07-10 01:01 | -5219.47 | 6.8587 | 44.4763 | 53.895 | -1529.6757
2042-07-11 02:01 | -5249.44 | 6.8587 | 44.4051 | 53.895 | -1538.459
2042-07-12 03:01 | -5158.46 | 6.8587 | 44.4571 | 53.895 | -1511.7954
2042-07-13 04:01 | -5195.38 | 6.8587 | 44.4389 | 53.895 | -1522.6156
2042-07-14 05:01 | -5258.24 | 6.8587 | 44.3772 | 53.895 | -1541.038
2042-07-15 06:01 | -4917.94 | 6.8587 | 44.6117 | 53.895 | -1441.3059
2042-07-16 07:01 | -5400.79 | 6.8587 | 44.327 | 53.895 | -1582.8153
2042-07-17 08:01 | -4279.4 | 6.8587 | 45.0577 | 53.895 | -1254.1683
2042-07-18 09:01 | -3884.94 | 6.8587 | 45.4456 | 53.895 | -1138.5635
2042-07-19 10:01 | -2124.58 | 6.8587 | 46.7702 | 53.895 | -622.6529
2042-07-20 11:01 | -1199.73 | 4.0554 | 47.1084 | 53.895 | -351.6062
2042-07-21 12:01 | -316.867 | 1.3567 | 47.6848 | 53.895 | -92.8646
2042-07-22 13:01 | 2606.44 | 1 | 48.642 | 53.895 | 763.8722
2042-07-23 14:01 | 2837.61 | 1 | 49.1687 | 53.895 | 831.6214
2042-07-24 15:01 | 2787.49 | 1 | 49.5842 | 53.895 | 816.9327
2042-07-25 16:01 | -613.947 | 2.7262 | 49.2633 | 53.895 | -179.9301
2042-07-26 17:01 | -1222.76 | 4.4904 | 48.8489 | 53.895 | -358.3556
2042-07-27 18:01 | -1417.88 | 4.9603 | 48.6781 | 53.895 | -415.5396
2042-07-28 19:01 | -2128.44 | 6.8587 | 48.5204 | 53.895 | -623.7842
2042-07-29 20:01 | -2593.65 | 6.8587 | 48.0848 | 53.895 | -760.1238
2042-07-30 21:01 | -3629.36 | 6.8587 | 47.2423 | 53.895 | -1063.6604
2042-07-31 22:01 | -4077.79 | 6.8587 | 46.7724 | 53.895 | -1195.0823
2042-08-01 23:01 | -4917.93 | 6.8587 | 46.051 | 53.895 | -1441.303
2042-08-03 00:01 | -5448.02 | 6.8587 | 45.4992 | 53.895 | -1596.6571
2042-08-04 01:01 | -5654.55 | 6.8587 | 45.147 | 53.895 | -1657.185
2042-08-05 02:01 | -5874.66 | 6.8587 | 44.8216 | 53.895 | -1721.6929
2042-08-06 03:01 | -5662.49 | 6.8587 | 44.8127 | 53.895 | -1659.512
2042-08-07 04:01 | -5512.01 | 6.8587 | 44.8513 | 53.895 | -1615.4107
2042-08-08 05:01 | -5187.87 | 6.8587 | 45.0457 | 53.895 | -1520.4146
2042-08-09 06:01 | -4386.72 | 6.8587 | 45.6029 | 53.895 | -1285.6207
2042-08-10 07:01 | -4216.48 | 6.8587 | 45.8174 | 53.895 | -1235.7283
2042-08-11 08:01 | -3978.68 | 6.8587 | 46.0477 | 53.895 | -1166.036
2042-08-12 09:01 | -4461.64 | 6.8587 | 45.786 | 53.895 | -1307.5776
2042-08-13 10:01 | -3884.76 | 6.8587 | 46.1603 | 53.895 | -1138.5108
2042-08-14 11:01 | -3398.37 | 6.8587 | 46.557 | 53.895 | -995.9639
2042-08-15 12:01 | -2516.37 | 6.8587 | 47.2527 | 53.895 | -737.4752
2042-08-16 13:01 | -1900.26 | 6.4379 | 47.729 | 53.895 | -556.9112
2042-08-17 14:01 | -1496.17 | 5.0605 | 47.8766 | 53.895 | -438.4841
2042-08-18 15:01 | -1130.1 | 3.9657 | 48.0754 | 53.895 | -331.1996
2042-08-19 16:01 | -279.845 | 1.2311 | 48.501 | 53.895 | -82.0145
2042-08-20 17:01 | 0 | 1 | 49.7899 | 53.895 | 0
2042-08-21 18:01 | 2836.06 | 1 | 49.4796 | 53.895 | 831.1671
2042-08-22 19:01 | 1059.6 | 1 | 50.2607 | 53.895 | 310.5381
2042-08-23 20:01 | 52.87 | 1 | 50.5271 | 53.895 | 15.4947
2042-08-24 21:01 | -945.034 | 3.7781 | 49.3381 | 53.895 | -276.9621
2042-08-25 22:01 | -1895.06 | 6.6065 | 49.1083 | 53.895 | -555.3873
2042-08-26 23:01 | -3299.89 | 6.8587 | 48.0978 | 53.895 | -967.1023
2042-08-28 00:01 | -3951.89 | 6.8587 | 47.3957 | 53.895 | -1158.1846
2042-08-29 01:01 | -4555.3 | 6.8587 | 46.7806 | 53.895 | -1335.0266
2042-08-30 02:01 | -4826.59 | 6.8587 | 46.4136 | 53.895 | -1414.5339
2042-08-31 03:01 | -5176.33 | 6.8587 | 46.0267 | 53.895 | -1517.0326
2042-09-01 04:01 | -5399.5 | 6.8587 | 45.7259 | 53.895 | -1582.4372
2042-09-02 05:01 | -5317 | 6.8587 | 45.6577 | 53.895 | -1558.2589
2042-09-03 06:01 | -5057.46 | 6.8587 | 45.7227 | 53.895 | -1482.1952
2042-09-04 07:01 | -5230.53 | 6.8587 | 45.5562 | 53.895 | -1532.917
2042-09-05 08:01 | -5302.95 | 6.8587 | 45.4295 | 53.895 | -1554.1412
2042-09-06 09:01 | -5958.47 | 6.8587 | 44.9131 | 53.895 | -1746.2552
2042-09-07 10:01 | -6064.47 | 6.8587 | 44.7031 | 53.895 | -1777.3207
2042-09-08 11:01 | -5642.35 | 6.8587 | 44.8837 | 53.895 | -1653.6096
2042-09-09 12:01 | -5707.56 | 6.8587 | 44.8021 | 53.895 | -1672.7207
2042-09-10 13:01 | -5912.6 | 6.8587 | 44.595 | 53.895 | -1732.812
2042-09-11 14:01 | -5934.14 | 6.8587 | 44.4788 | 53.895 | -1739.1248
2042-09-12 15:01 | -6193.59 | 6.8587 | 44.2237 | 53.895 | -1815.162
2042-09-13 16:01 | -5605.1 | 6.8587 | 44.5366 | 53.895 | -1642.6927
2042-09-14 17:01 | -5464.11 | 6.8587 | 44.6217 | 53.895 | -1601.3726
2042-09-15 18:01 | -5466.33 | 6.8587 | 44.59 | 53.895 | -1602.0232
2042-09-16 19:01 | -6080.06 | 6.8587 | 44.132 | 53.895 | -1781.8897
2042-09-17 20:01 | -6237.27 | 6.8587 | 43.9144 | 53.895 | -1827.9634
2042-09-18 21:01 | -7209.22 | 6.8587 | 43.1727 | 53.895 | -2112.8138
2042-09-19 22:01 | -7437.08 | 6.8587 | 42.842 | 53.895 | -2179.593
2042-09-20 23:01 | -8404.7 | 6.8587 | 42.035 | 53.895 | -2463.1744
2042-09-22 00:01 | -8624.43 | 6.8587 | 41.6693 | 53.895 | -2527.5709
2042-09-23 01:01 | -8865.12 | 6.8587 | 41.34 | 53.895 | -2598.1102
2042-09-24 02:01 | -9076.15 | 6.8587 | 41.0483 | 53.895 | -2659.957
2042-09-25 03:01 | -9234.94 | 6.8587 | 40.8094 | 53.895 | -2706.4937
2042-09-26 04:01 | -9055.26 | 6.8587 | 40.8014 | 53.895 | -2653.8347
2042-09-27 05:01 | -8948.98 | 6.8587 | 40.7977 | 53.895 | -2622.6871
2042-09-28 06:01 | -8905.82 | 6.8587 | 40.7601 | 53.895 | -2610.0382
2042-09-29 07:01 | -8887.78 | 6.8587 | 40.7096 | 53.895 | -2604.7512
2042-09-30 08:01 | -8809.53 | 6.8587 | 40.7002 | 53.895 | -2581.8184
2042-10-01 09:01 | -7812.56 | 6.8587 | 41.3477 | 53.895 | -2289.6353
2042-10-02 10:01 | -7043.58 | 6.8587 | 41.9553 | 53.895 | -2064.2695
2042-10-03 11:01 | -5985.17 | 6.8587 | 42.8045 | 53.895 | -1754.0802
2042-10-04 12:01 | -4563.69 | 6.8587 | 43.961 | 53.895 | -1337.4855
2042-10-05 13:01 | -4184.68 | 6.8587 | 44.5016 | 53.895 | -1226.4086
2042-10-06 14:01 | -3725.79 | 6.8587 | 45.0354 | 53.895 | -1091.9213
2042-10-07 15:01 | -4024.78 | 6.8587 | 45.0242 | 53.895 | -1179.5466
2042-10-08 16:01 | -4315.2 | 6.8587 | 44.9216 | 53.895 | -1264.6603
2042-10-09 17:01 | -5368.98 | 6.8587 | 44.236 | 53.895 | -1573.4927
2042-10-10 18:01 | -5954.83 | 6.8587 | 43.7268 | 53.895 | -1745.1884
2042-10-11 19:01 | -6736.29 | 6.8587 | 43.0757 | 53.895 | -1974.2117
2042-10-12 20:01 | -7294.73 | 6.8587 | 42.5379 | 53.895 | -2137.8743
2042-10-13 21:01 | -8588.75 | 6.8587 | 41.4893 | 53.895 | -2517.1142
2042-10-14 22:01 | -8601.98 | 6.8587 | 41.212 | 53.895 | -2520.9915
2042-10-15 23:01 | -9543.57 | 6.8587 | 40.4032 | 53.895 | -2796.9443
2042-10-17 00:01 | -9572.79 | 6.8587 | 40.1451 | 53.895 | -2805.5078
2042-10-18 01:01 | -9742.47 | 6.8587 | 39.8537 | 53.895 | -2855.2361
2042-10-19 02:01 | -9804.85 | 6.8587 | 39.6544 | 53.895 | -2873.5179
2042-10-20 03:01 | -9606.07 | 6.8587 | 39.6685 | 53.895 | -2815.2612
2042-10-21 04:01 | -9500.39 | 6.8587 | 39.6554 | 53.895 | -2784.2895
2042-10-22 05:01 | -9409.65 | 6.8587 | 39.6664 | 53.895 | -2757.6962
2042-10-23 06:01 | -9318.12 | 6.8587 | 39.6825 | 53.895 | -2730.8714
2042-10-24 07:01 | -9320.35 | 6.8587 | 39.6497 | 53.895 | -2731.5249
2042-10-25 08:01 | -8107.57 | 6.8587 | 40.4487 | 53.895 | -2376.0942
2042-10-26 09:01 | -6741.58 | 6.8587 | 41.5086 | 53.895 | -1975.7621
2042-10-27 10:01 | -4806.76 | 6.8587 | 43.0569 | 53.895 | -1408.7223
2042-10-28 11:01 | -3347.98 | 6.8587 | 44.4088 | 53.895 | -981.1961
2042-10-29 12:01 | -2270.25 | 6.8587 | 45.5262 | 53.895 | -665.3446
2042-10-30 13:01 | -1699.05 | 5.878 | 46.0952 | 53.895 | -497.9424
2042-10-31 14:01 | -1394.42 | 4.8838 | 46.4261 | 53.895 | -408.6642
2042-11-01 15:01 | -1399.4 | 4.9969 | 46.7136 | 53.895 | -410.1237
2042-11-02 16:01 | -1514.81 | 5.3692 | 46.8944 | 53.895 | -443.947
2042-11-03 17:01 | -3252.44 | 6.8587 | 46.1352 | 53.895 | -953.1961
2042-11-04 18:01 | -3710.86 | 6.8587 | 45.7316 | 53.895 | -1087.5457
2042-11-05 19:01 | -4899.94 | 6.8587 | 44.8596 | 53.895 | -1436.0307
2042-11-06 20:01 | -5300.23 | 6.8587 | 44.4429 | 53.895 | -1553.3441
2042-11-07 21:01 | -6293.57 | 6.8587 | 43.6435 | 53.895 | -1844.4633
2042-11-08 22:01 | -6594.26 | 6.8587 | 43.2362 | 53.895 | -1932.5868
2042-11-09 23:01 | -7344.06 | 6.8587 | 42.5783 | 53.895 | -2152.3315
2042-11-11 00:01 | -7929.66 | 6.8587 | 41.9859 | 53.895 | -2323.9539
2042-11-12 01:01 | -7918.82 | 6.8587 | 41.7987 | 53.895 | -2320.7771
2042-11-13 02:01 | -7851.66 | 6.8587 | 41.713 | 53.895 | -2301.0944
2042-11-14 03:01 | -7682.81 | 6.8587 | 41.7432 | 53.895 | -2251.6093
2042-11-15 04:01 | -7708.43 | 6.8587 | 41.6634 | 53.895 | -2259.1178
2042-11-16 05:01 | -8131.43 | 6.8587 | 41.3286 | 53.895 | -2383.0869
2042-11-17 06:01 | -8077.2 | 6.8587 | 41.2784 | 53.895 | -2367.1936
2042-11-18 07:01 | -7544.2 | 6.8587 | 41.599 | 53.895 | -2210.9868
2042-11-19 08:01 | -7203.24 | 6.8587 | 41.861 | 53.895 | -2111.0613
2042-11-20 09:01 | -7726.89 | 6.8587 | 41.5402 | 53.895 | -2264.5279
2042-11-21 10:01 | -7680.07 | 6.8587 | 41.4992 | 53.895 | -2250.8063
2042-11-22 11:01 | -7324.7 | 6.8587 | 41.6984 | 53.895 | -2146.6577
2042-11-23 12:01 | -7227.94 | 6.8587 | 41.7733 | 53.895 | -2118.3001
2042-11-24 13:01 | -7036.96 | 6.8587 | 41.8886 | 53.895 | -2062.3294
2042-11-25 14:01 | -7027.11 | 6.8587 | 41.8762 | 53.895 | -2059.4426
2042-11-26 15:01 | -6345.23 | 6.8587 | 42.3225 | 53.895 | -1859.6033
2042-11-27 16:01 | -5960.37 | 6.8587 | 42.6426 | 53.895 | -1746.812
2042-11-28 17:01 | -5142.42 | 6.8587 | 43.2807 | 53.895 | -1507.0945
2042-11-29 18:01 | -5332.47 | 6.8587 | 43.287 | 53.895 | -1562.7927
2042-11-30 19:01 | -5745.3 | 6.8587 | 43.0633 | 53.895 | -1683.7812
2042-12-01 20:01 | -5883.92 | 6.8587 | 42.9619 | 53.895 | -1724.4067
2042-12-02 21:01 | -5958.19 | 6.8587 | 42.9176 | 53.895 | -1746.1731
2042-12-03 22:01 | -6055.58 | 6.8587 | 42.8633 | 53.895 | -1774.7153
2042-12-04 23:01 | -6282.19 | 6.8587 | 42.7052 | 53.895 | -1841.1281
2042-12-06 00:01 | -7710.99 | 6.8587 | 41.7087 | 53.895 | -2259.8681
2042-12-07 01:01 | -8084.67 | 6.8587 | 41.2781 | 53.895 | -2369.3829
2042-12-08 02:01 | -8128.38 | 6.8587 | 41.1134 | 53.895 | -2382.193
2042-12-09 03:01 | -8429.21 | 6.8587 | 40.8252 | 53.895 | -2470.3576
2042-12-10 04:01 | -8601.78 | 6.8587 | 40.599 | 53.895 | -2520.9329
2042-12-11 05:01 | -8753.53 | 6.8587 | 40.3806 | 53.895 | -2565.4064
2042-12-12 06:01 | -8957.14 | 6.8587 | 40.1568 | 53.895 | -2625.0786
2042-12-13 07:01 | -8304.06 | 6.8587 | 40.518 | 53.895 | -2433.6797
2042-12-14 08:01 | -7907.28 | 6.8587 | 40.7978 | 53.895 | -2317.395
2042-12-15 09:01 | -7312.28 | 6.8587 | 41.242 | 53.895 | -2143.0177
2042-12-16 10:01 | -5825.14 | 6.8587 | 42.3293 | 53.895 | -1707.18
2042-12-17 11:01 | -6476.33 | 6.8587 | 42.0901 | 53.895 | -1898.025
2042-12-18 12:01 | -6271.64 | 6.8587 | 42.2737 | 53.895 | -1838.0362
2042-12-19 13:01 | -5192.24 | 6.8587 | 43.0585 | 53.895 | -1521.6953
2042-12-20 14:01 | -5235.23 | 6.8587 | 43.2099 | 53.895 | -1534.2945
2042-12-21 15:01 | -4602.74 | 6.8587 | 43.743 | 53.895 | -1348.9299
2042-12-22 16:01 | -4707.06 | 6.8587 | 43.7873 | 53.895 | -1379.5031
2042-12-23 17:01 | -4023.2 | 6.8587 | 44.342 | 53.895 | -1179.0835
2042-12-24 18:01 | -4858.41 | 6.8587 | 43.9282 | 53.895 | -1423.8594
2042-12-25 19:01 | -5361.13 | 6.8587 | 43.5822 | 53.895 | -1571.1921
2042-12-26 20:01 | -5728.78 | 6.8587 | 43.2874 | 53.895 | -1678.9397
2042-12-27 21:01 | -5980.11 | 6.8587 | 43.0645 | 53.895 | -1752.5972
2042-12-28 22:01 | -6167.54 | 6.8587 | 42.878 | 53.895 | -1807.5275
2042-12-29 23:01 | -6177.55 | 6.8587 | 42.8121 | 53.895 | -1810.4612
2042-12-31 00:01 | -7293.66 | 6.8587 | 42.03 | 53.895 | -2137.5607
2043-01-01 01:01 | -7655.4 | 6.8587 | 41.6325 | 53.895 | -2243.5763
2043-01-02 02:01 | -7259.15 | 6.8587 | 41.7778 | 53.895 | -2127.4469
2043-01-03 03:01 | -7035.11 | 6.8587 | 41.9094 | 53.895 | -2061.7872
2043-01-04 04:01 | -6797.46 | 6.8587 | 42.0747 | 53.895 | -1992.1389
2043-01-05 05:01 | -7013.96 | 6.8587 | 41.9287 | 53.895 | -2055.5888
2043-01-06 06:01 | -6970.87 | 6.8587 | 41.9463 | 53.895 | -2042.9603
2043-01-07 07:01 | -7002.94 | 6.8587 | 41.9286 | 53.895 | -2052.3591
2043-01-08 08:01 | -6947.79 | 6.8587 | 41.9626 | 53.895 | -2036.1962
2043-01-09 09:01 | -7404.38 | 6.8587 | 41.6474 | 53.895 | -2170.0096
2043-01-10 10:01 | -7313.81 | 6.8587 | 41.6354 | 53.895 | -2143.4661
2043-01-11 11:01 | -6825.09 | 6.8587 | 41.9361 | 53.895 | -2000.2364
2043-01-12 12:01 | -6379.89 | 6.8587 | 42.2844 | 53.895 | -1869.7612
2043-01-13 13:01 | -6626.97 | 6.8587 | 42.183 | 53.895 | -1942.1732
2043-01-14 14:01 | -6627.62 | 6.8587 | 42.1744 | 53.895 | -1942.3637
2043-01-15 15:01 | -6388.51 | 6.8587 | 42.3319 | 53.895 | -1872.2875
2043-01-16 16:01 | -5663.38 | 6.8587 | 42.8561 | 53.895 | -1659.7728
2043-01-17 17:01 | -5409.86 | 6.8587 | 43.1219 | 53.895 | -1585.4735
2043-01-18 18:01 | -5468.56 | 6.8587 | 43.1563 | 53.895 | -1602.6767
2043-01-19 19:01 | -5903.2 | 6.8587 | 42.9001 | 53.895 | -1730.0571
2043-01-20 20:01 | -6347.6 | 6.8587 | 42.5805 | 53.895 | -1860.2979
2043-01-21 21:01 | -7075.59 | 6.8587 | 42.0383 | 53.895 | -2073.6507
2043-01-22 22:01 | -7657.15 | 6.8587 | 41.5273 | 53.895 | -2244.0891
2043-01-23 23:01 | -8778.13 | 6.8587 | 40.6169 | 53.895 | -2572.616
2043-01-25 00:01 | -9386.49 | 6.8587 | 39.9773 | 53.895 | -2750.9087
2043-01-26 01:01 | -9739.65 | 6.8587 | 39.5292 | 53.895 | -2854.4096
2043-01-27 02:01 | -9773.64 | 6.8587 | 39.3311 | 53.895 | -2864.3711
2043-01-28 03:01 | -9870.89 | 6.8587 | 39.1356 | 53.895 | -2892.8723
2043-01-29 04:01 | -9672.07 | 6.8587 | 39.1478 | 53.895 | -2834.6039
2043-01-30 05:01 | -9540.95 | 6.8587 | 39.1673 | 53.895 | -2796.1764
2043-01-31 06:01 | -9162.67 | 6.8587 | 39.3788 | 53.895 | -2685.3135
2043-02-01 07:01 | -9235.01 | 6.8587 | 39.3256 | 53.895 | -2706.5143
2043-02-02 08:01 | -8928.38 | 6.8587 | 39.5008 | 53.895 | -2616.6499
2043-02-03 09:01 | -9076.85 | 6.8587 | 39.4023 | 53.895 | -2660.1621
2043-02-04 10:01 | -7100.49 | 6.8587 | 40.7245 | 53.895 | -2080.9482
2043-02-05 11:01 | -5635.17 | 6.8587 | 41.9476 | 53.895 | -1651.5053
2043-02-06 12:01 | -4918.37 | 6.8587 | 42.7332 | 53.895 | -1441.432
2043-02-07 13:01 | -5014.37 | 6.8587 | 42.9125 | 53.895 | -1469.5668
2043-02-08 14:01 | -5209.31 | 6.8587 | 42.9214 | 53.895 | -1526.6981
2043-02-09 15:01 | -5491.62 | 6.8587 | 42.8295 | 53.895 | -1609.4349
2043-02-10 16:01 | -5356.61 | 6.8587 | 42.9575 | 53.895 | -1569.8674
2043-02-11 17:01 | -5357.14 | 6.8587 | 42.9982 | 53.895 | -1570.0228
2043-02-12 18:01 | -5267.45 | 6.8587 | 43.0873 | 53.895 | -1543.7372
2043-02-13 19:01 | -5861.94 | 6.8587 | 42.7231 | 53.895 | -1717.965
2043-02-14 20:01 | -6074.18 | 6.8587 | 42.547 | 53.895 | -1780.1664
2043-02-15 21:01 | -6862.88 | 6.8587 | 41.9916 | 53.895 | -2011.3116
2043-02-16 22:01 | -7230.25 | 6.8587 | 41.6366 | 53.895 | -2118.9771
2043-02-17 23:01 | -7948.17 | 6.8587 | 41.0355 | 53.895 | -2329.3787
2043-02-19 00:01 | -8105.46 | 6.8587 | 40.7709 | 53.895 | -2375.4758
2043-02-20 01:01 | -8223.29 | 6.8587 | 40.58 | 53.895 | -2410.0084
2043-02-21 02:01 | -8367.1 | 6.8587 | 40.3931 | 53.895 | -2452.1549
2043-02-22 03:01 | -8352.04 | 6.8587 | 40.3273 | 53.895 | -2447.7413
2043-02-23 04:01 | -8293.63 | 6.8587 | 40.3091 | 53.895 | -2430.623
2043-02-24 05:01 | -8053.01 | 6.8587 | 40.4423 | 53.895 | -2360.1043
2043-02-25 06:01 | -7965.99 | 6.8587 | 40.4962 | 53.895 | -2334.6012
2043-02-26 07:01 | -7889.87 | 6.8587 | 40.547 | 53.895 | -2312.2926
2043-02-27 08:01 | -7921.54 | 6.8587 | 40.5237 | 53.895 | -2321.5742
2043-02-28 09:01 | -8529.38 | 6.8587 | 40.1044 | 53.895 | -2499.7145
2043-03-01 10:01 | -8363.9 | 6.8587 | 40.1295 | 53.895 | -2451.2171
2043-03-02 11:01 | -8048.36 | 6.8587 | 40.3037 | 53.895 | -2358.7415
2043-03-03 12:01 | -7698.01 | 6.8587 | 40.5462 | 53.895 | -2256.064
2043-03-04 13:01 | -7777.31 | 6.8587 | 40.5149 | 53.895 | -2279.3046
2043-03-05 14:01 | -7428.7 | 6.8587 | 40.7415 | 53.895 | -2177.1371
2043-03-06 15:01 | -7094.27 | 6.8587 | 41.0077 | 53.895 | -2079.1253
2043-03-07 16:01 | -6715.88 | 6.8587 | 41.3223 | 53.895 | -1968.2301
2043-03-08 17:01 | -6424.07 | 6.8587 | 41.5857 | 53.895 | -1882.7091
2043-03-09 18:01 | -6303.86 | 6.8587 | 41.728 | 53.895 | -1847.479
2043-03-10 19:01 | -6405.32 | 6.8587 | 41.7131 | 53.895 | -1877.214
2043-03-11 20:01 | -6814.45 | 6.8587 | 41.4554 | 53.895 | -1997.1182
2043-03-12 21:01 | -7912.23 | 6.8587 | 40.6813 | 53.895 | -2318.8457
2043-03-13 22:01 | -8164.85 | 6.8587 | 40.3682 | 53.895 | -2392.8813
2043-03-14 23:01 | -8943.93 | 6.8587 | 39.7319 | 53.895 | -2621.2071
2043-03-16 00:01 | -9276.13 | 6.8587 | 39.3503 | 53.895 | -2718.5653
2043-03-17 01:01 | -9328.47 | 6.8587 | 39.1744 | 53.895 | -2733.9047
2043-03-18 02:01 | -9430.89 | 6.8587 | 39.0059 | 53.895 | -2763.921
2043-03-19 03:01 | -9419.19 | 6.8587 | 38.9363 | 53.895 | -2760.4921
2043-03-20 04:01 | -9260.9 | 6.8587 | 38.9769 | 53.895 | -2714.1019
2043-03-21 05:01 | -9584.26 | 6.8587 | 38.7208 | 53.895 | -2808.8693
2043-03-22 06:01 | -9449.4 | 6.8587 | 38.7337 | 53.895 | -2769.3458
2043-03-23 07:01 | -10201.6 | 6.8587 | 38.1673 | 53.895 | -2989.7938
2043-03-24 08:01 | -11045.8 | 6.8587 | 37.4489 | 53.895 | -3237.2044
2043-03-25 09:01 | -11904.2 | 6.8587 | 36.6631 | 53.895 | -3488.7766
2043-03-26 10:01 | -12330.2 | 6.8587 | 36.125 | 53.895 | -3613.6249
2043-03-27 11:01 | -12510.6 | 6.8587 | 35.7845 | 53.895 | -3666.4949
2043-03-28 12:01 | -12497.8 | 6.8587 | 35.6008 | 53.895 | -3662.7436
2043-03-29 13:01 | -12084.5 | 6.8587 | 35.7339 | 53.895 | -3541.6173
2043-03-30 14:01 | -11984.2 | 6.8587 | 35.7264 | 53.895 | -3512.2223
2043-03-31 15:01 | -12335.9 | 6.8587 | 35.4121 | 53.895 | -3615.2954
2043-04-01 16:01 | -12418.3 | 6.8587 | 35.2249 | 53.895 | -3639.4445
2043-04-02 17:01 | -12565.3 | 6.8587 | 35.0039 | 53.895 | -3682.5259
2043-04-03 18:01 | -12838 | 6.8587 | 34.6918 | 53.895 | -3762.4464
2043-04-04 19:01 | -13015.6 | 6.8587 | 34.4236 | 53.895 | -3814.4958
2043-04-05 20:01 | -13221.9 | 6.8587 | 34.1432 | 53.895 | -3874.9564
2043-04-06 21:01 | -13578 | 6.8587 | 33.7767 | 53.895 | -3979.319
2043-04-07 22:01 | -13946 | 6.8587 | 33.3785 | 53.895 | -4087.1691
2043-04-08 23:01 | -14213.4 | 6.8587 | 33.0433 | 53.895 | -4165.5363
2043-04-10 00:01 | -14344.9 | 6.8587 | 32.809 | 53.895 | -4204.0752
2043-04-11 01:01 | -14338.4 | 6.8587 | 32.6809 | 53.895 | -4202.1702
2043-04-12 02:01 | -14448.1 | 6.8587 | 32.4933 | 53.895 | -4234.3201
2043-04-13 03:01 | -14430.7 | 6.8587 | 32.3938 | 53.895 | -4229.2207
2043-04-14 04:01 | -14322.6 | 6.8587 | 32.3729 | 53.895 | -4197.5397
2043-04-15 05:01 | -14258.3 | 6.8587 | 32.3466 | 53.895 | -4178.6952
2043-04-16 06:01 | -14120.9 | 6.8587 | 32.3769 | 53.895 | -4138.4273
2043-04-17 07:01 | -14101.8 | 6.8587 | 32.3417 | 53.895 | -4132.8296
2043-04-18 08:01 | -14074 | 6.8587 | 32.3134 | 53.895 | -4124.6822
2043-04-19 09:01 | -13599 | 6.8587 | 32.6022 | 53.895 | -3985.4735
2043-04-20 10:01 | -12918.4 | 6.8587 | 33.0956 | 53.895 | -3786.0093
2043-04-21 11:01 | -12065.3 | 6.8587 | 33.7678 | 53.895 | -3535.9904
2043-04-22 12:01 | -10335 | 6.8587 | 35.1 | 53.895 | -3028.8895
2043-04-23 13:01 | -9574.54 | 6.8587 | 35.909 | 53.895 | -2806.0207
2043-04-24 14:01 | -9131.06 | 6.8587 | 36.4724 | 53.895 | -2676.0495
2043-04-25 15:01 | -9222.94 | 6.8587 | 36.6183 | 53.895 | -2702.9769
2043-04-26 16:01 | -9124.73 | 6.8587 | 36.8183 | 53.895 | -2674.1944
2043-04-27 17:01 | -9893.28 | 6.8587 | 36.4075 | 53.895 | -2899.4342
2043-04-28 18:01 | -10063.9 | 6.8587 | 36.272 | 53.895 | -2949.4379
2043-04-29 19:01 | -10731 | 6.8587 | 35.7982 | 53.895 | -3144.9457
2043-04-30 20:01 | -11000.4 | 6.8587 | 35.54 | 53.895 | -3223.899
2043-05-01 21:01 | -11884.7 | 6.8587 | 34.8697 | 53.895 | -3483.0617
2043-05-02 22:01 | -11960.2 | 6.8587 | 34.6732 | 53.895 | -3505.1886
2043-05-03 23:01 | -12291.2 | 6.8587 | 34.3614 | 53.895 | -3602.1951
2043-05-05 00:01 | -12632.9 | 6.8587 | 34.0197 | 53.895 | -3702.3375
2043-05-06 01:01 | -12684.4 | 6.8587 | 33.8618 | 53.895 | -3717.4307
2043-05-07 02:01 | -12638.8 | 6.8587 | 33.7931 | 53.895 | -3704.0666
2043-05-08 03:01 | -12521.5 | 6.8587 | 33.8157 | 53.895 | -3669.6894
2043-05-09 04:01 | -12445 | 6.8587 | 33.8237 | 53.895 | -3647.2695
2043-05-10 05:01 | -12368.4 | 6.8587 | 33.8488 | 53.895 | -3624.8202
2043-05-11 06:01 | -12212.9 | 6.8587 | 33.9401 | 53.895 | -3579.2477
2043-05-12 07:01 | -11532.3 | 6.8587 | 34.4141 | 53.895 | -3379.7835
2043-05-13 08:01 | -10926.8 | 6.8587 | 34.9152 | 53.895 | -3202.329
2043-05-14 09:01 | -11345 | 6.8587 | 34.7512 | 53.895 | -3324.8913
2043-05-15 10:01 | -10951.2 | 6.8587 | 35.031 | 53.895 | -3209.4799
2043-05-16 11:01 | -10970.6 | 6.8587 | 35.0751 | 53.895 | -3215.1655
2043-05-17 12:01 | -10812.3 | 6.8587 | 35.2198 | 53.895 | -3168.7723
2043-05-18 13:01 | -10065.3 | 6.8587 | 35.7598 | 53.895 | -2949.8482
2043-05-19 14:01 | -9556.96 | 6.8587 | 36.2065 | 53.895 | -2800.8685
2043-05-20 15:01 | -8846.37 | 6.8587 | 36.8204 | 53.895 | -2592.6151
2043-05-21 16:01 | -8425.71 | 6.8587 | 37.2643 | 53.895 | -2469.3318
2043-05-22 17:01 | -6865.71 | 6.8587 | 38.4961 | 53.895 | -2012.141
2043-05-23 18:01 | -7117.16 | 6.8587 | 38.6316 | 53.895 | -2085.8337
2043-05-24 19:01 | -7373.38 | 6.8587 | 38.6183 | 53.895 | -2160.9244
2043-05-25 20:01 | -7371.67 | 6.8587 | 38.7004 | 53.895 | -2160.4232
2043-05-26 21:01 | -7443.81 | 6.8587 | 38.7507 | 53.895 | -2181.5654
2043-05-27 22:01 | -7692.55 | 6.8587 | 38.6679 | 53.895 | -2254.4639
2043-05-28 23:01 | -8633.96 | 6.8587 | 38.0533 | 53.895 | -2530.3639
2043-05-30 00:01 | -10549.8 | 6.8587 | 36.6705 | 53.895 | -3091.8412
2043-05-31 01:01 | -11113.6 | 6.8587 | 36.0292 | 53.895 | -3257.0746
2043-06-01 02:01 | -11804.2 | 6.8587 | 35.3576 | 53.895 | -3459.4695
2043-06-02 03:01 | -11860.3 | 6.8587 | 35.1189 | 53.895 | -3475.9108
2043-06-03 04:01 | -12251.9 | 6.8587 | 34.6978 | 53.895 | -3590.6774
2043-06-04 05:01 | -12821.1 | 6.8587 | 34.1309 | 53.895 | -3757.4935
2043-06-05 06:01 | -13261.1 | 6.8587 | 33.6436 | 53.895 | -3886.4448
2043-06-06 07:01 | -13325.3 | 6.8587 | 33.4095 | 53.895 | -3905.2599
2043-06-07 08:01 | -13058.8 | 6.8587 | 33.4528 | 53.895 | -3827.1565
2043-06-08 09:01 | -12910.8 | 6.8587 | 33.4708 | 53.895 | -3783.782
2043-06-09 10:01 | -12698.8 | 6.8587 | 33.5452 | 53.895 | -3721.6509
2043-06-10 11:01 | -12385.3 | 6.8587 | 33.7193 | 53.895 | -3629.7731
2043-06-11 12:01 | -11899.8 | 6.8587 | 34.0597 | 53.895 | -3487.4871
2043-06-12 13:01 | -12062.5 | 6.8587 | 33.9945 | 53.895 | -3535.1698
2043-06-13 14:01 | -11985.9 | 6.8587 | 34.031 | 53.895 | -3512.7205
2043-06-14 15:01 | -12026.1 | 6.8587 | 33.9837 | 53.895 | -3524.502
2043-06-15 16:01 | -12249 | 6.8587 | 33.8017 | 53.895 | -3589.8275
2043-06-16 17:01 | -12103.3 | 6.8587 | 33.835 | 53.895 | -3547.1271
2043-06-17 18:01 | -12263.8 | 6.8587 | 33.6913 | 53.895 | -3594.165
2043-06-18 19:01 | -12724.8 | 6.8587 | 33.3205 | 53.895 | -3729.2708
2043-06-19 20:01 | -13035.3 | 6.8587 | 32.9978 | 53.895 | -3820.2693
2043-06-20 21:01 | -13157.3 | 6.8587 | 32.8001 | 53.895 | -3856.024
2043-06-21 22:01 | -13212.2 | 6.8587 | 32.6697 | 53.895 | -3872.1136
2043-06-22 23:01 | -13246.9 | 6.8587 | 32.5644 | 53.895 | -3882.2832
2043-06-24 00:01 | -13761.2 | 6.8587 | 32.1404 | 53.895 | -4033.0096
2043-06-25 01:01 | -14094 | 6.8587 | 31.7928 | 53.895 | -4130.5437
2043-06-26 02:01 | -14020.1 | 6.8587 | 31.7232 | 53.895 | -4108.8857
2043-06-27 03:01 | -14042.9 | 6.8587 | 31.6354 | 53.895 | -4115.5677
2043-06-28 04:01 | -14013.5 | 6.8587 | 31.5921 | 53.895 | -4106.9514
2043-06-29 05:01 | -13975.2 | 6.8587 | 31.5603 | 53.895 | -4095.7268
2043-06-30 06:01 | -13825.5 | 6.8587 | 31.6238 | 53.895 | -4051.8541
2043-07-01 07:01 | -13977.7 | 6.8587 | 31.5053 | 53.895 | -4096.4595
2043-07-02 08:01 | -14033 | 6.8587 | 31.4229 | 53.895 | -4112.6663
2043-07-03 09:01 | -14012 | 6.8587 | 31.3926 | 53.895 | -4106.5118
2043-07-04 10:01 | -13840.3 | 6.8587 | 31.4742 | 53.895 | -4056.1915
2043-07-05 11:01 | -12604.5 | 6.8587 | 32.3135 | 53.895 | -3694.0143
2043-07-06 12:01 | -11251.3 | 6.8587 | 33.3829 | 53.895 | -3297.4305
2043-07-07 13:01 | -10716.7 | 6.8587 | 33.9913 | 53.895 | -3140.7547
2043-07-08 14:01 | -10331.8 | 6.8587 | 34.4448 | 53.895 | -3027.9517
2043-07-09 15:01 | -10166.7 | 6.8587 | 34.7219 | 53.895 | -2979.5656
2043-07-10 16:01 | -10217.2 | 6.8587 | 34.8298 | 53.895 | -2994.3657
2043-07-11 17:01 | -11355.8 | 6.8587 | 34.1285 | 53.895 | -3328.0565
2043-07-12 18:01 | -11756.3 | 6.8587 | 33.7602 | 53.895 | -3445.4314
2043-07-13 19:01 | -12072.7 | 6.8587 | 33.4547 | 53.895 | -3538.1591
2043-07-14 20:01 | -12341 | 6.8587 | 33.1969 | 53.895 | -3616.7901
2043-07-15 21:01 | -12893.8 | 6.8587 | 32.7362 | 53.895 | -3778.7998
2043-07-16 22:01 | -13264.2 | 6.8587 | 32.3556 | 53.895 | -3887.3533
2043-07-17 23:01 | -13598.3 | 6.8587 | 32.0057 | 53.895 | -3985.2683
2043-07-19 00:01 | -14078.7 | 6.8587 | 31.5528 | 53.895 | -4126.0597
2043-07-20 01:01 | -14319.6 | 6.8587 | 31.2379 | 53.895 | -4196.6605
2043-07-21 02:01 | -14510.5 | 6.8587 | 30.9673 | 53.895 | -4252.6078
2043-07-22 03:01 | -14577.9 | 6.8587 | 30.7961 | 53.895 | -4272.3608
2043-07-23 04:01 | -14617.7 | 6.8587 | 30.663 | 53.895 | -4284.025
2043-07-24 05:01 | -14697.3 | 6.8587 | 30.5271 | 53.895 | -4307.3534
2043-07-25 06:01 | -14694.9 | 6.8587 | 30.4563 | 53.895 | -4306.6501
2043-07-26 07:01 | -14597.9 | 6.8587 | 30.4663 | 53.895 | -4278.2222
2043-07-27 08:01 | -13955.8 | 6.8587 | 30.8754 | 53.895 | -4090.0412
2043-07-28 09:01 | -13016.9 | 6.8587 | 31.5753 | 53.895 | -3814.8768
2043-07-29 10:01 | -11227.2 | 6.8587 | 32.9476 | 53.895 | -3290.3675
2043-07-30 11:01 | -10086.2 | 6.8587 | 34.0235 | 53.895 | -2955.9734
2043-07-31 12:01 | -9347.68 | 6.8587 | 34.8315 | 53.895 | -2739.5346
2043-08-01 13:01 | -9150.66 | 6.8587 | 35.2357 | 53.895 | -2681.7937
2043-08-02 14:01 | -8463 | 6.8587 | 35.9125 | 53.895 | -2480.2605
2043-08-03 15:01 | -8643.16 | 6.8587 | 36.0252 | 53.895 | -2533.0601
2043-08-04 16:01 | -8373.75 | 6.8587 | 36.3441 | 53.895 | -2454.1039
2043-08-05 17:01 | -9631.51 | 6.8587 | 35.6173 | 53.895 | -2822.7169
2043-08-06 18:01 | -10106.2 | 6.8587 | 35.2474 | 53.895 | -2961.8348
2043-08-07 19:01 | -10726.9 | 6.8587 | 34.7757 | 53.895 | -3143.7441
2043-08-08 20:01 | -11029.8 | 6.8587 | 34.491 | 53.895 | -3232.5153
2043-08-09 21:01 | -11992.7 | 6.8587 | 33.7602 | 53.895 | -3514.7134
2043-08-10 22:01 | -12128.8 | 6.8587 | 33.4872 | 53.895 | -3554.6004
2043-08-11 23:01 | -12270.7 | 6.8587 | 33.2761 | 53.895 | -3596.1872
2043-08-13 00:01 | -12260.3 | 6.8587 | 33.1974 | 53.895 | -3593.1392
2043-08-14 01:01 | -12049.1 | 6.8587 | 33.2846 | 53.895 | -3531.2426
2043-08-15 02:01 | -11565.5 | 6.8587 | 33.5915 | 53.895 | -3389.5135
2043-08-16 03:01 | -11203.7 | 6.8587 | 33.8896 | 53.895 | -3283.4803
2043-08-17 04:01 | -10697.1 | 6.8587 | 34.2973 | 53.895 | -3135.0105
2043-08-18 05:01 | -10221.8 | 6.8587 | 34.7291 | 53.895 | -2995.7139
2043-08-19 06:01 | -9468.04 | 6.8587 | 35.378 | 53.895 | -2774.8086
2043-08-20 07:01 | -9188.1 | 6.8587 | 35.7554 | 53.895 | -2692.7663
2043-08-21 08:01 | -8851.22 | 6.8587 | 36.1398 | 53.895 | -2594.0365
2043-08-22 09:01 | -8933.84 | 6.8587 | 36.2372 | 53.895 | -2618.25
2043-08-23 10:01 | -8583.22 | 6.8587 | 36.5737 | 53.895 | -2515.4935
2043-08-24 11:01 | -7895.78 | 6.8587 | 37.1611 | 53.895 | -2314.0247
2043-08-25 12:01 | -7452.18 | 6.8587 | 37.6272 | 53.895 | -2184.0184
2043-08-26 13:01 | -6841.47 | 6.8587 | 38.2039 | 53.895 | -2005.0369
2043-08-27 14:01 | -6716.81 | 6.8587 | 38.4608 | 53.895 | -1968.5027
2043-08-28 15:01 | -6576.04 | 6.8587 | 38.6953 | 53.895 | -1927.2471
2043-08-29 16:01 | -5788.24 | 6.8587 | 39.3531 | 53.895 | -1696.3657
2043-08-30 17:01 | -5762.7 | 6.8587 | 39.5633 | 53.895 | -1688.8807
2043-08-31 18:01 | -5495.03 | 6.8587 | 39.8837 | 53.895 | -1610.4343
2043-09-01 19:01 | -5904.74 | 6.8587 | 39.7363 | 53.895 | -1730.5085
2043-09-02 20:01 | -6062.99 | 6.8587 | 39.6917 | 53.895 | -1776.887
2043-09-03 21:01 | -6802.34 | 6.8587 | 39.247 | 53.895 | -1993.5691
2043-09-04 22:01 | -6889.96 | 6.8587 | 39.1602 | 53.895 | -2019.2479
2043-09-05 23:01 | -7742.33 | 6.8587 | 38.5772 | 53.895 | -2269.0529
2043-09-07 00:01 | -7922.27 | 6.8587 | 38.3702 | 53.895 | -2321.7881
2043-09-08 01:01 | -7942.03 | 6.8587 | 38.3018 | 53.895 | -2327.5792
2043-09-09 02:01 | -7898.52 | 6.8587 | 38.312 | 53.895 | -2314.8277
2043-09-10 03:01 | -7816.6 | 6.8587 | 38.373 | 53.895 | -2290.8193
2043-09-11 04:01 | -7692.83 | 6.8587 | 38.463 | 53.895 | -2254.5459
2043-09-12 05:01 | -7275.71 | 6.8587 | 38.78 | 53.895 | -2132.3001
2043-09-13 06:01 | -6815.04 | 6.8587 | 39.1679 | 53.895 | -1997.2911
2043-09-14 07:01 | -6627.22 | 6.8587 | 39.4028 | 53.895 | -1942.2465
2043-09-15 08:01 | -6532.71 | 6.8587 | 39.5563 | 53.895 | -1914.5483
2043-09-16 09:01 | -7083.78 | 6.8587 | 39.2578 | 53.895 | -2076.051
2043-09-17 10:01 | -6764.99 | 6.8587 | 39.4671 | 53.895 | -1982.6229
2043-09-18 11:01 | -6669.11 | 6.8587 | 39.5825 | 53.895 | -1954.5232
2043-09-19 12:01 | -6510.62 | 6.8587 | 39.7399 | 53.895 | -1908.0744
2043-09-20 13:01 | -6256.94 | 6.8587 | 39.9601 | 53.895 | -1833.7281
2043-09-21 14:01 | -6486.4 | 6.8587 | 39.8635 | 53.895 | -1900.9762
2043-09-22 15:01 | -6073.52 | 6.8587 | 40.1706 | 53.895 | -1779.973
2043-09-23 16:01 | -5054.38 | 6.8587 | 40.9374 | 53.895 | -1481.2926
2043-09-24 17:01 | -4871.62 | 6.8587 | 41.2397 | 53.895 | -1427.7309
2043-09-25 18:01 | -4709.31 | 6.8587 | 41.4753 | 53.895 | -1380.1625
2043-09-26 19:01 | -4922.18 | 6.8587 | 41.4303 | 53.895 | -1442.5486
2043-09-27 20:01 | -4968.68 | 6.8587 | 41.4651 | 53.895 | -1456.1764
2043-09-28 21:01 | -5792.18 | 6.8587 | 40.9719 | 53.895 | -1697.5204
2043-09-29 22:01 | -5916.92 | 6.8587 | 40.8406 | 53.895 | -1734.0781
2043-09-30 23:01 | -6508.65 | 6.8587 | 40.4194 | 53.895 | -1907.497
2043-10-02 00:01 | -6696.13 | 6.8587 | 40.2306 | 53.895 | -1962.442
2043-10-03 01:01 | -6743.49 | 6.8587 | 40.1519 | 53.895 | -1976.3218
2043-10-04 02:01 | -6774.26 | 6.8587 | 40.1092 | 53.895 | -1985.3396
2043-10-05 03:01 | -6462.98 | 6.8587 | 40.3176 | 53.895 | -1894.1125
2043-10-06 04:01 | -6521.1 | 6.8587 | 40.3048 | 53.895 | -1911.1458
2043-10-07 05:01 | -6472.54 | 6.8587 | 40.3494 | 53.895 | -1896.9142
2043-10-08 06:01 | -6009.54 | 6.8587 | 40.6756 | 53.895 | -1761.2223
2043-10-09 07:01 | -6065.87 | 6.8587 | 40.7048 | 53.895 | -1777.731
2043-10-10 08:01 | -6129.54 | 6.8587 | 40.6959 | 53.895 | -1796.3908
2043-10-11 09:01 | -6838.22 | 6.8587 | 40.2304 | 53.895 | -2004.0845
2043-10-12 10:01 | -7052.98 | 6.8587 | 40.0189 | 53.895 | -2067.0244
2043-10-13 11:01 | -6508.18 | 6.8587 | 40.3428 | 53.895 | -1907.3593
2043-10-14 12:01 | -6031.99 | 6.8587 | 40.7102 | 53.895 | -1767.8018
2043-10-15 13:01 | -5785.12 | 6.8587 | 40.9551 | 53.895 | -1695.4513
2043-10-16 14:01 | -5890.85 | 6.8587 | 40.9486 | 53.895 | -1726.4377
2043-10-17 15:01 | -5802.81 | 6.8587 | 41.0426 | 53.895 | -1700.6357
2043-10-18 16:01 | -5375.98 | 6.8587 | 41.3762 | 53.895 | -1575.5442
2043-10-19 17:01 | -5314.91 | 6.8587 | 41.5 | 53.895 | -1557.6464
2043-10-20 18:01 | -5022.76 | 6.8587 | 41.7496 | 53.895 | -1472.0256
2043-10-21 19:01 | -5487.36 | 6.8587 | 41.4986 | 53.895 | -1608.1865
2043-10-22 20:01 | -5789.08 | 6.8587 | 41.2879 | 53.895 | -1696.6119
2043-10-23 21:01 | -6702.78 | 6.8587 | 40.6479 | 53.895 | -1964.3909
2043-10-24 22:01 | -6908.13 | 6.8587 | 40.4043 | 53.895 | -2024.5731
2043-10-25 23:01 | -7689.98 | 6.8587 | 39.7964 | 53.895 | -2253.7107
2043-10-27 00:01 | -8098.91 | 6.8587 | 39.3765 | 53.895 | -2373.5562
2043-10-28 01:01 | -8232.31 | 6.8587 | 39.1504 | 53.895 | -2412.6519
2043-10-29 02:01 | -8409.24 | 6.8587 | 38.9318 | 53.895 | -2464.505
2043-10-30 03:01 | -8471.38 | 6.8587 | 38.806 | 53.895 | -2482.7164
2043-10-31 04:01 | -8607.26 | 6.8587 | 38.6352 | 53.895 | -2522.5389
2043-11-01 05:01 | -8689.1 | 6.8587 | 38.5073 | 53.895 | -2546.5238
2043-11-02 06:01 | -8808.73 | 6.8587 | 38.3539 | 53.895 | -2581.5839
2043-11-03 07:01 | -8226.46 | 6.8587 | 38.6839 | 53.895 | -2410.9374
2043-11-04 08:01 | -7804.11 | 6.8587 | 38.9926 | 53.895 | -2287.1589
2043-11-05 09:01 | -8394.67 | 6.8587 | 38.6447 | 53.895 | -2460.2349
2043-11-06 10:01 | -8579.52 | 6.8587 | 38.4611 | 53.895 | -2514.4091
2043-11-07 11:01 | -8339.98 | 6.8587 | 38.5683 | 53.895 | -2444.2069
2043-11-08 12:01 | -7617.39 | 6.8587 | 39.0676 | 53.895 | -2232.4366
2043-11-09 13:01 | -7048.36 | 6.8587 | 39.5317 | 53.895 | -2065.6704
2043-11-10 14:01 | -5793.65 | 6.8587 | 40.4851 | 53.895 | -1697.9512
2043-11-11 15:01 | -5060.27 | 6.8587 | 41.1968 | 53.895 | -1483.0187
2043-11-12 16:01 | -5618.75 | 6.8587 | 41.0295 | 53.895 | -1646.6931
2043-11-13 17:01 | -4570.11 | 6.8587 | 41.8146 | 53.895 | -1339.367
2043-11-14 18:01 | -5110.39 | 6.8587 | 41.6333 | 53.895 | -1497.7075
2043-11-15 19:01 | -5651.58 | 6.8587 | 41.3324 | 53.895 | -1656.3146
2043-11-16 20:01 | -6044.97 | 6.8587 | 41.0329 | 53.895 | -1771.6058
2043-11-17 21:01 | -6136.81 | 6.8587 | 40.9367 | 53.895 | -1798.5215
2043-11-18 22:01 | -6335.18 | 6.8587 | 40.8089 | 53.895 | -1856.658
2043-11-19 23:01 | -6494.05 | 6.8587 | 40.6828 | 53.895 | -1903.2182
2043-11-21 00:01 | -7984.13 | 6.8587 | 39.6428 | 53.895 | -2339.9175
2043-11-22 01:01 | -8312.29 | 6.8587 | 39.2323 | 53.895 | -2436.0917
2043-11-23 02:01 | -8274.28 | 6.8587 | 39.1123 | 53.895 | -2424.9521
2043-11-24 03:01 | -8232.85 | 6.8587 | 39.0571 | 53.895 | -2412.8102
2043-11-25 04:01 | -8599.47 | 6.8587 | 38.745 | 53.895 | -2520.2559
2043-11-26 05:01 | -8570.36 | 6.8587 | 38.6468 | 53.895 | -2511.7246
2043-11-27 06:01 | -8378.37 | 6.8587 | 38.7177 | 53.895 | -2455.4579
2043-11-28 07:01 | -7897.74 | 6.8587 | 39.0299 | 53.895 | -2314.5991
2043-11-29 08:01 | -7263.62 | 6.8587 | 39.4972 | 53.895 | -2128.7569
2043-11-30 09:01 | -6727.84 | 6.8587 | 39.9501 | 53.895 | -1971.7353
2043-12-01 10:01 | -5323.9 | 6.8587 | 41.0272 | 53.895 | -1560.2811
2043-12-02 11:01 | -3866.79 | 6.8587 | 42.2651 | 53.895 | -1133.2443
2043-12-03 12:01 | -2499.81 | 6.8587 | 43.5371 | 53.895 | -732.622
2043-12-04 13:01 | -1831.01 | 6.5453 | 44.3084 | 53.895 | -536.6161
2043-12-05 14:01 | -1566.66 | 5.5578 | 44.6166 | 53.895 | -459.1427
2043-12-06 15:01 | -1521.19 | 5.4915 | 44.8978 | 53.895 | -445.8168
2043-12-07 16:01 | -2159.77 | 6.8587 | 44.9255 | 53.895 | -632.9661
2043-12-08 17:01 | -1681.65 | 5.9012 | 45.1426 | 53.895 | -492.843
2043-12-09 18:01 | -2292.96 | 6.8587 | 45.0525 | 53.895 | -672.0002
2043-12-10 19:01 | -2858.69 | 6.8587 | 44.711 | 53.895 | -837.7993
2043-12-11 20:01 | -3365.93 | 6.8587 | 44.3468 | 53.895 | -986.4567
2043-12-12 21:01 | -3662.48 | 6.8587 | 44.1098 | 53.895 | -1073.3669
2043-12-13 22:01 | -3759.09 | 6.8587 | 44.0178 | 53.895 | -1101.6805
2043-12-14 23:01 | -4025.05 | 6.8587 | 43.8093 | 53.895 | -1179.6257
2043-12-16 00:01 | -5190.76 | 6.8587 | 42.9741 | 53.895 | -1521.2616
2043-12-17 01:01 | -5267.76 | 6.8587 | 42.7628 | 53.895 | -1543.8281
2043-12-18 02:01 | -5359.95 | 6.8587 | 42.6097 | 53.895 | -1570.8463
2043-12-19 03:01 | -5349.58 | 6.8587 | 42.5615 | 53.895 | -1567.8071
2043-12-20 04:01 | -5219.62 | 6.8587 | 42.6149 | 53.895 | -1529.7196
2043-12-21 05:01 | -4950.82 | 6.8587 | 42.7827 | 53.895 | -1450.9421
2043-12-22 06:01 | -4303.87 | 6.8587 | 43.2658 | 53.895 | -1261.3398
2043-12-23 07:01 | -4181.63 | 6.8587 | 43.4551 | 53.895 | -1225.5148
2043-12-24 08:01 | -4206.33 | 6.8587 | 43.5188 | 53.895 | -1232.7536
2043-12-25 09:01 | -4769.32 | 6.8587 | 43.1861 | 53.895 | -1397.7497
2043-12-26 10:01 | -4621.57 | 6.8587 | 43.2581 | 53.895 | -1354.4485
2043-12-27 11:01 | -3823.06 | 6.8587 | 43.8135 | 53.895 | -1120.4283
2043-12-28 12:01 | -2963.85 | 6.8587 | 44.5095 | 53.895 | -868.6187
2043-12-29 13:01 | -3081.47 | 6.8587 | 44.59 | 53.895 | -903.0897
2043-12-30 14:01 | -3077.24 | 6.8587 | 44.6665 | 53.895 | -901.85
2043-12-31 15:01 | -2950.84 | 6.8587 | 44.8152 | 53.895 | -864.8058
2044-01-01 16:01 | -2091.51 | 6.8587 | 45.4838 | 53.895 | -612.9611
2044-01-02 17:01 | -1943.14 | 6.7678 | 45.7232 | 53.895 | -569.4781
2044-01-03 18:01 | -1940.47 | 6.7492 | 45.827 | 53.895 | -568.6956
2044-01-04 19:01 | -2405.46 | 6.8587 | 45.6082 | 53.895 | -704.9707
2044-01-05 20:01 | -2798.65 | 6.8587 | 45.3583 | 53.895 | -820.2034
2044-01-06 21:01 | -3813.91 | 6.8587 | 44.6638 | 53.895 | -1117.7467
2044-01-07 22:01 | -4095.84 | 6.8587 | 44.3612 | 53.895 | -1200.3722
2044-01-08 23:01 | -4679.88 | 6.8587 | 43.8734 | 53.895 | -1371.5374
2044-01-10 00:01 | -4744.86 | 6.8587 | 43.7167 | 53.895 | -1390.5812
2044-01-11 01:01 | -4989.96 | 6.8587 | 43.4805 | 53.895 | -1462.4129
2044-01-12 02:01 | -5129.36 | 6.8587 | 43.3162 | 53.895 | -1503.267
2044-01-13 03:01 | -5147.68 | 6.8587 | 43.2517 | 53.895 | -1508.6361
2044-01-14 04:01 | -5234.51 | 6.8587 | 43.1502 | 53.895 | -1534.0834
2044-01-15 05:01 | -5253.77 | 6.8587 | 43.0984 | 53.895 | -1539.728
2044-01-16 06:01 | -4885.25 | 6.8587 | 43.312 | 53.895 | -1431.7254
2044-01-17 07:01 | -4982.93 | 6.8587 | 43.264 | 53.895 | -1460.3526
2044-01-18 08:01 | -5118.27 | 6.8587 | 43.1644 | 53.895 | -1500.0169
2044-01-19 09:01 | -5591.16 | 6.8587 | 42.8233 | 53.895 | -1638.6072
2044-01-20 10:01 | -5505.78 | 6.8587 | 42.8155 | 53.895 | -1613.5848
2044-01-21 11:01 | -5207.87 | 6.8587 | 42.9906 | 53.895 | -1526.276
2044-01-22 12:01 | -4770.25 | 6.8587 | 43.2927 | 53.895 | -1398.0223
2044-01-23 13:01 | -4583.98 | 6.8587 | 43.4614 | 53.895 | -1343.4319
2044-01-24 14:01 | -4384.36 | 6.8587 | 43.6335 | 53.895 | -1284.9291
2044-01-25 15:01 | -4501.44 | 6.8587 | 43.5985 | 53.895 | -1319.2418
2044-01-26 16:01 | -3739.04 | 6.8587 | 44.1311 | 53.895 | -1095.8045
2044-01-27 17:01 | -3521.69 | 6.8587 | 44.378 | 53.895 | -1032.1055
2044-01-28 18:01 | -3311.41 | 6.8587 | 44.5999 | 53.895 | -970.4785
2044-01-29 19:01 | -3823.4 | 6.8587 | 44.3202 | 53.895 | -1120.5279
2044-01-30 20:01 | -4067.13 | 6.8587 | 44.1439 | 53.895 | -1191.9581
2044-01-31 21:01 | -4934.99 | 6.8587 | 43.5449 | 53.895 | -1446.3028
2044-02-01 22:01 | -5281.12 | 6.8587 | 43.2088 | 53.895 | -1547.7435
2044-02-02 23:01 | -6121.97 | 6.8587 | 42.5408 | 53.895 | -1794.1723
2044-02-04 00:01 | -6313.64 | 6.8587 | 42.2533 | 53.895 | -1850.3452
2044-02-05 01:01 | -6391 | 6.8587 | 42.0861 | 53.895 | -1873.0172
2044-02-06 02:01 | -6459.47 | 6.8587 | 41.9561 | 53.895 | -1893.0838
2044-02-07 03:01 | -6262.28 | 6.8587 | 42.0293 | 53.895 | -1835.2931
2044-02-08 04:01 | -6324.49 | 6.8587 | 41.9548 | 53.895 | -1853.5251
2044-02-09 05:01 | -6172.16 | 6.8587 | 42.0262 | 53.895 | -1808.8815
2044-02-10 06:01 | -5716.32 | 6.8587 | 42.3205 | 53.895 | -1675.288
2044-02-11 07:01 | -5830.05 | 6.8587 | 42.2814 | 53.895 | -1708.619
2044-02-12 08:01 | -5795.89 | 6.8587 | 42.3041 | 53.895 | -1698.6077
2044-02-13 09:01 | -5844.07 | 6.8587 | 42.2752 | 53.895 | -1712.7278
2044-02-14 10:01 | -5848.58 | 6.8587 | 42.2748 | 53.895 | -1714.0496
2044-02-15 11:01 | -5111.99 | 6.8587 | 42.7844 | 53.895 | -1498.1764
2044-02-16 12:01 | -3259.17 | 6.8587 | 44.1397 | 53.895 | -955.1684
2044-02-17 13:01 | -2347.07 | 6.8587 | 45.0443 | 53.895 | -687.8583
2044-02-18 14:01 | -1827.06 | 6.3874 | 45.5781 | 53.895 | -535.4584
2044-02-19 15:01 | -2287.48 | 6.8587 | 45.5836 | 53.895 | -670.3942
2044-02-20 16:01 | -2069.65 | 6.8587 | 45.8424 | 53.895 | -606.5545
2044-02-21 17:01 | -2543.72 | 6.8587 | 45.6433 | 53.895 | -745.4907
2044-02-22 18:01 | -2638.38 | 6.8587 | 45.6048 | 53.895 | -773.2328
2044-02-23 19:01 | -3034.19 | 6.8587 | 45.3536 | 53.895 | -889.2333
2044-02-24 20:01 | -3320.95 | 6.8587 | 45.1395 | 53.895 | -973.2744
2044-02-25 21:01 | -4183.63 | 6.8587 | 44.5371 | 53.895 | -1226.1009
2044-02-26 22:01 | -4383.08 | 6.8587 | 44.3069 | 53.895 | -1284.5539
2044-02-27 23:01 | -5104.9 | 6.8587 | 43.7569 | 53.895 | -1496.0985
2044-02-29 00:01 | -5130.34 | 6.8587 | 43.6171 | 53.895 | -1503.5542
2044-03-01 01:01 | -5335.54 | 6.8587 | 43.3955 | 53.895 | -1563.6924
2044-03-02 02:01 | -5354.57 | 6.8587 | 43.3007 | 53.895 | -1569.2696
2044-03-03 03:01 | -5705.02 | 6.8587 | 43.0096 | 53.895 | -1671.9763
2044-03-04 04:01 | -5889.7 | 6.8587 | 42.7979 | 53.895 | -1726.1007
2044-03-05 05:01 | -6487.77 | 6.8587 | 42.3174 | 53.895 | -1901.3777
2044-03-06 06:01 | -6275.04 | 6.8587 | 42.3357 | 53.895 | -1839.0327
2044-03-07 07:01 | -6715.82 | 6.8587 | 41.9784 | 53.895 | -1968.2126
2044-03-08 08:01 | -7019.38 | 6.8587 | 41.6693 | 53.895 | -2057.1772
2044-03-09 09:01 | -7971.22 | 6.8587 | 40.9107 | 53.895 | -2336.134
2044-03-10 10:01 | -8163.26 | 6.8587 | 40.5857 | 53.895 | -2392.4153
2044-03-11 11:01 | -7939.25 | 6.8587 | 40.5948 | 53.895 | -2326.7645
2044-03-12 12:01 | -8165.83 | 6.8587 | 40.3456 | 53.895 | -2393.1685
2044-03-13 13:01 | -8077.48 | 6.8587 | 40.2826 | 53.895 | -2367.2757
2044-03-14 14:01 | -8535.66 | 6.8587 | 39.8632 | 53.895 | -2501.555
2044-03-15 15:01 | -8615.06 | 6.8587 | 39.6741 | 53.895 | -2524.8249
2044-03-16 16:01 | -7554.17 | 6.8587 | 40.2836 | 53.895 | -2213.9087
2044-03-17 17:01 | -7430.82 | 6.8587 | 40.4045 | 53.895 | -2177.7584
2044-03-18 18:01 | -7482.91 | 6.8587 | 40.3695 | 53.895 | -2193.0244
2044-03-19 19:01 | -8140.25 | 6.8587 | 39.8798 | 53.895 | -2385.6718
2044-03-20 20:01 | -8118.66 | 6.8587 | 39.788 | 53.895 | -2379.3444
2044-03-21 21:01 | -9187.55 | 6.8587 | 39.0062 | 53.895 | -2692.6051
2044-03-22 22:01 | -9608.36 | 6.8587 | 38.5354 | 53.895 | -2815.9323
2044-03-23 23:01 | -10186.3 | 6.8587 | 37.9621 | 53.895 | -2985.3098
2044-03-25 00:01 | -10486.2 | 6.8587 | 37.5687 | 53.895 | -3073.2019
2044-03-26 01:01 | -10712.6 | 6.8587 | 37.2463 | 53.895 | -3139.5531
2044-03-27 02:01 | -10784.7 | 6.8587 | 37.0407 | 53.895 | -3160.6836
2044-03-28 03:01 | -10759.2 | 6.8587 | 36.9391 | 53.895 | -3153.2103
2044-03-29 04:01 | -10678.1 | 6.8587 | 36.8887 | 53.895 | -3129.4422
2044-03-30 05:01 | -10328.4 | 6.8587 | 37.0472 | 53.895 | -3026.9552
2044-03-31 06:01 | -10073.6 | 6.8587 | 37.1831 | 53.895 | -2952.2807
2044-04-01 07:01 | -10019.7 | 6.8587 | 37.2051 | 53.895 | -2936.4842
2044-04-02 08:01 | -10058.9 | 6.8587 | 37.148 | 53.895 | -2947.9726
2044-04-03 09:01 | -10730.3 | 6.8587 | 36.6566 | 53.895 | -3144.7405
2044-04-04 10:01 | -10331.5 | 6.8587 | 36.8194 | 53.895 | -3027.8638
2044-04-05 11:01 | -10081.1 | 6.8587 | 36.963 | 53.895 | -2954.4788
2044-04-06 12:01 | -10052.7 | 6.8587 | 36.9778 | 53.895 | -2946.1555
2044-04-07 13:01 | -9640.46 | 6.8587 | 37.2323 | 53.895 | -2825.3399
2044-04-08 14:01 | -9840.21 | 6.8587 | 37.1111 | 53.895 | -2883.8809
2044-04-09 15:01 | -10029.2 | 6.8587 | 36.9631 | 53.895 | -2939.2684
2044-04-10 16:01 | -9239.79 | 6.8587 | 37.4452 | 53.895 | -2707.9151
2044-04-11 17:01 | -9178.01 | 6.8587 | 37.5352 | 53.895 | -2689.8092
2044-04-12 18:01 | -8957.77 | 6.8587 | 37.7024 | 53.895 | -2625.2632
2044-04-13 19:01 | -9397.95 | 6.8587 | 37.4113 | 53.895 | -2754.2673
2044-04-14 20:01 | -9587.81 | 6.8587 | 37.2286 | 53.895 | -2809.9097
2044-04-15 21:01 | -10195.8 | 6.8587 | 36.7719 | 53.895 | -2988.094
2044-04-16 22:01 | -10264.6 | 6.8587 | 36.6156 | 53.895 | -3008.2573
2044-04-17 23:01 | -11050.3 | 6.8587 | 35.9987 | 53.895 | -3238.5232
2044-04-19 00:01 | -11411.4 | 6.8587 | 35.5933 | 53.895 | -3344.3512
2044-04-20 01:01 | -11366.2 | 6.8587 | 35.4738 | 53.895 | -3331.1044
2044-04-21 02:01 | -11398.1 | 6.8587 | 35.3586 | 53.895 | -3340.4534
2044-04-22 03:01 | -11352.2 | 6.8587 | 35.317 | 53.895 | -3327.0014
2044-04-23 04:01 | -11158.1 | 6.8587 | 35.3771 | 53.895 | -3270.1163
2044-04-24 05:01 | -11383.1 | 6.8587 | 35.1873 | 53.895 | -3336.0573
2044-04-25 06:01 | -11319.4 | 6.8587 | 35.1578 | 53.895 | -3317.3887
2044-04-26 07:01 | -10404.3 | 6.8587 | 35.7346 | 53.895 | -3049.1993
2044-04-27 08:01 | -9999.3 | 6.8587 | 36.0843 | 53.895 | -2930.5056
2044-04-28 09:01 | -10013.8 | 6.8587 | 36.1569 | 53.895 | -2934.7551
2044-04-29 10:01 | -9410.84 | 6.8587 | 36.5966 | 53.895 | -2758.0449
2044-04-30 11:01 | -8096.63 | 6.8587 | 37.6008 | 53.895 | -2372.888
2044-05-01 12:01 | -7362.07 | 6.8587 | 38.3417 | 53.895 | -2157.6097
2044-05-02 13:01 | -6915.8 | 6.8587 | 38.8648 | 53.895 | -2026.8209
2044-05-03 14:01 | -6574.49 | 6.8587 | 39.2851 | 53.895 | -1926.7928
2044-05-04 15:01 | -7573.88 | 6.8587 | 38.7812 | 53.895 | -2219.6851
2044-05-05 16:01 | -7922.07 | 6.8587 | 38.5434 | 53.895 | -2321.7295
2044-05-06 17:01 | -6701.93 | 6.8587 | 39.3568 | 53.895 | -1964.1418
2044-05-07 18:01 | -7238.93 | 6.8587 | 39.15 | 53.895 | -2121.521
2044-05-08 19:01 | -7607.5 | 6.8587 | 38.9231 | 53.895 | -2229.5382
2044-05-09 20:01 | -7839.96 | 6.8587 | 38.724 | 53.895 | -2297.6655
2044-05-10 21:01 | -7867.44 | 6.8587 | 38.702 | 53.895 | -2305.7191
2044-05-11 22:01 | -7952.31 | 6.8587 | 38.6645 | 53.895 | -2330.592
2044-05-12 23:01 | -7924.17 | 6.8587 | 38.6713 | 53.895 | -2322.345
2044-05-14 00:01 | -9175.58 | 6.8587 | 37.8144 | 53.895 | -2689.097
2044-05-15 01:01 | -9104.36 | 6.8587 | 37.7122 | 53.895 | -2668.2245
2044-05-16 02:01 | -9068.16 | 6.8587 | 37.6641 | 53.895 | -2657.6154
2044-05-17 03:01 | -8929.67 | 6.8587 | 37.7369 | 53.895 | -2617.0279
2044-05-18 04:01 | -8804.13 | 6.8587 | 37.8186 | 53.895 | -2580.2358
2044-05-19 05:01 | -8940.26 | 6.8587 | 37.7144 | 53.895 | -2620.1316
2044-05-20 06:01 | -8838.3 | 6.8587 | 37.7754 | 53.895 | -2590.25
2044-05-21 07:01 | -7982.96 | 6.8587 | 38.3682 | 53.895 | -2339.5746
2044-05-22 08:01 | -7285.1 | 6.8587 | 38.9588 | 53.895 | -2135.0521
2044-05-23 09:01 | -7413.59 | 6.8587 | 39.0198 | 53.895 | -2172.7088
2044-05-24 10:01 | -6970.13 | 6.8587 | 39.3869 | 53.895 | -2042.7435
2044-05-25 11:01 | -5741.95 | 6.8587 | 40.3272 | 53.895 | -1682.7994
2044-05-26 12:01 | -4308.45 | 6.8587 | 41.5463 | 53.895 | -1262.6821
2044-05-27 13:01 | -3792.65 | 6.8587 | 42.2122 | 53.895 | -1111.516
2044-05-28 14:01 | -3449.85 | 6.8587 | 42.692 | 53.895 | -1011.0512
2044-05-29 15:01 | -3487.48 | 6.8587 | 42.889 | 53.895 | -1022.0795
2044-05-30 16:01 | -4006.44 | 6.8587 | 42.7062 | 53.895 | -1174.1717
2044-05-31 17:01 | -3601.7 | 6.8587 | 43.0527 | 53.895 | -1055.5541
2044-06-01 18:01 | -4450.62 | 6.8587 | 42.5911 | 53.895 | -1304.348
2044-06-02 19:01 | -5019.06 | 6.8587 | 42.195 | 53.895 | -1470.9413
2044-06-03 20:01 | -5419.58 | 6.8587 | 41.8627 | 53.895 | -1588.3221
2044-06-04 21:01 | -6148.64 | 6.8587 | 41.3166 | 53.895 | -1801.9885
2044-06-05 22:01 | -6290.2 | 6.8587 | 41.1281 | 53.895 | -1843.4756
2044-06-06 23:01 | -6528.88 | 6.8587 | 40.8886 | 53.895 | -1913.4258
2044-06-08 00:01 | -7666.59 | 6.8587 | 40.0436 | 53.895 | -2246.8557
2044-06-09 01:01 | -7972.53 | 6.8587 | 39.6491 | 53.895 | -2336.5179
2044-06-10 02:01 | -8412.4 | 6.8587 | 39.197 | 53.895 | -2465.4311
2044-06-11 03:01 | -8573.77 | 6.8587 | 38.9476 | 53.895 | -2512.7239
2044-06-12 04:01 | -8462.73 | 6.8587 | 38.906 | 53.895 | -2480.1813
2044-06-13 05:01 | -8216.58 | 6.8587 | 38.9966 | 53.895 | -2408.0419
2044-06-14 06:01 | -7818.19 | 6.8587 | 39.2535 | 53.895 | -2291.2853
2044-06-15 07:01 | -7601.16 | 6.8587 | 39.4248 | 53.895 | -2227.6801
2044-06-16 08:01 | -7393.03 | 6.8587 | 39.5967 | 53.895 | -2166.6832
2044-06-17 09:01 | -7539.36 | 6.8587 | 39.5397 | 53.895 | -2209.5683
2044-06-18 10:01 | -6943.29 | 6.8587 | 39.9506 | 53.895 | -2034.8774
2044-06-19 11:01 | -6239.64 | 6.8587 | 40.498 | 53.895 | -1828.658
2044-06-20 12:01 | -5505.44 | 6.8587 | 41.121 | 53.895 | -1613.4852
2044-06-21 13:01 | -5183.64 | 6.8587 | 41.4911 | 53.895 | -1519.1749
2044-06-22 14:01 | -5086.1 | 6.8587 | 41.6846 | 53.895 | -1490.5888
2044-06-23 15:01 | -4710.72 | 6.8587 | 42.0482 | 53.895 | -1380.5758
2044-06-24 16:01 | -3855.21 | 6.8587 | 42.7619 | 53.895 | -1129.8505
2044-06-25 17:01 | -3424.87 | 6.8587 | 43.2447 | 53.895 | -1003.7303
2044-06-26 18:01 | -3633.88 | 6.8587 | 43.2736 | 53.895 | -1064.9851
2044-06-27 19:01 | -4600.77 | 6.8587 | 42.7041 | 53.895 | -1348.3526
2044-06-28 20:01 | -5399.02 | 6.8587 | 42.125 | 53.895 | -1582.2966
2044-06-29 21:01 | -6955.75 | 6.8587 | 40.9817 | 53.895 | -2038.5291
2044-06-30 22:01 | -7759.36 | 6.8587 | 40.2084 | 53.895 | -2274.0439
2044-07-01 23:01 | -9028.2 | 6.8587 | 39.1077 | 53.895 | -2645.9042
2044-07-03 00:01 | -9638.4 | 6.8587 | 38.3977 | 53.895 | -2824.7362
2044-07-04 01:01 | -10326.1 | 6.8587 | 37.6689 | 53.895 | -3026.2812
2044-07-05 02:01 | -10955.3 | 6.8587 | 36.9835 | 53.895 | -3210.6815
2044-07-06 03:01 | -11257.5 | 6.8587 | 36.5281 | 53.895 | -3299.2476
2044-07-07 04:01 | -11435 | 6.8587 | 36.1829 | 53.895 | -3351.2677
2044-07-08 05:01 | -11747 | 6.8587 | 35.779 | 53.895 | -3442.7059
2044-07-09 06:01 | -11567.2 | 6.8587 | 35.7051 | 53.895 | -3390.0117
2044-07-10 07:01 | -11179.7 | 6.8587 | 35.8412 | 53.895 | -3276.4466
2044-07-11 08:01 | -10951.5 | 6.8587 | 35.9356 | 53.895 | -3209.5678
2044-07-12 09:01 | -11388.4 | 6.8587 | 35.5987 | 53.895 | -3337.6106
2044-07-13 10:01 | -11002.5 | 6.8587 | 35.7548 | 53.895 | -3224.5144
2044-07-14 11:01 | -10968.9 | 6.8587 | 35.7465 | 53.895 | -3214.6673
2044-07-15 12:01 | -11212 | 6.8587 | 35.5385 | 53.895 | -3285.9128
2044-07-16 13:01 | -10978.6 | 6.8587 | 35.6093 | 53.895 | -3217.51
2044-07-17 14:01 | -10886.8 | 6.8587 | 35.6255 | 53.895 | -3190.6061
2044-07-18 15:01 | -11022.2 | 6.8587 | 35.5022 | 53.895 | -3230.2879
2044-07-19 16:01 | -11053.5 | 6.8587 | 35.4095 | 53.895 | -3239.4611
2044-07-20 17:01 | -10284.7 | 6.8587 | 35.868 | 53.895 | -3014.148
2044-07-21 18:01 | -11008.9 | 6.8587 | 35.4086 | 53.895 | -3226.3901
2044-07-22 19:01 | -11426.3 | 6.8587 | 35.0249 | 53.895 | -3348.718
2044-07-23 20:01 | -11745.2 | 6.8587 | 34.6729 | 53.895 | -3442.1783
2044-07-24 21:01 | -11964.6 | 6.8587 | 34.4134 | 53.895 | -3506.4781
2044-07-25 22:01 | -12109.3 | 6.8587 | 34.2097 | 53.895 | -3548.8855
2044-07-26 23:01 | -12178.7 | 6.8587 | 34.054 | 53.895 | -3569.2246
2044-07-28 00:01 | -12743.3 | 6.8587 | 33.5871 | 53.895 | -3734.6926
2044-07-29 01:01 | -13264.7 | 6.8587 | 33.0924 | 53.895 | -3887.4998
2044-07-30 02:01 | -13337.8 | 6.8587 | 32.8864 | 53.895 | -3908.9233
2044-07-31 03:01 | -13336.9 | 6.8587 | 32.7781 | 53.895 | -3908.6596
2044-08-01 04:01 | -13196.8 | 6.8587 | 32.7905 | 53.895 | -3867.6003
2044-08-02 05:01 | -13194.4 | 6.8587 | 32.723 | 53.895 | -3866.8969
2044-08-03 06:01 | -13064.7 | 6.8587 | 32.7528 | 53.895 | -3828.8856
2044-08-04 07:01 | -12962.6 | 6.8587 | 32.7873 | 53.895 | -3798.9631
2044-08-05 08:01 | -12982.1 | 6.8587 | 32.7461 | 53.895 | -3804.6779
2044-08-06 09:01 | -12545.4 | 6.8587 | 33.0128 | 53.895 | -3676.6938
2044-08-07 10:01 | -11563.8 | 6.8587 | 33.7046 | 53.895 | -3389.0152
2044-08-08 11:01 | -10263.3 | 6.8587 | 34.7171 | 53.895 | -3007.8763
2044-08-09 12:01 | -10533.9 | 6.8587 | 34.7411 | 53.895 | -3087.1813
2044-08-10 13:01 | -9394.13 | 6.8587 | 35.6004 | 53.895 | -2753.1477
2044-08-11 14:01 | -9889.06 | 6.8587 | 35.4522 | 53.895 | -2898.1974
2044-08-12 15:01 | -10478 | 6.8587 | 35.1138 | 53.895 | -3070.7987
2044-08-13 16:01 | -9647.92 | 6.8587 | 35.6453 | 53.895 | -2827.5262
2044-08-14 17:01 | -9322.79 | 6.8587 | 35.9492 | 53.895 | -2732.24
2044-08-15 18:01 | -9012.43 | 6.8587 | 36.2671 | 53.895 | -2641.2825
2044-08-16 19:01 | -9269.65 | 6.8587 | 36.1707 | 53.895 | -2716.6662
2044-08-17 20:01 | -9374.22 | 6.8587 | 36.1346 | 53.895 | -2747.3127
2044-08-18 21:01 | -10421.6 | 6.8587 | 35.4539 | 53.895 | -3054.2695
2044-08-19 22:01 | -10737 | 6.8587 | 35.1328 | 53.895 | -3146.7041
2044-08-20 23:01 | -11830.9 | 6.8587 | 34.2792 | 53.895 | -3467.2945
2044-08-22 00:01 | -11992.9 | 6.8587 | 33.9805 | 53.895 | -3514.772
2044-08-23 01:01 | -12324.3 | 6.8587 | 33.6128 | 53.895 | -3611.8958
2044-08-24 02:01 | -12537.3 | 6.8587 | 33.3335 | 53.895 | -3674.3199
2044-08-25 03:01 | -12616.8 | 6.8587 | 33.1738 | 53.895 | -3697.6191
2044-08-26 04:01 | -12740.6 | 6.8587 | 32.9934 | 53.895 | -3733.9013
2044-08-27 05:01 | -12741.9 | 6.8587 | 32.913 | 53.895 | -3734.2823
2044-08-28 06:01 | -12553.9 | 6.8587 | 32.9714 | 53.895 | -3679.1849
2044-08-29 07:01 | -12510.6 | 6.8587 | 32.9652 | 53.895 | -3666.4949
2044-08-30 08:01 | -12541.9 | 6.8587 | 32.906 | 53.895 | -3675.6681
2044-08-31 09:01 | -12422.5 | 6.8587 | 32.9498 | 53.895 | -3640.6754
2044-09-01 10:01 | -12273.7 | 6.8587 | 33.0281 | 53.895 | -3597.0664
2044-09-02 11:01 | -10609.3 | 6.8587 | 34.1693 | 53.895 | -3109.2789
2044-09-03 12:01 | -9624.19 | 6.8587 | 35.0409 | 53.895 | -2820.5717
2044-09-04 13:01 | -9240.16 | 6.8587 | 35.5184 | 53.895 | -2708.0236
2044-09-05 14:01 | -8610.48 | 6.8587 | 36.1117 | 53.895 | -2523.4826
2044-09-06 15:01 | -8369.32 | 6.8587 | 36.4675 | 53.895 | -2452.8056
2044-09-07 16:01 | -8114.89 | 6.8587 | 36.8112 | 53.895 | -2378.2395
2044-09-08 17:01 | -9218.21 | 6.8587 | 36.1816 | 53.895 | -2701.5907
2044-09-09 18:01 | -9835.32 | 6.8587 | 35.7037 | 53.895 | -2882.4478
2044-09-10 19:01 | -10422.5 | 6.8587 | 35.2148 | 53.895 | -3054.5332
2044-09-11 20:01 | -10959.2 | 6.8587 | 34.7433 | 53.895 | -3211.8245
2044-09-12 21:01 | -12017.2 | 6.8587 | 33.8966 | 53.895 | -3521.8937
2044-09-13 22:01 | -12238.3 | 6.8587 | 33.5313 | 53.895 | -3586.6917
2044-09-14 23:01 | -12613.5 | 6.8587 | 33.1216 | 53.895 | -3696.6519
2044-09-16 00:01 | -13034.8 | 6.8587 | 32.6835 | 53.895 | -3820.1228
2044-09-17 01:01 | -13181.8 | 6.8587 | 32.4201 | 53.895 | -3863.2042
2044-09-18 02:01 | -13183.1 | 6.8587 | 32.2807 | 53.895 | -3863.5852
2044-09-19 03:01 | -13114.9 | 6.8587 | 32.2313 | 53.895 | -3843.5978
2044-09-20 04:01 | -13130.9 | 6.8587 | 32.1394 | 53.895 | -3848.2869
2044-09-21 05:01 | -13050 | 6.8587 | 32.1279 | 53.895 | -3824.5775
2044-09-22 06:01 | -12794 | 6.8587 | 32.2598 | 53.895 | -3749.5513
2044-09-23 07:01 | -12525.5 | 6.8587 | 32.4385 | 53.895 | -3670.8617
2044-09-24 08:01 | -12353.6 | 6.8587 | 32.5736 | 53.895 | -3620.4828
2044-09-25 09:01 | -12084.3 | 6.8587 | 32.7834 | 53.895 | -3541.5587
2044-09-26 10:01 | -11426.6 | 6.8587 | 33.2765 | 53.895 | -3348.8059
2044-09-27 11:01 | -10626.2 | 6.8587 | 33.9211 | 53.895 | -3114.2318
2044-09-28 12:01 | -10546.7 | 6.8587 | 34.1208 | 53.895 | -3090.9327
2044-09-29 13:01 | -8103.61 | 6.8587 | 35.8827 | 53.895 | -2374.9337
2044-09-30 14:01 | -6871.72 | 6.8587 | 37.0838 | 53.895 | -2013.9023
2044-10-01 15:01 | -6915.91 | 6.8587 | 37.4206 | 53.895 | -2026.8531
2044-10-02 16:01 | -7170.05 | 6.8587 | 37.4458 | 53.895 | -2101.3342
2044-10-03 17:01 | -7404.81 | 6.8587 | 37.4028 | 53.895 | -2170.1356
2044-10-04 18:01 | -7531.72 | 6.8587 | 37.4178 | 53.895 | -2207.3292
2044-10-05 19:01 | -8220.92 | 6.8587 | 37.0026 | 53.895 | -2409.3138
2044-10-06 20:01 | -8693.02 | 6.8587 | 36.6403 | 53.895 | -2547.6727
2044-10-07 21:01 | -9487.09 | 6.8587 | 36.0469 | 53.895 | -2780.3916
2044-10-08 22:01 | -9775.91 | 6.8587 | 35.7491 | 53.895 | -2865.0364
2044-10-09 23:01 | -10584.3 | 6.8587 | 35.1183 | 53.895 | -3101.9521
2044-10-11 00:01 | -11304.7 | 6.8587 | 34.4905 | 53.895 | -3313.0805
2044-10-12 01:01 | -11274.6 | 6.8587 | 34.3327 | 53.895 | -3304.2591
2044-10-13 02:01 | -11294.5 | 6.8587 | 34.2083 | 53.895 | -3310.0912
2044-10-14 03:01 | -11206.7 | 6.8587 | 34.1937 | 53.895 | -3284.3596
2044-10-15 04:01 | -11182 | 6.8587 | 34.1563 | 53.895 | -3277.1207
2044-10-16 05:01 | -11312.9 | 6.8587 | 34.0293 | 53.895 | -3315.4837
2044-10-17 06:01 | -11190.7 | 6.8587 | 34.0697 | 53.895 | -3279.6704
2044-10-18 07:01 | -10179.3 | 6.8587 | 34.7502 | 53.895 | -2983.2583
2044-10-19 08:01 | -9602.06 | 6.8587 | 35.2621 | 53.895 | -2814.086
2044-10-20 09:01 | -9387.01 | 6.8587 | 35.5444 | 53.895 | -2751.0611
2044-10-21 10:01 | -7983.08 | 6.8587 | 36.6072 | 53.895 | -2339.6098
2044-10-22 11:01 | -6781.53 | 6.8587 | 37.6805 | 53.895 | -1987.4703
2044-10-23 12:01 | -6601.42 | 6.8587 | 38.1222 | 53.895 | -1934.6852
2044-10-24 13:01 | -5848.48 | 6.8587 | 38.8359 | 53.895 | -1714.0203
2044-10-25 14:01 | -6554.53 | 6.8587 | 38.5747 | 53.895 | -1920.9431
2044-10-26 15:01 | -5943.84 | 6.8587 | 39.0776 | 53.895 | -1741.9675
2044-10-27 16:01 | -6496.56 | 6.8587 | 38.8423 | 53.895 | -1903.9538
2044-10-28 17:01 | -5323.92 | 6.8587 | 39.6918 | 53.895 | -1560.2869
2044-10-29 18:01 | -5880.23 | 6.8587 | 39.5092 | 53.895 | -1723.3253
2044-10-30 19:01 | -6112.16 | 6.8587 | 39.4145 | 53.895 | -1791.2973
2044-10-31 20:01 | -6740.23 | 6.8587 | 39.0245 | 53.895 | -1975.3664
2044-11-01 21:01 | -6950.86 | 6.8587 | 38.8648 | 53.895 | -2037.096
2044-11-02 22:01 | -7504.08 | 6.8587 | 38.4834 | 53.895 | -2199.2288
2044-11-03 23:01 | -7748.3 | 6.8587 | 38.2446 | 53.895 | -2270.8026
2044-11-05 00:01 | -9423.84 | 6.8587 | 37.0425 | 53.895 | -2761.8549
2044-11-06 01:01 | -9692.25 | 6.8587 | 36.6228 | 53.895 | -2840.5181
2044-11-07 02:01 | -9762.05 | 6.8587 | 36.4252 | 53.895 | -2860.9744
2044-11-08 03:01 | -9442.98 | 6.8587 | 36.551 | 53.895 | -2767.4643
2044-11-09 04:01 | -9271.58 | 6.8587 | 36.6452 | 53.895 | -2717.2319
2044-11-10 05:01 | -9054.71 | 6.8587 | 36.7708 | 53.895 | -2653.6735
2044-11-11 06:01 | -8887.82 | 6.8587 | 36.9091 | 53.895 | -2604.7629
2044-11-12 07:01 | -8043.32 | 6.8587 | 37.519 | 53.895 | -2357.2644
2044-11-13 08:01 | -7531.19 | 6.8587 | 37.9957 | 53.895 | -2207.1739
2044-11-14 09:01 | -8096.91 | 6.8587 | 37.7387 | 53.895 | -2372.9701
2044-11-15 10:01 | -7978.77 | 6.8587 | 37.8175 | 53.895 | -2338.3467
2044-11-16 11:01 | -6274.49 | 6.8587 | 39.0034 | 53.895 | -1838.8715
2044-11-17 12:01 | -5998.88 | 6.8587 | 39.4457 | 53.895 | -1758.0982
2044-11-18 13:01 | -5930.85 | 6.8587 | 39.6586 | 53.895 | -1738.1606
2044-11-19 14:01 | -5900.02 | 6.8587 | 39.7773 | 53.895 | -1729.1252
2044-11-20 15:01 | -5866.89 | 6.8587 | 39.8959 | 53.895 | -1719.4157
2044-11-21 16:01 | -5472.11 | 6.8587 | 40.2613 | 53.895 | -1603.7171
2044-11-22 17:01 | -4299.26 | 6.8587 | 41.1634 | 53.895 | -1259.9887
2044-11-23 18:01 | -5017.68 | 6.8587 | 40.8886 | 53.895 | -1470.5368
2044-11-24 19:01 | -5527.58 | 6.8587 | 40.5859 | 53.895 | -1619.9738
2044-11-25 20:01 | -6054.65 | 6.8587 | 40.2073 | 53.895 | -1774.4428
2044-11-26 21:01 | -6298.61 | 6.8587 | 40.0163 | 53.895 | -1845.9404
2044-11-27 22:01 | -6363.27 | 6.8587 | 39.9565 | 53.895 | -1864.8903
2044-11-28 23:01 | -6755.27 | 6.8587 | 39.6567 | 53.895 | -1979.7742
2044-11-30 00:01 | -7746.89 | 6.8587 | 38.9303 | 53.895 | -2270.3893
2044-12-01 01:01 | -7908.12 | 6.8587 | 38.6833 | 53.895 | -2317.6412 |  | 15552000
2044-12-02 02:01 | -7919.1 | 6.8587 | 38.5961 | 53.895 | -2320.8591
2044-12-03 03:01 | -7882.53 | 6.8587 | 38.5829 | 53.895 | -2310.1415
2044-12-04 04:01 | -7758.17 | 6.8587 | 38.6368 | 53.895 | -2273.6952
2044-12-05 05:01 | -7563.5 | 6.8587 | 38.7483 | 53.895 | -2216.643
2044-12-06 06:01 | -7028.81 | 6.8587 | 39.137 | 53.895 | -2059.9409
2044-12-07 07:01 | -7058.81 | 6.8587 | 39.1915 | 53.895 | -2068.733
2044-12-08 08:01 | -7065.78 | 6.8587 | 39.2243 | 53.895 | -2070.7757
2044-12-09 09:01 | -7374.64 | 6.8587 | 39.0376 | 53.895 | -2161.2936
2044-12-10 10:01 | -7083.94 | 6.8587 | 39.2182 | 53.895 | -2076.0979
2044-12-11 11:01 | -6667.51 | 6.8587 | 39.5234 | 53.895 | -1954.0543
2044-12-12 12:01 | -6283.85 | 6.8587 | 39.8471 | 53.895 | -1841.6146
2044-12-13 13:01 | -5974.17 | 6.8587 | 40.1359 | 53.895 | -1750.8564
2044-12-14 14:01 | -5871.51 | 6.8587 | 40.2884 | 53.895 | -1720.7697
2044-12-15 15:01 | -5844.66 | 6.8587 | 40.377 | 53.895 | -1712.9008
2044-12-16 16:01 | -5125.67 | 6.8587 | 40.9213 | 53.895 | -1502.1856
2044-12-17 17:01 | -5014.83 | 6.8587 | 41.1151 | 53.895 | -1469.7016
2044-12-18 18:01 | -4965.75 | 6.8587 | 41.235 | 53.895 | -1455.3177
2044-12-19 19:01 | -5387.21 | 6.8587 | 41.0085 | 53.895 | -1578.8354
2044-12-20 20:01 | -5709.88 | 6.8587 | 40.7944 | 53.895 | -1673.4006
2044-12-21 21:01 | -6249.03 | 6.8587 | 40.4184 | 53.895 | -1831.4099
2044-12-22 22:01 | -6507.61 | 6.8587 | 40.1817 | 53.895 | -1907.1922
2044-12-23 23:01 | -7455.11 | 6.8587 | 39.4749 | 53.895 | -2184.8771
63072000
[5 empty] | -3636085.4736 | -415.0783 |  |  | 31536000 | 94608000

## Sheet1
| day | second
0.24658 | 90 | 7776000
0.49315 | 180 | 15552000
0.73973 | 270 | 23328000
1 | 365 | 31536000
1.2466 | 455 | 39312000
1.4932 | 545 | 47088000
1.7397 | 635 | 54864000
2 | 730 | 63072000
2.2466 | 820 | 70848000
2.4932 | 910 | 78624000
2.7397 | 1000 | 86400000
3 | 1095 | 94608000
3.2466 | 1185 | 102384000
3.4932 | 1275 | 110160000
3.7397 | 1365 | 117936000
4 | 1460 | 126144000
126057600

## Knoxville
| Property | Soil |  |  |  |  | Property | Soil
| Thermal conductivity [W/m K] | 1.72 |  | W/M-K | 0.57779 | BTU/HR-FT-R | Thermal conductivity [Btu/Hr-ft-R] | 0.99379
| Specific heat [J/kg K] | 1900
| Density [kg/m3] | 1300
| Volumeric specific heat [MJ/K-M3] | 2.47
| Thermal diffusivity [m2/hr] | 0.0025069 |  | m2/hr | 10.7639 | ft2/hr | Thermal diffusivity [ft2/hr] | 0.026984
VBGHE design and performance
| Borehole number | 2
| Borehole depth | 200 | ft | 61 | m
| Annual Max. LFT | 95.6 | F
| Annual Min. LFT | 39.2 | F
Time | Thermal load | Fluid flow | Outlet temperature | Far field ground temperature | Load
| Btu/hr | GPM | F | F | W
2020-01-01 | -7074.78 | 6.108 | 54.5272 | 59.8258 | -2073.4133
2020-01-02 01:00 | -6997.43 | 6.108 | 53.6128 | 59.8258 | -2050.7443
2020-01-03 02:00 | -7141.19 | 6.108 | 52.948 | 59.8258 | -2092.8762
2020-01-04 03:00 | -7239.66 | 6.108 | 52.5369 | 59.8258 | -2121.7349
2020-01-05 04:00 | -7197.76 | 6.108 | 52.2231 | 59.8258 | -2109.4552
2020-01-06 05:00 | -7129.36 | 6.108 | 51.9458 | 59.8258 | -2089.4092
2020-01-07 06:00 | -7038.92 | 6.108 | 51.8572 | 59.8258 | -2062.9038
2020-01-08 07:00 | -5991.28 | 6.108 | 52.4921 | 59.8258 | -1755.8708
2020-01-09 08:00 | -5374.99 | 6.108 | 52.944 | 59.8258 | -1575.2541
2020-01-10 09:00 | -5798.15 | 6.108 | 52.6396 | 59.8258 | -1699.27
2020-01-11 10:00 | -5405.92 | 6.108 | 52.8153 | 59.8258 | -1584.3188
2020-01-12 11:00 | -4429.77 | 6.108 | 53.4848 | 59.8258 | -1298.2374
2020-01-13 12:00 | -4147.5 | 6.108 | 53.8393 | 59.8258 | -1215.5123
2020-01-14 13:00 | -3866.8 | 6.108 | 54.1366 | 59.8258 | -1133.2472
2020-01-15 14:00 | -3257.75 | 6.108 | 54.6563 | 59.8258 | -954.7523
2020-01-16 15:00 | -3501.43 | 6.108 | 54.6057 | 59.8258 | -1026.1678
2020-01-17 16:00 | -3525.34 | 6.108 | 54.6321 | 59.8258 | -1033.1752
2020-01-18 17:00 | -2763.62 | 6.108 | 55.2137 | 59.8258 | -809.9371
2020-01-19 18:00 | -3731.99 | 6.108 | 54.6064 | 59.8258 | -1093.7383
2020-01-20 19:00 | -4246.19 | 6.108 | 54.1445 | 59.8258 | -1244.4354
2020-01-21 20:00 | -4724.24 | 6.108 | 53.6472 | 59.8258 | -1384.5381
2020-01-22 21:00 | -4962.11 | 6.108 | 53.3374 | 59.8258 | -1454.2509
2020-01-23 22:00 | -5370.61 | 6.108 | 52.9082 | 59.8258 | -1573.9704
2020-01-24 23:00 | -5656.02 | 6.108 | 52.5165 | 59.8258 | -1657.6158
2020-01-26 | -7030.53 | 6.108 | 51.3595 | 59.8258 | -2060.4449
2020-01-27 01:00 | -7468.95 | 6.108 | 50.7525 | 59.8258 | -2188.9332
2020-01-28 02:00 | -7720.58 | 6.108 | 50.3197 | 59.8258 | -2262.6786
2020-01-29 03:00 | -7938.21 | 6.108 | 49.9594 | 59.8258 | -2326.4597
2020-01-30 04:00 | -7841.1 | 6.108 | 49.8445 | 59.8258 | -2297.9996
2020-01-31 05:00 | -7681.29 | 6.108 | 49.8091 | 59.8258 | -2251.1639
2020-02-01 06:00 | -7239.94 | 6.108 | 50.0512 | 59.8258 | -2121.817
2020-02-02 07:00 | -7146.47 | 6.108 | 50.0905 | 59.8258 | -2094.4236
2020-02-03 08:00 | -6992.11 | 6.108 | 50.1648 | 59.8258 | -2049.1852
2020-02-04 09:00 | -7485.33 | 6.108 | 49.7637 | 59.8258 | -2193.7337
2020-02-05 10:00 | -7036.72 | 6.108 | 49.9892 | 59.8258 | -2062.2591
2020-02-06 11:00 | -6442.11 | 6.108 | 50.4043 | 59.8258 | -1887.9961
2020-02-07 12:00 | -5852.82 | 6.108 | 50.8925 | 59.8258 | -1715.2922
2020-02-08 13:00 | -5095.48 | 6.108 | 51.5393 | 59.8258 | -1493.3378
2020-02-09 14:00 | -4090.07 | 6.108 | 52.4176 | 59.8258 | -1198.6812
2020-02-10 15:00 | -3570.9 | 6.108 | 53.0206 | 59.8258 | -1046.5275
2020-02-11 16:00 | -3189.07 | 6.108 | 53.4965 | 59.8258 | -934.6242
2020-02-12 17:00 | -3472.43 | 6.108 | 53.4422 | 59.8258 | -1017.6688
2020-02-13 18:00 | -3607.62 | 6.108 | 53.4069 | 59.8258 | -1057.2891
2020-02-14 19:00 | -4081.88 | 6.108 | 53.0867 | 59.8258 | -1196.2809
2020-02-15 20:00 | -4372.64 | 6.108 | 52.8341 | 59.8258 | -1281.4943
2020-02-16 21:00 | -5257.86 | 6.108 | 52.1228 | 59.8258 | -1540.9267
2020-02-17 22:00 | -5509.49 | 6.108 | 51.7857 | 59.8258 | -1614.6721
2020-02-18 23:00 | -6154.98 | 6.108 | 51.181 | 59.8258 | -1803.8466
2020-02-20 | -6307.31 | 6.108 | 50.9264 | 59.8258 | -1848.4901
2020-02-21 01:00 | -6351.69 | 6.108 | 50.7826 | 59.8258 | -1861.4966
2020-02-22 02:00 | -6415.77 | 6.108 | 50.6459 | 59.8258 | -1880.2766
2020-02-23 03:00 | -6355.62 | 6.108 | 50.6173 | 59.8258 | -1862.6484
2020-02-24 04:00 | -6108.47 | 6.108 | 50.7434 | 59.8258 | -1790.2158
2020-02-25 05:00 | -5734.26 | 6.108 | 51.0147 | 59.8258 | -1680.5457
2020-02-26 06:00 | -5115.71 | 6.108 | 51.5068 | 59.8258 | -1499.2666
2020-02-27 07:00 | -4982.68 | 6.108 | 51.6927 | 59.8258 | -1460.2794
2020-02-28 08:00 | -4946.92 | 6.108 | 51.7773 | 59.8258 | -1449.7991
2020-02-29 09:00 | -5504.81 | 6.108 | 51.4052 | 59.8258 | -1613.3006
2020-03-01 10:00 | -5418.65 | 6.108 | 51.426 | 59.8258 | -1588.0496
2020-03-02 11:00 | -5285.65 | 6.108 | 51.5177 | 59.8258 | -1549.0711
2020-03-03 12:00 | -5406.47 | 6.108 | 51.435 | 59.8258 | -1584.4799
2020-03-04 13:00 | -5283.16 | 6.108 | 51.5004 | 59.8258 | -1548.3414
2020-03-05 14:00 | -5491.4 | 6.108 | 51.329 | 59.8258 | -1609.3705
2020-03-06 15:00 | -5655.93 | 6.108 | 51.1683 | 59.8258 | -1657.5895
2020-03-07 16:00 | -4980.57 | 6.108 | 51.6161 | 59.8258 | -1459.661
2020-03-08 17:00 | -4865.92 | 6.108 | 51.7453 | 59.8258 | -1426.0604
2020-03-09 18:00 | -4770.49 | 6.108 | 51.8417 | 59.8258 | -1398.0926
2020-03-10 19:00 | -5472.27 | 6.108 | 51.3231 | 59.8258 | -1603.764
2020-03-11 20:00 | -6172.09 | 6.108 | 50.7066 | 59.8258 | -1808.861
2020-03-12 21:00 | -7404.13 | 6.108 | 49.6468 | 59.8258 | -2169.9363
2020-03-13 22:00 | -7703.75 | 6.108 | 49.1667 | 59.8258 | -2257.7463
2020-03-14 23:00 | -8660.55 | 6.108 | 48.2479 | 59.8258 | -2538.1567
2020-03-16 | -8843.29 | 6.108 | 47.8412 | 59.8258 | -2591.7125
2020-03-17 01:00 | -8969.57 | 6.108 | 47.5347 | 59.8258 | -2628.7215
2020-03-18 02:00 | -9219.86 | 6.108 | 47.1805 | 59.8258 | -2702.0742
2020-03-19 03:00 | -9247.6 | 6.108 | 47.003 | 59.8258 | -2710.204
2020-03-20 04:00 | -9387.22 | 6.108 | 46.754 | 59.8258 | -2751.1226
2020-03-21 05:00 | -9369.36 | 6.108 | 46.6323 | 59.8258 | -2745.8884
2020-03-22 06:00 | -9249.6 | 6.108 | 46.5973 | 59.8258 | -2710.7902
2020-03-23 07:00 | -9294.83 | 6.108 | 46.4686 | 59.8258 | -2724.0458
2020-03-24 08:00 | -8897.08 | 6.108 | 46.6722 | 59.8258 | -2607.4768
2020-03-25 09:00 | -8152.91 | 6.108 | 47.2099 | 59.8258 | -2389.3821
2020-03-26 10:00 | -6943.22 | 6.108 | 48.184 | 59.8258 | -2034.8569
2020-03-27 11:00 | -5779.29 | 6.108 | 49.2415 | 59.8258 | -1693.7427
2020-03-28 12:00 | -4823.28 | 6.108 | 50.2051 | 59.8258 | -1413.5638
2020-03-29 13:00 | -4127.73 | 6.108 | 50.9949 | 59.8258 | -1209.7182
2020-03-30 14:00 | -3729.6 | 6.108 | 51.5538 | 59.8258 | -1093.0379
2020-03-31 15:00 | -3485.01 | 6.108 | 51.9619 | 59.8258 | -1021.3556
2020-04-01 16:00 | -3601.76 | 6.108 | 52.0548 | 59.8258 | -1055.5717
2020-04-02 17:00 | -4990.97 | 6.108 | 51.1227 | 59.8258 | -1462.7089
2020-04-03 18:00 | -5828.5 | 6.108 | 50.3871 | 59.8258 | -1708.1647
2020-04-04 19:00 | -6726.67 | 6.108 | 49.5641 | 59.8258 | -1971.3924
2020-04-05 20:00 | -7558.53 | 6.108 | 48.7539 | 59.8258 | -2215.1865
2020-04-06 21:00 | -8760.53 | 6.108 | 47.6264 | 59.8258 | -2567.4579
2020-04-07 22:00 | -9309.37 | 6.108 | 46.8928 | 59.8258 | -2728.307
2020-04-08 23:00 | -10565.5 | 6.108 | 45.6757 | 59.8258 | -3096.4424
2020-04-10 | -11025.4 | 6.108 | 44.9749 | 59.8258 | -3231.2258
2020-04-11 01:00 | -11340.6 | 6.108 | 44.4259 | 59.8258 | -3323.6018
2020-04-12 02:00 | -11620.9 | 6.108 | 43.9462 | 59.8258 | -3405.7496
2020-04-13 03:00 | -11771.3 | 6.108 | 43.5846 | 59.8258 | -3449.8275
2020-04-14 04:00 | -11607.9 | 6.108 | 43.4803 | 59.8258 | -3401.9397
2020-04-15 05:00 | -11617.4 | 6.108 | 43.3309 | 59.8258 | -3404.7238
2020-04-16 06:00 | -11158.6 | 6.108 | 43.5463 | 59.8258 | -3270.2628
2020-04-17 07:00 | -10866.5 | 6.108 | 43.7114 | 59.8258 | -3184.6568
2020-04-18 08:00 | -10195.8 | 6.108 | 44.1884 | 59.8258 | -2988.094
2020-04-19 09:00 | -10418.9 | 6.108 | 44.0676 | 59.8258 | -3053.4782
2020-04-20 10:00 | -8734.92 | 6.108 | 45.2967 | 59.8258 | -2559.9524
2020-04-21 11:00 | -7681.27 | 6.108 | 46.2822 | 59.8258 | -2251.158
2020-04-22 12:00 | -7035.22 | 6.108 | 47.004 | 59.8258 | -2061.8195
2020-04-23 13:00 | -6680.79 | 6.108 | 47.4679 | 59.8258 | -1957.9463
2020-04-24 14:00 | -6226.67 | 6.108 | 47.9667 | 59.8258 | -1824.8568
2020-04-25 15:00 | -6509.98 | 6.108 | 47.9375 | 59.8258 | -1907.8868
2020-04-26 16:00 | -5393.98 | 6.108 | 48.84 | 59.8258 | -1580.8195
2020-04-27 17:00 | -6037.3 | 6.108 | 48.5587 | 59.8258 | -1769.358
2020-04-28 18:00 | -6550.52 | 6.108 | 48.2164 | 59.8258 | -1919.7679
2020-04-29 19:00 | -7246.76 | 6.108 | 47.6607 | 59.8258 | -2123.8157
2020-04-30 20:00 | -7787.2 | 6.108 | 47.1668 | 59.8258 | -2282.203
2020-05-01 21:00 | -8871.28 | 6.108 | 46.267 | 59.8258 | -2599.9155
2020-05-02 22:00 | -9327.63 | 6.108 | 45.7032 | 59.8258 | -2733.6585
2020-05-03 23:00 | -10238 | 6.108 | 44.8295 | 59.8258 | -3000.4616
2020-05-05 | -10857 | 6.108 | 44.1212 | 59.8258 | -3181.8726
2020-05-06 01:00 | -11158.4 | 6.108 | 43.65 | 59.8258 | -3270.2042
2020-05-07 02:00 | -11218.6 | 6.108 | 43.3968 | 59.8258 | -3287.8471
2020-05-08 03:00 | -11416.3 | 6.108 | 43.1004 | 59.8258 | -3345.7873
2020-05-09 04:00 | -11547.2 | 6.108 | 42.8376 | 59.8258 | -3384.1503
2020-05-10 05:00 | -11733.8 | 6.108 | 42.5562 | 59.8258 | -3438.8373
2020-05-11 06:00 | -11836.5 | 6.108 | 42.3431 | 59.8258 | -3468.9357
2020-05-12 07:00 | -10872.4 | 6.108 | 42.9495 | 59.8258 | -3186.3859
2020-05-13 08:00 | -9438.72 | 6.108 | 44.0608 | 59.8258 | -2766.2158
2020-05-14 09:00 | -8773.37 | 6.108 | 44.7555 | 59.8258 | -2571.2209
2020-05-15 10:00 | -7263.54 | 6.108 | 46.0538 | 59.8258 | -2128.7334
2020-05-16 11:00 | -5493.84 | 6.108 | 47.6721 | 59.8258 | -1610.0856
2020-05-17 12:00 | -4074.81 | 6.108 | 49.1606 | 59.8258 | -1194.2089
2020-05-18 13:00 | -3282.77 | 6.108 | 50.1942 | 59.8258 | -962.0849
2020-05-19 14:00 | -2791.85 | 6.108 | 50.9302 | 59.8258 | -818.2105
2020-05-20 15:00 | -2555.17 | 6.108 | 51.4356 | 59.8258 | -748.8464
2020-05-21 16:00 | -3104.05 | 6.108 | 51.2892 | 59.8258 | -909.7073
2020-05-22 17:00 | -2709.06 | 6.108 | 51.7145 | 59.8258 | -793.9471
2020-05-23 18:00 | -3880.67 | 6.108 | 51.0168 | 59.8258 | -1137.3121
2020-05-24 19:00 | -4867.68 | 6.108 | 50.2701 | 59.8258 | -1426.5762
2020-05-25 20:00 | -5710.72 | 6.108 | 49.527 | 59.8258 | -1673.6468
2020-05-26 21:00 | -6481.21 | 6.108 | 48.8168 | 59.8258 | -1899.4551
2020-05-27 22:00 | -6965.41 | 6.108 | 48.2976 | 59.8258 | -2041.3602
2020-05-28 23:00 | -7440.76 | 6.108 | 47.7722 | 59.8258 | -2180.6715
2020-05-30 | -9037.51 | 6.108 | 46.4081 | 59.8258 | -2648.6327
2020-05-31 01:00 | -9372.32 | 6.108 | 45.8301 | 59.8258 | -2746.7559
2020-06-01 02:00 | -9631.8 | 6.108 | 45.3881 | 59.8258 | -2822.8019
2020-06-02 03:00 | -9751.55 | 6.108 | 45.1064 | 59.8258 | -2857.8972
2020-06-03 04:00 | -9719.33 | 6.108 | 44.9668 | 59.8258 | -2848.4544
2020-06-04 05:00 | -9745.35 | 6.108 | 44.811 | 59.8258 | -2856.0802
2020-06-05 06:00 | -9623.76 | 6.108 | 44.8132 | 59.8258 | -2820.4456
2020-06-06 07:00 | -8771.56 | 6.108 | 45.3957 | 59.8258 | -2570.6905
2020-06-07 08:00 | -8179.48 | 6.108 | 45.9003 | 59.8258 | -2397.169
2020-06-08 09:00 | -8258.02 | 6.108 | 45.9371 | 59.8258 | -2420.1868
2020-06-09 10:00 | -7603.65 | 6.108 | 46.441 | 59.8258 | -2228.4098
2020-06-10 11:00 | -7442.96 | 6.108 | 46.6415 | 59.8258 | -2181.3163
2020-06-11 12:00 | -7396.21 | 6.108 | 46.7484 | 59.8258 | -2167.6152
2020-06-12 13:00 | -7139.33 | 6.108 | 46.9664 | 59.8258 | -2092.3311
2020-06-13 14:00 | -7025.72 | 6.108 | 47.0897 | 59.8258 | -2059.0353
2020-06-14 15:00 | -6853.28 | 6.108 | 47.2591 | 59.8258 | -2008.4981
2020-06-15 16:00 | -6645.23 | 6.108 | 47.4474 | 59.8258 | -1947.5247
2020-06-16 17:00 | -5272.31 | 6.108 | 48.5221 | 59.8258 | -1545.1615
2020-06-17 18:00 | -5650.56 | 6.108 | 48.4582 | 59.8258 | -1656.0157
2020-06-18 19:00 | -5922.52 | 6.108 | 48.3276 | 59.8258 | -1735.7193
2020-06-19 20:00 | -6127.07 | 6.108 | 48.1826 | 59.8258 | -1795.667
2020-06-20 21:00 | -6249.91 | 6.108 | 48.1057 | 59.8258 | -1831.6678
2020-06-21 22:00 | -6427.66 | 6.108 | 47.9842 | 59.8258 | -1883.7612
2020-06-22 23:00 | -6645.86 | 6.108 | 47.7952 | 59.8258 | -1947.7093
2020-06-24 | -7723.7 | 6.108 | 46.9636 | 59.8258 | -2263.593
2020-06-25 01:00 | -7940.57 | 6.108 | 46.6542 | 59.8258 | -2327.1513
2020-06-26 02:00 | -8063.38 | 6.108 | 46.4617 | 59.8258 | -2363.1434
2020-06-27 03:00 | -8148.1 | 6.108 | 46.333 | 59.8258 | -2387.9724
2020-06-28 04:00 | -8252.3 | 6.108 | 46.1946 | 59.8258 | -2418.5104
2020-06-29 05:00 | -8362.08 | 6.108 | 46.0366 | 59.8258 | -2450.6837
2020-06-30 06:00 | -8263.86 | 6.108 | 46.0574 | 59.8258 | -2421.8983
2020-07-01 07:00 | -8428.29 | 6.108 | 45.9049 | 59.8258 | -2470.088
2020-07-02 08:00 | -8633.49 | 6.108 | 45.6937 | 59.8258 | -2530.2262
2020-07-03 09:00 | -9222.76 | 6.108 | 45.1719 | 59.8258 | -2702.9241
2020-07-04 10:00 | -8803.36 | 6.108 | 45.3395 | 59.8258 | -2580.0101
2020-07-05 11:00 | -8444.73 | 6.108 | 45.5596 | 59.8258 | -2474.9061
2020-07-06 12:00 | -7988.17 | 6.108 | 45.9032 | 59.8258 | -2341.1015
2020-07-07 13:00 | -7920.98 | 6.108 | 45.9833 | 59.8258 | -2321.4101
2020-07-08 14:00 | -7666.83 | 6.108 | 46.1774 | 59.8258 | -2246.9261
2020-07-09 15:00 | -7650.92 | 6.108 | 46.2204 | 59.8258 | -2242.2633
2020-07-10 16:00 | -7617.08 | 6.108 | 46.2538 | 59.8258 | -2232.3458
2020-07-11 17:00 | -7851.38 | 6.108 | 46.0666 | 59.8258 | -2301.0123
2020-07-12 18:00 | -8169.55 | 6.108 | 45.7761 | 59.8258 | -2394.2588
2020-07-13 19:00 | -8745.71 | 6.108 | 45.2657 | 59.8258 | -2563.1146
2020-07-14 20:00 | -9070.99 | 6.108 | 44.8916 | 59.8258 | -2658.4447
2020-07-15 21:00 | -10018.9 | 6.108 | 44.0593 | 59.8258 | -2936.2497
2020-07-16 22:00 | -10467.1 | 6.108 | 43.5068 | 59.8258 | -3067.6042
2020-07-17 23:00 | -11573.1 | 6.108 | 42.4688 | 59.8258 | -3391.7408
2020-07-19 | -11964.9 | 6.108 | 41.891 | 59.8258 | -3506.566
2020-07-20 01:00 | -12124.2 | 6.108 | 41.5309 | 59.8258 | -3553.2523
2020-07-21 02:00 | -12361.7 | 6.108 | 41.1579 | 59.8258 | -3622.8566
2020-07-22 03:00 | -12537.8 | 6.108 | 40.8435 | 59.8258 | -3674.4665
2020-07-23 04:00 | -12648.4 | 6.108 | 40.5838 | 59.8258 | -3706.8801
2020-07-24 05:00 | -12662.3 | 6.108 | 40.4292 | 59.8258 | -3710.9538
2020-07-25 06:00 | -12597.2 | 6.108 | 40.3564 | 59.8258 | -3691.8749
2020-07-26 07:00 | -12398.7 | 6.108 | 40.4059 | 59.8258 | -3633.7003
2020-07-27 08:00 | -11925.6 | 6.108 | 40.6949 | 59.8258 | -3495.0484
2020-07-28 09:00 | -10549.1 | 6.108 | 41.7381 | 59.8258 | -3091.636
2020-07-29 10:00 | -9039.01 | 6.108 | 43.0402 | 59.8258 | -2649.0723
2020-07-30 11:00 | -7382.16 | 6.108 | 44.5717 | 59.8258 | -2163.4975
2020-07-31 12:00 | -6645.41 | 6.108 | 45.501 | 59.8258 | -1947.5774
2020-08-01 13:00 | -5583.47 | 6.108 | 46.6223 | 59.8258 | -1636.3535
2020-08-02 14:00 | -5166.34 | 6.108 | 47.2938 | 59.8258 | -1514.1048
2020-08-03 15:00 | -4836.49 | 6.108 | 47.8404 | 59.8258 | -1417.4353
2020-08-04 16:00 | -4565.42 | 6.108 | 48.2917 | 59.8258 | -1337.9925
2020-08-05 17:00 | -5817.44 | 6.108 | 47.5628 | 59.8258 | -1704.9234
2020-08-06 18:00 | -6423.73 | 6.108 | 47.1049 | 59.8258 | -1882.6094
2020-08-07 19:00 | -7242.6 | 6.108 | 46.4454 | 59.8258 | -2122.5965
2020-08-08 20:00 | -7916.89 | 6.108 | 45.8477 | 59.8258 | -2320.2114
2020-08-09 21:00 | -9014.05 | 6.108 | 44.8908 | 59.8258 | -2641.7573
2020-08-10 22:00 | -9474.18 | 6.108 | 44.3082 | 59.8258 | -2776.6081
2020-08-11 23:00 | -10557.3 | 6.108 | 43.2983 | 59.8258 | -3094.0392
2020-08-13 | -10931 | 6.108 | 42.7483 | 59.8258 | -3203.5599
2020-08-14 01:00 | -11010.6 | 6.108 | 42.4574 | 59.8258 | -3226.8883
2020-08-15 02:00 | -11046.9 | 6.108 | 42.2609 | 59.8258 | -3237.5268
2020-08-16 03:00 | -10976.6 | 6.108 | 42.1804 | 59.8258 | -3216.9239
2020-08-17 04:00 | -11035.8 | 6.108 | 42.0257 | 59.8258 | -3234.2737
2020-08-18 05:00 | -11101 | 6.108 | 41.8947 | 59.8258 | -3253.3819
2020-08-19 06:00 | -10894 | 6.108 | 41.9758 | 59.8258 | -3192.7162
2020-08-20 07:00 | -10588.4 | 6.108 | 42.1758 | 59.8258 | -3103.1537
2020-08-21 08:00 | -9456.61 | 6.108 | 43.036 | 59.8258 | -2771.4588
2020-08-22 09:00 | -8649 | 6.108 | 43.7888 | 59.8258 | -2534.7717
2020-08-23 10:00 | -7528.48 | 6.108 | 44.8057 | 59.8258 | -2206.3797
2020-08-24 11:00 | -5568.31 | 6.108 | 46.5232 | 59.8258 | -1631.9106
2020-08-25 12:00 | -3873.81 | 6.108 | 48.2082 | 59.8258 | -1135.3016
2020-08-26 13:00 | -3115.53 | 6.108 | 49.2553 | 59.8258 | -913.0717
2020-08-27 14:00 | -2568.62 | 6.108 | 50.0522 | 59.8258 | -752.7882
2020-08-28 15:00 | -2783.32 | 6.108 | 50.2287 | 59.8258 | -815.7106
2020-08-29 16:00 | -2906.05 | 6.108 | 50.361 | 59.8258 | -851.6792
2020-08-30 17:00 | -3628.2 | 6.108 | 49.9836 | 59.8258 | -1063.3205
2020-08-31 18:00 | -3934.29 | 6.108 | 49.7983 | 59.8258 | -1153.0266
2020-09-01 19:00 | -4777.61 | 6.108 | 49.2006 | 59.8258 | -1400.1793
2020-09-02 20:00 | -5520.26 | 6.108 | 48.585 | 59.8258 | -1617.8285
2020-09-03 21:00 | -6785.09 | 6.108 | 47.5399 | 59.8258 | -1988.5136
2020-09-04 22:00 | -7281.18 | 6.108 | 46.9635 | 59.8258 | -2133.9032
2020-09-05 23:00 | -8361.33 | 6.108 | 45.983 | 59.8258 | -2450.4639
2020-09-07 | -8708.5 | 6.108 | 45.469 | 59.8258 | -2552.2094
2020-09-08 01:00 | -8765.35 | 6.108 | 45.2181 | 59.8258 | -2568.8705
2020-09-09 02:00 | -8911.88 | 6.108 | 44.9617 | 59.8258 | -2611.8142
2020-09-10 03:00 | -8799.73 | 6.108 | 44.9267 | 59.8258 | -2578.9463
2020-09-11 04:00 | -8512.15 | 6.108 | 45.0634 | 59.8258 | -2494.6649
2020-09-12 05:00 | -8286.96 | 6.108 | 45.2248 | 59.8258 | -2428.6682
2020-09-13 06:00 | -7691.92 | 6.108 | 45.6846 | 59.8258 | -2254.2792
2020-09-14 07:00 | -7559.17 | 6.108 | 45.8634 | 59.8258 | -2215.374
2020-09-15 08:00 | -7169.92 | 6.108 | 46.2138 | 59.8258 | -2101.2961
2020-09-16 09:00 | -7554.87 | 6.108 | 46.0114 | 59.8258 | -2214.1138
2020-09-17 10:00 | -6997.38 | 6.108 | 46.4242 | 59.8258 | -2050.7296
2020-09-18 11:00 | -6549.52 | 6.108 | 46.8323 | 59.8258 | -1919.4748
2020-09-19 12:00 | -6633.95 | 6.108 | 46.8613 | 59.8258 | -1944.2188
2020-09-20 13:00 | -6311.04 | 6.108 | 47.1291 | 59.8258 | -1849.5832
2020-09-21 14:00 | -6334.7 | 6.108 | 47.1591 | 59.8258 | -1856.5173
2020-09-22 15:00 | -6317.81 | 6.108 | 47.2079 | 59.8258 | -1851.5673
2020-09-23 16:00 | -5368.3 | 6.108 | 47.9335 | 59.8258 | -1573.2934
2020-09-24 17:00 | -5011.01 | 6.108 | 48.3381 | 59.8258 | -1468.5821
2020-09-25 18:00 | -4779.04 | 6.108 | 48.641 | 59.8258 | -1400.5984
2020-09-26 19:00 | -5192.04 | 6.108 | 48.4371 | 59.8258 | -1521.6367
2020-09-27 20:00 | -5386.79 | 6.108 | 48.3171 | 59.8258 | -1578.7123
2020-09-28 21:00 | -6303.69 | 6.108 | 47.6591 | 59.8258 | -1847.4292
2020-09-29 22:00 | -6564.64 | 6.108 | 47.3687 | 59.8258 | -1923.9061
2020-09-30 23:00 | -7415.45 | 6.108 | 46.6559 | 59.8258 | -2173.2539
2020-10-02 | -7647.17 | 6.108 | 46.3373 | 59.8258 | -2241.1643
2020-10-03 01:00 | -7834.94 | 6.108 | 46.0854 | 59.8258 | -2296.1942
2020-10-04 02:00 | -7850.31 | 6.108 | 45.986 | 59.8258 | -2300.6988
2020-10-05 03:00 | -7939.96 | 6.108 | 45.8679 | 59.8258 | -2326.9726
2020-10-06 04:00 | -7713 | 6.108 | 45.9767 | 59.8258 | -2260.4572
2020-10-07 05:00 | -7393.22 | 6.108 | 46.2073 | 59.8258 | -2166.7389
2020-10-08 06:00 | -6847.64 | 6.108 | 46.6404 | 59.8258 | -2006.8452
2020-10-09 07:00 | -7037.13 | 6.108 | 46.5773 | 59.8258 | -2062.3792
2020-10-10 08:00 | -7150.23 | 6.108 | 46.4994 | 59.8258 | -2095.5256
2020-10-11 09:00 | -7680.69 | 6.108 | 46.0967 | 59.8258 | -2250.988
2020-10-12 10:00 | -6522.11 | 6.108 | 46.894 | 59.8258 | -1911.4418
2020-10-13 11:00 | -4957.35 | 6.108 | 48.1852 | 59.8258 | -1452.8559
2020-10-14 12:00 | -3142.13 | 6.108 | 49.8148 | 59.8258 | -920.8674
2020-10-15 13:00 | -2741.5 | 6.108 | 50.5024 | 59.8258 | -803.4543
2020-10-16 14:00 | -1489.14 | 4.7885 | 51.4164 | 59.8258 | -436.4239
2020-10-17 15:00 | -1977.49 | 6.108 | 51.7437 | 59.8258 | -579.5451
2020-10-18 16:00 | -2445.09 | 6.108 | 51.5906 | 59.8258 | -716.5851
2020-10-19 17:00 | -2875.48 | 6.108 | 51.3476 | 59.8258 | -842.72
2020-10-20 18:00 | -3852.92 | 6.108 | 50.6317 | 59.8258 | -1129.1794
2020-10-21 19:00 | -4766.32 | 6.108 | 49.8687 | 59.8258 | -1396.8705
2020-10-22 20:00 | -5515.94 | 6.108 | 49.1504 | 59.8258 | -1616.5624
2020-10-23 21:00 | -6755.14 | 6.108 | 48.0752 | 59.8258 | -1979.7361
2020-10-24 22:00 | -7082.15 | 6.108 | 47.5895 | 59.8258 | -2075.5733
2020-10-25 23:00 | -7802.76 | 6.108 | 46.8632 | 59.8258 | -2286.7632
2020-10-27 | -8158.75 | 6.108 | 46.3773 | 59.8258 | -2391.0936
2020-10-28 01:00 | -8275.23 | 6.108 | 46.0936 | 59.8258 | -2425.2305
2020-10-29 02:00 | -8362.25 | 6.108 | 45.8657 | 59.8258 | -2450.7336
2020-10-30 03:00 | -8415.28 | 6.108 | 45.705 | 59.8258 | -2466.2751
2020-10-31 04:00 | -8289.93 | 6.108 | 45.691 | 59.8258 | -2429.5387
2020-11-01 05:00 | -8168.5 | 6.108 | 45.7167 | 59.8258 | -2393.951
2020-11-02 06:00 | -7975.55 | 6.108 | 45.8217 | 59.8258 | -2337.403
2020-11-03 07:00 | -7281.34 | 6.108 | 46.3326 | 59.8258 | -2133.9501
2020-11-04 08:00 | -6946.13 | 6.108 | 46.6633 | 59.8258 | -2035.7098
2020-11-05 09:00 | -7622.52 | 6.108 | 46.2499 | 59.8258 | -2233.9401
2020-11-06 10:00 | -7032.43 | 6.108 | 46.6404 | 59.8258 | -2061.0018
2020-11-07 11:00 | -6211.78 | 6.108 | 47.3068 | 59.8258 | -1820.493
2020-11-08 12:00 | -5215.35 | 6.108 | 48.1956 | 59.8258 | -1528.4682
2020-11-09 13:00 | -4812.96 | 6.108 | 48.6876 | 59.8258 | -1410.5393
2020-11-10 14:00 | -4536.33 | 6.108 | 49.0398 | 59.8258 | -1329.4671
2020-11-11 15:00 | -3893.96 | 6.108 | 49.6655 | 59.8258 | -1141.207
2020-11-12 16:00 | -3668.06 | 6.108 | 50.021 | 59.8258 | -1075.0023
2020-11-13 17:00 | -1958.31 | 6.108 | 51.4579 | 59.8258 | -573.924
2020-11-14 18:00 | -2250.47 | 6.108 | 51.5736 | 59.8258 | -659.5477
2020-11-15 19:00 | -2536.9 | 6.108 | 51.5387 | 59.8258 | -743.492
2020-11-16 20:00 | -2922.54 | 6.108 | 51.3438 | 59.8258 | -856.5119
2020-11-17 21:00 | -3196.53 | 6.108 | 51.2111 | 59.8258 | -936.8105
2020-11-18 22:00 | -3759.1 | 6.108 | 50.848 | 59.8258 | -1101.6835
2020-11-19 23:00 | -4312.11 | 6.108 | 50.4037 | 59.8258 | -1263.7547
2020-11-21 | -6243.89 | 6.108 | 48.8889 | 59.8258 | -1829.9035
2020-11-22 01:00 | -6683.26 | 6.108 | 48.2809 | 59.8258 | -1958.6702
2020-11-23 02:00 | -7037.71 | 6.108 | 47.8139 | 59.8258 | -2062.5492
2020-11-24 03:00 | -7220.31 | 6.108 | 47.5187 | 59.8258 | -2116.064
2020-11-25 04:00 | -7329.32 | 6.108 | 47.2985 | 59.8258 | -2148.0117
2020-11-26 05:00 | -7600.57 | 6.108 | 46.9558 | 59.8258 | -2227.5072
2020-11-27 06:00 | -7679.67 | 6.108 | 46.7772 | 59.8258 | -2250.6891
2020-11-28 07:00 | -6972.91 | 6.108 | 47.2072 | 59.8258 | -2043.5582
2020-11-29 08:00 | -6158.35 | 6.108 | 47.8386 | 59.8258 | -1804.8342
2020-11-30 09:00 | -5700.38 | 6.108 | 48.2872 | 59.8258 | -1670.6165
2020-12-01 10:00 | -4648.71 | 6.108 | 49.1725 | 59.8258 | -1362.4024
2020-12-02 11:00 | -3333.67 | 6.108 | 50.345 | 59.8258 | -977.0022
2020-12-03 12:00 | -2293.26 | 6.108 | 51.4246 | 59.8258 | -672.0882
2020-12-04 13:00 | -1669.81 | 5.3055 | 52.0153 | 59.8258 | -489.373
2020-12-05 14:00 | -1333.37 | 4.2781 | 52.3013 | 59.8258 | -390.7722
2020-12-06 15:00 | -1057.66 | 3.5012 | 52.5817 | 59.8258 | -309.9695
2020-12-07 16:00 | -1524.63 | 5.0445 | 52.7957 | 59.8258 | -446.8249
2020-12-08 17:00 | -1570.98 | 5.0252 | 52.8347 | 59.8258 | -460.4088
2020-12-09 18:00 | -2884.4 | 6.108 | 52.1856 | 59.8258 | -845.3342
2020-12-10 19:00 | -3863.14 | 6.108 | 51.3539 | 59.8258 | -1132.1746
2020-12-11 20:00 | -4551.82 | 6.108 | 50.6703 | 59.8258 | -1334.0068
2020-12-12 21:00 | -5184.75 | 6.108 | 50.031 | 59.8258 | -1519.5002
2020-12-13 22:00 | -5680.54 | 6.108 | 49.4844 | 59.8258 | -1664.8019
2020-12-14 23:00 | -6254.3 | 6.108 | 48.8641 | 59.8258 | -1832.9544
2020-12-16 | -7898.98 | 6.108 | 47.4419 | 59.8258 | -2314.9625
2020-12-17 01:00 | -8300.19 | 6.108 | 46.7935 | 59.8258 | -2432.5456
2020-12-18 02:00 | -8479.89 | 6.108 | 46.3871 | 59.8258 | -2485.2104
2020-12-19 03:00 | -8668.48 | 6.108 | 46.042 | 59.8258 | -2540.4807
2020-12-20 04:00 | -9113.95 | 6.108 | 45.5181 | 59.8258 | -2671.0351
2020-12-21 05:00 | -9440.46 | 6.108 | 45.0533 | 59.8258 | -2766.7257
2020-12-22 06:00 | -9888.92 | 6.108 | 44.5355 | 59.8258 | -2898.1564
2020-12-23 07:00 | -8892.01 | 6.108 | 45.0919 | 59.8258 | -2605.9909
2020-12-24 08:00 | -7570.33 | 6.108 | 46.0757 | 59.8258 | -2218.6447
2020-12-25 09:00 | -6656.26 | 6.108 | 46.904 | 59.8258 | -1950.7572
2020-12-26 10:00 | -5174.3 | 6.108 | 48.1801 | 59.8258 | -1516.4376
2020-12-27 11:00 | -3963.07 | 6.108 | 49.3611 | 59.8258 | -1161.4612
2020-12-28 12:00 | -2707.26 | 6.108 | 50.6446 | 59.8258 | -793.4196
2020-12-29 13:00 | -2752.58 | 6.108 | 50.9793 | 59.8258 | -806.7016
2020-12-30 14:00 | -2799.4 | 6.108 | 51.1619 | 59.8258 | -820.4232
2020-12-31 15:00 | -3323.05 | 6.108 | 50.9174 | 59.8258 | -973.8898
2021-01-01 16:00 | -3584.98 | 6.108 | 50.7731 | 59.8258 | -1050.6539
2021-01-02 17:00 | -2785.82 | 6.108 | 51.3905 | 59.8258 | -816.4432
2021-01-03 18:00 | -3677.44 | 6.108 | 50.8674 | 59.8258 | -1077.7513
2021-01-04 19:00 | -4512.81 | 6.108 | 50.2233 | 59.8258 | -1322.5741
2021-01-05 20:00 | -5150.16 | 6.108 | 49.6275 | 59.8258 | -1509.3629
2021-01-06 21:00 | -5780.45 | 6.108 | 49.0352 | 59.8258 | -1694.0827
2021-01-07 22:00 | -5939.67 | 6.108 | 48.769 | 59.8258 | -1740.7454
2021-01-08 23:00 | -5909.86 | 6.108 | 48.6556 | 59.8258 | -1732.009
2021-01-10 | -6844.57 | 6.108 | 47.8748 | 59.8258 | -2005.9455
2021-01-11 01:00 | -7152.31 | 6.108 | 47.4624 | 59.8258 | -2096.1351
2021-01-12 02:00 | -7448.52 | 6.108 | 47.0868 | 59.8258 | -2182.9457
2021-01-13 03:00 | -7637.79 | 6.108 | 46.8229 | 59.8258 | -2238.4153
2021-01-14 04:00 | -7367.14 | 6.108 | 46.916 | 59.8258 | -2159.0956
2021-01-15 05:00 | -7164.64 | 6.108 | 47.0093 | 59.8258 | -2099.7487
2021-01-16 06:00 | -6570.8 | 6.108 | 47.4491 | 59.8258 | -1925.7114
2021-01-17 07:00 | -6464.59 | 6.108 | 47.5927 | 59.8258 | -1894.5843
2021-01-18 08:00 | -6109.22 | 6.108 | 47.901 | 59.8258 | -1790.4356
2021-01-19 09:00 | -6456.72 | 6.108 | 47.7098 | 59.8258 | -1892.2778
2021-01-20 10:00 | -5986.61 | 6.108 | 48.0426 | 59.8258 | -1754.5022
2021-01-21 11:00 | -5528.32 | 6.108 | 48.4216 | 59.8258 | -1620.1907
2021-01-22 12:00 | -5105.08 | 6.108 | 48.8063 | 59.8258 | -1496.1513
2021-01-23 13:00 | -5046.64 | 6.108 | 48.9314 | 59.8258 | -1479.0242
2021-01-24 14:00 | -5176.49 | 6.108 | 48.8754 | 59.8258 | -1517.0795
2021-01-25 15:00 | -5294.95 | 6.108 | 48.8049 | 59.8258 | -1551.7967
2021-01-26 16:00 | -4548.91 | 6.108 | 49.3625 | 59.8258 | -1333.1539
2021-01-27 17:00 | -4523.75 | 6.108 | 49.4767 | 59.8258 | -1325.7803
2021-01-28 18:00 | -4373.97 | 6.108 | 49.6428 | 59.8258 | -1281.8841
2021-01-29 19:00 | -5000.5 | 6.108 | 49.2263 | 59.8258 | -1465.5019
2021-01-30 20:00 | -5390.84 | 6.108 | 48.8966 | 59.8258 | -1579.8992
2021-01-31 21:00 | -6480.32 | 6.108 | 48.0333 | 59.8258 | -1899.1943
2021-02-01 22:00 | -6822.69 | 6.108 | 47.6049 | 59.8258 | -1999.5331
2021-02-02 23:00 | -7561.47 | 6.108 | 46.9056 | 59.8258 | -2216.0481
2021-02-04 | -7818.56 | 6.108 | 46.5282 | 59.8258 | -2291.3937
2021-02-05 01:00 | -8149.94 | 6.108 | 46.1313 | 59.8258 | -2388.5116
2021-02-06 02:00 | -8515.07 | 6.108 | 45.7163 | 59.8258 | -2495.5207
2021-02-07 03:00 | -8797.41 | 6.108 | 45.3692 | 59.8258 | -2578.2664
2021-02-08 04:00 | -8768.5 | 6.108 | 45.2489 | 59.8258 | -2569.7937
2021-02-09 05:00 | -8835.94 | 6.108 | 45.1058 | 59.8258 | -2589.5584
2021-02-10 06:00 | -8536 | 6.108 | 45.2396 | 59.8258 | -2501.6547
2021-02-11 07:00 | -8781.13 | 6.108 | 45.0178 | 59.8258 | -2573.4952
2021-02-12 08:00 | -8891.59 | 6.108 | 44.8535 | 59.8258 | -2605.8678
2021-02-13 09:00 | -9482.45 | 6.108 | 44.3346 | 59.8258 | -2779.0318
2021-02-14 10:00 | -8560.13 | 6.108 | 44.8819 | 59.8258 | -2508.7265
2021-02-15 11:00 | -8009.23 | 6.108 | 45.3187 | 59.8258 | -2347.2736
2021-02-16 12:00 | -6723.58 | 6.108 | 46.3388 | 59.8258 | -1970.4868
2021-02-17 13:00 | -6424.41 | 6.108 | 46.7384 | 59.8258 | -1882.8087
2021-02-18 14:00 | -7322.61 | 6.108 | 46.191 | 59.8258 | -2146.0451
2021-02-19 15:00 | -7140.46 | 6.108 | 46.2869 | 59.8258 | -2092.6623
2021-02-20 16:00 | -7016.51 | 6.108 | 46.3816 | 59.8258 | -2056.3361
2021-02-21 17:00 | -7488.75 | 6.108 | 46.0493 | 59.8258 | -2194.736
2021-02-22 18:00 | -7800.77 | 6.108 | 45.7281 | 59.8258 | -2286.18
2021-02-23 19:00 | -8440.25 | 6.108 | 45.1435 | 59.8258 | -2473.5931
2021-02-24 20:00 | -8805.36 | 6.108 | 44.7378 | 59.8258 | -2580.5963
2021-02-25 21:00 | -9804.81 | 6.108 | 43.8637 | 59.8258 | -2873.5062
2021-02-26 22:00 | -10354.7 | 6.108 | 43.2217 | 59.8258 | -3034.663
2021-02-27 23:00 | -11239.3 | 6.108 | 42.3325 | 59.8258 | -3293.9137
2021-03-01 | -11678 | 6.108 | 41.7221 | 59.8258 | -3422.484
2021-03-02 01:00 | -11941 | 6.108 | 41.2697 | 59.8258 | -3499.5616
2021-03-03 02:00 | -11999.1 | 6.108 | 41.0143 | 59.8258 | -3516.5891
2021-03-04 03:00 | -12122.3 | 6.108 | 40.7562 | 59.8258 | -3552.6954
2021-03-05 04:00 | -12158.9 | 6.108 | 40.5691 | 59.8258 | -3563.4218
2021-03-06 05:00 | -12121.9 | 6.108 | 40.4678 | 59.8258 | -3552.5782
2021-03-07 06:00 | -11939.9 | 6.108 | 40.498 | 59.8258 | -3499.2393
2021-03-08 07:00 | -11758.2 | 6.108 | 40.566 | 59.8258 | -3445.9883
2021-03-09 08:00 | -10481.9 | 6.108 | 41.4774 | 59.8258 | -3071.9416
2021-03-10 09:00 | -9633.49 | 6.108 | 42.2455 | 59.8258 | -2823.2972
2021-03-11 10:00 | -8109.06 | 6.108 | 43.5564 | 59.8258 | -2376.5309
2021-03-12 11:00 | -6671.25 | 6.108 | 44.92 | 59.8258 | -1955.1504
2021-03-13 12:00 | -5523.45 | 6.108 | 46.1335 | 59.8258 | -1618.7634
2021-03-14 13:00 | -4916.71 | 6.108 | 46.9565 | 59.8258 | -1440.9455
2021-03-15 14:00 | -4490.38 | 6.108 | 47.5866 | 59.8258 | -1316.0005
2021-03-16 15:00 | -4382.24 | 6.108 | 47.9424 | 59.8258 | -1284.3078
2021-03-17 16:00 | -4341.79 | 6.108 | 48.1799 | 59.8258 | -1272.453
2021-03-18 17:00 | -5763.49 | 6.108 | 47.2736 | 59.8258 | -1689.1122
2021-03-19 18:00 | -6781.44 | 6.108 | 46.4421 | 59.8258 | -1987.4439
2021-03-20 19:00 | -7714.45 | 6.108 | 45.6057 | 59.8258 | -2260.8821
2021-03-21 20:00 | -8380.54 | 6.108 | 44.9292 | 59.8258 | -2456.0938
2021-03-22 21:00 | -9555.62 | 6.108 | 43.865 | 59.8258 | -2800.4758
2021-03-23 22:00 | -10089.4 | 6.108 | 43.1772 | 59.8258 | -2956.9113
2021-03-24 23:00 | -11221.7 | 6.108 | 42.0811 | 59.8258 | -3288.7556
2021-03-26 | -11635.5 | 6.108 | 41.4555 | 59.8258 | -3410.0284
2021-03-27 01:00 | -11870.6 | 6.108 | 41.0108 | 59.8258 | -3478.9294
2021-03-28 02:00 | -11928.9 | 6.108 | 40.7429 | 59.8258 | -3496.0155
2021-03-29 03:00 | -11987.3 | 6.108 | 40.5228 | 59.8258 | -3513.1308
2021-03-30 04:00 | -11903.2 | 6.108 | 40.4261 | 59.8258 | -3488.4836
2021-03-31 05:00 | -11688.4 | 6.108 | 40.4882 | 59.8258 | -3425.5319
2021-04-01 06:00 | -11311.7 | 6.108 | 40.7192 | 59.8258 | -3315.132
2021-04-02 07:00 | -11054.2 | 6.108 | 40.9117 | 59.8258 | -3239.6662
2021-04-03 08:00 | -9974.27 | 6.108 | 41.7309 | 59.8258 | -2923.17
2021-04-04 09:00 | -8992.04 | 6.108 | 42.61 | 59.8258 | -2635.3068
2021-04-05 10:00 | -7162.05 | 6.108 | 44.1814 | 59.8258 | -2098.9897
2021-04-06 11:00 | -5305.47 | 6.108 | 45.9261 | 59.8258 | -1554.8798
2021-04-07 12:00 | -3790.09 | 6.108 | 47.5117 | 59.8258 | -1110.7657
2021-04-08 13:00 | -3644.89 | 6.108 | 48.0965 | 59.8258 | -1068.2118
2021-04-09 14:00 | -3518.4 | 6.108 | 48.5118 | 59.8258 | -1031.1413
2021-04-10 15:00 | -4570.15 | 6.108 | 47.9769 | 59.8258 | -1339.3788
2021-04-11 16:00 | -4328.71 | 6.108 | 48.2116 | 59.8258 | -1268.6197
2021-04-12 17:00 | -4363.65 | 6.108 | 48.292 | 59.8258 | -1278.8596
2021-04-13 18:00 | -4502.95 | 6.108 | 48.2803 | 59.8258 | -1319.6844
2021-04-14 19:00 | -5085.86 | 6.108 | 47.9123 | 59.8258 | -1490.5184
2021-04-15 20:00 | -5393.14 | 6.108 | 47.6709 | 59.8258 | -1580.5733
2021-04-16 21:00 | -6383.8 | 6.108 | 46.9364 | 59.8258 | -1870.9071
2021-04-17 22:00 | -6728.88 | 6.108 | 46.5661 | 59.8258 | -1972.0401
2021-04-18 23:00 | -7690.16 | 6.108 | 45.7424 | 59.8258 | -2253.7634
2021-04-20 | -8240.32 | 6.108 | 45.1392 | 59.8258 | -2414.9994
2021-04-21 01:00 | -8465.21 | 6.108 | 44.7869 | 59.8258 | -2480.9082
2021-04-22 02:00 | -8717.67 | 6.108 | 44.4549 | 59.8258 | -2554.8969
2021-04-23 03:00 | -8747.93 | 6.108 | 44.323 | 59.8258 | -2563.7652
2021-04-24 04:00 | -8710.36 | 6.108 | 44.2651 | 59.8258 | -2552.7545
2021-04-25 05:00 | -8656.38 | 6.108 | 44.2559 | 59.8258 | -2536.9345
2021-04-26 06:00 | -8599.99 | 6.108 | 44.2651 | 59.8258 | -2520.4083
2021-04-27 07:00 | -8059.64 | 6.108 | 44.652 | 59.8258 | -2362.0473
2021-04-28 08:00 | -7823.8 | 6.108 | 44.8788 | 59.8258 | -2292.9294
2021-04-29 09:00 | -8707.22 | 6.108 | 44.2662 | 59.8258 | -2551.8343
2021-04-30 10:00 | -8649.77 | 6.108 | 44.192 | 59.8258 | -2534.9973
2021-05-01 11:00 | -8301 | 6.108 | 44.3827 | 59.8258 | -2432.783
2021-05-02 12:00 | -7876.5 | 6.108 | 44.6972 | 59.8258 | -2308.3743
2021-05-03 13:00 | -7705.97 | 6.108 | 44.8438 | 59.8258 | -2258.3969
2021-05-04 14:00 | -7691.79 | 6.108 | 44.854 | 59.8258 | -2254.2411
2021-05-05 15:00 | -7465.49 | 6.108 | 45.0279 | 59.8258 | -2187.9191
2021-05-06 16:00 | -7358.71 | 6.108 | 45.1326 | 59.8258 | -2156.625
2021-05-07 17:00 | -5985.12 | 6.108 | 46.1882 | 59.8258 | -1754.0655
2021-05-08 18:00 | -6340.86 | 6.108 | 46.1132 | 59.8258 | -1858.3226
2021-05-09 19:00 | -6710.83 | 6.108 | 45.8916 | 59.8258 | -1966.7501
2021-05-10 20:00 | -6993.69 | 6.108 | 45.6595 | 59.8258 | -2049.6482
2021-05-11 21:00 | -7193.08 | 6.108 | 45.5017 | 59.8258 | -2108.0837
2021-05-12 22:00 | -7332.29 | 6.108 | 45.3921 | 59.8258 | -2148.8821
2021-05-13 23:00 | -7526.02 | 6.108 | 45.219 | 59.8258 | -2205.6587
2021-05-15 | -8857.59 | 6.108 | 44.1857 | 59.8258 | -2595.9034
2021-05-16 01:00 | -9066.39 | 6.108 | 43.8365 | 59.8258 | -2657.0966
2021-05-17 02:00 | -9219.73 | 6.108 | 43.5945 | 59.8258 | -2702.0361
2021-05-18 03:00 | -9273.67 | 6.108 | 43.4672 | 59.8258 | -2717.8444
2021-05-19 04:00 | -9444.67 | 6.108 | 43.2619 | 59.8258 | -2767.9595
2021-05-20 05:00 | -9625.78 | 6.108 | 43.0212 | 59.8258 | -2821.0376
2021-05-21 06:00 | -9824.59 | 6.108 | 42.7863 | 59.8258 | -2879.3031
2021-05-22 07:00 | -9022.92 | 6.108 | 43.2996 | 59.8258 | -2644.3568
2021-05-23 08:00 | -7895.01 | 6.108 | 44.1912 | 59.8258 | -2313.799
2021-05-24 09:00 | -7763.83 | 6.108 | 44.4552 | 59.8258 | -2275.354
2021-05-25 10:00 | -6924.61 | 6.108 | 45.1735 | 59.8258 | -2029.4029
2021-05-26 11:00 | -6624.34 | 6.108 | 45.5532 | 59.8258 | -1941.4024
2021-05-27 12:00 | -6520.71 | 6.108 | 45.7829 | 59.8258 | -1911.0315
2021-05-28 13:00 | -6050.65 | 6.108 | 46.2378 | 59.8258 | -1773.2705
2021-05-29 14:00 | -5134.91 | 6.108 | 47.0531 | 59.8258 | -1504.8936
2021-05-30 15:00 | -3883.01 | 6.108 | 48.2149 | 59.8258 | -1137.9979
2021-05-31 16:00 | -4711.67 | 6.108 | 47.8973 | 59.8258 | -1380.8542
2021-06-01 17:00 | -3856.47 | 6.108 | 48.6132 | 59.8258 | -1130.2198
2021-06-02 18:00 | -4971.32 | 6.108 | 47.9754 | 59.8258 | -1456.9501
2021-06-03 19:00 | -5656.61 | 6.108 | 47.4701 | 59.8258 | -1657.7887
2021-06-04 20:00 | -6191.45 | 6.108 | 46.9877 | 59.8258 | -1814.5349
2021-06-05 21:00 | -6595.18 | 6.108 | 46.5839 | 59.8258 | -1932.8565
2021-06-06 22:00 | -7052.13 | 6.108 | 46.1513 | 59.8258 | -2066.7753
2021-06-07 23:00 | -7537.5 | 6.108 | 45.6586 | 59.8258 | -2209.0232
2021-06-09 | -8956.5 | 6.108 | 44.4719 | 59.8258 | -2624.891
2021-06-10 01:00 | -9259.16 | 6.108 | 43.9839 | 59.8258 | -2713.5919
2021-06-11 02:00 | -9497.1 | 6.108 | 43.6074 | 59.8258 | -2783.3253
2021-06-12 03:00 | -9560.37 | 6.108 | 43.3918 | 59.8258 | -2801.8679
2021-06-13 04:00 | -9692.63 | 6.108 | 43.1612 | 59.8258 | -2840.6294
2021-06-14 05:00 | -9663.85 | 6.108 | 43.0478 | 59.8258 | -2832.1949
2021-06-15 06:00 | -9520.53 | 6.108 | 43.081 | 59.8258 | -2790.1919
2021-06-16 07:00 | -9288.1 | 6.108 | 43.212 | 59.8258 | -2722.0734
2021-06-17 08:00 | -8422.28 | 6.108 | 43.8449 | 59.8258 | -2468.3266
2021-06-18 09:00 | -7649.51 | 6.108 | 44.5157 | 59.8258 | -2241.8501
2021-06-19 10:00 | -6886.94 | 6.108 | 45.2266 | 59.8258 | -2018.3629
2021-06-20 11:00 | -6030.73 | 6.108 | 46.0366 | 59.8258 | -1767.4325
2021-06-21 12:00 | -5604.55 | 6.108 | 46.5783 | 59.8258 | -1642.5315
2021-06-22 13:00 | -4864.87 | 6.108 | 47.3316 | 59.8258 | -1425.7527
2021-06-23 14:00 | -3775.09 | 6.108 | 48.3721 | 59.8258 | -1106.3697
2021-06-24 15:00 | -2815.16 | 6.108 | 49.382 | 59.8258 | -825.042
2021-06-25 16:00 | -2486.93 | 6.108 | 49.9499 | 59.8258 | -728.8472
2021-06-26 17:00 | -3442.88 | 6.108 | 49.4796 | 59.8258 | -1009.0085
2021-06-27 18:00 | -4444.67 | 6.108 | 48.7898 | 59.8258 | -1302.6042
2021-06-28 19:00 | -5396.35 | 6.108 | 48.0305 | 59.8258 | -1581.5141
2021-06-29 20:00 | -6125.02 | 6.108 | 47.3685 | 59.8258 | -1795.0662
2021-06-30 21:00 | -7412.44 | 6.108 | 46.2494 | 59.8258 | -2172.3717
2021-07-01 22:00 | -7725.65 | 6.108 | 45.7469 | 59.8258 | -2264.1645
2021-07-02 23:00 | -8346.84 | 6.108 | 45.0875 | 59.8258 | -2446.2173
2021-07-04 | -8465.94 | 6.108 | 44.8145 | 59.8258 | -2481.1221
2021-07-05 01:00 | -8666.53 | 6.108 | 44.5275 | 59.8258 | -2539.9092
2021-07-06 02:00 | -8984.93 | 6.108 | 44.1585 | 59.8258 | -2633.223
2021-07-07 03:00 | -9054.51 | 6.108 | 43.9677 | 59.8258 | -2653.6149
2021-07-08 04:00 | -9009.61 | 6.108 | 43.8841 | 59.8258 | -2640.456
2021-07-09 05:00 | -8897.24 | 6.108 | 43.8984 | 59.8258 | -2607.5236
2021-07-10 06:00 | -8573.73 | 6.108 | 44.1008 | 59.8258 | -2512.7122
2021-07-11 07:00 | -8328.48 | 6.108 | 44.2918 | 59.8258 | -2440.8365
2021-07-12 08:00 | -7336.87 | 6.108 | 45.0608 | 59.8258 | -2150.2243
2021-07-13 09:00 | -6388.89 | 6.108 | 45.9184 | 59.8258 | -1872.3988
2021-07-14 10:00 | -4597.72 | 6.108 | 47.4663 | 59.8258 | -1347.4587
2021-07-15 11:00 | -3205.61 | 6.108 | 48.8658 | 59.8258 | -939.4716
2021-07-16 12:00 | -1786.81 | 5.8902 | 50.2778 | 59.8258 | -523.6623
2021-07-17 13:00 | -1320.18 | 4.2682 | 50.6885 | 59.8258 | -386.9066
2021-07-18 14:00 | -918.782 | 3.1275 | 51.1052 | 59.8258 | -269.2684
2021-07-19 15:00 | -809.726 | 2.8862 | 51.4642 | 59.8258 | -237.3073
2021-07-20 16:00 | -841.407 | 3.0034 | 51.6995 | 59.8258 | -246.592
2021-07-21 17:00 | -1329.34 | 4.5413 | 51.8218 | 59.8258 | -389.5911
2021-07-22 18:00 | -1567.61 | 5.1397 | 51.8492 | 59.8258 | -459.4211
2021-07-23 19:00 | -2019.16 | 6.108 | 51.808 | 59.8258 | -591.7574
2021-07-24 20:00 | -2425.43 | 6.108 | 51.5325 | 59.8258 | -710.8234
2021-07-25 21:00 | -3324.73 | 6.108 | 50.8624 | 59.8258 | -974.3822
2021-07-26 22:00 | -3625 | 6.108 | 50.5405 | 59.8258 | -1062.3826
2021-07-27 23:00 | -4539.44 | 6.108 | 49.7836 | 59.8258 | -1330.3785
2021-07-29 | -4781.14 | 6.108 | 49.4494 | 59.8258 | -1401.2138
2021-07-30 01:00 | -4942.67 | 6.108 | 49.2128 | 59.8258 | -1448.5536
2021-07-31 02:00 | -5004.31 | 6.108 | 49.0824 | 59.8258 | -1466.6185
2021-08-01 03:00 | -5031.56 | 6.108 | 49.007 | 59.8258 | -1474.6047
2021-08-02 04:00 | -4850.75 | 6.108 | 49.1004 | 59.8258 | -1421.6145
2021-08-03 05:00 | -4548.43 | 6.108 | 49.3393 | 59.8258 | -1333.0132
2021-08-04 06:00 | -4006.59 | 6.108 | 49.7957 | 59.8258 | -1174.2156
2021-08-05 07:00 | -3832.01 | 6.108 | 50.0333 | 59.8258 | -1123.0513
2021-08-06 08:00 | -3655.44 | 6.108 | 50.2521 | 59.8258 | -1071.3037
2021-08-07 09:00 | -3973.58 | 6.108 | 50.1002 | 59.8258 | -1164.5413
2021-08-08 10:00 | -3428.72 | 6.108 | 50.5222 | 59.8258 | -1004.8586
2021-08-09 11:00 | -3044.21 | 6.108 | 50.9034 | 59.8258 | -892.1699
2021-08-10 12:00 | -2824.4 | 6.108 | 51.1734 | 59.8258 | -827.7499
2021-08-11 13:00 | -2666.24 | 6.108 | 51.3793 | 59.8258 | -781.3978
2021-08-12 14:00 | -2419.74 | 6.108 | 51.6386 | 59.8258 | -709.1558
2021-08-13 15:00 | -2193.84 | 6.108 | 51.9035 | 59.8258 | -642.951
2021-08-14 16:00 | -1446.79 | 4.5723 | 52.1881 | 59.8258 | -424.0123
2021-08-15 17:00 | -1250.91 | 4.09 | 52.3994 | 59.8258 | -366.6055
2021-08-16 18:00 | -1118.04 | 3.7132 | 52.5541 | 59.8258 | -327.6652
2021-08-17 19:00 | -1601.7 | 5.2765 | 52.6607 | 59.8258 | -469.4119
2021-08-18 20:00 | -1939.89 | 6.108 | 52.6301 | 59.8258 | -568.5256
2021-08-19 21:00 | -3054.92 | 6.108 | 51.8121 | 59.8258 | -895.3087
2021-08-20 22:00 | -3345.34 | 6.108 | 51.4745 | 59.8258 | -980.4224
2021-08-21 23:00 | -4186.7 | 6.108 | 50.7587 | 59.8258 | -1227.0006
2021-08-23 | -4384.09 | 6.108 | 50.4633 | 59.8258 | -1284.8499
2021-08-24 01:00 | -4480.24 | 6.108 | 50.2867 | 59.8258 | -1313.0287
2021-08-25 02:00 | -4525.61 | 6.108 | 50.1821 | 59.8258 | -1326.3254
2021-08-26 03:00 | -4483.67 | 6.108 | 50.1727 | 59.8258 | -1314.034
2021-08-27 04:00 | -4372.05 | 6.108 | 50.2245 | 59.8258 | -1281.3214
2021-08-28 05:00 | -4233.56 | 6.108 | 50.3263 | 59.8258 | -1240.734
2021-08-29 06:00 | -3852.51 | 6.108 | 50.6204 | 59.8258 | -1129.0592
2021-08-30 07:00 | -3720.48 | 6.108 | 50.7733 | 59.8258 | -1090.3651
2021-08-31 08:00 | -3576.72 | 6.108 | 50.9257 | 59.8258 | -1048.2332
2021-09-01 09:00 | -3768.86 | 6.108 | 50.8358 | 59.8258 | -1104.5438
2021-09-02 10:00 | -3100.44 | 6.108 | 51.3423 | 59.8258 | -908.6493
2021-09-03 11:00 | -2537.1 | 6.108 | 51.867 | 59.8258 | -743.5506
2021-09-04 12:00 | -1462.19 | 4.6205 | 52.4524 | 59.8258 | -428.5256
2021-09-05 13:00 | -1575.96 | 5.0947 | 52.7071 | 59.8258 | -461.8683
2021-09-06 14:00 | -1460.25 | 4.6715 | 52.8104 | 59.8258 | -427.957
2021-09-07 15:00 | -1524.11 | 4.9107 | 52.9253 | 59.8258 | -446.6725
2021-09-08 16:00 | -983.288 | 3.1814 | 53.002 | 59.8258 | -288.1733
2021-09-09 17:00 | -685.671 | 2.4268 | 53.2552 | 59.8258 | -200.9503
2021-09-10 18:00 | -529.338 | 2.0151 | 53.4636 | 59.8258 | -155.1337
2021-09-11 19:00 | -783.257 | 2.8387 | 53.5143 | 59.8258 | -229.55
2021-09-12 20:00 | -869.056 | 3.0215 | 53.5173 | 59.8258 | -254.6952
2021-09-13 21:00 | -1540.34 | 5.0922 | 53.52 | 59.8258 | -451.4291
2021-09-14 22:00 | -1869.15 | 5.9153 | 53.4328 | 59.8258 | -547.7938
2021-09-15 23:00 | -2887.96 | 6.108 | 52.6807 | 59.8258 | -846.3775
2021-09-17 | -3248.83 | 6.108 | 52.2657 | 59.8258 | -952.1381
2021-09-18 01:00 | -3470.9 | 6.108 | 51.9837 | 59.8258 | -1017.2204
2021-09-19 02:00 | -3561.69 | 6.108 | 51.8269 | 59.8258 | -1043.8283
2021-09-20 03:00 | -3627.56 | 6.108 | 51.7175 | 59.8258 | -1063.1329
2021-09-21 04:00 | -3450.69 | 6.108 | 51.7944 | 59.8258 | -1011.2974
2021-09-22 05:00 | -3278.49 | 6.108 | 51.9173 | 59.8258 | -960.8306
2021-09-23 06:00 | -2761.94 | 6.108 | 52.3165 | 59.8258 | -809.4447
2021-09-24 07:00 | -2746.3 | 6.108 | 52.4013 | 59.8258 | -804.8611
2021-09-25 08:00 | -2670.84 | 6.108 | 52.4967 | 59.8258 | -782.7459
2021-09-26 09:00 | -3171.8 | 6.108 | 52.1607 | 59.8258 | -929.5628
2021-09-27 10:00 | -2738.76 | 6.108 | 52.443 | 59.8258 | -802.6513
2021-09-28 11:00 | -2127.71 | 6.108 | 52.9449 | 59.8258 | -623.5702
2021-09-29 12:00 | -1724.91 | 5.3821 | 53.175 | 59.8258 | -505.5212
2021-09-30 13:00 | -1378.39 | 4.3524 | 53.3005 | 59.8258 | -403.9662
2021-10-01 14:00 | -1245.21 | 4.0368 | 53.4468 | 59.8258 | -364.935
2021-10-02 15:00 | -1322.65 | 4.3051 | 53.557 | 59.8258 | -387.6305
2021-10-03 16:00 | -988.579 | 3.2352 | 53.6195 | 59.8258 | -289.7239
2021-10-04 17:00 | -1259.46 | 4.1815 | 53.7274 | 59.8258 | -369.1113
2021-10-05 18:00 | -1859.46 | 5.9583 | 53.6991 | 59.8258 | -544.9539
2021-10-06 19:00 | -2976.48 | 6.108 | 52.8349 | 59.8258 | -872.3202
2021-10-07 20:00 | -3731.12 | 6.108 | 52.096 | 59.8258 | -1093.4833
2021-10-08 21:00 | -5213.46 | 6.108 | 50.8094 | 59.8258 | -1527.9143
2021-10-09 22:00 | -5614.81 | 6.108 | 50.2015 | 59.8258 | -1645.5384
2021-10-10 23:00 | -6641.29 | 6.108 | 49.1902 | 59.8258 | -1946.37
2021-10-12 | -7125.37 | 6.108 | 48.5303 | 59.8258 | -2088.2398
2021-10-13 01:00 | -7354.75 | 6.108 | 48.0918 | 59.8258 | -2155.4645
2021-10-14 02:00 | -7453.11 | 6.108 | 47.8007 | 59.8258 | -2184.2909
2021-10-15 03:00 | -7556.89 | 6.108 | 47.5571 | 59.8258 | -2214.7058
2021-10-16 04:00 | -7610.64 | 6.108 | 47.3543 | 59.8258 | -2230.4584
2021-10-17 05:00 | -7772.38 | 6.108 | 47.097 | 59.8258 | -2277.8597
2021-10-18 06:00 | -7774.75 | 6.108 | 46.9568 | 59.8258 | -2278.5543
2021-10-19 07:00 | -7066.98 | 6.108 | 47.3786 | 59.8258 | -2071.1274
2021-10-20 08:00 | -6817.68 | 6.108 | 47.5676 | 59.8258 | -1998.0648
2021-10-21 09:00 | -7579.57 | 6.108 | 47.0103 | 59.8258 | -2221.3527
2021-10-22 10:00 | -7232.46 | 6.108 | 47.1389 | 59.8258 | -2119.6248
2021-10-23 11:00 | -6872.75 | 6.108 | 47.3685 | 59.8258 | -2014.2042
2021-10-24 12:00 | -6487.12 | 6.108 | 47.6706 | 59.8258 | -1901.1872
2021-10-25 13:00 | -6381.93 | 6.108 | 47.7662 | 59.8258 | -1870.3591
2021-10-26 14:00 | -6486.96 | 6.108 | 47.677 | 59.8258 | -1901.1403
2021-10-27 15:00 | -6398 | 6.108 | 47.7194 | 59.8258 | -1875.0687
2021-10-28 16:00 | -6512.5 | 6.108 | 47.6124 | 59.8258 | -1908.6253
2021-10-29 17:00 | -5168.42 | 6.108 | 48.5792 | 59.8258 | -1514.7144
2021-10-30 18:00 | -5744.7 | 6.108 | 48.2872 | 59.8258 | -1683.6054
2021-10-31 19:00 | -6262.86 | 6.108 | 47.8824 | 59.8258 | -1835.4631
2021-11-01 20:00 | -6942.8 | 6.108 | 47.2761 | 59.8258 | -2034.7338
2021-11-02 21:00 | -7341.98 | 6.108 | 46.8558 | 59.8258 | -2151.7219
2021-11-03 22:00 | -7653.01 | 6.108 | 46.5066 | 59.8258 | -2242.8758
2021-11-04 23:00 | -7964.36 | 6.108 | 46.1371 | 59.8258 | -2334.1235
2021-11-06 | -9413.76 | 6.108 | 44.913 | 59.8258 | -2758.9007
2021-11-07 01:00 | -9712.45 | 6.108 | 44.3938 | 59.8258 | -2846.4381
2021-11-08 02:00 | -9713.05 | 6.108 | 44.1724 | 59.8258 | -2846.614
2021-11-09 03:00 | -9826.19 | 6.108 | 43.9432 | 59.8258 | -2879.772
2021-11-10 04:00 | -9975.33 | 6.108 | 43.6891 | 59.8258 | -2923.4806
2021-11-11 05:00 | -10168.5 | 6.108 | 43.3793 | 59.8258 | -2980.0932
2021-11-12 06:00 | -10286.7 | 6.108 | 43.149 | 59.8258 | -3014.7342
2021-11-13 07:00 | -9443.9 | 6.108 | 43.6515 | 59.8258 | -2767.7339
2021-11-14 08:00 | -8387.05 | 6.108 | 44.4531 | 59.8258 | -2458.0017
2021-11-15 09:00 | -7895.19 | 6.108 | 44.9443 | 59.8258 | -2313.8518
2021-11-16 10:00 | -6591.92 | 6.108 | 46.0252 | 59.8258 | -1931.901
2021-11-17 11:00 | -5097.94 | 6.108 | 47.3671 | 59.8258 | -1494.0587
2021-11-18 12:00 | -3971.1 | 6.108 | 48.5599 | 59.8258 | -1163.8145
2021-11-19 13:00 | -3437.97 | 6.108 | 49.3118 | 59.8258 | -1007.5695
2021-11-20 14:00 | -3227.35 | 6.108 | 49.7534 | 59.8258 | -945.8429
2021-11-21 15:00 | -3184.41 | 6.108 | 50.018 | 59.8258 | -933.2584
2021-11-22 16:00 | -3889.96 | 6.108 | 49.667 | 59.8258 | -1140.0347
2021-11-23 17:00 | -3535.13 | 6.108 | 49.9647 | 59.8258 | -1036.0443
2021-11-24 18:00 | -4500.56 | 6.108 | 49.3408 | 59.8258 | -1318.9839
2021-11-25 19:00 | -5040.09 | 6.108 | 48.8925 | 59.8258 | -1477.1046
2021-11-26 20:00 | -5391.05 | 6.108 | 48.5449 | 59.8258 | -1579.9608
2021-11-27 21:00 | -5579.66 | 6.108 | 48.3373 | 59.8258 | -1635.2369
2021-11-28 22:00 | -5807.55 | 6.108 | 48.118 | 59.8258 | -1702.0249
2021-11-29 23:00 | -5876.92 | 6.108 | 47.9903 | 59.8258 | -1722.3552
2021-12-01 | -7004.5 | 6.108 | 47.0978 | 59.8258 | -2052.8163
2021-12-02 01:00 | -7237.15 | 6.108 | 46.7418 | 59.8258 | -2120.9993
2021-12-03 02:00 | -7455.33 | 6.108 | 46.439 | 59.8258 | -2184.9415
2021-12-04 03:00 | -7563.58 | 6.108 | 46.2459 | 59.8258 | -2216.6665
2021-12-05 04:00 | -7569.82 | 6.108 | 46.1496 | 59.8258 | -2218.4952
2021-12-06 05:00 | -7568.56 | 6.108 | 46.071 | 59.8258 | -2218.126
2021-12-07 06:00 | -7284.78 | 6.108 | 46.2463 | 59.8258 | -2134.9583
2021-12-08 07:00 | -7049.92 | 6.108 | 46.428 | 59.8258 | -2066.1276
2021-12-09 08:00 | -6641.03 | 6.108 | 46.7577 | 59.8258 | -1946.2938
2021-12-10 09:00 | -6948.59 | 6.108 | 46.5861 | 59.8258 | -2036.4307
2021-12-11 10:00 | -6527.97 | 6.108 | 46.8799 | 59.8258 | -1913.1592
2021-12-12 11:00 | -5487.67 | 6.108 | 47.6917 | 59.8258 | -1608.2773
2021-12-13 12:00 | -4229.6 | 6.108 | 48.7938 | 59.8258 | -1239.5734
2021-12-14 13:00 | -4205.27 | 6.108 | 49.0609 | 59.8258 | -1232.443
2021-12-15 14:00 | -3577.23 | 6.108 | 49.6672 | 59.8258 | -1048.3826
2021-12-16 15:00 | -3108.96 | 6.108 | 50.2019 | 59.8258 | -911.1462
2021-12-17 16:00 | -2779.54 | 6.108 | 50.6542 | 59.8258 | -814.6028
2021-12-18 17:00 | -2974.67 | 6.108 | 50.6784 | 59.8258 | -871.7897
2021-12-19 18:00 | -3754.37 | 6.108 | 50.1779 | 59.8258 | -1100.2972
2021-12-20 19:00 | -4483.56 | 6.108 | 49.6098 | 59.8258 | -1314.0017
2021-12-21 20:00 | -5070.66 | 6.108 | 49.0847 | 59.8258 | -1486.0638
2021-12-22 21:00 | -6146.29 | 6.108 | 48.1768 | 59.8258 | -1801.2998
2021-12-23 22:00 | -6628.85 | 6.108 | 47.6151 | 59.8258 | -1942.7242
2021-12-24 23:00 | -7697.57 | 6.108 | 46.6245 | 59.8258 | -2255.9351
2021-12-26 | -8089.77 | 6.108 | 46.075 | 59.8258 | -2370.8775
2021-12-27 01:00 | -8379.46 | 6.108 | 45.6469 | 59.8258 | -2455.7773
2021-12-28 02:00 | -8584.81 | 6.108 | 45.3097 | 59.8258 | -2515.9595
2021-12-29 03:00 | -8723.52 | 6.108 | 45.0452 | 59.8258 | -2556.6113
2021-12-30 04:00 | -8606.95 | 6.108 | 44.9833 | 59.8258 | -2522.448
2021-12-31 05:00 | -8382.8 | 6.108 | 45.0612 | 59.8258 | -2456.7562
2022-01-01 06:00 | -7949.96 | 6.108 | 45.3412 | 59.8258 | -2329.9033
2022-01-02 07:00 | -7610.8 | 6.108 | 45.6045 | 59.8258 | -2230.5053
2022-01-03 08:00 | -6547.62 | 6.108 | 46.4315 | 59.8258 | -1918.918
2022-01-04 09:00 | -5537.97 | 6.108 | 47.3463 | 59.8258 | -1623.0188
2022-01-05 10:00 | -4031.07 | 6.108 | 48.6953 | 59.8258 | -1181.39
2022-01-06 11:00 | -2922.65 | 6.108 | 49.8513 | 59.8258 | -856.5442
2022-01-07 12:00 | -2360.99 | 6.108 | 50.61 | 59.8258 | -691.9379
2022-01-08 13:00 | -1874.19 | 6.0372 | 51.2498 | 59.8258 | -549.2709
2022-01-09 14:00 | -1330.58 | 4.2381 | 51.4916 | 59.8258 | -389.9545
2022-01-10 15:00 | -2013.5 | 6.108 | 51.6852 | 59.8258 | -590.0986
2022-01-11 16:00 | -2024.74 | 6.108 | 51.7621 | 59.8258 | -593.3927
2022-01-12 17:00 | -2482.46 | 6.108 | 51.4962 | 59.8258 | -727.5372
2022-01-13 18:00 | -2784.5 | 6.108 | 51.2996 | 59.8258 | -816.0564
2022-01-14 19:00 | -3587.53 | 6.108 | 50.7057 | 59.8258 | -1051.4013
2022-01-15 20:00 | -4276.96 | 6.108 | 50.1009 | 59.8258 | -1253.4532
2022-01-16 21:00 | -5522.1 | 6.108 | 49.0542 | 59.8258 | -1618.3678
2022-01-17 22:00 | -6135.68 | 6.108 | 48.3639 | 59.8258 | -1798.1903
2022-01-18 23:00 | -7211.04 | 6.108 | 47.3438 | 59.8258 | -2113.3472
2022-01-20 | -7744.09 | 6.108 | 46.6674 | 59.8258 | -2269.5687
2022-01-21 01:00 | -8075.52 | 6.108 | 46.1684 | 59.8258 | -2366.7013
2022-01-22 02:00 | -8371.61 | 6.108 | 45.7301 | 59.8258 | -2453.4767
2022-01-23 03:00 | -8561.35 | 6.108 | 45.4062 | 59.8258 | -2509.084
2022-01-24 04:00 | -8564.06 | 6.108 | 45.2392 | 59.8258 | -2509.8782
2022-01-25 05:00 | -8572.64 | 6.108 | 45.1178 | 59.8258 | -2512.3928
2022-01-26 06:00 | -8264.66 | 6.108 | 45.2525 | 59.8258 | -2422.1327
2022-01-27 07:00 | -7941.57 | 6.108 | 45.4549 | 59.8258 | -2327.4444
2022-01-28 08:00 | -7080.99 | 6.108 | 46.0948 | 59.8258 | -2075.2333
2022-01-29 09:00 | -5909.41 | 6.108 | 47.0721 | 59.8258 | -1731.8771
2022-01-30 10:00 | -4987.05 | 6.108 | 47.957 | 59.8258 | -1461.5601
2022-01-31 11:00 | -3792.35 | 6.108 | 49.0767 | 59.8258 | -1111.4281
2022-02-01 12:00 | -3668.27 | 6.108 | 49.453 | 59.8258 | -1075.0638
2022-02-02 13:00 | -3608.45 | 6.108 | 49.6903 | 59.8258 | -1057.5323
2022-02-03 14:00 | -3514.74 | 6.108 | 49.8917 | 59.8258 | -1030.0686
2022-02-04 15:00 | -3332.52 | 6.108 | 50.1426 | 59.8258 | -976.6652
2022-02-05 16:00 | -2668.69 | 6.108 | 50.7509 | 59.8258 | -782.1158
2022-02-06 17:00 | -2763.28 | 6.108 | 50.8418 | 59.8258 | -809.8374
2022-02-07 18:00 | -2847.03 | 6.108 | 50.8823 | 59.8258 | -834.3821
2022-02-08 19:00 | -3373.08 | 6.108 | 50.565 | 59.8258 | -988.5522
2022-02-09 20:00 | -3575.02 | 6.108 | 50.4215 | 59.8258 | -1047.7349
2022-02-10 21:00 | -4635.97 | 6.108 | 49.6328 | 59.8258 | -1358.6687
2022-02-11 22:00 | -5069.41 | 6.108 | 49.178 | 59.8258 | -1485.6974
2022-02-12 23:00 | -6007.56 | 6.108 | 48.3512 | 59.8258 | -1760.642
2022-02-14 | -6439.26 | 6.108 | 47.8437 | 59.8258 | -1887.1608
2022-02-15 01:00 | -6729.32 | 6.108 | 47.467 | 59.8258 | -1972.169
2022-02-16 02:00 | -6927.4 | 6.108 | 47.1827 | 59.8258 | -2030.2205
2022-02-17 03:00 | -7087.65 | 6.108 | 46.9552 | 59.8258 | -2077.1852
2022-02-18 04:00 | -6954.3 | 6.108 | 46.9498 | 59.8258 | -2038.1041
2022-02-19 05:00 | -7001.53 | 6.108 | 46.8654 | 59.8258 | -2051.9459
2022-02-20 06:00 | -6593.25 | 6.108 | 47.122 | 59.8258 | -1932.2908
2022-02-21 07:00 | -6786.4 | 6.108 | 46.9898 | 59.8258 | -1988.8975
2022-02-22 08:00 | -6634.78 | 6.108 | 47.0648 | 59.8258 | -1944.4621
2022-02-23 09:00 | -7019.75 | 6.108 | 46.7604 | 59.8258 | -2057.2856
2022-02-24 10:00 | -6959.85 | 6.108 | 46.7247 | 59.8258 | -2039.7307
2022-02-25 11:00 | -6794.71 | 6.108 | 46.7931 | 59.8258 | -1991.3329
2022-02-26 12:00 | -6436.93 | 6.108 | 47.0305 | 59.8258 | -1886.478
2022-02-27 13:00 | -6520.38 | 6.108 | 46.9792 | 59.8258 | -1910.9347
2022-02-28 14:00 | -6329.27 | 6.108 | 47.0922 | 59.8258 | -1854.9259
2022-03-01 15:00 | -6508.06 | 6.108 | 46.9576 | 59.8258 | -1907.3241
2022-03-02 16:00 | -5577.42 | 6.108 | 47.6176 | 59.8258 | -1634.5804
2022-03-03 17:00 | -5558.56 | 6.108 | 47.7229 | 59.8258 | -1629.0531
2022-03-04 18:00 | -5587.82 | 6.108 | 47.7361 | 59.8258 | -1637.6284
2022-03-05 19:00 | -5837.79 | 6.108 | 47.557 | 59.8258 | -1710.8874
2022-03-06 20:00 | -6441.31 | 6.108 | 47.0763 | 59.8258 | -1887.7616
2022-03-07 21:00 | -7436.83 | 6.108 | 46.2521 | 59.8258 | -2179.5197
2022-03-08 22:00 | -7613.3 | 6.108 | 45.9319 | 59.8258 | -2231.238
2022-03-09 23:00 | -8415.6 | 6.108 | 45.2028 | 59.8258 | -2466.3689
2022-03-11 | -8607.64 | 6.108 | 44.8692 | 59.8258 | -2522.6503
2022-03-12 01:00 | -8652.82 | 6.108 | 44.6828 | 59.8258 | -2535.8912
2022-03-13 02:00 | -8699.08 | 6.108 | 44.5426 | 59.8258 | -2549.4487
2022-03-14 03:00 | -8571.4 | 6.108 | 44.5628 | 59.8258 | -2512.0294
2022-03-15 04:00 | -8357.3 | 6.108 | 44.6628 | 59.8258 | -2449.2829
2022-03-16 05:00 | -8271.17 | 6.108 | 44.7088 | 59.8258 | -2424.0406
2022-03-17 06:00 | -7851.12 | 6.108 | 45.0017 | 59.8258 | -2300.9361
2022-03-18 07:00 | -7266.99 | 6.108 | 45.4678 | 59.8258 | -2129.7445
2022-03-19 08:00 | -7318.33 | 6.108 | 45.513 | 59.8258 | -2144.7908
2022-03-20 09:00 | -8036.92 | 6.108 | 45.0079 | 59.8258 | -2355.3887
2022-03-21 10:00 | -7549.57 | 6.108 | 45.2858 | 59.8258 | -2212.5606
2022-03-22 11:00 | -7365.14 | 6.108 | 45.4485 | 59.8258 | -2158.5095
2022-03-23 12:00 | -7118.39 | 6.108 | 45.6669 | 59.8258 | -2086.1942
2022-03-24 13:00 | -7666.8 | 6.108 | 45.2809 | 59.8258 | -2246.9173
2022-03-25 14:00 | -7803.9 | 6.108 | 45.1066 | 59.8258 | -2287.0973
2022-03-26 15:00 | -7640.27 | 6.108 | 45.1783 | 59.8258 | -2239.1421
2022-03-27 16:00 | -6796.03 | 6.108 | 45.7904 | 59.8258 | -1991.7198
2022-03-28 17:00 | -6830.38 | 6.108 | 45.8489 | 59.8258 | -2001.7868
2022-03-29 18:00 | -7030.64 | 6.108 | 45.7136 | 59.8258 | -2060.4772
2022-03-30 19:00 | -7745.56 | 6.108 | 45.1463 | 59.8258 | -2269.9996
2022-03-31 20:00 | -8112.82 | 6.108 | 44.7626 | 59.8258 | -2377.6328
2022-04-01 21:00 | -9274.59 | 6.108 | 43.7939 | 59.8258 | -2718.114
2022-04-02 22:00 | -9620.6 | 6.108 | 43.3015 | 59.8258 | -2819.5195
2022-04-03 23:00 | -10594 | 6.108 | 42.3782 | 59.8258 | -3104.7949
2022-04-05 | -11162.7 | 6.108 | 41.6885 | 59.8258 | -3271.4644
2022-04-06 01:00 | -11453.9 | 6.108 | 41.223 | 59.8258 | -3356.8067
2022-04-07 02:00 | -11585 | 6.108 | 40.9168 | 59.8258 | -3395.2283
2022-04-08 03:00 | -11818.8 | 6.108 | 40.5766 | 59.8258 | -3463.7484
2022-04-09 04:00 | -11652.8 | 6.108 | 40.5198 | 59.8258 | -3415.0986
2022-04-10 05:00 | -11670.8 | 6.108 | 40.3883 | 59.8258 | -3420.3738
2022-04-11 06:00 | -11693.2 | 6.108 | 40.2595 | 59.8258 | -3426.9386
2022-04-12 07:00 | -10819 | 6.108 | 40.8119 | 59.8258 | -3170.7359
2022-04-13 08:00 | -10251.3 | 6.108 | 41.2632 | 59.8258 | -3004.3595
2022-04-14 09:00 | -10748.7 | 6.108 | 40.9606 | 59.8258 | -3150.133
2022-04-15 10:00 | -10583.4 | 6.108 | 41.0172 | 59.8258 | -3101.6884
2022-04-16 11:00 | -9501.75 | 6.108 | 41.8071 | 59.8258 | -2784.688
2022-04-17 12:00 | -8983.7 | 6.108 | 42.3337 | 59.8258 | -2632.8626
2022-04-18 13:00 | -8608.78 | 6.108 | 42.7392 | 59.8258 | -2522.9844
2022-04-19 14:00 | -8282.14 | 6.108 | 43.0799 | 59.8258 | -2427.2556
2022-04-20 15:00 | -8268.91 | 6.108 | 43.2041 | 59.8258 | -2423.3783
2022-04-21 16:00 | -8209.33 | 6.108 | 43.3192 | 59.8258 | -2405.9171
2022-04-22 17:00 | -6737.96 | 6.108 | 44.4714 | 59.8258 | -1974.7011
2022-04-23 18:00 | -7539.19 | 6.108 | 44.1034 | 59.8258 | -2209.5185
2022-04-24 19:00 | -7856.46 | 6.108 | 43.8876 | 59.8258 | -2302.5011
2022-04-25 20:00 | -8252.91 | 6.108 | 43.5561 | 59.8258 | -2418.6892
2022-04-26 21:00 | -8542.62 | 6.108 | 43.3143 | 59.8258 | -2503.5948
2022-04-27 22:00 | -8657.17 | 6.108 | 43.1991 | 59.8258 | -2537.1661
2022-04-28 23:00 | -8605.52 | 6.108 | 43.1887 | 59.8258 | -2522.029
2022-04-30 | -9895.18 | 6.108 | 42.2088 | 59.8258 | -2899.991
2022-05-01 01:00 | -10188.1 | 6.108 | 41.8049 | 59.8258 | -2985.8374
2022-05-02 02:00 | -10337.6 | 6.108 | 41.5506 | 59.8258 | -3029.6515
2022-05-03 03:00 | -10715.8 | 6.108 | 41.1727 | 59.8258 | -3140.491
2022-05-04 04:00 | -10784.9 | 6.108 | 40.9942 | 59.8258 | -3160.7422
2022-05-05 05:00 | -10761.7 | 6.108 | 40.8857 | 59.8258 | -3153.9429
2022-05-06 06:00 | -10711.1 | 6.108 | 40.8554 | 59.8258 | -3139.1135
2022-05-07 07:00 | -9355.69 | 6.108 | 41.8211 | 59.8258 | -2741.8821
2022-05-08 08:00 | -9285.22 | 6.108 | 42.0066 | 59.8258 | -2721.2294
2022-05-09 09:00 | -9236.49 | 6.108 | 42.1175 | 59.8258 | -2706.948
2022-05-10 10:00 | -7327.48 | 6.108 | 43.5854 | 59.8258 | -2147.4724
2022-05-11 11:00 | -5367.72 | 6.108 | 45.3403 | 59.8258 | -1573.1234
2022-05-12 12:00 | -4629.28 | 6.108 | 46.3405 | 59.8258 | -1356.708
2022-05-13 13:00 | -3447.67 | 6.108 | 47.5665 | 59.8258 | -1010.4123
2022-05-14 14:00 | -2754.58 | 6.108 | 48.4757 | 59.8258 | -807.2877
2022-05-15 15:00 | -2430.82 | 6.108 | 49.1118 | 59.8258 | -712.403
2022-05-16 16:00 | -2664.55 | 6.108 | 49.2466 | 59.8258 | -780.9025
2022-05-17 17:00 | -2252.06 | 6.108 | 49.7377 | 59.8258 | -660.0136
2022-05-18 18:00 | -3871.96 | 6.108 | 48.7506 | 59.8258 | -1134.7595
2022-05-19 19:00 | -4916.34 | 6.108 | 47.9187 | 59.8258 | -1440.837
2022-05-20 20:00 | -5311.79 | 6.108 | 47.4966 | 59.8258 | -1556.732
2022-05-21 21:00 | -5915.55 | 6.108 | 46.9791 | 59.8258 | -1733.6766
2022-05-22 22:00 | -6061.58 | 6.108 | 46.7671 | 59.8258 | -1776.4737
2022-05-23 23:00 | -6478.8 | 6.108 | 46.3526 | 59.8258 | -1898.7488
2022-05-25 | -7479.47 | 6.108 | 45.51 | 59.8258 | -2192.0163
2022-05-26 01:00 | -7868.94 | 6.108 | 45.0305 | 59.8258 | -2306.1587
2022-05-27 02:00 | -7965.11 | 6.108 | 44.7938 | 59.8258 | -2334.3433
2022-05-28 03:00 | -7756.67 | 6.108 | 44.8439 | 59.8258 | -2273.2556
2022-05-29 04:00 | -7743.2 | 6.108 | 44.8014 | 59.8258 | -2269.3079
2022-05-30 05:00 | -7249.59 | 6.108 | 45.1181 | 59.8258 | -2124.6451
2022-05-31 06:00 | -7176.77 | 6.108 | 45.2195 | 59.8258 | -2103.3037
2022-06-01 07:00 | -7128.78 | 6.108 | 45.2928 | 59.8258 | -2089.2392
2022-06-02 08:00 | -7094.98 | 6.108 | 45.3443 | 59.8258 | -2079.3334
2022-06-03 09:00 | -7754.34 | 6.108 | 44.8772 | 59.8258 | -2272.5727
2022-06-04 10:00 | -7292.29 | 6.108 | 45.1472 | 59.8258 | -2137.1592
2022-06-05 11:00 | -6887.4 | 6.108 | 45.4539 | 59.8258 | -2018.4977
2022-06-06 12:00 | -6023.27 | 6.108 | 46.1605 | 59.8258 | -1765.2462
2022-06-07 13:00 | -5655.85 | 6.108 | 46.5684 | 59.8258 | -1657.566
2022-06-08 14:00 | -6131.35 | 6.108 | 46.3236 | 59.8258 | -1796.9213
2022-06-09 15:00 | -5454.93 | 6.108 | 46.8387 | 59.8258 | -1598.6822
2022-06-10 16:00 | -4973.81 | 6.108 | 47.3054 | 59.8258 | -1457.6798
2022-06-11 17:00 | -4891.13 | 6.108 | 47.494 | 59.8258 | -1433.4487
2022-06-12 18:00 | -4489.56 | 6.108 | 47.8743 | 59.8258 | -1315.7602
2022-06-13 19:00 | -5150.38 | 6.108 | 47.4893 | 59.8258 | -1509.4274
2022-06-14 20:00 | -5343.5 | 6.108 | 47.3533 | 59.8258 | -1566.0253
2022-06-15 21:00 | -5988.27 | 6.108 | 46.8739 | 59.8258 | -1754.9887
2022-06-16 22:00 | -6456.67 | 6.108 | 46.4569 | 59.8258 | -1892.2632
2022-06-17 23:00 | -7295.67 | 6.108 | 45.7376 | 59.8258 | -2138.1498
2022-06-19 | -7428.75 | 6.108 | 45.4741 | 59.8258 | -2177.1517
2022-06-20 01:00 | -7484.01 | 6.108 | 45.3305 | 59.8258 | -2193.3468
2022-06-21 02:00 | -7447.46 | 6.108 | 45.2964 | 59.8258 | -2182.6351
2022-06-22 03:00 | -7488.1 | 6.108 | 45.2241 | 59.8258 | -2194.5455
2022-06-23 04:00 | -7437.53 | 6.108 | 45.2195 | 59.8258 | -2179.7249
2022-06-24 05:00 | -7094.92 | 6.108 | 45.4582 | 59.8258 | -2079.3158
2022-06-25 06:00 | -6546.7 | 6.108 | 45.8948 | 59.8258 | -1918.6484
2022-06-26 07:00 | -6425.1 | 6.108 | 46.068 | 59.8258 | -1883.0109
2022-06-27 08:00 | -6539.18 | 6.108 | 46.0369 | 59.8258 | -1916.4445
2022-06-28 09:00 | -6746.65 | 6.108 | 45.9069 | 59.8258 | -1977.2479
2022-06-29 10:00 | -6475.52 | 6.108 | 46.105 | 59.8258 | -1897.7876
2022-06-30 11:00 | -6056.23 | 6.108 | 46.4609 | 59.8258 | -1774.9058
2022-07-01 12:00 | -5690.36 | 6.108 | 46.8065 | 59.8258 | -1667.6799
2022-07-02 13:00 | -5614.09 | 6.108 | 46.9441 | 59.8258 | -1645.3274
2022-07-03 14:00 | -5504.33 | 6.108 | 47.0838 | 59.8258 | -1613.1599
2022-07-04 15:00 | -5353.55 | 6.108 | 47.2519 | 59.8258 | -1568.9706
2022-07-05 16:00 | -4728.13 | 6.108 | 47.7784 | 59.8258 | -1385.6781
2022-07-06 17:00 | -5007.62 | 6.108 | 47.6836 | 59.8258 | -1467.5886
2022-07-07 18:00 | -5156.13 | 6.108 | 47.596 | 59.8258 | -1511.1125
2022-07-08 19:00 | -5390.57 | 6.108 | 47.4235 | 59.8258 | -1579.8201
2022-07-09 20:00 | -6124.16 | 6.108 | 46.8638 | 59.8258 | -1794.8141
2022-07-10 21:00 | -6884.7 | 6.108 | 46.2076 | 59.8258 | -2017.7064
2022-07-11 22:00 | -7311.81 | 6.108 | 45.7341 | 59.8258 | -2142.88
2022-07-12 23:00 | -8284.93 | 6.108 | 44.8701 | 59.8258 | -2428.0733
2022-07-14 | -8635.23 | 6.108 | 44.3947 | 59.8258 | -2530.7361
2022-07-15 01:00 | -8887.65 | 6.108 | 44.0232 | 59.8258 | -2604.7131
2022-07-16 02:00 | -9214.37 | 6.108 | 43.6308 | 59.8258 | -2700.4653
2022-07-17 03:00 | -9735.83 | 6.108 | 43.0887 | 59.8258 | -2853.2901
2022-07-18 04:00 | -9797.86 | 6.108 | 42.8499 | 59.8258 | -2871.4693
2022-07-19 05:00 | -9729.08 | 6.108 | 42.7656 | 59.8258 | -2851.3119
2022-07-20 06:00 | -9305.03 | 6.108 | 42.9869 | 59.8258 | -2727.0351
2022-07-21 07:00 | -9322.81 | 6.108 | 42.9384 | 59.8258 | -2732.2459
2022-07-22 08:00 | -8549.22 | 6.108 | 43.4705 | 59.8258 | -2505.5291
2022-07-23 09:00 | -7932.13 | 6.108 | 44.0025 | 59.8258 | -2324.6778
2022-07-24 10:00 | -7183.57 | 6.108 | 44.6756 | 59.8258 | -2105.2965
2022-07-25 11:00 | -5700.42 | 6.108 | 45.9453 | 59.8258 | -1670.6282
2022-07-26 12:00 | -4249.82 | 6.108 | 47.3178 | 59.8258 | -1245.4993
2022-07-27 13:00 | -4493.98 | 6.108 | 47.5043 | 59.8258 | -1317.0555
2022-07-28 14:00 | -3979.05 | 6.108 | 48.0775 | 59.8258 | -1166.1444
2022-07-29 15:00 | -3511.82 | 6.108 | 48.639 | 59.8258 | -1029.2128
2022-07-30 16:00 | -4038.82 | 6.108 | 48.4755 | 59.8258 | -1183.6613
2022-07-31 17:00 | -4881.1 | 6.108 | 47.9227 | 59.8258 | -1430.5092
2022-08-01 18:00 | -5739.82 | 6.108 | 47.2188 | 59.8258 | -1682.1752
2022-08-02 19:00 | -6837.89 | 6.108 | 46.2933 | 59.8258 | -2003.9877
2022-08-03 20:00 | -7494.7 | 6.108 | 45.6113 | 59.8258 | -2196.4797
2022-08-04 21:00 | -9115.69 | 6.108 | 44.1962 | 59.8258 | -2671.545
2022-08-05 22:00 | -8932.43 | 6.108 | 43.997 | 59.8258 | -2617.8368
2022-08-06 23:00 | -10854.6 | 6.108 | 42.3676 | 59.8258 | -3181.1692
2022-08-08 | -11162.3 | 6.108 | 41.7363 | 59.8258 | -3271.3472
2022-08-09 01:00 | -11436.3 | 6.108 | 41.2273 | 59.8258 | -3351.6487
2022-08-10 02:00 | -11988.5 | 6.108 | 40.566 | 59.8258 | -3513.4825
2022-08-11 03:00 | -11978.8 | 6.108 | 40.3137 | 59.8258 | -3510.6397
2022-08-12 04:00 | -11869.8 | 6.108 | 40.1835 | 59.8258 | -3478.695
2022-08-13 05:00 | -11985.8 | 6.108 | 39.9696 | 59.8258 | -3512.6912
2022-08-14 06:00 | -11640.5 | 6.108 | 40.0933 | 59.8258 | -3411.4938
2022-08-15 07:00 | -11527 | 6.108 | 40.1105 | 59.8258 | -3378.2302
2022-08-16 08:00 | -9882.39 | 6.108 | 41.2984 | 59.8258 | -2896.2426
2022-08-17 09:00 | -9111.05 | 6.108 | 42.0532 | 59.8258 | -2670.1852
2022-08-18 10:00 | -7651.85 | 6.108 | 43.3172 | 59.8258 | -2242.5359
2022-08-19 11:00 | -6054.09 | 6.108 | 44.7958 | 59.8258 | -1774.2786
2022-08-20 12:00 | -5027.29 | 6.108 | 45.9366 | 59.8258 | -1473.3533
2022-08-21 13:00 | -3865.01 | 6.108 | 47.1764 | 59.8258 | -1132.7226
2022-08-22 14:00 | -3440.01 | 6.108 | 47.8712 | 59.8258 | -1008.1674
2022-08-23 15:00 | -2948.36 | 6.108 | 48.5503 | 59.8258 | -864.079
2022-08-24 16:00 | -2526.34 | 6.108 | 49.1464 | 59.8258 | -740.3972
2022-08-25 17:00 | -3724.58 | 6.108 | 48.5111 | 59.8258 | -1091.5666
2022-08-26 18:00 | -4758.04 | 6.108 | 47.7731 | 59.8258 | -1394.4439
2022-08-27 19:00 | -6503.68 | 6.108 | 46.3923 | 59.8258 | -1906.0405
2022-08-28 20:00 | -7372.44 | 6.108 | 45.507 | 59.8258 | -2160.6489
2022-08-29 21:00 | -8513.85 | 6.108 | 44.4263 | 59.8258 | -2495.1631
2022-08-30 22:00 | -8945.78 | 6.108 | 43.8058 | 59.8258 | -2621.7493
2022-08-31 23:00 | -10333.2 | 6.108 | 42.5269 | 59.8258 | -3028.362
2022-09-02 | -10573.3 | 6.108 | 41.9989 | 59.8258 | -3098.7283
2022-09-03 01:00 | -10998 | 6.108 | 41.4264 | 59.8258 | -3223.1956
2022-09-04 02:00 | -11397.7 | 6.108 | 40.8944 | 59.8258 | -3340.3361
2022-09-05 03:00 | -11236.2 | 6.108 | 40.7856 | 59.8258 | -3293.0052
2022-09-06 04:00 | -11399.6 | 6.108 | 40.4978 | 59.8258 | -3340.893
2022-09-07 05:00 | -11440.2 | 6.108 | 40.3289 | 59.8258 | -3352.7917
2022-09-08 06:00 | -11089.8 | 6.108 | 40.4677 | 59.8258 | -3250.0996
2022-09-09 07:00 | -10927.8 | 6.108 | 40.5512 | 59.8258 | -3202.622
2022-09-10 08:00 | -9792.86 | 6.108 | 41.3797 | 59.8258 | -2870.004
2022-09-11 09:00 | -8725.68 | 6.108 | 42.299 | 59.8258 | -2557.2444
2022-09-12 10:00 | -7005.87 | 6.108 | 43.7823 | 59.8258 | -2053.2178
2022-09-13 11:00 | -5634.76 | 6.108 | 45.1405 | 59.8258 | -1651.3851
2022-09-14 12:00 | -4268.69 | 6.108 | 46.5286 | 59.8258 | -1251.0295
2022-09-15 13:00 | -3061.84 | 6.108 | 47.8397 | 59.8258 | -897.3367
2022-09-16 14:00 | -3644.38 | 6.108 | 47.8209 | 59.8258 | -1068.0623
2022-09-17 15:00 | -3650.77 | 6.108 | 48.0066 | 59.8258 | -1069.9351
2022-09-18 16:00 | -3076.57 | 6.108 | 48.5796 | 59.8258 | -901.6537
2022-09-19 17:00 | -3699.07 | 6.108 | 48.3316 | 59.8258 | -1084.0904
2022-09-20 18:00 | -4605.78 | 6.108 | 47.7239 | 59.8258 | -1349.8209
2022-09-21 19:00 | -5648 | 6.108 | 46.8898 | 59.8258 | -1655.2654
2022-09-22 20:00 | -6005.64 | 6.108 | 46.5079 | 59.8258 | -1760.0793
2022-09-23 21:00 | -7535.64 | 6.108 | 45.2878 | 59.8258 | -2208.4781
2022-09-24 22:00 | -8083.56 | 6.108 | 44.6198 | 59.8258 | -2369.0576
2022-09-25 23:00 | -8803.82 | 6.108 | 43.8622 | 59.8258 | -2580.1449
2022-09-27 | -9518.13 | 6.108 | 43.101 | 59.8258 | -2789.4885
2022-09-28 01:00 | -9812.09 | 6.108 | 42.6315 | 59.8258 | -2875.6397
2022-09-29 02:00 | -10322.4 | 6.108 | 42.044 | 59.8258 | -3025.1968
2022-09-30 03:00 | -9794.27 | 6.108 | 42.2445 | 59.8258 | -2870.4172
2022-10-01 04:00 | -9849.67 | 6.108 | 42.1265 | 59.8258 | -2886.6533
2022-10-02 05:00 | -9991.46 | 6.108 | 41.945 | 59.8258 | -2928.2079
2022-10-03 06:00 | -10235.7 | 6.108 | 41.6737 | 59.8258 | -2999.7876
2022-10-04 07:00 | -9587.18 | 6.108 | 42.0689 | 59.8258 | -2809.7251
2022-10-05 08:00 | -8162.89 | 6.108 | 43.1648 | 59.8258 | -2392.3069
2022-10-06 09:00 | -7337.08 | 6.108 | 43.9751 | 59.8258 | -2150.2859
2022-10-07 10:00 | -6416.84 | 6.108 | 44.8563 | 59.8258 | -1880.5902
2022-10-08 11:00 | -4569.4 | 6.108 | 46.4624 | 59.8258 | -1339.1589
2022-10-09 12:00 | -2848.54 | 6.108 | 48.1463 | 59.8258 | -834.8247
2022-10-10 13:00 | -1996.77 | 6.108 | 49.2525 | 59.8258 | -585.1955
2022-10-11 14:00 | -1547.46 | 5.063 | 49.7445 | 59.8258 | -453.5158
2022-10-12 15:00 | -618.199 | 2.1033 | 50.1171 | 59.8258 | -181.1762
2022-10-13 16:00 | -905.44 | 3.3383 | 50.5917 | 59.8258 | -265.3583
2022-10-14 17:00 | -412.998 | 1.6123 | 50.8866 | 59.8258 | -121.0378
2022-10-15 18:00 | -1965.43 | 6.108 | 50.8431 | 59.8258 | -576.0107
2022-10-16 19:00 | -3724 | 6.108 | 49.5295 | 59.8258 | -1091.3967
2022-10-17 20:00 | -4807.52 | 6.108 | 48.5303 | 59.8258 | -1408.945
2022-10-18 21:00 | -5753.31 | 6.108 | 47.6229 | 59.8258 | -1686.1287
2022-10-19 22:00 | -5759.05 | 6.108 | 47.4157 | 59.8258 | -1687.8109
2022-10-20 23:00 | -6108.46 | 6.108 | 47.0204 | 59.8258 | -1790.2129
2022-10-22 | -8003.85 | 6.108 | 45.4684 | 59.8258 | -2345.6969
2022-10-23 01:00 | -8229.11 | 6.108 | 44.9624 | 59.8258 | -2411.7141
2022-10-24 02:00 | -8664.07 | 6.108 | 44.4155 | 59.8258 | -2539.1883
2022-10-25 03:00 | -8580.79 | 6.108 | 44.2854 | 59.8258 | -2514.7813
2022-10-26 04:00 | -8611.62 | 6.108 | 44.1188 | 59.8258 | -2523.8167
2022-10-27 05:00 | -8711.03 | 6.108 | 43.9094 | 59.8258 | -2552.9509
2022-10-28 06:00 | -8500.84 | 6.108 | 43.9791 | 59.8258 | -2491.3503
2022-10-29 07:00 | -7491.84 | 6.108 | 44.7074 | 59.8258 | -2195.6416
2022-10-30 08:00 | -6893.58 | 6.108 | 45.267 | 59.8258 | -2020.3089
2022-10-31 09:00 | -7312.45 | 6.108 | 45.0779 | 59.8258 | -2143.0675
2022-11-01 10:00 | -7164.88 | 6.108 | 45.1756 | 59.8258 | -2099.819
2022-11-02 11:00 | -6826.33 | 6.108 | 45.43 | 59.8258 | -2000.5998
2022-11-03 12:00 | -6268.66 | 6.108 | 45.9024 | 59.8258 | -1837.1629
2022-11-04 13:00 | -5373.05 | 6.108 | 46.6522 | 59.8258 | -1574.6855
2022-11-05 14:00 | -5519.79 | 6.108 | 46.6871 | 59.8258 | -1617.6908
2022-11-06 15:00 | -4944.6 | 6.108 | 47.1756 | 59.8258 | -1449.1192
2022-11-07 16:00 | -4634.59 | 6.108 | 47.5194 | 59.8258 | -1358.2643
2022-11-08 17:00 | -3029.94 | 6.108 | 48.8432 | 59.8258 | -887.9878
2022-11-09 18:00 | -3783.13 | 6.108 | 48.5773 | 59.8258 | -1108.726
2022-11-10 19:00 | -4001.93 | 6.108 | 48.489 | 59.8258 | -1172.8499
2022-11-11 20:00 | -4338.83 | 6.108 | 48.2752 | 59.8258 | -1271.5856
2022-11-12 21:00 | -5375.78 | 6.108 | 47.5323 | 59.8258 | -1575.4856
2022-11-13 22:00 | -6335.94 | 6.108 | 46.723 | 59.8258 | -1856.8807
2022-11-14 23:00 | -6838.01 | 6.108 | 46.1632 | 59.8258 | -2004.0229
2022-11-16 | -8288.74 | 6.108 | 44.9371 | 59.8258 | -2429.1899
2022-11-17 01:00 | -9011.8 | 6.108 | 44.1155 | 59.8258 | -2641.0979
2022-11-18 02:00 | -9380.3 | 6.108 | 43.5771 | 59.8258 | -2749.0946
2022-11-19 03:00 | -9465.6 | 6.108 | 43.3092 | 59.8258 | -2774.0935
2022-11-20 04:00 | -9528.95 | 6.108 | 43.1116 | 59.8258 | -2792.6596
2022-11-21 05:00 | -9723.82 | 6.108 | 42.8181 | 59.8258 | -2849.7703
2022-11-22 06:00 | -9159.73 | 6.108 | 43.1169 | 59.8258 | -2684.4519
2022-11-23 07:00 | -9116.05 | 6.108 | 43.1265 | 59.8258 | -2671.6505
2022-11-24 08:00 | -8999.42 | 6.108 | 43.1723 | 59.8258 | -2637.4696
2022-11-25 09:00 | -9396.38 | 6.108 | 42.8383 | 59.8258 | -2753.8071
2022-11-26 10:00 | -9040.05 | 6.108 | 43.0132 | 59.8258 | -2649.3771
2022-11-27 11:00 | -8993.69 | 6.108 | 43.0233 | 59.8258 | -2635.7904
2022-11-28 12:00 | -8381.22 | 6.108 | 43.4525 | 59.8258 | -2456.2931
2022-11-29 13:00 | -7960.68 | 6.108 | 43.8047 | 59.8258 | -2333.045
2022-11-30 14:00 | -8085.21 | 6.108 | 43.7669 | 59.8258 | -2369.5411
2022-12-01 15:00 | -7658.1 | 6.108 | 44.0842 | 59.8258 | -2244.3676
2022-12-02 16:00 | -7208 | 6.108 | 44.4623 | 59.8258 | -2112.4563
2022-12-03 17:00 | -7304.93 | 6.108 | 44.4617 | 59.8258 | -2140.8637
2022-12-04 18:00 | -7343.45 | 6.108 | 44.4411 | 59.8258 | -2152.1527
2022-12-05 19:00 | -7968.06 | 6.108 | 43.9637 | 59.8258 | -2335.2079
2022-12-06 20:00 | -8060.86 | 6.108 | 43.8134 | 59.8258 | -2362.4049
2022-12-07 21:00 | -8609.62 | 6.108 | 43.3507 | 59.8258 | -2523.2305
2022-12-08 22:00 | -8873.54 | 6.108 | 43.0449 | 59.8258 | -2600.5779
2022-12-09 23:00 | -10469.8 | 6.108 | 41.7414 | 59.8258 | -3068.3955
2022-12-11 | -10537.6 | 6.108 | 41.409 | 59.8258 | -3088.2657
2022-12-12 01:00 | -10300.5 | 6.108 | 41.4185 | 59.8258 | -3018.7786
2022-12-13 02:00 | -10559.6 | 6.108 | 41.1538 | 59.8258 | -3094.7133
2022-12-14 03:00 | -10756.7 | 6.108 | 40.8949 | 59.8258 | -3152.4776
2022-12-15 04:00 | -10708.4 | 6.108 | 40.8024 | 59.8258 | -3138.3222
2022-12-16 05:00 | -11065.5 | 6.108 | 40.4704 | 59.8258 | -3242.9779
2022-12-17 06:00 | -10600.2 | 6.108 | 40.7105 | 59.8258 | -3106.612
2022-12-18 07:00 | -10882.2 | 6.108 | 40.4701 | 59.8258 | -3189.258
2022-12-19 08:00 | -10163.2 | 6.108 | 40.9326 | 59.8258 | -2978.5399
2022-12-20 09:00 | -9406.18 | 6.108 | 41.5393 | 59.8258 | -2756.6792
2022-12-21 10:00 | -7620.59 | 6.108 | 42.9903 | 59.8258 | -2233.3745
2022-12-22 11:00 | -6907.73 | 6.108 | 43.8326 | 59.8258 | -2024.4558
2022-12-23 12:00 | -5611.11 | 6.108 | 45.0627 | 59.8258 | -1644.454
2022-12-24 13:00 | -5133.81 | 6.108 | 45.7481 | 59.8258 | -1504.5712
2022-12-25 14:00 | -4552.31 | 6.108 | 46.4659 | 59.8258 | -1334.1504
2022-12-26 15:00 | -4596.62 | 6.108 | 46.7012 | 59.8258 | -1347.1363
2022-12-27 16:00 | -4413.92 | 6.108 | 47.0051 | 59.8258 | -1293.5923
2022-12-28 17:00 | -5227.13 | 6.108 | 46.5527 | 59.8258 | -1531.9206
2022-12-29 18:00 | -6099.45 | 6.108 | 45.9029 | 59.8258 | -1787.5723
2022-12-30 19:00 | -7142.08 | 6.108 | 45.0433 | 59.8258 | -2093.137
2022-12-31 20:00 | -7906.8 | 6.108 | 44.3073 | 59.8258 | -2317.2543
2023-01-01 21:00 | -8874.46 | 6.108 | 43.4043 | 59.8258 | -2600.8475
2023-01-02 22:00 | -9385.9 | 6.108 | 42.7712 | 59.8258 | -2750.7358
2023-01-03 23:00 | -9760.2 | 6.108 | 42.2767 | 59.8258 | -2860.4323
2023-01-05 | -9857.66 | 6.108 | 42.0136 | 59.8258 | -2888.995
2023-01-06 01:00 | -10512.3 | 6.108 | 41.3764 | 59.8258 | -3080.851
2023-01-07 02:00 | -10962.3 | 6.108 | 40.8338 | 59.8258 | -3212.733
2023-01-08 03:00 | -10652 | 6.108 | 40.8683 | 59.8258 | -3121.793
2023-01-09 04:00 | -10566.4 | 6.108 | 40.8366 | 59.8258 | -3096.7062
2023-01-10 05:00 | -10225.6 | 6.108 | 41.0269 | 59.8258 | -2996.8275
2023-01-11 06:00 | -9875.89 | 6.108 | 41.2638 | 59.8258 | -2894.3376
2023-01-12 07:00 | -9893.8 | 6.108 | 41.276 | 59.8258 | -2899.5866
2023-01-13 08:00 | -8895.71 | 6.108 | 42.0321 | 59.8258 | -2607.0752
2023-01-14 09:00 | -8220.75 | 6.108 | 42.6731 | 59.8258 | -2409.264
2023-01-15 10:00 | -7363.58 | 6.108 | 43.4773 | 59.8258 | -2158.0523
2023-01-16 11:00 | -6088.88 | 6.108 | 44.6291 | 59.8258 | -1784.4746
2023-01-17 12:00 | -5690.33 | 6.108 | 45.2044 | 59.8258 | -1667.6711
2023-01-18 13:00 | -4400.27 | 6.108 | 46.4036 | 59.8258 | -1289.5918
2023-01-19 14:00 | -3558.22 | 6.108 | 47.3546 | 59.8258 | -1042.8113
2023-01-20 15:00 | -3432.57 | 6.108 | 47.7727 | 59.8258 | -1005.987
2023-01-21 16:00 | -2706.23 | 6.108 | 48.5431 | 59.8258 | -793.1177
2023-01-22 17:00 | -3073.36 | 6.108 | 48.5271 | 59.8258 | -900.7129
2023-01-23 18:00 | -4470.91 | 6.108 | 47.6352 | 59.8258 | -1310.2944
2023-01-24 19:00 | -5399.9 | 6.108 | 46.879 | 59.8258 | -1582.5545
2023-01-25 20:00 | -5739.11 | 6.108 | 46.5074 | 59.8258 | -1681.9671
2023-01-26 21:00 | -7016.03 | 6.108 | 45.4846 | 59.8258 | -2056.1954
2023-01-27 22:00 | -7649.32 | 6.108 | 44.7975 | 59.8258 | -2241.7944
2023-01-28 23:00 | -8571 | 6.108 | 43.8938 | 59.8258 | -2511.9121
2023-01-30 | -9055.82 | 6.108 | 43.3029 | 59.8258 | -2653.9989
2023-01-31 01:00 | -9463.72 | 6.108 | 42.7889 | 59.8258 | -2773.5425
2023-02-01 02:00 | -10400.4 | 6.108 | 41.882 | 59.8258 | -3048.0564
2023-02-02 03:00 | -10687.1 | 6.108 | 41.4011 | 59.8258 | -3132.0798
2023-02-03 04:00 | -10397.4 | 6.108 | 41.3913 | 59.8258 | -3047.1771
2023-02-04 05:00 | -10659.2 | 6.108 | 41.0804 | 59.8258 | -3123.9031
2023-02-05 06:00 | -9838.73 | 6.108 | 41.5651 | 59.8258 | -2883.4471
2023-02-06 07:00 | -10431.2 | 6.108 | 41.1239 | 59.8258 | -3057.0829
2023-02-07 08:00 | -9126.63 | 6.108 | 42.0062 | 59.8258 | -2674.7512
2023-02-08 09:00 | -7982.16 | 6.108 | 42.9728 | 59.8258 | -2339.3402
2023-02-09 10:00 | -6150.61 | 6.108 | 44.5476 | 59.8258 | -1802.5659
2023-02-10 11:00 | -4823.71 | 6.108 | 45.8872 | 59.8258 | -1413.6899
2023-02-11 12:00 | -4704.5 | 6.108 | 46.3328 | 59.8258 | -1378.7528
2023-02-12 13:00 | -3603.56 | 6.108 | 47.4005 | 59.8258 | -1056.0992
2023-02-13 14:00 | -4028.46 | 6.108 | 47.3944 | 59.8258 | -1180.6251
2023-02-14 15:00 | -3840.1 | 6.108 | 47.6982 | 59.8258 | -1125.4222
2023-02-15 16:00 | -3662.52 | 6.108 | 47.9568 | 59.8258 | -1073.3787
2023-02-16 17:00 | -4802.4 | 6.108 | 47.2294 | 59.8258 | -1407.4445
2023-02-17 18:00 | -5790.74 | 6.108 | 46.4413 | 59.8258 | -1697.0984
2023-02-18 19:00 | -7038.1 | 6.108 | 45.3725 | 59.8258 | -2062.6635
2023-02-19 20:00 | -7601.28 | 6.108 | 44.7417 | 59.8258 | -2227.7153
2023-02-20 21:00 | -8763.58 | 6.108 | 43.6843 | 59.8258 | -2568.3518
2023-02-21 22:00 | -9559.59 | 6.108 | 42.7975 | 59.8258 | -2801.6393
2023-02-22 23:00 | -10682.7 | 6.108 | 41.6602 | 59.8258 | -3130.7903
2023-02-24 | -11052.5 | 6.108 | 41.0473 | 59.8258 | -3239.168
2023-02-25 01:00 | -11496 | 6.108 | 40.4436 | 59.8258 | -3369.145
2023-02-26 02:00 | -11769 | 6.108 | 39.9926 | 59.8258 | -3449.1534
2023-02-27 03:00 | -11970.6 | 6.108 | 39.6221 | 59.8258 | -3508.2366
2023-02-28 04:00 | -12130.3 | 6.108 | 39.3011 | 59.8258 | -3555.04
2023-03-01 05:00 | -12095.7 | 6.108 | 39.1661 | 59.8258 | -3544.8997
2023-03-02 06:00 | -11847.3 | 6.108 | 39.2276 | 59.8258 | -3472.1009
2023-03-03 07:00 | -11519.3 | 6.108 | 39.4155 | 59.8258 | -3375.9736
2023-03-04 08:00 | -9624.35 | 6.108 | 40.8186 | 59.8258 | -2820.6186
2023-03-05 09:00 | -7732.53 | 6.108 | 42.4647 | 59.8258 | -2266.1808
2023-03-06 10:00 | -6438.27 | 6.108 | 43.7944 | 59.8258 | -1886.8707
2023-03-07 11:00 | -4625.82 | 6.108 | 45.5139 | 59.8258 | -1355.694
2023-03-08 12:00 | -3329.01 | 6.108 | 46.948 | 59.8258 | -975.6365
2023-03-09 13:00 | -2522.73 | 6.108 | 48.0274 | 59.8258 | -739.3392
2023-03-10 14:00 | -2212.25 | 6.108 | 48.6672 | 59.8258 | -648.3465
2023-03-11 15:00 | -2272.65 | 6.108 | 48.9369 | 59.8258 | -666.048
2023-03-12 16:00 | -2486.4 | 6.108 | 49.0056 | 59.8258 | -728.6919
2023-03-13 17:00 | -3460.5 | 6.108 | 48.4334 | 59.8258 | -1014.1724
2023-03-14 18:00 | -3913.84 | 6.108 | 48.1103 | 59.8258 | -1147.0333
2023-03-15 19:00 | -4841.49 | 6.108 | 47.422 | 59.8258 | -1418.9007
2023-03-16 20:00 | -5343.83 | 6.108 | 46.9608 | 59.8258 | -1566.122
2023-03-17 21:00 | -6484.14 | 6.108 | 46.0119 | 59.8258 | -1900.3138
2023-03-18 22:00 | -6682.52 | 6.108 | 45.6713 | 59.8258 | -1958.4533
2023-03-19 23:00 | -7699.53 | 6.108 | 44.7855 | 59.8258 | -2256.5095
2023-03-21 | -8310.77 | 6.108 | 44.1134 | 59.8258 | -2435.6463
2023-03-22 01:00 | -8634.3 | 6.108 | 43.6553 | 59.8258 | -2530.4635
2023-03-23 02:00 | -8672.51 | 6.108 | 43.4513 | 59.8258 | -2541.6618
2023-03-24 03:00 | -9094.85 | 6.108 | 43.0219 | 59.8258 | -2665.4374
2023-03-25 04:00 | -8847.59 | 6.108 | 43.0585 | 59.8258 | -2592.9727
2023-03-26 05:00 | -9008.38 | 6.108 | 42.8842 | 59.8258 | -2640.0956
2023-03-27 06:00 | -8820.65 | 6.108 | 42.9642 | 59.8258 | -2585.0773
2023-03-28 07:00 | -7954.04 | 6.108 | 43.6016 | 59.8258 | -2331.099
2023-03-29 08:00 | -7136.4 | 6.108 | 44.3074 | 59.8258 | -2091.4724
2023-03-30 09:00 | -7378.36 | 6.108 | 44.2778 | 59.8258 | -2162.3839
2023-03-31 10:00 | -6184.58 | 6.108 | 45.1974 | 59.8258 | -1812.5215
2023-04-01 11:00 | -5625.82 | 6.108 | 45.7896 | 59.8258 | -1648.7651
2023-04-02 12:00 | -2984.38 | 6.108 | 47.9555 | 59.8258 | -874.6354
2023-04-03 13:00 | -1828.24 | 6.108 | 49.2677 | 59.8258 | -535.8043
2023-04-04 14:00 | -1629.31 | 5.3327 | 49.6501 | 59.8258 | -477.5036
2023-04-05 15:00 | -1096.76 | 3.6423 | 49.9602 | 59.8258 | -321.4286
2023-04-06 16:00 | -1088.15 | 3.7829 | 50.3058 | 59.8258 | -318.9053
2023-04-07 17:00 | -981.7 | 3.4087 | 50.5508 | 59.8258 | -287.7079
2023-04-08 18:00 | -2456.16 | 6.108 | 50.2191 | 59.8258 | -719.8294
2023-04-09 19:00 | -3780.67 | 6.108 | 49.1789 | 59.8258 | -1108.005
2023-04-10 20:00 | -4910.68 | 6.108 | 48.1744 | 59.8258 | -1439.1782
2023-04-11 21:00 | -5314.3 | 6.108 | 47.6895 | 59.8258 | -1557.4676
2023-04-12 22:00 | -6211.6 | 6.108 | 46.8798 | 59.8258 | -1820.4403
2023-04-13 23:00 | -6548.34 | 6.108 | 46.4309 | 59.8258 | -1919.129
2023-04-15 | -8090.39 | 6.108 | 45.1037 | 59.8258 | -2371.0593
2023-04-16 01:00 | -8785.69 | 6.108 | 44.2696 | 59.8258 | -2574.8316
2023-04-17 02:00 | -9223.04 | 6.108 | 43.661 | 59.8258 | -2703.0062
2023-04-18 03:00 | -9027.94 | 6.108 | 43.5676 | 59.8258 | -2645.828
2023-04-19 04:00 | -9084.92 | 6.108 | 43.3813 | 59.8258 | -2662.5272
2023-04-20 05:00 | -8795.06 | 6.108 | 43.4587 | 59.8258 | -2577.5776
2023-04-21 06:00 | -9211.13 | 6.108 | 43.0912 | 59.8258 | -2699.5157
2023-04-22 07:00 | -8381 | 6.108 | 43.614 | 59.8258 | -2456.2286
2023-04-23 08:00 | -7661.05 | 6.108 | 44.195 | 59.8258 | -2245.2321
2023-04-24 09:00 | -7701.13 | 6.108 | 44.2638 | 59.8258 | -2256.9784
2023-04-25 10:00 | -7061.45 | 6.108 | 44.7663 | 59.8258 | -2069.5067
2023-04-26 11:00 | -5422.48 | 6.108 | 46.0729 | 59.8258 | -1589.172
2023-04-27 12:00 | -5186.49 | 6.108 | 46.5205 | 59.8258 | -1520.0102
2023-04-28 13:00 | -4856.08 | 6.108 | 46.9315 | 59.8258 | -1423.1766
2023-04-29 14:00 | -4618.58 | 6.108 | 47.2333 | 59.8258 | -1353.5722
2023-04-30 15:00 | -4508.09 | 6.108 | 47.4399 | 59.8258 | -1321.1908
2023-05-01 16:00 | -4472.05 | 6.108 | 47.566 | 59.8258 | -1310.6285
2023-05-02 17:00 | -3360.83 | 6.108 | 48.4521 | 59.8258 | -984.962
2023-05-03 18:00 | -4213.27 | 6.108 | 48.0226 | 59.8258 | -1234.7875
2023-05-04 19:00 | -4606.97 | 6.108 | 47.7506 | 59.8258 | -1350.1696
2023-05-05 20:00 | -5062.35 | 6.108 | 47.3844 | 59.8258 | -1483.6283
2023-05-06 21:00 | -5314.55 | 6.108 | 47.1668 | 59.8258 | -1557.5409
2023-05-07 22:00 | -5850.77 | 6.108 | 46.7394 | 59.8258 | -1714.6914
2023-05-08 23:00 | -6056.13 | 6.108 | 46.4795 | 59.8258 | -1774.8765
2023-05-10 | -7535.2 | 6.108 | 45.3027 | 59.8258 | -2208.3491
2023-05-11 01:00 | -7770.05 | 6.108 | 44.897 | 59.8258 | -2277.1769
2023-05-12 02:00 | -7764.16 | 6.108 | 44.7462 | 59.8258 | -2275.4507
2023-05-13 03:00 | -7758.2 | 6.108 | 44.6664 | 59.8258 | -2273.704
2023-05-14 04:00 | -7563.79 | 6.108 | 44.7482 | 59.8258 | -2216.728
2023-05-15 05:00 | -7765.88 | 6.108 | 44.5492 | 59.8258 | -2275.9548
2023-05-16 06:00 | -7689.34 | 6.108 | 44.5641 | 59.8258 | -2253.5231
2023-05-17 07:00 | -6935.45 | 6.108 | 45.1075 | 59.8258 | -2032.5798
2023-05-18 08:00 | -6604.35 | 6.108 | 45.4358 | 59.8258 | -1935.5439
2023-05-19 09:00 | -6925.97 | 6.108 | 45.2742 | 59.8258 | -2029.8014
2023-05-20 10:00 | -6079.98 | 6.108 | 45.8925 | 59.8258 | -1781.8662
2023-05-21 11:00 | -5555.26 | 6.108 | 46.3872 | 59.8258 | -1628.086
2023-05-22 12:00 | -4922.85 | 6.108 | 47.0022 | 59.8258 | -1442.7449
2023-05-23 13:00 | -4701.39 | 6.108 | 47.3136 | 59.8258 | -1377.8414
2023-05-24 14:00 | -4403.4 | 6.108 | 47.6491 | 59.8258 | -1290.5091
2023-05-25 15:00 | -3941.38 | 6.108 | 48.1188 | 59.8258 | -1155.1045
2023-05-26 16:00 | -4224.78 | 6.108 | 48.045 | 59.8258 | -1238.1608
2023-05-27 17:00 | -2847.31 | 6.108 | 49.1265 | 59.8258 | -834.4642
2023-05-28 18:00 | -3604.25 | 6.108 | 48.7914 | 59.8258 | -1056.3014
2023-05-29 19:00 | -4185.82 | 6.108 | 48.4084 | 59.8258 | -1226.7427
2023-05-30 20:00 | -4765.78 | 6.108 | 47.939 | 59.8258 | -1396.7122
2023-05-31 21:00 | -5125.73 | 6.108 | 47.6128 | 59.8258 | -1502.2032
2023-06-01 22:00 | -5654.63 | 6.108 | 47.1678 | 59.8258 | -1657.2085
2023-06-02 23:00 | -5689.21 | 6.108 | 47.0288 | 59.8258 | -1667.3429
2023-06-04 | -6953.62 | 6.108 | 46.0286 | 59.8258 | -2037.9049
2023-06-05 01:00 | -7113.15 | 6.108 | 45.7188 | 59.8258 | -2084.6585
2023-06-06 02:00 | -7214.71 | 6.108 | 45.5178 | 59.8258 | -2114.4228
2023-06-07 03:00 | -7652.11 | 6.108 | 45.1058 | 59.8258 | -2242.6121
2023-06-08 04:00 | -7463.48 | 6.108 | 45.1302 | 59.8258 | -2187.3301
2023-06-09 05:00 | -7076.32 | 6.108 | 45.3451 | 59.8258 | -2073.8647
2023-06-10 06:00 | -6430.68 | 6.108 | 45.8499 | 59.8258 | -1884.6463
2023-06-11 07:00 | -6416.59 | 6.108 | 45.9424 | 59.8258 | -1880.5169
2023-06-12 08:00 | -6257.39 | 6.108 | 46.0967 | 59.8258 | -1833.86
2023-06-13 09:00 | -6601.63 | 6.108 | 45.8848 | 59.8258 | -1934.7468
2023-06-14 10:00 | -5842.25 | 6.108 | 46.4373 | 59.8258 | -1712.1945
2023-06-15 11:00 | -5169.17 | 6.108 | 47.0251 | 59.8258 | -1514.9342
2023-06-16 12:00 | -4623.77 | 6.108 | 47.5699 | 59.8258 | -1355.0932
2023-06-17 13:00 | -4142.68 | 6.108 | 48.0736 | 59.8258 | -1214.0997
2023-06-18 14:00 | -1719.11 | 5.7502 | 49.9613 | 59.8258 | -503.8214
2023-06-19 15:00 | -1098.53 | 3.5791 | 50.3659 | 59.8258 | -321.9474
2023-06-20 16:00 | -408.391 | 1.5703 | 50.9347 | 59.8258 | -119.6876
2023-06-21 17:00 | -810.75 | 3.0589 | 51.2158 | 59.8258 | -237.6074
2023-06-22 18:00 | -1887.32 | 6.108 | 51.1928 | 59.8258 | -553.1189
2023-06-23 19:00 | -3290.08 | 6.108 | 50.1622 | 59.8258 | -964.2273
2023-06-24 20:00 | -4345.95 | 6.108 | 49.2217 | 59.8258 | -1273.6722
2023-06-25 21:00 | -5575.41 | 6.108 | 48.1174 | 59.8258 | -1633.9914
2023-06-26 22:00 | -6387.35 | 6.108 | 47.2461 | 59.8258 | -1871.9475
2023-06-27 23:00 | -7558.03 | 6.108 | 46.1052 | 59.8258 | -2215.0399
2023-06-29 | -7526.79 | 6.108 | 45.8261 | 59.8258 | -2205.8844
2023-06-30 01:00 | -8220.29 | 6.108 | 45.1318 | 59.8258 | -2409.1292
2023-07-01 02:00 | -8377.83 | 6.108 | 44.7798 | 59.8258 | -2455.2996
2023-07-02 03:00 | -8607.38 | 6.108 | 44.4158 | 59.8258 | -2522.5741
2023-07-03 04:00 | -8624.1 | 6.108 | 44.2218 | 59.8258 | -2527.4742
2023-07-04 05:00 | -8653.17 | 6.108 | 44.0655 | 59.8258 | -2535.9938
2023-07-05 06:00 | -8494.27 | 6.108 | 44.0627 | 59.8258 | -2489.4248
2023-07-06 07:00 | -8304.63 | 6.108 | 44.1361 | 59.8258 | -2433.8468
2023-07-07 08:00 | -6354.71 | 6.108 | 45.5655 | 59.8258 | -1862.3817
2023-07-08 09:00 | -5001.84 | 6.108 | 46.8209 | 59.8258 | -1465.8946
2023-07-09 10:00 | -2821.12 | 6.108 | 48.7633 | 59.8258 | -826.7887
2023-07-10 11:00 | -1124.39 | 3.6841 | 49.943 | 59.8258 | -329.5262
2023-07-11 12:00 | 2302.82 | 1 | 51.657 | 59.8258 | 674.8899
2023-07-12 13:00 | 3127.47 | 1 | 52.3905 | 59.8258 | 916.571
2023-07-13 14:00 | 3181.9 | 1 | 71.9195 | 59.8258 | 932.5228
2023-07-14 15:00 | 3155.2 | 1.0082 | 68.0003 | 59.8258 | 924.6978
2023-07-15 16:00 | 3130.41 | 1 | 70.2634 | 59.8258 | 917.4326
2023-07-16 17:00 | 2981.21 | 1 | 54.0305 | 59.8258 | 873.7064
2023-07-17 18:00 | 0 | 0 | 54.4977 | 59.8258 | 0
2023-07-18 19:00 | -1222.75 | 3.9459 | 52.8651 | 59.8258 | -358.3527
2023-07-19 20:00 | -1696.55 | 5.5489 | 52.6716 | 59.8258 | -497.2097
2023-07-20 21:00 | -3378.55 | 6.108 | 51.4254 | 59.8258 | -990.1553
2023-07-21 22:00 | -3895.04 | 6.108 | 50.745 | 59.8258 | -1141.5235
2023-07-22 23:00 | -4960.1 | 6.108 | 49.6865 | 59.8258 | -1453.6618
2023-07-24 | -5249.76 | 6.108 | 49.1852 | 59.8258 | -1538.5528
2023-07-25 01:00 | -5501.05 | 6.108 | 48.7767 | 59.8258 | -1612.1986
2023-07-26 02:00 | -5655.44 | 6.108 | 48.4721 | 59.8258 | -1657.4459
2023-07-27 03:00 | -5607.99 | 6.108 | 48.3632 | 59.8258 | -1643.5396
2023-07-28 04:00 | -5519.94 | 6.108 | 48.3208 | 59.8258 | -1617.7347
2023-07-29 05:00 | -5367.83 | 6.108 | 48.3656 | 59.8258 | -1573.1557
2023-07-30 06:00 | -5179.1 | 6.108 | 48.4903 | 59.8258 | -1517.8444
2023-07-31 07:00 | -5276.94 | 6.108 | 48.4312 | 59.8258 | -1546.5185
2023-08-01 08:00 | -3929.92 | 6.108 | 49.4232 | 59.8258 | -1151.7459
2023-08-02 09:00 | -3352.77 | 6.108 | 50.0327 | 59.8258 | -982.5999
2023-08-03 10:00 | -2800.04 | 6.108 | 50.6161 | 59.8258 | -820.6107
2023-08-04 11:00 | -1790.71 | 5.7739 | 51.4538 | 59.8258 | -524.8053
2023-08-05 12:00 | -1163.95 | 3.7225 | 51.6619 | 59.8258 | -341.1201
2023-08-06 13:00 | -875.497 | 3.0108 | 51.9907 | 59.8258 | -256.5828
2023-08-07 14:00 | -185.85 | 0.90509 | 52.5422 | 59.8258 | -54.4673
2023-08-08 15:00 | 336.643 | 1 | 53.6597 | 59.8258 | 98.6603
2023-08-09 16:00 | 2676.59 | 1 | 53.6632 | 59.8258 | 784.4311
2023-08-10 17:00 | 3039.67 | 1 | 54.0816 | 59.8258 | 890.8393
2023-08-11 18:00 | 2899.29 | 1 | 54.4491 | 59.8258 | 849.698
2023-08-12 19:00 | -273.042 | 1.444 | 54.0753 | 59.8258 | -80.0207
2023-08-13 20:00 | -783.163 | 2.8941 | 53.4809 | 59.8258 | -229.5224
2023-08-14 21:00 | -1841.66 | 6.0751 | 53.2262 | 59.8258 | -539.7373
2023-08-15 22:00 | -2563.7 | 6.108 | 52.5231 | 59.8258 | -751.3463
2023-08-16 23:00 | -3765.99 | 6.108 | 51.4217 | 59.8258 | -1103.7027
2023-08-18 | -4021.27 | 6.108 | 50.9428 | 59.8258 | -1178.5179
2023-08-19 01:00 | -4457.15 | 6.108 | 50.4608 | 59.8258 | -1306.2617
2023-08-20 02:00 | -4618.81 | 6.108 | 50.1864 | 59.8258 | -1353.6396
2023-08-21 03:00 | -4185.62 | 6.108 | 50.3892 | 59.8258 | -1226.6841
2023-08-22 04:00 | -4406.33 | 6.108 | 50.1743 | 59.8258 | -1291.3678
2023-08-23 05:00 | -4532.69 | 6.108 | 50.0033 | 59.8258 | -1328.4003
2023-08-24 06:00 | -3394.22 | 6.108 | 50.767 | 59.8258 | -994.7477
2023-08-25 07:00 | -3312.6 | 6.108 | 50.9548 | 59.8258 | -970.8272
2023-08-26 08:00 | -2402.92 | 6.108 | 51.7082 | 59.8258 | -704.2263
2023-08-27 09:00 | -1931.4 | 6.108 | 52.2082 | 59.8258 | -566.0375
2023-08-28 10:00 | -1356.04 | 4.2607 | 52.3531 | 59.8258 | -397.4161
2023-08-29 11:00 | -374.893 | 1.3594 | 52.7256 | 59.8258 | -109.8703
2023-08-30 12:00 | 2276.11 | 1 | 54.0246 | 59.8258 | 667.062
2023-08-31 13:00 | 2065.7 | 1 | 54.5564 | 59.8258 | 605.3969
2023-09-01 14:00 | 3177.9 | 1 | 54.7355 | 59.8258 | 931.3506
2023-09-02 15:00 | 3162.84 | 1 | 75.2425 | 59.8258 | 926.9369
2023-09-03 16:00 | 3342.45 | 1.0603 | 70.0018 | 59.8258 | 979.5754
2023-09-04 17:00 | 3138.99 | 1 | 73.1189 | 59.8258 | 919.9472
2023-09-05 18:00 | 3009.95 | 1 | 55.6453 | 59.8258 | 882.1293
2023-09-06 19:00 | 0 | 0 | 56.0474 | 59.8258 | 0
2023-09-07 20:00 | -437.043 | 1.5534 | 54.4552 | 59.8258 | -128.0847
2023-09-08 21:00 | -1311.76 | 4.4745 | 54.2295 | 59.8258 | -384.4389
2023-09-09 22:00 | -1820.35 | 5.7844 | 53.9621 | 59.8258 | -533.4919
2023-09-10 23:00 | -2564.21 | 6.108 | 53.3112 | 59.8258 | -751.4958
2023-09-12 | -2681.25 | 6.108 | 52.9871 | 59.8258 | -785.7968
2023-09-13 01:00 | -2529.71 | 6.108 | 52.9834 | 59.8258 | -741.3848
2023-09-14 02:00 | -2581 | 6.108 | 52.88 | 59.8258 | -756.4164
2023-09-15 03:00 | -2525.18 | 6.108 | 52.8636 | 59.8258 | -740.0572
2023-09-16 04:00 | -2641.67 | 6.108 | 52.7338 | 59.8258 | -774.1971
2023-09-17 05:00 | -2783 | 6.108 | 52.5869 | 59.8258 | -815.6168
2023-09-18 06:00 | -2786.84 | 6.108 | 52.5243 | 59.8258 | -816.7422
2023-09-19 07:00 | -1949.27 | 6.108 | 53.1344 | 59.8258 | -571.2746
2023-09-20 08:00 | -1402.7 | 4.356 | 53.2157 | 59.8258 | -411.0908
2023-09-21 09:00 | -1705.46 | 5.4809 | 53.3944 | 59.8258 | -499.821
2023-09-22 10:00 | -1675.26 | 5.2673 | 53.3891 | 59.8258 | -490.9702
2023-09-23 11:00 | -1159.03 | 3.6725 | 53.4273 | 59.8258 | -339.6782
2023-09-24 12:00 | -452.456 | 1.6438 | 53.7007 | 59.8258 | -132.6018
2023-09-25 13:00 | -89.1343 | 0.73349 | 54.542 | 59.8258 | -26.1227
2023-09-26 14:00 | -77.2688 | 0.78602 | 54.7517 | 59.8258 | -22.6452
2023-09-27 15:00 | 60.7128 | 1 | 55.2617 | 59.8258 | 17.7932
2023-09-28 16:00 | 129.052 | 1 | 55.3166 | 59.8258 | 37.8214
2023-09-29 17:00 | 2708.61 | 1 | 55.1443 | 59.8258 | 793.8152
2023-09-30 18:00 | 2998.56 | 1 | 55.5041 | 59.8258 | 878.7912
2023-10-01 19:00 | 0 | 0 | 56.0551 | 59.8258 | 0
2023-10-02 20:00 | -471.926 | 1.9689 | 54.7262 | 59.8258 | -138.3079
2023-10-03 21:00 | -675.168 | 2.4798 | 54.4558 | 59.8258 | -197.8722
2023-10-04 22:00 | -1031.81 | 3.5227 | 54.3484 | 59.8258 | -302.3937
2023-10-05 23:00 | -1263 | 4.1363 | 54.203 | 59.8258 | -370.1488
2023-10-07 | -2676.97 | 6.108 | 53.4912 | 59.8258 | -784.5425
2023-10-08 01:00 | -3154.48 | 6.108 | 52.9243 | 59.8258 | -924.4868
2023-10-09 02:00 | -3394.48 | 6.108 | 52.5703 | 59.8258 | -994.8239
2023-10-10 03:00 | -3514.28 | 6.108 | 52.3517 | 59.8258 | -1029.9338
2023-10-11 04:00 | -3612.65 | 6.108 | 52.1713 | 59.8258 | -1058.7632
2023-10-12 05:00 | -3839.96 | 6.108 | 51.8731 | 59.8258 | -1125.3812
2023-10-13 06:00 | -3910.64 | 6.108 | 51.6959 | 59.8258 | -1146.0954
2023-10-14 07:00 | -3221.71 | 6.108 | 52.1343 | 59.8258 | -944.19
2023-10-15 08:00 | -2520.08 | 6.108 | 52.6903 | 59.8258 | -738.5625
2023-10-16 09:00 | -3124.22 | 6.108 | 52.33 | 59.8258 | -915.6185
2023-10-17 10:00 | -2696.39 | 6.108 | 52.5959 | 59.8258 | -790.2339
2023-10-18 11:00 | -2179.43 | 6.108 | 52.9968 | 59.8258 | -638.7279
2023-10-19 12:00 | -1736.05 | 5.415 | 53.2411 | 59.8258 | -508.786
2023-10-20 13:00 | -1866.77 | 5.8807 | 53.338 | 59.8258 | -547.0963
2023-10-21 14:00 | -2085.93 | 6.108 | 53.2323 | 59.8258 | -611.3257
2023-10-22 15:00 | -2086.78 | 6.108 | 53.2119 | 59.8258 | -611.5748
2023-10-23 16:00 | -2094.61 | 6.108 | 53.1933 | 59.8258 | -613.8696
2023-10-24 17:00 | -945.277 | 2.9288 | 53.2517 | 59.8258 | -277.0333
2023-10-25 18:00 | -1424.03 | 4.7402 | 53.4806 | 59.8258 | -417.342
2023-10-26 19:00 | -1799.03 | 5.7314 | 53.4373 | 59.8258 | -527.2436
2023-10-27 20:00 | -2239.81 | 6.108 | 53.1519 | 59.8258 | -656.4235
2023-10-28 21:00 | -2534.55 | 6.108 | 52.8782 | 59.8258 | -742.8033
2023-10-29 22:00 | -2476.72 | 6.108 | 52.8667 | 59.8258 | -725.855
2023-10-30 23:00 | -2781.05 | 6.108 | 52.5972 | 59.8258 | -815.0453
2023-11-01 | -3758.22 | 6.108 | 51.8043 | 59.8258 | -1101.4256
2023-11-02 01:00 | -3946.47 | 6.108 | 51.4969 | 59.8258 | -1156.5962
2023-11-03 02:00 | -4155.69 | 6.108 | 51.2295 | 59.8258 | -1217.9125
2023-11-04 03:00 | -4138.7 | 6.108 | 51.1543 | 59.8258 | -1212.9332
2023-11-05 04:00 | -4081.39 | 6.108 | 51.1299 | 59.8258 | -1196.1373
2023-11-06 05:00 | -3871.52 | 6.108 | 51.2293 | 59.8258 | -1134.6305
2023-11-07 06:00 | -3247.06 | 6.108 | 51.6929 | 59.8258 | -951.6193
2023-11-08 07:00 | -3225.59 | 6.108 | 51.7776 | 59.8258 | -945.3271
2023-11-09 08:00 | -2916.83 | 6.108 | 52.0389 | 59.8258 | -854.8385
2023-11-10 09:00 | -2927.16 | 6.108 | 52.0868 | 59.8258 | -857.8659
2023-11-11 10:00 | -2158.83 | 6.108 | 52.6924 | 59.8258 | -632.6906
2023-11-12 11:00 | -773.175 | 2.4039 | 52.9485 | 59.8258 | -226.5952
2023-11-13 12:00 | 0 | 1 | 54.6788 | 59.8258 | 0
2023-11-14 13:00 | 3080.03 | 1 | 54.6628 | 59.8258 | 902.6677
2023-11-15 14:00 | 3069.09 | 1 | 55.2422 | 59.8258 | 899.4615
2023-11-16 15:00 | 3145.3 | 1 | 55.6093 | 59.8258 | 921.7964
2023-11-17 16:00 | 3133.04 | 1 | 55.8677 | 59.8258 | 918.2034
2023-11-18 17:00 | 3151.17 | 1 | 56.0682 | 59.8258 | 923.5168
2023-11-19 18:00 | 3054.61 | 1 | 56.258 | 59.8258 | 895.2178
2023-11-20 19:00 | -374.701 | 1.7059 | 55.6307 | 59.8258 | -109.814
2023-11-21 20:00 | -962.935 | 3.3585 | 54.9749 | 59.8258 | -282.2084
2023-11-22 21:00 | -2187.59 | 6.108 | 54.4225 | 59.8258 | -641.1193
2023-11-23 22:00 | -2567.07 | 6.108 | 53.8865 | 59.8258 | -752.334
2023-11-24 23:00 | -3255.63 | 6.108 | 53.1449 | 59.8258 | -954.131
2023-11-26 | -3551.16 | 6.108 | 52.6721 | 59.8258 | -1040.7423
2023-11-27 01:00 | -4035.89 | 6.108 | 52.1159 | 59.8258 | -1182.8026
2023-11-28 02:00 | -4044.58 | 6.108 | 51.9063 | 59.8258 | -1185.3494
2023-11-29 03:00 | -4466.81 | 6.108 | 51.4502 | 59.8258 | -1309.0928
2023-11-30 04:00 | -4329.16 | 6.108 | 51.3819 | 59.8258 | -1268.7516
2023-12-01 05:00 | -4385.65 | 6.108 | 51.2271 | 59.8258 | -1285.3071
2023-12-02 06:00 | -3846.13 | 6.108 | 51.5208 | 59.8258 | -1127.1894
2023-12-03 07:00 | -3761.73 | 6.108 | 51.5931 | 59.8258 | -1102.4542
2023-12-04 08:00 | -3521.84 | 6.108 | 51.7659 | 59.8258 | -1032.1494
2023-12-05 09:00 | -3617.43 | 6.108 | 51.7219 | 59.8258 | -1060.1641
2023-12-06 10:00 | -3515.94 | 6.108 | 51.7898 | 59.8258 | -1030.4203
2023-12-07 11:00 | -1965.55 | 6.108 | 52.9532 | 59.8258 | -576.0458
2023-12-08 12:00 | -1135.21 | 3.523 | 53.1395 | 59.8258 | -332.6972
2023-12-09 13:00 | -414.811 | 1.5458 | 53.584 | 59.8258 | -121.5691
2023-12-10 14:00 | 0 | 0 | 55.0091 | 59.8258 | 0
2023-12-11 15:00 | 2801.39 | 1 | 54.9485 | 59.8258 | 821.0064
2023-12-12 16:00 | 2857.17 | 1 | 55.4589 | 59.8258 | 837.3539
2023-12-13 17:00 | 96.1092 | 1 | 56.0113 | 59.8258 | 28.1668
2023-12-14 18:00 | -856.842 | 3.1345 | 54.5765 | 59.8258 | -251.1156
2023-12-15 19:00 | -2100.98 | 6.108 | 54.1 | 59.8258 | -615.7365
2023-12-16 20:00 | -2941.04 | 6.108 | 53.2863 | 59.8258 | -861.9337
2023-12-17 21:00 | -4253.86 | 6.108 | 52.0532 | 59.8258 | -1246.6833
2023-12-18 22:00 | -4805.11 | 6.108 | 51.3018 | 59.8258 | -1408.2387
2023-12-19 23:00 | -6234.63 | 6.108 | 49.9713 | 59.8258 | -1827.1897
2023-12-21 | -7099.74 | 6.108 | 48.9613 | 59.8258 | -2080.7284
2023-12-22 01:00 | -7269.66 | 6.108 | 48.4792 | 59.8258 | -2130.527
2023-12-23 02:00 | -7771.5 | 6.108 | 47.8396 | 59.8258 | -2277.6018
2023-12-24 03:00 | -8034.8 | 6.108 | 47.3497 | 59.8258 | -2354.7674
2023-12-25 04:00 | -8001.08 | 6.108 | 47.0929 | 59.8258 | -2344.8851
2023-12-26 05:00 | -8103.19 | 6.108 | 46.8356 | 59.8258 | -2374.8106
2023-12-27 06:00 | -8104.49 | 6.108 | 46.6722 | 59.8258 | -2375.1916
2023-12-28 07:00 | -7614.51 | 6.108 | 46.8993 | 59.8258 | -2231.5926
2023-12-29 08:00 | -6096.33 | 6.108 | 47.9892 | 59.8258 | -1786.658
2023-12-30 09:00 | -4925.84 | 6.108 | 49.0214 | 59.8258 | -1443.6212
2023-12-31 10:00 | -3128.55 | 6.108 | 50.5817 | 59.8258 | -916.8875
2024-01-01 11:00 | -1331 | 4.2651 | 51.8385 | 59.8258 | -390.0776
2024-01-02 12:00 | 2233.7 | 1 | 53.5224 | 59.8258 | 654.6328
2024-01-03 13:00 | 2918.78 | 1 | 54.2081 | 59.8258 | 855.41
2024-01-04 14:00 | 2922.54 | 1 | 73.4774 | 59.8258 | 856.5119
2024-01-05 15:00 | 2888.78 | 1 | 70.9696 | 59.8258 | 846.6178
2024-01-06 16:00 | 3069.35 | 1.0569 | 68.9025 | 59.8258 | 899.5377
2024-01-07 17:00 | 2888.63 | 1 | 74.5436 | 59.8258 | 846.5739
2024-01-08 18:00 | 0 | 0 | 56.046 | 59.8258 | 0
2024-01-09 19:00 | -1391 | 4.7033 | 54.4609 | 59.8258 | -407.6619
2024-01-10 20:00 | -2675.87 | 6.108 | 53.5515 | 59.8258 | -784.2201
2024-01-11 21:00 | -4215.02 | 6.108 | 52.14 | 59.8258 | -1235.3004
2024-01-12 22:00 | -4921.83 | 6.108 | 51.2419 | 59.8258 | -1442.446
2024-01-13 23:00 | -6121.34 | 6.108 | 50.0048 | 59.8258 | -1793.9877
2024-01-15 | -6562 | 6.108 | 49.298 | 59.8258 | -1923.1324
2024-01-16 01:00 | -6938.55 | 6.108 | 48.7 | 59.8258 | -2033.4883
2024-01-17 02:00 | -7205.42 | 6.108 | 48.2319 | 59.8258 | -2111.7001
2024-01-18 03:00 | -7372.43 | 6.108 | 47.8777 | 59.8258 | -2160.6459
2024-01-19 04:00 | -7140.65 | 6.108 | 47.8424 | 59.8258 | -2092.7179
2024-01-20 05:00 | -6967.56 | 6.108 | 47.845 | 59.8258 | -2041.9903
2024-01-21 06:00 | -6461.61 | 6.108 | 48.1554 | 59.8258 | -1893.711
2024-01-22 07:00 | -6028.06 | 6.108 | 48.4838 | 59.8258 | -1766.65
2024-01-23 08:00 | -5548.5 | 6.108 | 48.8797 | 59.8258 | -1626.1048
2024-01-24 09:00 | -5803.54 | 6.108 | 48.7619 | 59.8258 | -1700.8497
2024-01-25 10:00 | -5154.61 | 6.108 | 49.2341 | 59.8258 | -1510.6671
2024-01-26 11:00 | -4288.63 | 6.108 | 49.9498 | 59.8258 | -1256.8734
2024-01-27 12:00 | -3218.3 | 6.108 | 50.8762 | 59.8258 | -943.1906
2024-01-28 13:00 | -2694.47 | 6.108 | 51.4549 | 59.8258 | -789.6712
2024-01-29 14:00 | -2443.92 | 6.108 | 51.8 | 59.8258 | -716.2422
2024-01-30 15:00 | -2433.07 | 6.108 | 51.9328 | 59.8258 | -713.0624
2024-01-31 16:00 | -1484.34 | 4.6911 | 52.3809 | 59.8258 | -435.0171
2024-02-01 17:00 | -1577.83 | 5.1012 | 52.596 | 59.8258 | -462.4163
2024-02-02 18:00 | -1788.99 | 5.7218 | 52.6883 | 59.8258 | -524.3012
2024-02-03 19:00 | -2197.13 | 6.108 | 52.5204 | 59.8258 | -643.9152
2024-02-04 20:00 | -2773.09 | 6.108 | 52.0946 | 59.8258 | -812.7125
2024-02-05 21:00 | -3796.25 | 6.108 | 51.3019 | 59.8258 | -1112.571
2024-02-06 22:00 | -4109.09 | 6.108 | 50.9249 | 59.8258 | -1204.2554
2024-02-07 23:00 | -4697.11 | 6.108 | 50.3816 | 59.8258 | -1376.5871
2024-02-09 | -4879.6 | 6.108 | 50.1141 | 59.8258 | -1430.0696
2024-02-10 01:00 | -5250.75 | 6.108 | 49.7312 | 59.8258 | -1538.8429
2024-02-11 02:00 | -5275.98 | 6.108 | 49.6015 | 59.8258 | -1546.2371
2024-02-12 03:00 | -4992.11 | 6.108 | 49.753 | 59.8258 | -1463.043
2024-02-13 04:00 | -5033.87 | 6.108 | 49.7084 | 59.8258 | -1475.2817
2024-02-14 05:00 | -4846.21 | 6.108 | 49.8278 | 59.8258 | -1420.284
2024-02-15 06:00 | -4312.39 | 6.108 | 50.2282 | 59.8258 | -1263.8368
2024-02-16 07:00 | -4175.53 | 6.108 | 50.404 | 59.8258 | -1223.727
2024-02-17 08:00 | -3529.13 | 6.108 | 50.942 | 59.8258 | -1034.2859
2024-02-18 09:00 | -3482.6 | 6.108 | 51.0953 | 59.8258 | -1020.6493
2024-02-19 10:00 | -2794.03 | 6.108 | 51.6885 | 59.8258 | -818.8494
2024-02-20 11:00 | -2321.7 | 6.108 | 52.1781 | 59.8258 | -680.4231
2024-02-21 12:00 | -1872.56 | 5.9103 | 52.5985 | 59.8258 | -548.7932
2024-02-22 13:00 | -621.293 | 1.9523 | 52.719 | 59.8258 | -182.083
2024-02-23 14:00 | 308.839 | 1 | 54.4006 | 59.8258 | 90.5118
2024-02-24 15:00 | 3130.8 | 1 | 54.4347 | 59.8258 | 917.5469
2024-02-25 16:00 | 3096.73 | 1 | 72.8929 | 59.8258 | 907.562
2024-02-26 17:00 | 3017.19 | 1 | 55.3225 | 59.8258 | 884.2511
2024-02-27 18:00 | 0 | 0 | 55.8237 | 59.8258 | 0
2024-02-28 19:00 | -1374.47 | 4.3624 | 54.1832 | 59.8258 | -402.8174
2024-02-29 20:00 | -2339.74 | 6.108 | 53.644 | 59.8258 | -685.7101
2024-03-01 21:00 | -3727.36 | 6.108 | 52.3714 | 59.8258 | -1092.3814
2024-03-02 22:00 | -4853.28 | 6.108 | 51.2036 | 59.8258 | -1422.356
2024-03-03 23:00 | -5943.42 | 6.108 | 50.0254 | 59.8258 | -1741.8445
2024-03-05 | -6627.83 | 6.108 | 49.1803 | 59.8258 | -1942.4252
2024-03-06 01:00 | -7003.95 | 6.108 | 48.5955 | 59.8258 | -2052.6551
2024-03-07 02:00 | -7430.51 | 6.108 | 48.0109 | 59.8258 | -2177.6675
2024-03-08 03:00 | -7398.27 | 6.108 | 47.7562 | 59.8258 | -2168.2189
2024-03-09 04:00 | -7826.76 | 6.108 | 47.2232 | 59.8258 | -2293.7969
2024-03-10 05:00 | -7934.98 | 6.108 | 46.9086 | 59.8258 | -2325.5131
2024-03-11 06:00 | -8283.61 | 6.108 | 46.4659 | 59.8258 | -2427.6864
2024-03-12 07:00 | -7391.54 | 6.108 | 46.9515 | 59.8258 | -2166.2465
2024-03-13 08:00 | -5468.7 | 6.108 | 48.3745 | 59.8258 | -1602.7178
2024-03-14 09:00 | -4591.41 | 6.108 | 49.2514 | 59.8258 | -1345.6094
2024-03-15 10:00 | -2986.68 | 6.108 | 50.6677 | 59.8258 | -875.3095
2024-03-16 11:00 | -1587.37 | 5.0935 | 51.8002 | 59.8258 | -465.2122
2024-03-17 12:00 | 123.681 | 1 | 53.6157 | 59.8258 | 36.2473
2024-03-18 13:00 | 3109.95 | 1 | 53.8255 | 59.8258 | 911.4364
2024-03-19 14:00 | 3190.41 | 1 | 77.4749 | 59.8258 | 935.0169
2024-03-20 15:00 | 3091.24 | 1 | 77.8002 | 59.8258 | 905.953
2024-03-21 16:00 | 3117.73 | 1 | 78.5722 | 59.8258 | 913.7165
2024-03-22 17:00 | 3643.96 | 1.168 | 69.9938 | 59.8258 | 1067.9393
2024-03-23 18:00 | 2997.48 | 1 | 55.7859 | 59.8258 | 878.4747
2024-03-24 19:00 | 0 | 0 | 56.1864 | 59.8258 | 0
2024-03-25 20:00 | -972.966 | 3.1454 | 54.4899 | 59.8258 | -285.1482
2024-03-26 21:00 | -1397.23 | 4.583 | 54.3009 | 59.8258 | -409.4877
2024-03-27 22:00 | -2232.52 | 6.108 | 53.9045 | 59.8258 | -654.287
2024-03-28 23:00 | -3069.45 | 6.108 | 53.0824 | 59.8258 | -899.567
2024-03-30 | -4567.95 | 6.108 | 51.7123 | 59.8258 | -1338.734
2024-03-31 01:00 | -5438.11 | 6.108 | 50.7206 | 59.8258 | -1593.7527
2024-04-01 02:00 | -5431.2 | 6.108 | 50.4067 | 59.8258 | -1591.7276
2024-04-02 03:00 | -4799.31 | 6.108 | 50.6756 | 59.8258 | -1406.5389
2024-04-03 04:00 | -4560.43 | 6.108 | 50.7879 | 59.8258 | -1336.5301
2024-04-04 05:00 | -4270.41 | 6.108 | 50.9481 | 59.8258 | -1251.5336
2024-04-05 06:00 | -4431.45 | 6.108 | 50.8161 | 59.8258 | -1298.7298
2024-04-06 07:00 | -3225.49 | 6.108 | 51.7098 | 59.8258 | -945.2978
2024-04-07 08:00 | -2034.29 | 6.108 | 52.7521 | 59.8258 | -596.1915
2024-04-08 09:00 | -1691.23 | 5.2807 | 53.0411 | 59.8258 | -495.6506
2024-04-09 10:00 | -645.597 | 2.0816 | 53.2415 | 59.8258 | -189.2058
2024-04-10 11:00 | 2658.64 | 1 | 54.6659 | 59.8258 | 779.1705
2024-04-11 12:00 | 3204.29 | 1 | 79.817 | 59.8258 | 939.0847
2024-04-12 13:00 | 3238.47 | 1 | 73.4962 | 59.8258 | 949.1019
2024-04-13 14:00 | 3204.21 | 1.0269 | 70.4641 | 59.8258 | 939.0613
2024-04-14 15:00 | 3165.14 | 1.0377 | 70.3606 | 59.8258 | 927.611
2024-04-15 16:00 | 3182.21 | 1 | 76.2459 | 59.8258 | 932.6137
2024-04-16 17:00 | 4241.03 | 1.2958 | 71.635 | 59.8258 | 1242.9232
2024-04-17 18:00 | 3076.97 | 1 | 81.1532 | 59.8258 | 901.7709
2024-04-18 19:00 | 3140.6 | 1 | 56.6858 | 59.8258 | 920.419
2024-04-19 20:00 | 3109.13 | 1 | 56.7789 | 59.8258 | 911.1961
2024-04-20 21:00 | -537.787 | 2.1806 | 56.037 | 59.8258 | -157.6098
2024-04-21 22:00 | -1257.96 | 4.187 | 55.4061 | 59.8258 | -368.6717
2024-04-22 23:00 | -1596.06 | 5.0422 | 55.0054 | 59.8258 | -467.759
2024-04-24 | -3368.24 | 6.108 | 53.7571 | 59.8258 | -987.1337
2024-04-25 01:00 | -3887.61 | 6.108 | 52.9982 | 59.8258 | -1139.346
2024-04-26 02:00 | -4179.65 | 6.108 | 52.4543 | 59.8258 | -1224.9345
2024-04-27 03:00 | -4595.12 | 6.108 | 51.9491 | 59.8258 | -1346.6967
2024-04-28 04:00 | -4654.83 | 6.108 | 51.7038 | 59.8258 | -1364.196
2024-04-29 05:00 | -4859.32 | 6.108 | 51.37 | 59.8258 | -1424.1261
2024-04-30 06:00 | -4631.2 | 6.108 | 51.4053 | 59.8258 | -1357.2707
2024-05-01 07:00 | -4497.07 | 6.108 | 51.4157 | 59.8258 | -1317.9611
2024-05-02 08:00 | -3364.69 | 6.108 | 52.1806 | 59.8258 | -986.0933
2024-05-03 09:00 | -2715.21 | 6.108 | 52.7711 | 59.8258 | -795.7495
2024-05-04 10:00 | -1227.95 | 3.8254 | 53.4536 | 59.8258 | -359.8766
2024-05-05 11:00 | -271.315 | 1.0679 | 53.9892 | 59.8258 | -79.5146
2024-05-06 12:00 | 2815.67 | 1 | 55.1712 | 59.8258 | 825.1914
2024-05-07 13:00 | 2939.06 | 1 | 76.6545 | 59.8258 | 861.3535
2024-05-08 14:00 | 2946.56 | 1 | 71.2039 | 59.8258 | 863.5515
2024-05-09 15:00 | 2956.12 | 1 | 72.2498 | 59.8258 | 866.3533
2024-05-10 16:00 | 3055.6 | 1.0447 | 70.1488 | 59.8258 | 895.508
2024-05-11 17:00 | 2870.68 | 1 | 56.6919 | 59.8258 | 841.3133
2024-05-12 18:00 | 0 | 0 | 57.0368 | 59.8258 | 0
2024-05-13 19:00 | -1226.13 | 3.9994 | 55.3364 | 59.8258 | -359.3432
2024-05-14 20:00 | -2151.28 | 6.108 | 54.8284 | 59.8258 | -630.4779
2024-05-15 21:00 | -3435.16 | 6.108 | 53.6225 | 59.8258 | -1006.746
2024-05-16 22:00 | -4375.71 | 6.108 | 52.5795 | 59.8258 | -1282.394
2024-05-17 23:00 | -5618.27 | 6.108 | 51.2844 | 59.8258 | -1646.5524
2024-05-19 | -6172.87 | 6.108 | 50.4786 | 59.8258 | -1809.0896
2024-05-20 01:00 | -6894.34 | 6.108 | 49.608 | 59.8258 | -2020.5316
2024-05-21 02:00 | -7222.17 | 6.108 | 49.031 | 59.8258 | -2116.6091
2024-05-22 03:00 | -7594.52 | 6.108 | 48.4655 | 59.8258 | -2225.7341
2024-05-23 04:00 | -7542.16 | 6.108 | 48.2316 | 59.8258 | -2210.3889
2024-05-24 05:00 | -7673.39 | 6.108 | 47.9305 | 59.8258 | -2248.8486
2024-05-25 06:00 | -7533.59 | 6.108 | 47.8681 | 59.8258 | -2207.8773
2024-05-26 07:00 | -7191.97 | 6.108 | 48.0085 | 59.8258 | -2107.7583
2024-05-27 08:00 | -6176.48 | 6.108 | 48.706 | 59.8258 | -1810.1476
2024-05-28 09:00 | -5511.03 | 6.108 | 49.2747 | 59.8258 | -1615.1235
2024-05-29 10:00 | -3915.61 | 6.108 | 50.5586 | 59.8258 | -1147.552
2024-05-30 11:00 | -2545.53 | 6.108 | 51.8188 | 59.8258 | -746.0212
2024-05-31 12:00 | -1222.47 | 3.85 | 52.558 | 59.8258 | -358.2706
2024-06-01 13:00 | -542.353 | 1.9171 | 53.0458 | 59.8258 | -158.948
2024-06-02 14:00 | -238.412 | 1.1684 | 53.6887 | 59.8258 | -69.8717
2024-06-03 15:00 | -165.766 | 1.0166 | 54.1007 | 59.8258 | -48.5812
2024-06-04 16:00 | 2714.4 | 1 | 54.7684 | 59.8258 | 795.5121
2024-06-05 17:00 | -58.5808 | 0.78388 | 55.1644 | 59.8258 | -17.1683
2024-06-06 18:00 | -1102.9 | 3.8954 | 54.1593 | 59.8258 | -323.2281
2024-06-07 19:00 | -2189.93 | 6.108 | 53.6736 | 59.8258 | -641.8051
2024-06-08 20:00 | -2922.32 | 6.108 | 52.9764 | 59.8258 | -856.4474
2024-06-09 21:00 | -4370.62 | 6.108 | 51.751 | 59.8258 | -1280.9023
2024-06-10 22:00 | -5324.3 | 6.108 | 50.7012 | 59.8258 | -1560.3983
2024-06-11 23:00 | -6643.27 | 6.108 | 49.4118 | 59.8258 | -1946.9502
2024-06-13 | -6789.18 | 6.108 | 48.944 | 59.8258 | -1989.7122
2024-06-14 01:00 | -7493.57 | 6.108 | 48.1703 | 59.8258 | -2196.1486
2024-06-15 02:00 | -7607.06 | 6.108 | 47.8131 | 59.8258 | -2229.4092
2024-06-16 03:00 | -8210.05 | 6.108 | 47.1545 | 59.8258 | -2406.1281
2024-06-17 04:00 | -8260.21 | 6.108 | 46.8475 | 59.8258 | -2420.8286
2024-06-18 05:00 | -8213.29 | 6.108 | 46.7096 | 59.8258 | -2407.0777
2024-06-19 06:00 | -7635.5 | 6.108 | 47.0154 | 59.8258 | -2237.7442
2024-06-20 07:00 | -7148.82 | 6.108 | 47.3564 | 59.8258 | -2095.1123
2024-06-21 08:00 | -5201.43 | 6.108 | 48.8262 | 59.8258 | -1524.3887
2024-06-22 09:00 | -3915.06 | 6.108 | 50.0428 | 59.8258 | -1147.3908
2024-06-23 10:00 | -1915.77 | 6.108 | 51.8369 | 59.8258 | -561.4568
2024-06-24 11:00 | -637.535 | 1.9942 | 52.2299 | 59.8258 | -186.8431
2024-06-25 12:00 | 2772.92 | 1 | 53.87 | 59.8258 | 812.6626
2024-06-26 13:00 | 3026.79 | 1 | 69.6747 | 59.8258 | 887.0646
2024-06-27 14:00 | 2983.21 | 1 | 69.302 | 59.8258 | 874.2925
2024-06-28 15:00 | 3159.56 | 1.0399 | 69.5286 | 59.8258 | 925.9756
2024-06-29 16:00 | 3336.97 | 1.1212 | 69.5126 | 59.8258 | 977.9694
2024-06-30 17:00 | 2985.55 | 1 | 79.4345 | 59.8258 | 874.9783
2024-07-01 18:00 | 1574.95 | 1 | 56.1624 | 59.8258 | 461.5723
2024-07-02 19:00 | -648.096 | 2.5413 | 55.1004 | 59.8258 | -189.9382
2024-07-03 20:00 | -1442.65 | 4.7634 | 54.6234 | 59.8258 | -422.799
2024-07-04 21:00 | -2559.07 | 6.108 | 53.895 | 59.8258 | -749.9894
2024-07-05 22:00 | -3255.77 | 6.108 | 53.1256 | 59.8258 | -954.172
2024-07-06 23:00 | -4192.65 | 6.108 | 52.1779 | 59.8258 | -1228.7444
2024-07-08 | -4672.15 | 6.108 | 51.5213 | 59.8258 | -1369.272
2024-07-09 01:00 | -5008.87 | 6.108 | 51.0391 | 59.8258 | -1467.9549
2024-07-10 02:00 | -5385.8 | 6.108 | 50.5608 | 59.8258 | -1578.4222
2024-07-11 03:00 | -5326.67 | 6.108 | 50.4212 | 59.8258 | -1561.0929
2024-07-12 04:00 | -5142.2 | 6.108 | 50.431 | 59.8258 | -1507.0301
2024-07-13 05:00 | -5078.14 | 6.108 | 50.4105 | 59.8258 | -1488.2559
2024-07-14 06:00 | -4725.79 | 6.108 | 50.6258 | 59.8258 | -1384.9923
2024-07-15 07:00 | -4455.08 | 6.108 | 50.8455 | 59.8258 | -1305.6551
2024-07-16 08:00 | -3958.93 | 6.108 | 51.2498 | 59.8258 | -1160.2479
2024-07-17 09:00 | -3232.79 | 6.108 | 51.8681 | 59.8258 | -947.4372
2024-07-18 10:00 | -2600.43 | 6.108 | 52.4624 | 59.8258 | -762.1108
2024-07-19 11:00 | -1448.46 | 4.5381 | 53.0875 | 59.8258 | -424.5017
2024-07-20 12:00 | -1472.51 | 4.7343 | 53.3319 | 59.8258 | -431.5501
2024-07-21 13:00 | -1127.93 | 3.6312 | 53.4415 | 59.8258 | -330.5637
2024-07-22 14:00 | -973.241 | 3.2586 | 53.6054 | 59.8258 | -285.2288
2024-07-23 15:00 | -789.549 | 2.7238 | 53.7384 | 59.8258 | -231.394
2024-07-24 16:00 | 0 | 1 | 55.1411 | 59.8258 | 0
2024-07-25 17:00 | 3101.1 | 1 | 55.0149 | 59.8258 | 908.8427
2024-07-26 18:00 | 3138.25 | 1 | 55.5422 | 59.8258 | 919.7303
2024-07-27 19:00 | -164.818 | 1.092 | 55.4627 | 59.8258 | -48.3034
2024-07-28 20:00 | -553.734 | 2.1825 | 54.768 | 59.8258 | -162.2834
2024-07-29 21:00 | -1415.55 | 4.7229 | 54.4749 | 59.8258 | -414.8568
2024-07-30 22:00 | -1778.74 | 5.6009 | 54.3103 | 59.8258 | -521.2972
2024-07-31 23:00 | -2737.05 | 6.108 | 53.5695 | 59.8258 | -802.1502
2024-08-02 | -3137.94 | 6.108 | 53.049 | 59.8258 | -919.6394
2024-08-03 01:00 | -3125.84 | 6.108 | 52.927 | 59.8258 | -916.0933
2024-08-04 02:00 | -3405.59 | 6.108 | 52.6543 | 59.8258 | -998.0799
2024-08-05 03:00 | -3442.5 | 6.108 | 52.558 | 59.8258 | -1008.8972
2024-08-06 04:00 | -3578.33 | 6.108 | 52.3964 | 59.8258 | -1048.705
2024-08-07 05:00 | -3527.19 | 6.108 | 52.3541 | 59.8258 | -1033.7173
2024-08-08 06:00 | -3126.71 | 6.108 | 52.5942 | 59.8258 | -916.3482
2024-08-09 07:00 | -3088.64 | 6.108 | 52.6534 | 59.8258 | -905.191
2024-08-10 08:00 | -2889.03 | 6.108 | 52.8139 | 59.8258 | -846.6911
2024-08-11 09:00 | -3082.21 | 6.108 | 52.693 | 59.8258 | -903.3066
2024-08-12 10:00 | -2403.81 | 6.108 | 53.1806 | 59.8258 | -704.4872
2024-08-13 11:00 | 0 | 0 | 55.0552 | 59.8258 | 0
2024-08-14 12:00 | 2540.96 | 1 | 73.4378 | 59.8258 | 744.6819
2024-08-15 13:00 | 2699.51 | 1 | 69.6041 | 59.8258 | 791.1483
2024-08-16 14:00 | 3180.53 | 1 | 73.3111 | 59.8258 | 932.1213
2024-08-17 15:00 | 3195.25 | 1.0267 | 70.7905 | 59.8258 | 936.4353
2024-08-18 16:00 | 3024.25 | 1.0347 | 70.1779 | 59.8258 | 886.3202
2024-08-19 17:00 | 2947.55 | 1 | 74.9875 | 59.8258 | 863.8416
2024-08-20 18:00 | 2847.25 | 1 | 56.7603 | 59.8258 | 834.4466
2024-08-21 19:00 | -662.88 | 2.5399 | 55.922 | 59.8258 | -194.271
2024-08-22 20:00 | -1574.54 | 5.1192 | 55.3321 | 59.8258 | -461.4521
2024-08-23 21:00 | -3163.19 | 6.108 | 54.0834 | 59.8258 | -927.0395
2024-08-24 22:00 | -3828.84 | 6.108 | 53.2531 | 59.8258 | -1122.1222
2024-08-25 23:00 | -5262.27 | 6.108 | 51.8629 | 59.8258 | -1542.2191
2024-08-27 | -5982.21 | 6.108 | 50.8802 | 59.8258 | -1753.2127
2024-08-28 01:00 | -6941.2 | 6.108 | 49.8048 | 59.8258 | -2034.2649
2024-08-29 02:00 | -7122.67 | 6.108 | 49.2898 | 59.8258 | -2087.4485
2024-08-30 03:00 | -7444.08 | 6.108 | 48.7619 | 59.8258 | -2181.6445
2024-08-31 04:00 | -7415.32 | 6.108 | 48.5134 | 59.8258 | -2173.2158
2024-09-01 05:00 | -7630.07 | 6.108 | 48.1443 | 59.8258 | -2236.1528
2024-09-02 06:00 | -7979.15 | 6.108 | 47.6672 | 59.8258 | -2338.458
2024-09-03 07:00 | -6993.77 | 6.108 | 48.2168 | 59.8258 | -2049.6717
2024-09-04 08:00 | -4870.1 | 6.108 | 49.796 | 59.8258 | -1427.2854
2024-09-05 09:00 | -4046.87 | 6.108 | 50.6687 | 59.8258 | -1186.0205
2024-09-06 10:00 | -2163.83 | 6.108 | 52.2906 | 59.8258 | -634.156
2024-09-07 11:00 | -1304.25 | 4.0805 | 52.7946 | 59.8258 | -382.2379
2024-09-08 12:00 | -1403.1 | 4.5746 | 53.1837 | 59.8258 | -411.208
2024-09-09 13:00 | -1564.4 | 5.0182 | 53.3476 | 59.8258 | -458.4804
2024-09-10 14:00 | -1542.96 | 4.899 | 53.4219 | 59.8258 | -452.1969
2024-09-11 15:00 | -1371.93 | 4.3708 | 53.5128 | 59.8258 | -402.073
2024-09-12 16:00 | -545.058 | 1.8563 | 53.667 | 59.8258 | -159.7407
2024-09-13 17:00 | 2685.23 | 1 | 54.928 | 59.8258 | 786.9632
2024-09-14 18:00 | -499.651 | 2.0959 | 54.6134 | 59.8258 | -146.4333
2024-09-15 19:00 | -1564.71 | 5.2065 | 54.2552 | 59.8258 | -458.5712
2024-09-16 20:00 | -2199.58 | 6.108 | 53.8144 | 59.8258 | -644.6333
2024-09-17 21:00 | -2606.83 | 6.108 | 53.4251 | 59.8258 | -763.9865
2024-09-18 22:00 | -2748.7 | 6.108 | 53.2186 | 59.8258 | -805.5645
2024-09-19 23:00 | -2967.42 | 6.108 | 52.9108 | 59.8258 | -869.665
2024-09-21 | -4637.98 | 6.108 | 51.5867 | 59.8258 | -1359.2578
2024-09-22 01:00 | -4733.32 | 6.108 | 51.2633 | 59.8258 | -1387.1992
2024-09-23 02:00 | -5104.64 | 6.108 | 50.8406 | 59.8258 | -1496.0223
2024-09-24 03:00 | -5030.2 | 6.108 | 50.7742 | 59.8258 | -1474.2061
2024-09-25 04:00 | -5233.05 | 6.108 | 50.5294 | 59.8258 | -1533.6556
2024-09-26 05:00 | -5388.69 | 6.108 | 50.2697 | 59.8258 | -1579.2691
2024-09-27 06:00 | -5255.64 | 6.108 | 50.2887 | 59.8258 | -1540.276
2024-09-28 07:00 | -4533.52 | 6.108 | 50.7916 | 59.8258 | -1328.6436
2024-09-29 08:00 | -3803.95 | 6.108 | 51.3955 | 59.8258 | -1114.8277
2024-09-30 09:00 | -3891.43 | 6.108 | 51.4365 | 59.8258 | -1140.4656
2024-10-01 10:00 | -3264.08 | 6.108 | 51.9238 | 59.8258 | -956.6074
2024-10-02 11:00 | -2043.93 | 6.108 | 52.9124 | 59.8258 | -599.0168
2024-10-03 12:00 | -461.639 | 1.4265 | 53.166 | 59.8258 | -135.293
2024-10-04 13:00 | -625.333 | 2.3994 | 53.7751 | 59.8258 | -183.267
2024-10-05 14:00 | -477.899 | 1.8485 | 53.9331 | 59.8258 | -140.0584
2024-10-06 15:00 | -373.359 | 1.5799 | 54.1589 | 59.8258 | -109.4207
2024-10-07 16:00 | 2238.63 | 1 | 55.1689 | 59.8258 | 656.0777
2024-10-08 17:00 | 2945.31 | 1 | 72.6896 | 59.8258 | 863.1852
2024-10-09 18:00 | 2891.99 | 1 | 55.8734 | 59.8258 | 847.5586
2024-10-10 19:00 | 3014.96 | 1 | 56.102 | 59.8258 | 883.5976
2024-10-11 20:00 | 3061.81 | 1 | 56.3207 | 59.8258 | 897.3279
2024-10-12 21:00 | 3140.32 | 1 | 56.5459 | 59.8258 | 920.3369
2024-10-13 22:00 | 50.399 | 1 | 56.9915 | 59.8258 | 14.7705
2024-10-14 23:00 | 538.481 | 1 | 56.6715 | 59.8258 | 157.8132
2024-10-16 | -878.094 | 3.1893 | 55.4152 | 59.8258 | -257.3439
2024-10-17 01:00 | -1297.75 | 4.2262 | 55.1177 | 59.8258 | -380.333
2024-10-18 02:00 | -1757.26 | 5.5384 | 54.9268 | 59.8258 | -515.0021
2024-10-19 03:00 | -2066.9 | 6.108 | 54.6918 | 59.8258 | -605.7486
2024-10-20 04:00 | -2296.33 | 6.108 | 54.4202 | 59.8258 | -672.9879
2024-10-21 05:00 | -2474.7 | 6.108 | 54.1708 | 59.8258 | -725.263
2024-10-22 06:00 | -2580.87 | 6.108 | 54.0075 | 59.8258 | -756.3783
2024-10-23 07:00 | -3268.68 | 6.108 | 53.4115 | 59.8258 | -957.9555
2024-10-24 08:00 | -2902.29 | 6.108 | 53.5207 | 59.8258 | -850.5772
2024-10-25 09:00 | -3171.84 | 6.108 | 53.25 | 59.8258 | -929.5745
2024-10-26 10:00 | -1545.39 | 4.8053 | 54.0794 | 59.8258 | -452.9091
2024-10-27 11:00 | -294.931 | 1.0334 | 54.3775 | 59.8258 | -86.4357
2024-10-28 12:00 | 2842.96 | 1 | 55.6748 | 59.8258 | 833.1893
2024-10-29 13:00 | 2909.47 | 1 | 56.2255 | 59.8258 | 852.6815
2024-10-30 14:00 | 2922.95 | 1 | 56.5647 | 59.8258 | 856.6321
2024-10-31 15:00 | 2875.47 | 1 | 56.8076 | 59.8258 | 842.7171
2024-11-01 16:00 | 2912.16 | 1 | 56.9805 | 59.8258 | 853.4698
2024-11-02 17:00 | 2868.86 | 1 | 57.1221 | 59.8258 | 840.7799
2024-11-03 18:00 | -177.217 | 1.1123 | 56.7139 | 59.8258 | -51.9372
2024-11-04 19:00 | -1288.42 | 4.3453 | 55.7579 | 59.8258 | -377.5986
2024-11-05 20:00 | -2057.76 | 6.108 | 55.2659 | 59.8258 | -603.0699
2024-11-06 21:00 | -3447.05 | 6.108 | 53.9874 | 59.8258 | -1010.2306
2024-11-07 22:00 | -4402.18 | 6.108 | 52.9244 | 59.8258 | -1290.1516
2024-11-08 23:00 | -5390.71 | 6.108 | 51.7969 | 59.8258 | -1579.8611
2024-11-10 | -6202.22 | 6.108 | 50.8174 | 59.8258 | -1817.6913
2024-11-11 01:00 | -6329.05 | 6.108 | 50.3572 | 59.8258 | -1854.8615
2024-11-12 02:00 | -6646.22 | 6.108 | 49.8399 | 59.8258 | -1947.8148
2024-11-13 03:00 | -7053.57 | 6.108 | 49.2804 | 59.8258 | -2067.1973
2024-11-14 04:00 | -6833.65 | 6.108 | 49.182 | 59.8258 | -2002.7451
2024-11-15 05:00 | -6875.7 | 6.108 | 48.9769 | 59.8258 | -2015.0688
2024-11-16 06:00 | -6875.08 | 6.108 | 48.852 | 59.8258 | -2014.8871
2024-11-17 07:00 | -6069.48 | 6.108 | 49.344 | 59.8258 | -1778.789
2024-11-18 08:00 | -4447.54 | 6.108 | 50.5721 | 59.8258 | -1303.4453
2024-11-19 09:00 | -3280.56 | 6.108 | 51.6618 | 59.8258 | -961.4372
2024-11-20 10:00 | -1444.53 | 4.569 | 52.9167 | 59.8258 | -423.35
2024-11-21 11:00 | 0 | 1 | 54.7372 | 59.8258 | 0
2024-11-22 12:00 | -60.3983 | 0.76673 | 54.7792 | 59.8258 | -17.701
2024-11-23 13:00 | -405.559 | 1.7755 | 54.3253 | 59.8258 | -118.8576
2024-11-24 14:00 | -413.323 | 1.7047 | 54.3658 | 59.8258 | -121.133
2024-11-25 15:00 | 2497.63 | 1 | 55.3657 | 59.8258 | 731.9831
2024-11-26 16:00 | 3094.24 | 1 | 71.0047 | 59.8258 | 906.8322
2024-11-27 17:00 | 3062.39 | 1 | 56.1145 | 59.8258 | 897.4979
2024-11-28 18:00 | 3144.18 | 1 | 56.3434 | 59.8258 | 921.4682
2024-11-29 19:00 | 0 | 0 | 56.851 | 59.8258 | 0
2024-11-30 20:00 | -618.332 | 2.08 | 55.2712 | 59.8258 | -181.2152
2024-12-01 21:00 | -1494.87 | 4.9362 | 55.0579 | 59.8258 | -438.1032
2024-12-02 22:00 | -2197.53 | 6.108 | 54.6119 | 59.8258 | -644.0325
2024-12-03 23:00 | -3389.72 | 6.108 | 53.4982 | 59.8258 | -993.4289
2024-12-05 | -4035.11 | 6.108 | 52.7095 | 59.8258 | -1182.574
2024-12-06 01:00 | -4093.54 | 6.108 | 52.4441 | 59.8258 | -1199.6981
2024-12-07 02:00 | -4064.67 | 6.108 | 52.3326 | 59.8258 | -1191.2372
2024-12-08 03:00 | -3913.22 | 6.108 | 52.3332 | 59.8258 | -1146.8516
2024-12-09 04:00 | -3604.92 | 6.108 | 52.4812 | 59.8258 | -1056.4978
2024-12-10 05:00 | -3306.46 | 6.108 | 52.6833 | 59.8258 | -969.0278
2024-12-11 06:00 | -3164.13 | 6.108 | 52.8007 | 59.8258 | -927.315
2024-12-12 07:00 | -3348.26 | 6.108 | 52.698 | 59.8258 | -981.2781
2024-12-13 08:00 | -3530.8 | 6.108 | 52.5446 | 59.8258 | -1034.7753
2024-12-14 09:00 | -4344.56 | 6.108 | 51.8971 | 59.8258 | -1273.2648
2024-12-15 10:00 | -4109.29 | 6.108 | 51.9223 | 59.8258 | -1204.314
2024-12-16 11:00 | -3727.15 | 6.108 | 52.1353 | 59.8258 | -1092.3198
2024-12-17 12:00 | -3155.31 | 6.108 | 52.5517 | 59.8258 | -924.7301
2024-12-18 13:00 | -2676.56 | 6.108 | 52.9518 | 59.8258 | -784.4223
2024-12-19 14:00 | -2795.27 | 6.108 | 52.9273 | 59.8258 | -819.2128
2024-12-20 15:00 | -2645.72 | 6.108 | 53.0403 | 59.8258 | -775.384
2024-12-21 16:00 | -1992.56 | 6.108 | 53.5259 | 59.8258 | -583.9617
2024-12-22 17:00 | -1940.8 | 6.0186 | 53.6099 | 59.8258 | -568.7923
2024-12-23 18:00 | -2117.15 | 6.108 | 53.5301 | 59.8258 | -620.4754
2024-12-24 19:00 | -2781.98 | 6.108 | 53.029 | 59.8258 | -815.3179
2024-12-25 20:00 | -3517.34 | 6.108 | 52.4042 | 59.8258 | -1030.8306
2024-12-26 21:00 | -4957.1 | 6.108 | 51.2109 | 59.8258 | -1452.7826
2024-12-27 22:00 | -5997.23 | 6.108 | 50.1733 | 59.8258 | -1757.6146
2024-12-28 23:00 | -7004.94 | 6.108 | 49.13 | 59.8258 | -2052.9453
2024-12-30 | -7067.51 | 6.108 | 48.7732 | 59.8258 | -2071.2827
2024-12-31 01:00 | -7368.88 | 6.108 | 48.3345 | 59.8258 | -2159.6055
2025-01-01 02:00 | -7602.22 | 6.108 | 47.963 | 59.8258 | -2227.9907
2025-01-02 03:00 | -7762.93 | 6.108 | 47.6654 | 59.8258 | -2275.0902
2025-01-03 04:00 | -7914.15 | 6.108 | 47.3909 | 59.8258 | -2319.4084
2025-01-04 05:00 | -8051.23 | 6.108 | 47.1446 | 59.8258 | -2359.5826
2025-01-05 06:00 | -7849.66 | 6.108 | 47.1502 | 59.8258 | -2300.5083
2025-01-06 07:00 | -7344.47 | 6.108 | 47.4371 | 59.8258 | -2152.4517
2025-01-07 08:00 | -5671.73 | 6.108 | 48.6722 | 59.8258 | -1662.22
2025-01-08 09:00 | -4660.96 | 6.108 | 49.6249 | 59.8258 | -1365.9925
2025-01-09 10:00 | -2979.39 | 6.108 | 51.1115 | 59.8258 | -873.173
2025-01-10 11:00 | -1348.88 | 4.2908 | 52.2477 | 59.8258 | -395.3177
2025-01-11 12:00 | -341.407 | 1.2497 | 52.857 | 59.8258 | -100.0565
2025-01-12 13:00 | 2523.87 | 1 | 54.2945 | 59.8258 | 739.6733
2025-01-13 14:00 | 2929.02 | 1 | 54.9026 | 59.8258 | 858.411
2025-01-14 15:00 | 2918.67 | 1 | 55.3738 | 59.8258 | 855.3777
2025-01-15 16:00 | 2918.35 | 1 | 77.4364 | 59.8258 | 855.284
2025-01-16 17:00 | 2819.85 | 1 | 55.9256 | 59.8258 | 826.4165
2025-01-17 18:00 | -255.71 | 1.3348 | 55.5193 | 59.8258 | -74.9412
2025-01-18 19:00 | -1387.8 | 4.6904 | 54.7885 | 59.8258 | -406.724
2025-01-19 20:00 | -2251.77 | 6.108 | 54.2032 | 59.8258 | -659.9286
2025-01-20 21:00 | -3700.22 | 6.108 | 52.9165 | 59.8258 | -1084.4274
2025-01-21 22:00 | -4588.04 | 6.108 | 51.9322 | 59.8258 | -1344.6218
2025-01-22 23:00 | -5915.01 | 6.108 | 50.6021 | 59.8258 | -1733.5183
2025-01-24 | -6203.19 | 6.108 | 50.0325 | 59.8258 | -1817.9755
2025-01-25 01:00 | -6704.08 | 6.108 | 49.3673 | 59.8258 | -1964.7719
2025-01-26 02:00 | -7238.26 | 6.108 | 48.6874 | 59.8258 | -2121.3246
2025-01-27 03:00 | -7397.43 | 6.108 | 48.2884 | 59.8258 | -2167.9727
2025-01-28 04:00 | -7300.85 | 6.108 | 48.1287 | 59.8258 | -2139.6679
2025-01-29 05:00 | -7164.82 | 6.108 | 48.0715 | 59.8258 | -2099.8015
2025-01-30 06:00 | -6774.6 | 6.108 | 48.264 | 59.8258 | -1985.4393
2025-01-31 07:00 | -6628.11 | 6.108 | 48.3389 | 59.8258 | -1942.5073
2025-02-01 08:00 | -5166.17 | 6.108 | 49.4065 | 59.8258 | -1514.055
2025-02-02 09:00 | -4190.8 | 6.108 | 50.3045 | 59.8258 | -1228.2022
2025-02-03 10:00 | -2899.94 | 6.108 | 51.4776 | 59.8258 | -849.8885
2025-02-04 11:00 | -1290.91 | 4.0876 | 52.4762 | 59.8258 | -378.3284
2025-02-05 12:00 | 0 | 1 | 54.2924 | 59.8258 | 0
2025-02-06 13:00 | 13.7325 | 1 | 54.683 | 59.8258 | 4.0246
2025-02-07 14:00 | 1078.84 | 1 | 54.8257 | 59.8258 | 316.1768
2025-02-08 15:00 | 1989.23 | 1 | 55.0612 | 59.8258 | 582.9858
2025-02-09 16:00 | 2899.72 | 1 | 55.3264 | 59.8258 | 849.824
2025-02-10 17:00 | 1882.18 | 1 | 55.7577 | 59.8258 | 551.6125
2025-02-11 18:00 | -183.282 | 1.1601 | 55.305 | 59.8258 | -53.7147
2025-02-12 19:00 | -1016.46 | 3.5833 | 54.5938 | 59.8258 | -297.895
2025-02-13 20:00 | -2336.9 | 6.108 | 54.0139 | 59.8258 | -684.8778
2025-02-14 21:00 | -3728.02 | 6.108 | 52.7624 | 59.8258 | -1092.5748
2025-02-15 22:00 | -4504.52 | 6.108 | 51.8578 | 59.8258 | -1320.1445
2025-02-16 23:00 | -5646.6 | 6.108 | 50.7152 | 59.8258 | -1654.8551
2025-02-18 | -6371.14 | 6.108 | 49.8563 | 59.8258 | -1867.1968
2025-02-19 01:00 | -6224.36 | 6.108 | 49.6671 | 59.8258 | -1824.1798
2025-02-20 02:00 | -6605.79 | 6.108 | 49.2059 | 59.8258 | -1935.9659
2025-02-21 03:00 | -6284.79 | 6.108 | 49.2592 | 59.8258 | -1841.8901
2025-02-22 04:00 | -6620.46 | 6.108 | 48.8879 | 59.8258 | -1940.2653
2025-02-23 05:00 | -7224.6 | 6.108 | 48.3001 | 59.8258 | -2117.3213
2025-02-24 06:00 | -6891.49 | 6.108 | 48.3778 | 59.8258 | -2019.6963
2025-02-25 07:00 | -5640.66 | 6.108 | 49.241 | 59.8258 | -1653.1143
2025-02-26 08:00 | -4544.8 | 6.108 | 50.1699 | 59.8258 | -1331.9494
2025-02-27 09:00 | -3753.21 | 6.108 | 50.9355 | 59.8258 | -1099.9573
2025-02-28 10:00 | -2383.23 | 6.108 | 52.1379 | 59.8258 | -698.4558
2025-03-01 11:00 | -1506.39 | 4.7338 | 52.7534 | 59.8258 | -441.4793
2025-03-02 12:00 | -609.679 | 2.0311 | 53.1228 | 59.8258 | -178.6793
2025-03-03 13:00 | -209.092 | 1.0649 | 53.8767 | 59.8258 | -61.2788
2025-03-04 14:00 | 2288.46 | 1 | 54.8027 | 59.8258 | 670.6814
2025-03-05 15:00 | 2150.43 | 1 | 55.2944 | 59.8258 | 630.2288
2025-03-06 16:00 | -195.169 | 1.1996 | 55.0062 | 59.8258 | -57.1984
2025-03-07 17:00 | -162.17 | 0.9948 | 54.8699 | 59.8258 | -47.5273
2025-03-08 18:00 | -1215.87 | 4.2156 | 54.3023 | 59.8258 | -356.3363
2025-03-09 19:00 | -2747.98 | 6.108 | 53.4968 | 59.8258 | -805.3534
2025-03-10 20:00 | -3732.49 | 6.108 | 52.4809 | 59.8258 | -1093.8848
2025-03-11 21:00 | -4411 | 6.108 | 51.6915 | 59.8258 | -1292.7365
2025-03-12 22:00 | -5160.4 | 6.108 | 50.9112 | 59.8258 | -1512.3639
2025-03-13 23:00 | -5592.33 | 6.108 | 50.3411 | 59.8258 | -1638.9501
2025-03-15 | -7203.95 | 6.108 | 48.9127 | 59.8258 | -2111.2693
2025-03-16 01:00 | -7782.42 | 6.108 | 48.1185 | 59.8258 | -2280.8022
2025-03-17 02:00 | -7846.19 | 6.108 | 47.7378 | 59.8258 | -2299.4913
2025-03-18 03:00 | -8289 | 6.108 | 47.1686 | 59.8258 | -2429.2661
2025-03-19 04:00 | -8738.31 | 6.108 | 46.6014 | 59.8258 | -2560.9459
2025-03-20 05:00 | -8720.48 | 6.108 | 46.3634 | 59.8258 | -2555.7204
2025-03-21 06:00 | -9173.06 | 6.108 | 45.8615 | 59.8258 | -2688.3585
2025-03-22 07:00 | -7838.32 | 6.108 | 46.6786 | 59.8258 | -2297.1848
2025-03-23 08:00 | -6665.15 | 6.108 | 47.5867 | 59.8258 | -1953.3626
2025-03-24 09:00 | -5528.65 | 6.108 | 48.5774 | 59.8258 | -1620.2874
2025-03-25 10:00 | -4407.95 | 6.108 | 49.6034 | 59.8258 | -1291.8426
2025-03-26 11:00 | -3041.42 | 6.108 | 50.8547 | 59.8258 | -891.3522
2025-03-27 12:00 | -2000.76 | 6.108 | 51.9636 | 59.8258 | -586.3649
2025-03-28 13:00 | -1519.65 | 4.7856 | 52.334 | 59.8258 | -445.3655
2025-03-29 14:00 | -1554.11 | 5.015 | 52.6115 | 59.8258 | -455.4647
2025-03-30 15:00 | -1239.95 | 3.9882 | 52.7552 | 59.8258 | -363.3935
2025-03-31 16:00 | -1303.78 | 4.2868 | 52.9538 | 59.8258 | -382.1002
2025-04-01 17:00 | -376.438 | 1.3541 | 53.1804 | 59.8258 | -110.3231
2025-04-02 18:00 | -1415.45 | 4.8667 | 53.3537 | 59.8258 | -414.8274
2025-04-03 19:00 | -3118.7 | 6.108 | 52.3711 | 59.8258 | -914.0007
2025-04-04 20:00 | -4252.65 | 6.108 | 51.3343 | 59.8258 | -1246.3287
2025-04-05 21:00 | -5186.37 | 6.108 | 50.4151 | 59.8258 | -1519.975
2025-04-06 22:00 | -6077.62 | 6.108 | 49.5198 | 59.8258 | -1781.1746
2025-04-07 23:00 | -6550.82 | 6.108 | 48.8791 | 59.8258 | -1919.8558
2025-04-09 | -8071.02 | 6.108 | 47.4949 | 59.8258 | -2365.3825
2025-04-10 01:00 | -8822.34 | 6.108 | 46.5715 | 59.8258 | -2585.5726
2025-04-11 02:00 | -9099.47 | 6.108 | 46.0344 | 59.8258 | -2666.7914
2025-04-12 03:00 | -9329.51 | 6.108 | 45.6107 | 59.8258 | -2734.2095
2025-04-13 04:00 | -9386.23 | 6.108 | 45.3529 | 59.8258 | -2750.8325
2025-04-14 05:00 | -9540.23 | 6.108 | 45.0393 | 59.8258 | -2795.9654
2025-04-15 06:00 | -8728.79 | 6.108 | 45.4906 | 59.8258 | -2558.1558
2025-04-16 07:00 | -7948.71 | 6.108 | 46.0667 | 59.8258 | -2329.5369
2025-04-17 08:00 | -6187.8 | 6.108 | 47.4518 | 59.8258 | -1813.4652
2025-04-18 09:00 | -4232.32 | 6.108 | 49.1572 | 59.8258 | -1240.3706
2025-04-19 10:00 | -2312.44 | 6.108 | 50.9716 | 59.8258 | -677.7093
2025-04-20 11:00 | -661.076 | 2.0905 | 51.7089 | 59.8258 | -193.7423
2025-04-21 12:00 | 2731.69 | 1 | 53.4186 | 59.8258 | 800.5793
2025-04-22 13:00 | 2933.94 | 1 | 73.6106 | 59.8258 | 859.8529
2025-04-23 14:00 | 2916.52 | 1 | 70.3848 | 59.8258 | 854.7476
2025-04-24 15:00 | 3171.31 | 1.0657 | 68.9003 | 59.8258 | 929.4192
2025-04-25 16:00 | 3970.06 | 1.3073 | 69.509 | 59.8258 | 1163.5097
2025-04-26 17:00 | 2949.9 | 1 | 71.0263 | 59.8258 | 864.5303
2025-04-27 18:00 | 2861.46 | 1 | 55.855 | 59.8258 | 838.6111
2025-04-28 19:00 | -575.416 | 2.3044 | 55.106 | 59.8258 | -168.6378
2025-04-29 20:00 | -1599.07 | 5.2714 | 54.5623 | 59.8258 | -468.6412
2025-04-30 21:00 | -3285.31 | 6.108 | 53.2289 | 59.8258 | -962.8293
2025-05-01 22:00 | -3975.31 | 6.108 | 52.3659 | 59.8258 | -1165.0484
2025-05-02 23:00 | -5045.44 | 6.108 | 51.265 | 59.8258 | -1478.6725
2025-05-04 | -5495.31 | 6.108 | 50.5578 | 59.8258 | -1610.5164
2025-05-05 01:00 | -6160.86 | 6.108 | 49.7958 | 59.8258 | -1805.5698
2025-05-06 02:00 | -6502.58 | 6.108 | 49.2741 | 59.8258 | -1905.7181
2025-05-07 03:00 | -6703.83 | 6.108 | 48.9032 | 59.8258 | -1964.6986
2025-05-08 04:00 | -7040.82 | 6.108 | 48.4536 | 59.8258 | -2063.4607
2025-05-09 05:00 | -7380.97 | 6.108 | 48.0151 | 59.8258 | -2163.1488
2025-05-10 06:00 | -6574.28 | 6.108 | 48.4255 | 59.8258 | -1926.7313
2025-05-11 07:00 | -5931.46 | 6.108 | 48.9023 | 59.8258 | -1738.3393
2025-05-12 08:00 | -3700.93 | 6.108 | 50.6278 | 59.8258 | -1084.6355
2025-05-13 09:00 | -2607.53 | 6.108 | 51.7483 | 59.8258 | -764.1916
2025-05-14 10:00 | -819.752 | 2.5751 | 52.5375 | 59.8258 | -240.2456
2025-05-15 11:00 | 1320.3 | 1 | 54.2896 | 59.8258 | 386.9417
2025-05-16 12:00 | 3015.57 | 1 | 72.8674 | 59.8258 | 883.7763
2025-05-17 13:00 | 3626.58 | 1.1957 | 69.346 | 59.8258 | 1062.8457
2025-05-18 14:00 | 4408.57 | 1.4326 | 69.9769 | 59.8258 | 1292.0243
2025-05-19 15:00 | 3030.92 | 1.0008 | 70.1675 | 59.8258 | 888.275
2025-05-20 16:00 | 4745.04 | 1.5042 | 70.8502 | 59.8258 | 1390.6339
2025-05-21 17:00 | 3563.13 | 1.1742 | 70.6626 | 59.8258 | 1044.2503
2025-05-22 18:00 | 2938.39 | 1 | 77.6744 | 59.8258 | 861.1571
2025-05-23 19:00 | 2797.75 | 1 | 56.6701 | 59.8258 | 819.9396
2025-05-24 20:00 | -369.235 | 1.6914 | 55.9847 | 59.8258 | -108.2121
2025-05-25 21:00 | -1611.27 | 5.3097 | 55.2912 | 59.8258 | -472.2166
2025-05-26 22:00 | -2445.41 | 6.108 | 54.5054 | 59.8258 | -716.6789
2025-05-27 23:00 | -3680.54 | 6.108 | 53.3145 | 59.8258 | -1078.6598
2025-05-29 | -4030.71 | 6.108 | 52.7109 | 59.8258 | -1181.2845
2025-05-30 01:00 | -4481.53 | 6.108 | 52.0858 | 59.8258 | -1313.4068
2025-05-31 02:00 | -4630.02 | 6.108 | 51.7549 | 59.8258 | -1356.9249
2025-06-01 03:00 | -4575.68 | 6.108 | 51.6398 | 59.8258 | -1340.9994
2025-06-02 04:00 | -4479.15 | 6.108 | 51.5899 | 59.8258 | -1312.7093
2025-06-03 05:00 | -4274.43 | 6.108 | 51.6815 | 59.8258 | -1252.7118
2025-06-04 06:00 | -3684.94 | 6.108 | 52.0901 | 59.8258 | -1079.9493
2025-06-05 07:00 | -3480.02 | 6.108 | 52.2797 | 59.8258 | -1019.8932
2025-06-06 08:00 | -3050.88 | 6.108 | 52.6431 | 59.8258 | -894.1247
2025-06-07 09:00 | -2931.09 | 6.108 | 52.8005 | 59.8258 | -859.0177
2025-06-08 10:00 | -2422.89 | 6.108 | 53.2214 | 59.8258 | -710.079
2025-06-09 11:00 | -2353.69 | 6.108 | 53.3511 | 59.8258 | -689.7984
2025-06-10 12:00 | -2194.22 | 6.108 | 53.493 | 59.8258 | -643.0624
2025-06-11 13:00 | -2390.07 | 6.108 | 53.3648 | 59.8258 | -700.4604
2025-06-12 14:00 | -2466.35 | 6.108 | 53.2718 | 59.8258 | -722.8158
2025-06-13 15:00 | -2520.07 | 6.108 | 53.1927 | 59.8258 | -738.5596
2025-06-14 16:00 | -1926.66 | 6.0118 | 53.5571 | 59.8258 | -564.6483
2025-06-15 17:00 | -1850.72 | 5.7459 | 53.5853 | 59.8258 | -542.3925
2025-06-16 18:00 | -1861.9 | 5.8087 | 53.6029 | 59.8258 | -545.669
2025-06-17 19:00 | -2236.49 | 6.108 | 53.3965 | 59.8258 | -655.4505
2025-06-18 20:00 | -2596.71 | 6.108 | 53.0953 | 59.8258 | -761.0206
2025-06-19 21:00 | -3759.85 | 6.108 | 52.1785 | 59.8258 | -1101.9033
2025-06-20 22:00 | -4180.67 | 6.108 | 51.6807 | 59.8258 | -1225.2334
2025-06-21 23:00 | -4917.75 | 6.108 | 50.9765 | 59.8258 | -1441.2503
2025-06-23 | -5499.74 | 6.108 | 50.3561 | 59.8258 | -1611.8147
2025-06-24 01:00 | -5699.64 | 6.108 | 50.0156 | 59.8258 | -1670.3996
2025-06-25 02:00 | -5799.13 | 6.108 | 49.7933 | 59.8258 | -1699.5572
2025-06-26 03:00 | -5782.71 | 6.108 | 49.7041 | 59.8258 | -1694.745
2025-06-27 04:00 | -5785.77 | 6.108 | 49.6189 | 59.8258 | -1695.6418
2025-06-28 05:00 | -5677.89 | 6.108 | 49.6346 | 59.8258 | -1664.0253
2025-06-29 06:00 | -5044.86 | 6.108 | 50.0674 | 59.8258 | -1478.5025
2025-06-30 07:00 | -5009.43 | 6.108 | 50.1368 | 59.8258 | -1468.119
2025-07-01 08:00 | -4579.95 | 6.108 | 50.4619 | 59.8258 | -1342.2508
2025-07-02 09:00 | -4397.43 | 6.108 | 50.6449 | 59.8258 | -1288.7595
2025-07-03 10:00 | -3717.35 | 6.108 | 51.1947 | 59.8258 | -1089.4477
2025-07-04 11:00 | -3156.5 | 6.108 | 51.7196 | 59.8258 | -925.0788
2025-07-05 12:00 | -2650.66 | 6.108 | 52.2188 | 59.8258 | -776.8318
2025-07-06 13:00 | -2340.15 | 6.108 | 52.5848 | 59.8258 | -685.8303
2025-07-07 14:00 | -1883.19 | 5.9111 | 52.9971 | 59.8258 | -551.9085
2025-07-08 15:00 | -1806.71 | 5.6542 | 53.1363 | 59.8258 | -529.4944
2025-07-09 16:00 | -1256.08 | 3.9446 | 53.2311 | 59.8258 | -368.1207
2025-07-10 17:00 | -1215.14 | 3.9868 | 53.4297 | 59.8258 | -356.1224
2025-07-11 18:00 | -1255.23 | 4.1025 | 53.5174 | 59.8258 | -367.8716
2025-07-12 19:00 | -1906.28 | 6.108 | 53.5568 | 59.8258 | -558.6755
2025-07-13 20:00 | -2377.95 | 6.108 | 53.1778 | 59.8258 | -696.9084
2025-07-14 21:00 | -3165.98 | 6.108 | 52.5446 | 59.8258 | -927.8571
2025-07-15 22:00 | -3548.4 | 6.108 | 52.1432 | 59.8258 | -1039.9334
2025-07-16 23:00 | -4620.2 | 6.108 | 51.236 | 59.8258 | -1354.047
2025-07-18 | -4860.57 | 6.108 | 50.8554 | 59.8258 | -1424.4925
2025-07-19 01:00 | -5177.56 | 6.108 | 50.4747 | 59.8258 | -1517.393
2025-07-20 02:00 | -5398.65 | 6.108 | 50.1802 | 59.8258 | -1582.1881
2025-07-21 03:00 | -5514.98 | 6.108 | 49.9779 | 59.8258 | -1616.2811
2025-07-22 04:00 | -5402.38 | 6.108 | 49.9576 | 59.8258 | -1583.2813
2025-07-23 05:00 | -5217.79 | 6.108 | 50.0445 | 59.8258 | -1529.1833
2025-07-24 06:00 | -4834.61 | 6.108 | 50.3025 | 59.8258 | -1416.8843
2025-07-25 07:00 | -4568.99 | 6.108 | 50.5228 | 59.8258 | -1339.0388
2025-07-26 08:00 | -4240.43 | 6.108 | 50.8005 | 59.8258 | -1242.7474
2025-07-27 09:00 | -4122.82 | 6.108 | 50.943 | 59.8258 | -1208.2793
2025-07-28 10:00 | -3533.11 | 6.108 | 51.4192 | 59.8258 | -1035.4523
2025-07-29 11:00 | -2692.6 | 6.108 | 52.147 | 59.8258 | -789.1232
2025-07-30 12:00 | -1990.47 | 6.108 | 52.832 | 59.8258 | -583.3492
2025-07-31 13:00 | -1756.09 | 5.4836 | 53.0371 | 59.8258 | -514.6592
2025-08-01 14:00 | -1463 | 4.6142 | 53.1859 | 59.8258 | -428.763
2025-08-02 15:00 | -1306.4 | 4.2058 | 53.3508 | 59.8258 | -382.868
2025-08-03 16:00 | -669.532 | 2.2614 | 53.5268 | 59.8258 | -196.2205
2025-08-04 17:00 | -292.382 | 1.2939 | 54.0079 | 59.8258 | -85.6887
2025-08-05 18:00 | -446.658 | 1.8576 | 54.0949 | 59.8258 | -130.9025
2025-08-06 19:00 | -1124.41 | 3.8864 | 53.9644 | 59.8258 | -329.532
2025-08-07 20:00 | -1585.59 | 5.1208 | 53.863 | 59.8258 | -464.6906
2025-08-08 21:00 | -2546.97 | 6.108 | 53.3509 | 59.8258 | -746.4432
2025-08-09 22:00 | -3236.16 | 6.108 | 52.7137 | 59.8258 | -948.4249
2025-08-10 23:00 | -4062.77 | 6.108 | 51.9423 | 59.8258 | -1190.6804
2025-08-12 | -4494.9 | 6.108 | 51.425 | 59.8258 | -1317.3252
2025-08-13 01:00 | -4840.79 | 6.108 | 51.0009 | 59.8258 | -1418.6955
2025-08-14 02:00 | -5186.83 | 6.108 | 50.5921 | 59.8258 | -1520.1098
2025-08-15 03:00 | -5369.52 | 6.108 | 50.3142 | 59.8258 | -1573.651
2025-08-16 04:00 | -5491.77 | 6.108 | 50.0965 | 59.8258 | -1609.4789
2025-08-17 05:00 | -5393.7 | 6.108 | 50.0634 | 59.8258 | -1580.7374
2025-08-18 06:00 | -5655.77 | 6.108 | 49.7928 | 59.8258 | -1657.5426
2025-08-19 07:00 | -4515.63 | 6.108 | 50.5501 | 59.8258 | -1323.4005
2025-08-20 08:00 | -3334.22 | 6.108 | 51.5129 | 59.8258 | -977.1634
2025-08-21 09:00 | -3758.4 | 6.108 | 51.3882 | 59.8258 | -1101.4783
2025-08-22 10:00 | -3481.51 | 6.108 | 51.6248 | 59.8258 | -1020.3299
2025-08-23 11:00 | -2898.71 | 6.108 | 52.1087 | 59.8258 | -849.528
2025-08-24 12:00 | -981.032 | 3.0777 | 52.9453 | 59.8258 | -287.5121
2025-08-25 13:00 | -420.618 | 1.6109 | 53.5304 | 59.8258 | -123.271
2025-08-26 14:00 | -912.837 | 3.2695 | 53.6905 | 59.8258 | -267.5261
2025-08-27 15:00 | -1150.51 | 3.8424 | 53.6858 | 59.8258 | -337.1812
2025-08-28 16:00 | -2011.7 | 6.108 | 53.602 | 59.8258 | -589.5711
2025-08-29 17:00 | -1653.28 | 5.124 | 53.5782 | 59.8258 | -484.5285
2025-08-30 18:00 | -2186.84 | 6.108 | 53.4341 | 59.8258 | -640.8995
2025-08-31 19:00 | -2764.28 | 6.108 | 52.9358 | 59.8258 | -810.1305
2025-09-01 20:00 | -3939.05 | 6.108 | 51.9357 | 59.8258 | -1154.4216
2025-09-02 21:00 | -4448.75 | 6.108 | 51.345 | 59.8258 | -1303.7999
2025-09-03 22:00 | -4721.71 | 6.108 | 50.9727 | 59.8258 | -1383.7966
2025-09-04 23:00 | -5221.52 | 6.108 | 50.4585 | 59.8258 | -1530.2765
2025-09-06 | -6371.45 | 6.108 | 49.4151 | 59.8258 | -1867.2877
2025-09-07 01:00 | -6639.91 | 6.108 | 48.9225 | 59.8258 | -1945.9655
2025-09-08 02:00 | -6659.13 | 6.108 | 48.7001 | 59.8258 | -1951.5984
2025-09-09 03:00 | -6941.83 | 6.108 | 48.3479 | 59.8258 | -2034.4495
2025-09-10 04:00 | -6887.03 | 6.108 | 48.237 | 59.8258 | -2018.3893
2025-09-11 05:00 | -6815.85 | 6.108 | 48.1697 | 59.8258 | -1997.5285
2025-09-12 06:00 | -7147.68 | 6.108 | 47.8475 | 59.8258 | -2094.7782
2025-09-13 07:00 | -6107.57 | 6.108 | 48.5084 | 59.8258 | -1789.9521
2025-09-14 08:00 | -5334 | 6.108 | 49.1345 | 59.8258 | -1563.2411
2025-09-15 09:00 | -5006.2 | 6.108 | 49.4968 | 59.8258 | -1467.1724
2025-09-16 10:00 | -4380.86 | 6.108 | 50.0431 | 59.8258 | -1283.9033
2025-09-17 11:00 | -3613.84 | 6.108 | 50.7327 | 59.8258 | -1059.112
2025-09-18 12:00 | -2193.3 | 6.108 | 51.9758 | 59.8258 | -642.7928
2025-09-19 13:00 | -1846.84 | 5.8326 | 52.4518 | 59.8258 | -541.2554
2025-09-20 14:00 | -1377.74 | 4.3411 | 52.6506 | 59.8258 | -403.7757
2025-09-21 15:00 | -1319.36 | 4.3019 | 52.8962 | 59.8258 | -386.6662
2025-09-22 16:00 | -1596.26 | 5.169 | 53.0428 | 59.8258 | -467.8176
2025-09-23 17:00 | -554.717 | 1.8143 | 53.1282 | 59.8258 | -162.5715
2025-09-24 18:00 | -1472.15 | 5.0034 | 53.3943 | 59.8258 | -431.4446
2025-09-25 19:00 | -2699.13 | 6.108 | 52.7416 | 59.8258 | -791.0369
2025-09-26 20:00 | -3644.81 | 6.108 | 51.8923 | 59.8258 | -1068.1884
2025-09-27 21:00 | -4042.22 | 6.108 | 51.4292 | 59.8258 | -1184.6577
2025-09-28 22:00 | -4716.35 | 6.108 | 50.8045 | 59.8258 | -1382.2257
2025-09-29 23:00 | -5115.94 | 6.108 | 50.3228 | 59.8258 | -1499.334
2025-10-01 | -6408.2 | 6.108 | 49.1833 | 59.8258 | -1878.058
2025-10-02 01:00 | -6942.31 | 6.108 | 48.5075 | 59.8258 | -2034.5902
2025-10-03 02:00 | -7385.32 | 6.108 | 47.9328 | 59.8258 | -2164.4236
2025-10-04 03:00 | -7640.87 | 6.108 | 47.5242 | 59.8258 | -2239.3179
2025-10-05 04:00 | -7716.28 | 6.108 | 47.2789 | 59.8258 | -2261.4184
2025-10-06 05:00 | -8027.91 | 6.108 | 46.8722 | 59.8258 | -2352.7482
2025-10-07 06:00 | -7566.58 | 6.108 | 47.0589 | 59.8258 | -2217.5457
2025-10-08 07:00 | -6350.55 | 6.108 | 47.914 | 59.8258 | -1861.1625
2025-10-09 08:00 | -4459.83 | 6.108 | 49.4385 | 59.8258 | -1307.0472
2025-10-10 09:00 | -2977.02 | 6.108 | 50.8376 | 59.8258 | -872.4784
2025-10-11 10:00 | -1128.15 | 3.5957 | 51.9705 | 59.8258 | -330.6281
2025-10-12 11:00 | 1343.4 | 1 | 53.7414 | 59.8258 | 393.7117
2025-10-13 12:00 | 3130.04 | 1 | 77.8094 | 59.8258 | 917.3242
2025-10-14 13:00 | 3051.72 | 1 | 69.1983 | 59.8258 | 894.3708
2025-10-15 14:00 | 3434.14 | 1.1006 | 69.7807 | 59.8258 | 1006.4471
2025-10-16 15:00 | 3706.26 | 1.2087 | 69.8905 | 59.8258 | 1086.1976
2025-10-17 16:00 | 4529.05 | 1.4342 | 70.6447 | 59.8258 | 1327.3335
2025-10-18 17:00 | 3033.96 | 1 | 70.7042 | 59.8258 | 889.1659
2025-10-19 18:00 | 3015.74 | 1 | 79.8854 | 59.8258 | 883.8261
2025-10-20 19:00 | 0 | 0 | 56.7413 | 59.8258 | 0
2025-10-21 20:00 | -1017.96 | 3.4829 | 55.1375 | 59.8258 | -298.3346
2025-10-22 21:00 | -2516.36 | 6.108 | 54.3451 | 59.8258 | -737.4723
2025-10-23 22:00 | -3446.04 | 6.108 | 53.3226 | 59.8258 | -1009.9346
2025-10-24 23:00 | -4432.01 | 6.108 | 52.2619 | 59.8258 | -1298.8939
2025-10-26 | -4711.57 | 6.108 | 51.6925 | 59.8258 | -1380.8249
2025-10-27 01:00 | -5348.64 | 6.108 | 50.9801 | 59.8258 | -1567.5316
2025-10-28 02:00 | -5532.23 | 6.108 | 50.5921 | 59.8258 | -1621.3366
2025-10-29 03:00 | -6034.2 | 6.108 | 50.0199 | 59.8258 | -1768.4495
2025-10-30 04:00 | -6052.04 | 6.108 | 49.7863 | 59.8258 | -1773.6778
2025-10-31 05:00 | -5697.27 | 6.108 | 49.9068 | 59.8258 | -1669.705
2025-11-01 06:00 | -4992.05 | 6.108 | 50.3614 | 59.8258 | -1463.0254
2025-11-02 07:00 | -4375.78 | 6.108 | 50.8645 | 59.8258 | -1282.4145
2025-11-03 08:00 | -2689.62 | 6.108 | 52.2025 | 59.8258 | -788.2498
2025-11-04 09:00 | -1830.62 | 5.7627 | 53.0262 | 59.8258 | -536.5018
2025-11-05 10:00 | -750.699 | 2.3554 | 53.2747 | 59.8258 | -220.0082
2025-11-06 11:00 | 445.971 | 1 | 54.9831 | 59.8258 | 130.7012
2025-11-07 12:00 | 2902.47 | 1 | 55.0915 | 59.8258 | 850.63
2025-11-08 13:00 | -120.129 | 0.95389 | 55.314 | 59.8258 | -35.2063
2025-11-09 14:00 | -440.796 | 1.8562 | 54.7141 | 59.8258 | -129.1846
2025-11-10 15:00 | -504.004 | 1.9673 | 54.5671 | 59.8258 | -147.709
2025-11-11 16:00 | 0 | 0 | 55.7661 | 59.8258 | 0
2025-11-12 17:00 | 1979.89 | 1 | 55.6726 | 59.8258 | 580.2485
2025-11-13 18:00 | 280.481 | 1 | 56.0851 | 59.8258 | 82.2009
2025-11-14 19:00 | -442.79 | 1.9018 | 55.028 | 59.8258 | -129.7689
2025-11-15 20:00 | -863.28 | 3.0492 | 54.7131 | 59.8258 | -253.0024
2025-11-16 21:00 | -1580.75 | 5.1409 | 54.5654 | 59.8258 | -463.2721
2025-11-17 22:00 | -1941.84 | 6.0558 | 54.4043 | 59.8258 | -569.0971
2025-11-18 23:00 | -2630.08 | 6.108 | 53.7549 | 59.8258 | -770.8004
2025-11-20 | -2789.64 | 6.108 | 53.457 | 59.8258 | -817.5628
2025-11-21 01:00 | -2802.91 | 6.108 | 53.356 | 59.8258 | -821.4518
2025-11-22 02:00 | -2778.7 | 6.108 | 53.3307 | 59.8258 | -814.3566
2025-11-23 03:00 | -2699.54 | 6.108 | 53.3774 | 59.8258 | -791.1571
2025-11-24 04:00 | -2375.18 | 6.108 | 53.6211 | 59.8258 | -696.0965
2025-11-25 05:00 | -2056.66 | 6.108 | 53.8917 | 59.8258 | -602.7475
2025-11-26 06:00 | -1575.54 | 4.8487 | 54.0157 | 59.8258 | -461.7452
2025-11-27 07:00 | -1352.4 | 4.2767 | 54.1628 | 59.8258 | -396.3493
2025-11-28 08:00 | -1019.59 | 3.3048 | 54.2826 | 59.8258 | -298.8123
2025-11-29 09:00 | -1056.07 | 3.5107 | 54.4176 | 59.8258 | -309.5036
2025-11-30 10:00 | -627.983 | 2.1779 | 54.5235 | 59.8258 | -184.0436
2025-12-01 11:00 | -258.105 | 1.1854 | 54.9305 | 59.8258 | -75.6431
2025-12-02 12:00 | 2325.89 | 1 | 55.8055 | 59.8258 | 681.6511
2025-12-03 13:00 | 3001.92 | 1 | 56.152 | 59.8258 | 879.7759
2025-12-04 14:00 | 3162.62 | 1 | 56.4701 | 59.8258 | 926.8724
2025-12-05 15:00 | 3297.47 | 1 | 56.686 | 59.8258 | 966.3931
2025-12-06 16:00 | 3184.87 | 1 | 72.6171 | 59.8258 | 933.3933
2025-12-07 17:00 | 3329.06 | 1.0292 | 72.1117 | 59.8258 | 975.6512
2025-12-08 18:00 | 3091.92 | 1 | 72.6629 | 59.8258 | 906.1523
2025-12-09 19:00 | 3078.9 | 1 | 57.2325 | 59.8258 | 902.3365
2025-12-10 20:00 | 3136.98 | 1 | 57.321 | 59.8258 | 919.3581
2025-12-11 21:00 | -197.329 | 1.1591 | 56.9254 | 59.8258 | -57.8314
2025-12-12 22:00 | -434.934 | 1.787 | 56.2444 | 59.8258 | -127.4666
2025-12-13 23:00 | -1078.21 | 3.6589 | 55.822 | 59.8258 | -315.9922
2025-12-15 | -1236.05 | 3.9654 | 55.5754 | 59.8258 | -362.2505
2025-12-16 01:00 | -1274.83 | 4.0602 | 55.4146 | 59.8258 | -373.6158
2025-12-17 02:00 | -1486.79 | 4.7028 | 55.2786 | 59.8258 | -435.7351
2025-12-18 03:00 | -1563.04 | 4.8754 | 55.1861 | 59.8258 | -458.0818
2025-12-19 04:00 | -1489.14 | 4.6363 | 55.1183 | 59.8258 | -436.4239
2025-12-20 05:00 | -1425.53 | 4.4681 | 55.0949 | 59.8258 | -417.7816
2025-12-21 06:00 | -1008.64 | 3.2165 | 55.0938 | 59.8258 | -295.6032
2025-12-22 07:00 | -699.791 | 2.4051 | 55.2191 | 59.8258 | -205.0885
2025-12-23 08:00 | -367.813 | 1.4839 | 55.4503 | 59.8258 | -107.7953
2025-12-24 09:00 | -488.896 | 1.9341 | 55.513 | 59.8258 | -143.2813
2025-12-25 10:00 | 0 | 1 | 56.7059 | 59.8258 | 0
2025-12-26 11:00 | 2358.19 | 1 | 56.5917 | 59.8258 | 691.1173
2025-12-27 12:00 | 2989.25 | 1 | 56.8963 | 59.8258 | 876.0627
2025-12-28 13:00 | 3102.77 | 1 | 57.1801 | 59.8258 | 909.3321
2025-12-29 14:00 | 3231.58 | 1 | 79.2747 | 59.8258 | 947.0826
2025-12-30 15:00 | 3234.93 | 1 | 74.1449 | 59.8258 | 948.0644
2025-12-31 16:00 | 4085.3 | 1.315 | 72.1722 | 59.8258 | 1197.2832
2026-01-01 17:00 | 4826.24 | 1.535 | 72.5483 | 59.8258 | 1414.4313
2026-01-02 18:00 | 3917.28 | 1.2471 | 72.7817 | 59.8258 | 1148.0414
2026-01-03 19:00 | 3091.78 | 1 | 76.1133 | 59.8258 | 906.1113
2026-01-04 20:00 | 3091.73 | 1 | 83.5181 | 59.8258 | 906.0966
2026-01-05 21:00 | 0 | 0 | 58.4853 | 59.8258 | 0
2026-01-06 22:00 | 0 | 0 | 58.1292 | 59.8258 | 0
2026-01-07 23:00 | -793.805 | 2.8812 | 56.6487 | 59.8258 | -232.6413
2026-01-09 | -1297.39 | 4.1889 | 56.2916 | 59.8258 | -380.2275
2026-01-10 01:00 | -1436.55 | 4.4905 | 56.0385 | 59.8258 | -421.0112
2026-01-11 02:00 | -1445.95 | 4.4988 | 55.8622 | 59.8258 | -423.7661
2026-01-12 03:00 | -1459.58 | 4.5435 | 55.7885 | 59.8258 | -427.7607
2026-01-13 04:00 | -1551.84 | 4.8235 | 55.7047 | 59.8258 | -454.7994
2026-01-14 05:00 | -1360.07 | 4.2194 | 55.616 | 59.8258 | -398.5972
2026-01-15 06:00 | -917.08 | 2.9438 | 55.6274 | 59.8258 | -268.7696
2026-01-16 07:00 | -454.778 | 1.6822 | 55.8401 | 59.8258 | -133.2823
2026-01-17 08:00 | 1772.09 | 1 | 56.9778 | 59.8258 | 519.3483
2026-01-18 09:00 | 2265.29 | 1 | 57.2829 | 59.8258 | 663.891
2026-01-19 10:00 | 3218.25 | 1 | 75.6482 | 59.8258 | 943.176
2026-01-20 11:00 | 5202.58 | 1.601 | 72.8754 | 59.8258 | 1524.7257
2026-01-21 12:00 | 5990.6 | 1.938 | 72.6148 | 59.8258 | 1755.6716
2026-01-22 13:00 | 6462.19 | 2.066 | 73.1938 | 59.8258 | 1893.8809
2026-01-23 14:00 | 7213.13 | 2.3949 | 72.9691 | 59.8258 | 2113.9597
2026-01-24 15:00 | 7847.42 | 2.5547 | 73.588 | 59.8258 | 2299.8518
2026-01-25 16:00 | 8437.75 | 2.8105 | 73.614 | 59.8258 | 2472.8604
2026-01-26 17:00 | 8014.62 | 2.5531 | 74.5597 | 59.8258 | 2348.8533
2026-01-27 18:00 | 6967.01 | 2.1643 | 75.115 | 59.8258 | 2041.8291
2026-01-28 19:00 | 4857.21 | 1.4724 | 75.5302 | 59.8258 | 1423.5077
2026-01-29 20:00 | 3134.94 | 1 | 74.5864 | 59.8258 | 918.7602
2026-01-30 21:00 | 3097.55 | 1 | 59.679 | 59.8258 | 907.8023
2026-01-31 22:00 | 119.208 | 1 | 59.8112 | 59.8258 | 34.9364
2026-02-01 23:00 | -612.186 | 2.3385 | 58.1319 | 59.8258 | -179.414
2026-02-03 | -1014.68 | 3.3424 | 57.5409 | 59.8258 | -297.3734
2026-02-04 01:00 | -1348.02 | 4.2424 | 57.2111 | 59.8258 | -395.0657
2026-02-05 02:00 | -1372.65 | 4.2409 | 56.9521 | 59.8258 | -402.284
2026-02-06 03:00 | -1300.98 | 4.0389 | 56.7515 | 59.8258 | -381.2796
2026-02-07 04:00 | -1488.73 | 4.6258 | 56.6304 | 59.8258 | -436.3037
2026-02-08 05:00 | -1546.17 | 4.7481 | 56.4806 | 59.8258 | -453.1377
2026-02-09 06:00 | -1417.91 | 4.3584 | 56.3651 | 59.8258 | -415.5484
2026-02-10 07:00 | -607.332 | 1.981 | 56.3856 | 59.8258 | -177.9914
2026-02-11 08:00 | 0 | 1 | 57.8401 | 59.8258 | 0
2026-02-12 09:00 | -195.226 | 1.169 | 57.1474 | 59.8258 | -57.2151
2026-02-13 10:00 | -139.371 | 0.90706 | 57.2223 | 59.8258 | -40.8456
2026-02-14 11:00 | -992.867 | 3.4383 | 56.605 | 59.8258 | -290.9806
2026-02-15 12:00 | -1381.53 | 4.3818 | 56.3622 | 59.8258 | -404.8865
2026-02-16 13:00 | -1830.44 | 5.6494 | 56.1804 | 59.8258 | -536.449
2026-02-17 14:00 | -1713.24 | 5.1806 | 55.977 | 59.8258 | -502.1011
2026-02-18 15:00 | -1645.34 | 5.0302 | 55.8759 | 59.8258 | -482.2016
2026-02-19 16:00 | -1227.23 | 3.7881 | 55.7828 | 59.8258 | -359.6656
2026-02-20 17:00 | 314.347 | 1 | 57.202 | 59.8258 | 92.126
2026-02-21 18:00 | -417.275 | 1.8285 | 56.3485 | 59.8258 | -122.2912
2026-02-22 19:00 | -1120.91 | 3.774 | 56.0169 | 59.8258 | -328.5063
2026-02-23 20:00 | -1792.15 | 5.6244 | 55.7961 | 59.8258 | -525.2273
2026-02-24 21:00 | -2187.45 | 6.108 | 55.4775 | 59.8258 | -641.0783
2026-02-25 22:00 | -2441.58 | 6.108 | 55.165 | 59.8258 | -715.5565
2026-02-26 23:00 | -2504.94 | 6.108 | 54.9894 | 59.8258 | -734.1254
2026-02-28 | -3865.56 | 6.108 | 53.8873 | 59.8258 | -1132.8838
2026-03-01 01:00 | -4041.74 | 6.108 | 53.5212 | 59.8258 | -1184.5171
2026-03-02 02:00 | -4113.06 | 6.108 | 53.3046 | 59.8258 | -1205.4189
2026-03-03 03:00 | -4052.43 | 6.108 | 53.2423 | 59.8258 | -1187.65
2026-03-04 04:00 | -4214.87 | 6.108 | 53.0332 | 59.8258 | -1235.2565
2026-03-05 05:00 | -4513.39 | 6.108 | 52.6817 | 59.8258 | -1322.744
2026-03-06 06:00 | -3494.42 | 6.108 | 53.321 | 59.8258 | -1024.1134
2026-03-07 07:00 | -2555.82 | 6.108 | 54.0677 | 59.8258 | -749.0369
2026-03-08 08:00 | -2338.06 | 6.108 | 54.3521 | 59.8258 | -685.2177
2026-03-09 09:00 | -1065.51 | 3.2486 | 54.6634 | 59.8258 | -312.2702
2026-03-10 10:00 | 2036.62 | 1 | 56.1867 | 59.8258 | 596.8744
2026-03-11 11:00 | 2946.73 | 1 | 74.3349 | 59.8258 | 863.6013
2026-03-12 12:00 | 3892.72 | 1.3141 | 70.8857 | 59.8258 | 1140.8436
2026-03-13 13:00 | 4123.23 | 1.3617 | 71.5823 | 59.8258 | 1208.3994
2026-03-14 14:00 | 5332.6 | 1.7665 | 71.8597 | 59.8258 | 1562.8308
2026-03-15 15:00 | 4657.56 | 1.5353 | 72.3447 | 59.8258 | 1364.9961
2026-03-16 16:00 | 6902.92 | 2.3213 | 72.2324 | 59.8258 | 2023.0462
2026-03-17 17:00 | 5729.19 | 1.7746 | 73.8551 | 59.8258 | 1679.0598
2026-03-18 18:00 | 3958.01 | 1.2283 | 73.994 | 59.8258 | 1159.9782
2026-03-19 19:00 | 3168.79 | 1 | 83.4401 | 59.8258 | 928.6807
2026-03-20 20:00 | 3136.76 | 1 | 58.7987 | 59.8258 | 919.2936
2026-03-21 21:00 | 0 | 0 | 59.1164 | 59.8258 | 0
2026-03-22 22:00 | -345.6 | 1.5555 | 57.649 | 59.8258 | -101.2854
2026-03-23 23:00 | -1590.96 | 5.1414 | 56.9585 | 59.8258 | -466.2643
2026-03-25 | -2184.16 | 6.108 | 56.4423 | 59.8258 | -640.1141
2026-03-26 01:00 | -2642.08 | 6.108 | 55.8211 | 59.8258 | -774.3172
2026-03-27 02:00 | -2817.33 | 6.108 | 55.4132 | 59.8258 | -825.6779
2026-03-28 03:00 | -2679.84 | 6.108 | 55.3411 | 59.8258 | -785.3836
2026-03-29 04:00 | -2985.92 | 6.108 | 54.9652 | 59.8258 | -875.0868
2026-03-30 05:00 | -2467.85 | 6.108 | 55.2064 | 59.8258 | -723.2554
2026-03-31 06:00 | -2399.49 | 6.108 | 55.2219 | 59.8258 | -703.2211
2026-04-01 07:00 | -1758.15 | 5.3257 | 55.472 | 59.8258 | -515.2629
2026-04-02 08:00 | -1486.31 | 4.5557 | 55.5191 | 59.8258 | -435.5945
2026-04-03 09:00 | -345.045 | 1.1933 | 55.739 | 59.8258 | -101.1227
2026-04-04 10:00 | 2407.59 | 1 | 57.0209 | 59.8258 | 705.595
2026-04-05 11:00 | 3145.3 | 1 | 75.7341 | 59.8258 | 921.7964
2026-04-06 12:00 | 2968.45 | 1 | 57.7891 | 59.8258 | 869.9668
2026-04-07 13:00 | 3572.47 | 1.1542 | 72.4564 | 59.8258 | 1046.9876
2026-04-08 14:00 | 4568.05 | 1.4876 | 72.5406 | 59.8258 | 1338.7633
2026-04-09 15:00 | 5776.15 | 1.9813 | 72.1565 | 59.8258 | 1692.8225
2026-04-10 16:00 | 5511.96 | 1.9725 | 71.9527 | 59.8258 | 1615.396
2026-04-11 17:00 | 4808.09 | 1.6375 | 72.7919 | 59.8258 | 1409.1121
2026-04-12 18:00 | 2876.65 | 1 | 74.9391 | 59.8258 | 843.0629
2026-04-13 19:00 | 2785.09 | 1 | 59.0514 | 59.8258 | 816.2293
2026-04-14 20:00 | -796.357 | 2.8598 | 57.9814 | 59.8258 | -233.3892
2026-04-15 21:00 | -1763.25 | 5.5142 | 57.3132 | 59.8258 | -516.7576
2026-04-16 22:00 | -3313.47 | 6.108 | 55.8657 | 59.8258 | -971.0822
2026-04-17 23:00 | -3940.48 | 6.108 | 54.9478 | 59.8258 | -1154.8407
2026-04-19 | -4586.3 | 6.108 | 54.1073 | 59.8258 | -1344.1118
2026-04-20 01:00 | -4770.79 | 6.108 | 53.612 | 59.8258 | -1398.1805
2026-04-21 02:00 | -5024.59 | 6.108 | 53.1703 | 59.8258 | -1472.562
2026-04-22 03:00 | -4988.45 | 6.108 | 52.9514 | 59.8258 | -1461.9704
2026-04-23 04:00 | -4952.55 | 6.108 | 52.7994 | 59.8258 | -1451.4491
2026-04-24 05:00 | -4674.31 | 6.108 | 52.8609 | 59.8258 | -1369.905
2026-04-25 06:00 | -4694.02 | 6.108 | 52.7667 | 59.8258 | -1375.6815
2026-04-26 07:00 | -4712.37 | 6.108 | 52.6504 | 59.8258 | -1381.0593
2026-04-27 08:00 | -5257.79 | 6.108 | 52.1672 | 59.8258 | -1540.9061
2026-04-28 09:00 | -4626.33 | 6.108 | 52.4909 | 59.8258 | -1355.8435
2026-04-29 10:00 | -3922.7 | 6.108 | 52.9772 | 59.8258 | -1149.6299
2026-04-30 11:00 | -3631.4 | 6.108 | 53.2222 | 59.8258 | -1064.2583
2026-05-01 12:00 | -3300.25 | 6.108 | 53.478 | 59.8258 | -967.2078
2026-05-02 13:00 | -3121.71 | 6.108 | 53.6213 | 59.8258 | -914.8829
2026-05-03 14:00 | -2725.33 | 6.108 | 53.928 | 59.8258 | -798.7154
2026-05-04 15:00 | -1882.39 | 5.8046 | 54.5063 | 59.8258 | -551.6741
2026-05-05 16:00 | -1662.42 | 5.1061 | 54.5843 | 59.8258 | -487.2072
2026-05-06 17:00 | -1720.6 | 5.3543 | 54.6562 | 59.8258 | -504.2581
2026-05-07 18:00 | -2412.66 | 6.108 | 54.3341 | 59.8258 | -707.0808
2026-05-08 19:00 | -2768.59 | 6.108 | 53.987 | 59.8258 | -811.3936
2026-05-09 20:00 | -4136.06 | 6.108 | 52.8958 | 59.8258 | -1212.1595
2026-05-10 21:00 | -4740.38 | 6.108 | 52.2219 | 59.8258 | -1389.2682
2026-05-11 22:00 | -5654.29 | 6.108 | 51.3255 | 59.8258 | -1657.1088
2026-05-12 23:00 | -6056.7 | 6.108 | 50.7756 | 59.8258 | -1775.0435
2026-05-14 | -6363.25 | 6.108 | 50.3348 | 59.8258 | -1864.8845
2026-05-15 01:00 | -6477.2 | 6.108 | 50.0608 | 59.8258 | -1898.2799
2026-05-16 02:00 | -6559.71 | 6.108 | 49.8554 | 59.8258 | -1922.4612
2026-05-17 03:00 | -6383.91 | 6.108 | 49.8537 | 59.8258 | -1870.9393
2026-05-18 04:00 | -6337.01 | 6.108 | 49.8077 | 59.8258 | -1857.1943
2026-05-19 05:00 | -5983.62 | 6.108 | 49.9977 | 59.8258 | -1753.6259
2026-05-20 06:00 | -6080.9 | 6.108 | 49.9033 | 59.8258 | -1782.1359
2026-05-21 07:00 | -5557.18 | 6.108 | 50.2423 | 59.8258 | -1628.6487
2026-05-22 08:00 | -4870.34 | 6.108 | 50.7863 | 59.8258 | -1427.3558
2026-05-23 09:00 | -3393.15 | 6.108 | 51.9858 | 59.8258 | -994.4341
2026-05-24 10:00 | -2306.87 | 6.108 | 53.0325 | 59.8258 | -676.0769
2026-05-25 11:00 | -686.783 | 2.1204 | 53.5376 | 59.8258 | -201.2762
2026-05-26 12:00 | 2406.02 | 1 | 55.1908 | 59.8258 | 705.1349
2026-05-27 13:00 | 2927.35 | 1 | 55.8018 | 59.8258 | 857.9216
2026-05-28 14:00 | 2953.94 | 1 | 78.5979 | 59.8258 | 865.7144
2026-05-29 15:00 | 3401.05 | 1.1629 | 70.1972 | 59.8258 | 996.7494
2026-05-30 16:00 | 3170.13 | 1.0716 | 70.6884 | 59.8258 | 929.0734
2026-05-31 17:00 | 2933.66 | 1 | 75.3775 | 59.8258 | 859.7709
2026-06-01 18:00 | 2783.7 | 1 | 57.2387 | 59.8258 | 815.8219
2026-06-02 19:00 | -337.109 | 1.5798 | 56.6248 | 59.8258 | -98.7969
2026-06-03 20:00 | -1564.21 | 5.1313 | 55.9226 | 59.8258 | -458.4247
2026-06-04 21:00 | -2436.8 | 6.108 | 55.2018 | 59.8258 | -714.1556
2026-06-05 22:00 | -3634.91 | 6.108 | 54.074 | 59.8258 | -1065.287
2026-06-06 23:00 | -3995.88 | 6.108 | 53.4924 | 59.8258 | -1171.0768
2026-06-08 | -4321.56 | 6.108 | 52.9607 | 59.8258 | -1266.5242
2026-06-09 01:00 | -4368.29 | 6.108 | 52.7225 | 59.8258 | -1280.2194
2026-06-10 02:00 | -4412.79 | 6.108 | 52.5399 | 59.8258 | -1293.2611
2026-06-11 03:00 | -4409.33 | 6.108 | 52.4146 | 59.8258 | -1292.2471
2026-06-12 04:00 | -4578.41 | 6.108 | 52.1944 | 59.8258 | -1341.7995
2026-06-13 05:00 | -4230.3 | 6.108 | 52.3484 | 59.8258 | -1239.7785
2026-06-14 06:00 | -4399.79 | 6.108 | 52.1796 | 59.8258 | -1289.4512
2026-06-15 07:00 | -3499.06 | 6.108 | 52.8075 | 59.8258 | -1025.4733
2026-06-16 08:00 | -2728.19 | 6.108 | 53.4708 | 59.8258 | -799.5536
2026-06-17 09:00 | -1223.63 | 3.7744 | 54.1705 | 59.8258 | -358.6106
2026-06-18 10:00 | 553.49 | 1 | 55.8862 | 59.8258 | 162.2119
2026-06-19 11:00 | 3079.85 | 1 | 76.4833 | 59.8258 | 902.6149
2026-06-20 12:00 | 4247.85 | 1.3289 | 71.4986 | 59.8258 | 1244.9219
2026-06-21 13:00 | 4585.25 | 1.5539 | 70.8852 | 59.8258 | 1343.8041
2026-06-22 14:00 | 5198.03 | 1.7234 | 71.5553 | 59.8258 | 1523.3922
2026-06-23 15:00 | 6056.54 | 2.0128 | 71.8755 | 59.8258 | 1774.9967
2026-06-24 16:00 | 5874.14 | 1.9749 | 72.1053 | 59.8258 | 1721.5405
2026-06-25 17:00 | 5131.75 | 1.6902 | 72.6266 | 59.8258 | 1503.9675
2026-06-26 18:00 | 3176.28 | 1 | 73.5831 | 59.8258 | 930.8758
2026-06-27 19:00 | 2958.1 | 1 | 58.4539 | 59.8258 | 866.9335
2026-06-28 20:00 | 0 | 0 | 58.6971 | 59.8258 | 0
2026-06-29 21:00 | -519.126 | 1.9791 | 57.1203 | 59.8258 | -152.1408
2026-06-30 22:00 | -1565.65 | 5.0529 | 56.6325 | 59.8258 | -458.8467
2026-07-01 23:00 | -2018.6 | 6.108 | 56.2479 | 59.8258 | -591.5933
2026-07-03 | -2278.52 | 6.108 | 55.8124 | 59.8258 | -667.7683
2026-07-04 01:00 | -2755.76 | 6.108 | 55.243 | 59.8258 | -807.6335
2026-07-05 02:00 | -2970.85 | 6.108 | 54.8962 | 59.8258 | -870.6702
2026-07-06 03:00 | -3134.69 | 6.108 | 54.596 | 59.8258 | -918.687
2026-07-07 04:00 | -3327.82 | 6.108 | 54.3073 | 59.8258 | -975.2878
2026-07-08 05:00 | -3024.86 | 6.108 | 54.3955 | 59.8258 | -886.499
2026-07-09 06:00 | -3307.74 | 6.108 | 54.1321 | 59.8258 | -969.4029
2026-07-10 07:00 | -3307.41 | 6.108 | 54.0366 | 59.8258 | -969.3062
2026-07-11 08:00 | -3982.42 | 6.108 | 53.4723 | 59.8258 | -1167.1321
2026-07-12 09:00 | -3768.08 | 6.108 | 53.4863 | 59.8258 | -1104.3152
2026-07-13 10:00 | -3320.91 | 6.108 | 53.7416 | 59.8258 | -973.2626
2026-07-14 11:00 | -3025.52 | 6.108 | 53.9319 | 59.8258 | -886.6924
2026-07-15 12:00 | -2868.2 | 6.108 | 54.0194 | 59.8258 | -840.5864
2026-07-16 13:00 | -3162.63 | 6.108 | 53.7587 | 59.8258 | -926.8754
2026-07-17 14:00 | -2776.35 | 6.108 | 53.9611 | 59.8258 | -813.6679
2026-07-18 15:00 | -2156.74 | 6.108 | 54.3921 | 59.8258 | -632.0781
2026-07-19 16:00 | -2070.27 | 6.108 | 54.4898 | 59.8258 | -606.7362
2026-07-20 17:00 | -2318.59 | 6.108 | 54.295 | 59.8258 | -679.5117
2026-07-21 18:00 | -3267.71 | 6.108 | 53.5298 | 59.8258 | -957.6713
2026-07-22 19:00 | -3770.21 | 6.108 | 52.9977 | 59.8258 | -1104.9395
2026-07-23 20:00 | -4957.58 | 6.108 | 51.9706 | 59.8258 | -1452.9233
2026-07-24 21:00 | -5386.68 | 6.108 | 51.4026 | 59.8258 | -1578.6801
2026-07-25 22:00 | -6228.66 | 6.108 | 50.5564 | 59.8258 | -1825.4401
2026-07-26 23:00 | -7091.92 | 6.108 | 49.651 | 59.8258 | -2078.4366
2026-07-28 | -7423.66 | 6.108 | 49.1124 | 59.8258 | -2175.66
2026-07-29 01:00 | -7815.34 | 6.108 | 48.5806 | 59.8258 | -2290.4501
2026-07-30 02:00 | -7708.6 | 6.108 | 48.4426 | 59.8258 | -2259.1677
2026-07-31 03:00 | -8139.87 | 6.108 | 47.9533 | 59.8258 | -2385.5604
2026-08-01 04:00 | -8173.1 | 6.108 | 47.7301 | 59.8258 | -2395.2992
2026-08-02 05:00 | -8571.28 | 6.108 | 47.269 | 59.8258 | -2511.9942
2026-08-03 06:00 | -7653.51 | 6.108 | 47.7787 | 59.8258 | -2243.0224
2026-08-04 07:00 | -7193.63 | 6.108 | 48.1083 | 59.8258 | -2108.2448
2026-08-05 08:00 | -6489.71 | 6.108 | 48.6563 | 59.8258 | -1901.9463
2026-08-06 09:00 | -5135.94 | 6.108 | 49.7392 | 59.8258 | -1505.1954
2026-08-07 10:00 | -3644.8 | 6.108 | 51.0551 | 59.8258 | -1068.1854
2026-08-08 11:00 | -2248.82 | 6.108 | 52.4089 | 59.8258 | -659.0641
2026-08-09 12:00 | -1285.73 | 4.0156 | 52.9685 | 59.8258 | -376.8103
2026-08-10 13:00 | -800.521 | 2.6904 | 53.4079 | 59.8258 | -234.6095
2026-08-11 14:00 | 0 | 0 | 55.0526 | 59.8258 | 0
2026-08-12 15:00 | 2644.55 | 1 | 55.1146 | 59.8258 | 775.0411
2026-08-13 16:00 | 2942.13 | 1 | 78.967 | 59.8258 | 862.2532
2026-08-14 17:00 | 2727.68 | 1 | 56.0523 | 59.8258 | 799.4041
2026-08-15 18:00 | -709.12 | 2.7026 | 55.3394 | 59.8258 | -207.8226
2026-08-16 19:00 | -1987.63 | 6.108 | 54.817 | 59.8258 | -582.5169
2026-08-17 20:00 | -2951.18 | 6.108 | 53.8774 | 59.8258 | -864.9055
2026-08-18 21:00 | -3617.9 | 6.108 | 53.1483 | 59.8258 | -1060.3018
2026-08-19 22:00 | -4260.59 | 6.108 | 52.4322 | 59.8258 | -1248.6557
2026-08-20 23:00 | -6298.73 | 6.108 | 50.6492 | 59.8258 | -1845.9755
2026-08-22 | -6908.92 | 6.108 | 49.7854 | 59.8258 | -2024.8046
2026-08-23 01:00 | -7492.91 | 6.108 | 49.0254 | 59.8258 | -2195.9552
2026-08-24 02:00 | -7899.09 | 6.108 | 48.4368 | 59.8258 | -2314.9948
2026-08-25 03:00 | -8216.87 | 6.108 | 47.9011 | 59.8258 | -2408.1269
2026-08-26 04:00 | -8459.84 | 6.108 | 47.4335 | 59.8258 | -2479.3344
2026-08-27 05:00 | -8517.31 | 6.108 | 47.1542 | 59.8258 | -2496.1772
2026-08-28 06:00 | -7693 | 6.108 | 47.6041 | 59.8258 | -2254.5957
2026-08-29 07:00 | -6418.52 | 6.108 | 48.5426 | 59.8258 | -1881.0825
2026-08-30 08:00 | -5717.09 | 6.108 | 49.1965 | 59.8258 | -1675.5137
2026-08-31 09:00 | -4450.66 | 6.108 | 50.2728 | 59.8258 | -1304.3597
2026-09-01 10:00 | -2759.19 | 6.108 | 51.7584 | 59.8258 | -808.6388
2026-09-02 11:00 | -1496.71 | 4.7224 | 52.7386 | 59.8258 | -438.6424
2026-09-03 12:00 | -638.978 | 2.1214 | 53.1815 | 59.8258 | -187.266
2026-09-04 13:00 | 222.941 | 1 | 54.8827 | 59.8258 | 65.3376
2026-09-05 14:00 | 2920.69 | 1 | 54.9911 | 59.8258 | 855.9697
2026-09-06 15:00 | 2913.67 | 1 | 55.5841 | 59.8258 | 853.9124
2026-09-07 16:00 | 3122.34 | 1.0648 | 69.6748 | 59.8258 | 915.0675
2026-09-08 17:00 | 2856.55 | 1 | 56.2319 | 59.8258 | 837.1722
2026-09-09 18:00 | 0 | 0 | 56.7159 | 59.8258 | 0
2026-09-10 19:00 | -991.927 | 3.4123 | 55.2057 | 59.8258 | -290.7051
2026-09-11 20:00 | -1657.68 | 5.3163 | 54.912 | 59.8258 | -485.8181
2026-09-12 21:00 | -2226.45 | 6.108 | 54.529 | 59.8258 | -652.5081
2026-09-13 22:00 | -3239.82 | 6.108 | 53.605 | 59.8258 | -949.4975
2026-09-14 23:00 | -4627.87 | 6.108 | 52.3224 | 59.8258 | -1356.2948
2026-09-16 | -5330.31 | 6.108 | 51.5013 | 59.8258 | -1562.1597
2026-09-17 01:00 | -5851.19 | 6.108 | 50.8519 | 59.8258 | -1714.8145
2026-09-18 02:00 | -5941.69 | 6.108 | 50.5288 | 59.8258 | -1741.3374
2026-09-19 03:00 | -6128.55 | 6.108 | 50.1915 | 59.8258 | -1796.1007
2026-09-20 04:00 | -6130.38 | 6.108 | 50.0131 | 59.8258 | -1796.637
2026-09-21 05:00 | -5942.73 | 6.108 | 50.0267 | 59.8258 | -1741.6422
2026-09-22 06:00 | -5876.31 | 6.108 | 50.0227 | 59.8258 | -1722.1765
2026-09-23 07:00 | -5092.47 | 6.108 | 50.5678 | 59.8258 | -1492.4556
2026-09-24 08:00 | -4389.97 | 6.108 | 51.1515 | 59.8258 | -1286.5732
2026-09-25 09:00 | -2448.86 | 6.108 | 52.71 | 59.8258 | -717.69
2026-09-26 10:00 | -819.861 | 2.5431 | 53.3584 | 59.8258 | -240.2775
2026-09-27 11:00 | 2765.13 | 1 | 54.9751 | 59.8258 | 810.3796
2026-09-28 12:00 | 3021.42 | 1 | 72.7142 | 59.8258 | 885.4908
2026-09-29 13:00 | 4188.25 | 1.3398 | 70.6714 | 59.8258 | 1227.4549
2026-09-30 14:00 | 5665.01 | 1.8003 | 71.2125 | 59.8258 | 1660.2505
2026-10-01 15:00 | 7061.58 | 2.3062 | 71.3407 | 59.8258 | 2069.5448
2026-10-02 16:00 | 6638.33 | 2.1974 | 71.7056 | 59.8258 | 1945.5025
2026-10-03 17:00 | 5636.83 | 1.8858 | 71.8458 | 59.8258 | 1651.9918
2026-10-04 18:00 | 3462.91 | 1.1642 | 71.9339 | 59.8258 | 1014.8787
2026-10-05 19:00 | 3074.2 | 1 | 57.946 | 59.8258 | 900.9591
2026-10-06 20:00 | 0 | 0 | 58.1934 | 59.8258 | 0
2026-10-07 21:00 | -940.416 | 3.0653 | 56.3856 | 59.8258 | -275.6087
2026-10-08 22:00 | -1886.71 | 5.9646 | 56.0052 | 59.8258 | -552.9401
2026-10-09 23:00 | -2329.53 | 6.108 | 55.3942 | 59.8258 | -682.7178
2026-10-11 | -2502.18 | 6.108 | 55.0306 | 59.8258 | -733.3166
2026-10-12 01:00 | -2515.41 | 6.108 | 54.8219 | 59.8258 | -737.1939
2026-10-13 02:00 | -2519.28 | 6.108 | 54.6991 | 59.8258 | -738.3281
2026-10-14 03:00 | -2331.26 | 6.108 | 54.7339 | 59.8258 | -683.2249
2026-10-15 04:00 | -2128.09 | 6.108 | 54.8342 | 59.8258 | -623.6816
2026-10-16 05:00 | -1796.34 | 5.4707 | 54.9101 | 59.8258 | -526.4553
2026-10-17 06:00 | -1769.1 | 5.4425 | 54.9642 | 59.8258 | -518.472
2026-10-18 07:00 | -1277.41 | 3.9392 | 54.978 | 59.8258 | -374.3719
2026-10-19 08:00 | -1152.58 | 3.7059 | 55.1351 | 59.8258 | -337.7879
2026-10-20 09:00 | -565.392 | 1.9482 | 55.3033 | 59.8258 | -165.7
2026-10-21 10:00 | 1722.56 | 1 | 56.6061 | 59.8258 | 504.8325
2026-10-22 11:00 | 3164.36 | 1 | 56.8464 | 59.8258 | 927.3824
2026-10-23 12:00 | 3177.36 | 1 | 75.0928 | 59.8258 | 931.1923
2026-10-24 13:00 | 3263.66 | 1.0313 | 72.234 | 59.8258 | 956.4843
2026-10-25 14:00 | 3116.85 | 1 | 80.4214 | 59.8258 | 913.4586
2026-10-26 15:00 | 3350.42 | 1 | 78.3408 | 59.8258 | 981.9112
2026-10-27 16:00 | 3084.31 | 1 | 57.8879 | 59.8258 | 903.922
2026-10-28 17:00 | 3195.34 | 1 | 57.9209 | 59.8258 | 936.4617
2026-10-29 18:00 | 2727.26 | 1 | 58.0402 | 59.8258 | 799.281
2026-10-30 19:00 | -219.417 | 1.237 | 57.4823 | 59.8258 | -64.3048
2026-10-31 20:00 | -1124.21 | 3.8028 | 56.6039 | 59.8258 | -329.4734
2026-11-01 21:00 | -1491.68 | 4.6847 | 56.2185 | 59.8258 | -437.1683
2026-11-02 22:00 | -2477.59 | 6.108 | 55.6333 | 59.8258 | -726.11
2026-11-03 23:00 | -2689.41 | 6.108 | 55.1926 | 59.8258 | -788.1883
2026-11-05 | -3031.55 | 6.108 | 54.7092 | 59.8258 | -888.4596
2026-11-06 01:00 | -3365.56 | 6.108 | 54.2998 | 59.8258 | -986.3483
2026-11-07 02:00 | -3617.1 | 6.108 | 53.9559 | 59.8258 | -1060.0674
2026-11-08 03:00 | -3665.54 | 6.108 | 53.7665 | 59.8258 | -1074.2637
2026-11-09 04:00 | -3735.98 | 6.108 | 53.6044 | 59.8258 | -1094.9077
2026-11-10 05:00 | -3517.5 | 6.108 | 53.6622 | 59.8258 | -1030.8775
2026-11-11 06:00 | -3559.19 | 6.108 | 53.5723 | 59.8258 | -1043.0956
2026-11-12 07:00 | -3619.84 | 6.108 | 53.4871 | 59.8258 | -1060.8704
2026-11-13 08:00 | -4132.69 | 6.108 | 53.0612 | 59.8258 | -1211.1719
2026-11-14 09:00 | -3798.48 | 6.108 | 53.1978 | 59.8258 | -1113.2246
2026-11-15 10:00 | -2988.15 | 6.108 | 53.7605 | 59.8258 | -875.7403
2026-11-16 11:00 | -1988.29 | 6.108 | 54.5506 | 59.8258 | -582.7103
2026-11-17 12:00 | -960.565 | 2.9177 | 54.6507 | 59.8258 | -281.5138
2026-11-18 13:00 | 1719.98 | 1 | 56.1889 | 59.8258 | 504.0764
2026-11-19 14:00 | 2904.24 | 1 | 56.5462 | 59.8258 | 851.1487
2026-11-20 15:00 | 2933.15 | 1 | 56.9625 | 59.8258 | 859.6214
2026-11-21 16:00 | 2906.43 | 1 | 57.2123 | 59.8258 | 851.7905
2026-11-22 17:00 | 2889.17 | 1 | 57.3924 | 59.8258 | 846.7321
2026-11-23 18:00 | -255.756 | 1.3246 | 56.9288 | 59.8258 | -74.9547
2026-11-24 19:00 | -1131.13 | 3.8388 | 56.1662 | 59.8258 | -331.5015
2026-11-25 20:00 | -2584.01 | 6.108 | 55.3379 | 59.8258 | -757.2986
2026-11-26 21:00 | -3452.46 | 6.108 | 54.4044 | 59.8258 | -1011.8161
2026-11-27 22:00 | -4719.73 | 6.108 | 53.167 | 59.8258 | -1383.2163
2026-11-28 23:00 | -5217.12 | 6.108 | 52.4265 | 59.8258 | -1528.9869
2026-11-30 | -5281.76 | 6.108 | 52.109 | 59.8258 | -1547.9311
2026-12-01 01:00 | -5582.75 | 6.108 | 51.6704 | 59.8258 | -1636.1425
2026-12-02 02:00 | -5782.21 | 6.108 | 51.309 | 59.8258 | -1694.5985
2026-12-03 03:00 | -5761.2 | 6.108 | 51.125 | 59.8258 | -1688.441
2026-12-04 04:00 | -6132.45 | 6.108 | 50.701 | 59.8258 | -1797.2437
2026-12-05 05:00 | -5748.48 | 6.108 | 50.807 | 59.8258 | -1684.7132
2026-12-06 06:00 | -5558.62 | 6.108 | 50.8777 | 59.8258 | -1629.0707
2026-12-07 07:00 | -4983.05 | 6.108 | 51.2677 | 59.8258 | -1460.3878
2026-12-08 08:00 | -4424.71 | 6.108 | 51.7215 | 59.8258 | -1296.7545
2026-12-09 09:00 | -2891.35 | 6.108 | 52.9462 | 59.8258 | -847.371
2026-12-10 10:00 | -1655.61 | 5.1519 | 53.8821 | 59.8258 | -485.2114
2026-12-11 11:00 | -778.658 | 2.4769 | 54.1973 | 59.8258 | -228.2021
2026-12-12 12:00 | -316.498 | 1.3328 | 54.8188 | 59.8258 | -92.7564
2026-12-13 13:00 | 2644.79 | 1 | 55.8931 | 59.8258 | 775.1114
2026-12-14 14:00 | 2933.95 | 1 | 56.4102 | 59.8258 | 859.8559
2026-12-15 15:00 | 2934.61 | 1 | 70.9143 | 59.8258 | 860.0493
2026-12-16 16:00 | 2959.54 | 1.016 | 70.5768 | 59.8258 | 867.3556
2026-12-17 17:00 | 2901.85 | 1 | 71.7316 | 59.8258 | 850.4483
2026-12-18 18:00 | 2781.36 | 1 | 57.3761 | 59.8258 | 815.1362
2026-12-19 19:00 | -623.7 | 2.4083 | 56.5595 | 59.8258 | -182.7884
2026-12-20 20:00 | -2178.56 | 6.108 | 55.7789 | 59.8258 | -638.4729
2026-12-21 21:00 | -3161.61 | 6.108 | 54.6795 | 59.8258 | -926.5764
2026-12-22 22:00 | -4705.31 | 6.108 | 53.2286 | 59.8258 | -1378.9902
2026-12-23 23:00 | -5381.48 | 6.108 | 52.3216 | 59.8258 | -1577.1561
2026-12-25 | -5715.39 | 6.108 | 51.7012 | 59.8258 | -1675.0155
2026-12-26 01:00 | -6035.12 | 6.108 | 51.1852 | 59.8258 | -1768.7191
2026-12-27 02:00 | -6536.19 | 6.108 | 50.5659 | 59.8258 | -1915.5682
2026-12-28 03:00 | -6774.45 | 6.108 | 50.1271 | 59.8258 | -1985.3953
2026-12-29 04:00 | -6761.93 | 6.108 | 49.9212 | 59.8258 | -1981.7261
2026-12-30 05:00 | -6192.8 | 6.108 | 50.179 | 59.8258 | -1814.9305
2026-12-31 06:00 | -5876.16 | 6.108 | 50.3414 | 59.8258 | -1722.1325
2027-01-01 07:00 | -5326.23 | 6.108 | 50.7306 | 59.8258 | -1560.9639
2027-01-02 08:00 | -4926.48 | 6.108 | 51.0705 | 59.8258 | -1443.8088
2027-01-03 09:00 | -2984.2 | 6.108 | 52.5831 | 59.8258 | -874.5827
2027-01-04 10:00 | -1381.16 | 4.3086 | 53.6341 | 59.8258 | -404.778
2027-01-05 11:00 | -248.01 | 0.94359 | 54.2529 | 59.8258 | -72.6846
2027-01-06 12:00 | 2732.28 | 1 | 55.5657 | 59.8258 | 800.7522
2027-01-07 13:00 | 3020.66 | 1 | 73.5468 | 59.8258 | 885.2681
2027-01-08 14:00 | 3222.48 | 1.0891 | 70.3449 | 59.8258 | 944.4157
2027-01-09 15:00 | 4298.78 | 1.4437 | 70.714 | 59.8258 | 1259.8481
2027-01-10 16:00 | 4333.21 | 1.4627 | 71.0133 | 59.8258 | 1269.9385
2027-01-11 17:00 | 3291.5 | 1.1126 | 71.2747 | 59.8258 | 964.6434
2027-01-12 18:00 | 3019.53 | 1 | 57.5072 | 59.8258 | 884.9369
2027-01-13 19:00 | 0 | 0 | 57.8498 | 59.8258 | 0
2027-01-14 20:00 | -1088.7 | 3.5535 | 56.1628 | 59.8258 | -319.0665
2027-01-15 21:00 | -1772.43 | 5.5839 | 55.8291 | 59.8258 | -519.448
2027-01-16 22:00 | -2971.05 | 6.108 | 54.8389 | 59.8258 | -870.7288
2027-01-17 23:00 | -3845.21 | 6.108 | 53.8951 | 59.8258 | -1126.9198
2027-01-19 | -4319.19 | 6.108 | 53.1978 | 59.8258 | -1265.8296
2027-01-20 01:00 | -4548.59 | 6.108 | 52.7788 | 59.8258 | -1333.0601
2027-01-21 02:00 | -4753.56 | 6.108 | 52.4303 | 59.8258 | -1393.1309
2027-01-22 03:00 | -4759.42 | 6.108 | 52.2369 | 59.8258 | -1394.8483
2027-01-23 04:00 | -5065.58 | 6.108 | 51.8651 | 59.8258 | -1484.575
2027-01-24 05:00 | -5050.34 | 6.108 | 51.7262 | 59.8258 | -1480.1085
2027-01-25 06:00 | -4232.8 | 6.108 | 52.2208 | 59.8258 | -1240.5112
2027-01-26 07:00 | -3446.37 | 6.108 | 52.8484 | 59.8258 | -1010.0313
2027-01-27 08:00 | -3350.99 | 6.108 | 53.0313 | 59.8258 | -982.0782
2027-01-28 09:00 | -2269.49 | 6.108 | 53.8842 | 59.8258 | -665.1219
2027-01-29 10:00 | -1088.28 | 3.3351 | 54.2492 | 59.8258 | -318.9434
2027-01-30 11:00 | 0 | 1 | 56.0021 | 59.8258 | 0
2027-01-31 12:00 | 147.109 | 1 | 56.2575 | 59.8258 | 43.1134
2027-02-01 13:00 | 2939.15 | 1 | 56.1725 | 59.8258 | 861.3798
2027-02-02 14:00 | 3009.78 | 1 | 56.6609 | 59.8258 | 882.0794
2027-02-03 15:00 | 3097.87 | 1 | 56.9617 | 59.8258 | 907.8961
2027-02-04 16:00 | 3153.81 | 1 | 77.5144 | 59.8258 | 924.2905
2027-02-05 17:00 | 3189.12 | 1 | 57.3174 | 59.8258 | 934.6388
2027-02-06 18:00 | -276.68 | 1.404 | 56.8714 | 59.8258 | -81.0869
2027-02-07 19:00 | -735.011 | 2.6555 | 56.1552 | 59.8258 | -215.4105
2027-02-08 20:00 | -1264.39 | 4.1373 | 55.8168 | 59.8258 | -370.5561
2027-02-09 21:00 | -1640.78 | 5.141 | 55.6155 | 59.8258 | -480.8652
2027-02-10 22:00 | -1713.53 | 5.272 | 55.4413 | 59.8258 | -502.1861
2027-02-11 23:00 | -3257.19 | 6.108 | 54.3673 | 59.8258 | -954.5882
2027-02-13 | -3715.09 | 6.108 | 53.7884 | 59.8258 | -1088.7854
2027-02-14 01:00 | -3886.13 | 6.108 | 53.4342 | 59.8258 | -1138.9123
2027-02-15 02:00 | -3791.09 | 6.108 | 53.3497 | 59.8258 | -1111.0588
2027-02-16 03:00 | -3899.7 | 6.108 | 53.1599 | 59.8258 | -1142.8893
2027-02-17 04:00 | -4047.69 | 6.108 | 52.9288 | 59.8258 | -1186.2608
2027-02-18 05:00 | -4025.6 | 6.108 | 52.8408 | 59.8258 | -1179.7869
2027-02-19 06:00 | -3136.43 | 6.108 | 53.462 | 59.8258 | -919.1969
2027-02-20 07:00 | -2553.95 | 6.108 | 53.9819 | 59.8258 | -748.4889
2027-02-21 08:00 | -2663.39 | 6.108 | 54.013 | 59.8258 | -780.5626
2027-02-22 09:00 | -2063.32 | 6.108 | 54.4901 | 59.8258 | -604.6994
2027-02-23 10:00 | -1461.92 | 4.4582 | 54.6191 | 59.8258 | -428.4465
2027-02-24 11:00 | 0 | 0 | 56.2641 | 59.8258 | 0
2027-02-25 12:00 | 2631.13 | 1 | 56.2939 | 59.8258 | 771.1081
2027-02-26 13:00 | 3136.32 | 1 | 80.7353 | 59.8258 | 919.1647
2027-02-27 14:00 | 3257.15 | 1.0527 | 71.4905 | 59.8258 | 954.5764
2027-02-28 15:00 | 3851.97 | 1.2416 | 71.7784 | 59.8258 | 1128.901
2027-03-01 16:00 | 6364.4 | 2.0482 | 72.0629 | 59.8258 | 1865.2215
2027-03-02 17:00 | 4555.17 | 1.4791 | 72.4942 | 59.8258 | 1334.9885
2027-03-03 18:00 | 3117.23 | 1 | 75.6839 | 59.8258 | 913.5699
2027-03-04 19:00 | 3063.97 | 1 | 58.1458 | 59.8258 | 897.961
2027-03-05 20:00 | 1403.95 | 1 | 58.3593 | 59.8258 | 411.4571
2027-03-06 21:00 | -215.793 | 1.2241 | 57.542 | 59.8258 | -63.2427
2027-03-07 22:00 | -630.825 | 2.3431 | 56.8024 | 59.8258 | -184.8766
2027-03-08 23:00 | -1774.24 | 5.6607 | 56.4214 | 59.8258 | -519.9784
2027-03-10 | -2267.04 | 6.108 | 55.9056 | 59.8258 | -664.4038
2027-03-11 01:00 | -2560.17 | 6.108 | 55.4435 | 59.8258 | -750.3118
2027-03-12 02:00 | -2800.02 | 6.108 | 55.0858 | 59.8258 | -820.6049
2027-03-13 03:00 | -3001.92 | 6.108 | 54.7882 | 59.8258 | -879.7759
2027-03-14 04:00 | -3083.53 | 6.108 | 54.5602 | 59.8258 | -903.6934
2027-03-15 05:00 | -2948.78 | 6.108 | 54.549 | 59.8258 | -864.2021
2027-03-16 06:00 | -2910.95 | 6.108 | 54.5148 | 59.8258 | -853.1152
2027-03-17 07:00 | -2179.93 | 6.108 | 54.9996 | 59.8258 | -638.8744
2027-03-18 08:00 | -1676.09 | 5.0844 | 55.1764 | 59.8258 | -491.2135
2027-03-19 09:00 | -300.854 | 1.0112 | 55.4109 | 59.8258 | -88.1716
2027-03-20 10:00 | 2694.35 | 1 | 78.0398 | 59.8258 | 789.636
2027-03-21 11:00 | 4156.33 | 1.3172 | 71.9485 | 59.8258 | 1218.1001
2027-03-22 12:00 | 5363.53 | 1.6955 | 72.5006 | 59.8258 | 1571.8955
2027-03-23 13:00 | 5888.7 | 1.8981 | 72.6721 | 59.8258 | 1725.8076
2027-03-24 14:00 | 6456.16 | 2.0672 | 73.1597 | 59.8258 | 1892.1137
2027-03-25 15:00 | 7762.26 | 2.508 | 73.3929 | 59.8258 | 2274.8938
2027-03-26 16:00 | 7801.19 | 2.4787 | 74.0464 | 59.8258 | 2286.3031
2027-03-27 17:00 | 7223.51 | 2.2796 | 74.4481 | 59.8258 | 2117.0018
2027-03-28 18:00 | 4787 | 1.5014 | 74.7172 | 59.8258 | 1402.9312
2027-03-29 19:00 | 3456.7 | 1.0973 | 74.403 | 59.8258 | 1013.0588
2027-03-30 20:00 | 3078.24 | 1 | 59.5476 | 59.8258 | 902.1431
2027-03-31 21:00 | 0 | 0 | 59.7282 | 59.8258 | 0
2027-04-01 22:00 | -929.057 | 2.9633 | 57.808 | 59.8258 | -272.2797
2027-04-02 23:00 | -1269.58 | 4.0378 | 57.3929 | 59.8258 | -372.0772
2027-04-04 | -1538.86 | 4.7463 | 57.0964 | 59.8258 | -450.9953
2027-04-05 01:00 | -1856.73 | 5.6394 | 56.8641 | 59.8258 | -544.1538
2027-04-06 02:00 | -2041.77 | 6.108 | 56.6189 | 59.8258 | -598.3837
2027-04-07 03:00 | -2028.86 | 6.051 | 56.4506 | 59.8258 | -594.6002
2027-04-08 04:00 | -1950.82 | 5.8304 | 56.3347 | 59.8258 | -571.7289
2027-04-09 05:00 | -1679.21 | 5.0402 | 56.2504 | 59.8258 | -492.1279
2027-04-10 06:00 | -1523.19 | 4.6516 | 56.2488 | 59.8258 | -446.4029
2027-04-11 07:00 | -968.853 | 3.0299 | 56.2726 | 59.8258 | -283.9428
2027-04-12 08:00 | -1107.32 | 3.6005 | 56.3828 | 59.8258 | -324.5235
2027-04-13 09:00 | -676.692 | 2.2615 | 56.4369 | 59.8258 | -198.3188
2027-04-14 10:00 | 2206.87 | 1 | 57.6675 | 59.8258 | 646.7698
2027-04-15 11:00 | 3099.94 | 1 | 78.0453 | 59.8258 | 908.5027
2027-04-16 12:00 | 3134.84 | 1 | 58.3106 | 59.8258 | 918.7309
2027-04-17 13:00 | 3145.91 | 1 | 58.4894 | 59.8258 | 921.9752
2027-04-18 14:00 | -285.788 | 1.3946 | 57.9649 | 59.8258 | -83.7562
2027-04-19 15:00 | -335.235 | 1.4508 | 57.4897 | 59.8258 | -98.2477
2027-04-20 16:00 | -408.053 | 1.6626 | 57.1819 | 59.8258 | -119.5885
2027-04-21 17:00 | -654.015 | 2.3695 | 56.8993 | 59.8258 | -191.6729
2027-04-22 18:00 | -1548.94 | 4.9709 | 56.587 | 59.8258 | -453.9495
2027-04-23 19:00 | -2057.6 | 6.108 | 56.2206 | 59.8258 | -603.023
2027-04-24 20:00 | -3407.84 | 6.108 | 55.0376 | 59.8258 | -998.7393
2027-04-25 21:00 | -4020.23 | 6.108 | 54.3022 | 59.8258 | -1178.2131
2027-04-26 22:00 | -5268.95 | 6.108 | 53.0784 | 59.8258 | -1544.1768
2027-04-27 23:00 | -5700.75 | 6.108 | 52.3788 | 59.8258 | -1670.7249
2027-04-29 | -5971.83 | 6.108 | 51.8576 | 59.8258 | -1750.1706
2027-04-30 01:00 | -6329.62 | 6.108 | 51.3166 | 59.8258 | -1855.0285
2027-05-01 02:00 | -6556.96 | 6.108 | 50.9267 | 59.8258 | -1921.6553
2027-05-02 03:00 | -6518.58 | 6.108 | 50.7499 | 59.8258 | -1910.4072
2027-05-03 04:00 | -6277.73 | 6.108 | 50.7856 | 59.8258 | -1839.821
2027-05-04 05:00 | -6308.61 | 6.108 | 50.6668 | 59.8258 | -1848.8711
2027-05-05 06:00 | -6009.22 | 6.108 | 50.7903 | 59.8258 | -1761.1285
2027-05-06 07:00 | -5372.55 | 6.108 | 51.2088 | 59.8258 | -1574.539
2027-05-07 08:00 | -5091.93 | 6.108 | 51.4511 | 59.8258 | -1492.2974
2027-05-08 09:00 | -3950.21 | 6.108 | 52.3279 | 59.8258 | -1157.6923
2027-05-09 10:00 | -2452.57 | 6.108 | 53.5694 | 59.8258 | -718.7773
2027-05-10 11:00 | -1186.68 | 3.6501 | 54.1577 | 59.8258 | -347.7816
2027-05-11 12:00 | -375.444 | 1.3928 | 54.6923 | 59.8258 | -110.0318
2027-05-12 13:00 | 1179.25 | 1 | 56.0819 | 59.8258 | 345.6041
2027-05-13 14:00 | 2927.85 | 1 | 56.3176 | 59.8258 | 858.0681
2027-05-14 15:00 | 2931.11 | 1 | 72.012 | 59.8258 | 859.0235
2027-05-15 16:00 | 2981.23 | 1.0123 | 70.8212 | 59.8258 | 873.7123
2027-05-16 17:00 | 2930.27 | 1 | 73.8305 | 59.8258 | 858.7774
2027-05-17 18:00 | 2811 | 1 | 57.5122 | 59.8258 | 823.8228
2027-05-18 19:00 | -324.379 | 1.53 | 56.9478 | 59.8258 | -95.0661
2027-05-19 20:00 | -1618.58 | 5.2775 | 56.2192 | 59.8258 | -474.359
2027-05-20 21:00 | -2355.67 | 6.108 | 55.5659 | 59.8258 | -690.3787
2027-05-21 22:00 | -3465.44 | 6.108 | 54.5152 | 59.8258 | -1015.6202
2027-05-22 23:00 | -4155 | 6.108 | 53.7056 | 59.8258 | -1217.7103
2027-05-24 | -4777.88 | 6.108 | 52.9372 | 59.8258 | -1400.2584
2027-05-25 01:00 | -5003.55 | 6.108 | 52.516 | 59.8258 | -1466.3958
2027-05-26 02:00 | -5542.04 | 6.108 | 51.9004 | 59.8258 | -1624.2116
2027-05-27 03:00 | -5390.2 | 6.108 | 51.7794 | 59.8258 | -1579.7117
2027-05-28 04:00 | -5413.75 | 6.108 | 51.6105 | 59.8258 | -1586.6135
2027-05-29 05:00 | -5108.16 | 6.108 | 51.7104 | 59.8258 | -1497.0539
2027-05-30 06:00 | -4717.55 | 6.108 | 51.9248 | 59.8258 | -1382.5774
2027-05-31 07:00 | -3554.36 | 6.108 | 52.7903 | 59.8258 | -1041.6801
2027-06-01 08:00 | -2854.45 | 6.108 | 53.4614 | 59.8258 | -836.5567
2027-06-02 09:00 | -1338 | 4.1297 | 54.2723 | 59.8258 | -392.1291
2027-06-03 10:00 | 163.595 | 1 | 56.0233 | 59.8258 | 47.945
2027-06-04 11:00 | 2971.79 | 1 | 56.1392 | 59.8258 | 870.9457
2027-06-05 12:00 | 2985.94 | 1 | 56.7357 | 59.8258 | 875.0926
2027-06-06 13:00 | 3147.73 | 1 | 57.0742 | 59.8258 | 922.5086
2027-06-07 14:00 | 3143.7 | 1 | 73.6598 | 59.8258 | 921.3275
2027-06-08 15:00 | 5056.69 | 1.6045 | 72.2376 | 59.8258 | 1481.9695
2027-06-09 16:00 | 5342.4 | 1.7336 | 72.3574 | 59.8258 | 1565.7029
2027-06-10 17:00 | 5574.34 | 1.6877 | 73.6723 | 59.8258 | 1633.6778
2027-06-11 18:00 | 3523.27 | 1.1679 | 72.6268 | 59.8258 | 1032.5685
2027-06-12 19:00 | 2917.44 | 1 | 80.7666 | 59.8258 | 855.0173
2027-06-13 20:00 | 0 | 0 | 58.7813 | 59.8258 | 0
2027-06-14 21:00 | -615.775 | 2.1283 | 57.0973 | 59.8258 | -180.4658
2027-06-15 22:00 | -1706.47 | 5.4531 | 56.7283 | 59.8258 | -500.117
2027-06-16 23:00 | -2257.48 | 6.108 | 56.1608 | 59.8258 | -661.6021
2027-06-18 | -2779.46 | 6.108 | 55.5205 | 59.8258 | -814.5793
2027-06-19 01:00 | -3117.12 | 6.108 | 55.0306 | 59.8258 | -913.5377
2027-06-20 02:00 | -3203.41 | 6.108 | 54.8023 | 59.8258 | -938.8268
2027-06-21 03:00 | -3075.62 | 6.108 | 54.7515 | 59.8258 | -901.3752
2027-06-22 04:00 | -2961.51 | 6.108 | 54.7461 | 59.8258 | -867.9329
2027-06-23 05:00 | -2504.13 | 6.108 | 55.0168 | 59.8258 | -733.8881
2027-06-24 06:00 | -2226.03 | 6.108 | 55.237 | 59.8258 | -652.385
2027-06-25 07:00 | -1967.82 | 5.9624 | 55.4186 | 59.8258 | -576.7111
2027-06-26 08:00 | -1964 | 5.9484 | 55.4748 | 59.8258 | -575.5916
2027-06-27 09:00 | -1325.27 | 4.0049 | 55.4896 | 59.8258 | -388.3983
2027-06-28 10:00 | -685.358 | 2.2671 | 55.7087 | 59.8258 | -200.8586
2027-06-29 11:00 | 2449.51 | 1 | 56.9958 | 59.8258 | 717.8805
2027-06-30 12:00 | 3120.44 | 1 | 57.414 | 59.8258 | 914.5107
2027-07-01 13:00 | 3195.63 | 1 | 79.8602 | 59.8258 | 936.5467
2027-07-02 14:00 | 3274.28 | 1 | 77.0264 | 59.8258 | 959.5967
2027-07-03 15:00 | 4532.73 | 1.4037 | 73.1901 | 59.8258 | 1328.412
2027-07-04 16:00 | 4793.24 | 1.5152 | 73.2177 | 59.8258 | 1404.76
2027-07-05 17:00 | 4667.35 | 1.4607 | 73.5689 | 59.8258 | 1367.8653
2027-07-06 18:00 | 3532.49 | 1.1309 | 73.373 | 59.8258 | 1035.2706
2027-07-07 19:00 | 3057.62 | 1 | 81.1524 | 59.8258 | 896.1
2027-07-08 20:00 | 0 | 0 | 59.0837 | 59.8258 | 0
2027-07-09 21:00 | -334.167 | 1.3767 | 57.6001 | 59.8258 | -97.9347
2027-07-10 22:00 | -1215.14 | 4.0339 | 57.1098 | 59.8258 | -356.1224
2027-07-11 23:00 | -1821.92 | 5.6151 | 56.7575 | 59.8258 | -533.952
2027-07-13 | -1957.38 | 5.8838 | 56.4747 | 59.8258 | -573.6515
2027-07-14 01:00 | -2110.86 | 6.108 | 56.2299 | 59.8258 | -618.632
2027-07-15 02:00 | -2104.75 | 6.108 | 56.1277 | 59.8258 | -616.8413
2027-07-16 03:00 | -2085.75 | 6.108 | 56.0417 | 59.8258 | -611.273
2027-07-17 04:00 | -2075.37 | 6.108 | 55.9734 | 59.8258 | -608.2309
2027-07-18 05:00 | -2263.83 | 6.108 | 55.7672 | 59.8258 | -663.4631
2027-07-19 06:00 | -1619.5 | 4.8686 | 55.8597 | 59.8258 | -474.6286
2027-07-20 07:00 | -1309.6 | 4.0452 | 55.9211 | 59.8258 | -383.8059
2027-07-21 08:00 | -2040.76 | 6.108 | 55.9427 | 59.8258 | -598.0877
2027-07-22 09:00 | -1675.17 | 5.0294 | 55.8642 | 59.8258 | -490.9439
2027-07-23 10:00 | -1116.44 | 3.4489 | 55.8997 | 59.8258 | -327.1963
2027-07-24 11:00 | -674.068 | 2.2789 | 56.0839 | 59.8258 | -197.5498
2027-07-25 12:00 | -353.538 | 1.4382 | 56.3663 | 59.8258 | -103.6118
2027-07-26 13:00 | -164.33 | 0.9586 | 56.7544 | 59.8258 | -48.1604
2027-07-27 14:00 | 1894.17 | 1 | 57.4356 | 59.8258 | 555.1264
2027-07-28 15:00 | 2966.1 | 1 | 57.6382 | 59.8258 | 869.2781
2027-07-29 16:00 | 3567.25 | 1.1389 | 72.5771 | 59.8258 | 1045.4578
2027-07-30 17:00 | 3101.99 | 1 | 78.3152 | 59.8258 | 909.1035
2027-07-31 18:00 | 3187.04 | 1 | 58.2784 | 59.8258 | 934.0292
2027-08-01 19:00 | 674.531 | 1 | 58.6431 | 59.8258 | 197.6855
2027-08-02 20:00 | -122.036 | 0.95164 | 57.9041 | 59.8258 | -35.7652
2027-08-03 21:00 | -355.128 | 1.552 | 57.241 | 59.8258 | -104.0777
2027-08-04 22:00 | -750.815 | 2.6641 | 56.8885 | 59.8258 | -220.0422
2027-08-05 23:00 | -1981.3 | 6.108 | 56.5868 | 59.8258 | -580.6617
2027-08-07 | -2392.82 | 6.108 | 56.0266 | 59.8258 | -701.2663
2027-08-08 01:00 | -2611.61 | 6.108 | 55.6959 | 59.8258 | -765.3873
2027-08-09 02:00 | -2793.47 | 6.108 | 55.4241 | 59.8258 | -818.6852
2027-08-10 03:00 | -2691.76 | 6.108 | 55.3591 | 59.8258 | -788.877
2027-08-11 04:00 | -2738.47 | 6.108 | 55.2165 | 59.8258 | -802.5663
2027-08-12 05:00 | -2703.69 | 6.108 | 55.1621 | 59.8258 | -792.3733
2027-08-13 06:00 | -1802.08 | 5.4669 | 55.6046 | 59.8258 | -528.1375
2027-08-14 07:00 | -1285.73 | 3.9238 | 55.6906 | 59.8258 | -376.8103
2027-08-15 08:00 | -1402.56 | 4.4253 | 55.8549 | 59.8258 | -411.0498
2027-08-16 09:00 | -1010.81 | 3.194 | 55.8872 | 59.8258 | -296.2392
2027-08-17 10:00 | 94.1302 | 1 | 57.4021 | 59.8258 | 27.5868
2027-08-18 11:00 | 2220.16 | 1.0515 | 67.3067 | 59.8258 | 650.6647
2027-08-19 12:00 | 4137.51 | 1.4951 | 70.6752 | 59.8258 | 1212.5845
2027-08-20 13:00 | 4875.69 | 1.711 | 71.5254 | 59.8258 | 1428.9237
2027-08-21 14:00 | 6211.83 | 2.106 | 72.3697 | 59.8258 | 1820.5077
2027-08-22 15:00 | 6824.96 | 2.2115 | 73.439 | 59.8258 | 2000.1983
2027-08-23 16:00 | 8764.22 | 2.9811 | 73.1614 | 59.8258 | 2568.5393
2027-08-24 17:00 | 7716.57 | 2.4953 | 74.4067 | 59.8258 | 2261.5034
2027-08-25 18:00 | 6022.74 | 1.9274 | 74.7792 | 59.8258 | 1765.0909
2027-08-26 19:00 | 3841.74 | 1.1877 | 75.2695 | 59.8258 | 1125.9029
2027-08-27 20:00 | 3142.14 | 1 | 80.6159 | 59.8258 | 920.8703
2027-08-28 21:00 | 3090.2 | 1 | 59.8716 | 59.8258 | 905.6482
2027-08-29 22:00 | 0 | 0 | 60.084 | 59.8258 | 0
2027-08-30 23:00 | -1203.46 | 3.9411 | 58.2295 | 59.8258 | -352.6993
2027-09-01 | -1807.07 | 5.5096 | 57.7053 | 59.8258 | -529.5999
2027-09-02 01:00 | -2243.34 | 6.108 | 57.2398 | 59.8258 | -657.4581
2027-09-03 02:00 | -2356.88 | 6.108 | 56.8865 | 59.8258 | -690.7333
2027-09-04 03:00 | -2444.51 | 6.108 | 56.5761 | 59.8258 | -716.4152
2027-09-05 04:00 | -2474.04 | 6.108 | 56.3676 | 59.8258 | -725.0696
2027-09-06 05:00 | -2240.76 | 6.108 | 56.4001 | 59.8258 | -656.7019
2027-09-07 06:00 | -1891.48 | 5.6462 | 56.4642 | 59.8258 | -554.3381
2027-09-08 07:00 | -991.3 | 2.9884 | 56.4585 | 59.8258 | -290.5214
2027-09-09 08:00 | -414.447 | 1.5393 | 56.834 | 59.8258 | -121.4624
2027-09-10 09:00 | 2223.04 | 1 | 74.2511 | 59.8258 | 651.5087
2027-09-11 10:00 | 4282.76 | 1.4424 | 72.1658 | 59.8258 | 1255.1531
2027-09-12 11:00 | 5922.33 | 2.0965 | 72.0301 | 59.8258 | 1735.6636
2027-09-13 12:00 | 6812.35 | 2.3947 | 72.6446 | 59.8258 | 1996.5027
2027-09-14 13:00 | 7739.03 | 2.6283 | 73.5593 | 59.8258 | 2268.0858
2027-09-15 14:00 | 8471.78 | 2.799 | 74.3878 | 59.8258 | 2482.8336
2027-09-16 15:00 | 10095 | 3.25 | 75.1467 | 59.8258 | 2958.5525
2027-09-17 16:00 | 10463.8 | 3.3216 | 75.8361 | 59.8258 | 3066.6371
2027-09-18 17:00 | 10058.7 | 3.1708 | 76.3304 | 59.8258 | 2947.914
2027-09-19 18:00 | 7949.84 | 2.4605 | 76.8588 | 59.8258 | 2329.8681
2027-09-20 19:00 | 6005.18 | 1.8186 | 77.1549 | 59.8258 | 1759.9445
2027-09-21 20:00 | 3286 | 1 | 78.5629 | 59.8258 | 963.0315
2027-09-22 21:00 | 3145.64 | 1 | 61.1746 | 59.8258 | 921.8961
2027-09-23 22:00 | 0 | 0 | 61.2198 | 59.8258 | 0
2027-09-24 23:00 | -679.67 | 2.1618 | 59.2097 | 59.8258 | -199.1916
2027-09-26 | -1017.85 | 3.3127 | 58.8104 | 59.8258 | -298.3024
2027-09-27 01:00 | -1357.1 | 4.2037 | 58.4452 | 59.8258 | -397.7267
2027-09-28 02:00 | -1511.59 | 4.5833 | 58.1702 | 59.8258 | -443.0033
2027-09-29 03:00 | -1606.15 | 4.8391 | 57.9122 | 59.8258 | -470.7161
2027-09-30 04:00 | -1731.46 | 5.1945 | 57.7328 | 59.8258 | -507.4408
2027-10-01 05:00 | -1384.23 | 4.1457 | 57.5666 | 59.8258 | -405.6778
2027-10-02 06:00 | -1082.38 | 3.3639 | 57.5434 | 59.8258 | -317.2143
2027-10-03 07:00 | 0 | 0 | 58.9883 | 59.8258 | 0
2027-10-04 08:00 | 1865.4 | 1 | 58.9441 | 59.8258 | 546.6948
2027-10-05 09:00 | 2880.9 | 1 | 73.279 | 59.8258 | 844.3084
2027-10-06 10:00 | 4922.41 | 1.6972 | 72.9557 | 59.8258 | 1442.616
2027-10-07 11:00 | 6712 | 2.3334 | 73.2788 | 59.8258 | 1967.093
2027-10-08 12:00 | 7983.72 | 2.6437 | 74.4462 | 59.8258 | 2339.7974
2027-10-09 13:00 | 8857.57 | 2.9051 | 75.0635 | 59.8258 | 2595.8975
2027-10-10 14:00 | 10009.6 | 3.2549 | 75.6037 | 59.8258 | 2933.5242
2027-10-11 15:00 | 11638.8 | 3.7768 | 76.0793 | 59.8258 | 3410.9956
2027-10-12 16:00 | 11751.6 | 3.806 | 76.6337 | 59.8258 | 3444.054
2027-10-13 17:00 | 11452.5 | 3.6921 | 77.0731 | 59.8258 | 3356.3964
2027-10-14 18:00 | 9347.6 | 2.9284 | 77.7529 | 59.8258 | 2739.5111
2027-10-15 19:00 | 7324.44 | 2.2126 | 78.2732 | 59.8258 | 2146.5815
2027-10-16 20:00 | 5092.8 | 1.4815 | 78.6637 | 59.8258 | 1492.5523
2027-10-17 21:00 | 3656.57 | 1.1462 | 77.1746 | 59.8258 | 1071.6349
2027-10-18 22:00 | 3068.49 | 1 | 61.9605 | 59.8258 | 899.2856
2027-10-19 23:00 | 2753.66 | 1 | 61.7086 | 59.8258 | 807.0181
2027-10-21 | -60.4041 | 0.75214 | 61.3755 | 59.8258 | -17.7027
2027-10-22 01:00 | -405.714 | 1.6596 | 60.1063 | 59.8258 | -118.903
2027-10-23 02:00 | -698.977 | 2.4212 | 59.5504 | 59.8258 | -204.8499
2027-10-24 03:00 | -901.376 | 2.9394 | 59.2064 | 59.8258 | -264.1672
2027-10-25 04:00 | -1097.34 | 3.4647 | 58.9123 | 59.8258 | -321.5986
2027-10-26 05:00 | -759.519 | 2.4505 | 58.6959 | 59.8258 | -222.593
2027-10-27 06:00 | -540.951 | 1.9196 | 58.7271 | 59.8258 | -158.5371
2027-10-28 07:00 | 0 | 1 | 59.9614 | 59.8258 | 0
2027-10-29 08:00 | 2766.86 | 1 | 59.7281 | 59.8258 | 810.8866
2027-10-30 09:00 | 3155.05 | 1.0102 | 74.6556 | 59.8258 | 924.6539
2027-10-31 10:00 | 5939.43 | 1.9142 | 74.7295 | 59.8258 | 1740.6751
2027-11-01 11:00 | 7722.45 | 2.5711 | 74.7347 | 59.8258 | 2263.2267
2027-11-02 12:00 | 8682.36 | 2.893 | 75.2757 | 59.8258 | 2544.5485
2027-11-03 13:00 | 9521.46 | 3.097 | 76.0801 | 59.8258 | 2790.4645
2027-11-04 14:00 | 10364.8 | 3.3623 | 76.5154 | 59.8258 | 3037.623
2027-11-05 15:00 | 11938.1 | 3.8569 | 76.9804 | 59.8258 | 3498.7117
2027-11-06 16:00 | 11986.3 | 3.8642 | 77.5002 | 59.8258 | 3512.8378
2027-11-07 17:00 | 11679.8 | 3.685 | 78.1484 | 59.8258 | 3423.0115
2027-11-08 18:00 | 9513.61 | 2.993 | 78.4334 | 59.8258 | 2788.1639
2027-11-09 19:00 | 7417.61 | 2.2937 | 78.6456 | 59.8258 | 2173.8869
2027-11-10 20:00 | 4717.11 | 1.443 | 78.5888 | 59.8258 | 1382.4485
2027-11-11 21:00 | 3249.1 | 1 | 79.6435 | 59.8258 | 952.2172
2027-11-12 22:00 | 3053.97 | 1 | 62.5134 | 59.8258 | 895.0303
2027-11-13 23:00 | 0 | 0 | 62.5052 | 59.8258 | 0
2027-11-15 | -454.968 | 1.663 | 60.6625 | 59.8258 | -133.338
2027-11-16 01:00 | -811.913 | 2.7214 | 60.1222 | 59.8258 | -237.9482
2027-11-17 02:00 | -1105.23 | 3.4715 | 59.74 | 59.8258 | -323.9109
2027-11-18 03:00 | -1273.52 | 3.8962 | 59.4229 | 59.8258 | -373.2319
2027-11-19 04:00 | -1231.67 | 3.7488 | 59.1473 | 59.8258 | -360.9668
2027-11-20 05:00 | -910.697 | 2.8467 | 59.0133 | 59.8258 | -266.8989
2027-11-21 06:00 | -610.818 | 2.0743 | 59.0357 | 59.8258 | -179.0131
2027-11-22 07:00 | 1845.78 | 1 | 60.176 | 59.8258 | 540.9447
2027-11-23 08:00 | 2917.28 | 1 | 60.3569 | 59.8258 | 854.9704
2027-11-24 09:00 | 3934.17 | 1.2736 | 75.0645 | 59.8258 | 1152.9914
2027-11-25 10:00 | 6489.96 | 2.2272 | 74.464 | 59.8258 | 1902.0195
2027-11-26 11:00 | 8446.59 | 2.8763 | 75.0789 | 59.8258 | 2475.4512
2027-11-27 12:00 | 9642.79 | 3.1531 | 76.22 | 59.8258 | 2826.0228
2027-11-28 13:00 | 10282.1 | 3.3207 | 76.8841 | 59.8258 | 3013.386
2027-11-29 14:00 | 10938.9 | 3.5135 | 77.3728 | 59.8258 | 3205.8751
2027-11-30 15:00 | 12485.8 | 3.989 | 77.832 | 59.8258 | 3659.2268
2027-12-01 16:00 | 12457.7 | 4.0009 | 78.2383 | 59.8258 | 3650.9915
2027-12-02 17:00 | 12171.4 | 3.8678 | 78.7138 | 59.8258 | 3567.0852
2027-12-03 18:00 | 10198.6 | 3.1948 | 79.1526 | 59.8258 | 2988.9146
2027-12-04 19:00 | 8034.12 | 2.5226 | 79.0808 | 59.8258 | 2354.5681
2027-12-05 20:00 | 5453.75 | 1.6056 | 79.8367 | 59.8258 | 1598.3363
2027-12-06 21:00 | 3897.88 | 1.1735 | 79.0781 | 59.8258 | 1142.3559
2027-12-07 22:00 | 3121.25 | 1 | 63.1891 | 59.8258 | 914.7481
2027-12-08 23:00 | 0 | 0 | 63.118 | 59.8258 | 0
2027-12-10 | -460.322 | 1.7118 | 61.242 | 59.8258 | -134.9071
2027-12-11 01:00 | -702.222 | 2.3927 | 60.6744 | 59.8258 | -205.801
2027-12-12 02:00 | -968.278 | 3.0914 | 60.2844 | 59.8258 | -283.7743
2027-12-13 03:00 | -1103.43 | 3.4224 | 59.9549 | 59.8258 | -323.3834
2027-12-14 04:00 | -1068.92 | 3.3044 | 59.6853 | 59.8258 | -313.2695
2027-12-15 05:00 | -944.565 | 2.9672 | 59.5366 | 59.8258 | -276.8247
2027-12-16 06:00 | -586.694 | 1.9825 | 59.5156 | 59.8258 | -171.943
2027-12-17 07:00 | 2358.97 | 1 | 60.595 | 59.8258 | 691.3459
2027-12-18 08:00 | 2190.44 | 1 | 60.9394 | 59.8258 | 641.9546
2027-12-19 09:00 | 3701.34 | 1.3044 | 74.2763 | 59.8258 | 1084.7557
2027-12-20 10:00 | 6187.6 | 2.1444 | 74.6779 | 59.8258 | 1813.4066
2027-12-21 11:00 | 7842.12 | 2.7749 | 74.8994 | 59.8258 | 2298.2985
2027-12-22 12:00 | 9048.03 | 2.9944 | 76.3089 | 59.8258 | 2651.7158
2027-12-23 13:00 | 9833.29 | 3.1773 | 77.0709 | 59.8258 | 2881.8528
2027-12-24 14:00 | 10576.3 | 3.457 | 77.3186 | 59.8258 | 3099.6076
2027-12-25 15:00 | 12173 | 3.9206 | 77.8994 | 59.8258 | 3567.5541
2027-12-26 16:00 | 12434.6 | 3.9935 | 78.4088 | 59.8258 | 3644.2215
2027-12-27 17:00 | 11355.8 | 3.5861 | 79.0102 | 59.8258 | 3328.0565
2027-12-28 18:00 | 9192.48 | 2.952 | 78.9079 | 59.8258 | 2694.0499
2027-12-29 19:00 | 7004.37 | 2.2432 | 78.8144 | 59.8258 | 2052.7782
2027-12-30 20:00 | 4387.91 | 1.3852 | 78.7647 | 59.8258 | 1285.9695
2027-12-31 21:00 | 3377.78 | 1.0756 | 78.1775 | 59.8258 | 989.9296
2028-01-01 22:00 | 3034.14 | 1 | 63.1487 | 59.8258 | 889.2187
2028-01-02 23:00 | 3010.82 | 1 | 62.8871 | 59.8258 | 882.3842
2028-01-04 | 0 | 0 | 62.9767 | 59.8258 | 0
2028-01-05 01:00 | -254.938 | 1.1389 | 61.416 | 59.8258 | -74.715
2028-01-06 02:00 | -334.553 | 1.4136 | 61.0149 | 59.8258 | -98.0478
2028-01-07 03:00 | -557.431 | 2.0165 | 60.604 | 59.8258 | -163.3669
2028-01-08 04:00 | -672.206 | 2.2928 | 60.2859 | 59.8258 | -197.0041
2028-01-09 05:00 | -727.428 | 2.4303 | 60.0262 | 59.8258 | -213.1881
2028-01-10 06:00 | -220.499 | 0.98935 | 60.2397 | 59.8258 | -64.6219
2028-01-11 07:00 | 222.716 | 1 | 61.1892 | 59.8258 | 65.2716
2028-01-12 08:00 | -621.678 | 2.2888 | 59.97 | 59.8258 | -182.1958
2028-01-13 09:00 | -421.516 | 1.5734 | 59.8359 | 59.8258 | -123.5341
2028-01-14 10:00 | 2602.34 | 1 | 78.3705 | 59.8258 | 762.6706
2028-01-15 11:00 | 3000.93 | 1 | 75.8233 | 59.8258 | 879.4858
2028-01-16 12:00 | 3044.63 | 1 | 77.5295 | 59.8258 | 892.293
2028-01-17 13:00 | 751.427 | 1 | 61.4351 | 59.8258 | 220.2215
2028-01-18 14:00 | -21.468 | 0.64693 | 61.0867 | 59.8258 | -6.2916
2028-01-19 15:00 | 2641.14 | 1 | 60.7444 | 59.8258 | 774.0417
2028-01-20 16:00 | 2972.55 | 1.1716 | 72.77 | 59.8258 | 871.1684
2028-01-21 17:00 | 2969.63 | 1 | 84.4637 | 59.8258 | 870.3126
2028-01-22 18:00 | 3044.22 | 1 | 60.9135 | 59.8258 | 892.1728
2028-01-23 19:00 | 0 | 0 | 61.2453 | 59.8258 | 0
2028-01-24 20:00 | -169.349 | 0.96736 | 60.1273 | 59.8258 | -49.6313
2028-01-25 21:00 | -725.591 | 2.556 | 59.4128 | 59.8258 | -212.6497
2028-01-26 22:00 | -1285.43 | 4.0362 | 59.0415 | 59.8258 | -376.7223
2028-01-27 23:00 | -2834.42 | 6.108 | 58.1314 | 59.8258 | -830.6865
2028-01-29 | -3283.05 | 6.108 | 57.4067 | 59.8258 | -962.167
2028-01-30 01:00 | -3410.84 | 6.108 | 57.0667 | 59.8258 | -999.6185
2028-01-31 02:00 | -3645.61 | 6.108 | 56.7226 | 59.8258 | -1068.4228
2028-02-01 03:00 | -3751.48 | 6.108 | 56.4497 | 59.8258 | -1099.4503
2028-02-02 04:00 | -3698.53 | 6.108 | 56.3089 | 59.8258 | -1083.9321
2028-02-03 05:00 | -3796.67 | 6.108 | 56.1113 | 59.8258 | -1112.6941
2028-02-04 06:00 | -2749.1 | 6.108 | 56.7631 | 59.8258 | -805.6817
2028-02-05 07:00 | -2103.06 | 6.108 | 57.2874 | 59.8258 | -616.346
2028-02-06 08:00 | -2233.14 | 6.108 | 57.2717 | 59.8258 | -654.4687
2028-02-07 09:00 | -1582.59 | 4.6573 | 57.3799 | 59.8258 | -463.8113
2028-02-08 10:00 | -610.847 | 1.9339 | 57.5281 | 59.8258 | -179.0216
2028-02-09 11:00 | 1647.29 | 1 | 58.9854 | 59.8258 | 482.773
2028-02-10 12:00 | 3172.09 | 1 | 59.2082 | 59.8258 | 929.6478
2028-02-11 13:00 | 3257.3 | 1 | 80.4608 | 59.8258 | 954.6204
2028-02-12 14:00 | 4330.37 | 1.3295 | 75.0147 | 59.8258 | 1269.1062
2028-02-13 15:00 | 4677.64 | 1.5515 | 74.2254 | 59.8258 | 1370.881
2028-02-14 16:00 | 7488.41 | 2.4769 | 74.5167 | 59.8258 | 2194.6363
2028-02-15 17:00 | 6583.86 | 2.1399 | 75.31 | 59.8258 | 1929.5389
2028-02-16 18:00 | 5066.57 | 1.5503 | 76.403 | 59.8258 | 1484.8651
2028-02-17 19:00 | 3429.05 | 1.051 | 76.3635 | 59.8258 | 1004.9554
2028-02-18 20:00 | 3125.3 | 1 | 61.0314 | 59.8258 | 915.935
2028-02-19 21:00 | 3130.49 | 1 | 60.9993 | 59.8258 | 917.4561
2028-02-20 22:00 | 3081.82 | 1 | 60.9689 | 59.8258 | 903.1923
2028-02-21 23:00 | -844.567 | 2.9405 | 59.9053 | 59.8258 | -247.5182
2028-02-23 | -1111.39 | 3.4919 | 59.2361 | 59.8258 | -325.7163
2028-02-24 01:00 | -1441.92 | 4.4072 | 58.8965 | 59.8258 | -422.585
2028-02-25 02:00 | -1585.72 | 4.7491 | 58.668 | 59.8258 | -464.7287
2028-02-26 03:00 | -1457.41 | 4.354 | 58.4711 | 59.8258 | -427.1247
2028-02-27 04:00 | -1233.55 | 3.7499 | 58.3104 | 59.8258 | -361.5178
2028-02-28 05:00 | -461.428 | 1.5722 | 58.4121 | 59.8258 | -135.2312
2028-02-29 06:00 | -308.071 | 1.336 | 58.7462 | 59.8258 | -90.2867
2028-03-01 07:00 | 512.706 | 1 | 59.7916 | 59.8258 | 150.2593
2028-03-02 08:00 | 1704.22 | 1 | 59.8033 | 59.8258 | 499.4576
2028-03-03 09:00 | 2777.14 | 1 | 59.9269 | 59.8258 | 813.8994
2028-03-04 10:00 | 3091.07 | 1 | 78.7391 | 59.8258 | 905.9032
2028-03-05 11:00 | 3896.77 | 1.2027 | 75.4125 | 59.8258 | 1142.0306
2028-03-06 12:00 | 4486.27 | 1.3812 | 75.6937 | 59.8258 | 1314.7959
2028-03-07 13:00 | 5620.39 | 1.7141 | 76.079 | 59.8258 | 1647.1737
2028-03-08 14:00 | 5908.94 | 1.8995 | 75.6217 | 59.8258 | 1731.7394
2028-03-09 15:00 | 8201.37 | 2.803 | 74.9967 | 59.8258 | 2403.5843
2028-03-10 16:00 | 8970.94 | 2.9977 | 75.7596 | 59.8258 | 2629.123
2028-03-11 17:00 | 9192.51 | 2.9851 | 76.5583 | 59.8258 | 2694.0587
2028-03-12 18:00 | 7804.96 | 2.4545 | 77.3327 | 59.8258 | 2287.408
2028-03-13 19:00 | 6422.75 | 1.8911 | 78.3966 | 59.8258 | 1882.3222
2028-03-14 20:00 | 3768.28 | 1.0952 | 78.5474 | 59.8258 | 1104.3739
2028-03-15 21:00 | 3255.88 | 1 | 84.8015 | 59.8258 | 954.2042
2028-03-16 22:00 | 0 | 0 | 62.2232 | 59.8258 | 0
2028-03-17 23:00 | -293.687 | 1.3207 | 60.6495 | 59.8258 | -86.0712
2028-03-19 | -341.205 | 1.4295 | 60.2127 | 59.8258 | -99.9973
2028-03-20 01:00 | -571.24 | 2.0727 | 59.8262 | 59.8258 | -167.4139
2028-03-21 02:00 | -730.615 | 2.4735 | 59.5586 | 59.8258 | -214.1221
2028-03-22 03:00 | -808.298 | 2.6648 | 59.3232 | 59.8258 | -236.8888
2028-03-23 04:00 | -789.294 | 2.5969 | 59.1917 | 59.8258 | -231.3192
2028-03-24 05:00 | -579.71 | 2.0068 | 59.1434 | 59.8258 | -169.8962
2028-03-25 06:00 | 0 | 1 | 60.3943 | 59.8258 | 0
2028-03-26 07:00 | 1914.94 | 1 | 60.2267 | 59.8258 | 561.2135
2028-03-27 08:00 | 2757.57 | 1 | 60.4024 | 59.8258 | 808.164
2028-03-28 09:00 | 3896.23 | 1.2436 | 75.2428 | 59.8258 | 1141.8723
2028-03-29 10:00 | 5650.01 | 1.817 | 75.3829 | 59.8258 | 1655.8545
2028-03-30 11:00 | 6045.07 | 1.8445 | 76.5781 | 59.8258 | 1771.6351
2028-03-31 12:00 | 4968.9 | 1.4737 | 77.3336 | 59.8258 | 1456.2408
2028-04-01 13:00 | 3730.77 | 1.1432 | 76.8845 | 59.8258 | 1093.3808
2028-04-02 14:00 | 4211.6 | 1.2583 | 77.1628 | 59.8258 | 1234.2981
2028-04-03 15:00 | 5478.17 | 1.7586 | 76.1213 | 59.8258 | 1605.4931
2028-04-04 16:00 | 6563.02 | 2.2134 | 75.5932 | 59.8258 | 1923.4313
2028-04-05 17:00 | 6692.69 | 2.1168 | 76.7056 | 59.8258 | 1961.4338
2028-04-06 18:00 | 5748 | 1.7583 | 77.3592 | 59.8258 | 1684.5725
2028-04-07 19:00 | 4628.74 | 1.424 | 77.2895 | 59.8258 | 1356.5498
2028-04-08 20:00 | 3129 | 1 | 84.2329 | 59.8258 | 917.0194
2028-04-09 21:00 | 3175.34 | 1 | 61.8223 | 59.8258 | 930.6003
2028-04-10 22:00 | 163.573 | 1 | 61.9714 | 59.8258 | 47.9385
2028-04-11 23:00 | 494.422 | 1 | 61.4562 | 59.8258 | 144.9008
2028-04-13 | 1018.74 | 1 | 61.1783 | 59.8258 | 298.5632
2028-04-14 01:00 | 0 | 0 | 61.2365 | 59.8258 | 0
2028-04-15 02:00 | 3525.21 | 1 | 60.7411 | 59.8258 | 1033.1371
2028-04-16 03:00 | 3585.4 | 1 | 61.0606 | 59.8258 | 1050.777
2028-04-17 04:00 | 3468.52 | 1 | 61.2951 | 59.8258 | 1016.5229
2028-04-18 05:00 | 3279.54 | 1 | 61.3826 | 59.8258 | 961.1383
2028-04-19 06:00 | 3253.49 | 1 | 84.9274 | 59.8258 | 953.5038
2028-04-20 07:00 | 3393.6 | 1 | 80.0465 | 59.8258 | 994.566
2028-04-21 08:00 | 3221.92 | 1 | 78.0366 | 59.8258 | 944.2515
2028-04-22 09:00 | 3198.34 | 1 | 77.1904 | 59.8258 | 937.3409
2028-04-23 10:00 | 3247.7 | 1.0386 | 76.1078 | 59.8258 | 951.8069
2028-04-24 11:00 | 4003.5 | 1.2516 | 76.4513 | 59.8258 | 1173.31
2028-04-25 12:00 | 4741.88 | 1.4572 | 76.8152 | 59.8258 | 1389.7078
2028-04-26 13:00 | 6611.09 | 2.1816 | 75.968 | 59.8258 | 1937.5192
2028-04-27 14:00 | 6803.77 | 2.3239 | 75.8338 | 59.8258 | 1993.9882
2028-04-28 15:00 | 7478.19 | 2.4446 | 76.6411 | 59.8258 | 2191.6411
2028-04-29 16:00 | 7735.91 | 2.5028 | 77.0007 | 59.8258 | 2267.1714
2028-04-30 17:00 | 7648.8 | 2.4188 | 77.5179 | 59.8258 | 2241.642
2028-05-01 18:00 | 5920.5 | 1.7233 | 78.9114 | 59.8258 | 1735.1273
2028-05-02 19:00 | 3962.21 | 1.2517 | 77.5522 | 59.8258 | 1161.2091
2028-05-03 20:00 | 3088.44 | 1 | 62.5307 | 59.8258 | 905.1324
2028-05-04 21:00 | 3153.35 | 1 | 62.2905 | 59.8258 | 924.1557
2028-05-05 22:00 | -507.145 | 1.957 | 61.2899 | 59.8258 | -148.6295
2028-05-06 23:00 | -840.988 | 2.7652 | 60.5107 | 59.8258 | -246.4693
2028-05-08 | -1314.37 | 4.048 | 60.036 | 59.8258 | -385.2038
2028-05-09 01:00 | -1518.88 | 4.5281 | 59.7159 | 59.8258 | -445.1398
2028-05-10 02:00 | -1870.26 | 5.51 | 59.4367 | 59.8258 | -548.1191
2028-05-11 03:00 | -1744.36 | 5.0719 | 59.1237 | 59.8258 | -511.2215
2028-05-12 04:00 | -1776.13 | 5.217 | 58.9737 | 59.8258 | -520.5323
2028-05-13 05:00 | -1532.47 | 4.5059 | 58.8176 | 59.8258 | -449.1226
2028-05-14 06:00 | -1547.59 | 4.6238 | 58.744 | 59.8258 | -453.5539
2028-05-15 07:00 | -1480.15 | 4.4221 | 58.6492 | 59.8258 | -433.7891
2028-05-16 08:00 | -2100.71 | 6.108 | 58.5317 | 59.8258 | -615.6573
2028-05-17 09:00 | -1792.51 | 5.2072 | 58.3541 | 59.8258 | -525.3328
2028-05-18 10:00 | -1732.83 | 5.1221 | 58.3137 | 59.8258 | -507.8423
2028-05-19 11:00 | -1394.36 | 4.1453 | 58.2533 | 59.8258 | -408.6466
2028-05-20 12:00 | -1451.06 | 4.407 | 58.2522 | 59.8258 | -425.2637
2028-05-21 13:00 | -1387.09 | 4.1989 | 58.1765 | 59.8258 | -406.516
2028-05-22 14:00 | -1212.35 | 3.7116 | 58.1374 | 59.8258 | -355.3047
2028-05-23 15:00 | -574.148 | 1.9052 | 58.2001 | 59.8258 | -168.2662
2028-05-24 16:00 | 483.346 | 1 | 59.5553 | 59.8258 | 141.6547
2028-05-25 17:00 | 1849.88 | 1 | 59.5429 | 59.8258 | 542.1463
2028-05-26 18:00 | -358.824 | 1.6043 | 58.9123 | 59.8258 | -105.1609
2028-05-27 19:00 | -755.576 | 2.622 | 58.4494 | 59.8258 | -221.4375
2028-05-28 20:00 | -1582.85 | 4.9431 | 58.1774 | 59.8258 | -463.8875
2028-05-29 21:00 | -1674.84 | 5.0028 | 57.9511 | 59.8258 | -490.8472
2028-05-30 22:00 | -2656.01 | 6.108 | 57.3893 | 59.8258 | -778.3997
2028-05-31 23:00 | -3136.15 | 6.108 | 56.797 | 59.8258 | -919.1148
2028-06-02 | -3149.01 | 6.108 | 56.6008 | 59.8258 | -922.8837
2028-06-03 01:00 | -3305.45 | 6.108 | 56.3701 | 59.8258 | -968.7318
2028-06-04 02:00 | -3193.08 | 6.108 | 56.3459 | 59.8258 | -935.7994
2028-06-05 03:00 | -3007.38 | 6.108 | 56.3952 | 59.8258 | -881.3761
2028-06-06 04:00 | -2819.24 | 6.108 | 56.4813 | 59.8258 | -826.2377
2028-06-07 05:00 | -2563.67 | 6.108 | 56.6224 | 59.8258 | -751.3375
2028-06-08 06:00 | -2431.26 | 6.108 | 56.7142 | 59.8258 | -712.532
2028-06-09 07:00 | -2410.89 | 6.108 | 56.7231 | 59.8258 | -706.5621
2028-06-10 08:00 | -2792.14 | 6.108 | 56.4262 | 59.8258 | -818.2955
2028-06-11 09:00 | -2671.26 | 6.108 | 56.4392 | 59.8258 | -782.869
2028-06-12 10:00 | -2200.2 | 6.108 | 56.7552 | 59.8258 | -644.815
2028-06-13 11:00 | -1673.68 | 4.9594 | 56.884 | 59.8258 | -490.5072
2028-06-14 12:00 | -1110.36 | 3.3892 | 56.9878 | 59.8258 | -325.4144
2028-06-15 13:00 | -788.516 | 2.5897 | 57.1776 | 59.8258 | -231.0912
2028-06-16 14:00 | -162.542 | 0.83192 | 57.7593 | 59.8258 | -47.6364
2028-06-17 15:00 | 2194.92 | 1 | 58.5797 | 59.8258 | 643.2676
2028-06-18 16:00 | 2896.19 | 1 | 58.8881 | 59.8258 | 848.7895
2028-06-19 17:00 | 3098.44 | 1 | 83.7148 | 59.8258 | 908.0631
2028-06-20 18:00 | 3106.06 | 1 | 59.3497 | 59.8258 | 910.2963
2028-06-21 19:00 | 2424.65 | 1 | 59.5947 | 59.8258 | 710.5948
2028-06-22 20:00 | -579.76 | 2.2363 | 58.6968 | 59.8258 | -169.9109
2028-06-23 21:00 | -867.363 | 2.8977 | 58.1645 | 59.8258 | -254.199
2028-06-24 22:00 | -1629.85 | 5.0751 | 57.8741 | 59.8258 | -477.6619
2028-06-25 23:00 | -2190.86 | 6.108 | 57.5221 | 59.8258 | -642.0777
2028-06-27 | -2488.41 | 6.108 | 57.0894 | 59.8258 | -729.281
2028-06-28 01:00 | -2619.38 | 6.108 | 56.8128 | 59.8258 | -767.6645
2028-06-29 02:00 | -2653.04 | 6.108 | 56.6898 | 59.8258 | -777.5293
2028-06-30 03:00 | -2627.68 | 6.108 | 56.6025 | 59.8258 | -770.097
2028-07-01 04:00 | -2850.62 | 6.108 | 56.3476 | 59.8258 | -835.4343
2028-07-02 05:00 | -2867.31 | 6.108 | 56.2239 | 59.8258 | -840.3256
2028-07-03 06:00 | -1857.18 | 5.556 | 56.7444 | 59.8258 | -544.2857
2028-07-04 07:00 | -1050.93 | 3.1604 | 56.8043 | 59.8258 | -307.9972
2028-07-05 08:00 | -1044.94 | 3.3719 | 57.0551 | 59.8258 | -306.2417
2028-07-06 09:00 | -531.041 | 1.8356 | 57.212 | 59.8258 | -155.6328
2028-07-07 10:00 | 2194.15 | 1 | 58.46 | 59.8258 | 643.0419
2028-07-08 11:00 | 2931.06 | 1 | 75.6994 | 59.8258 | 859.0089
2028-07-09 12:00 | 4376.6 | 1.4371 | 73.3855 | 59.8258 | 1282.6548
2028-07-10 13:00 | 5424.62 | 1.7698 | 73.8836 | 59.8258 | 1589.7992
2028-07-11 14:00 | 6076 | 2.0219 | 74.0421 | 59.8258 | 1780.6998
2028-07-12 15:00 | 6612.18 | 2.1921 | 74.4765 | 59.8258 | 1937.8387
2028-07-13 16:00 | 9111.17 | 2.9484 | 75.1197 | 59.8258 | 2670.2203
2028-07-14 17:00 | 7954.36 | 2.5101 | 76.069 | 59.8258 | 2331.1928
2028-07-15 18:00 | 6647.94 | 2.041 | 76.7097 | 59.8258 | 1948.3189
2028-07-16 19:00 | 4594.46 | 1.4158 | 76.6718 | 59.8258 | 1346.5033
2028-07-17 20:00 | 3359.4 | 1.051 | 76.3072 | 59.8258 | 984.543
2028-07-18 21:00 | 3183.7 | 1 | 61.239 | 59.8258 | 933.0504
2028-07-19 22:00 | 3070.14 | 1 | 61.1273 | 59.8258 | 899.7692
2028-07-20 23:00 | -901.564 | 3.079 | 59.9891 | 59.8258 | -264.2223
2028-07-22 | -1277.49 | 3.9539 | 59.2665 | 59.8258 | -374.3954
2028-07-23 01:00 | -1666.8 | 5.0167 | 58.8576 | 59.8258 | -488.4909
2028-07-24 02:00 | -1999.02 | 5.9007 | 58.5813 | 59.8258 | -585.8549
2028-07-25 03:00 | -2326.24 | 6.108 | 58.1283 | 59.8258 | -681.7536
2028-07-26 04:00 | -2598.37 | 6.108 | 57.626 | 59.8258 | -761.5071
2028-07-27 05:00 | -2675.51 | 6.108 | 57.3656 | 59.8258 | -784.1146
2028-07-28 06:00 | -1682.49 | 4.9573 | 57.6453 | 59.8258 | -493.0891
2028-07-29 07:00 | -742.285 | 2.2823 | 57.7136 | 59.8258 | -217.5423
2028-07-30 08:00 | -143.89 | 0.80227 | 58.4874 | 59.8258 | -42.17
2028-07-31 09:00 | 1854.05 | 1 | 59.2533 | 59.8258 | 543.3684
2028-08-01 10:00 | 2716.99 | 1 | 73.8028 | 59.8258 | 796.2712
2028-08-02 11:00 | 4359.99 | 1.421 | 74.0626 | 59.8258 | 1277.7869
2028-08-03 12:00 | 5313.11 | 1.7511 | 74.3012 | 59.8258 | 1557.1188
2028-08-04 13:00 | 6071.79 | 1.9065 | 75.367 | 59.8258 | 1779.466
2028-08-05 14:00 | 5351.27 | 1.6913 | 75.6323 | 59.8258 | 1568.3024
2028-08-06 15:00 | 5636.15 | 1.6867 | 76.5723 | 59.8258 | 1651.7925
2028-08-07 16:00 | 7915.61 | 2.4173 | 76.4035 | 59.8258 | 2319.8363
2028-08-08 17:00 | 6719.02 | 2.0915 | 76.5654 | 59.8258 | 1969.1504
2028-08-09 18:00 | 5469.07 | 1.6692 | 76.9787 | 59.8258 | 1602.8262
2028-08-10 19:00 | 4297.47 | 1.3097 | 76.9301 | 59.8258 | 1259.4641
2028-08-11 20:00 | 3231.17 | 1.0108 | 76.4534 | 59.8258 | 946.9624
2028-08-12 21:00 | 3160.35 | 1 | 80.5385 | 59.8258 | 926.2072
2028-08-13 22:00 | 3094.94 | 1 | 61.2814 | 59.8258 | 907.0374
2028-08-14 23:00 | -561.363 | 2.1051 | 60.2892 | 59.8258 | -164.5193
2028-08-16 | -685.729 | 2.3414 | 59.6426 | 59.8258 | -200.9673
2028-08-17 01:00 | -760.411 | 2.5413 | 59.3015 | 59.8258 | -222.8545
2028-08-18 02:00 | -717.363 | 2.4044 | 59.1511 | 59.8258 | -210.2383
2028-08-19 03:00 | -513.372 | 1.837 | 59.0972 | 59.8258 | -150.4545
2028-08-20 04:00 | -332.188 | 1.3742 | 59.1359 | 59.8258 | -97.3547
2028-08-21 05:00 | 292.724 | 1 | 60.1948 | 59.8258 | 85.7889
2028-08-22 06:00 | 3355.22 | 1 | 59.9737 | 59.8258 | 983.3179
2028-08-23 07:00 | 2083.88 | 1 | 60.5219 | 59.8258 | 610.7249
2028-08-24 08:00 | 2865.25 | 1 | 60.5263 | 59.8258 | 839.7219
2028-08-25 09:00 | 3227.42 | 1 | 82.402 | 59.8258 | 945.8634
2028-08-26 10:00 | 4975.04 | 1.5336 | 75.8754 | 59.8258 | 1458.0403
2028-08-27 11:00 | 6834.43 | 2.2578 | 75.2554 | 59.8258 | 2002.9737
2028-08-28 12:00 | 7627.47 | 2.5644 | 75.4415 | 59.8258 | 2235.3908
2028-08-29 13:00 | 8731.86 | 2.8701 | 76.141 | 59.8258 | 2559.0556
2028-08-30 14:00 | 8988.34 | 2.9807 | 76.4339 | 59.8258 | 2634.2224
2028-08-31 15:00 | 10545.3 | 3.5185 | 76.6898 | 59.8258 | 3090.5224
2028-09-01 16:00 | 11477.7 | 3.7056 | 77.586 | 59.8258 | 3363.7818
2028-09-02 17:00 | 11609.2 | 3.6976 | 78.209 | 59.8258 | 3402.3207
2028-09-03 18:00 | 9563.01 | 3.046 | 78.5235 | 59.8258 | 2802.6416
2028-09-04 19:00 | 7876.48 | 2.4058 | 79.137 | 59.8258 | 2308.3684
2028-09-05 20:00 | 5517.92 | 1.5876 | 79.9384 | 59.8258 | 1617.1427
2028-09-06 21:00 | 4124.01 | 1.2354 | 78.9886 | 59.8258 | 1208.628
2028-09-07 22:00 | 3167.63 | 1 | 63.0919 | 59.8258 | 928.3407
2028-09-08 23:00 | 3088.63 | 1 | 62.7852 | 59.8258 | 905.1881
2028-09-10 | 1546.75 | 1 | 62.7334 | 59.8258 | 453.3077
2028-09-11 01:00 | -17.3434 | 0.62836 | 62.4088 | 59.8258 | -5.0828
2028-09-12 02:00 | -97.8928 | 0.80115 | 61.5672 | 59.8258 | -28.6895
2028-09-13 03:00 | -37.9772 | 0.62355 | 61.5852 | 59.8258 | -11.13
2028-09-14 04:00 | 79.614 | 1 | 61.672 | 59.8258 | 23.3326
2028-09-15 05:00 | 1734.87 | 1 | 61.3508 | 59.8258 | 508.4402
2028-09-16 06:00 | 2605.11 | 1 | 61.3543 | 59.8258 | 763.4824
2028-09-17 07:00 | 2964.04 | 1 | 80.6434 | 59.8258 | 868.6744
2028-09-18 08:00 | 3214.22 | 1 | 76.8118 | 59.8258 | 941.9949
2028-09-19 09:00 | 4522.58 | 1.3729 | 77.0355 | 59.8258 | 1325.4374
2028-09-20 10:00 | 6071.74 | 1.9105 | 76.7587 | 59.8258 | 1779.4513
2028-09-21 11:00 | 7587.72 | 2.5105 | 76.3774 | 59.8258 | 2223.7412
2028-09-22 12:00 | 8682.64 | 2.8416 | 76.9244 | 59.8258 | 2544.6306
2028-09-23 13:00 | 9223.04 | 2.978 | 77.5196 | 59.8258 | 2703.0062
2028-09-24 14:00 | 9648.06 | 3.1867 | 77.5625 | 59.8258 | 2827.5673
2028-09-25 15:00 | 11680 | 3.7826 | 78.1358 | 59.8258 | 3423.0701
2028-09-26 16:00 | 12097.2 | 3.9173 | 78.6259 | 59.8258 | 3545.3393
2028-09-27 17:00 | 11881.8 | 3.8245 | 79.0794 | 59.8258 | 3482.2118
2028-09-28 18:00 | 9892.12 | 3.1865 | 79.3047 | 59.8258 | 2899.0942
2028-09-29 19:00 | 8094.96 | 2.5443 | 79.6185 | 59.8258 | 2372.3986
2028-09-30 20:00 | 5534.42 | 1.6699 | 80.0738 | 59.8258 | 1621.9784
2028-10-01 21:00 | 4450.18 | 1.316 | 79.9914 | 59.8258 | 1304.219
2028-10-02 22:00 | 3193.41 | 1 | 86.0493 | 59.8258 | 935.8961
2028-10-03 23:00 | 3244.11 | 1 | 63.5245 | 59.8258 | 950.7548
2028-10-05 | 3147.39 | 1 | 63.3275 | 59.8258 | 922.409
2028-10-06 01:00 | 3069.03 | 1 | 63.1907 | 59.8258 | 899.4439
2028-10-07 02:00 | 3179.15 | 1 | 63.0841 | 59.8258 | 931.7169
2028-10-08 03:00 | 2502.54 | 1 | 63.0717 | 59.8258 | 733.4221
2028-10-09 04:00 | 3321.09 | 1 | 62.8522 | 59.8258 | 973.3154
2028-10-10 05:00 | 3299.18 | 1 | 62.8446 | 59.8258 | 966.8942
2028-10-11 06:00 | 3321.07 | 1 | 80.8481 | 59.8258 | 973.3095
2028-10-12 07:00 | 4395.44 | 1.288 | 78.6623 | 59.8258 | 1288.1763
2028-10-13 08:00 | 4501.26 | 1.3443 | 78.5132 | 59.8258 | 1319.1891
2028-10-14 09:00 | 5743.85 | 1.8298 | 77.6588 | 59.8258 | 1683.3563
2028-10-15 10:00 | 6281.45 | 2.0653 | 77.4222 | 59.8258 | 1840.9113
2028-10-16 11:00 | 7405.75 | 2.4674 | 77.4282 | 59.8258 | 2170.4111
2028-10-17 12:00 | 7400.61 | 2.3246 | 78.5254 | 59.8258 | 2168.9047
2028-10-18 13:00 | 6771.66 | 2.2403 | 77.9405 | 59.8258 | 1984.5776
2028-10-19 14:00 | 5833.49 | 1.7631 | 79.2714 | 59.8258 | 1709.6272
2028-10-20 15:00 | 6990.98 | 2.2127 | 78.4664 | 59.8258 | 2048.854
2028-10-21 16:00 | 7198.79 | 2.3398 | 78.176 | 59.8258 | 2109.7571
2028-10-22 17:00 | 7548.76 | 2.4404 | 78.3107 | 59.8258 | 2212.3232
2028-10-23 18:00 | 6742.33 | 2.0752 | 79.1029 | 59.8258 | 1975.9819
2028-10-24 19:00 | 5558.83 | 1.6459 | 79.6554 | 59.8258 | 1629.1323
2028-10-25 20:00 | 3328.97 | 1 | 79.78 | 59.8258 | 975.6248
2028-10-26 21:00 | 3239.25 | 1 | 85.1134 | 59.8258 | 949.3305
2028-10-27 22:00 | 2904.29 | 1 | 63.2834 | 59.8258 | 851.1634
2028-10-28 23:00 | 80.094 | 1 | 63.3624 | 59.8258 | 23.4732
2028-10-30 | -213.662 | 1.1199 | 61.9718 | 59.8258 | -62.6182
2028-10-31 01:00 | -405.999 | 1.6066 | 61.3377 | 59.8258 | -118.9866
2028-11-01 02:00 | -381.892 | 1.5021 | 61.1271 | 59.8258 | -111.9215
2028-11-02 03:00 | -166.076 | 0.91418 | 61.2737 | 59.8258 | -48.6721
2028-11-03 04:00 | -116.951 | 0.83136 | 61.3116 | 59.8258 | -34.275
2028-11-04 05:00 | 1551.47 | 1 | 61.7193 | 59.8258 | 454.691
2028-11-05 06:00 | 2475.04 | 1 | 61.766 | 59.8258 | 725.3626
2028-11-06 07:00 | 2879.54 | 1 | 61.8975 | 59.8258 | 843.9099
2028-11-07 08:00 | -49.1351 | 0.70203 | 61.9675 | 59.8258 | -14.4001
2028-11-08 09:00 | 0 | 1 | 61.9498 | 59.8258 | 0
2028-11-09 10:00 | 3105.22 | 1 | 61.4865 | 59.8258 | 910.0501
2028-11-10 11:00 | 3399.42 | 1.0573 | 76.8168 | 59.8258 | 996.2717
2028-11-11 12:00 | 4336.39 | 1.3519 | 76.8864 | 59.8258 | 1270.8705
2028-11-12 13:00 | 3316.86 | 1 | 86.228 | 59.8258 | 972.0757
2028-11-13 14:00 | 3117.92 | 1 | 82.7637 | 59.8258 | 913.7722
2028-11-14 15:00 | 4135.58 | 1.3222 | 76.6774 | 59.8258 | 1212.0189
2028-11-15 16:00 | 4237.3 | 1.3445 | 76.9079 | 59.8258 | 1241.83
2028-11-16 17:00 | 5313.46 | 1.6814 | 76.9864 | 59.8258 | 1557.2214
2028-11-17 18:00 | 4076.59 | 1.2691 | 77.3652 | 59.8258 | 1194.7306
2028-11-18 19:00 | 3028.32 | 1 | 81.7135 | 59.8258 | 887.513
2028-11-19 20:00 | 2934.25 | 1 | 62.2429 | 59.8258 | 859.9438
2028-11-20 21:00 | -22.8367 | 0.64112 | 62.3057 | 59.8258 | -6.6928
2028-11-21 22:00 | -828.72 | 2.8224 | 60.6884 | 59.8258 | -242.8739
2028-11-22 23:00 | -1229.62 | 3.7963 | 60.1695 | 59.8258 | -360.366
2028-11-24 | -1497.75 | 4.4833 | 59.8568 | 59.8258 | -438.9472
2028-11-25 01:00 | -1667.96 | 4.9193 | 59.6187 | 59.8258 | -488.8308
2028-11-26 02:00 | -1613.05 | 4.7326 | 59.4043 | 59.8258 | -472.7383
2028-11-27 03:00 | -1456.53 | 4.3067 | 59.2926 | 59.8258 | -426.8668
2028-11-28 04:00 | -1260.18 | 3.7867 | 59.232 | 59.8258 | -369.3223
2028-11-29 05:00 | -842.772 | 2.6417 | 59.2111 | 59.8258 | -246.9921
2028-11-30 06:00 | -460.044 | 1.6571 | 59.3685 | 59.8258 | -134.8256
2028-12-01 07:00 | 198.212 | 1 | 60.6276 | 59.8258 | 58.0902
2028-12-02 08:00 | 2417.33 | 1 | 60.5017 | 59.8258 | 708.4495
2028-12-03 09:00 | 3165.23 | 1 | 80.3054 | 59.8258 | 927.6373
2028-12-04 10:00 | 5187.2 | 1.6572 | 75.6366 | 59.8258 | 1520.2183
2028-12-05 11:00 | 7110.55 | 2.3535 | 75.5681 | 59.8258 | 2083.8965
2028-12-06 12:00 | 8609.4 | 2.7255 | 76.728 | 59.8258 | 2523.1661
2028-12-07 13:00 | 9738.3 | 3.2303 | 76.6175 | 59.8258 | 2854.014
2028-12-08 14:00 | 11008.9 | 3.5063 | 77.6954 | 59.8258 | 3226.3901
2028-12-09 15:00 | 11980.5 | 3.7923 | 78.3151 | 59.8258 | 3511.138
2028-12-10 16:00 | 12220.6 | 3.795 | 79.0999 | 59.8258 | 3581.5043
2028-12-11 17:00 | 11188.3 | 3.4971 | 79.3929 | 59.8258 | 3278.9671
2028-12-12 18:00 | 9600.54 | 2.9936 | 79.6091 | 59.8258 | 2813.6405
2028-12-13 19:00 | 8021.72 | 2.4561 | 79.8727 | 59.8258 | 2350.9341
2028-12-14 20:00 | 5684.34 | 1.7076 | 80.0245 | 59.8258 | 1665.9156
2028-12-15 21:00 | 4470.63 | 1.327 | 79.8817 | 59.8258 | 1310.2123
2028-12-16 22:00 | 3198.46 | 1 | 63.873 | 59.8258 | 937.3761
2028-12-17 23:00 | 2852.87 | 1 | 63.5687 | 59.8258 | 836.0937
2028-12-19 | 120.924 | 1 | 63.5606 | 59.8258 | 35.4393
2028-12-20 01:00 | -140.05 | 0.92227 | 62.3393 | 59.8258 | -41.0446
2028-12-21 02:00 | -301.353 | 1.3318 | 61.6325 | 59.8258 | -88.3178
2028-12-22 03:00 | -512.224 | 1.8851 | 61.1609 | 59.8258 | -150.118
2028-12-23 04:00 | -714.318 | 2.4077 | 60.7973 | 59.8258 | -209.3459
2028-12-24 05:00 | -775.68 | 2.5408 | 60.5079 | 59.8258 | -227.3294
2028-12-25 06:00 | 0 | 1 | 61.7415 | 59.8258 | 0
2028-12-26 07:00 | 1848.01 | 1 | 61.5462 | 59.8258 | 541.5983
2028-12-27 08:00 | 0 | 0 | 61.9153 | 59.8258 | 0
2028-12-28 09:00 | 3868.15 | 1 | 61.4032 | 59.8258 | 1133.6429
2028-12-29 10:00 | 3733.41 | 1 | 79.7368 | 59.8258 | 1094.1545
2028-12-30 11:00 | 5283.02 | 1.5111 | 78.3193 | 59.8258 | 1548.3003
2028-12-31 12:00 | 6077.35 | 1.8551 | 77.612 | 59.8258 | 1781.0955
2029-01-01 13:00 | 6362.14 | 2.0494 | 77.1083 | 59.8258 | 1864.5592
2029-01-02 14:00 | 7328.42 | 2.428 | 76.9686 | 59.8258 | 2147.7479
2029-01-03 15:00 | 7704.8 | 2.4867 | 77.5798 | 59.8258 | 2258.054
2029-01-04 16:00 | 10588.6 | 3.5646 | 77.2158 | 59.8258 | 3103.2123
2029-01-05 17:00 | 9562.05 | 3.0659 | 78.4436 | 59.8258 | 2802.3602
2029-01-06 18:00 | 8330.16 | 2.6183 | 78.9501 | 59.8258 | 2441.3289
2029-01-07 19:00 | 6559.06 | 2.0159 | 79.2832 | 59.8258 | 1922.2707
2029-01-08 20:00 | 5635.49 | 1.6686 | 79.7306 | 59.8258 | 1651.5991
2029-01-09 21:00 | 4762.59 | 1.4186 | 79.5022 | 59.8258 | 1395.7773
2029-01-10 22:00 | 3776.01 | 1.1802 | 78.588 | 59.8258 | 1106.6393
2029-01-11 23:00 | 3059.85 | 1 | 63.4545 | 59.8258 | 896.7535
2029-01-13 | 1366.61 | 1 | 63.3963 | 59.8258 | 400.5139
2029-01-14 01:00 | 2084.51 | 1 | 62.9979 | 59.8258 | 610.9096
2029-01-15 02:00 | 83.794 | 1 | 63.0718 | 59.8258 | 24.5576
2029-01-16 03:00 | -31.1082 | 0.62634 | 62.508 | 59.8258 | -9.1169
2029-01-17 04:00 | -39.1343 | 0.63794 | 62.1735 | 59.8258 | -11.4691
2029-01-18 05:00 | -51.3074 | 0.67144 | 61.925 | 59.8258 | -15.0367
2029-01-19 06:00 | 2091.1 | 1 | 75.8309 | 59.8258 | 612.8409
2029-01-20 07:00 | 3077.25 | 1.0803 | 75.3168 | 59.8258 | 901.853
2029-01-21 08:00 | 2423.8 | 1 | 62.303 | 59.8258 | 710.3457
2029-01-22 09:00 | 0 | 0 | 62.5161 | 59.8258 | 0
2029-01-23 10:00 | -127.733 | 0.91404 | 61.5411 | 59.8258 | -37.4348
2029-01-24 11:00 | 2246.91 | 1 | 61.7832 | 59.8258 | 658.5043
2029-01-25 12:00 | 2921.7 | 1 | 61.8985 | 59.8258 | 856.2657
2029-01-26 13:00 | 2999.92 | 1 | 61.993 | 59.8258 | 879.1898
2029-01-27 14:00 | 3362.74 | 1 | 61.9818 | 59.8258 | 985.5218
2029-01-28 15:00 | 2735.51 | 1 | 62.1302 | 59.8258 | 801.6988
2029-01-29 16:00 | 3117.2 | 1.1208 | 75.0886 | 59.8258 | 913.5611
2029-01-30 17:00 | 2966.81 | 1 | 85.2788 | 59.8258 | 869.4862
2029-01-31 18:00 | 3093.92 | 1 | 62.0038 | 59.8258 | 906.7384
2029-02-01 19:00 | 0 | 0 | 62.26 | 59.8258 | 0
2029-02-02 20:00 | -702.631 | 2.4633 | 60.5142 | 59.8258 | -205.9208
2029-02-03 21:00 | -1116.04 | 3.5124 | 60.0542 | 59.8258 | -327.079
2029-02-04 22:00 | -1507.57 | 4.5433 | 59.7719 | 59.8258 | -441.8252
2029-02-05 23:00 | -2790.72 | 6.108 | 58.966 | 59.8258 | -817.8793
2029-02-07 | -3075.38 | 6.108 | 58.3852 | 59.8258 | -901.3049
2029-02-08 01:00 | -3394.88 | 6.108 | 57.8932 | 59.8258 | -994.9411
2029-02-09 02:00 | -3660.94 | 6.108 | 57.4817 | 59.8258 | -1072.9156
2029-02-10 03:00 | -3547.16 | 6.108 | 57.3639 | 59.8258 | -1039.57
2029-02-11 04:00 | -3797.08 | 6.108 | 57.0213 | 59.8258 | -1112.8143
2029-02-12 05:00 | -3637.36 | 6.108 | 56.9825 | 59.8258 | -1066.005
2029-02-13 06:00 | -2999.7 | 6.108 | 57.3222 | 59.8258 | -879.1253
2029-02-14 07:00 | -2252.76 | 6.108 | 57.861 | 59.8258 | -660.2188
2029-02-15 08:00 | -1936.31 | 5.6575 | 58.0489 | 59.8258 | -567.4764
2029-02-16 09:00 | -1025.18 | 3.0233 | 58.1081 | 59.8258 | -300.4506
2029-02-17 10:00 | 0 | 1 | 59.7973 | 59.8258 | 0
2029-02-18 11:00 | 3245.14 | 1 | 59.7131 | 59.8258 | 951.0567
2029-02-19 12:00 | 3132.93 | 1 | 76.7656 | 59.8258 | 918.1711
2029-02-20 13:00 | 3492.62 | 1.1468 | 74.7446 | 59.8258 | 1023.5859
2029-02-21 14:00 | 4732 | 1.4787 | 75.6773 | 59.8258 | 1386.8123
2029-02-22 15:00 | 6374.42 | 2.0805 | 75.4002 | 59.8258 | 1868.1581
2029-02-23 16:00 | 7165.54 | 2.3175 | 75.9909 | 59.8258 | 2100.0125
2029-02-24 17:00 | 6615.65 | 2.1377 | 76.3705 | 59.8258 | 1938.8556
2029-02-25 18:00 | 5192.45 | 1.6365 | 76.9222 | 59.8258 | 1521.7569
2029-02-26 19:00 | 3061.48 | 1 | 76.8239 | 59.8258 | 897.2312
2029-02-27 20:00 | 2918.12 | 1 | 61.9653 | 59.8258 | 855.2166
2029-02-28 21:00 | -158.784 | 1.0058 | 61.4117 | 59.8258 | -46.535
2029-03-01 22:00 | -1118.22 | 3.6254 | 60.266 | 59.8258 | -327.7179
2029-03-02 23:00 | -2064.71 | 6.108 | 59.713 | 59.8258 | -605.1068
2029-03-04 | -2510.48 | 6.108 | 59.0304 | 59.8258 | -735.7491
2029-03-05 01:00 | -2879.13 | 6.108 | 58.4759 | 59.8258 | -843.7897
2029-03-06 02:00 | -3037.1 | 6.108 | 58.0828 | 59.8258 | -890.0861
2029-03-07 03:00 | -3070.65 | 6.108 | 57.8484 | 59.8258 | -899.9187
2029-03-08 04:00 | -3157.34 | 6.108 | 57.6054 | 59.8258 | -925.325
2029-03-09 05:00 | -2785.74 | 6.108 | 57.7268 | 59.8258 | -816.4198
2029-03-10 06:00 | -2072.05 | 6.0804 | 58.1678 | 59.8258 | -607.2579
2029-03-11 07:00 | -1207.81 | 3.51 | 58.1675 | 59.8258 | -353.9742
2029-03-12 08:00 | -362.149 | 1.3079 | 58.5579 | 59.8258 | -106.1354
2029-03-13 09:00 | 2113.66 | 1 | 59.8058 | 59.8258 | 619.4526
2029-03-14 10:00 | 2932.51 | 1 | 73.9571 | 59.8258 | 859.4338
2029-03-15 11:00 | 5148.72 | 1.6759 | 74.7972 | 59.8258 | 1508.9409
2029-03-16 12:00 | 6197.27 | 1.9924 | 75.46 | 59.8258 | 1816.2405
2029-03-17 13:00 | 7216.08 | 2.344 | 75.7724 | 59.8258 | 2114.8243
2029-03-18 14:00 | 7934.87 | 2.594 | 76.1193 | 59.8258 | 2325.4808
2029-03-19 15:00 | 9462.21 | 3.0753 | 76.5718 | 59.8258 | 2773.1
2029-03-20 16:00 | 9581.82 | 3.1175 | 77.0409 | 59.8258 | 2808.1542
2029-03-21 17:00 | 8677.66 | 2.7496 | 77.7626 | 59.8258 | 2543.1711
2029-03-22 18:00 | 7431.61 | 2.3082 | 78.197 | 59.8258 | 2177.9899
2029-03-23 19:00 | 5389.54 | 1.6428 | 78.4926 | 59.8258 | 1579.5183
2029-03-24 20:00 | 3182.81 | 1 | 82.7884 | 59.8258 | 932.7895
2029-03-25 21:00 | 3068.1 | 1 | 62.6722 | 59.8258 | 899.1713
2029-03-26 22:00 | -623.168 | 2.2558 | 61.4943 | 59.8258 | -182.6325
2029-03-27 23:00 | -1110.34 | 3.4876 | 60.6916 | 59.8258 | -325.4085
2029-03-29 | -1538.47 | 4.6098 | 60.184 | 59.8258 | -450.881
2029-03-30 01:00 | -1943.29 | 5.6826 | 59.8451 | 59.8258 | -569.5221
2029-03-31 02:00 | -2054.87 | 5.922 | 59.5495 | 59.8258 | -602.2229
2029-04-01 03:00 | -1929.93 | 5.5573 | 59.2822 | 59.8258 | -565.6067
2029-04-02 04:00 | -2069.39 | 6.0074 | 59.1522 | 59.8258 | -606.4783
2029-04-03 05:00 | -1464.58 | 4.2217 | 58.9896 | 59.8258 | -429.226
2029-04-04 06:00 | -1445.71 | 4.341 | 59.0075 | 59.8258 | -423.6958
2029-04-05 07:00 | -967.592 | 2.9537 | 58.9796 | 59.8258 | -283.5732
2029-04-06 08:00 | -503.201 | 1.7538 | 59.181 | 59.8258 | -147.4737
2029-04-07 09:00 | 2086.15 | 1 | 60.3403 | 59.8258 | 611.3902
2029-04-08 10:00 | 3019.51 | 1 | 77.0084 | 59.8258 | 884.931
2029-04-09 11:00 | 4449.14 | 1.4234 | 75.4832 | 59.8258 | 1303.9142
2029-04-10 12:00 | 5664.93 | 1.7941 | 75.9819 | 59.8258 | 1660.2271
2029-04-11 13:00 | 6382.69 | 2.0806 | 75.9599 | 59.8258 | 1870.5818
2029-04-12 14:00 | 7237.01 | 2.3477 | 76.3793 | 59.8258 | 2120.9583
2029-04-13 15:00 | 8937.13 | 2.9186 | 76.589 | 59.8258 | 2619.2143
2029-04-14 16:00 | 9337.32 | 3.0417 | 77.0655 | 59.8258 | 2736.4984
2029-04-15 17:00 | 9415.69 | 2.967 | 77.8805 | 59.8258 | 2759.4663
2029-04-16 18:00 | 7863.4 | 2.4569 | 78.2684 | 59.8258 | 2304.5351
2029-04-17 19:00 | 5821.17 | 1.762 | 78.778 | 59.8258 | 1706.0165
2029-04-18 20:00 | 3273.76 | 1.0041 | 78.4178 | 59.8258 | 959.4443
2029-04-19 21:00 | 3167.18 | 1 | 62.8245 | 59.8258 | 928.2088
2029-04-20 22:00 | 0 | 0 | 62.9137 | 59.8258 | 0
2029-04-21 23:00 | -454.826 | 1.6275 | 61.0804 | 59.8258 | -133.2963
2029-04-23 | -639.829 | 2.2267 | 60.6427 | 59.8258 | -187.5154
2029-04-24 01:00 | -909.909 | 2.9417 | 60.2912 | 59.8258 | -266.668
2029-04-25 02:00 | -1156.34 | 3.5836 | 60.0205 | 59.8258 | -338.8898
2029-04-26 03:00 | -1099.59 | 3.373 | 59.7658 | 59.8258 | -322.258
2029-04-27 04:00 | -1318.77 | 4.0249 | 59.6193 | 59.8258 | -386.4933
2029-04-28 05:00 | -751.894 | 2.351 | 59.4928 | 59.8258 | -220.3584
2029-04-29 06:00 | -217.925 | 0.9931 | 59.8965 | 59.8258 | -63.8675
2029-04-30 07:00 | 2089.07 | 1 | 60.7337 | 59.8258 | 612.246
2029-05-01 08:00 | 2922.54 | 1 | 60.9696 | 59.8258 | 856.5119
2029-05-02 09:00 | 3084.7 | 1 | 85.0109 | 59.8258 | 904.0363
2029-05-03 10:00 | 4722.19 | 1.378 | 77.3018 | 59.8258 | 1383.9373
2029-05-04 11:00 | 6142.4 | 1.9685 | 76.2545 | 59.8258 | 1800.1597
2029-05-05 12:00 | 7193.53 | 2.3035 | 76.6809 | 59.8258 | 2108.2155
2029-05-06 13:00 | 8372.73 | 2.6386 | 77.2728 | 59.8258 | 2453.8049
2029-05-07 14:00 | 8902.05 | 2.9394 | 77.0054 | 59.8258 | 2608.9333
2029-05-08 15:00 | 10200.3 | 3.4152 | 77.1572 | 59.8258 | 2989.4128
2029-05-09 16:00 | 10723.8 | 3.4892 | 77.9667 | 59.8258 | 3142.8355
2029-05-10 17:00 | 10609.5 | 3.3758 | 78.6418 | 59.8258 | 3109.3375
2029-05-11 18:00 | 8677.63 | 2.6971 | 79.2432 | 59.8258 | 2543.1623
2029-05-12 19:00 | 7286.7 | 2.15 | 79.9803 | 59.8258 | 2135.521
2029-05-13 20:00 | 4729.4 | 1.3027 | 80.9663 | 59.8258 | 1386.0503
2029-05-14 21:00 | 3451.65 | 1 | 80.1024 | 59.8258 | 1011.5788
2029-05-15 22:00 | 3210.76 | 1 | 63.3905 | 59.8258 | 940.9809
2029-05-16 23:00 | 0 | 0 | 63.4641 | 59.8258 | 0
2029-05-18 | -163.452 | 0.88899 | 62.0525 | 59.8258 | -47.9031
2029-05-19 01:00 | -656.285 | 2.3165 | 61.2206 | 59.8258 | -192.3381
2029-05-20 02:00 | -1412 | 4.3266 | 60.7542 | 59.8258 | -413.8164
2029-05-21 03:00 | -1676.3 | 4.9117 | 60.3582 | 59.8258 | -491.275
2029-05-22 04:00 | -2003.59 | 5.8119 | 60.0408 | 59.8258 | -587.1943
2029-05-23 05:00 | -2045.48 | 5.8642 | 59.7837 | 59.8258 | -599.471
2029-05-24 06:00 | -2283.63 | 6.108 | 59.474 | 59.8258 | -669.2659
2029-05-25 07:00 | -2182.71 | 6.108 | 59.346 | 59.8258 | -639.6892
2029-05-26 08:00 | -2871.6 | 6.108 | 58.6978 | 59.8258 | -841.5829
2029-05-27 09:00 | -2453.45 | 6.108 | 58.7961 | 59.8258 | -719.0352
2029-05-28 10:00 | -2122.63 | 6.108 | 58.9163 | 59.8258 | -622.0814
2029-05-29 11:00 | -2287.8 | 6.108 | 58.7305 | 59.8258 | -670.488
2029-05-30 12:00 | -1901.85 | 5.5058 | 58.7412 | 59.8258 | -557.3772
2029-05-31 13:00 | -1741.42 | 5.0929 | 58.6797 | 59.8258 | -510.3598
2029-06-01 14:00 | -1187.98 | 3.5291 | 58.6475 | 59.8258 | -348.1626
2029-06-02 15:00 | -205.041 | 0.85136 | 59.0604 | 59.8258 | -60.0916
2029-06-03 16:00 | 2788.95 | 1 | 59.9851 | 59.8258 | 817.3606
2029-06-04 17:00 | 3120.33 | 1 | 60.3603 | 59.8258 | 914.4785
2029-06-05 18:00 | 1255.43 | 1 | 60.7863 | 59.8258 | 367.9302
2029-06-06 19:00 | -621.676 | 2.3267 | 59.5693 | 59.8258 | -182.1953
2029-06-07 20:00 | -1706.48 | 5.2711 | 59.066 | 59.8258 | -500.1199
2029-06-08 21:00 | -2491.1 | 6.108 | 58.4448 | 59.8258 | -730.0693
2029-06-09 22:00 | -3719.56 | 6.108 | 57.248 | 59.8258 | -1090.0954
2029-06-10 23:00 | -4381.94 | 6.108 | 56.4034 | 59.8258 | -1284.2198
2029-06-12 | -4827.61 | 6.108 | 55.768 | 59.8258 | -1414.8328
2029-06-13 01:00 | -5072.28 | 6.108 | 55.3476 | 59.8258 | -1486.5385
2029-06-14 02:00 | -5341.23 | 6.108 | 54.9477 | 59.8258 | -1565.36
2029-06-15 03:00 | -5578.15 | 6.108 | 54.5721 | 59.8258 | -1634.7944
2029-06-16 04:00 | -5595.97 | 6.108 | 54.3482 | 59.8258 | -1640.0169
2029-06-17 05:00 | -5549.72 | 6.108 | 54.2019 | 59.8258 | -1626.4624
2029-06-18 06:00 | -4489.13 | 6.108 | 54.8614 | 59.8258 | -1315.6341
2029-06-19 07:00 | -3400.57 | 6.108 | 55.7039 | 59.8258 | -996.6087
2029-06-20 08:00 | -3247.15 | 6.108 | 55.9501 | 59.8258 | -951.6457
2029-06-21 09:00 | -2373.86 | 6.108 | 56.6644 | 59.8258 | -695.7097
2029-06-22 10:00 | -1625.22 | 4.813 | 57.0341 | 59.8258 | -476.305
2029-06-23 11:00 | -685.896 | 2.1434 | 57.2955 | 59.8258 | -201.0163
2029-06-24 12:00 | 2260.85 | 1 | 58.7778 | 59.8258 | 662.5897
2029-06-25 13:00 | 2939.67 | 1 | 59.2261 | 59.8258 | 861.5322
2029-06-26 14:00 | 2972.54 | 1 | 59.6182 | 59.8258 | 871.1655
2029-06-27 15:00 | 2920.41 | 1 | 59.8528 | 59.8258 | 855.8877
2029-06-28 16:00 | 3839.72 | 1.2956 | 73.862 | 59.8258 | 1125.3108
2029-06-29 17:00 | 2948.92 | 1.008 | 73.917 | 59.8258 | 864.2431
2029-06-30 18:00 | 2889.33 | 1 | 60.3132 | 59.8258 | 846.779
2029-07-01 19:00 | 0 | 0 | 60.6135 | 59.8258 | 0
2029-07-02 20:00 | -660.562 | 2.3918 | 59.0399 | 59.8258 | -193.5916
2029-07-03 21:00 | -1354.42 | 4.2728 | 58.6244 | 59.8258 | -396.9413
2029-07-04 22:00 | -1887.95 | 5.6666 | 58.3485 | 59.8258 | -553.3035
2029-07-05 23:00 | -3761.66 | 6.108 | 56.8662 | 59.8258 | -1102.4337
2029-07-07 | -4546.31 | 6.108 | 55.8575 | 59.8258 | -1332.3919
2029-07-08 01:00 | -5013.97 | 6.108 | 55.1657 | 59.8258 | -1469.4496
2029-07-09 02:00 | -5529.09 | 6.108 | 54.5024 | 59.8258 | -1620.4163
2029-07-10 03:00 | -5225.77 | 6.108 | 54.4536 | 59.8258 | -1531.522
2029-07-11 04:00 | -5523.73 | 6.108 | 54.0452 | 59.8258 | -1618.8455
2029-07-12 05:00 | -5480.77 | 6.108 | 53.9032 | 59.8258 | -1606.2551
2029-07-13 06:00 | -4068.42 | 6.108 | 54.813 | 59.8258 | -1192.3362
2029-07-14 07:00 | -2710.56 | 6.108 | 55.9188 | 59.8258 | -794.3867
2029-07-15 08:00 | -2122.89 | 6.108 | 56.5722 | 59.8258 | -622.1576
2029-07-16 09:00 | -1346.09 | 3.9857 | 56.7693 | 59.8258 | -394.5
2029-07-17 10:00 | 0.042022 | 1 | 58.504 | 59.8258 | 0.012315
2029-07-18 11:00 | 2860.53 | 1 | 58.5702 | 59.8258 | 838.3386
2029-07-19 12:00 | 3021.11 | 1 | 59.1193 | 59.8258 | 885.3999
2029-07-20 13:00 | 2995.11 | 1 | 59.4664 | 59.8258 | 877.7801
2029-07-21 14:00 | 3034.75 | 1 | 59.6845 | 59.8258 | 889.3974
2029-07-22 15:00 | 2916.45 | 1 | 59.8908 | 59.8258 | 854.7271
2029-07-23 16:00 | 3055.93 | 1 | 76.9501 | 59.8258 | 895.6047
2029-07-24 17:00 | 2996.69 | 1 | 80.3099 | 59.8258 | 878.2431
2029-07-25 18:00 | 2851.69 | 1 | 60.1951 | 59.8258 | 835.7478
2029-07-26 19:00 | -91.0011 | 0.82922 | 60.0187 | 59.8258 | -26.6698
2029-07-27 20:00 | -568.459 | 2.1362 | 58.9803 | 59.8258 | -166.5989
2029-07-28 21:00 | -1097.7 | 3.5559 | 58.5728 | 59.8258 | -321.7041
2029-07-29 22:00 | -1536.65 | 4.7098 | 58.3299 | 59.8258 | -450.3477
2029-07-30 23:00 | -2801.58 | 6.108 | 57.532 | 59.8258 | -821.062
2029-08-01 | -3505.59 | 6.108 | 56.6887 | 59.8258 | -1027.387
2029-08-02 01:00 | -3897.21 | 6.108 | 56.1405 | 59.8258 | -1142.1595
2029-08-03 02:00 | -4170.73 | 6.108 | 55.7269 | 59.8258 | -1222.3203
2029-08-04 03:00 | -4167.76 | 6.108 | 55.5419 | 59.8258 | -1221.4499
2029-08-05 04:00 | -4044.64 | 6.108 | 55.4871 | 59.8258 | -1185.367
2029-08-06 05:00 | -3829.86 | 6.108 | 55.5556 | 59.8258 | -1122.4212
2029-08-07 06:00 | -3284.11 | 6.108 | 55.8983 | 59.8258 | -962.4776
2029-08-08 07:00 | -2579.76 | 6.108 | 56.4453 | 59.8258 | -756.053
2029-08-09 08:00 | -2310.68 | 6.108 | 56.7313 | 59.8258 | -677.1935
2029-08-10 09:00 | -1303.74 | 3.8559 | 56.9738 | 59.8258 | -382.0885
2029-08-11 10:00 | -1279.57 | 3.9891 | 57.2029 | 59.8258 | -375.0049
2029-08-12 11:00 | -602.594 | 1.9805 | 57.3477 | 59.8258 | -176.6029
2029-08-13 12:00 | -755.581 | 2.6173 | 57.5325 | 59.8258 | -221.4389
2029-08-14 13:00 | -150.964 | 0.79368 | 58.0191 | 59.8258 | -44.2432
2029-08-15 14:00 | 0 | 1 | 58.9931 | 59.8258 | 0
2029-08-16 15:00 | 2863.59 | 1 | 58.8074 | 59.8258 | 839.2354
2029-08-17 16:00 | 3097.02 | 1 | 77.6232 | 59.8258 | 907.647
2029-08-18 17:00 | 3047.23 | 1 | 82.0378 | 59.8258 | 893.055
2029-08-19 18:00 | 2998.03 | 1 | 59.6353 | 59.8258 | 878.6359
2029-08-20 19:00 | -232.905 | 1.2258 | 59.1908 | 59.8258 | -68.2577
2029-08-21 20:00 | -1519.98 | 4.8633 | 58.3506 | 59.8258 | -445.4622
2029-08-22 21:00 | -2267.87 | 6.108 | 57.7405 | 59.8258 | -664.6471
2029-08-23 22:00 | -3651.14 | 6.108 | 56.4434 | 59.8258 | -1070.0435
2029-08-24 23:00 | -4186.63 | 6.108 | 55.69 | 59.8258 | -1226.9801
2029-08-26 | -4614.81 | 6.108 | 55.0584 | 59.8258 | -1352.4673
2029-08-27 01:00 | -4887.18 | 6.108 | 54.6346 | 59.8258 | -1432.2911
2029-08-28 02:00 | -5097.82 | 6.108 | 54.2948 | 59.8258 | -1494.0236
2029-08-29 03:00 | -5127.3 | 6.108 | 54.076 | 59.8258 | -1502.6633
2029-08-30 04:00 | -5148.29 | 6.108 | 53.9109 | 59.8258 | -1508.8149
2029-08-31 05:00 | -4755.53 | 6.108 | 54.0734 | 59.8258 | -1393.7083
2029-09-01 06:00 | -4104.78 | 6.108 | 54.4883 | 59.8258 | -1202.9923
2029-09-02 07:00 | -3281.17 | 6.108 | 55.1344 | 59.8258 | -961.616
2029-09-03 08:00 | -2718.8 | 6.108 | 55.6635 | 59.8258 | -796.8016
2029-09-04 09:00 | -1460.91 | 4.3821 | 56.2864 | 59.8258 | -428.1505
2029-09-05 10:00 | 0 | 0 | 58.0501 | 59.8258 | 0
2029-09-06 11:00 | 2844.73 | 1 | 58.1269 | 59.8258 | 833.7081
2029-09-07 12:00 | 3252.12 | 1 | 74.6244 | 59.8258 | 953.1023
2029-09-08 13:00 | 3848.37 | 1.2208 | 73.7692 | 59.8258 | 1127.8459
2029-09-09 14:00 | 5110.84 | 1.5795 | 74.4973 | 59.8258 | 1497.8393
2029-09-10 15:00 | 6980.16 | 2.2624 | 74.2279 | 59.8258 | 2045.683
2029-09-11 16:00 | 7789.8 | 2.4937 | 74.9524 | 59.8258 | 2282.965
2029-09-12 17:00 | 7874.35 | 2.5204 | 75.3967 | 59.8258 | 2307.7442
2029-09-13 18:00 | 6306.83 | 1.9721 | 76.0746 | 59.8258 | 1848.3494
2029-09-14 19:00 | 3982.35 | 1.2893 | 75.6801 | 59.8258 | 1167.1116
2029-09-15 20:00 | 3074.42 | 1 | 61.1266 | 59.8258 | 901.0236
2029-09-16 21:00 | 0 | 0 | 61.2607 | 59.8258 | 0
2029-09-17 22:00 | -1296.82 | 4.0685 | 59.3431 | 59.8258 | -380.0604
2029-09-18 23:00 | -1811.67 | 5.4293 | 58.8218 | 59.8258 | -530.9481
2029-09-20 | -2501.5 | 6.108 | 58.1669 | 59.8258 | -733.1173
2029-09-21 01:00 | -2619.21 | 6.108 | 57.7986 | 59.8258 | -767.6147
2029-09-22 02:00 | -3138.18 | 6.108 | 57.1797 | 59.8258 | -919.7098
2029-09-23 03:00 | -3392.69 | 6.108 | 56.7671 | 59.8258 | -994.2993
2029-09-24 04:00 | -3491.92 | 6.108 | 56.4897 | 59.8258 | -1023.3807
2029-09-25 05:00 | -3179.66 | 6.108 | 56.5468 | 59.8258 | -931.8664
2029-09-26 06:00 | -2492.79 | 6.108 | 56.9668 | 59.8258 | -730.5646
2029-09-27 07:00 | -1344.62 | 3.9679 | 57.2863 | 59.8258 | -394.0692
2029-09-28 08:00 | -679.505 | 2.2019 | 57.5531 | 59.8258 | -199.1433
2029-09-29 09:00 | 2189.11 | 1 | 58.9365 | 59.8258 | 641.5648
2029-09-30 10:00 | 3022.62 | 1 | 73.9916 | 59.8258 | 885.8425
2029-10-01 11:00 | 4804.3 | 1.5337 | 74.3113 | 59.8258 | 1408.0013
2029-10-02 12:00 | 6280.16 | 2.0301 | 74.5938 | 59.8258 | 1840.5332
2029-10-03 13:00 | 6674.18 | 2.157 | 75.1036 | 59.8258 | 1956.0091
2029-10-04 14:00 | 7376.53 | 2.3767 | 75.542 | 59.8258 | 2161.8475
2029-10-05 15:00 | 9289.36 | 2.9934 | 75.8697 | 59.8258 | 2722.4427
2029-10-06 16:00 | 9863.69 | 3.1981 | 76.3015 | 59.8258 | 2890.7622
2029-10-07 17:00 | 9668.39 | 3.1123 | 76.8293 | 59.8258 | 2833.5254
2029-10-08 18:00 | 7918.33 | 2.5132 | 77.3089 | 59.8258 | 2320.6334
2029-10-09 19:00 | 5801.56 | 1.804 | 77.645 | 59.8258 | 1700.2694
2029-10-10 20:00 | 3258.23 | 1 | 79.466 | 59.8258 | 954.893
2029-10-11 21:00 | 3139.18 | 1 | 62.1204 | 59.8258 | 920.0028
2029-10-12 22:00 | -458.456 | 1.8105 | 61.0527 | 59.8258 | -134.3602
2029-10-13 23:00 | -1103.86 | 3.5304 | 60.1813 | 59.8258 | -323.5094
2029-10-15 | -1409.96 | 4.2696 | 59.6516 | 59.8258 | -413.2185
2029-10-16 01:00 | -1894.39 | 5.6121 | 59.3354 | 59.8258 | -555.1909
2029-10-17 02:00 | -2049.23 | 5.9518 | 59.0481 | 59.8258 | -600.57
2029-10-18 03:00 | -2124.08 | 6.108 | 58.7744 | 59.8258 | -622.5064
2029-10-19 04:00 | -2389.7 | 6.108 | 58.4094 | 59.8258 | -700.3519
2029-10-20 05:00 | -2085.91 | 6.0743 | 58.4477 | 59.8258 | -611.3199
2029-10-21 06:00 | -1206.31 | 3.499 | 58.3352 | 59.8258 | -353.5346
2029-10-22 07:00 | -224.762 | 0.91265 | 58.8175 | 59.8258 | -65.8712
2029-10-23 08:00 | 2064 | 1 | 59.8999 | 59.8258 | 604.8987
2029-10-24 09:00 | 2997.24 | 1 | 81.2937 | 59.8258 | 878.4043
2029-10-25 10:00 | 4270.47 | 1.3794 | 74.8942 | 59.8258 | 1251.5512
2029-10-26 11:00 | 5867.46 | 1.8892 | 75.3048 | 59.8258 | 1719.5828
2029-10-27 12:00 | 6963.11 | 2.2749 | 75.5365 | 59.8258 | 2040.6861
2029-10-28 13:00 | 8158.32 | 2.6134 | 76.2467 | 59.8258 | 2390.9676
2029-10-29 14:00 | 8747.66 | 2.7955 | 76.7014 | 59.8258 | 2563.6861
2029-10-30 15:00 | 10046 | 3.2827 | 76.7406 | 59.8258 | 2944.192
2029-10-31 16:00 | 9996.7 | 3.2657 | 77.1759 | 59.8258 | 2929.7436
2029-11-01 17:00 | 10123.6 | 3.2464 | 77.7288 | 59.8258 | 2966.9343
2029-11-02 18:00 | 8717.23 | 2.6739 | 78.6312 | 59.8258 | 2554.7679
2029-11-03 19:00 | 6634.14 | 2.0452 | 78.6031 | 59.8258 | 1944.2745
2029-11-04 20:00 | 4117.96 | 1.2724 | 78.3908 | 59.8258 | 1206.8549
2029-11-05 21:00 | 3216.91 | 1 | 81.6452 | 59.8258 | 942.7833
2029-11-06 22:00 | 1245.8 | 1 | 62.8067 | 59.8258 | 365.1079
2029-11-07 23:00 | -198.308 | 1.1223 | 61.6737 | 59.8258 | -58.1183
2029-11-09 | -715.242 | 2.4766 | 60.6942 | 59.8258 | -209.6167
2029-11-10 01:00 | -1074.7 | 3.3872 | 60.215 | 59.8258 | -314.9635
2029-11-11 02:00 | -1239.98 | 3.785 | 59.9021 | 59.8258 | -363.4023
2029-11-12 03:00 | -1253.25 | 3.7972 | 59.6474 | 59.8258 | -367.2913
2029-11-13 04:00 | -1560.24 | 4.6857 | 59.4589 | 59.8258 | -457.2612
2029-11-14 05:00 | -1059.14 | 3.1717 | 59.2682 | 59.8258 | -310.4033
2029-11-15 06:00 | -450.359 | 1.5782 | 59.4108 | 59.8258 | -131.9872
2029-11-16 07:00 | 2088.3 | 1 | 60.5433 | 59.8258 | 612.0203
2029-11-17 08:00 | 3026.64 | 1 | 82.3143 | 59.8258 | 887.0206
2029-11-18 09:00 | 4565.49 | 1.4404 | 75.7908 | 59.8258 | 1338.013
2029-11-19 10:00 | 6279.53 | 2.1591 | 74.9685 | 59.8258 | 1840.3486
2029-11-20 11:00 | 7746.54 | 2.6132 | 75.687 | 59.8258 | 2270.2868
2029-11-21 12:00 | 8937.92 | 2.8419 | 77.0055 | 59.8258 | 2619.4458
2029-11-22 13:00 | 9150.73 | 2.9131 | 77.4404 | 59.8258 | 2681.8142
2029-11-23 14:00 | 9736.46 | 3.1207 | 77.6821 | 59.8258 | 2853.4748
2029-11-24 15:00 | 11270.4 | 3.6446 | 77.8639 | 59.8258 | 3303.0282
2029-11-25 16:00 | 11813.1 | 3.7694 | 78.4981 | 59.8258 | 3462.0779
2029-11-26 17:00 | 11706 | 3.6596 | 79.1687 | 59.8258 | 3430.6899
2029-11-27 18:00 | 9395.44 | 2.8917 | 79.6659 | 59.8258 | 2753.5317
2029-11-28 19:00 | 7572.67 | 2.3255 | 79.6265 | 59.8258 | 2219.3305
2029-11-29 20:00 | 5003.02 | 1.4867 | 79.9441 | 59.8258 | 1466.2404
2029-11-30 21:00 | 3550.83 | 1.0985 | 78.9371 | 59.8258 | 1040.6455
2029-12-01 22:00 | 3075.98 | 1 | 63.4881 | 59.8258 | 901.4807
2029-12-02 23:00 | 0 | 0 | 63.472 | 59.8258 | 0
2029-12-04 | -463.97 | 1.4957 | 61.4514 | 59.8258 | -135.9762
2029-12-05 01:00 | -721.806 | 2.4529 | 61.0989 | 59.8258 | -211.5405
2029-12-06 02:00 | -930.332 | 2.9626 | 60.7333 | 59.8258 | -272.6534
2029-12-07 03:00 | -1200.81 | 3.689 | 60.4243 | 59.8258 | -351.9227
2029-12-08 04:00 | -1342.2 | 4.0358 | 60.1261 | 59.8258 | -393.36
2029-12-09 05:00 | -1409 | 4.2037 | 59.9177 | 59.8258 | -412.9371
2029-12-10 06:00 | -280.074 | 0.98972 | 59.9937 | 59.8258 | -82.0816
2029-12-11 07:00 | 2209 | 1 | 79.1251 | 59.8258 | 647.394
2029-12-12 08:00 | 2877.81 | 1 | 84.3033 | 59.8258 | 843.4029
2029-12-13 09:00 | 3939.08 | 1.2552 | 76.1744 | 59.8258 | 1154.4304
2029-12-14 10:00 | 5812.42 | 1.9373 | 75.8002 | 59.8258 | 1703.4521
2029-12-15 11:00 | 7396.96 | 2.5179 | 75.9466 | 59.8258 | 2167.835
2029-12-16 12:00 | 8794.11 | 2.8155 | 77.2701 | 59.8258 | 2577.2992
2029-12-17 13:00 | 9116.3 | 3.0848 | 76.9551 | 59.8258 | 2671.7238
2029-12-18 14:00 | 9990.75 | 3.1915 | 78.1018 | 59.8258 | 2927.9998
2029-12-19 15:00 | 9333.37 | 2.8636 | 79.0561 | 59.8258 | 2735.3407
2029-12-20 16:00 | 10550 | 3.3759 | 78.601 | 59.8258 | 3091.8998
2029-12-21 17:00 | 9003.61 | 2.9658 | 78.5053 | 59.8258 | 2638.6976
2029-12-22 18:00 | 7843.29 | 2.42 | 79.4724 | 59.8258 | 2298.6414
2029-12-23 19:00 | 5944.75 | 1.8139 | 79.5406 | 59.8258 | 1742.2342
2029-12-24 20:00 | 4896.37 | 1.489 | 79.3484 | 59.8258 | 1434.9844
2029-12-25 21:00 | 3719.82 | 1.1449 | 78.9504 | 59.8258 | 1090.1716
2029-12-26 22:00 | 3166.16 | 1 | 81.4433 | 59.8258 | 927.9099
2029-12-27 23:00 | 0 | 0 | 63.5837 | 59.8258 | 0
2029-12-29 | -655.949 | 2.2546 | 61.6759 | 59.8258 | -192.2397
2029-12-30 01:00 | -983.025 | 3.1124 | 61.1399 | 59.8258 | -288.0962
2029-12-31 02:00 | -1377.48 | 4.1564 | 60.7654 | 59.8258 | -403.6995
2030-01-01 03:00 | -1526.97 | 4.4983 | 60.448 | 59.8258 | -447.5107
2030-01-02 04:00 | -1626.37 | 4.7644 | 60.1723 | 59.8258 | -476.642
2030-01-03 05:00 | -1697.53 | 4.9528 | 59.9956 | 59.8258 | -497.4969
2030-01-04 06:00 | -494.916 | 1.5236 | 59.9208 | 59.8258 | -145.0456
2030-01-05 07:00 | 1934.14 | 1 | 61.2658 | 59.8258 | 566.8405
2030-01-06 08:00 | 2853.86 | 1 | 82.6745 | 59.8258 | 836.3838
2030-01-07 09:00 | 3884.79 | 1.2709 | 75.9457 | 59.8258 | 1138.5196
2030-01-08 10:00 | 5961.12 | 1.9864 | 75.9432 | 59.8258 | 1747.0318
2030-01-09 11:00 | 7726.99 | 2.5748 | 76.3963 | 59.8258 | 2264.5572
2030-01-10 12:00 | 7065.51 | 2.2756 | 77.3861 | 59.8258 | 2070.6966
2030-01-11 13:00 | 6502.96 | 2.0539 | 77.8626 | 59.8258 | 1905.8294
2030-01-12 14:00 | 5908.91 | 1.6962 | 79.386 | 59.8258 | 1731.7306
2030-01-13 15:00 | 5850.75 | 1.7876 | 78.4376 | 59.8258 | 1714.6856
2030-01-14 16:00 | 9019.35 | 3.0897 | 76.8147 | 59.8258 | 2643.3106
2030-01-15 17:00 | 7907.09 | 2.6341 | 77.6356 | 59.8258 | 2317.3393
2030-01-16 18:00 | 7111.12 | 2.293 | 78.2158 | 59.8258 | 2084.0635
2030-01-17 19:00 | 5888.57 | 1.7881 | 79.0732 | 59.8258 | 1725.7695
2030-01-18 20:00 | 4971.77 | 1.5316 | 78.774 | 59.8258 | 1457.082
2030-01-19 21:00 | 3873.82 | 1.1773 | 78.869 | 59.8258 | 1135.3046
2030-01-20 22:00 | 3177.51 | 1 | 78.5166 | 59.8258 | 931.2363
2030-01-21 23:00 | 0 | 0 | 63.3637 | 59.8258 | 0
2030-01-23 | -546.487 | 1.8918 | 61.4935 | 59.8258 | -160.1595
2030-01-24 01:00 | -789.843 | 2.6095 | 61.053 | 59.8258 | -231.4801
2030-01-25 02:00 | -974.375 | 3.071 | 60.7471 | 59.8258 | -285.5611
2030-01-26 03:00 | -1103.35 | 3.4003 | 60.5096 | 59.8258 | -323.36
2030-01-27 04:00 | -1268.86 | 3.8481 | 60.264 | 59.8258 | -371.8662
2030-01-28 05:00 | -1426.68 | 4.2623 | 60.0958 | 59.8258 | -418.1186
2030-01-29 06:00 | -244.391 | 0.88182 | 60.21 | 59.8258 | -71.6239
2030-01-30 07:00 | 1961.89 | 1 | 74.0919 | 59.8258 | 574.9732
2030-01-31 08:00 | 2708.32 | 1 | 81.6457 | 59.8258 | 793.7302
2030-02-01 09:00 | 3524.08 | 1.1664 | 75.7851 | 59.8258 | 1032.8059
2030-02-02 10:00 | 5017.56 | 1.6088 | 76.4328 | 59.8258 | 1470.5017
2030-02-03 11:00 | 6283.42 | 2.0897 | 76.2597 | 59.8258 | 1841.4886
2030-02-04 12:00 | 6960.8 | 2.3152 | 76.6398 | 59.8258 | 2040.0091
2030-02-05 13:00 | 6670.15 | 2.0961 | 77.7498 | 59.8258 | 1954.828
2030-02-06 14:00 | 6539.58 | 2.0703 | 77.8103 | 59.8258 | 1916.5617
2030-02-07 15:00 | 7399.66 | 2.3441 | 77.9241 | 59.8258 | 2168.6263
2030-02-08 16:00 | 10214.9 | 3.454 | 77.2071 | 59.8258 | 2993.6917
2030-02-09 17:00 | 9840.6 | 3.1119 | 78.6793 | 59.8258 | 2883.9952
2030-02-10 18:00 | 8648.69 | 2.7049 | 79.116 | 59.8258 | 2534.6808
2030-02-11 19:00 | 7152.59 | 2.1879 | 79.4853 | 59.8258 | 2096.2172
2030-02-12 20:00 | 5950.13 | 1.8198 | 79.4106 | 59.8258 | 1743.811
2030-02-13 21:00 | 4769.05 | 1.3914 | 80.0007 | 59.8258 | 1397.6706
2030-02-14 22:00 | 3475.91 | 1.0918 | 78.64 | 59.8258 | 1018.6887
2030-02-15 23:00 | 2951.08 | 1 | 63.5348 | 59.8258 | 864.8762
2030-02-17 | 0 | 0 | 63.579 | 59.8258 | 0
2030-02-18 01:00 | -358.299 | 1.3996 | 61.8899 | 59.8258 | -105.0071
2030-02-19 02:00 | -429.595 | 1.6444 | 61.5201 | 59.8258 | -125.9019
2030-02-20 03:00 | -537.239 | 1.9262 | 61.224 | 59.8258 | -157.4492
2030-02-21 04:00 | -622.268 | 2.1434 | 60.9572 | 59.8258 | -182.3687
2030-02-22 05:00 | -304.882 | 1.2426 | 60.961 | 59.8258 | -89.3521
2030-02-23 06:00 | 2206.76 | 1 | 61.8105 | 59.8258 | 646.7375
2030-02-24 07:00 | 3030.98 | 1 | 83.1492 | 59.8258 | 888.2926
2030-02-25 08:00 | 3044.32 | 1 | 77.1928 | 59.8258 | 892.2021
2030-02-26 09:00 | 5272.38 | 1.7018 | 76.7066 | 59.8258 | 1545.182
2030-02-27 10:00 | 7220.99 | 2.4722 | 76.252 | 59.8258 | 2116.2633
2030-02-28 11:00 | 9032.09 | 3.0493 | 76.9195 | 59.8258 | 2647.0443
2030-03-01 12:00 | 9287.19 | 3.0195 | 77.9559 | 59.8258 | 2721.8067
2030-03-02 13:00 | 8954.1 | 2.9183 | 78.2929 | 59.8258 | 2624.1877
2030-03-03 14:00 | 10045.8 | 3.1823 | 78.9429 | 59.8258 | 2944.1334
2030-03-04 15:00 | 11796.6 | 3.7675 | 79.1676 | 59.8258 | 3457.2422
2030-03-05 16:00 | 12459.1 | 3.9931 | 79.5848 | 59.8258 | 3651.4018
2030-03-06 17:00 | 12433 | 3.9778 | 79.9952 | 59.8258 | 3643.7526
2030-03-07 18:00 | 10966 | 3.4188 | 80.6384 | 59.8258 | 3213.8174
2030-03-08 19:00 | 9474.85 | 2.8894 | 81.0291 | 59.8258 | 2776.8044
2030-03-09 20:00 | 6899.31 | 2.0627 | 81.2677 | 59.8258 | 2021.9882
2030-03-10 21:00 | 5924.95 | 1.7317 | 81.2803 | 59.8258 | 1736.4314
2030-03-11 22:00 | 3250.64 | 1.007 | 80.1048 | 59.8258 | 952.6685
2030-03-12 23:00 | 3226.79 | 1 | 88.009 | 59.8258 | 945.6788
2030-03-14 | 3189.33 | 1 | 64.2425 | 59.8258 | 934.7004
2030-03-15 01:00 | 3116.97 | 1 | 64.0928 | 59.8258 | 913.4937
2030-03-16 02:00 | 0 | 0 | 64.2461 | 59.8258 | 0
2030-03-17 03:00 | 338.334 | 1 | 63.6731 | 59.8258 | 99.1559
2030-03-18 04:00 | -69.7687 | 0.74759 | 63.0126 | 59.8258 | -20.4472
2030-03-19 05:00 | 1868.65 | 1 | 63.0437 | 59.8258 | 547.6473
2030-03-20 06:00 | 2875.41 | 1 | 62.9969 | 59.8258 | 842.6995
2030-03-21 07:00 | 3180.53 | 1 | 79.8111 | 59.8258 | 932.1213
2030-03-22 08:00 | 3760.22 | 1.1801 | 77.9969 | 59.8258 | 1102.0117
2030-03-23 09:00 | 5575.97 | 1.8141 | 77.5928 | 59.8258 | 1634.1555
2030-03-24 10:00 | 7465.26 | 2.5279 | 77.3741 | 59.8258 | 2187.8517
2030-03-25 11:00 | 9315.68 | 3.1362 | 77.8568 | 59.8258 | 2730.1563
2030-03-26 12:00 | 10115.9 | 3.2967 | 78.7679 | 59.8258 | 2964.6776
2030-03-27 13:00 | 10479.8 | 3.3966 | 79.2446 | 59.8258 | 3071.3262
2030-03-28 14:00 | 11313.8 | 3.6007 | 79.8563 | 59.8258 | 3315.7475
2030-03-29 15:00 | 12563.8 | 4.1528 | 79.6802 | 59.8258 | 3682.0863
2030-03-30 16:00 | 13542.9 | 4.3016 | 80.6605 | 59.8258 | 3969.0322
2030-03-31 17:00 | 13434.5 | 4.2737 | 81.0328 | 59.8258 | 3937.2633
2030-04-01 18:00 | 11836.5 | 3.6922 | 81.5923 | 59.8258 | 3468.9357
2030-04-02 19:00 | 9807.75 | 3.0693 | 81.582 | 59.8258 | 2874.3678
2030-04-03 20:00 | 7399.32 | 2.2505 | 81.856 | 59.8258 | 2168.5266
2030-04-04 21:00 | 6333.94 | 1.8759 | 81.9115 | 59.8258 | 1856.2946
2030-04-05 22:00 | 4049.03 | 1.2051 | 81.5295 | 59.8258 | 1186.6536
2030-04-06 23:00 | 3346.3 | 1 | 84.327 | 59.8258 | 980.7037
2030-04-08 | 3243.36 | 1 | 89.5359 | 59.8258 | 950.535
2030-04-09 01:00 | 3181.08 | 1 | 64.7686 | 59.8258 | 932.2825
2030-04-10 02:00 | 3151.55 | 1 | 64.6272 | 59.8258 | 923.6281
2030-04-11 03:00 | 3217.75 | 1 | 64.4788 | 59.8258 | 943.0294
2030-04-12 04:00 | 3121.56 | 1 | 64.4017 | 59.8258 | 914.8389
2030-04-13 05:00 | 3203.54 | 1 | 64.2977 | 59.8258 | 938.8649
2030-04-14 06:00 | 3322.66 | 1 | 83.9583 | 59.8258 | 973.7755
2030-04-15 07:00 | 4319.92 | 1.3131 | 79.474 | 59.8258 | 1266.0436
2030-04-16 08:00 | 4988.42 | 1.5376 | 79.3745 | 59.8258 | 1461.9616
2030-04-17 09:00 | 6719.98 | 2.2924 | 78.0602 | 59.8258 | 1969.4317
2030-04-18 10:00 | 8759.88 | 3.0121 | 78.2431 | 59.8258 | 2567.2674
2030-04-19 11:00 | 10507.7 | 3.4256 | 79.4008 | 59.8258 | 3079.5029
2030-04-20 12:00 | 11317.2 | 3.7453 | 79.6801 | 59.8258 | 3316.7439
2030-04-21 13:00 | 12025 | 3.8292 | 80.6315 | 59.8258 | 3524.1796
2030-04-22 14:00 | 12501.2 | 4.0691 | 80.6969 | 59.8258 | 3663.7401
2030-04-23 15:00 | 13894.3 | 4.3958 | 81.4187 | 59.8258 | 4072.0174
2030-04-24 16:00 | 14462.3 | 4.5549 | 81.8842 | 59.8258 | 4238.4817
2030-04-25 17:00 | 14236.7 | 4.4903 | 82.2121 | 59.8258 | 4172.3649
2030-04-26 18:00 | 12718.6 | 3.9726 | 82.5947 | 59.8258 | 3727.4537
2030-04-27 19:00 | 10734.3 | 3.2807 | 82.937 | 59.8258 | 3145.9128
2030-04-28 20:00 | 7808.71 | 2.3617 | 82.9492 | 59.8258 | 2288.507
2030-04-29 21:00 | 6359.12 | 1.9088 | 82.6361 | 59.8258 | 1863.6741
2030-04-30 22:00 | 3944.67 | 1.1791 | 82.3025 | 59.8258 | 1156.0687
2030-05-01 23:00 | 3180.92 | 1 | 83.6485 | 59.8258 | 932.2356
2030-05-03 | 3151.63 | 1 | 86.2696 | 59.8258 | 923.6516
2030-05-04 01:00 | 3114.54 | 1 | 65.4382 | 59.8258 | 912.7816
2030-05-05 02:00 | 3101.69 | 1 | 65.2511 | 59.8258 | 909.0156
2030-05-06 03:00 | 3123.67 | 1 | 65.0697 | 59.8258 | 915.4573
2030-05-07 04:00 | 3194.45 | 1 | 64.9397 | 59.8258 | 936.2009
2030-05-08 05:00 | 3238.53 | 1 | 64.8346 | 59.8258 | 949.1195
2030-05-09 06:00 | 3244.94 | 1 | 64.7462 | 59.8258 | 950.998
2030-05-10 07:00 | 3205.94 | 1 | 64.6705 | 59.8258 | 939.5683
2030-05-11 08:00 | 3087.88 | 1 | 64.6197 | 59.8258 | 904.9683
2030-05-12 09:00 | 3293.64 | 1 | 64.5238 | 59.8258 | 965.2706
2030-05-13 10:00 | 3242.17 | 1 | 64.4926 | 59.8258 | 950.1862
2030-05-14 11:00 | 3267.96 | 1 | 88.5699 | 59.8258 | 957.7445
2030-05-15 12:00 | 3342.75 | 1.034 | 79.3974 | 59.8258 | 979.6633
2030-05-16 13:00 | 4086.97 | 1.2748 | 79.2252 | 59.8258 | 1197.7727
2030-05-17 14:00 | 4960.89 | 1.5925 | 78.8339 | 59.8258 | 1453.8933
2030-05-18 15:00 | 6316.19 | 2.0675 | 78.6365 | 59.8258 | 1851.0926
2030-05-19 16:00 | 6421.37 | 2.0701 | 79.0345 | 59.8258 | 1881.9178
2030-05-20 17:00 | 6536.07 | 2.1336 | 78.9482 | 59.8258 | 1915.533
2030-05-21 18:00 | 4885.92 | 1.5363 | 79.5604 | 59.8258 | 1431.9218
2030-05-22 19:00 | 3587.67 | 1.1421 | 79.2261 | 59.8258 | 1051.4423
2030-05-23 20:00 | 3146.16 | 1 | 64.3513 | 59.8258 | 922.0485
2030-05-24 21:00 | 0 | 0 | 64.4514 | 59.8258 | 0
2030-05-25 22:00 | -780.978 | 2.6522 | 62.5777 | 59.8258 | -228.8821
2030-05-26 23:00 | -1346.56 | 4.0511 | 61.9725 | 59.8258 | -394.6378
2030-05-28 | -1534.72 | 4.4643 | 61.6052 | 59.8258 | -449.782
2030-05-29 01:00 | -1646.65 | 4.7543 | 61.3338 | 59.8258 | -482.5855
2030-05-30 02:00 | -1674.2 | 4.8194 | 61.0846 | 59.8258 | -490.6596
2030-05-31 03:00 | -1847.3 | 5.3133 | 60.9047 | 59.8258 | -541.3902
2030-06-01 04:00 | -1793.91 | 5.1276 | 60.7138 | 59.8258 | -525.7431
2030-06-02 05:00 | -1847.92 | 5.3084 | 60.5695 | 59.8258 | -541.5719
2030-06-03 06:00 | -816.064 | 2.3812 | 60.4509 | 59.8258 | -239.1647
2030-06-04 07:00 | -143.853 | 0.77234 | 61.1813 | 59.8258 | -42.1592
2030-06-05 08:00 | -343.666 | 1.4696 | 61.0166 | 59.8258 | -100.7186
2030-06-06 09:00 | -127.929 | 0.81158 | 61.3464 | 59.8258 | -37.4923
2030-06-07 10:00 | 2171.11 | 1 | 61.8731 | 59.8258 | 636.2895
2030-06-08 11:00 | 3090.48 | 1.0641 | 75.6822 | 59.8258 | 905.7303
2030-06-09 12:00 | 4135.7 | 1.2893 | 77.2917 | 59.8258 | 1212.054
2030-06-10 13:00 | 5522.5 | 1.8192 | 76.7516 | 59.8258 | 1618.485
2030-06-11 14:00 | 7146.38 | 2.408 | 76.7861 | 59.8258 | 2094.3972
2030-06-12 15:00 | 8252.22 | 2.7195 | 77.5258 | 59.8258 | 2418.4869
2030-06-13 16:00 | 10709.1 | 3.54 | 77.8644 | 59.8258 | 3138.5274
2030-06-14 17:00 | 9792.51 | 3.0161 | 79.4723 | 59.8258 | 2869.9014
2030-06-15 18:00 | 8113.53 | 2.5002 | 79.7414 | 59.8258 | 2377.8409
2030-06-16 19:00 | 6861.58 | 2.0966 | 79.86 | 59.8258 | 2010.9306
2030-06-17 20:00 | 5947.97 | 1.7466 | 80.3969 | 59.8258 | 1743.1779
2030-06-18 21:00 | 4856.12 | 1.4185 | 80.4101 | 59.8258 | 1423.1883
2030-06-19 22:00 | 3813.16 | 1.1927 | 79.1874 | 59.8258 | 1117.5269
2030-06-20 23:00 | 2749.16 | 1 | 64.1126 | 59.8258 | 805.6993
2030-06-22 | -69.3656 | 0.75537 | 63.6989 | 59.8258 | -20.3291
2030-06-23 01:00 | -338.27 | 1.4326 | 62.518 | 59.8258 | -99.1372
2030-06-24 02:00 | -525.169 | 1.8945 | 61.9772 | 59.8258 | -153.9118
2030-06-25 03:00 | -644.896 | 2.1912 | 61.646 | 59.8258 | -189.0004
2030-06-26 04:00 | -687.9 | 2.291 | 61.3653 | 59.8258 | -201.6036
2030-06-27 05:00 | -858.101 | 2.7623 | 61.1046 | 59.8258 | -251.4846
2030-06-28 06:00 | 0 | 0 | 62.3725 | 59.8258 | 0
2030-06-29 07:00 | 2016.92 | 1 | 62.1813 | 59.8258 | 591.1009
2030-06-30 08:00 | 0 | 0 | 62.5964 | 59.8258 | 0
2030-07-01 09:00 | 3469.02 | 1 | 62.1135 | 59.8258 | 1016.6694
2030-07-02 10:00 | 3510.05 | 1 | 62.4505 | 59.8258 | 1028.6941
2030-07-03 11:00 | 3312.55 | 1 | 84.3425 | 59.8258 | 970.8126
2030-07-04 12:00 | 3698.33 | 1.1213 | 78.1248 | 59.8258 | 1083.8735
2030-07-05 13:00 | 5061.34 | 1.5366 | 78.2027 | 59.8258 | 1483.3323
2030-07-06 14:00 | 4710.07 | 1.3991 | 78.8312 | 59.8258 | 1380.3853
2030-07-07 15:00 | 5534.65 | 1.7425 | 78.0241 | 59.8258 | 1622.0458
2030-07-08 16:00 | 8863.09 | 3.0749 | 76.8016 | 59.8258 | 2597.5153
2030-07-09 17:00 | 8498.55 | 2.8447 | 77.8536 | 59.8258 | 2490.6791
2030-07-10 18:00 | 7471.45 | 2.3688 | 78.9189 | 59.8258 | 2189.6658
2030-07-11 19:00 | 6244.99 | 1.9336 | 79.2963 | 59.8258 | 1830.2259
2030-07-12 20:00 | 5607.31 | 1.6051 | 80.4769 | 59.8258 | 1643.3403
2030-07-13 21:00 | 4895.22 | 1.4241 | 80.1723 | 59.8258 | 1434.6474
2030-07-14 22:00 | 4053.17 | 1.2569 | 79.0743 | 59.8258 | 1187.8669
2030-07-15 23:00 | 3139.71 | 1 | 63.8982 | 59.8258 | 920.1582
2030-07-17 | 2954.53 | 1 | 63.7431 | 59.8258 | 865.8873
2030-07-18 01:00 | 36.1268 | 1 | 63.8954 | 59.8258 | 10.5877
2030-07-19 02:00 | 489.717 | 1 | 63.4093 | 59.8258 | 143.5219
2030-07-20 03:00 | 3329.97 | 1 | 62.9521 | 59.8258 | 975.9179
2030-07-21 04:00 | 1172.11 | 1 | 63.3871 | 59.8258 | 343.5115
2030-07-22 05:00 | 1910.99 | 1 | 63.1166 | 59.8258 | 560.0559
2030-07-23 06:00 | 2770.44 | 1 | 82.1801 | 59.8258 | 811.9358
2030-07-24 07:00 | 3628.1 | 1.1905 | 77.2685 | 59.8258 | 1063.2911
2030-07-25 08:00 | 4214.45 | 1.3362 | 77.9563 | 59.8258 | 1235.1334
2030-07-26 09:00 | 5684.16 | 1.8832 | 77.44 | 59.8258 | 1665.8629
2030-07-27 10:00 | 7380.08 | 2.495 | 77.4555 | 59.8258 | 2162.8879
2030-07-28 11:00 | 8960.44 | 2.9631 | 78.1649 | 59.8258 | 2626.0457
2030-07-29 12:00 | 9791.9 | 3.0895 | 79.2834 | 59.8258 | 2869.7226
2030-07-30 13:00 | 9814.35 | 3.1991 | 79.2431 | 59.8258 | 2876.3021
2030-07-31 14:00 | 10722.6 | 3.4451 | 79.7486 | 59.8258 | 3142.4839
2030-08-01 15:00 | 12555.9 | 4.118 | 79.7742 | 59.8258 | 3679.771
2030-08-02 16:00 | 13275.1 | 4.3192 | 80.3619 | 59.8258 | 3890.5478
2030-08-03 17:00 | 13490 | 4.2791 | 81.1251 | 59.8258 | 3953.5287
2030-08-04 18:00 | 11999.7 | 3.7445 | 81.6834 | 59.8258 | 3516.7649
2030-08-05 19:00 | 10086.3 | 3.139 | 81.8096 | 59.8258 | 2956.0027
2030-08-06 20:00 | 7397.7 | 2.2406 | 82.1048 | 59.8258 | 2168.0519
2030-08-07 21:00 | 6353.42 | 1.8416 | 82.4091 | 59.8258 | 1862.0036
2030-08-08 22:00 | 3804.76 | 1.0982 | 82.1613 | 59.8258 | 1115.0651
2030-08-09 23:00 | 3232.53 | 1 | 85.1402 | 59.8258 | 947.361
2030-08-11 | 3235.42 | 1 | 90.1491 | 59.8258 | 948.208
2030-08-12 01:00 | 3155.05 | 1 | 64.908 | 59.8258 | 924.6539
2030-08-13 02:00 | 3027.09 | 1 | 64.7734 | 59.8258 | 887.1525
2030-08-14 03:00 | 3131.99 | 1 | 64.5816 | 59.8258 | 917.8957
2030-08-15 04:00 | 3226.94 | 1 | 64.4776 | 59.8258 | 945.7228
2030-08-16 05:00 | 3233.53 | 1 | 90.0011 | 59.8258 | 947.6541
2030-08-17 06:00 | 3360.76 | 1 | 80.6757 | 59.8258 | 984.9415
2030-08-18 07:00 | 4712.46 | 1.4455 | 79.4417 | 59.8258 | 1381.0857
2030-08-19 08:00 | 5591.9 | 1.8317 | 78.6537 | 59.8258 | 1638.8241
2030-08-20 09:00 | 7269.76 | 2.3408 | 79.0787 | 59.8258 | 2130.5563
2030-08-21 10:00 | 9327.54 | 2.9759 | 79.5369 | 59.8258 | 2733.6321
2030-08-22 11:00 | 10619.1 | 3.5785 | 79.257 | 59.8258 | 3112.151
2030-08-23 12:00 | 12102.6 | 3.8802 | 80.4259 | 59.8258 | 3546.9219
2030-08-24 13:00 | 12685.7 | 4.0521 | 80.9799 | 59.8258 | 3717.8117
2030-08-25 14:00 | 12886.8 | 4.2827 | 80.8554 | 59.8258 | 3776.7483
2030-08-26 15:00 | 15040.9 | 4.8026 | 81.7282 | 59.8258 | 4408.0527
2030-08-27 16:00 | 15320.1 | 4.8827 | 82.2717 | 59.8258 | 4489.8781
2030-08-28 17:00 | 15203 | 4.8689 | 82.6025 | 59.8258 | 4455.5595
2030-08-29 18:00 | 13590.9 | 4.2845 | 83.1099 | 59.8258 | 3983.0996
2030-08-30 19:00 | 11890.3 | 3.6542 | 83.5302 | 59.8258 | 3484.7029
2030-08-31 20:00 | 9126.46 | 2.7648 | 83.6651 | 59.8258 | 2674.7014
2030-09-01 21:00 | 7478.36 | 2.2653 | 83.3015 | 59.8258 | 2191.691
2030-09-02 22:00 | 5465.5 | 1.5599 | 83.8432 | 59.8258 | 1601.7799
2030-09-03 23:00 | 4478.98 | 1.2814 | 83.3229 | 59.8258 | 1312.6595
2030-09-05 | 3708.23 | 1.1227 | 82.0232 | 59.8258 | 1086.7749
2030-09-06 01:00 | 3217.5 | 1 | 82.2318 | 59.8258 | 942.9562
2030-09-07 02:00 | 3101.7 | 1 | 83.7153 | 59.8258 | 909.0185
2030-09-08 03:00 | 3144.01 | 1 | 83.4878 | 59.8258 | 921.4184
2030-09-09 04:00 | 3164.29 | 1 | 83.836 | 59.8258 | 927.3619
2030-09-10 05:00 | 3817.12 | 1.1957 | 80.2912 | 59.8258 | 1118.6874
2030-09-11 06:00 | 5096.8 | 1.5965 | 80.2622 | 59.8258 | 1493.7246
2030-09-12 07:00 | 6392.67 | 2.0872 | 79.7887 | 59.8258 | 1873.5066
2030-09-13 08:00 | 7107.04 | 2.2179 | 80.6683 | 59.8258 | 2082.8678
2030-09-14 09:00 | 8523.74 | 2.9172 | 79.586 | 59.8258 | 2498.0616
2030-09-15 10:00 | 10722.9 | 3.6088 | 80.1299 | 59.8258 | 3142.5718
2030-09-16 11:00 | 12550.7 | 4.0699 | 81.1374 | 59.8258 | 3678.2471
2030-09-17 12:00 | 13283.2 | 4.3575 | 81.5165 | 59.8258 | 3892.9216
2030-09-18 13:00 | 13829.5 | 4.5361 | 81.9535 | 59.8258 | 4053.0264
2030-09-19 14:00 | 14868.8 | 4.8643 | 82.3704 | 59.8258 | 4357.6151
2030-09-20 15:00 | 15293.7 | 4.8325 | 83.2789 | 59.8258 | 4482.141
2030-09-21 16:00 | 15290.6 | 4.5715 | 84.439 | 59.8258 | 4481.2325
2030-09-22 17:00 | 13255.9 | 4.1423 | 84.0175 | 59.8258 | 3884.9208
2030-09-23 18:00 | 11036.6 | 3.3246 | 84.5002 | 59.8258 | 3234.5082
2030-09-24 19:00 | 9185.32 | 2.8736 | 83.6741 | 59.8258 | 2691.9516
2030-09-25 20:00 | 6752.45 | 2.0539 | 83.7715 | 59.8258 | 1978.9477
2030-09-26 21:00 | 5734.34 | 1.6935 | 83.7304 | 59.8258 | 1680.5692
2030-09-27 22:00 | 3277.56 | 1.0189 | 82.5344 | 59.8258 | 960.558
2030-09-28 23:00 | 3253.03 | 1 | 89.8904 | 59.8258 | 953.369
2030-09-30 | 3310.3 | 1 | 66.576 | 59.8258 | 970.1532
2030-10-01 01:00 | 3204.64 | 1 | 66.3571 | 59.8258 | 939.1873
2030-10-02 02:00 | 3187.08 | 1 | 66.1509 | 59.8258 | 934.0409
2030-10-03 03:00 | 3144.48 | 1 | 65.9666 | 59.8258 | 921.5561
2030-10-04 04:00 | 3213.21 | 1 | 65.827 | 59.8258 | 941.6989
2030-10-05 05:00 | 3288.52 | 1 | 89.7238 | 59.8258 | 963.7701
2030-10-06 06:00 | 3303.95 | 1 | 87.4951 | 59.8258 | 968.2922
2030-10-07 07:00 | 4483.89 | 1.4362 | 80.0946 | 59.8258 | 1314.0984
2030-10-08 08:00 | 5387.2 | 1.739 | 80.1011 | 59.8258 | 1578.8325
2030-10-09 09:00 | 6865.27 | 2.3991 | 79.1679 | 59.8258 | 2012.012
2030-10-10 10:00 | 8505.53 | 2.9274 | 79.6331 | 59.8258 | 2492.7248
2030-10-11 11:00 | 9789.82 | 3.12 | 81.0489 | 59.8258 | 2869.113
2030-10-12 12:00 | 9689.45 | 3.0864 | 81.436 | 59.8258 | 2839.6975
2030-10-13 13:00 | 10741.4 | 3.3961 | 81.7439 | 59.8258 | 3147.9936
2030-10-14 14:00 | 11707 | 3.7177 | 81.9593 | 59.8258 | 3430.983
2030-10-15 15:00 | 13492.2 | 4.3825 | 81.9443 | 59.8258 | 3954.1735
2030-10-16 16:00 | 13992.9 | 4.5679 | 82.2951 | 59.8258 | 4100.9142
2030-10-17 17:00 | 14329.2 | 4.5422 | 83.0504 | 59.8258 | 4199.474
2030-10-18 18:00 | 12720.2 | 4.0038 | 83.4771 | 59.8258 | 3727.9226
2030-10-19 19:00 | 10945.5 | 3.369 | 83.858 | 59.8258 | 3207.8094
2030-10-20 20:00 | 8268.27 | 2.489 | 84.0779 | 59.8258 | 2423.1907
2030-10-21 21:00 | 7055.28 | 2.162 | 83.4354 | 59.8258 | 2067.6985
2030-10-22 22:00 | 5403.65 | 1.4891 | 84.7743 | 59.8258 | 1583.6535
2030-10-23 23:00 | 4531.68 | 1.2865 | 83.8684 | 59.8258 | 1328.1043
2030-10-25 | 3705.51 | 1.1265 | 82.4449 | 59.8258 | 1085.9778
2030-10-26 01:00 | 3229.45 | 1 | 82.309 | 59.8258 | 946.4584
2030-10-27 02:00 | 3204.13 | 1 | 84.1468 | 59.8258 | 939.0378
2030-10-28 03:00 | 3118.97 | 1 | 83.5987 | 59.8258 | 914.0799
2030-10-29 04:00 | 3075.11 | 1 | 82.2567 | 59.8258 | 901.2258
2030-10-30 05:00 | 3840.67 | 1.2061 | 80.7906 | 59.8258 | 1125.5893
2030-10-31 06:00 | 4896.17 | 1.5425 | 80.7173 | 59.8258 | 1434.9258
2030-11-01 07:00 | 5897.89 | 1.9641 | 80.0254 | 59.8258 | 1728.5009
2030-11-02 08:00 | 6255.35 | 1.9781 | 80.9228 | 59.8258 | 1833.2621
2030-11-03 09:00 | 7517.5 | 2.5479 | 80.0703 | 59.8258 | 2203.1618
2030-11-04 10:00 | 8477.26 | 2.8321 | 80.5039 | 59.8258 | 2484.4397
2030-11-05 11:00 | 9947.31 | 3.1765 | 81.3917 | 59.8258 | 2915.2688
2030-11-06 12:00 | 11058.2 | 3.6146 | 81.402 | 59.8258 | 3240.8385
2030-11-07 13:00 | 10282 | 3.2975 | 82.0318 | 59.8258 | 3013.3567
2030-11-08 14:00 | 11871.1 | 3.6959 | 82.5715 | 59.8258 | 3479.076
2030-11-09 15:00 | 13440.5 | 4.2734 | 82.5564 | 59.8258 | 3939.0217
2030-11-10 16:00 | 14265.2 | 4.543 | 82.9529 | 59.8258 | 4180.7174
2030-11-11 17:00 | 14059.5 | 4.4688 | 83.3356 | 59.8258 | 4120.4327
2030-11-12 18:00 | 11353.5 | 3.452 | 84.2082 | 59.8258 | 3327.3824
2030-11-13 19:00 | 9230.39 | 2.9556 | 83.3068 | 59.8258 | 2705.1603
2030-11-14 20:00 | 6894.72 | 2.0296 | 84.2795 | 59.8258 | 2020.643
2030-11-15 21:00 | 5826.76 | 1.7356 | 83.6643 | 59.8258 | 1707.6548
2030-11-16 22:00 | 3332.45 | 1 | 83.5861 | 59.8258 | 976.6447
2030-11-17 23:00 | 3162.41 | 1 | 67.0883 | 59.8258 | 926.8109
2030-11-19 | 3231.79 | 1 | 66.7099 | 59.8258 | 947.1442
2030-11-20 01:00 | 3072.7 | 1 | 66.5113 | 59.8258 | 900.5195
2030-11-21 02:00 | 3169.38 | 1 | 66.3054 | 59.8258 | 928.8536
2030-11-22 03:00 | 2474.54 | 1 | 66.1976 | 59.8258 | 725.2161
2030-11-23 04:00 | 1263.49 | 1 | 66.0884 | 59.8258 | 370.2924
2030-11-24 05:00 | 883.662 | 1 | 65.7758 | 59.8258 | 258.9758
2030-11-25 06:00 | 2223.07 | 1.2354 | 73.8138 | 59.8258 | 651.5175
2030-11-26 07:00 | 4382.06 | 1.7042 | 77.3021 | 59.8258 | 1284.255
2030-11-27 08:00 | 4573.79 | 1.5953 | 78.8749 | 59.8258 | 1340.4455
2030-11-28 09:00 | 6014.33 | 2.0472 | 79.2901 | 59.8258 | 1762.6261
2030-11-29 10:00 | 7731.62 | 2.7252 | 79.0752 | 59.8258 | 2265.9141
2030-11-30 11:00 | 9787.68 | 3.2109 | 80.4287 | 59.8258 | 2868.4859
2030-12-01 12:00 | 10459.1 | 3.406 | 81.0171 | 59.8258 | 3065.2596
2030-12-02 13:00 | 10296.7 | 3.2903 | 81.6446 | 59.8258 | 3017.6649
2030-12-03 14:00 | 9586.24 | 3.018 | 82.0714 | 59.8258 | 2809.4496
2030-12-04 15:00 | 8226.88 | 2.6288 | 81.9183 | 59.8258 | 2411.0605
2030-12-05 16:00 | 11659.6 | 3.7806 | 81.5783 | 59.8258 | 3417.0914
2030-12-06 17:00 | 11479.1 | 3.57 | 82.5912 | 59.8258 | 3364.1921
2030-12-07 18:00 | 10280.8 | 3.2384 | 82.6418 | 59.8258 | 3013.0051
2030-12-08 19:00 | 8632.08 | 2.7412 | 82.4948 | 59.8258 | 2529.8129
2030-12-09 20:00 | 7748.52 | 2.3851 | 82.8058 | 59.8258 | 2270.867
2030-12-10 21:00 | 7173.74 | 2.09 | 83.5415 | 59.8258 | 2102.4157
2030-12-11 22:00 | 6361.66 | 1.9546 | 82.5798 | 59.8258 | 1864.4185
2030-12-12 23:00 | 3416.59 | 1 | 84.7195 | 59.8258 | 1001.3037
2030-12-14 | 3225.15 | 1 | 88.9913 | 59.8258 | 945.1982
2030-12-15 01:00 | 3221.74 | 1 | 66.3813 | 59.8258 | 944.1988
2030-12-16 02:00 | 3156.92 | 1 | 66.2206 | 59.8258 | 925.2019
2030-12-17 03:00 | 3192.8 | 1 | 66.0726 | 59.8258 | 935.7173
2030-12-18 04:00 | 3157.02 | 1 | 65.9261 | 59.8258 | 925.2312
2030-12-19 05:00 | 3320.34 | 1 | 65.8251 | 59.8258 | 973.0956
2030-12-20 06:00 | 3335.72 | 1 | 87.4621 | 59.8258 | 977.603
2030-12-21 07:00 | 5013.64 | 1.5554 | 80.6997 | 59.8258 | 1469.3528
2030-12-22 08:00 | 5094.95 | 1.5315 | 81.3517 | 59.8258 | 1493.1824
2030-12-23 09:00 | 6261.21 | 2.06 | 80.1056 | 59.8258 | 1834.9795
2030-12-24 10:00 | 8017.12 | 2.8415 | 79.2659 | 59.8258 | 2349.5859
2030-12-25 11:00 | 9760.57 | 3.2814 | 80.3025 | 59.8258 | 2860.5407
2030-12-26 12:00 | 10524.7 | 3.4343 | 81.1426 | 59.8258 | 3084.4851
2030-12-27 13:00 | 9066.49 | 2.7289 | 82.6684 | 59.8258 | 2657.1259
2030-12-28 14:00 | 9416.49 | 3.0202 | 81.7648 | 59.8258 | 2759.7008
2030-12-29 15:00 | 10568.4 | 3.2688 | 82.4019 | 59.8258 | 3097.2923
2030-12-30 16:00 | 12595 | 3.9941 | 82.2647 | 59.8258 | 3691.2301
2030-12-31 17:00 | 10223.3 | 3.2873 | 82.4786 | 59.8258 | 2996.1535
2031-01-01 18:00 | 8700.9 | 2.7721 | 82.5425 | 59.8258 | 2549.9821
2031-01-02 19:00 | 7614.08 | 2.2754 | 83.3109 | 59.8258 | 2231.4666
2031-01-03 20:00 | 6682.9 | 2.0082 | 83.0724 | 59.8258 | 1958.5647
2031-01-04 21:00 | 5766.66 | 1.7382 | 82.8293 | 59.8258 | 1690.0412
2031-01-05 22:00 | 5191.49 | 1.5628 | 82.5665 | 59.8258 | 1521.4755
2031-01-06 23:00 | 3240.05 | 1 | 88.0424 | 59.8258 | 949.5649
2031-01-08 | 3303.34 | 1 | 66.4763 | 59.8258 | 968.1134
2031-01-09 01:00 | 3131.85 | 1 | 66.2827 | 59.8258 | 917.8546
2031-01-10 02:00 | 3250.76 | 1 | 66.1115 | 59.8258 | 952.7037
2031-01-11 03:00 | 3276.25 | 1 | 65.9823 | 59.8258 | 960.1741
2031-01-12 04:00 | 3190.48 | 1 | 89.1016 | 59.8258 | 935.0374
2031-01-13 05:00 | 3460.22 | 1 | 81.9057 | 59.8258 | 1014.0904
2031-01-14 06:00 | 3702.18 | 1.1378 | 80.9006 | 59.8258 | 1085.0019
2031-01-15 07:00 | 4342.74 | 1.3386 | 80.8482 | 59.8258 | 1272.7315
2031-01-16 08:00 | 4110.22 | 1.302 | 80.5146 | 59.8258 | 1204.5866
2031-01-17 09:00 | 5389.63 | 1.7113 | 80.4573 | 59.8258 | 1579.5446
2031-01-18 10:00 | 6441.02 | 2.2091 | 79.5217 | 59.8258 | 1887.6766
2031-01-19 11:00 | 7703.55 | 2.5534 | 80.1959 | 59.8258 | 2257.6876
2031-01-20 12:00 | 8990.04 | 2.9545 | 80.5769 | 59.8258 | 2634.7206
2031-01-21 13:00 | 9329.1 | 2.9819 | 81.2984 | 59.8258 | 2734.0893
2031-01-22 14:00 | 8619.6 | 2.8425 | 81.1255 | 59.8258 | 2526.1554
2031-01-23 15:00 | 10943.8 | 3.7267 | 80.7462 | 59.8258 | 3207.3112
2031-01-24 16:00 | 10969.7 | 3.67 | 81.3536 | 59.8258 | 3214.9017
2031-01-25 17:00 | 10984.9 | 3.4978 | 82.2903 | 59.8258 | 3219.3564
2031-01-26 18:00 | 10207.8 | 3.1649 | 82.8297 | 59.8258 | 2991.6109
2031-01-27 19:00 | 8587.47 | 2.6211 | 83.1118 | 59.8258 | 2516.739
2031-01-28 20:00 | 6559.61 | 1.8795 | 83.9932 | 59.8258 | 1922.4319
2031-01-29 21:00 | 5454.2 | 1.614 | 83.1702 | 59.8258 | 1598.4682
2031-01-30 22:00 | 3339.48 | 1 | 84.3084 | 59.8258 | 978.705
2031-01-31 23:00 | 3086.41 | 1 | 86.3284 | 59.8258 | 904.5375
2031-02-02 | 3143.21 | 1 | 91.7035 | 59.8258 | 921.1839
2031-02-03 01:00 | 3194.8 | 1 | 66.1811 | 59.8258 | 936.3035
2031-02-04 02:00 | 3168.51 | 1 | 66.0671 | 59.8258 | 928.5986
2031-02-05 03:00 | 3226.84 | 1 | 65.9235 | 59.8258 | 945.6935
2031-02-06 04:00 | 3154.93 | 1 | 65.8495 | 59.8258 | 924.6187
2031-02-07 05:00 | 3318.19 | 1 | 85.187 | 59.8258 | 972.4655
2031-02-08 06:00 | 3624.06 | 1.0941 | 81.0956 | 59.8258 | 1062.1071
2031-02-09 07:00 | 4993.89 | 1.5481 | 80.6799 | 59.8258 | 1463.5647
2031-02-10 08:00 | 4422.19 | 1.3513 | 81.0626 | 59.8258 | 1296.016
2031-02-11 09:00 | 5238.47 | 1.5451 | 81.5925 | 59.8258 | 1535.244
2031-02-12 10:00 | 5398.76 | 1.7077 | 80.6482 | 59.8258 | 1582.2204
2031-02-13 11:00 | 6204.05 | 1.9473 | 80.8401 | 59.8258 | 1818.2276
2031-02-14 12:00 | 6703 | 2.2698 | 79.9084 | 59.8258 | 1964.4554
2031-02-15 13:00 | 7908.3 | 2.6701 | 80.0684 | 59.8258 | 2317.6939
2031-02-16 14:00 | 10094.9 | 3.2761 | 80.8498 | 59.8258 | 2958.5231
2031-02-17 15:00 | 12831.9 | 4.1277 | 81.3799 | 59.8258 | 3760.6587
2031-02-18 16:00 | 13643 | 4.5071 | 81.6184 | 59.8258 | 3998.3686
2031-02-19 17:00 | 13273 | 4.321 | 82.3088 | 59.8258 | 3889.9323
2031-02-20 18:00 | 11951.5 | 3.7795 | 83.0202 | 59.8258 | 3502.6389
2031-02-21 19:00 | 10421.6 | 3.2078 | 83.5023 | 59.8258 | 3054.2695
2031-02-22 20:00 | 8063.28 | 2.4096 | 83.893 | 59.8258 | 2363.1141
2031-02-23 21:00 | 6923.19 | 2.1041 | 83.327 | 59.8258 | 2028.9867
2031-02-24 22:00 | 5537.31 | 1.5027 | 84.8522 | 59.8258 | 1622.8254
2031-02-25 23:00 | 4569.28 | 1.3135 | 83.5913 | 59.8258 | 1339.1238
2031-02-27 | 3477.8 | 1.0639 | 82.3307 | 59.8258 | 1019.2426
2031-02-28 01:00 | 3054.98 | 1 | 82.7979 | 59.8258 | 895.3263
2031-03-01 02:00 | 3149.64 | 1 | 85.2615 | 59.8258 | 923.0684
2031-03-02 03:00 | 3154 | 1 | 83.8814 | 59.8258 | 924.3462
2031-03-03 04:00 | 3229.62 | 1 | 84.0271 | 59.8258 | 946.5082
2031-03-04 05:00 | 3764.26 | 1.1885 | 80.762 | 59.8258 | 1103.1957
2031-03-05 06:00 | 4515.01 | 1.383 | 81.1818 | 59.8258 | 1323.2188
2031-03-06 07:00 | 5069.46 | 1.6716 | 80.1713 | 59.8258 | 1485.7121
2031-03-07 08:00 | 4908.37 | 1.4956 | 81.4081 | 59.8258 | 1438.5012
2031-03-08 09:00 | 5816.86 | 1.9122 | 80.3216 | 59.8258 | 1704.7534
2031-03-09 10:00 | 6460.72 | 2.1354 | 80.3823 | 59.8258 | 1893.4501
2031-03-10 11:00 | 6932.11 | 2.2983 | 80.5019 | 59.8258 | 2031.6009
2031-03-11 12:00 | 8254.01 | 2.7032 | 80.8138 | 59.8258 | 2419.0115
2031-03-12 13:00 | 9180.16 | 3.1193 | 80.5677 | 59.8258 | 2690.4393
2031-03-13 14:00 | 9740.15 | 3.1241 | 81.6561 | 59.8258 | 2854.5562
2031-03-14 15:00 | 11909.1 | 3.8625 | 81.7141 | 59.8258 | 3490.2127
2031-03-15 16:00 | 12886.1 | 4.1579 | 82.2158 | 59.8258 | 3776.5431
2031-03-16 17:00 | 13262.3 | 4.2566 | 82.6994 | 59.8258 | 3886.7965
2031-03-17 18:00 | 11994.9 | 3.7781 | 83.2818 | 59.8258 | 3515.3582
2031-03-18 19:00 | 10333.2 | 3.2555 | 83.3546 | 59.8258 | 3028.362
2031-03-19 20:00 | 7751.22 | 2.3603 | 83.7819 | 59.8258 | 2271.6583
2031-03-20 21:00 | 6740.84 | 1.9225 | 84.4508 | 59.8258 | 1975.5452
2031-03-21 22:00 | 4379.49 | 1.2914 | 83.6386 | 59.8258 | 1283.5018
2031-03-22 23:00 | 3409.61 | 1.033 | 82.7547 | 59.8258 | 999.2581
2031-03-24 | 3190.44 | 1 | 85.1878 | 59.8258 | 935.0257
2031-03-25 01:00 | 3252.76 | 1 | 88.3778 | 59.8258 | 953.2899
2031-03-26 02:00 | 3099.48 | 1 | 66.5263 | 59.8258 | 908.3679
2031-03-27 03:00 | 3198.91 | 1 | 66.3327 | 59.8258 | 937.508
2031-03-28 04:00 | 3118.22 | 1 | 91.2723 | 59.8258 | 913.8601
2031-03-29 05:00 | 3330.79 | 1.0239 | 81.1956 | 59.8258 | 976.1582
2031-03-30 06:00 | 4678.42 | 1.3955 | 81.5786 | 59.8258 | 1371.1096
2031-03-31 07:00 | 6002.57 | 2.0209 | 79.9206 | 59.8258 | 1759.1796
2031-04-01 08:00 | 6960.64 | 2.2055 | 80.9967 | 59.8258 | 2039.9622
2031-04-02 09:00 | 9021.87 | 2.8994 | 81.0178 | 59.8258 | 2644.0491
2031-04-03 10:00 | 10810.7 | 3.5277 | 81.2317 | 59.8258 | 3168.3034
2031-04-04 11:00 | 11827.1 | 3.9596 | 81.401 | 59.8258 | 3466.1809
2031-04-05 12:00 | 12568.4 | 3.9871 | 82.6094 | 59.8258 | 3683.4344
2031-04-06 13:00 | 12606.1 | 4.1139 | 82.6049 | 59.8258 | 3694.4832
2031-04-07 14:00 | 13400.3 | 4.2706 | 83.2348 | 59.8258 | 3927.2403
2031-04-08 15:00 | 15214.1 | 4.7811 | 83.735 | 59.8258 | 4458.8126
2031-04-09 16:00 | 15097.7 | 4.8786 | 83.793 | 59.8258 | 4424.6991
2031-04-10 17:00 | 15172 | 4.799 | 84.3882 | 59.8258 | 4446.4743
2031-04-11 18:00 | 13627.5 | 4.1965 | 85.0143 | 59.8258 | 3993.826
2031-04-12 19:00 | 11620 | 3.5831 | 85.0206 | 59.8258 | 3405.4858
2031-04-13 20:00 | 9262.38 | 2.7731 | 85.3009 | 59.8258 | 2714.5356
2031-04-14 21:00 | 7344.62 | 2.3302 | 84.0665 | 59.8258 | 2152.4956
2031-04-15 22:00 | 5281.53 | 1.5502 | 84.804 | 59.8258 | 1547.8636
2031-04-16 23:00 | 4181.82 | 1.2212 | 84.3535 | 59.8258 | 1225.5705
2031-04-18 | 3341.34 | 1.0182 | 83.2361 | 59.8258 | 979.2501
2031-04-19 01:00 | 3263.97 | 1 | 86.8436 | 59.8258 | 956.5752
2031-04-20 02:00 | 3110.42 | 1 | 90.9158 | 59.8258 | 911.5741
2031-04-21 03:00 | 3147.73 | 1 | 90.2998 | 59.8258 | 922.5086
2031-04-22 04:00 | 3102.47 | 1 | 87.0461 | 59.8258 | 909.2442
2031-04-23 05:00 | 3221.24 | 1.0364 | 81.1517 | 59.8258 | 944.0523
2031-04-24 06:00 | 4594.42 | 1.4132 | 81.6886 | 59.8258 | 1346.4916
2031-04-25 07:00 | 5842.49 | 1.9256 | 80.7636 | 59.8258 | 1712.2648
2031-04-26 08:00 | 6238.96 | 2.0659 | 80.8858 | 59.8258 | 1828.4587
2031-04-27 09:00 | 7800.68 | 2.6084 | 80.8705 | 59.8258 | 2286.1536
2031-04-28 10:00 | 8756.63 | 3.0459 | 80.6204 | 59.8258 | 2566.3149
2031-04-29 11:00 | 9819.86 | 3.2699 | 81.5123 | 59.8258 | 2877.9169
2031-04-30 12:00 | 10318.5 | 3.3359 | 82.2353 | 59.8258 | 3024.0538
2031-05-01 13:00 | 11050 | 3.5038 | 82.766 | 59.8258 | 3238.4353
2031-05-02 14:00 | 11496.1 | 3.7007 | 82.8273 | 59.8258 | 3369.1743
2031-05-03 15:00 | 13130.1 | 4.3018 | 82.7967 | 59.8258 | 3848.0525
2031-05-04 16:00 | 13588.5 | 4.4272 | 83.2458 | 59.8258 | 3982.3962
2031-05-05 17:00 | 13421.7 | 4.2955 | 83.7991 | 59.8258 | 3933.512
2031-05-06 18:00 | 12128.1 | 3.7617 | 84.4431 | 59.8258 | 3554.3952
2031-05-07 19:00 | 10157.7 | 3.1676 | 84.3632 | 59.8258 | 2976.928
2031-05-08 20:00 | 7761.07 | 2.3482 | 84.6366 | 59.8258 | 2274.5451
2031-05-09 21:00 | 6568.57 | 1.9431 | 84.5895 | 59.8258 | 1925.0578
2031-05-10 22:00 | 4270.43 | 1.2671 | 84.2003 | 59.8258 | 1251.5395
2031-05-11 23:00 | 3240.44 | 1 | 88.8603 | 59.8258 | 949.6792
2031-05-13 | 3093.49 | 1 | 67.5635 | 59.8258 | 906.6124
2031-05-14 01:00 | 3117.95 | 1 | 67.2694 | 59.8258 | 913.7809
2031-05-15 02:00 | 1559.72 | 1 | 67.208 | 59.8258 | 457.1088
2031-05-16 03:00 | -34.9932 | 0.64986 | 66.6974 | 59.8258 | -10.2555
2031-05-17 04:00 | -234.097 | 1.1233 | 65.5029 | 59.8258 | -68.6071
2031-05-18 05:00 | -243.615 | 1.1148 | 65.1102 | 59.8258 | -71.3965
2031-05-19 06:00 | 2098.93 | 1 | 65.6482 | 59.8258 | 615.1357
2031-05-20 07:00 | 3429.63 | 1.2084 | 78.8925 | 59.8258 | 1005.1253
2031-05-21 08:00 | 4125.43 | 1.3074 | 80.4739 | 59.8258 | 1209.0442
2031-05-22 09:00 | 5156.7 | 1.7415 | 79.7148 | 59.8258 | 1511.2796
2031-05-23 10:00 | 6902.59 | 2.3084 | 80.0532 | 59.8258 | 2022.9494
2031-05-24 11:00 | 7456.49 | 2.5365 | 80.1867 | 59.8258 | 2185.2815
2031-05-25 12:00 | 7294.38 | 2.4118 | 80.8252 | 59.8258 | 2137.7718
2031-05-26 13:00 | 7656.52 | 2.4799 | 81.2103 | 59.8258 | 2243.9045
2031-05-27 14:00 | 8642.94 | 2.8054 | 81.3066 | 59.8258 | 2532.9957
2031-05-28 15:00 | 9935.95 | 3.1827 | 81.714 | 59.8258 | 2911.9395
2031-05-29 16:00 | 12259.2 | 3.9505 | 81.9103 | 59.8258 | 3592.8169
2031-05-30 17:00 | 11045.3 | 3.5105 | 82.6054 | 59.8258 | 3237.0579
2031-05-31 18:00 | 9739.36 | 3.0516 | 82.9608 | 59.8258 | 2854.3247
2031-06-01 19:00 | 7796.98 | 2.4573 | 82.8372 | 59.8258 | 2285.0693
2031-06-02 20:00 | 6288.56 | 1.9866 | 82.6097 | 59.8258 | 1842.995
2031-06-03 21:00 | 5415.59 | 1.6868 | 82.5416 | 59.8258 | 1587.1528
2031-06-04 22:00 | 4761.87 | 1.4805 | 82.2783 | 59.8258 | 1395.5663
2031-06-05 23:00 | 3073.59 | 1 | 67.0678 | 59.8258 | 900.7803
2031-06-07 | 3140.86 | 1 | 66.6917 | 59.8258 | 920.4952
2031-06-08 01:00 | 0 | 0 | 66.7663 | 59.8258 | 0
2031-06-09 02:00 | -384.875 | 1.5499 | 65.0777 | 59.8258 | -112.7957
2031-06-10 03:00 | -651.396 | 2.1675 | 64.426 | 59.8258 | -190.9053
2031-06-11 04:00 | -959.444 | 2.9508 | 63.9854 | 59.8258 | -281.1853
2031-06-12 05:00 | -1163.78 | 3.4462 | 63.6373 | 59.8258 | -341.0702
2031-06-13 06:00 | 0 | 1 | 64.8837 | 59.8258 | 0
2031-06-14 07:00 | 2392.81 | 1 | 81.4961 | 59.8258 | 701.2634
2031-06-15 08:00 | 2868.25 | 1 | 87.2088 | 59.8258 | 840.6011
2031-06-16 09:00 | 3292.01 | 1.0892 | 79.034 | 59.8258 | 964.7929
2031-06-17 10:00 | 4918.1 | 1.5779 | 79.5672 | 59.8258 | 1441.3528
2031-06-18 11:00 | 6187.24 | 2.05 | 79.398 | 59.8258 | 1813.301
2031-06-19 12:00 | 7154.35 | 2.3138 | 80.0571 | 59.8258 | 2096.733
2031-06-20 13:00 | 7627.77 | 2.5005 | 80.1689 | 59.8258 | 2235.4787
2031-06-21 14:00 | 8693.7 | 2.8457 | 80.4422 | 59.8258 | 2547.872
2031-06-22 15:00 | 9298.25 | 3.0047 | 80.9411 | 59.8258 | 2725.0481
2031-06-23 16:00 | 11747.7 | 3.8253 | 81.0964 | 59.8258 | 3442.911
2031-06-24 17:00 | 10871.4 | 3.4681 | 81.9103 | 59.8258 | 3186.0928
2031-06-25 18:00 | 9313.48 | 2.9618 | 82.1813 | 59.8258 | 2729.5115
2031-06-26 19:00 | 7629.74 | 2.3556 | 82.5754 | 59.8258 | 2236.0561
2031-06-27 20:00 | 6177.37 | 1.9157 | 82.3495 | 59.8258 | 1810.4084
2031-06-28 21:00 | 4582.74 | 1.3408 | 83.0174 | 59.8258 | 1343.0685
2031-06-29 22:00 | 3348.61 | 1.0265 | 81.9507 | 59.8258 | 981.3807
2031-06-30 23:00 | 3080.67 | 1 | 66.4078 | 59.8258 | 902.8553
2031-07-02 | -67.6068 | 0.72207 | 66.0088 | 59.8258 | -19.8136
2031-07-03 01:00 | -328.881 | 1.3756 | 64.7672 | 59.8258 | -96.3855
2031-07-04 02:00 | -477.069 | 1.7237 | 64.1998 | 59.8258 | -139.8151
2031-07-05 03:00 | -619.189 | 2.081 | 63.8485 | 59.8258 | -181.4664
2031-07-06 04:00 | -797.053 | 2.5369 | 63.517 | 59.8258 | -233.5932
2031-07-07 05:00 | -260.694 | 1.0541 | 63.5714 | 59.8258 | -76.4019
2031-07-08 06:00 | 2195.29 | 1 | 64.4218 | 59.8258 | 643.376
2031-07-09 07:00 | 2991.98 | 1 | 83.0722 | 59.8258 | 876.8628
2031-07-10 08:00 | 3281.33 | 1.0518 | 79.2803 | 59.8258 | 961.6629
2031-07-11 09:00 | 5386.89 | 1.7504 | 79.2009 | 59.8258 | 1578.7416
2031-07-12 10:00 | 7101.16 | 2.3647 | 79.2091 | 59.8258 | 2081.1446
2031-07-13 11:00 | 8462.02 | 2.8058 | 79.703 | 59.8258 | 2479.9733
2031-07-14 12:00 | 8992.21 | 2.9754 | 80.1581 | 59.8258 | 2635.3566
2031-07-15 13:00 | 9700.73 | 3.1503 | 80.7626 | 59.8258 | 2843.0033
2031-07-16 14:00 | 10389.2 | 3.2877 | 81.4783 | 59.8258 | 3044.774
2031-07-17 15:00 | 11406.9 | 3.6536 | 81.6288 | 59.8258 | 3343.0324
2031-07-18 16:00 | 12098.3 | 3.8166 | 82.1888 | 59.8258 | 3545.6617
2031-07-19 17:00 | 11781 | 3.725 | 82.488 | 59.8258 | 3452.6703
2031-07-20 18:00 | 10284.5 | 3.2228 | 82.8156 | 59.8258 | 3014.0894
2031-07-21 19:00 | 8503.93 | 2.634 | 82.9689 | 59.8258 | 2492.2559
2031-07-22 20:00 | 6042.63 | 1.8364 | 83.0886 | 59.8258 | 1770.92
2031-07-23 21:00 | 4972.24 | 1.4555 | 83.2782 | 59.8258 | 1457.2197
2031-07-24 22:00 | 3206.25 | 1 | 88.1938 | 59.8258 | 939.6591
2031-07-25 23:00 | 3160.56 | 1 | 66.5854 | 59.8258 | 926.2687
2031-07-27 | 3124.08 | 1 | 66.3242 | 59.8258 | 915.5775
2031-07-28 01:00 | 3152.48 | 1 | 66.1503 | 59.8258 | 923.9007
2031-07-29 02:00 | 794.024 | 1 | 66.2492 | 59.8258 | 232.7055
2031-07-30 03:00 | 2108.26 | 1 | 65.7093 | 59.8258 | 617.87
2031-07-31 04:00 | 3164.06 | 1 | 65.5397 | 59.8258 | 927.2944
2031-08-01 05:00 | 3266.94 | 1 | 65.6089 | 59.8258 | 957.4456
2031-08-02 06:00 | 3253.64 | 1 | 65.5955 | 59.8258 | 953.5478
2031-08-03 07:00 | 3258.13 | 1 | 80.9698 | 59.8258 | 954.8636
2031-08-04 08:00 | 4313.86 | 1.3506 | 80.4397 | 59.8258 | 1264.2676
2031-08-05 09:00 | 6296.15 | 2.0633 | 79.9128 | 59.8258 | 1845.2194
2031-08-06 10:00 | 7680.03 | 2.5549 | 80.0221 | 59.8258 | 2250.7946
2031-08-07 11:00 | 9098.87 | 3.0337 | 80.3323 | 59.8258 | 2666.6156
2031-08-08 12:00 | 10112.6 | 3.3486 | 80.8093 | 59.8258 | 2963.7105
2031-08-09 13:00 | 10579 | 3.4276 | 81.5011 | 59.8258 | 3100.3988
2031-08-10 14:00 | 11264.3 | 3.5879 | 82.083 | 59.8258 | 3301.2405
2031-08-11 15:00 | 12914.5 | 4.2078 | 82.0566 | 59.8258 | 3784.8663
2031-08-12 16:00 | 13292.5 | 4.2466 | 82.7514 | 59.8258 | 3895.6472
2031-08-13 17:00 | 13124 | 4.1983 | 83.0558 | 59.8258 | 3846.2647
2031-08-14 18:00 | 11875.9 | 3.688 | 83.7065 | 59.8258 | 3480.4827
2031-08-15 19:00 | 10010.6 | 3.103 | 83.792 | 59.8258 | 2933.8173
2031-08-16 20:00 | 7281.6 | 2.2239 | 83.8925 | 59.8258 | 2134.0263
2031-08-17 21:00 | 6330.27 | 1.8674 | 84.0221 | 59.8258 | 1855.219
2031-08-18 22:00 | 3848.84 | 1.1509 | 83.5045 | 59.8258 | 1127.9837
2031-08-19 23:00 | 3247.14 | 1 | 88.1954 | 59.8258 | 951.6428
2031-08-21 | 3130.51 | 1 | 67.0277 | 59.8258 | 917.4619
2031-08-22 01:00 | 3134.22 | 1 | 66.7757 | 59.8258 | 918.5492
2031-08-23 02:00 | 3164 | 1 | 66.6112 | 59.8258 | 927.2769
2031-08-24 03:00 | 3187.19 | 1 | 66.4523 | 59.8258 | 934.0732
2031-08-25 04:00 | 3177.94 | 1 | 66.3455 | 59.8258 | 931.3623
2031-08-26 05:00 | 3262.61 | 1 | 66.2397 | 59.8258 | 956.1766
2031-08-27 06:00 | 3180.68 | 1 | 85.9482 | 59.8258 | 932.1653
2031-08-28 07:00 | 3862.66 | 1.1854 | 81.239 | 59.8258 | 1132.0339
2031-08-29 08:00 | 4480.99 | 1.3804 | 81.2261 | 59.8258 | 1313.2485
2031-08-30 09:00 | 5857.9 | 1.8944 | 80.5916 | 59.8258 | 1716.781
2031-08-31 10:00 | 7619.72 | 2.5033 | 80.5809 | 59.8258 | 2233.1195
2031-09-01 11:00 | 7953.59 | 2.6199 | 80.8926 | 59.8258 | 2330.9671
2031-09-02 12:00 | 8627.51 | 2.8333 | 81.1744 | 59.8258 | 2528.4736
2031-09-03 13:00 | 8622.62 | 2.6663 | 82.271 | 59.8258 | 2527.0405
2031-09-04 14:00 | 6164.7 | 1.807 | 83.2514 | 59.8258 | 1806.6952
2031-09-05 15:00 | 6884.18 | 2.1382 | 82.1227 | 59.8258 | 2017.554
2031-09-06 16:00 | 6779.68 | 2.1513 | 81.7562 | 59.8258 | 1986.9281
2031-09-07 17:00 | 7102 | 2.3551 | 81.1019 | 59.8258 | 2081.3907
2031-09-08 18:00 | 5875.75 | 1.8227 | 82.0522 | 59.8258 | 1722.0123
2031-09-09 19:00 | 4844.28 | 1.4762 | 82.143 | 59.8258 | 1419.7183
2031-09-10 20:00 | 3168.29 | 1 | 85.9264 | 59.8258 | 928.5341
2031-09-11 21:00 | 3196.93 | 1 | 66.3556 | 59.8258 | 936.9277
2031-09-12 22:00 | 0 | 0 | 66.4578 | 59.8258 | 0
2031-09-13 23:00 | -380.863 | 1.4466 | 64.6726 | 59.8258 | -111.6199
2031-09-15 | -581.137 | 1.996 | 64.1174 | 59.8258 | -170.3144
2031-09-16 01:00 | -718.03 | 2.3253 | 63.7415 | 59.8258 | -210.4338
2031-09-17 02:00 | -640.163 | 2.0925 | 63.538 | 59.8258 | -187.6133
2031-09-18 03:00 | -666.649 | 2.1892 | 63.3413 | 59.8258 | -195.3755
2031-09-19 04:00 | -659.899 | 2.166 | 63.2054 | 59.8258 | -193.3973
2031-09-20 05:00 | -164.325 | 0.82939 | 63.5611 | 59.8258 | -48.1589
2031-09-21 06:00 | 1992.97 | 1 | 64.2461 | 59.8258 | 584.0819
2031-09-22 07:00 | 2824.14 | 1 | 64.3983 | 59.8258 | 827.6737
2031-09-23 08:00 | 3076.39 | 1 | 83.4434 | 59.8258 | 901.6009
2031-09-24 09:00 | 4339.26 | 1.3615 | 79.515 | 59.8258 | 1271.7116
2031-09-25 10:00 | 5956.76 | 1.9743 | 78.9962 | 59.8258 | 1745.754
2031-09-26 11:00 | 7226.86 | 2.3694 | 79.5232 | 59.8258 | 2117.9836
2031-09-27 12:00 | 7922.93 | 2.4886 | 80.493 | 59.8258 | 2321.9816
2031-09-28 13:00 | 8816.72 | 2.8004 | 80.6361 | 59.8258 | 2583.9256
2031-09-29 14:00 | 9428.76 | 3.0773 | 80.6005 | 59.8258 | 2763.2968
2031-09-30 15:00 | 11230.1 | 3.7441 | 80.6187 | 59.8258 | 3291.2174
2031-10-01 16:00 | 12000.1 | 3.8948 | 81.4488 | 59.8258 | 3516.8821
2031-10-02 17:00 | 12140.2 | 3.8461 | 82.1988 | 59.8258 | 3557.9414
2031-10-03 18:00 | 10562.7 | 3.3006 | 82.6998 | 59.8258 | 3095.6218
2031-10-04 19:00 | 9114.86 | 2.8125 | 82.9226 | 59.8258 | 2671.3018
2031-10-05 20:00 | 6670.91 | 1.9592 | 83.606 | 59.8258 | 1955.0507
2031-10-06 21:00 | 5523.91 | 1.6423 | 83.0969 | 59.8258 | 1618.8982
2031-10-07 22:00 | 3272.44 | 1 | 85.4583 | 59.8258 | 959.0575
2031-10-08 23:00 | 3176.43 | 1 | 92.1318 | 59.8258 | 930.9197
2031-10-10 | 3205.1 | 1 | 66.4054 | 59.8258 | 939.3221
2031-10-11 01:00 | 3099.9 | 1 | 66.2556 | 59.8258 | 908.491
2031-10-12 02:00 | 1601 | 1 | 66.257 | 59.8258 | 469.2068
2031-10-13 03:00 | 2224.06 | 1 | 65.8731 | 59.8258 | 651.8076
2031-10-14 04:00 | 3199.41 | 1 | 65.6743 | 59.8258 | 937.6545
2031-10-15 05:00 | 3254.3 | 1 | 65.7044 | 59.8258 | 953.7412
2031-10-16 06:00 | 3238.89 | 1 | 89.3171 | 59.8258 | 949.225
2031-10-17 07:00 | 3997.97 | 1.1784 | 81.3721 | 59.8258 | 1171.6893
2031-10-18 08:00 | 4592.73 | 1.3815 | 81.1711 | 59.8258 | 1345.9963
2031-10-19 09:00 | 6067.01 | 2.0596 | 79.5523 | 59.8258 | 1778.0651
2031-10-20 10:00 | 7710.96 | 2.6984 | 79.3893 | 59.8258 | 2259.8593
2031-10-21 11:00 | 8847.72 | 3.0612 | 79.8867 | 59.8258 | 2593.0108
2031-10-22 12:00 | 9841.06 | 3.2232 | 80.9827 | 59.8258 | 2884.13
2031-10-23 13:00 | 10639.3 | 3.4571 | 81.4375 | 59.8258 | 3118.071
2031-10-24 14:00 | 11600.7 | 3.6942 | 82.0865 | 59.8258 | 3399.8296
2031-10-25 15:00 | 13361.6 | 4.2997 | 82.2914 | 59.8258 | 3915.8984
2031-10-26 16:00 | 14007.6 | 4.4218 | 83.032 | 59.8258 | 4105.2223
2031-10-27 17:00 | 14013.8 | 4.4164 | 83.4516 | 59.8258 | 4107.0394
2031-10-28 18:00 | 12524.8 | 3.8836 | 83.9898 | 59.8258 | 3670.6565
2031-10-29 19:00 | 10402.4 | 3.2047 | 84.1525 | 59.8258 | 3048.6425
2031-10-30 20:00 | 7814.08 | 2.3312 | 84.4972 | 59.8258 | 2290.0808
2031-10-31 21:00 | 6475.93 | 1.9359 | 84.0903 | 59.8258 | 1897.9077
2031-11-01 22:00 | 4230.04 | 1.2321 | 84.1538 | 59.8258 | 1239.7023
2031-11-02 23:00 | 3225.07 | 1 | 87.2762 | 59.8258 | 945.1747
2031-11-04 | 3159.9 | 1 | 67.2462 | 59.8258 | 926.0753
2031-11-05 01:00 | 3089.46 | 1 | 66.9833 | 59.8258 | 905.4313
2031-11-06 02:00 | 3153.16 | 1 | 66.7889 | 59.8258 | 924.1
2031-11-07 03:00 | 2905.35 | 1 | 66.6426 | 59.8258 | 851.474
2031-11-08 04:00 | 74.0119 | 1 | 66.7299 | 59.8258 | 21.6907
2031-11-09 05:00 | 50.3337 | 1 | 66.21 | 59.8258 | 14.7514
2031-11-10 06:00 | 2197.99 | 1.2197 | 74.1239 | 59.8258 | 644.1673
2031-11-11 07:00 | 4468.85 | 1.8164 | 77.1769 | 59.8258 | 1309.6907
2031-11-12 08:00 | 4855.7 | 1.6802 | 79.4106 | 59.8258 | 1423.0652
2031-11-13 09:00 | 6204.59 | 2.1596 | 79.4534 | 59.8258 | 1818.3858
2031-11-14 10:00 | 8367.65 | 2.8268 | 80.1299 | 59.8258 | 2452.3161
2031-11-15 11:00 | 9576.89 | 3.2974 | 80.3603 | 59.8258 | 2806.7094
2031-11-16 12:00 | 9976.49 | 3.4073 | 80.8968 | 59.8258 | 2923.8206
2031-11-17 13:00 | 10880.2 | 3.4886 | 82.0464 | 59.8258 | 3188.6719
2031-11-18 14:00 | 11581.9 | 3.7264 | 82.3149 | 59.8258 | 3394.3198
2031-11-19 15:00 | 11891.8 | 3.9068 | 82.326 | 59.8258 | 3485.1426
2031-11-20 16:00 | 14296.3 | 4.7188 | 82.5039 | 59.8258 | 4189.8319
2031-11-21 17:00 | 13539.8 | 4.3957 | 83.2513 | 59.8258 | 3968.1237
2031-11-22 18:00 | 12326.6 | 3.8793 | 83.9464 | 59.8258 | 3612.5699
2031-11-23 19:00 | 10525.1 | 3.2121 | 84.4219 | 59.8258 | 3084.6023
2031-11-24 20:00 | 8869.71 | 2.7291 | 84.1785 | 59.8258 | 2599.4554
2031-11-25 21:00 | 7423.88 | 2.2898 | 83.931 | 59.8258 | 2175.7245
2031-11-26 22:00 | 6373.56 | 1.9916 | 83.4296 | 59.8258 | 1867.906
2031-11-27 23:00 | 3330.5 | 1 | 85.8742 | 59.8258 | 976.0732
2031-11-29 | 3244.39 | 1 | 67.6358 | 59.8258 | 950.8368
2031-11-30 01:00 | 3172.15 | 1 | 67.2877 | 59.8258 | 929.6654
2031-12-01 02:00 | 2698.78 | 1 | 67.1029 | 59.8258 | 790.9343
2031-12-02 03:00 | 616.59 | 1 | 67.0351 | 59.8258 | 180.7047
2031-12-03 04:00 | -24.9023 | 0.61165 | 66.4029 | 59.8258 | -7.2981
2031-12-04 05:00 | -249.278 | 1.1677 | 65.2349 | 59.8258 | -73.0562
2031-12-05 06:00 | 2055.16 | 1 | 77.4306 | 59.8258 | 602.3079
2031-12-06 07:00 | 4262.04 | 1.4722 | 79.1962 | 59.8258 | 1249.0806
2031-12-07 08:00 | 4675.17 | 1.5246 | 80.2346 | 59.8258 | 1370.1571
2031-12-08 09:00 | 6098.63 | 2.0433 | 80.0133 | 59.8258 | 1787.332
2031-12-09 10:00 | 7859.15 | 2.6966 | 79.9457 | 59.8258 | 2303.2895
2031-12-10 11:00 | 9163.34 | 3.155 | 80.3285 | 59.8258 | 2685.5099
2031-12-11 12:00 | 10429.1 | 3.3877 | 81.5241 | 59.8258 | 3056.4675
2031-12-12 13:00 | 11404.7 | 3.6526 | 82.105 | 59.8258 | 3342.3876
2031-12-13 14:00 | 11343.9 | 3.8033 | 81.8616 | 59.8258 | 3324.5689
2031-12-14 15:00 | 12003.5 | 3.9077 | 82.5367 | 59.8258 | 3517.8786
2031-12-15 16:00 | 14863 | 4.8406 | 82.7959 | 59.8258 | 4355.9153
2031-12-16 17:00 | 14156.3 | 4.4752 | 83.8354 | 59.8258 | 4148.802
2031-12-17 18:00 | 12929 | 4.02 | 84.3727 | 59.8258 | 3789.1159
2031-12-18 19:00 | 10939.4 | 3.4094 | 84.3851 | 59.8258 | 3206.0217
2031-12-19 20:00 | 9623.97 | 2.9342 | 84.5959 | 59.8258 | 2820.5072
2031-12-20 21:00 | 8527.8 | 2.5433 | 84.7697 | 59.8258 | 2499.2515
2031-12-21 22:00 | 7748.5 | 2.4137 | 83.8836 | 59.8258 | 2270.8612
2031-12-22 23:00 | 5455.38 | 1.5471 | 85.1256 | 59.8258 | 1598.8141
2031-12-24 | 4344.27 | 1.318 | 83.6469 | 59.8258 | 1273.1799
2031-12-25 01:00 | 3725.93 | 1.1238 | 83.3531 | 59.8258 | 1091.9623
2031-12-26 02:00 | 3288.03 | 1 | 83.0684 | 59.8258 | 963.6265
2031-12-27 03:00 | 3273.93 | 1 | 83.6675 | 59.8258 | 959.4942
2031-12-28 04:00 | 3260.75 | 1 | 83.4876 | 59.8258 | 955.6315
2031-12-29 05:00 | 3824.42 | 1.2235 | 81.5893 | 59.8258 | 1120.8269
2031-12-30 06:00 | 4311.33 | 1.3415 | 81.9513 | 59.8258 | 1263.5261
2031-12-31 07:00 | 4801.03 | 1.5002 | 81.8928 | 59.8258 | 1407.043
2032-01-01 08:00 | 5556.28 | 1.8881 | 80.7598 | 59.8258 | 1628.3849
2032-01-02 09:00 | 7528.44 | 2.5434 | 80.935 | 59.8258 | 2206.368
2032-01-03 10:00 | 9090.91 | 3.0672 | 81.2477 | 59.8258 | 2664.2827
2032-01-04 11:00 | 10460.4 | 3.4738 | 81.8334 | 59.8258 | 3065.6406
2032-01-05 12:00 | 11496.5 | 3.6816 | 82.7348 | 59.8258 | 3369.2916
2032-01-06 13:00 | 12253.4 | 3.9209 | 83.1351 | 59.8258 | 3591.117
2032-01-07 14:00 | 12687.6 | 4.1108 | 83.3322 | 59.8258 | 3718.3685
2032-01-08 15:00 | 14466.8 | 4.6232 | 83.824 | 59.8258 | 4239.8006
2032-01-09 16:00 | 14802 | 4.8087 | 84.0234 | 59.8258 | 4338.038
2032-01-10 17:00 | 14616.1 | 4.6907 | 84.5308 | 59.8258 | 4283.5561
2032-01-11 18:00 | 13189.8 | 4.0658 | 85.3351 | 59.8258 | 3865.5488
2032-01-12 19:00 | 11242.7 | 3.4972 | 85.2248 | 59.8258 | 3294.9101
2032-01-13 20:00 | 8881.04 | 2.7286 | 85.2548 | 59.8258 | 2602.7759
2032-01-14 21:00 | 7585.26 | 2.3395 | 84.8263 | 59.8258 | 2223.0203
2032-01-15 22:00 | 5731.4 | 1.6593 | 85.4365 | 59.8258 | 1679.7075
2032-01-16 23:00 | 4781.39 | 1.3606 | 85.2609 | 59.8258 | 1401.2871
2032-01-18 | 4006.79 | 1.2533 | 83.4124 | 59.8258 | 1174.2742
2032-01-19 01:00 | 3448.18 | 1.0845 | 82.9871 | 59.8258 | 1010.5618
2032-01-20 02:00 | 3365.09 | 1 | 83.8509 | 59.8258 | 986.2105
2032-01-21 03:00 | 3305.51 | 1.0074 | 82.9193 | 59.8258 | 968.7494
2032-01-22 04:00 | 3447.52 | 1.0356 | 82.9597 | 59.8258 | 1010.3684
2032-01-23 05:00 | 4529.94 | 1.4465 | 81.9188 | 59.8258 | 1327.5944
2032-01-24 06:00 | 5004.41 | 1.5869 | 82.0498 | 59.8258 | 1466.6478
2032-01-25 07:00 | 5717 | 1.8334 | 81.9369 | 59.8258 | 1675.4873
2032-01-26 08:00 | 5806.21 | 1.8676 | 82.0024 | 59.8258 | 1701.6322
2032-01-27 09:00 | 7198.45 | 2.5387 | 80.8063 | 59.8258 | 2109.6574
2032-01-28 10:00 | 9396.42 | 3.2155 | 81.4141 | 59.8258 | 2753.8189
2032-01-29 11:00 | 10502.9 | 3.3937 | 82.6055 | 59.8258 | 3078.0961
2032-01-30 12:00 | 10089.3 | 3.1464 | 83.4903 | 59.8258 | 2956.8819
2032-01-31 13:00 | 10401.1 | 3.2799 | 83.4864 | 59.8258 | 3048.2615
2032-02-01 14:00 | 9541.05 | 3.0562 | 83.4484 | 59.8258 | 2796.2057
2032-02-02 15:00 | 10257.5 | 3.0966 | 84.3316 | 59.8258 | 3006.1765
2032-02-03 16:00 | 11566.6 | 3.7845 | 83.2405 | 59.8258 | 3389.8358
2032-02-04 17:00 | 12001.9 | 3.7932 | 83.9546 | 59.8258 | 3517.4097
2032-02-05 18:00 | 10734.3 | 3.437 | 83.9747 | 59.8258 | 3145.9128
2032-02-06 19:00 | 9470.16 | 2.9517 | 84.3364 | 59.8258 | 2775.4299
2032-02-07 20:00 | 7384.87 | 2.259 | 84.5145 | 59.8258 | 2164.2918
2032-02-08 21:00 | 6554.66 | 1.9918 | 84.3214 | 59.8258 | 1920.9812
2032-02-09 22:00 | 4895.94 | 1.4268 | 84.6867 | 59.8258 | 1434.8584
2032-02-10 23:00 | 4148.85 | 1.2408 | 83.8885 | 59.8258 | 1215.9079
2032-02-12 | 3759.99 | 1.1208 | 83.6034 | 59.8258 | 1101.9443
2032-02-13 01:00 | 3373.75 | 1.0453 | 82.7633 | 59.8258 | 988.7485
2032-02-14 02:00 | 3256.87 | 1 | 83.2812 | 59.8258 | 954.4944
2032-02-15 03:00 | 3416.89 | 1.0257 | 82.8534 | 59.8258 | 1001.3916
2032-02-16 04:00 | 3513.42 | 1.0904 | 82.2458 | 59.8258 | 1029.6818
2032-02-17 05:00 | 4447.01 | 1.3657 | 82.3025 | 59.8258 | 1303.29
2032-02-18 06:00 | 5222.48 | 1.7213 | 81.3188 | 59.8258 | 1530.5578
2032-02-19 07:00 | 6230.77 | 1.9998 | 81.7886 | 59.8258 | 1826.0584
2032-02-20 08:00 | 6452.64 | 2.0883 | 81.8521 | 59.8258 | 1891.0821
2032-02-21 09:00 | 8154.55 | 2.7543 | 81.3717 | 59.8258 | 2389.8627
2032-02-22 10:00 | 9833.94 | 3.3839 | 81.4136 | 59.8258 | 2882.0433
2032-02-23 11:00 | 11858.8 | 3.8537 | 82.583 | 59.8258 | 3475.4712
2032-02-24 12:00 | 12855 | 4.1767 | 83.0827 | 59.8258 | 3767.4286
2032-02-25 13:00 | 11876.4 | 3.6867 | 84.1859 | 59.8258 | 3480.6293
2032-02-26 14:00 | 12123.5 | 3.932 | 83.734 | 59.8258 | 3553.0471
2032-02-27 15:00 | 14727.4 | 4.7668 | 83.9359 | 59.8258 | 4316.1749
2032-02-28 16:00 | 15590.4 | 4.9816 | 84.6223 | 59.8258 | 4569.0952
2032-02-29 17:00 | 15581 | 5.0749 | 84.7632 | 59.8258 | 4566.3403
2032-03-01 18:00 | 13999.3 | 4.3362 | 85.7497 | 59.8258 | 4102.7898
2032-03-02 19:00 | 11876.5 | 3.6961 | 85.7276 | 59.8258 | 3480.6586
2032-03-03 20:00 | 9027.93 | 2.7692 | 85.8096 | 59.8258 | 2645.8251
2032-03-04 21:00 | 7887.52 | 2.3721 | 85.6852 | 59.8258 | 2311.6039
2032-03-05 22:00 | 5945.81 | 1.6658 | 86.4413 | 59.8258 | 1742.5449
2032-03-06 23:00 | 4956.91 | 1.3737 | 86.1414 | 59.8258 | 1452.7269
2032-03-08 | 3915.54 | 1.1809 | 84.3727 | 59.8258 | 1147.5315
2032-03-09 01:00 | 3240.09 | 1 | 83.6762 | 59.8258 | 949.5766
2032-03-10 02:00 | 3068.47 | 1 | 84.2815 | 59.8258 | 899.2798
2032-03-11 03:00 | 3138.05 | 1 | 83.8564 | 59.8258 | 919.6717
2032-03-12 04:00 | 3223.29 | 1 | 83.3249 | 59.8258 | 944.653
2032-03-13 05:00 | 4265.69 | 1.3433 | 82.3561 | 59.8258 | 1250.1503
2032-03-14 06:00 | 5459.31 | 1.6606 | 82.8575 | 59.8258 | 1599.9658
2032-03-15 07:00 | 6293.99 | 2.1578 | 81.2806 | 59.8258 | 1844.5864
2032-03-16 08:00 | 6887.93 | 2.2372 | 82.1873 | 59.8258 | 2018.653
2032-03-17 09:00 | 8141.96 | 2.7475 | 81.8049 | 59.8258 | 2386.1729
2032-03-18 10:00 | 9651.39 | 3.199 | 82.3054 | 59.8258 | 2828.5432
2032-03-19 11:00 | 11214.7 | 3.6054 | 83.0709 | 59.8258 | 3286.7041
2032-03-20 12:00 | 11873.7 | 3.8058 | 83.5186 | 59.8258 | 3479.838
2032-03-21 13:00 | 12552 | 3.9662 | 84.0701 | 59.8258 | 3678.6281
2032-03-22 14:00 | 12955.2 | 4.2117 | 84.0045 | 59.8258 | 3796.7943
2032-03-23 15:00 | 14266.1 | 4.5514 | 84.5535 | 59.8258 | 4180.9812
2032-03-24 16:00 | 14280 | 4.5313 | 85.0018 | 59.8258 | 4185.0549
2032-03-25 17:00 | 14304.2 | 4.5687 | 85.1451 | 59.8258 | 4192.1472
2032-03-26 18:00 | 12942 | 4.1358 | 85.3267 | 59.8258 | 3792.9258
2032-03-27 19:00 | 11606.1 | 3.6011 | 85.75 | 59.8258 | 3401.4121
2032-03-28 20:00 | 9166.97 | 2.7158 | 86.3508 | 59.8258 | 2686.5737
2032-03-29 21:00 | 7888.14 | 2.3558 | 85.8827 | 59.8258 | 2311.7856
2032-03-30 22:00 | 5805.21 | 1.6432 | 86.397 | 59.8258 | 1701.3391
2032-03-31 23:00 | 4711.88 | 1.3969 | 85.1988 | 59.8258 | 1380.9157
2032-04-02 | 3883.14 | 1.1808 | 84.3923 | 59.8258 | 1138.036
2032-04-03 01:00 | 3416.29 | 1.0635 | 83.6706 | 59.8258 | 1001.2158
2032-04-04 02:00 | 3151.61 | 1 | 83.4608 | 59.8258 | 923.6457
2032-04-05 03:00 | 3204.05 | 1 | 83.6129 | 59.8258 | 939.0144
2032-04-06 04:00 | 3163.55 | 1 | 83.0875 | 59.8258 | 927.145
2032-04-07 05:00 | 4319.3 | 1.3419 | 82.7636 | 59.8258 | 1265.8619
2032-04-08 06:00 | 5172.16 | 1.6686 | 82.2258 | 59.8258 | 1515.8105
2032-04-09 07:00 | 6343.64 | 2.1059 | 81.9008 | 59.8258 | 1859.1374
2032-04-10 08:00 | 6856.1 | 2.2836 | 82.0324 | 59.8258 | 2009.3246
2032-04-11 09:00 | 8516.42 | 2.7767 | 82.4704 | 59.8258 | 2495.9163
2032-04-12 10:00 | 10055.4 | 3.3577 | 82.4466 | 59.8258 | 2946.9468
2032-04-13 11:00 | 11139.4 | 3.684 | 82.9559 | 59.8258 | 3264.6359
2032-04-14 12:00 | 12333.5 | 3.8648 | 84.0807 | 59.8258 | 3614.592
2032-04-15 13:00 | 13266.3 | 4.151 | 84.4861 | 59.8258 | 3887.9687
2032-04-16 14:00 | 13542.7 | 4.382 | 84.4029 | 59.8258 | 3968.9736
2032-04-17 15:00 | 15196 | 4.9605 | 84.5574 | 59.8258 | 4453.508
2032-04-18 16:00 | 15923.8 | 5.1224 | 85.185 | 59.8258 | 4666.8051
2032-04-19 17:00 | 15768.9 | 5.037 | 85.6682 | 59.8258 | 4621.4084
2032-04-20 18:00 | 14615 | 4.5105 | 86.4167 | 59.8258 | 4283.2337
2032-04-21 19:00 | 12836.7 | 3.9528 | 86.5099 | 59.8258 | 3762.0654
2032-04-22 20:00 | 10229.7 | 3.0602 | 86.8541 | 59.8258 | 2998.0291
2032-04-23 21:00 | 8736.97 | 2.63 | 86.4036 | 59.8258 | 2560.5531
2032-04-24 22:00 | 6752.53 | 1.924 | 86.9024 | 59.8258 | 1978.9712
2032-04-25 23:00 | 5377.52 | 1.5415 | 86.3477 | 59.8258 | 1575.9955
2032-04-27 | 4140.2 | 1.2967 | 84.5403 | 59.8258 | 1213.3728
2032-04-28 01:00 | 3392.49 | 1.05 | 84.2684 | 59.8258 | 994.2407
2032-04-29 02:00 | 3074.49 | 1 | 86.6539 | 59.8258 | 901.0441
2032-04-30 03:00 | 3243.37 | 1 | 92.7165 | 59.8258 | 950.5379
2032-05-01 04:00 | 3112.82 | 1 | 68.3141 | 59.8258 | 912.2775
2032-05-02 05:00 | 3183.79 | 1 | 68.1036 | 59.8258 | 933.0767
2032-05-03 06:00 | 4288.04 | 1.3425 | 82.8368 | 59.8258 | 1256.7005
2032-05-04 07:00 | 6290.27 | 2.0576 | 82.17 | 59.8258 | 1843.4962
2032-05-05 08:00 | 6531.19 | 2.0256 | 83.1811 | 59.8258 | 1914.1028
2032-05-06 09:00 | 7652.26 | 2.5063 | 82.5164 | 59.8258 | 2242.656
2032-05-07 10:00 | 9271.56 | 3.1789 | 82.0885 | 59.8258 | 2717.226
2032-05-08 11:00 | 11555.6 | 3.7885 | 83.0409 | 59.8258 | 3386.6121
2032-05-09 12:00 | 12130 | 3.9335 | 83.7037 | 59.8258 | 3554.9521
2032-05-10 13:00 | 12681.5 | 4.1474 | 83.9425 | 59.8258 | 3716.5808
2032-05-11 14:00 | 12665.3 | 3.8286 | 85.4069 | 59.8258 | 3711.833
2032-05-12 15:00 | 12931.4 | 4.0924 | 84.9498 | 59.8258 | 3789.8192
2032-05-13 16:00 | 15270.5 | 5.035 | 84.5603 | 59.8258 | 4475.3418
2032-05-14 17:00 | 13675.1 | 4.3304 | 85.592 | 59.8258 | 4007.7762
2032-05-15 18:00 | 12969.3 | 4.0727 | 85.7966 | 59.8258 | 3800.9266
2032-05-16 19:00 | 11749.5 | 3.5387 | 86.3998 | 59.8258 | 3443.4385
2032-05-17 20:00 | 10089.7 | 3.1181 | 85.9527 | 59.8258 | 2956.9992
2032-05-18 21:00 | 8657.39 | 2.707 | 85.5826 | 59.8258 | 2537.2306
2032-05-19 22:00 | 7687.28 | 2.3642 | 85.5176 | 59.8258 | 2252.9194
2032-05-20 23:00 | 4178.18 | 1.2028 | 86.2627 | 59.8258 | 1224.5037
2032-05-22 | 3282.05 | 1.0118 | 84.5753 | 59.8258 | 961.8739
2032-05-23 01:00 | 3115.14 | 1 | 90.9988 | 59.8258 | 912.9574
2032-05-24 02:00 | 3023.37 | 1 | 68.6745 | 59.8258 | 886.0623
2032-05-25 03:00 | 2895.44 | 1 | 68.4375 | 59.8258 | 848.5697
2032-05-26 04:00 | 0 | 0 | 68.4333 | 59.8258 | 0
2032-05-27 05:00 | -120.092 | 0.83251 | 67.2143 | 59.8258 | -35.1955
2032-05-28 06:00 | 2237.96 | 1 | 67.2853 | 59.8258 | 655.8813
2032-05-29 07:00 | 2858.05 | 1 | 82.0959 | 59.8258 | 837.6118
2032-05-30 08:00 | 2955.82 | 1 | 84.5276 | 59.8258 | 866.2653
2032-05-31 09:00 | 3510.3 | 1.1588 | 81.2755 | 59.8258 | 1028.7674
2032-06-01 10:00 | 4362.77 | 1.5046 | 80.7061 | 59.8258 | 1278.6017
2032-06-02 11:00 | 5458.97 | 1.8738 | 80.8883 | 59.8258 | 1599.8662
2032-06-03 12:00 | 6006.3 | 2.0065 | 81.406 | 59.8258 | 1760.2728
2032-06-04 13:00 | 6492.39 | 2.083 | 82.0864 | 59.8258 | 1902.7317
2032-06-05 14:00 | 6581.32 | 2.1811 | 81.7455 | 59.8258 | 1928.7945
2032-06-06 15:00 | 6819.77 | 2.2527 | 81.849 | 59.8258 | 1998.6773
2032-06-07 16:00 | 9825.28 | 3.2084 | 82.0581 | 59.8258 | 2879.5053
2032-06-08 17:00 | 8737.92 | 2.9085 | 82.2418 | 59.8258 | 2560.8316
2032-06-09 18:00 | 7781.57 | 2.5225 | 82.7041 | 59.8258 | 2280.553
2032-06-10 19:00 | 6405.63 | 1.9909 | 83.2315 | 59.8258 | 1877.3048
2032-06-11 20:00 | 4995.47 | 1.5887 | 82.7435 | 59.8258 | 1464.0277
2032-06-12 21:00 | 3532.43 | 1.0772 | 83.1299 | 59.8258 | 1035.253
2032-06-13 22:00 | 3081.73 | 1 | 87.7002 | 59.8258 | 903.1659
2032-06-14 23:00 | 0 | 0 | 67.5228 | 59.8258 | 0
2032-06-16 | -855.521 | 2.6831 | 65.4813 | 59.8258 | -250.7285
2032-06-17 01:00 | -1251.94 | 3.6526 | 64.8942 | 59.8258 | -366.9074
2032-06-18 02:00 | -1443.62 | 4.0975 | 64.5063 | 59.8258 | -423.0833
2032-06-19 03:00 | -1588.49 | 4.463 | 64.2042 | 59.8258 | -465.5405
2032-06-20 04:00 | -1675.39 | 4.6816 | 63.9075 | 59.8258 | -491.0083
2032-06-21 05:00 | -1294.32 | 3.639 | 63.7125 | 59.8258 | -379.3277
2032-06-22 06:00 | -750.388 | 2.267 | 63.6915 | 59.8258 | -219.917
2032-06-23 07:00 | 2245.92 | 1 | 64.943 | 59.8258 | 658.2142
2032-06-24 08:00 | 2528.72 | 1 | 65.2375 | 59.8258 | 741.0947
2032-06-25 09:00 | 3239.43 | 1.0575 | 79.6739 | 59.8258 | 949.3832
2032-06-26 10:00 | 6000.95 | 1.923 | 80.0356 | 59.8258 | 1758.7048
2032-06-27 11:00 | 7710.04 | 2.4831 | 80.4432 | 59.8258 | 2259.5897
2032-06-28 12:00 | 8127.48 | 2.5609 | 81.286 | 59.8258 | 2381.9293
2032-06-29 13:00 | 8206.38 | 2.5871 | 81.6033 | 59.8258 | 2405.0526
2032-06-30 14:00 | 7967.89 | 2.4202 | 82.4016 | 59.8258 | 2335.158
2032-07-01 15:00 | 8877.17 | 2.755 | 82.2533 | 59.8258 | 2601.6417
2032-07-02 16:00 | 9235.42 | 2.8958 | 82.3253 | 59.8258 | 2706.6344
2032-07-03 17:00 | 9262.56 | 2.7412 | 83.3898 | 59.8258 | 2714.5884
2032-07-04 18:00 | 7438.88 | 2.3555 | 82.5323 | 59.8258 | 2180.1205
2032-07-05 19:00 | 6413.08 | 1.9642 | 82.8898 | 59.8258 | 1879.4882
2032-07-06 20:00 | 4237.34 | 1.2157 | 83.7509 | 59.8258 | 1241.8418
2032-07-07 21:00 | 3183.61 | 1 | 82.1179 | 59.8258 | 933.024
2032-07-08 22:00 | 3200.93 | 1 | 66.8413 | 59.8258 | 938.1
2032-07-09 23:00 | 3033.77 | 1 | 66.6513 | 59.8258 | 889.1102
2032-07-11 | 0 | 0 | 66.7708 | 59.8258 | 0
2032-07-12 01:00 | 68.362 | 1 | 66.2327 | 59.8258 | 20.0349
2032-07-13 02:00 | 3361.71 | 1 | 65.6471 | 59.8258 | 985.2199
2032-07-14 03:00 | 590.961 | 1 | 66.1727 | 59.8258 | 173.1936
2032-07-15 04:00 | 2585.41 | 1 | 65.7058 | 59.8258 | 757.7089
2032-07-16 05:00 | 2968.5 | 1 | 65.7001 | 59.8258 | 869.9815
2032-07-17 06:00 | 3138.34 | 1 | 65.8262 | 59.8258 | 919.7567
2032-07-18 07:00 | 3192.26 | 1 | 90.43 | 59.8258 | 935.5591
2032-07-19 08:00 | 3191.81 | 1 | 65.8676 | 59.8258 | 935.4272
2032-07-20 09:00 | 3167.76 | 1 | 65.9296 | 59.8258 | 928.3788
2032-07-21 10:00 | 3256.47 | 1 | 84.2591 | 59.8258 | 954.3771
2032-07-22 11:00 | 3928 | 1.1847 | 81.2909 | 59.8258 | 1151.1832
2032-07-23 12:00 | 5536.31 | 1.8143 | 80.1617 | 59.8258 | 1622.5323
2032-07-24 13:00 | 6615.66 | 2.1506 | 80.5244 | 59.8258 | 1938.8586
2032-07-25 14:00 | 7351.54 | 2.4301 | 80.5351 | 59.8258 | 2154.5237
2032-07-26 15:00 | 9310.6 | 3.1 | 80.6802 | 59.8258 | 2728.6675
2032-07-27 16:00 | 9942.26 | 3.2363 | 81.3955 | 59.8258 | 2913.7888
2032-07-28 17:00 | 9990.94 | 3.2061 | 81.9347 | 59.8258 | 2928.0555
2032-07-29 18:00 | 8749.51 | 2.7904 | 82.2484 | 59.8258 | 2564.2283
2032-07-30 19:00 | 8109.58 | 2.4104 | 83.3117 | 59.8258 | 2376.6833
2032-07-31 20:00 | 6043.14 | 1.6852 | 84.3335 | 59.8258 | 1771.0695
2032-08-01 21:00 | 5101.47 | 1.4608 | 83.6774 | 59.8258 | 1495.0933
2032-08-02 22:00 | 3093.38 | 1 | 87.4031 | 59.8258 | 906.5802
2032-08-03 23:00 | 2866.21 | 1 | 66.8729 | 59.8258 | 840.0032
2032-08-05 | 0 | 0 | 66.9105 | 59.8258 | 0
2032-08-06 01:00 | 0 | 0 | 66.3773 | 59.8258 | 0
2032-08-07 02:00 | -202.249 | 1.048 | 65.1514 | 59.8258 | -59.2733
2032-08-08 03:00 | -254.672 | 1.154 | 64.7691 | 59.8258 | -74.637
2032-08-09 04:00 | -341.928 | 1.3797 | 64.4217 | 59.8258 | -100.2092
2032-08-10 05:00 | -343.105 | 1.3679 | 64.1829 | 59.8258 | -100.5541
2032-08-11 06:00 | 1869.76 | 1 | 65.0214 | 59.8258 | 547.9726
2032-08-12 07:00 | 2554.68 | 1 | 77.7204 | 59.8258 | 748.7028
2032-08-13 08:00 | 3286.19 | 1.0477 | 79.8274 | 59.8258 | 963.0872
2032-08-14 09:00 | 4903.29 | 1.6551 | 79.1609 | 59.8258 | 1437.0124
2032-08-15 10:00 | 6615.4 | 2.2936 | 79.107 | 59.8258 | 1938.7824
2032-08-16 11:00 | 8456.74 | 2.7433 | 80.422 | 59.8258 | 2478.4258
2032-08-17 12:00 | 8981.57 | 2.8693 | 81.1205 | 59.8258 | 2632.2383
2032-08-18 13:00 | 9052.34 | 2.8358 | 81.773 | 59.8258 | 2652.979
2032-08-19 14:00 | 10213.2 | 3.1869 | 82.0943 | 59.8258 | 2993.1935
2032-08-20 15:00 | 10920.8 | 3.4906 | 82.0979 | 59.8258 | 3200.5705
2032-08-21 16:00 | 13574.2 | 4.4436 | 82.0842 | 59.8258 | 3978.2053
2032-08-22 17:00 | 12260.7 | 3.908 | 83.0458 | 59.8258 | 3593.2565
2032-08-23 18:00 | 11271 | 3.4792 | 83.718 | 59.8258 | 3303.204
2032-08-24 19:00 | 9757.25 | 3.0179 | 83.745 | 59.8258 | 2859.5677
2032-08-25 20:00 | 8077.14 | 2.5393 | 83.4475 | 59.8258 | 2367.1761
2032-08-26 21:00 | 7306.85 | 2.1789 | 84.0402 | 59.8258 | 2141.4263
2032-08-27 22:00 | 6559.72 | 2.0034 | 83.4589 | 59.8258 | 1922.4642
2032-08-28 23:00 | 3777.29 | 1.1006 | 83.9866 | 59.8258 | 1107.0144
2032-08-30 | 3297.33 | 1 | 86.2272 | 59.8258 | 966.352
2032-08-31 01:00 | 3179.94 | 1 | 91.7288 | 59.8258 | 931.9484
2032-09-01 02:00 | 3172.8 | 1 | 67.0294 | 59.8258 | 929.8559
2032-09-02 03:00 | 3198.27 | 1 | 66.8782 | 59.8258 | 937.3204
2032-09-03 04:00 | 3066.55 | 1 | 66.7248 | 59.8258 | 898.7171
2032-09-04 05:00 | 3207.01 | 1 | 86.9135 | 59.8258 | 939.8819
2032-09-05 06:00 | 3953.57 | 1.1748 | 82.1682 | 59.8258 | 1158.677
2032-09-06 07:00 | 4983.19 | 1.5493 | 81.5303 | 59.8258 | 1460.4288
2032-09-07 08:00 | 4736.41 | 1.5192 | 81.2254 | 59.8258 | 1388.1047
2032-09-08 09:00 | 6317.24 | 2.0853 | 80.8373 | 59.8258 | 1851.4003
2032-09-09 10:00 | 8420.13 | 2.8358 | 80.7685 | 59.8258 | 2467.6965
2032-09-10 11:00 | 9657.96 | 3.2806 | 81.0818 | 59.8258 | 2830.4687
2032-09-11 12:00 | 10705.7 | 3.5194 | 81.9325 | 59.8258 | 3137.531
2032-09-12 13:00 | 11538.5 | 3.7555 | 82.4496 | 59.8258 | 3381.6005
2032-09-13 14:00 | 12251.9 | 4.0396 | 82.6564 | 59.8258 | 3590.6774
2032-09-14 15:00 | 14554 | 4.4854 | 83.9698 | 59.8258 | 4265.3564
2032-09-15 16:00 | 15353 | 4.7121 | 84.5581 | 59.8258 | 4499.5201
2032-09-16 17:00 | 14590.6 | 4.5739 | 84.7157 | 59.8258 | 4276.0828
2032-09-17 18:00 | 12801.3 | 3.9883 | 85.0325 | 59.8258 | 3751.6907
2032-09-18 19:00 | 11041.1 | 3.3864 | 85.2451 | 59.8258 | 3235.827
2032-09-19 20:00 | 8446.76 | 2.5306 | 85.4781 | 59.8258 | 2475.501
2032-09-20 21:00 | 7055.23 | 2.1437 | 84.8856 | 59.8258 | 2067.6838
2032-09-21 22:00 | 4590.8 | 1.3244 | 85.3002 | 59.8258 | 1345.4307
2032-09-22 23:00 | 3577.79 | 1.0858 | 83.9813 | 59.8258 | 1048.5467
2032-09-24 | 3200.25 | 1 | 88.3691 | 59.8258 | 937.9007
2032-09-25 01:00 | 3147.93 | 1 | 67.876 | 59.8258 | 922.5672
2032-09-26 02:00 | 3219.49 | 1 | 67.6526 | 59.8258 | 943.5394
2032-09-27 03:00 | 3116.53 | 1 | 67.468 | 59.8258 | 913.3648
2032-09-28 04:00 | 3155.87 | 1 | 67.3026 | 59.8258 | 924.8942
2032-09-29 05:00 | 3252.49 | 1 | 87.5151 | 59.8258 | 953.2107
2032-09-30 06:00 | 3881.4 | 1.1437 | 82.8523 | 59.8258 | 1137.5261
2032-10-01 07:00 | 5045.13 | 1.6738 | 81.1182 | 59.8258 | 1478.5816
2032-10-02 08:00 | 5601.86 | 1.8212 | 81.5427 | 59.8258 | 1641.7431
2032-10-03 09:00 | 7092.53 | 2.4187 | 81.0109 | 59.8258 | 2078.6154
2032-10-04 10:00 | 8638.14 | 2.9425 | 81.2881 | 59.8258 | 2531.5889
2032-10-05 11:00 | 9627.15 | 3.3238 | 81.4727 | 59.8258 | 2821.4392
2032-10-06 12:00 | 10348.8 | 3.5099 | 82.0532 | 59.8258 | 3032.9339
2032-10-07 13:00 | 10861.6 | 3.7268 | 82.199 | 59.8258 | 3183.2207
2032-10-08 14:00 | 11974.1 | 3.8225 | 83.4692 | 59.8258 | 3509.2623
2032-10-09 15:00 | 14253.9 | 4.5344 | 83.8327 | 59.8258 | 4177.4057
2032-10-10 16:00 | 14998.3 | 4.8657 | 84.0587 | 59.8258 | 4395.5678
2032-10-11 17:00 | 14956.5 | 4.8376 | 84.5286 | 59.8258 | 4383.3175
2032-10-12 18:00 | 13907.4 | 4.3786 | 85.2138 | 59.8258 | 4075.8566
2032-10-13 19:00 | 11830.2 | 3.6491 | 85.6431 | 59.8258 | 3467.0894
2032-10-14 20:00 | 8873.56 | 2.709 | 85.7015 | 59.8258 | 2600.5837
2032-10-15 21:00 | 7481.36 | 2.2866 | 85.2758 | 59.8258 | 2192.5702
2032-10-16 22:00 | 5311.27 | 1.5461 | 85.6507 | 59.8258 | 1556.5796
2032-10-17 23:00 | 3255.83 | 1 | 84.5712 | 59.8258 | 954.1896
2032-10-19 | 3174.73 | 1 | 90.0742 | 59.8258 | 930.4215
2032-10-20 01:00 | 3156.53 | 1 | 68.2596 | 59.8258 | 925.0876
2032-10-21 02:00 | 3043.36 | 1 | 68.0449 | 59.8258 | 891.9208
2032-10-22 03:00 | 0 | 0 | 68.084 | 59.8258 | 0
2032-10-23 04:00 | -215.64 | 1.0669 | 66.5519 | 59.8258 | -63.1978
2032-10-24 05:00 | -341.467 | 1.3634 | 65.9163 | 59.8258 | -100.0741
2032-10-25 06:00 | 2163.84 | 1 | 66.5624 | 59.8258 | 634.1589
2032-10-26 07:00 | 3403.23 | 1.1752 | 80.0773 | 59.8258 | 997.3883
2032-10-27 08:00 | 4521.39 | 1.4563 | 81.1213 | 59.8258 | 1325.0886
2032-10-28 09:00 | 6130.59 | 2.0825 | 80.5706 | 59.8258 | 1796.6986
2032-10-29 10:00 | 8131.96 | 2.7208 | 81.0885 | 59.8258 | 2383.2422
2032-10-30 11:00 | 9732.51 | 3.2522 | 81.5764 | 59.8258 | 2852.3171
2032-10-31 12:00 | 10895.5 | 3.5463 | 82.3971 | 59.8258 | 3193.1558
2032-11-01 13:00 | 11837.8 | 3.8469 | 82.8392 | 59.8258 | 3469.3167
2032-11-02 14:00 | 12780.2 | 4.1396 | 83.2791 | 59.8258 | 3745.5069
2032-11-03 15:00 | 13723.6 | 4.4231 | 83.7522 | 59.8258 | 4021.9901
2032-11-04 16:00 | 16290.1 | 5.2291 | 84.1962 | 59.8258 | 4774.157
2032-11-05 17:00 | 15149.9 | 4.8079 | 84.996 | 59.8258 | 4439.9974
2032-11-06 18:00 | 13688.6 | 4.3575 | 85.2151 | 59.8258 | 4011.7326
2032-11-07 19:00 | 11838.6 | 3.6512 | 85.7028 | 59.8258 | 3469.5512
2032-11-08 20:00 | 10015.1 | 3.1353 | 85.3748 | 59.8258 | 2935.1361
2032-11-09 21:00 | 8910.77 | 2.7235 | 85.499 | 59.8258 | 2611.4889
2032-11-10 22:00 | 7838.94 | 2.3845 | 85.2995 | 59.8258 | 2297.3665
2032-11-11 23:00 | 4635.58 | 1.3081 | 86.2125 | 59.8258 | 1358.5544
2032-11-13 | 3333.78 | 1 | 85.8177 | 59.8258 | 977.0345
2032-11-14 01:00 | 3192.37 | 1 | 92.7806 | 59.8258 | 935.5913
2032-11-15 02:00 | 3182.96 | 1 | 68.3347 | 59.8258 | 932.8335
2032-11-16 03:00 | 3142.31 | 1 | 68.1159 | 59.8258 | 920.9202
2032-11-17 04:00 | 3147.09 | 1 | 67.8797 | 59.8258 | 922.321
2032-11-18 05:00 | 3120.99 | 1 | 67.736 | 59.8258 | 914.6719
2032-11-19 06:00 | 3304.43 | 1 | 83.6951 | 59.8258 | 968.4328
2032-11-20 07:00 | 5574.95 | 1.7665 | 82.2056 | 59.8258 | 1633.8566
2032-11-21 08:00 | 6230.42 | 2.0456 | 81.9288 | 59.8258 | 1825.9559
2032-11-22 09:00 | 7637.48 | 2.6158 | 81.5253 | 59.8258 | 2238.3244
2032-11-23 10:00 | 9613.98 | 3.252 | 81.9306 | 59.8258 | 2817.5794
2032-11-24 11:00 | 11514.7 | 3.8414 | 82.5433 | 59.8258 | 3374.6254
2032-11-25 12:00 | 12394.1 | 4.0575 | 83.333 | 59.8258 | 3632.3521
2032-11-26 13:00 | 13531.4 | 4.314 | 84.1213 | 59.8258 | 3965.6619
2032-11-27 14:00 | 14496.5 | 4.6846 | 84.3583 | 59.8258 | 4248.5048
2032-11-28 15:00 | 14796.6 | 4.8576 | 84.5623 | 59.8258 | 4336.4554
2032-11-29 16:00 | 17387.4 | 5.4978 | 85.3883 | 59.8258 | 5095.7439
2032-11-30 17:00 | 17023.8 | 5.4249 | 85.8537 | 59.8258 | 4989.1833
2032-12-01 18:00 | 15778.5 | 5.024 | 86.233 | 59.8258 | 4624.2219
2032-12-02 19:00 | 13751.6 | 4.3061 | 86.5761 | 59.8258 | 4030.1961
2032-12-03 20:00 | 11770.6 | 3.6526 | 86.6101 | 59.8258 | 3449.6223
2032-12-04 21:00 | 10230.8 | 3.2082 | 86.2339 | 59.8258 | 2998.3515
2032-12-05 22:00 | 8966.35 | 2.7689 | 86.1406 | 59.8258 | 2627.7778
2032-12-06 23:00 | 6228.22 | 1.8134 | 86.726 | 59.8258 | 1825.3111
2032-12-08 | 5258.49 | 1.4929 | 86.5833 | 59.8258 | 1541.1113
2032-12-09 01:00 | 4343.78 | 1.301 | 85.3036 | 59.8258 | 1273.0363
2032-12-10 02:00 | 3613.1 | 1.1275 | 84.3095 | 59.8258 | 1058.8951
2032-12-11 03:00 | 3433.69 | 1.0517 | 84.2265 | 59.8258 | 1006.3152
2032-12-12 04:00 | 3473.94 | 1.0809 | 83.6842 | 59.8258 | 1018.1113
2032-12-13 05:00 | 4191.29 | 1.321 | 83.292 | 59.8258 | 1228.3458
2032-12-14 06:00 | 5273.67 | 1.6549 | 83.2761 | 59.8258 | 1545.5601
2032-12-15 07:00 | 6538.31 | 2.1735 | 82.5105 | 59.8258 | 1916.1895
2032-12-16 08:00 | 7398.39 | 2.4432 | 82.7735 | 59.8258 | 2168.2541
2032-12-17 09:00 | 9117.36 | 3.0517 | 82.7688 | 59.8258 | 2672.0345
2032-12-18 10:00 | 11009.8 | 3.6642 | 83.1609 | 59.8258 | 3226.6539
2032-12-19 11:00 | 12740.2 | 4.2145 | 83.6862 | 59.8258 | 3733.784
2032-12-20 12:00 | 14226.4 | 4.5904 | 84.5235 | 59.8258 | 4169.3463
2032-12-21 13:00 | 15118.1 | 4.858 | 85.0837 | 59.8258 | 4430.6777
2032-12-22 14:00 | 15603.1 | 5.15 | 85.1692 | 59.8258 | 4572.8172
2032-12-23 15:00 | 17631.7 | 5.4925 | 86.3672 | 59.8258 | 5167.3412
2032-12-24 16:00 | 17866.4 | 5.5432 | 86.9553 | 59.8258 | 5236.125
2032-12-25 17:00 | 17048.9 | 5.3946 | 87.0646 | 59.8258 | 4996.5394
2032-12-26 18:00 | 15177.6 | 4.7627 | 87.3609 | 59.8258 | 4448.1155
2032-12-27 19:00 | 13343.8 | 4.1834 | 87.3185 | 59.8258 | 3910.6817
2032-12-28 20:00 | 10895 | 3.3839 | 87.2877 | 59.8258 | 3193.0093
2032-12-29 21:00 | 9219.18 | 2.9015 | 86.707 | 59.8258 | 2701.8749
2032-12-30 22:00 | 6877.34 | 2.0756 | 86.9053 | 59.8258 | 2015.5494
2032-12-31 23:00 | 6213.9 | 1.8653 | 86.4424 | 59.8258 | 1821.1143
2033-01-02 | 5307.22 | 1.5798 | 86.1641 | 59.8258 | 1555.3926
2033-01-03 01:00 | 4584.98 | 1.3876 | 85.5374 | 59.8258 | 1343.725
2033-01-04 02:00 | 4049.81 | 1.2317 | 85.1184 | 59.8258 | 1186.8821
2033-01-05 03:00 | 3870 | 1.2106 | 84.3701 | 59.8258 | 1134.185
2033-01-06 04:00 | 4224.7 | 1.3248 | 84.0839 | 59.8258 | 1238.1373
2033-01-07 05:00 | 4970.57 | 1.5527 | 83.9823 | 59.8258 | 1456.7303
2033-01-08 06:00 | 5473.1 | 1.7103 | 83.9411 | 59.8258 | 1604.0073
2033-01-09 07:00 | 6637.28 | 2.1832 | 83.2056 | 59.8258 | 1945.1948
2033-01-10 08:00 | 7039.37 | 2.2363 | 83.834 | 59.8258 | 2063.0357
2033-01-11 09:00 | 9191.75 | 2.9402 | 83.8389 | 59.8258 | 2693.836
2033-01-12 10:00 | 10877 | 3.5484 | 83.8958 | 59.8258 | 3187.734
2033-01-13 11:00 | 12642.6 | 4.1309 | 84.2751 | 59.8258 | 3705.1803
2033-01-14 12:00 | 13928.1 | 4.4284 | 85.1225 | 59.8258 | 4081.9232
2033-01-15 13:00 | 14293.6 | 4.6932 | 85.1215 | 59.8258 | 4189.0406
2033-01-16 14:00 | 15657.1 | 5.0599 | 85.7012 | 59.8258 | 4588.6431
2033-01-17 15:00 | 17244.8 | 5.5094 | 86.2762 | 59.8258 | 5053.952
2033-01-18 16:00 | 17400.3 | 5.4438 | 87.071 | 59.8258 | 5099.5245
2033-01-19 17:00 | 17652.9 | 5.4726 | 87.538 | 59.8258 | 5173.5543
2033-01-20 18:00 | 15716 | 4.8713 | 87.8385 | 59.8258 | 4605.9049
2033-01-21 19:00 | 12970.9 | 4.1294 | 87.4672 | 59.8258 | 3801.3955
2033-01-22 20:00 | 10066.2 | 3.1614 | 87.399 | 59.8258 | 2950.112
2033-01-23 21:00 | 9065.64 | 2.7791 | 87.2628 | 59.8258 | 2656.8768
2033-01-24 22:00 | 7261.22 | 2.2062 | 87.0281 | 59.8258 | 2128.0535
2033-01-25 23:00 | 6723.29 | 2.0388 | 86.5828 | 59.8258 | 1970.4018
2033-01-27 | 5941.35 | 1.801 | 86.2194 | 59.8258 | 1741.2378
2033-01-28 01:00 | 5549.48 | 1.6377 | 86.3091 | 59.8258 | 1626.392
2033-01-29 02:00 | 5145.68 | 1.517 | 86.0668 | 59.8258 | 1508.0499
2033-01-30 03:00 | 4871.39 | 1.5237 | 84.9265 | 59.8258 | 1427.6635
2033-01-31 04:00 | 5062.43 | 1.5684 | 84.8504 | 59.8258 | 1483.6518
2033-02-01 05:00 | 5751.22 | 1.8067 | 84.4852 | 59.8258 | 1685.5162
2033-02-02 06:00 | 6205.88 | 1.9823 | 84.2063 | 59.8258 | 1818.7639
2033-02-03 07:00 | 7226.3 | 2.3492 | 83.9609 | 59.8258 | 2117.8195
2033-02-04 08:00 | 7389.94 | 2.3221 | 84.5798 | 59.8258 | 2165.7776
2033-02-05 09:00 | 8738.08 | 2.9154 | 83.8059 | 59.8258 | 2560.8785
2033-02-06 10:00 | 9978.05 | 3.2482 | 84.3593 | 59.8258 | 2924.2778
2033-02-07 11:00 | 11865.4 | 3.9223 | 84.4116 | 59.8258 | 3477.4055
2033-02-08 12:00 | 12650.9 | 4.1015 | 85.0796 | 59.8258 | 3707.6128
2033-02-09 13:00 | 12439.1 | 3.9388 | 85.7485 | 59.8258 | 3645.5403
2033-02-10 14:00 | 12752.5 | 3.9227 | 86.3535 | 59.8258 | 3737.3888
2033-02-11 15:00 | 13918.2 | 4.5416 | 85.6618 | 59.8258 | 4079.0218
2033-02-12 16:00 | 14693.5 | 4.7566 | 86.0492 | 59.8258 | 4306.2398
2033-02-13 17:00 | 14469.9 | 4.5585 | 86.6974 | 59.8258 | 4240.7091
2033-02-14 18:00 | 13381.2 | 4.0627 | 87.3878 | 59.8258 | 3921.6426
2033-02-15 19:00 | 12028.6 | 3.6791 | 87.2787 | 59.8258 | 3525.2347
2033-02-16 20:00 | 9748.4 | 2.9567 | 87.3171 | 59.8258 | 2856.974
2033-02-17 21:00 | 9012.55 | 2.7499 | 86.9057 | 59.8258 | 2641.3177
2033-02-18 22:00 | 7046.15 | 2.0392 | 87.4666 | 59.8258 | 2065.0227
2033-02-19 23:00 | 6067.6 | 1.8085 | 86.5971 | 59.8258 | 1778.238
2033-02-21 | 4764.78 | 1.4174 | 86.2495 | 59.8258 | 1396.4192
2033-02-22 01:00 | 4058.8 | 1.253 | 85.2918 | 59.8258 | 1189.5169
2033-02-23 02:00 | 3595.09 | 1.12 | 84.8232 | 59.8258 | 1053.6169
2033-02-24 03:00 | 3776.68 | 1.1783 | 84.4898 | 59.8258 | 1106.8356
2033-02-25 04:00 | 4003.47 | 1.251 | 84.2652 | 59.8258 | 1173.3012
2033-02-26 05:00 | 5181.72 | 1.6144 | 84.1556 | 59.8258 | 1518.6122
2033-02-27 06:00 | 5474.67 | 1.7128 | 84.1238 | 59.8258 | 1604.4674
2033-02-28 07:00 | 6168.71 | 1.9206 | 84.2063 | 59.8258 | 1807.8704
2033-03-01 08:00 | 5584.14 | 1.6695 | 84.9013 | 59.8258 | 1636.5499
2033-03-02 09:00 | 5692.94 | 1.7976 | 84.0293 | 59.8258 | 1668.436
2033-03-03 10:00 | 6551.31 | 2.214 | 83.0437 | 59.8258 | 1919.9994
2033-03-04 11:00 | 8463.82 | 2.8453 | 83.1695 | 59.8258 | 2480.5008
2033-03-05 12:00 | 9320.38 | 3.1111 | 83.5311 | 59.8258 | 2731.5337
2033-03-06 13:00 | 10054.4 | 3.3849 | 83.6496 | 59.8258 | 2946.6538
2033-03-07 14:00 | 10838.8 | 3.5201 | 84.3782 | 59.8258 | 3176.5387
2033-03-08 15:00 | 12601.6 | 4.1616 | 84.3905 | 59.8258 | 3693.1644
2033-03-09 16:00 | 13279 | 4.3815 | 84.7922 | 59.8258 | 3891.6907
2033-03-10 17:00 | 12685.1 | 4.0621 | 85.5184 | 59.8258 | 3717.6358
2033-03-11 18:00 | 11425.9 | 3.5856 | 85.9301 | 59.8258 | 3348.6007
2033-03-12 19:00 | 10561.4 | 3.2326 | 86.2504 | 59.8258 | 3095.2408
2033-03-13 20:00 | 8207.33 | 2.5462 | 85.9986 | 59.8258 | 2405.331
2033-03-14 21:00 | 7625.26 | 2.2463 | 86.4611 | 59.8258 | 2234.7431
2033-03-15 22:00 | 5956.91 | 1.6854 | 86.8616 | 59.8258 | 1745.798
2033-03-16 23:00 | 5227.57 | 1.4927 | 86.3637 | 59.8258 | 1532.0495
2033-03-18 | 4599.37 | 1.3584 | 85.5283 | 59.8258 | 1347.9423
2033-03-19 01:00 | 4023.71 | 1.2835 | 84.1103 | 59.8258 | 1179.233
2033-03-20 02:00 | 3800.39 | 1.1954 | 84.0705 | 59.8258 | 1113.7844
2033-03-21 03:00 | 4069.84 | 1.2658 | 84.0052 | 59.8258 | 1192.7524
2033-03-22 04:00 | 4306.57 | 1.3337 | 83.9369 | 59.8258 | 1262.1311
2033-03-23 05:00 | 5257.74 | 1.7037 | 83.1871 | 59.8258 | 1540.8915
2033-03-24 06:00 | 5560.25 | 1.8065 | 83.1872 | 59.8258 | 1629.5484
2033-03-25 07:00 | 5827.04 | 1.7709 | 84.1875 | 59.8258 | 1707.7368
2033-03-26 08:00 | 4759.72 | 1.4593 | 84.1093 | 59.8258 | 1394.9362
2033-03-27 09:00 | 5965.26 | 1.9573 | 82.9977 | 59.8258 | 1748.2451
2033-03-28 10:00 | 6368.85 | 2.0567 | 83.3084 | 59.8258 | 1866.5257
2033-03-29 11:00 | 6871.5 | 2.1936 | 83.5458 | 59.8258 | 2013.8379
2033-03-30 12:00 | 6794.46 | 2.1792 | 83.549 | 59.8258 | 1991.2597
2033-03-31 13:00 | 6950.24 | 2.1723 | 83.9338 | 59.8258 | 2036.9143
2033-04-01 14:00 | 8050.13 | 2.6314 | 83.3289 | 59.8258 | 2359.2602
2033-04-02 15:00 | 9434.25 | 3.116 | 83.3152 | 59.8258 | 2764.9057
2033-04-03 16:00 | 9906.03 | 3.2071 | 83.8301 | 59.8258 | 2903.1708
2033-04-04 17:00 | 10134.6 | 3.1665 | 84.508 | 59.8258 | 2970.1581
2033-04-05 18:00 | 9112.12 | 2.8572 | 84.5995 | 59.8258 | 2670.4988
2033-04-06 19:00 | 8475.16 | 2.5994 | 84.9058 | 59.8258 | 2483.8242
2033-04-07 20:00 | 6703.56 | 1.9069 | 86.0331 | 59.8258 | 1964.6195
2033-04-08 21:00 | 5888.18 | 1.7676 | 84.9409 | 59.8258 | 1725.6552
2033-04-09 22:00 | 4133.86 | 1.1998 | 85.2389 | 59.8258 | 1211.5148
2033-04-10 23:00 | 3213.98 | 1 | 85.916 | 59.8258 | 941.9246
2033-04-12 | 3193.46 | 1 | 88.0367 | 59.8258 | 935.9107
2033-04-13 01:00 | 3183.6 | 1 | 89.4875 | 59.8258 | 933.0211
2033-04-14 02:00 | 3132.39 | 1 | 90.0446 | 59.8258 | 918.0129
2033-04-15 03:00 | 3178.64 | 1 | 92.3366 | 59.8258 | 931.5674
2033-04-16 04:00 | 3168.92 | 1 | 93.5391 | 59.8258 | 928.7188
2033-04-17 05:00 | 3204.8 | 1 | 92.4329 | 59.8258 | 939.2342
2033-04-18 06:00 | 4409.61 | 1.3993 | 82.3893 | 59.8258 | 1292.3291
2033-04-19 07:00 | 5539.61 | 1.9243 | 81.2348 | 59.8258 | 1623.4994
2033-04-20 08:00 | 5150.35 | 1.5351 | 83.6036 | 59.8258 | 1509.4186
2033-04-21 09:00 | 5992.83 | 1.9027 | 82.6831 | 59.8258 | 1756.3251
2033-04-22 10:00 | 7168.35 | 2.3801 | 82.1855 | 59.8258 | 2100.836
2033-04-23 11:00 | 9060.95 | 3.0973 | 82.0427 | 59.8258 | 2655.5023
2033-04-24 12:00 | 10313.6 | 3.4677 | 82.6509 | 59.8258 | 3022.6178
2033-04-25 13:00 | 11305.7 | 3.6267 | 83.6836 | 59.8258 | 3313.3736
2033-04-26 14:00 | 12182.8 | 3.9243 | 83.9994 | 59.8258 | 3570.4262
2033-04-27 15:00 | 12720.7 | 4.2445 | 83.8698 | 59.8258 | 3728.0692
2033-04-28 16:00 | 15692.9 | 5.177 | 84.3346 | 59.8258 | 4599.135
2033-04-29 17:00 | 15384 | 4.8809 | 85.5098 | 59.8258 | 4508.6053
2033-04-30 18:00 | 14248.3 | 4.3517 | 86.4379 | 59.8258 | 4175.7645
2033-05-01 19:00 | 12097.8 | 3.759 | 86.2945 | 59.8258 | 3545.5152
2033-05-02 20:00 | 10568.7 | 3.2315 | 86.4332 | 59.8258 | 3097.3802
2033-05-03 21:00 | 8962.07 | 2.8525 | 85.685 | 59.8258 | 2626.5234
2033-05-04 22:00 | 8372.12 | 2.5183 | 86.2359 | 59.8258 | 2453.6262
2033-05-05 23:00 | 5449.66 | 1.4933 | 87.5028 | 59.8258 | 1597.1377
2033-05-07 | 4023.55 | 1.2691 | 84.7953 | 59.8258 | 1179.1861
2033-05-08 01:00 | 3464.82 | 1.0361 | 85.1028 | 59.8258 | 1015.4385
2033-05-09 02:00 | 3324.43 | 1 | 86.365 | 59.8258 | 974.2943
2033-05-10 03:00 | 3277.34 | 1 | 87.1985 | 59.8258 | 960.4935
2033-05-11 04:00 | 3025.59 | 1 | 87.2943 | 59.8258 | 886.7129
2033-05-12 05:00 | 3219.55 | 1 | 90.9458 | 59.8258 | 943.557
2033-05-13 06:00 | 5163.09 | 1.5844 | 83.412 | 59.8258 | 1513.1523
2033-05-14 07:00 | 6757.81 | 2.3175 | 81.993 | 59.8258 | 1980.5186
2033-05-15 08:00 | 7336.62 | 2.3119 | 83.4338 | 59.8258 | 2150.1511
2033-05-16 09:00 | 8561.01 | 2.88 | 82.7006 | 59.8258 | 2508.9844
2033-05-17 10:00 | 10434.1 | 3.5039 | 82.9912 | 59.8258 | 3057.9329
2033-05-18 11:00 | 12232.8 | 4.0499 | 83.6298 | 59.8258 | 3585.0798
2033-05-19 12:00 | 13596.5 | 4.3891 | 84.4875 | 59.8258 | 3984.7408
2033-05-20 13:00 | 14456.6 | 4.5422 | 85.3657 | 59.8258 | 4236.8112
2033-05-21 14:00 | 14639.4 | 4.8083 | 85.1851 | 59.8258 | 4290.3846
2033-05-22 15:00 | 15607.4 | 5.0063 | 85.8586 | 59.8258 | 4574.0774
2033-05-23 16:00 | 18346.5 | 5.7519 | 86.5485 | 59.8258 | 5376.8284
2033-05-24 17:00 | 17434.3 | 5.3936 | 87.3939 | 59.8258 | 5109.489
2033-05-25 18:00 | 16139.8 | 5.0621 | 87.4911 | 59.8258 | 4730.1085
2033-05-26 19:00 | 14277.7 | 4.3578 | 87.9561 | 59.8258 | 4184.3808
2033-05-27 20:00 | 12929.7 | 3.8757 | 88.1481 | 59.8258 | 3789.321
2033-05-28 21:00 | 11608.7 | 3.525 | 87.8155 | 59.8258 | 3402.1741
2033-05-29 22:00 | 10558.1 | 3.2418 | 87.4019 | 59.8258 | 3094.2737
2033-05-30 23:00 | 8033.23 | 2.2954 | 88.2714 | 59.8258 | 2354.3073
2033-06-01 | 7042.81 | 2.0947 | 87.1808 | 59.8258 | 2064.0439
2033-06-02 01:00 | 6516.48 | 2.0029 | 86.3039 | 59.8258 | 1909.7918
2033-06-03 02:00 | 5918.68 | 1.8683 | 85.6341 | 59.8258 | 1734.5939
2033-06-04 03:00 | 5858.52 | 1.863 | 85.2465 | 59.8258 | 1716.9627
2033-06-05 04:00 | 6118.9 | 1.8893 | 85.4314 | 59.8258 | 1793.2726
2033-06-06 05:00 | 6789.27 | 2.2088 | 84.5547 | 59.8258 | 1989.7386
2033-06-07 06:00 | 7620.74 | 2.5418 | 84.1875 | 59.8258 | 2233.4184
2033-06-08 07:00 | 9149.62 | 3.0324 | 84.333 | 59.8258 | 2681.4889
2033-06-09 08:00 | 10051 | 3.2396 | 84.9483 | 59.8258 | 2945.6573
2033-06-10 09:00 | 12033.6 | 3.9231 | 85.0211 | 59.8258 | 3526.7
2033-06-11 10:00 | 14316.5 | 4.4539 | 86.0812 | 59.8258 | 4195.752
2033-06-12 11:00 | 14975.9 | 4.9343 | 85.8177 | 59.8258 | 4389.003
2033-06-13 12:00 | 16735.2 | 5.2857 | 86.8406 | 59.8258 | 4904.603
2033-06-14 13:00 | 16820.3 | 5.3726 | 87.1947 | 59.8258 | 4929.5433
2033-06-15 14:00 | 18307.6 | 5.5228 | 88.4157 | 59.8258 | 5365.4279
2033-06-16 15:00 | 18880.5 | 5.8172 | 88.5655 | 59.8258 | 5533.3283
2033-06-17 16:00 | 15968.4 | 5.1254 | 88.3645 | 59.8258 | 4679.8761
2033-06-18 17:00 | 14489.3 | 4.7016 | 88.1006 | 59.8258 | 4246.3947
2033-06-19 18:00 | 12883 | 4.083 | 88.2337 | 59.8258 | 3775.6346
2033-06-20 19:00 | 11821.6 | 3.5919 | 88.614 | 59.8258 | 3464.569
2033-06-21 20:00 | 9191.72 | 2.8314 | 88.1467 | 59.8258 | 2693.8272
2033-06-22 21:00 | 8301.14 | 2.5262 | 87.794 | 59.8258 | 2432.824
2033-06-23 22:00 | 6384 | 1.8424 | 88.1981 | 59.8258 | 1870.9657
2033-06-24 23:00 | 5491.5 | 1.6617 | 86.9788 | 59.8258 | 1609.3998
2033-06-26 | 4962.85 | 1.4391 | 87.1952 | 59.8258 | 1454.4678
2033-06-27 01:00 | 4253.41 | 1.3011 | 86.0072 | 59.8258 | 1246.5514
2033-06-28 02:00 | 3850.44 | 1.2178 | 85.1621 | 59.8258 | 1128.4526
2033-06-29 03:00 | 4106.04 | 1.2784 | 85.0487 | 59.8258 | 1203.3615
2033-06-30 04:00 | 4213.79 | 1.3143 | 84.8381 | 59.8258 | 1234.9399
2033-07-01 05:00 | 5039.82 | 1.6129 | 84.3256 | 59.8258 | 1477.0254
2033-07-02 06:00 | 5451.27 | 1.7167 | 84.5337 | 59.8258 | 1597.6095
2033-07-03 07:00 | 6431.82 | 2.149 | 83.6922 | 59.8258 | 1884.9804
2033-07-04 08:00 | 7272.39 | 2.3514 | 84.258 | 59.8258 | 2131.3271
2033-07-05 09:00 | 9172.81 | 3.0621 | 83.9476 | 59.8258 | 2688.2852
2033-07-06 10:00 | 11097.7 | 3.6415 | 84.4968 | 59.8258 | 3252.4148
2033-07-07 11:00 | 13126.8 | 4.2626 | 85.0586 | 59.8258 | 3847.0853
2033-07-08 12:00 | 14239.6 | 4.6464 | 85.4955 | 59.8258 | 4173.2148
2033-07-09 13:00 | 14867 | 4.8886 | 85.8481 | 59.8258 | 4357.0876
2033-07-10 14:00 | 15816 | 5.0669 | 86.6003 | 59.8258 | 4635.212
2033-07-11 15:00 | 17738.7 | 5.5215 | 87.3969 | 59.8258 | 5198.6998
2033-07-12 16:00 | 17980.6 | 5.6423 | 87.8152 | 59.8258 | 5269.5937
2033-07-13 17:00 | 18148.5 | 5.585 | 88.4875 | 59.8258 | 5318.8003
2033-07-14 18:00 | 16642 | 5.1422 | 88.7494 | 59.8258 | 4877.2887
2033-07-15 19:00 | 14201 | 4.4348 | 88.686 | 59.8258 | 4161.9023
2033-07-16 20:00 | 11560.3 | 3.5145 | 88.9167 | 59.8258 | 3387.9895
2033-07-17 21:00 | 9900.68 | 3.0501 | 88.3219 | 59.8258 | 2901.6029
2033-07-18 22:00 | 7966.89 | 2.3519 | 88.5716 | 59.8258 | 2334.865
2033-07-19 23:00 | 7508.78 | 2.2276 | 88.0005 | 59.8258 | 2200.6062
2033-07-21 | 7220.96 | 2.1661 | 87.4686 | 59.8258 | 2116.2545
2033-07-22 01:00 | 6014.38 | 1.9168 | 86.3241 | 59.8258 | 1762.6408
2033-07-23 02:00 | 6003.52 | 1.6753 | 88.0277 | 59.8258 | 1759.458
2033-07-24 03:00 | 5365.44 | 1.6971 | 85.8567 | 59.8258 | 1572.4552
2033-07-25 04:00 | 5451.31 | 1.7056 | 85.7706 | 59.8258 | 1597.6213
2033-07-26 05:00 | 6082.7 | 1.963 | 85.1235 | 59.8258 | 1782.6634
2033-07-27 06:00 | 6238.92 | 2.0207 | 84.9945 | 59.8258 | 1828.447
2033-07-28 07:00 | 7226.18 | 2.3825 | 84.6861 | 59.8258 | 2117.7843
2033-07-29 08:00 | 8175.44 | 2.5292 | 85.6651 | 59.8258 | 2395.9849
2033-07-30 09:00 | 9827.29 | 3.1698 | 85.207 | 59.8258 | 2880.0944
2033-07-31 10:00 | 11880.6 | 3.8108 | 85.5683 | 59.8258 | 3481.8602
2033-08-01 11:00 | 13104.7 | 4.2226 | 85.9149 | 59.8258 | 3840.6085
2033-08-02 12:00 | 14391.7 | 4.5077 | 86.7132 | 59.8258 | 4217.7909
2033-08-03 13:00 | 14975 | 4.7483 | 86.9504 | 59.8258 | 4388.7393
2033-08-04 14:00 | 14703.8 | 4.9695 | 86.4111 | 59.8258 | 4309.2584
2033-08-05 15:00 | 15596.7 | 5.2458 | 86.6636 | 59.8258 | 4570.9416
2033-08-06 16:00 | 16364.6 | 5.2224 | 87.6534 | 59.8258 | 4795.9908
2033-08-07 17:00 | 16538 | 5.2724 | 87.959 | 59.8258 | 4846.8094
2033-08-08 18:00 | 14637.2 | 4.6083 | 88.3773 | 59.8258 | 4289.7399
2033-08-09 19:00 | 13702.1 | 4.1107 | 89.0295 | 59.8258 | 4015.6891
2033-08-10 20:00 | 10590.3 | 3.2568 | 88.5991 | 59.8258 | 3103.7106
2033-08-11 21:00 | 9042.97 | 2.7737 | 88.2445 | 59.8258 | 2650.2329
2033-08-12 22:00 | 6797.34 | 2.0104 | 88.3802 | 59.8258 | 1992.1037
2033-08-13 23:00 | 5895.25 | 1.756 | 87.7286 | 59.8258 | 1727.7272
2033-08-15 | 5450.96 | 1.6361 | 87.1614 | 59.8258 | 1597.5187
2033-08-16 01:00 | 5205.86 | 1.5203 | 87.2248 | 59.8258 | 1525.687
2033-08-17 02:00 | 4672.41 | 1.444 | 86.1022 | 59.8258 | 1369.3482
2033-08-18 03:00 | 4690.02 | 1.4377 | 85.9469 | 59.8258 | 1374.5092
2033-08-19 04:00 | 4866.61 | 1.5478 | 85.2121 | 59.8258 | 1426.2626
2033-08-20 05:00 | 5512.67 | 1.8734 | 84.1478 | 59.8258 | 1615.6041
2033-08-21 06:00 | 6609.26 | 2.1711 | 84.5701 | 59.8258 | 1936.9829
2033-08-22 07:00 | 7848.5 | 2.5078 | 85.0271 | 59.8258 | 2300.1683
2033-08-23 08:00 | 8028.95 | 2.5606 | 85.2495 | 59.8258 | 2353.053
2033-08-24 09:00 | 9835.95 | 3.1625 | 85.2376 | 59.8258 | 2882.6324
2033-08-25 10:00 | 11237.5 | 3.755 | 85.0023 | 59.8258 | 3293.3861
2033-08-26 11:00 | 12408.6 | 3.9836 | 85.9242 | 59.8258 | 3636.6017
2033-08-27 12:00 | 13063.4 | 4.2823 | 85.9793 | 59.8258 | 3828.5046
2033-08-28 13:00 | 13470.6 | 4.3382 | 86.5228 | 59.8258 | 3947.8432
2033-08-29 14:00 | 13787.4 | 4.4715 | 86.6953 | 59.8258 | 4040.6881
2033-08-30 15:00 | 15480 | 5.0551 | 86.8074 | 59.8258 | 4536.7402
2033-08-31 16:00 | 16200.2 | 5.1801 | 87.4731 | 59.8258 | 4747.8099
2033-09-01 17:00 | 16185.4 | 5.1681 | 87.8218 | 59.8258 | 4743.4725
2033-09-02 18:00 | 14780.7 | 4.6893 | 88.1399 | 59.8258 | 4331.7956
2033-09-03 19:00 | 12406.1 | 3.9218 | 88.1995 | 59.8258 | 3635.869
2033-09-04 20:00 | 9622.92 | 2.942 | 88.4761 | 59.8258 | 2820.1995
2033-09-05 21:00 | 8352.56 | 2.519 | 88.22 | 59.8258 | 2447.8937
2033-09-06 22:00 | 6307.67 | 1.8554 | 88.201 | 59.8258 | 1848.5956
2033-09-07 23:00 | 5395.13 | 1.5765 | 87.7834 | 59.8258 | 1581.1565
2033-09-09 | 5039.44 | 1.4978 | 87.0642 | 59.8258 | 1476.9141
2033-09-10 01:00 | 4375.31 | 1.3322 | 86.3726 | 59.8258 | 1282.2768
2033-09-11 02:00 | 4107.11 | 1.2798 | 85.7278 | 59.8258 | 1203.6751
2033-09-12 03:00 | 4043.57 | 1.2878 | 85.1334 | 59.8258 | 1185.0534
2033-09-13 04:00 | 4289.2 | 1.3581 | 85.0036 | 59.8258 | 1257.0404
2033-09-14 05:00 | 5283.77 | 1.6601 | 84.9587 | 59.8258 | 1548.5201
2033-09-15 06:00 | 6095.62 | 1.9959 | 84.3526 | 59.8258 | 1786.4499
2033-09-16 07:00 | 7614.47 | 2.4327 | 84.7546 | 59.8258 | 2231.5809
2033-09-17 08:00 | 7999.67 | 2.4426 | 85.6349 | 59.8258 | 2344.4718
2033-09-18 09:00 | 9266.42 | 2.9537 | 85.155 | 59.8258 | 2715.7196
2033-09-19 10:00 | 10736.5 | 3.552 | 84.881 | 59.8258 | 3146.5575
2033-09-20 11:00 | 11973.4 | 3.9471 | 85.2699 | 59.8258 | 3509.0571
2033-09-21 12:00 | 12466 | 3.9753 | 86.0964 | 59.8258 | 3653.424
2033-09-22 13:00 | 11680.2 | 3.7427 | 86.3063 | 59.8258 | 3423.1287
2033-09-23 14:00 | 12735.7 | 4.0026 | 86.6683 | 59.8258 | 3732.4652
2033-09-24 15:00 | 14432.4 | 4.697 | 86.3783 | 59.8258 | 4229.7189
2033-09-25 16:00 | 15726 | 5.0391 | 86.9689 | 59.8258 | 4608.8356
2033-09-26 17:00 | 15388.9 | 5.0603 | 86.9895 | 59.8258 | 4510.0414
2033-09-27 18:00 | 13802.4 | 4.4097 | 87.6063 | 59.8258 | 4045.0841
2033-09-28 19:00 | 11991.3 | 3.7414 | 87.9366 | 59.8258 | 3514.3031
2033-09-29 20:00 | 9509.01 | 2.9051 | 88.0963 | 59.8258 | 2786.8157
2033-09-30 21:00 | 8220.47 | 2.5181 | 87.6784 | 59.8258 | 2409.1819
2033-10-01 22:00 | 6423.71 | 1.899 | 87.8462 | 59.8258 | 1882.6036
2033-10-02 23:00 | 5563.42 | 1.6954 | 86.9237 | 59.8258 | 1630.4775
2033-10-04 | 5155.15 | 1.5752 | 86.4884 | 59.8258 | 1510.8253
2033-10-05 01:00 | 4921.36 | 1.5242 | 86.0006 | 59.8258 | 1442.3082
2033-10-06 02:00 | 4564.28 | 1.4033 | 85.893 | 59.8258 | 1337.6584
2033-10-07 03:00 | 4134.67 | 1.2086 | 86.4331 | 59.8258 | 1211.7522
2033-10-08 04:00 | 3689.67 | 1.108 | 85.7822 | 59.8258 | 1081.3355
2033-10-09 05:00 | 3487.22 | 1.0719 | 85.1865 | 59.8258 | 1022.0033
2033-10-10 06:00 | 5224.07 | 1.6706 | 84.3855 | 59.8258 | 1531.0238
2033-10-11 07:00 | 6181.22 | 2.0689 | 83.8056 | 59.8258 | 1811.5368
2033-10-12 08:00 | 5505.42 | 1.6373 | 85.6548 | 59.8258 | 1613.4793
2033-10-13 09:00 | 5663.13 | 1.8079 | 84.5324 | 59.8258 | 1659.6996
2033-10-14 10:00 | 5102.67 | 1.6348 | 84.4611 | 59.8258 | 1495.445
2033-10-15 11:00 | 5229.85 | 1.6887 | 84.2617 | 59.8258 | 1532.7177
2033-10-16 12:00 | 5494.03 | 1.712 | 84.6874 | 59.8258 | 1610.1413
2033-10-17 13:00 | 5366.51 | 1.7072 | 84.3327 | 59.8258 | 1572.7688
2033-10-18 14:00 | 5544.44 | 1.821 | 83.7995 | 59.8258 | 1624.915
2033-10-19 15:00 | 5766.79 | 1.9326 | 83.4448 | 59.8258 | 1690.0793
2033-10-20 16:00 | 9043.97 | 3.1648 | 82.8077 | 59.8258 | 2650.526
2033-10-21 17:00 | 8876.08 | 2.8079 | 84.5808 | 59.8258 | 2601.3223
2033-10-22 18:00 | 8082.61 | 2.5133 | 84.9916 | 59.8258 | 2368.7792
2033-10-23 19:00 | 6997.55 | 2.1551 | 85.0995 | 59.8258 | 2050.7795
2033-10-24 20:00 | 6065.75 | 1.8465 | 85.1743 | 59.8258 | 1777.6958
2033-10-25 21:00 | 5358.78 | 1.625 | 85.1017 | 59.8258 | 1570.5034
2033-10-26 22:00 | 4905.99 | 1.5216 | 84.5808 | 59.8258 | 1437.8037
2033-10-27 23:00 | 3123.95 | 1 | 69.4195 | 59.8258 | 915.5394
2033-10-29 | 3070.96 | 1 | 69.0904 | 59.8258 | 900.0095
2033-10-30 01:00 | 2597.78 | 1 | 68.934 | 59.8258 | 761.3342
2033-10-31 02:00 | 3206 | 1 | 68.7014 | 59.8258 | 939.5859
2033-11-01 03:00 | 3179.89 | 1 | 68.6553 | 59.8258 | 931.9338
2033-11-02 04:00 | 280.377 | 1 | 68.8213 | 59.8258 | 82.1704
2033-11-03 05:00 | 1434.23 | 1 | 68.2454 | 59.8258 | 420.3313
2033-11-04 06:00 | 1740.12 | 1 | 76.5752 | 59.8258 | 509.9788
2033-11-05 07:00 | 3195.87 | 1.2002 | 80.3255 | 59.8258 | 936.617
2033-11-06 08:00 | 2786.01 | 1 | 84.3222 | 59.8258 | 816.4989
2033-11-07 09:00 | 3963.29 | 1.2992 | 82.0792 | 59.8258 | 1161.5256
2033-11-08 10:00 | 5704.71 | 1.9504 | 81.627 | 59.8258 | 1671.8855
2033-11-09 11:00 | 6791.25 | 2.3204 | 81.929 | 59.8258 | 1990.3189
2033-11-10 12:00 | 7955.49 | 2.656 | 82.5299 | 59.8258 | 2331.524
2033-11-11 13:00 | 8921.85 | 2.9115 | 83.1451 | 59.8258 | 2614.7361
2033-11-12 14:00 | 10146.9 | 3.3164 | 83.4484 | 59.8258 | 2973.7628
2033-11-13 15:00 | 11200 | 3.6119 | 84.0006 | 59.8258 | 3282.396
2033-11-14 16:00 | 13604.5 | 4.5626 | 83.8219 | 59.8258 | 3987.0854
2033-11-15 17:00 | 12888.1 | 4.0684 | 85.2445 | 59.8258 | 3777.1293
2033-11-16 18:00 | 11410 | 3.5642 | 85.6833 | 59.8258 | 3343.9409
2033-11-17 19:00 | 9705.14 | 3.0645 | 85.5477 | 59.8258 | 2844.2958
2033-11-18 20:00 | 8889.67 | 2.6437 | 86.3308 | 59.8258 | 2605.3051
2033-11-19 21:00 | 8009.09 | 2.4017 | 86.1015 | 59.8258 | 2347.2326
2033-11-20 22:00 | 7475.7 | 2.2564 | 85.8238 | 59.8258 | 2190.9114
2033-11-21 23:00 | 4622.12 | 1.2744 | 87.1149 | 59.8258 | 1354.6097
2033-11-23 | 3613.96 | 1.1088 | 84.9768 | 59.8258 | 1059.1471
2033-11-24 01:00 | 3258.07 | 1 | 86.3282 | 59.8258 | 954.8461
2033-11-25 02:00 | 3197.83 | 1 | 88.4644 | 59.8258 | 937.1915
2033-11-26 03:00 | 3124.67 | 1 | 87.423 | 59.8258 | 915.7504
2033-11-27 04:00 | 3187.86 | 1 | 88.7422 | 59.8258 | 934.2695
2033-11-28 05:00 | 3265.68 | 1.0459 | 83.12 | 59.8258 | 957.0763
2033-11-29 06:00 | 3740.65 | 1.1852 | 83.1907 | 59.8258 | 1096.2763
2033-11-30 07:00 | 4864.83 | 1.5455 | 83.1249 | 59.8258 | 1425.7409
2033-12-01 08:00 | 5203.49 | 1.6635 | 83.1505 | 59.8258 | 1524.9924
2033-12-02 09:00 | 6737.47 | 2.3243 | 82.1779 | 59.8258 | 1974.5575
2033-12-03 10:00 | 8238.33 | 2.775 | 82.7196 | 59.8258 | 2414.4162
2033-12-04 11:00 | 9499.87 | 3.1385 | 83.3309 | 59.8258 | 2784.1371
2033-12-05 12:00 | 10436.4 | 3.3409 | 84.1473 | 59.8258 | 3058.6069
2033-12-06 13:00 | 11116.7 | 3.6046 | 84.3155 | 59.8258 | 3257.9832
2033-12-07 14:00 | 12333.9 | 3.9852 | 84.6955 | 59.8258 | 3614.7093
2033-12-08 15:00 | 13807.2 | 4.3614 | 85.3983 | 59.8258 | 4046.4909
2033-12-09 16:00 | 14357.9 | 4.6182 | 85.569 | 59.8258 | 4207.8851
2033-12-10 17:00 | 14113.8 | 4.55 | 85.8975 | 59.8258 | 4136.3465
2033-12-11 18:00 | 12711.8 | 3.9602 | 86.6288 | 59.8258 | 3725.4608
2033-12-12 19:00 | 10838.6 | 3.3243 | 86.8928 | 59.8258 | 3176.4801
2033-12-13 20:00 | 8093.17 | 2.422 | 87.1147 | 59.8258 | 2371.874
2033-12-14 21:00 | 6810.38 | 1.9968 | 87.0135 | 59.8258 | 1995.9254
2033-12-15 22:00 | 4457.86 | 1.248 | 87.363 | 59.8258 | 1306.4698
2033-12-16 23:00 | 3441.77 | 1.0575 | 85.3813 | 59.8258 | 1008.6832
2033-12-18 | 3210.11 | 1 | 88.9593 | 59.8258 | 940.7904
2033-12-19 01:00 | 3139.87 | 1 | 93.9305 | 59.8258 | 920.2051
2033-12-20 02:00 | 3072.87 | 1 | 69.2204 | 59.8258 | 900.5693
2033-12-21 03:00 | 3157.42 | 1 | 69.0027 | 59.8258 | 925.3485
2033-12-22 04:00 | 3154.27 | 1 | 68.8565 | 59.8258 | 924.4253
2033-12-23 05:00 | 3117.84 | 1 | 87.3408 | 59.8258 | 913.7487
2033-12-24 06:00 | 3377.58 | 1.0048 | 84.2283 | 59.8258 | 989.871
2033-12-25 07:00 | 4921.52 | 1.4858 | 83.9275 | 59.8258 | 1442.3551
2033-12-26 08:00 | 5643.53 | 1.8572 | 82.8281 | 59.8258 | 1653.9554
2033-12-27 09:00 | 7296.63 | 2.527 | 82.2831 | 59.8258 | 2138.4312
2033-12-28 10:00 | 9315.02 | 3.2127 | 82.6218 | 59.8258 | 2729.9629
2033-12-29 11:00 | 10605.2 | 3.549 | 83.4689 | 59.8258 | 3108.0773
2033-12-30 12:00 | 10971.9 | 3.6153 | 84.1177 | 59.8258 | 3215.5465
2033-12-31 13:00 | 11018.7 | 3.645 | 84.3682 | 59.8258 | 3229.2622
2034-01-01 14:00 | 11706.3 | 3.8002 | 84.8453 | 59.8258 | 3430.7779
2034-01-02 15:00 | 13701.9 | 4.4028 | 85.2224 | 59.8258 | 4015.6305
2034-01-03 16:00 | 14643.4 | 4.6094 | 85.9314 | 59.8258 | 4291.5569
2034-01-04 17:00 | 14380.7 | 4.5936 | 86.1067 | 59.8258 | 4214.5671
2034-01-05 18:00 | 12757 | 4.0388 | 86.4758 | 59.8258 | 3738.7076
2034-01-06 19:00 | 10979.1 | 3.4021 | 86.7921 | 59.8258 | 3217.6566
2034-01-07 20:00 | 8134.86 | 2.4325 | 87.1939 | 59.8258 | 2384.0921
2034-01-08 21:00 | 6745.31 | 1.9986 | 86.9108 | 59.8258 | 1976.8552
2034-01-09 22:00 | 4328.92 | 1.2417 | 87.0093 | 59.8258 | 1268.6812
2034-01-10 23:00 | 3295.18 | 1 | 86.0235 | 59.8258 | 965.7219
2034-01-12 | 3162.18 | 1 | 91.1017 | 59.8258 | 926.7435
2034-01-13 01:00 | 3231.03 | 1 | 69.435 | 59.8258 | 946.9214
2034-01-14 02:00 | 3056.39 | 1 | 69.252 | 59.8258 | 895.7395
2034-01-15 03:00 | 3145.05 | 1 | 69.0229 | 59.8258 | 921.7232
2034-01-16 04:00 | 3158.27 | 1 | 68.8655 | 59.8258 | 925.5976
2034-01-17 05:00 | 3148.07 | 1 | 68.739 | 59.8258 | 922.6082
2034-01-18 06:00 | 3307.03 | 1 | 86.4292 | 59.8258 | 969.1948
2034-01-19 07:00 | 3769.64 | 1.1071 | 84.349 | 59.8258 | 1104.7724
2034-01-20 08:00 | 4346.48 | 1.3738 | 83.2437 | 59.8258 | 1273.8275
2034-01-21 09:00 | 6747.99 | 2.2368 | 82.6013 | 59.8258 | 1977.6406
2034-01-22 10:00 | 8248.07 | 2.8755 | 82.2454 | 59.8258 | 2417.2707
2034-01-23 11:00 | 9817.62 | 3.2694 | 83.2284 | 59.8258 | 2877.2604
2034-01-24 12:00 | 10512.2 | 3.4688 | 83.7631 | 59.8258 | 3080.8217
2034-01-25 13:00 | 11171.9 | 3.6292 | 84.3309 | 59.8258 | 3274.1607
2034-01-26 14:00 | 12338.3 | 3.9266 | 84.9465 | 59.8258 | 3615.9988
2034-01-27 15:00 | 13530.5 | 4.3052 | 85.2973 | 59.8258 | 3965.3981
2034-01-28 16:00 | 13191.3 | 4.1373 | 85.8879 | 59.8258 | 3865.9884
2034-01-29 17:00 | 13558.3 | 4.271 | 86.0167 | 59.8258 | 3973.5455
2034-01-30 18:00 | 12012.9 | 3.7151 | 86.5153 | 59.8258 | 3520.6335
2034-01-31 19:00 | 10283.1 | 3.1889 | 86.4835 | 59.8258 | 3013.6791
2034-02-01 20:00 | 8057.93 | 2.4433 | 86.6636 | 59.8258 | 2361.5462
2034-02-02 21:00 | 6982.22 | 2.0424 | 86.8619 | 59.8258 | 2046.2867
2034-02-03 22:00 | 4697.84 | 1.3653 | 86.6693 | 59.8258 | 1376.801
2034-02-04 23:00 | 3707.21 | 1.1351 | 85.3815 | 59.8258 | 1086.476
2034-02-06 | 3156.47 | 1 | 87.3253 | 59.8258 | 925.07
2034-02-07 01:00 | 3206.46 | 1 | 93.9309 | 59.8258 | 939.7207
2034-02-08 02:00 | 3202.57 | 1 | 69.1803 | 59.8258 | 938.5806
2034-02-09 03:00 | 3129.49 | 1 | 94.7214 | 59.8258 | 917.163
2034-02-10 04:00 | 3153.56 | 1 | 92.2365 | 59.8258 | 924.2172
2034-02-11 05:00 | 3201.54 | 1 | 85.1616 | 59.8258 | 938.2788
2034-02-12 06:00 | 4103.01 | 1.2656 | 83.6896 | 59.8258 | 1202.4735
2034-02-13 07:00 | 5582.16 | 1.8239 | 82.8888 | 59.8258 | 1635.9696
2034-02-14 08:00 | 6228.78 | 2.0282 | 83.1373 | 59.8258 | 1825.4752
2034-02-15 09:00 | 8034.43 | 2.651 | 83.1103 | 59.8258 | 2354.659
2034-02-16 10:00 | 9728.84 | 3.2663 | 83.1965 | 59.8258 | 2851.2415
2034-02-17 11:00 | 11163.6 | 3.7662 | 83.5567 | 59.8258 | 3271.7282
2034-02-18 12:00 | 12593 | 3.947 | 85.0321 | 59.8258 | 3690.644
2034-02-19 13:00 | 12939 | 4.1089 | 85.3017 | 59.8258 | 3792.0466
2034-02-20 14:00 | 13418 | 4.2998 | 85.5249 | 59.8258 | 3932.4276
2034-02-21 15:00 | 12712 | 3.9231 | 86.3705 | 59.8258 | 3725.5194
2034-02-22 16:00 | 11745.8 | 3.7777 | 85.8913 | 59.8258 | 3442.3542
2034-02-23 17:00 | 12079.7 | 3.7113 | 86.5295 | 59.8258 | 3540.2106
2034-02-24 18:00 | 10321.8 | 3.1631 | 86.6484 | 59.8258 | 3025.021
2034-02-25 19:00 | 9108.06 | 2.7672 | 86.6253 | 59.8258 | 2669.3089
2034-02-26 20:00 | 6974.37 | 2.0191 | 87.1507 | 59.8258 | 2043.9861
2034-02-27 21:00 | 6028.59 | 1.8019 | 86.2766 | 59.8258 | 1766.8053
2034-02-28 22:00 | 3571.26 | 1.0521 | 86.1903 | 59.8258 | 1046.633
2034-03-01 23:00 | 3244.54 | 1 | 89.011 | 59.8258 | 950.8808
2034-03-03 | 3159.93 | 1 | 69.4825 | 59.8258 | 926.0841
2034-03-04 01:00 | 3141.15 | 1 | 69.2233 | 59.8258 | 920.5802
2034-03-05 02:00 | 3187.04 | 1 | 69.0087 | 59.8258 | 934.0292
2034-03-06 03:00 | 3185.38 | 1 | 68.8387 | 59.8258 | 933.5427
2034-03-07 04:00 | 3229.56 | 1 | 93.0911 | 59.8258 | 946.4906
2034-03-08 05:00 | 3509.6 | 1.0934 | 83.5552 | 59.8258 | 1028.5622
2034-03-09 06:00 | 3494.32 | 1.0753 | 83.7071 | 59.8258 | 1024.0841
2034-03-10 07:00 | 4359.53 | 1.3535 | 83.5053 | 59.8258 | 1277.6521
2034-03-11 08:00 | 3765.78 | 1.1567 | 83.7271 | 59.8258 | 1103.6412
2034-03-12 09:00 | 5381.58 | 1.7386 | 82.9068 | 59.8258 | 1577.1854
2034-03-13 10:00 | 7153.56 | 2.4746 | 82.1188 | 59.8258 | 2096.5015
2034-03-14 11:00 | 9599.33 | 3.2444 | 82.725 | 59.8258 | 2813.2859
2034-03-15 12:00 | 10969 | 3.637 | 83.4517 | 59.8258 | 3214.6966
2034-03-16 13:00 | 12010.6 | 3.9166 | 84.1124 | 59.8258 | 3519.9594
2034-03-17 14:00 | 11819.5 | 3.669 | 85.2403 | 59.8258 | 3463.9535
2034-03-18 15:00 | 12855 | 4.2057 | 84.7285 | 59.8258 | 3767.4286
2034-03-19 16:00 | 12170 | 3.7196 | 86.0448 | 59.8258 | 3566.6749
2034-03-20 17:00 | 10150.4 | 3.2861 | 85.3375 | 59.8258 | 2974.7886
2034-03-21 18:00 | 9202.58 | 2.8105 | 86.0262 | 59.8258 | 2697.01
2034-03-22 19:00 | 8149.16 | 2.4384 | 86.1662 | 59.8258 | 2388.283
2034-03-23 20:00 | 6011.54 | 1.7131 | 86.7823 | 59.8258 | 1761.8085
2034-03-24 21:00 | 4965.33 | 1.4828 | 85.6673 | 59.8258 | 1455.1946
2034-03-25 22:00 | 3205.37 | 1 | 89.543 | 59.8258 | 939.4012
2034-03-26 23:00 | 3115.58 | 1 | 69.3234 | 59.8258 | 913.0864
2034-03-28 | 3018.97 | 1 | 69.0407 | 59.8258 | 884.7728
2034-03-29 01:00 | 0 | 0 | 69.0795 | 59.8258 | 0
2034-03-30 02:00 | 131.023 | 1 | 68.4807 | 59.8258 | 38.3991
2034-03-31 03:00 | 0 | 0 | 68.1103 | 59.8258 | 0
2034-04-01 04:00 | -219.265 | 1.0726 | 66.9178 | 59.8258 | -64.2602
2034-04-02 05:00 | -268.188 | 1.1656 | 66.5389 | 59.8258 | -78.5981
2034-04-03 06:00 | 1867.89 | 1 | 67.1842 | 59.8258 | 547.4245
2034-04-04 07:00 | 3008.45 | 1.0587 | 80.4906 | 59.8258 | 881.6897
2034-04-05 08:00 | 3367.72 | 1.0748 | 81.9782 | 59.8258 | 986.9813
2034-04-06 09:00 | 5095.97 | 1.7231 | 81.2574 | 59.8258 | 1493.4814
2034-04-07 10:00 | 7261.85 | 2.4722 | 81.4344 | 59.8258 | 2128.2381
2034-04-08 11:00 | 8931.69 | 3.0475 | 81.839 | 59.8258 | 2617.6199
2034-04-09 12:00 | 10488.8 | 3.4752 | 82.6591 | 59.8258 | 3073.9638
2034-04-10 13:00 | 11102.6 | 3.6176 | 83.3605 | 59.8258 | 3253.8509
2034-04-11 14:00 | 11991.9 | 3.8912 | 83.8137 | 59.8258 | 3514.479
2034-04-12 15:00 | 12883.6 | 4.1516 | 84.2935 | 59.8258 | 3775.8104
2034-04-13 16:00 | 15489.5 | 5.0639 | 84.4713 | 59.8258 | 4539.5243
2034-04-14 17:00 | 14605.3 | 4.6254 | 85.569 | 59.8258 | 4280.3909
2034-04-15 18:00 | 13205.5 | 4.0662 | 86.2831 | 59.8258 | 3870.15
2034-04-16 19:00 | 10934.7 | 3.4569 | 85.9613 | 59.8258 | 3204.6442
2034-04-17 20:00 | 9657.66 | 2.9219 | 86.4717 | 59.8258 | 2830.3807
2034-04-18 21:00 | 8465.59 | 2.5559 | 86.3368 | 59.8258 | 2481.0195
2034-04-19 22:00 | 7415.08 | 2.2635 | 85.9315 | 59.8258 | 2173.1454
2034-04-20 23:00 | 4372.62 | 1.2316 | 86.9287 | 59.8258 | 1281.4884
2034-04-22 | 3376.87 | 1 | 85.7965 | 59.8258 | 989.6629
2034-04-23 01:00 | 3164.14 | 1 | 88.3978 | 59.8258 | 927.3179
2034-04-24 02:00 | 3165.79 | 1 | 92.5207 | 59.8258 | 927.8015
2034-04-25 03:00 | 3271.65 | 1 | 68.9111 | 59.8258 | 958.826
2034-04-26 04:00 | 3193.38 | 1 | 68.7237 | 59.8258 | 935.8873
2034-04-27 05:00 | 3220.85 | 1 | 68.5795 | 59.8258 | 943.938
2034-04-28 06:00 | 3382 | 1.0319 | 83.7587 | 59.8258 | 991.1664
2034-04-29 07:00 | 5394 | 1.7446 | 82.7923 | 59.8258 | 1580.8254
2034-04-30 08:00 | 5996.07 | 1.8665 | 83.5519 | 59.8258 | 1757.2747
2034-05-01 09:00 | 7320.74 | 2.4351 | 82.7671 | 59.8258 | 2145.4971
2034-05-02 10:00 | 9340.52 | 3.1559 | 82.7829 | 59.8258 | 2737.4362
2034-05-03 11:00 | 11151.2 | 3.6452 | 83.6599 | 59.8258 | 3268.0941
2034-05-04 12:00 | 12220.3 | 4.0213 | 84.0731 | 59.8258 | 3581.4164
2034-05-05 13:00 | 13251.3 | 4.2445 | 84.8827 | 59.8258 | 3883.5727
2034-05-06 14:00 | 14120.9 | 4.5441 | 85.2442 | 59.8258 | 4138.4273
2034-05-07 15:00 | 14436.4 | 4.6565 | 85.6234 | 59.8258 | 4230.8912
2034-05-08 16:00 | 15902.5 | 5.1409 | 85.8968 | 59.8258 | 4660.5627
2034-05-09 17:00 | 14340 | 4.4953 | 86.7787 | 59.8258 | 4202.6391
2034-05-10 18:00 | 12053.2 | 3.7351 | 87.0712 | 59.8258 | 3532.4442
2034-05-11 19:00 | 10390.2 | 3.1156 | 87.3842 | 59.8258 | 3045.067
2034-05-12 20:00 | 8656.74 | 2.7099 | 86.5114 | 59.8258 | 2537.0401
2034-05-13 21:00 | 7982.28 | 2.378 | 86.9437 | 59.8258 | 2339.3753
2034-05-14 22:00 | 6931.4 | 2.1936 | 85.7578 | 59.8258 | 2031.3928
2034-05-15 23:00 | 4575.45 | 1.2516 | 87.7356 | 59.8258 | 1340.932
2034-05-17 | 3552.96 | 1.0728 | 85.6736 | 59.8258 | 1041.2698
2034-05-18 01:00 | 3197.41 | 1 | 87.1835 | 59.8258 | 937.0684
2034-05-19 02:00 | 3185.95 | 1 | 88.4995 | 59.8258 | 933.7098
2034-05-20 03:00 | 3217.79 | 1 | 87.7829 | 59.8258 | 943.0412
2034-05-21 04:00 | 3091.45 | 1 | 84.7378 | 59.8258 | 906.0146
2034-05-22 05:00 | 3692.67 | 1.1421 | 83.9685 | 59.8258 | 1082.2147
2034-05-23 06:00 | 4705.92 | 1.4495 | 83.9922 | 59.8258 | 1379.169
2034-05-24 07:00 | 5778.75 | 1.8736 | 83.33 | 59.8258 | 1693.5844
2034-05-25 08:00 | 6510.98 | 2.1222 | 83.4202 | 59.8258 | 1908.1799
2034-05-26 09:00 | 8437.93 | 2.8214 | 83.2199 | 59.8258 | 2472.9132
2034-05-27 10:00 | 10289.6 | 3.3536 | 83.9054 | 59.8258 | 3015.5841
2034-05-28 11:00 | 11615.2 | 3.8175 | 84.2335 | 59.8258 | 3404.0791
2034-05-29 12:00 | 13096 | 4.0939 | 85.3771 | 59.8258 | 3838.0587
2034-05-30 13:00 | 13047.2 | 4.2693 | 85.1936 | 59.8258 | 3823.7569
2034-05-31 14:00 | 13624.4 | 4.485 | 85.4167 | 59.8258 | 3992.9175
2034-06-01 15:00 | 14736.8 | 4.7483 | 86.0023 | 59.8258 | 4318.9297
2034-06-02 16:00 | 14710.8 | 4.6555 | 86.6114 | 59.8258 | 4311.3099
2034-06-03 17:00 | 14704.8 | 4.623 | 86.9474 | 59.8258 | 4309.5515
2034-06-04 18:00 | 12956 | 4.0587 | 87.1865 | 59.8258 | 3797.0288
2034-06-05 19:00 | 11118 | 3.4064 | 87.4728 | 59.8258 | 3258.3642
2034-06-06 20:00 | 8660.12 | 2.5479 | 87.8962 | 59.8258 | 2538.0306
2034-06-07 21:00 | 7391.36 | 2.1993 | 87.3138 | 59.8258 | 2166.1938
2034-06-08 22:00 | 5441.98 | 1.4888 | 88.2765 | 59.8258 | 1594.8869
2034-06-09 23:00 | 4210.67 | 1.3131 | 85.7419 | 59.8258 | 1234.0256
2034-06-11 | 3455.8 | 1.0793 | 85.2587 | 59.8258 | 1012.795
2034-06-12 01:00 | 3271.4 | 1 | 85.1857 | 59.8258 | 958.7527
2034-06-13 02:00 | 3225.97 | 1 | 85.0799 | 59.8258 | 945.4385
2034-06-14 03:00 | 3304.09 | 1.0481 | 84.1242 | 59.8258 | 968.3332
2034-06-15 04:00 | 3453.89 | 1.0773 | 84.1993 | 59.8258 | 1012.2352
2034-06-16 05:00 | 4058.36 | 1.3089 | 83.5859 | 59.8258 | 1189.3879
2034-06-17 06:00 | 4684.42 | 1.4306 | 84.3505 | 59.8258 | 1372.868
2034-06-18 07:00 | 5972.62 | 2.0031 | 83.0339 | 59.8258 | 1750.4021
2034-06-19 08:00 | 6595.62 | 2.1024 | 83.9154 | 59.8258 | 1932.9854
2034-06-20 09:00 | 8150.78 | 2.8048 | 83.0069 | 59.8258 | 2388.7578
2034-06-21 10:00 | 10327.7 | 3.3571 | 84.0637 | 59.8258 | 3026.7501
2034-06-22 11:00 | 12028.7 | 3.9144 | 84.4947 | 59.8258 | 3525.264
2034-06-23 12:00 | 12581.8 | 4.1751 | 84.7123 | 59.8258 | 3687.3616
2034-06-24 13:00 | 13444.7 | 4.3 | 85.589 | 59.8258 | 3940.2526
2034-06-25 14:00 | 14050.6 | 4.5774 | 85.6959 | 59.8258 | 4117.8244
2034-06-26 15:00 | 16119.7 | 5.2326 | 86.0765 | 59.8258 | 4724.2177
2034-06-27 16:00 | 17071.9 | 5.3667 | 87.0328 | 59.8258 | 5003.28
2034-06-28 17:00 | 16883.6 | 5.3046 | 87.4969 | 59.8258 | 4948.0947
2034-06-29 18:00 | 15227.6 | 4.6707 | 88.1634 | 59.8258 | 4462.769
2034-06-30 19:00 | 13023.5 | 4.0789 | 87.9072 | 59.8258 | 3816.8111
2034-07-01 20:00 | 10356.2 | 3.1123 | 88.38 | 59.8258 | 3035.1026
2034-07-02 21:00 | 8995.66 | 2.7224 | 87.8894 | 59.8258 | 2636.3677
2034-07-03 22:00 | 6915.7 | 2.0002 | 88.2228 | 59.8258 | 2026.7916
2034-07-04 23:00 | 5842.45 | 1.7489 | 87.2023 | 59.8258 | 1712.2531
2034-07-06 | 5476.21 | 1.6759 | 86.4396 | 59.8258 | 1604.9187
2034-07-07 01:00 | 5088.2 | 1.5426 | 86.2796 | 59.8258 | 1491.2042
2034-07-08 02:00 | 4958.53 | 1.4987 | 86.0823 | 59.8258 | 1453.2017
2034-07-09 03:00 | 5070.39 | 1.582 | 85.3885 | 59.8258 | 1485.9846
2034-07-10 04:00 | 5142.76 | 1.6601 | 84.7511 | 59.8258 | 1507.1942
2034-07-11 05:00 | 5868.24 | 1.94 | 84.2963 | 59.8258 | 1719.8114
2034-07-12 06:00 | 6563.05 | 2.1241 | 84.5795 | 59.8258 | 1923.4401
2034-07-13 07:00 | 7599.1 | 2.487 | 84.4775 | 59.8258 | 2227.0764
2034-07-14 08:00 | 8347.36 | 2.6415 | 85.1158 | 59.8258 | 2446.3697
2034-07-15 09:00 | 10039 | 3.2216 | 85.0835 | 59.8258 | 2942.1405
2034-07-16 10:00 | 11156.9 | 3.6345 | 85.1952 | 59.8258 | 3269.7646
2034-07-17 11:00 | 12685 | 4.1489 | 85.4702 | 59.8258 | 3717.6065
2034-07-18 12:00 | 13478.1 | 4.3697 | 85.9931 | 59.8258 | 3950.0412
2034-07-19 13:00 | 13669.3 | 4.4158 | 86.4038 | 59.8258 | 4006.0764
2034-07-20 14:00 | 14456.3 | 4.6111 | 86.8476 | 59.8258 | 4236.7233
2034-07-21 15:00 | 16313.6 | 5.2205 | 87.0704 | 59.8258 | 4781.0442
2034-07-22 16:00 | 16556.2 | 5.2348 | 87.6873 | 59.8258 | 4852.1432
2034-07-23 17:00 | 16100.7 | 5.1433 | 87.8483 | 59.8258 | 4718.6494
2034-07-24 18:00 | 13816.9 | 4.2847 | 88.4489 | 59.8258 | 4049.3337
2034-07-25 19:00 | 12111.2 | 3.7592 | 88.314 | 59.8258 | 3549.4423
2034-07-26 20:00 | 9660.27 | 2.9296 | 88.4556 | 59.8258 | 2831.1457
2034-07-27 21:00 | 8459.31 | 2.5338 | 88.2263 | 59.8258 | 2479.179
2034-07-28 22:00 | 6414.11 | 1.883 | 88.1607 | 59.8258 | 1879.7901
2034-07-29 23:00 | 5685.87 | 1.6934 | 87.4379 | 59.8258 | 1666.364
2034-07-31 | 5260.4 | 1.5811 | 86.9044 | 59.8258 | 1541.6711
2034-08-01 01:00 | 4832.02 | 1.4552 | 86.574 | 59.8258 | 1416.1253
2034-08-02 02:00 | 4368.81 | 1.3817 | 85.5885 | 59.8258 | 1280.3718
2034-08-03 03:00 | 4366.61 | 1.3694 | 85.4288 | 59.8258 | 1279.7271
2034-08-04 04:00 | 4433.65 | 1.3843 | 85.2938 | 59.8258 | 1299.3745
2034-08-05 05:00 | 5174.08 | 1.6736 | 84.6239 | 59.8258 | 1516.3732
2034-08-06 06:00 | 5504.99 | 1.7625 | 84.7365 | 59.8258 | 1613.3533
2034-08-07 07:00 | 6415.33 | 2.1375 | 84.1596 | 59.8258 | 1880.1476
2034-08-08 08:00 | 6772.02 | 2.238 | 84.3672 | 59.8258 | 1984.6831
2034-08-09 09:00 | 8389.69 | 2.8143 | 84.2316 | 59.8258 | 2458.7754
2034-08-10 10:00 | 10002.2 | 3.3012 | 84.6978 | 59.8258 | 2931.3555
2034-08-11 11:00 | 11394.9 | 3.7024 | 85.2493 | 59.8258 | 3339.5155
2034-08-12 12:00 | 12349.8 | 3.9329 | 85.9009 | 59.8258 | 3619.3691
2034-08-13 13:00 | 12935.4 | 4.1865 | 86.014 | 59.8258 | 3790.9915
2034-08-14 14:00 | 13647.5 | 4.4451 | 86.2346 | 59.8258 | 3999.6874
2034-08-15 15:00 | 15209.2 | 4.9914 | 86.4103 | 59.8258 | 4457.3765
2034-08-16 16:00 | 15788.8 | 5.0977 | 87.034 | 59.8258 | 4627.2405
2034-08-17 17:00 | 15608.3 | 4.9679 | 87.5664 | 59.8258 | 4574.3412
2034-08-18 18:00 | 14064.6 | 4.3691 | 88.1406 | 59.8258 | 4121.9274
2034-08-19 19:00 | 12140.7 | 3.7739 | 88.1304 | 59.8258 | 3558.0879
2034-08-20 20:00 | 9647.45 | 2.9059 | 88.4408 | 59.8258 | 2827.3885
2034-08-21 21:00 | 8461.62 | 2.5175 | 88.243 | 59.8258 | 2479.856
2034-08-22 22:00 | 6346.38 | 1.8261 | 88.4193 | 59.8258 | 1859.9404
2034-08-23 23:00 | 5333.95 | 1.5635 | 87.6417 | 59.8258 | 1563.2264
2034-08-25 | 4402.35 | 1.3432 | 86.5962 | 59.8258 | 1290.2014
2034-08-26 01:00 | 3769.06 | 1.1631 | 86.0376 | 59.8258 | 1104.6024
2034-08-27 02:00 | 3325.64 | 1.0571 | 85.2688 | 59.8258 | 974.6489
2034-08-28 03:00 | 3369.23 | 1.0586 | 85.1122 | 59.8258 | 987.4238
2034-08-29 04:00 | 3570.26 | 1.1243 | 84.8476 | 59.8258 | 1046.3399
2034-08-30 05:00 | 4376.57 | 1.4045 | 84.4011 | 59.8258 | 1282.6461
2034-08-31 06:00 | 4856.86 | 1.5203 | 84.7154 | 59.8258 | 1423.4052
2034-09-01 07:00 | 5856.79 | 1.9517 | 83.8205 | 59.8258 | 1716.4557
2034-09-02 08:00 | 6544.83 | 2.2194 | 83.6906 | 59.8258 | 1918.1003
2034-09-03 09:00 | 8404.49 | 2.8681 | 83.721 | 59.8258 | 2463.1129
2034-09-04 10:00 | 10351.2 | 3.4339 | 84.4024 | 59.8258 | 3033.6373
2034-09-05 11:00 | 11885.2 | 3.8391 | 85.1866 | 59.8258 | 3483.2083
2034-09-06 12:00 | 12277.1 | 3.8516 | 86.0466 | 59.8258 | 3598.0628
2034-09-07 13:00 | 12414.1 | 3.9725 | 86.0828 | 59.8258 | 3638.2136
2034-09-08 14:00 | 12960.8 | 4.1508 | 86.3187 | 59.8258 | 3798.4355
2034-09-09 15:00 | 14870.8 | 4.7404 | 86.6201 | 59.8258 | 4358.2013
2034-09-10 16:00 | 15374.4 | 4.9531 | 86.8854 | 59.8258 | 4505.7919
2034-09-11 17:00 | 15307 | 4.8748 | 87.3689 | 59.8258 | 4486.0389
2034-09-12 18:00 | 13478.3 | 4.2256 | 87.8245 | 59.8258 | 3950.0998
2034-09-13 19:00 | 11959.7 | 3.683 | 88.057 | 59.8258 | 3505.0421
2034-09-14 20:00 | 9488 | 2.8376 | 88.3775 | 59.8258 | 2780.6583
2034-09-15 21:00 | 8336.75 | 2.4577 | 88.2324 | 59.8258 | 2443.2602
2034-09-16 22:00 | 6121.49 | 1.7698 | 88.2008 | 59.8258 | 1794.0316
2034-09-17 23:00 | 4564.72 | 1.3354 | 87.518 | 59.8258 | 1337.7874
2034-09-19 | 3716.09 | 1.1271 | 86.464 | 59.8258 | 1089.0785
2034-09-20 01:00 | 3098.12 | 1 | 86.33 | 59.8258 | 907.9693
2034-09-21 02:00 | 3111.73 | 1 | 92.2647 | 59.8258 | 911.958
2034-09-22 03:00 | 3094.2 | 1 | 70.087 | 59.8258 | 906.8205
2034-09-23 04:00 | 3110.85 | 1 | 69.8763 | 59.8258 | 911.7001
2034-09-24 05:00 | 3169.36 | 1 | 69.6847 | 59.8258 | 928.8477
2034-09-25 06:00 | 3228.02 | 1 | 86.0217 | 59.8258 | 946.0393
2034-09-26 07:00 | 4645.94 | 1.4035 | 84.8089 | 59.8258 | 1361.5906
2034-09-27 08:00 | 4465.44 | 1.3338 | 85.0751 | 59.8258 | 1308.6913
2034-09-28 09:00 | 5839.97 | 1.9119 | 83.7085 | 59.8258 | 1711.5263
2034-09-29 10:00 | 7670.65 | 2.6551 | 83.0788 | 59.8258 | 2248.0456
2034-09-30 11:00 | 9243.64 | 3.1272 | 83.6883 | 59.8258 | 2709.0435
2034-10-01 12:00 | 10339.5 | 3.4407 | 84.282 | 59.8258 | 3030.2083
2034-10-02 13:00 | 10963.2 | 3.6358 | 84.6682 | 59.8258 | 3212.9968
2034-10-03 14:00 | 11905.3 | 3.8787 | 85.2194 | 59.8258 | 3489.099
2034-10-04 15:00 | 12603.2 | 4.07 | 85.6535 | 59.8258 | 3693.6333
2034-10-05 16:00 | 14961.1 | 4.8461 | 85.8859 | 59.8258 | 4384.6656
2034-10-06 17:00 | 14168.6 | 4.3936 | 87.0205 | 59.8258 | 4152.4068
2034-10-07 18:00 | 12910.3 | 3.9414 | 87.4864 | 59.8258 | 3783.6354
2034-10-08 19:00 | 11085.8 | 3.4089 | 87.3972 | 59.8258 | 3248.9273
2034-10-09 20:00 | 9651.71 | 2.9808 | 87.2083 | 59.8258 | 2828.637
2034-10-10 21:00 | 8511.87 | 2.6081 | 87.1325 | 59.8258 | 2494.5828
2034-10-11 22:00 | 7712.99 | 2.3368 | 87.0435 | 59.8258 | 2260.4542
2034-10-12 23:00 | 4442.1 | 1.2644 | 87.7862 | 59.8258 | 1301.851
2034-10-14 | 3409.36 | 1.015 | 86.5049 | 59.8258 | 999.1848
2034-10-15 01:00 | 3157.11 | 1 | 88.0429 | 59.8258 | 925.2576
2034-10-16 02:00 | 3168.85 | 1 | 92.5725 | 59.8258 | 928.6983
2034-10-17 03:00 | 3152.6 | 1 | 94.8811 | 59.8258 | 923.9359
2034-10-18 04:00 | 3126.69 | 1 | 69.64 | 59.8258 | 916.3424
2034-10-19 05:00 | 3066.19 | 1 | 69.4914 | 59.8258 | 898.6116
2034-10-20 06:00 | 3215.74 | 1 | 85.267 | 59.8258 | 942.4404
2034-10-21 07:00 | 5151.81 | 1.5868 | 84.3413 | 59.8258 | 1509.8465
2034-10-22 08:00 | 5113.46 | 1.5731 | 84.5334 | 59.8258 | 1498.6072
2034-10-23 09:00 | 6447.33 | 2.1199 | 83.6198 | 59.8258 | 1889.5259
2034-10-24 10:00 | 8168.95 | 2.7771 | 83.3137 | 59.8258 | 2394.0829
2034-10-25 11:00 | 9597.98 | 3.216 | 83.8412 | 59.8258 | 2812.8903
2034-10-26 12:00 | 10840.6 | 3.525 | 84.638 | 59.8258 | 3177.0662
2034-10-27 13:00 | 11642.5 | 3.75 | 85.1385 | 59.8258 | 3412.0799
2034-10-28 14:00 | 12482.3 | 4.0105 | 85.5223 | 59.8258 | 3658.201
2034-10-29 15:00 | 13362.8 | 4.2079 | 86.1426 | 59.8258 | 3916.2501
2034-10-30 16:00 | 15646.2 | 5.0959 | 85.9738 | 59.8258 | 4585.4486
2034-10-31 17:00 | 14300.8 | 4.6097 | 86.6583 | 59.8258 | 4191.1508
2034-11-01 18:00 | 12907.4 | 4.0777 | 87.1277 | 59.8258 | 3782.7855
2034-11-02 19:00 | 11235.1 | 3.4736 | 87.4122 | 59.8258 | 3292.6828
2034-11-03 20:00 | 9904.84 | 3.0263 | 87.4545 | 59.8258 | 2902.8221
2034-11-04 21:00 | 8844.91 | 2.6731 | 87.4234 | 59.8258 | 2592.1872
2034-11-05 22:00 | 7872.14 | 2.418 | 86.9163 | 59.8258 | 2307.0965
2034-11-06 23:00 | 5543.62 | 1.5117 | 88.553 | 59.8258 | 1624.6746
2034-11-08 | 4472.3 | 1.3309 | 86.701 | 59.8258 | 1310.7017
2034-11-09 01:00 | 3681.1 | 1.1512 | 85.5639 | 59.8258 | 1078.8239
2034-11-10 02:00 | 3305.36 | 1.068 | 84.7523 | 59.8258 | 968.7054
2034-11-11 03:00 | 3360.22 | 1.0617 | 84.7712 | 59.8258 | 984.7833
2034-11-12 04:00 | 3581.69 | 1.1255 | 84.6003 | 59.8258 | 1049.6897
2034-11-13 05:00 | 4521.52 | 1.4125 | 84.5392 | 59.8258 | 1325.1267
2034-11-14 06:00 | 4778.54 | 1.4927 | 84.5487 | 59.8258 | 1400.4518
2034-11-15 07:00 | 5788.29 | 1.8952 | 83.8756 | 59.8258 | 1696.3803
2034-11-16 08:00 | 6408.72 | 2.0854 | 84.0782 | 59.8258 | 1878.2104
2034-11-17 09:00 | 8457.63 | 2.7853 | 84.0333 | 59.8258 | 2478.6867
2034-11-18 10:00 | 10299.9 | 3.3931 | 84.3499 | 59.8258 | 3018.6027
2034-11-19 11:00 | 11785.8 | 3.8897 | 84.75 | 59.8258 | 3454.077
2034-11-20 12:00 | 13201.2 | 4.2562 | 85.5246 | 59.8258 | 3868.8898
2034-11-21 13:00 | 13889.6 | 4.4993 | 85.9319 | 59.8258 | 4070.6399
2034-11-22 14:00 | 14482.1 | 4.7079 | 86.3006 | 59.8258 | 4244.2845
2034-11-23 15:00 | 16265.5 | 5.2442 | 86.766 | 59.8258 | 4766.9475
2034-11-24 16:00 | 16642 | 5.2954 | 87.4279 | 59.8258 | 4877.2887
2034-11-25 17:00 | 16335.8 | 5.1206 | 88.0183 | 59.8258 | 4787.5504
2034-11-26 18:00 | 14678.5 | 4.5142 | 88.5354 | 59.8258 | 4301.8437
2034-11-27 19:00 | 12943.4 | 3.9638 | 88.6052 | 59.8258 | 3793.3361
2034-11-28 20:00 | 10389.4 | 3.1544 | 88.6098 | 59.8258 | 3044.8326
2034-11-29 21:00 | 9312.69 | 2.7777 | 88.5024 | 59.8258 | 2729.28
2034-11-30 22:00 | 7056.74 | 2.1094 | 88.1377 | 59.8258 | 2068.1263
2034-12-01 23:00 | 6042.38 | 1.8112 | 87.6159 | 59.8258 | 1770.8468
2034-12-03 | 5295.11 | 1.5975 | 87.0967 | 59.8258 | 1551.8436
2034-12-04 01:00 | 4802.53 | 1.4335 | 86.9076 | 59.8258 | 1407.4826
2034-12-05 02:00 | 4480.12 | 1.3569 | 86.3975 | 59.8258 | 1312.9936
2034-12-06 03:00 | 4587.01 | 1.3877 | 86.1387 | 59.8258 | 1344.3199
2034-12-07 04:00 | 4648.27 | 1.4744 | 85.2602 | 59.8258 | 1362.2735
2034-12-08 05:00 | 5325.24 | 1.7451 | 84.6498 | 59.8258 | 1560.6738
2034-12-09 06:00 | 5682.5 | 1.853 | 84.6888 | 59.8258 | 1665.3764
2034-12-10 07:00 | 6685.01 | 2.1919 | 84.6031 | 59.8258 | 1959.183
2034-12-11 08:00 | 7495.26 | 2.4006 | 85.0503 | 59.8258 | 2196.6439
2034-12-12 09:00 | 9223.32 | 3.0362 | 84.8074 | 59.8258 | 2703.0883
2034-12-13 10:00 | 10825.4 | 3.5998 | 84.9721 | 59.8258 | 3172.6116
2034-12-14 11:00 | 12529.8 | 4.1436 | 85.4245 | 59.8258 | 3672.1219
2034-12-15 12:00 | 13643 | 4.458 | 86.0386 | 59.8258 | 3998.3686
2034-12-16 13:00 | 14315 | 4.613 | 86.6597 | 59.8258 | 4195.3124
2034-12-17 14:00 | 15356.6 | 4.8383 | 87.3545 | 59.8258 | 4500.5752
2034-12-18 15:00 | 17083.2 | 5.4027 | 87.676 | 59.8258 | 5006.5917
2034-12-19 16:00 | 17484.8 | 5.4984 | 88.2478 | 59.8258 | 5124.289
2034-12-20 17:00 | 17164.2 | 5.4065 | 88.5969 | 59.8258 | 5030.3305
2034-12-21 18:00 | 15547 | 4.9037 | 88.8197 | 59.8258 | 4556.3759
2034-12-22 19:00 | 13793.5 | 4.288 | 89.0497 | 59.8258 | 4042.4758
2034-12-23 20:00 | 11256.5 | 3.4125 | 89.3002 | 59.8258 | 3298.9545
2034-12-24 21:00 | 10095.7 | 3.0261 | 89.1037 | 59.8258 | 2958.7576
2034-12-25 22:00 | 7932.16 | 2.35 | 88.959 | 59.8258 | 2324.6866
2034-12-26 23:00 | 6977.93 | 2.1107 | 88.1747 | 59.8258 | 2045.0294
2034-12-28 | 6263.91 | 1.9241 | 87.5429 | 59.8258 | 1835.7708
2034-12-29 01:00 | 5882.43 | 1.7779 | 87.4514 | 59.8258 | 1723.9701
2034-12-30 02:00 | 5591.81 | 1.6861 | 87.2223 | 59.8258 | 1638.7977
2034-12-31 03:00 | 5691.01 | 1.7289 | 86.8556 | 59.8258 | 1667.8704
2035-01-01 04:00 | 5610.09 | 1.8016 | 85.8786 | 59.8258 | 1644.1551
2035-01-02 05:00 | 6215.49 | 2.0262 | 85.5106 | 59.8258 | 1821.5803
2035-01-03 06:00 | 6766.39 | 2.2227 | 85.3622 | 59.8258 | 1983.0332
2035-01-04 07:00 | 7781.72 | 2.594 | 85.1753 | 59.8258 | 2280.597
2035-01-05 08:00 | 8785.33 | 2.7851 | 86.0121 | 59.8258 | 2574.7261
2035-01-06 09:00 | 10705 | 3.4037 | 86.1463 | 59.8258 | 3137.3258
2035-01-07 10:00 | 12211 | 3.9765 | 86.1642 | 59.8258 | 3578.6908
2035-01-08 11:00 | 13563.2 | 4.4554 | 86.4429 | 59.8258 | 3974.9815
2035-01-09 12:00 | 14592.7 | 4.7425 | 87.0097 | 59.8258 | 4276.6982
2035-01-10 13:00 | 15011 | 4.8549 | 87.4829 | 59.8258 | 4399.2898
2035-01-11 14:00 | 15986.9 | 5.1209 | 87.945 | 59.8258 | 4685.2979
2035-01-12 15:00 | 17823.8 | 5.5896 | 88.5824 | 59.8258 | 5223.6401
2035-01-13 16:00 | 18113.3 | 5.6816 | 89.0586 | 59.8258 | 5308.4842
2035-01-14 17:00 | 17847.6 | 5.5446 | 89.5498 | 59.8258 | 5230.6152
2035-01-15 18:00 | 16490.8 | 5.1135 | 89.8051 | 59.8258 | 4832.9764
2035-01-16 19:00 | 14710.5 | 4.5259 | 89.9696 | 59.8258 | 4311.222
2035-01-17 20:00 | 11971.8 | 3.6203 | 90.1174 | 59.8258 | 3508.5882
2035-01-18 21:00 | 10603.6 | 3.215 | 89.6833 | 59.8258 | 3107.6084
2035-01-19 22:00 | 8222.04 | 2.4644 | 89.4969 | 59.8258 | 2409.6421
2035-01-20 23:00 | 7092.96 | 2.1735 | 88.6491 | 59.8258 | 2078.7414
2035-01-22 | 6204.91 | 1.917 | 88.0679 | 59.8258 | 1818.4796
2035-01-23 01:00 | 5652.45 | 1.7415 | 87.7115 | 59.8258 | 1656.5696
2035-01-24 02:00 | 5432.73 | 1.6458 | 87.6326 | 59.8258 | 1592.176
2035-01-25 03:00 | 5368.32 | 1.6801 | 86.858 | 59.8258 | 1573.2993
2035-01-26 04:00 | 5508.41 | 1.7277 | 86.6099 | 59.8258 | 1614.3556
2035-01-27 05:00 | 6170.14 | 1.9878 | 86.0573 | 59.8258 | 1808.2895
2035-01-28 06:00 | 6549.22 | 2.0937 | 86.1177 | 59.8258 | 1919.3869
2035-01-29 07:00 | 7589.78 | 2.4647 | 85.8701 | 59.8258 | 2224.3449
2035-01-30 08:00 | 8344.57 | 2.6865 | 86.0945 | 59.8258 | 2445.5521
2035-01-31 09:00 | 10203.3 | 3.35 | 85.944 | 59.8258 | 2990.292
2035-02-01 10:00 | 12066.5 | 3.9199 | 86.3992 | 59.8258 | 3536.3421
2035-02-02 11:00 | 13651.3 | 4.3887 | 86.9585 | 59.8258 | 4000.8011
2035-02-03 12:00 | 14979.9 | 4.7364 | 87.6465 | 59.8258 | 4390.1753
2035-02-04 13:00 | 15267.1 | 4.9069 | 87.8709 | 59.8258 | 4474.3453
2035-02-05 14:00 | 16087.9 | 5.1455 | 88.2814 | 59.8258 | 4714.8981
2035-02-06 15:00 | 17927.9 | 5.6342 | 88.86 | 59.8258 | 5254.1488
2035-02-07 16:00 | 18218.6 | 5.7122 | 89.3705 | 59.8258 | 5339.3446
2035-02-08 17:00 | 18003.6 | 5.5899 | 89.8609 | 59.8258 | 5276.3343
2035-02-09 18:00 | 16289.3 | 5.0955 | 89.9797 | 59.8258 | 4773.9226
2035-02-10 19:00 | 14137.8 | 4.4382 | 89.9279 | 59.8258 | 4143.3802
2035-02-11 20:00 | 11467.1 | 3.5105 | 90.1114 | 59.8258 | 3360.6753
2035-02-12 21:00 | 10051.7 | 3.0825 | 89.6598 | 59.8258 | 2945.8625
2035-02-13 22:00 | 7986.34 | 2.3679 | 89.7763 | 59.8258 | 2340.5652
2035-02-14 23:00 | 7014.62 | 2.1259 | 88.9335 | 59.8258 | 2055.7822
2035-02-16 | 6407.98 | 1.9399 | 88.5071 | 59.8258 | 1877.9936
2035-02-17 01:00 | 5997.25 | 1.8176 | 88.1399 | 59.8258 | 1757.6205
2035-02-18 02:00 | 5716.3 | 1.7815 | 87.4408 | 59.8258 | 1675.2822
2035-02-19 03:00 | 5783.89 | 1.8049 | 87.153 | 59.8258 | 1695.0908
2035-02-20 04:00 | 6060.14 | 1.8904 | 86.9711 | 59.8258 | 1776.0517
2035-02-21 05:00 | 6777.9 | 2.1776 | 86.4161 | 59.8258 | 1986.4064
2035-02-22 06:00 | 6987.58 | 2.1929 | 86.7364 | 59.8258 | 2047.8575
2035-02-23 07:00 | 7902.75 | 2.5221 | 86.4728 | 59.8258 | 2316.0674
2035-02-24 08:00 | 8494.51 | 2.7022 | 86.6168 | 59.8258 | 2489.4951
2035-02-25 09:00 | 10188.9 | 3.2948 | 86.4904 | 59.8258 | 2986.0718
2035-02-26 10:00 | 11502.4 | 3.7756 | 86.5543 | 59.8258 | 3371.0207
2035-02-27 11:00 | 13030.6 | 4.2858 | 86.8394 | 59.8258 | 3818.8919
2035-02-28 12:00 | 14125.8 | 4.5158 | 87.6186 | 59.8258 | 4139.8633
2035-03-01 13:00 | 14516.2 | 4.684 | 87.8648 | 59.8258 | 4254.2783
2035-03-02 14:00 | 15382.5 | 4.9413 | 88.2248 | 59.8258 | 4508.1657
2035-03-03 15:00 | 17142.2 | 5.4417 | 88.6847 | 59.8258 | 5023.8829
2035-03-04 16:00 | 17403.7 | 5.5266 | 89.1187 | 59.8258 | 5100.521
2035-03-05 17:00 | 16886.7 | 5.3298 | 89.5153 | 59.8258 | 4949.0032
2035-03-06 18:00 | 14919.9 | 4.6732 | 89.7863 | 59.8258 | 4372.5911
2035-03-07 19:00 | 13173.7 | 4.0975 | 89.8019 | 59.8258 | 3860.8304
2035-03-08 20:00 | 10382.2 | 3.2155 | 89.6775 | 59.8258 | 3042.7225
2035-03-09 21:00 | 8930.69 | 2.7432 | 89.3467 | 59.8258 | 2617.3269
2035-03-10 22:00 | 6874.43 | 2.0098 | 89.6733 | 59.8258 | 2014.6966
2035-03-11 23:00 | 5344.53 | 1.6058 | 88.7264 | 59.8258 | 1566.3271
2035-03-13 | 4570.5 | 1.3734 | 88.1948 | 59.8258 | 1339.4813
2035-03-14 01:00 | 3876.88 | 1.1949 | 87.3759 | 59.8258 | 1136.2014
2035-03-15 02:00 | 3402.65 | 1.0642 | 86.7793 | 59.8258 | 997.2183
2035-03-16 03:00 | 3189.97 | 1 | 87.3664 | 59.8258 | 934.8879
2035-03-17 04:00 | 3161.6 | 1 | 88.6239 | 59.8258 | 926.5735
2035-03-18 05:00 | 3131.8 | 1 | 88.6067 | 59.8258 | 917.84
2035-03-19 06:00 | 4619.09 | 1.4631 | 85.4529 | 59.8258 | 1353.7216
2035-03-20 07:00 | 6018.71 | 1.9887 | 84.8788 | 59.8258 | 1763.9098
2035-03-21 08:00 | 6138.86 | 1.8581 | 86.312 | 59.8258 | 1799.1223
2035-03-22 09:00 | 6807.41 | 2.0883 | 86.1581 | 59.8258 | 1995.0549
2035-03-23 10:00 | 6909.63 | 2.2176 | 85.5967 | 59.8258 | 2025.0127
2035-03-24 11:00 | 7857.65 | 2.6032 | 85.2172 | 59.8258 | 2302.8499
2035-03-25 12:00 | 7567.25 | 2.4816 | 85.4922 | 59.8258 | 2217.7421
2035-03-26 13:00 | 8361.24 | 2.6756 | 85.8399 | 59.8258 | 2450.4376
2035-03-27 14:00 | 8995.58 | 2.8742 | 85.949 | 59.8258 | 2636.3443
2035-03-28 15:00 | 9694.57 | 3.0809 | 86.1342 | 59.8258 | 2841.198
2035-03-29 16:00 | 12047.1 | 4.0071 | 85.6209 | 59.8258 | 3530.6565
2035-03-30 17:00 | 10759.2 | 3.4357 | 86.5803 | 59.8258 | 3153.2103
2035-03-31 18:00 | 9463.57 | 2.8918 | 87.2871 | 59.8258 | 2773.4986
2035-04-01 19:00 | 8095.18 | 2.4754 | 87.1415 | 59.8258 | 2372.4631
2035-04-02 20:00 | 6930.04 | 2.1922 | 86.4549 | 59.8258 | 2030.9942
2035-04-03 21:00 | 6038.61 | 1.8782 | 86.4663 | 59.8258 | 1769.7419
2035-04-04 22:00 | 5376.63 | 1.6984 | 85.9632 | 59.8258 | 1575.7347
2035-04-05 23:00 | 3207.21 | 1 | 95.2349 | 59.8258 | 939.9405
2035-04-07 | 3088.8 | 1 | 70.5573 | 59.8258 | 905.2379
2035-04-08 01:00 | 3116.93 | 1 | 70.2868 | 59.8258 | 913.482
2035-04-09 02:00 | 3055.75 | 1 | 70.1244 | 59.8258 | 895.5519
2035-04-10 03:00 | 3115.29 | 1 | 69.9585 | 59.8258 | 913.0014
2035-04-11 04:00 | 0 | 0 | 70.0779 | 59.8258 | 0
2035-04-12 05:00 | 2423.74 | 1 | 69.3307 | 59.8258 | 710.3281
2035-04-13 06:00 | 1946.43 | 1 | 81.6161 | 59.8258 | 570.4423
2035-04-14 07:00 | 2744.78 | 1.0389 | 81.4913 | 59.8258 | 804.4156
2035-04-15 08:00 | 2967.22 | 1 | 91.3482 | 59.8258 | 869.6063
2035-04-16 09:00 | 3041.57 | 1 | 85.3001 | 59.8258 | 891.3962
2035-04-17 10:00 | 3834.04 | 1.2396 | 83.4382 | 59.8258 | 1123.6462
2035-04-18 11:00 | 4928.46 | 1.5863 | 83.5443 | 59.8258 | 1444.389
2035-04-19 12:00 | 5360.88 | 1.7422 | 83.559 | 59.8258 | 1571.1188
2035-04-20 13:00 | 5794.11 | 1.8925 | 83.5844 | 59.8258 | 1698.086
2035-04-21 14:00 | 6516.61 | 2.1547 | 83.4938 | 59.8258 | 1909.8299
2035-04-22 15:00 | 7114.87 | 2.293 | 83.9763 | 59.8258 | 2085.1626
2035-04-23 16:00 | 9858.55 | 3.3304 | 83.4648 | 59.8258 | 2889.2558
2035-04-24 17:00 | 9316.43 | 3.0128 | 84.5001 | 59.8258 | 2730.3761
2035-04-25 18:00 | 8579.61 | 2.6809 | 85.1848 | 59.8258 | 2514.4355
2035-04-26 19:00 | 7276.34 | 2.2475 | 85.3836 | 59.8258 | 2132.4847
2035-04-27 20:00 | 6221.02 | 1.8944 | 85.5079 | 59.8258 | 1823.201
2035-04-28 21:00 | 5359.17 | 1.6002 | 85.6704 | 59.8258 | 1570.6177
2035-04-29 22:00 | 4493.46 | 1.3916 | 84.916 | 59.8258 | 1316.9031
2035-04-30 23:00 | 3199.59 | 1 | 69.6691 | 59.8258 | 937.7073
2035-05-02 | 3168.07 | 1 | 69.3756 | 59.8258 | 928.4697
2035-05-03 01:00 | 3075.37 | 1 | 69.2093 | 59.8258 | 901.302
2035-05-04 02:00 | 1024.35 | 1 | 69.2715 | 59.8258 | 300.2074
2035-05-05 03:00 | 1380.22 | 1 | 68.8551 | 59.8258 | 404.5026
2035-05-06 04:00 | 2726.71 | 1 | 68.5237 | 59.8258 | 799.1198
2035-05-07 05:00 | 3194.46 | 1 | 68.5272 | 59.8258 | 936.2038
2035-05-08 06:00 | 3208.54 | 1 | 68.5531 | 59.8258 | 940.3303
2035-05-09 07:00 | 3252.41 | 1 | 89.4998 | 59.8258 | 953.1873
2035-05-10 08:00 | 3273.41 | 1 | 84.0063 | 59.8258 | 959.3418
2035-05-11 09:00 | 5360.91 | 1.6942 | 83.2456 | 59.8258 | 1571.1276
2035-05-12 10:00 | 7193 | 2.3833 | 82.8238 | 59.8258 | 2108.0602
2035-05-13 11:00 | 8771.6 | 2.9019 | 83.2136 | 59.8258 | 2570.7022
2035-05-14 12:00 | 10115.6 | 3.2731 | 83.9268 | 59.8258 | 2964.5897
2035-05-15 13:00 | 10496.3 | 3.3707 | 84.4667 | 59.8258 | 3076.1619
2035-05-16 14:00 | 11181.2 | 3.6008 | 84.7944 | 59.8258 | 3276.8862
2035-05-17 15:00 | 12952.4 | 4.2017 | 85.0197 | 59.8258 | 3795.9737
2035-05-18 16:00 | 13281.8 | 4.3071 | 85.4664 | 59.8258 | 3892.5113
2035-05-19 17:00 | 13271.5 | 4.2351 | 86.0267 | 59.8258 | 3889.4927
2035-05-20 18:00 | 11758.8 | 3.7001 | 86.4679 | 59.8258 | 3446.1641
2035-05-21 19:00 | 10106.8 | 3.1265 | 86.7472 | 59.8258 | 2962.0107
2035-05-22 20:00 | 7657.22 | 2.312 | 87.0023 | 59.8258 | 2244.1097
2035-05-23 21:00 | 6641.01 | 1.9486 | 87.0856 | 59.8258 | 1946.2879
2035-05-24 22:00 | 4508.57 | 1.3374 | 86.6049 | 59.8258 | 1321.3314
2035-05-25 23:00 | 3699.39 | 1.1038 | 86.0494 | 59.8258 | 1084.1842
2035-05-27 | 3247.82 | 1 | 85.4446 | 59.8258 | 951.8421
2035-05-28 01:00 | 3194.92 | 1 | 86.7956 | 59.8258 | 936.3386
2035-05-29 02:00 | 3207.43 | 1 | 88.274 | 59.8258 | 940.0049
2035-05-30 03:00 | 3187.44 | 1 | 86.4636 | 59.8258 | 934.1465
2035-05-31 04:00 | 3143.61 | 1 | 85.3213 | 59.8258 | 921.3011
2035-06-01 05:00 | 3722.2 | 1.1635 | 83.9799 | 59.8258 | 1090.8691
2035-06-02 06:00 | 3836.04 | 1.1917 | 84.0469 | 59.8258 | 1124.2323
2035-06-03 07:00 | 4882.03 | 1.5168 | 84.012 | 59.8258 | 1430.7818
2035-06-04 08:00 | 5120.29 | 1.6624 | 83.4923 | 59.8258 | 1500.6089
2035-06-05 09:00 | 6681.21 | 2.2586 | 83.0087 | 59.8258 | 1958.0694
2035-06-06 10:00 | 8355.13 | 2.8437 | 83.162 | 59.8258 | 2448.6469
2035-06-07 11:00 | 9715.57 | 3.2439 | 83.7788 | 59.8258 | 2847.3525
2035-06-08 12:00 | 10647.9 | 3.4911 | 84.4159 | 59.8258 | 3120.5914
2035-06-09 13:00 | 11361.9 | 3.6882 | 84.9071 | 59.8258 | 3329.8442
2035-06-10 14:00 | 12085.7 | 3.8883 | 85.3695 | 59.8258 | 3541.969
2035-06-11 15:00 | 13842.1 | 4.4201 | 85.7823 | 59.8258 | 4056.7191
2035-06-12 16:00 | 13993.2 | 4.4857 | 86.1667 | 59.8258 | 4101.0021
2035-06-13 17:00 | 13522.6 | 4.3207 | 86.5178 | 59.8258 | 3963.0829
2035-06-14 18:00 | 11549.3 | 3.5986 | 87.0529 | 59.8258 | 3384.7657
2035-06-15 19:00 | 9885.19 | 3.0961 | 86.8876 | 59.8258 | 2897.0632
2035-06-16 20:00 | 7610.1 | 2.3099 | 87.172 | 59.8258 | 2230.3001
2035-06-17 21:00 | 6494.34 | 1.9754 | 86.7593 | 59.8258 | 1903.3032
2035-06-18 22:00 | 4377.56 | 1.2797 | 87.0229 | 59.8258 | 1282.9362
2035-06-19 23:00 | 3308.21 | 1.0243 | 85.6592 | 59.8258 | 969.5406
2035-06-21 | 3235.3 | 1 | 90.2689 | 59.8258 | 948.1728
2035-06-22 01:00 | 3201.42 | 1 | 93.245 | 59.8258 | 938.2436
2035-06-23 02:00 | 3194.07 | 1 | 93.966 | 59.8258 | 936.0895
2035-06-24 03:00 | 3184.1 | 1 | 90.0102 | 59.8258 | 933.1676
2035-06-25 04:00 | 3173.36 | 1 | 87.0478 | 59.8258 | 930.02
2035-06-26 05:00 | 3675.16 | 1.154 | 84.0455 | 59.8258 | 1077.0831
2035-06-27 06:00 | 3826.95 | 1.2021 | 84.0087 | 59.8258 | 1121.5683
2035-06-28 07:00 | 4371.19 | 1.3545 | 84.1725 | 59.8258 | 1281.0693
2035-06-29 08:00 | 3847.34 | 1.1864 | 84.285 | 59.8258 | 1127.5441
2035-06-30 09:00 | 5166.55 | 1.6081 | 84.0671 | 59.8258 | 1514.1663
2035-07-01 10:00 | 6043.1 | 1.9905 | 83.3796 | 59.8258 | 1771.0578
2035-07-02 11:00 | 7033.65 | 2.3564 | 83.3161 | 59.8258 | 2061.3593
2035-07-03 12:00 | 8004.83 | 2.6617 | 83.6146 | 59.8258 | 2345.9841
2035-07-04 13:00 | 8322.16 | 2.6847 | 84.2621 | 59.8258 | 2438.9843
2035-07-05 14:00 | 8884.86 | 2.8888 | 84.3329 | 59.8258 | 2603.8954
2035-07-06 15:00 | 10381.4 | 3.3839 | 84.4533 | 59.8258 | 3042.488
2035-07-07 16:00 | 10952.1 | 3.5823 | 84.7004 | 59.8258 | 3209.7437
2035-07-08 17:00 | 10387.9 | 3.3133 | 85.3078 | 59.8258 | 3044.393
2035-07-09 18:00 | 9199.16 | 2.9255 | 85.4385 | 59.8258 | 2696.0077
2035-07-10 19:00 | 7906.94 | 2.4684 | 85.6509 | 59.8258 | 2317.2954
2035-07-11 20:00 | 5775.89 | 1.6975 | 86.4378 | 59.8258 | 1692.7463
2035-07-12 21:00 | 4480.29 | 1.3518 | 85.6917 | 59.8258 | 1313.0434
2035-07-13 22:00 | 3116.5 | 1 | 93.5631 | 59.8258 | 913.356
2035-07-14 23:00 | 3006.9 | 1 | 69.546 | 59.8258 | 881.2354
2035-07-16 | 2541.19 | 1 | 69.3372 | 59.8258 | 744.7493
2035-07-17 01:00 | 93.194 | 1 | 69.3146 | 59.8258 | 27.3125
2035-07-18 02:00 | -215.375 | 1.0592 | 67.8858 | 59.8258 | -63.1202
2035-07-19 03:00 | -270.136 | 1.1616 | 67.3713 | 59.8258 | -79.169
2035-07-20 04:00 | -246.65 | 1.0961 | 67.1488 | 59.8258 | -72.286
2035-07-21 05:00 | 15.2221 | 1 | 67.9388 | 59.8258 | 4.4612
2035-07-22 06:00 | 284.641 | 1 | 67.734 | 59.8258 | 83.42
2035-07-23 07:00 | 2656.11 | 1 | 67.423 | 59.8258 | 778.429
2035-07-24 08:00 | 3082.89 | 1 | 67.6194 | 59.8258 | 903.5059
2035-07-25 09:00 | 3209.2 | 1 | 84.5726 | 59.8258 | 940.5237
2035-07-26 10:00 | 5041.08 | 1.5679 | 82.7796 | 59.8258 | 1477.3947
2035-07-27 11:00 | 6923.01 | 2.2763 | 82.2545 | 59.8258 | 2028.9339
2035-07-28 12:00 | 8277.76 | 2.7016 | 82.7664 | 59.8258 | 2425.972
2035-07-29 13:00 | 8831.98 | 2.9019 | 83.0662 | 59.8258 | 2588.3978
2035-07-30 14:00 | 9698.51 | 3.1712 | 83.4474 | 59.8258 | 2842.3527
2035-07-31 15:00 | 11668.4 | 3.774 | 83.9295 | 59.8258 | 3419.6705
2035-08-01 16:00 | 12203.1 | 3.9417 | 84.4343 | 59.8258 | 3576.3756
2035-08-02 17:00 | 11828.1 | 3.7946 | 84.913 | 59.8258 | 3466.4739
2035-08-03 18:00 | 10120.3 | 3.1971 | 85.3543 | 59.8258 | 2965.9671
2035-08-04 19:00 | 8425.49 | 2.642 | 85.4285 | 59.8258 | 2469.2674
2035-08-05 20:00 | 6052.38 | 1.8211 | 85.8894 | 59.8258 | 1773.7775
2035-08-06 21:00 | 4720.34 | 1.4055 | 85.6884 | 59.8258 | 1383.3951
2035-08-07 22:00 | 3147.83 | 1 | 91.7085 | 59.8258 | 922.5379
2035-08-08 23:00 | 3168.7 | 1 | 69.2677 | 59.8258 | 928.6543
2035-08-10 | 3100.51 | 1 | 69.0136 | 59.8258 | 908.6698
2035-08-11 01:00 | 0 | 0 | 69.1153 | 59.8258 | 0
2035-08-12 02:00 | 68.4488 | 1 | 68.5591 | 59.8258 | 20.0604
2035-08-13 03:00 | 76.8184 | 1 | 68.2039 | 59.8258 | 22.5133
2035-08-14 04:00 | 524.568 | 1 | 67.9411 | 59.8258 | 153.7357
2035-08-15 05:00 | 2187.06 | 1 | 67.6266 | 59.8258 | 640.964
2035-08-16 06:00 | 2858.67 | 1 | 67.6213 | 59.8258 | 837.7935
2035-08-17 07:00 | 3163.62 | 1 | 67.7044 | 59.8258 | 927.1655
2035-08-18 08:00 | 3190.82 | 1 | 84.89 | 59.8258 | 935.137
2035-08-19 09:00 | 5364.04 | 1.6337 | 83.0949 | 59.8258 | 1572.0449
2035-08-20 10:00 | 7239.7 | 2.4003 | 82.1929 | 59.8258 | 2121.7466
2035-08-21 11:00 | 9066.06 | 2.9918 | 82.6513 | 59.8258 | 2656.9999
2035-08-22 12:00 | 10445 | 3.3994 | 83.2776 | 59.8258 | 3061.1273
2035-08-23 13:00 | 11098.2 | 3.5728 | 83.9116 | 59.8258 | 3252.5613
2035-08-24 14:00 | 11824.1 | 3.8155 | 84.2959 | 59.8258 | 3465.3016
2035-08-25 15:00 | 13540.1 | 4.3258 | 84.7964 | 59.8258 | 3968.2116
2035-08-26 16:00 | 13998 | 4.4521 | 85.3427 | 59.8258 | 4102.4088
2035-08-27 17:00 | 13821.5 | 4.3783 | 85.7703 | 59.8258 | 4050.6818
2035-08-28 18:00 | 12163.1 | 3.7906 | 86.2531 | 59.8258 | 3564.6527
2035-08-29 19:00 | 10266.7 | 3.2108 | 86.2164 | 59.8258 | 3008.8728
2035-08-30 20:00 | 7900.53 | 2.3668 | 86.7259 | 59.8258 | 2315.4168
2035-08-31 21:00 | 6662.31 | 1.9927 | 86.4026 | 59.8258 | 1952.5303
2035-09-01 22:00 | 4452.56 | 1.3025 | 86.4214 | 59.8258 | 1304.9165
2035-09-02 23:00 | 3250.12 | 1 | 87.8328 | 59.8258 | 952.5161
2035-09-04 | 3245.96 | 1 | 94.8709 | 59.8258 | 951.297
2035-09-05 01:00 | 3142.56 | 1 | 69.2972 | 59.8258 | 920.9934
2035-09-06 02:00 | 3108.82 | 1 | 69.1177 | 59.8258 | 911.1052
2035-09-07 03:00 | 3098.35 | 1 | 68.937 | 59.8258 | 908.0367
2035-09-08 04:00 | 3131.85 | 1 | 68.7987 | 59.8258 | 917.8546
2035-09-09 05:00 | 1611.76 | 1 | 68.8248 | 59.8258 | 472.3602
2035-09-10 06:00 | 3215.54 | 1 | 68.3724 | 59.8258 | 942.3817
2035-09-11 07:00 | 3544.17 | 1.0772 | 83.7312 | 59.8258 | 1038.6937
2035-09-12 08:00 | 3908.42 | 1.2098 | 83.4593 | 59.8258 | 1145.4448
2035-09-13 09:00 | 5422.06 | 1.6843 | 83.4144 | 59.8258 | 1589.0489
2035-09-14 10:00 | 7210.61 | 2.376 | 82.7575 | 59.8258 | 2113.2212
2035-09-15 11:00 | 8857.1 | 2.912 | 83.151 | 59.8258 | 2595.7598
2035-09-16 12:00 | 10220.2 | 3.3078 | 83.7531 | 59.8258 | 2995.2449
2035-09-17 13:00 | 10817.9 | 3.4847 | 84.2234 | 59.8258 | 3170.4135
2035-09-18 14:00 | 11481 | 3.6848 | 84.6098 | 59.8258 | 3364.749
2035-09-19 15:00 | 12154.5 | 3.8397 | 85.1269 | 59.8258 | 3562.1323
2035-09-20 16:00 | 14281.7 | 4.6746 | 84.8938 | 59.8258 | 4185.5531
2035-09-21 17:00 | 13219.8 | 4.1969 | 85.8263 | 59.8258 | 3874.3409
2035-09-22 18:00 | 11925.4 | 3.7379 | 86.1915 | 59.8258 | 3494.9897
2035-09-23 19:00 | 10125.3 | 3.1789 | 86.164 | 59.8258 | 2967.4325
2035-09-24 20:00 | 9000.35 | 2.7891 | 86.2204 | 59.8258 | 2637.7422
2035-09-25 21:00 | 7840.05 | 2.4478 | 85.9504 | 59.8258 | 2297.6918
2035-09-26 22:00 | 7167.04 | 2.1868 | 86.0502 | 59.8258 | 2100.4521
2035-09-27 23:00 | 4052.51 | 1.1646 | 86.7718 | 59.8258 | 1187.6734
2035-09-29 | 3277.21 | 1 | 86.8937 | 59.8258 | 960.4554
2035-09-30 01:00 | 3236.72 | 1 | 91.6599 | 59.8258 | 948.589
2035-10-01 02:00 | 3211.24 | 1 | 69.3912 | 59.8258 | 941.1215
2035-10-02 03:00 | 3116.35 | 1 | 69.2071 | 59.8258 | 913.312
2035-10-03 04:00 | 3119.67 | 1 | 68.9852 | 59.8258 | 914.285
2035-10-04 05:00 | 3155.88 | 1 | 68.8529 | 59.8258 | 924.8971
2035-10-05 06:00 | 3224.31 | 1 | 84.6137 | 59.8258 | 944.952
2035-10-06 07:00 | 5264.35 | 1.617 | 83.8098 | 59.8258 | 1542.8287
2035-10-07 08:00 | 5800.26 | 1.787 | 83.9707 | 59.8258 | 1699.8884
2035-10-08 09:00 | 7220.24 | 2.3406 | 83.3884 | 59.8258 | 2116.0435
2035-10-09 10:00 | 9201.67 | 3.0237 | 83.4332 | 59.8258 | 2696.7433
2035-10-10 11:00 | 10864.2 | 3.5897 | 83.7808 | 59.8258 | 3183.9827
2035-10-11 12:00 | 11875.6 | 3.8657 | 84.4758 | 59.8258 | 3480.3948
2035-10-12 13:00 | 12474.9 | 4.059 | 84.8933 | 59.8258 | 3656.0323
2035-10-13 14:00 | 13106.2 | 4.2576 | 85.2759 | 59.8258 | 3841.0481
2035-10-14 15:00 | 13873 | 4.4527 | 85.7796 | 59.8258 | 4065.775
2035-10-15 16:00 | 16381.2 | 5.299 | 85.9801 | 59.8258 | 4800.8558
2035-10-16 17:00 | 15558.8 | 4.9126 | 86.9014 | 59.8258 | 4559.8342
2035-10-17 18:00 | 14131.9 | 4.386 | 87.4404 | 59.8258 | 4141.6511
2035-10-18 19:00 | 12130.3 | 3.7658 | 87.4756 | 59.8258 | 3555.04
2035-10-19 20:00 | 10833.6 | 3.3286 | 87.4986 | 59.8258 | 3175.0147
2035-10-20 21:00 | 9693.86 | 2.9646 | 87.4019 | 59.8258 | 2840.9899
2035-10-21 22:00 | 8688.12 | 2.6643 | 87.1161 | 59.8258 | 2546.2366
2035-10-22 23:00 | 6165.12 | 1.7864 | 87.7411 | 59.8258 | 1806.8183
2035-10-24 | 5381.13 | 1.5544 | 87.3155 | 59.8258 | 1577.0535
2035-10-25 01:00 | 4745.06 | 1.4217 | 86.3888 | 59.8258 | 1390.6398
2035-10-26 02:00 | 4495.4 | 1.3676 | 85.8645 | 59.8258 | 1317.4717
2035-10-27 03:00 | 4464.38 | 1.3905 | 85.2679 | 59.8258 | 1308.3806
2035-10-28 04:00 | 4495.36 | 1.4441 | 84.6016 | 59.8258 | 1317.46
2035-10-29 05:00 | 5116.2 | 1.6567 | 84.3502 | 59.8258 | 1499.4102
2035-10-30 06:00 | 5346.41 | 1.7248 | 84.3775 | 59.8258 | 1566.8781
2035-10-31 07:00 | 6377.89 | 2.0968 | 84.0986 | 59.8258 | 1869.175
2035-11-01 08:00 | 7203.08 | 2.29 | 84.6822 | 59.8258 | 2111.0144
2035-11-02 09:00 | 9060.78 | 2.9782 | 84.3612 | 59.8258 | 2655.4525
2035-11-03 10:00 | 11003.3 | 3.6002 | 84.7377 | 59.8258 | 3224.7489
2035-11-04 11:00 | 12916.4 | 4.2729 | 85.025 | 59.8258 | 3785.4232
2035-11-05 12:00 | 14199.3 | 4.5464 | 86.0052 | 59.8258 | 4161.404
2035-11-06 13:00 | 14599.7 | 4.7642 | 86.2388 | 59.8258 | 4278.7497
2035-11-07 14:00 | 15177.5 | 4.9192 | 86.7293 | 59.8258 | 4448.0862
2035-11-08 15:00 | 16943.9 | 5.4423 | 87.2061 | 59.8258 | 4965.7669
2035-11-09 16:00 | 17503.1 | 5.5443 | 87.8856 | 59.8258 | 5129.6522
2035-11-10 17:00 | 17436.2 | 5.4364 | 88.5131 | 59.8258 | 5110.0458
2035-11-11 18:00 | 15974.6 | 4.9155 | 88.994 | 59.8258 | 4681.6931
2035-11-12 19:00 | 13827.8 | 4.279 | 88.9853 | 59.8258 | 4052.5281
2035-11-13 20:00 | 11292.5 | 3.4345 | 89.1056 | 59.8258 | 3309.5051
2035-11-14 21:00 | 9936.88 | 3.0136 | 88.7819 | 59.8258 | 2912.2121
2035-11-15 22:00 | 7821.37 | 2.318 | 88.7791 | 59.8258 | 2292.2173
2035-11-16 23:00 | 6754 | 2.0574 | 87.8832 | 59.8258 | 1979.402
2035-11-18 | 6054.29 | 1.8431 | 87.4602 | 59.8258 | 1774.3372
2035-11-19 01:00 | 5685.1 | 1.6978 | 87.4069 | 59.8258 | 1666.1383
2035-11-20 02:00 | 5596.59 | 1.6789 | 87.0726 | 59.8258 | 1640.1986
2035-11-21 03:00 | 5550.45 | 1.7292 | 86.2862 | 59.8258 | 1626.6763
2035-11-22 04:00 | 5671.64 | 1.7892 | 85.9344 | 59.8258 | 1662.1936
2035-11-23 05:00 | 6354.99 | 2.0547 | 85.4497 | 59.8258 | 1862.4637
2035-11-24 06:00 | 6427.35 | 2.0426 | 85.684 | 59.8258 | 1883.6703
2035-11-25 07:00 | 7193.23 | 2.3343 | 85.3568 | 59.8258 | 2108.1276
2035-11-26 08:00 | 7666.03 | 2.4318 | 85.7554 | 59.8258 | 2246.6916
2035-11-27 09:00 | 9389.71 | 3.08 | 85.3635 | 59.8258 | 2751.8524
2035-11-28 10:00 | 11359.7 | 3.7292 | 85.6176 | 59.8258 | 3329.1994
2035-11-29 11:00 | 13064.4 | 4.2881 | 86.0167 | 59.8258 | 3828.7977
2035-11-30 12:00 | 14364.3 | 4.6052 | 86.8006 | 59.8258 | 4209.7608
2035-12-01 13:00 | 14163.8 | 4.5897 | 87.1034 | 59.8258 | 4151
2035-12-02 14:00 | 14170.7 | 4.4947 | 87.6855 | 59.8258 | 4153.0222
2035-12-03 15:00 | 14458.2 | 4.6191 | 87.7691 | 59.8258 | 4237.2801
2035-12-04 16:00 | 13906.4 | 4.4833 | 87.8194 | 59.8258 | 4075.5635
2035-12-05 17:00 | 13264.1 | 4.2361 | 87.9983 | 59.8258 | 3887.324
2035-12-06 18:00 | 11687.6 | 3.6839 | 88.1559 | 59.8258 | 3425.2974
2035-12-07 19:00 | 10525 | 3.2913 | 88.0963 | 59.8258 | 3084.573
2035-12-08 20:00 | 8623.88 | 2.5712 | 88.6098 | 59.8258 | 2527.4097
2035-12-09 21:00 | 7797.9 | 2.3426 | 88.1369 | 59.8258 | 2285.3389
2035-12-10 22:00 | 5918.15 | 1.6944 | 88.5809 | 59.8258 | 1734.4386
2035-12-11 23:00 | 5166.63 | 1.5229 | 87.6779 | 59.8258 | 1514.1898
2035-12-13 | 4554.21 | 1.3776 | 86.8999 | 59.8258 | 1334.7072
2035-12-14 01:00 | 4103.86 | 1.2894 | 86.0101 | 59.8258 | 1202.7226
2035-12-15 02:00 | 3940.56 | 1.214 | 86.0143 | 59.8258 | 1154.8641
2035-12-16 03:00 | 4298.3 | 1.3261 | 85.7454 | 59.8258 | 1259.7074
2035-12-17 04:00 | 4527.81 | 1.4451 | 85.1265 | 59.8258 | 1326.9701
2035-12-18 05:00 | 5286.3 | 1.7103 | 84.8441 | 59.8258 | 1549.2616
2035-12-19 06:00 | 5399.78 | 1.7193 | 85.0901 | 59.8258 | 1582.5193
2035-12-20 07:00 | 5967.24 | 1.9505 | 84.7138 | 59.8258 | 1748.8254
2035-12-21 08:00 | 5846.85 | 1.8592 | 85.1683 | 59.8258 | 1713.5426
2035-12-22 09:00 | 6928.17 | 2.3196 | 84.4328 | 59.8258 | 2030.4462
2035-12-23 10:00 | 8252.9 | 2.7207 | 84.763 | 59.8258 | 2418.6862
2035-12-24 11:00 | 9582.25 | 3.0831 | 85.3148 | 59.8258 | 2808.2803
2035-12-25 12:00 | 11007.8 | 3.5218 | 85.665 | 59.8258 | 3226.0677
2035-12-26 13:00 | 11304.3 | 3.6254 | 85.9706 | 59.8258 | 3312.9633
2035-12-27 14:00 | 10900.7 | 3.4426 | 86.4499 | 59.8258 | 3194.6798
2035-12-28 15:00 | 11798.5 | 3.8131 | 86.2128 | 59.8258 | 3457.799
2035-12-29 16:00 | 12148.4 | 3.9272 | 86.4057 | 59.8258 | 3560.3446
2035-12-30 17:00 | 12093.8 | 3.8703 | 86.7243 | 59.8258 | 3544.3429
2035-12-31 18:00 | 10857.1 | 3.4211 | 87.0531 | 59.8258 | 3181.9019
2036-01-01 19:00 | 10064.3 | 3.0924 | 87.3534 | 59.8258 | 2949.5552
2036-01-02 20:00 | 8102.37 | 2.4352 | 87.6171 | 59.8258 | 2374.5702
2036-01-03 21:00 | 7398.46 | 2.1995 | 87.5085 | 59.8258 | 2168.2746
2036-01-04 22:00 | 5453.65 | 1.5778 | 87.7031 | 59.8258 | 1598.307
2036-01-05 23:00 | 4522.79 | 1.3248 | 87.1156 | 59.8258 | 1325.4989
2036-01-07 | 3658.24 | 1.1428 | 85.777 | 59.8258 | 1072.1243
2036-01-08 01:00 | 3102.01 | 1.0059 | 84.8948 | 59.8258 | 909.1094
2036-01-09 02:00 | 3163.72 | 1 | 86.8539 | 59.8258 | 927.1948
2036-01-10 03:00 | 3167.34 | 1 | 85.0054 | 59.8258 | 928.2557
2036-01-11 04:00 | 3429.34 | 1.0793 | 84.6378 | 59.8258 | 1005.0403
2036-01-12 05:00 | 4286.94 | 1.3637 | 84.3622 | 59.8258 | 1256.3781
2036-01-13 06:00 | 4529.19 | 1.3936 | 84.8644 | 59.8258 | 1327.3746
2036-01-14 07:00 | 5222.68 | 1.6589 | 84.4 | 59.8258 | 1530.6164
2036-01-15 08:00 | 4870.73 | 1.4794 | 85.1361 | 59.8258 | 1427.4701
2036-01-16 09:00 | 5938.74 | 1.9686 | 83.8438 | 59.8258 | 1740.4729
2036-01-17 10:00 | 7657.64 | 2.587 | 83.6924 | 59.8258 | 2244.2327
2036-01-18 11:00 | 8915.46 | 2.9765 | 84.1224 | 59.8258 | 2612.8634
2036-01-19 12:00 | 9241.83 | 2.9305 | 85.1454 | 59.8258 | 2708.513
2036-01-20 13:00 | 9564.83 | 3.042 | 85.3029 | 59.8258 | 2803.175
2036-01-21 14:00 | 10197.8 | 3.3388 | 85.0833 | 59.8258 | 2988.6802
2036-01-22 15:00 | 12039.5 | 3.9138 | 85.3928 | 59.8258 | 3528.4291
2036-01-23 16:00 | 12844.7 | 4.1956 | 85.6967 | 59.8258 | 3764.41
2036-01-24 17:00 | 12789.5 | 4.091 | 86.3175 | 59.8258 | 3748.2324
2036-01-25 18:00 | 11401.6 | 3.546 | 86.9427 | 59.8258 | 3341.4791
2036-01-26 19:00 | 9988.11 | 3.1162 | 86.8988 | 59.8258 | 2927.2261
2036-01-27 20:00 | 7971.18 | 2.3844 | 87.4324 | 59.8258 | 2336.1223
2036-01-28 21:00 | 6871.68 | 2.072 | 87.0166 | 59.8258 | 2013.8906
2036-01-29 22:00 | 4935.36 | 1.4116 | 87.5451 | 59.8258 | 1446.4112
2036-01-30 23:00 | 3973.1 | 1.2397 | 85.7798 | 59.8258 | 1164.4007
2036-02-01 | 3370.66 | 1.0585 | 85.3079 | 59.8258 | 987.8429
2036-02-02 01:00 | 3178.26 | 1 | 85.3287 | 59.8258 | 931.4561
2036-02-03 02:00 | 3224.25 | 1 | 85.8953 | 59.8258 | 944.9344
2036-02-04 03:00 | 3505.59 | 1.0912 | 84.7086 | 59.8258 | 1027.387
2036-02-05 04:00 | 3900.03 | 1.2209 | 84.5124 | 59.8258 | 1142.986
2036-02-06 05:00 | 4926.78 | 1.5554 | 84.3233 | 59.8258 | 1443.8967
2036-02-07 06:00 | 5006.18 | 1.5801 | 84.3989 | 59.8258 | 1467.1665
2036-02-08 07:00 | 5557.72 | 1.7855 | 84.1653 | 59.8258 | 1628.8069
2036-02-09 08:00 | 5483.41 | 1.7132 | 84.6489 | 59.8258 | 1607.0288
2036-02-10 09:00 | 6781.39 | 2.2155 | 84.0334 | 59.8258 | 1987.4292
2036-02-11 10:00 | 8447.4 | 2.7758 | 84.133 | 59.8258 | 2475.6886
2036-02-12 11:00 | 9464.92 | 3.0324 | 84.7996 | 59.8258 | 2773.8942
2036-02-13 12:00 | 10035.7 | 3.1985 | 85.1815 | 59.8258 | 2941.1733
2036-02-14 13:00 | 10593.4 | 3.3996 | 85.3396 | 59.8258 | 3104.6191
2036-02-15 14:00 | 11455 | 3.7608 | 85.2799 | 59.8258 | 3357.1291
2036-02-16 15:00 | 13001.2 | 4.2651 | 85.5647 | 59.8258 | 3810.2756
2036-02-17 16:00 | 13654.3 | 4.4733 | 85.9546 | 59.8258 | 4001.6803
2036-02-18 17:00 | 13420.5 | 4.2979 | 86.5882 | 59.8258 | 3933.1603
2036-02-19 18:00 | 11797.2 | 3.7306 | 86.9681 | 59.8258 | 3457.418
2036-02-20 19:00 | 10420 | 3.269 | 87.047 | 59.8258 | 3053.8005
2036-02-21 20:00 | 8315.86 | 2.5109 | 87.4991 | 59.8258 | 2437.138
2036-02-22 21:00 | 7275.52 | 2.2095 | 87.0989 | 59.8258 | 2132.2444
2036-02-23 22:00 | 5540.75 | 1.6087 | 87.495 | 59.8258 | 1623.8335
2036-02-24 23:00 | 4247.99 | 1.2835 | 86.4795 | 59.8258 | 1244.963
2036-02-26 | 3718.04 | 1.1516 | 85.7029 | 59.8258 | 1089.65
2036-02-27 01:00 | 3271.17 | 1.0174 | 85.3262 | 59.8258 | 958.6853
2036-02-28 02:00 | 3174.78 | 1 | 86.0305 | 59.8258 | 930.4362
2036-02-29 03:00 | 3260.58 | 1 | 87.9797 | 59.8258 | 955.5817
2036-03-01 04:00 | 3198.08 | 1 | 88.5745 | 59.8258 | 937.2647
2036-03-02 05:00 | 3096.58 | 1 | 87.8804 | 59.8258 | 907.518
2036-03-03 06:00 | 4410.8 | 1.3757 | 84.2949 | 59.8258 | 1292.6779
2036-03-04 07:00 | 5648.53 | 1.8509 | 83.6522 | 59.8258 | 1655.4207
2036-03-05 08:00 | 5254.14 | 1.6388 | 84.5462 | 59.8258 | 1539.8364
2036-03-06 09:00 | 6284.33 | 2.0245 | 84.0843 | 59.8258 | 1841.7553
2036-03-07 10:00 | 7493.05 | 2.4357 | 84.0857 | 59.8258 | 2195.9962
2036-03-08 11:00 | 8813.86 | 2.9505 | 83.9285 | 59.8258 | 2583.0874
2036-03-09 12:00 | 9518.13 | 3.122 | 84.5081 | 59.8258 | 2789.4885
2036-03-10 13:00 | 9705.62 | 3.0967 | 85.1497 | 59.8258 | 2844.4364
2036-03-11 14:00 | 10370.5 | 3.3258 | 85.2683 | 59.8258 | 3039.2935
2036-03-12 15:00 | 10704.2 | 3.3884 | 85.6642 | 59.8258 | 3137.0913
2036-03-13 16:00 | 13058.6 | 4.2622 | 85.3969 | 59.8258 | 3827.0979
2036-03-14 17:00 | 11794 | 3.7274 | 86.2945 | 59.8258 | 3456.4802
2036-03-15 18:00 | 10537.6 | 3.2589 | 86.7175 | 59.8258 | 3088.2657
2036-03-16 19:00 | 9466.06 | 2.8966 | 86.7981 | 59.8258 | 2774.2283
2036-03-17 20:00 | 8688.13 | 2.6336 | 86.8429 | 59.8258 | 2546.2396
2036-03-18 21:00 | 8028.76 | 2.4456 | 86.6631 | 59.8258 | 2352.9973
2036-03-19 22:00 | 7393.42 | 2.2789 | 86.3249 | 59.8258 | 2166.7975
2036-03-20 23:00 | 4513.5 | 1.3137 | 87.0514 | 59.8258 | 1322.7763
2036-03-22 | 3756.34 | 1.1302 | 86.0709 | 59.8258 | 1100.8746
2036-03-23 01:00 | 3251.74 | 1.0259 | 85.0103 | 59.8258 | 952.9909
2036-03-24 02:00 | 3217.76 | 1 | 87.0723 | 59.8258 | 943.0324
2036-03-25 03:00 | 3202.19 | 1 | 87.8514 | 59.8258 | 938.4692
2036-03-26 04:00 | 3189.71 | 1 | 89.0747 | 59.8258 | 934.8117
2036-03-27 05:00 | 3142.69 | 1 | 90.0392 | 59.8258 | 921.0315
2036-03-28 06:00 | 4284.46 | 1.3118 | 84.4693 | 59.8258 | 1255.6513
2036-03-29 07:00 | 5186.67 | 1.692 | 83.6127 | 59.8258 | 1520.0629
2036-03-30 08:00 | 4843.9 | 1.5214 | 84.2813 | 59.8258 | 1419.607
2036-03-31 09:00 | 5518.17 | 1.8408 | 83.4094 | 59.8258 | 1617.216
2036-04-01 10:00 | 7478.37 | 2.4839 | 83.5155 | 59.8258 | 2191.6939
2036-04-02 11:00 | 9040.31 | 2.9418 | 84.1078 | 59.8258 | 2649.4533
2036-04-03 12:00 | 10617.8 | 3.3321 | 84.9853 | 59.8258 | 3111.77
2036-04-04 13:00 | 10418.2 | 3.2912 | 85.2972 | 59.8258 | 3053.273
2036-04-05 14:00 | 10338.1 | 3.2804 | 85.4735 | 59.8258 | 3029.798
2036-04-06 15:00 | 10024.9 | 3.1714 | 85.6805 | 59.8258 | 2938.0082
2036-04-07 16:00 | 11952.4 | 3.9325 | 85.1839 | 59.8258 | 3502.9027
2036-04-08 17:00 | 10719.9 | 3.4053 | 86.0125 | 59.8258 | 3141.6926
2036-04-09 18:00 | 9665.57 | 3.014 | 86.3107 | 59.8258 | 2832.6989
2036-04-10 19:00 | 8825.47 | 2.6887 | 86.5521 | 59.8258 | 2586.4899
2036-04-11 20:00 | 8379.16 | 2.5593 | 86.4164 | 59.8258 | 2455.6894
2036-04-12 21:00 | 7972.5 | 2.4312 | 86.3759 | 59.8258 | 2336.5091
2036-04-13 22:00 | 7365.75 | 2.3131 | 85.8244 | 59.8258 | 2158.6882
2036-04-14 23:00 | 5110.17 | 1.454 | 87.2125 | 59.8258 | 1497.643
2036-04-16 | 4393.44 | 1.3145 | 86.0497 | 59.8258 | 1287.5902
2036-04-17 01:00 | 4020.47 | 1.2343 | 85.3665 | 59.8258 | 1178.2834
2036-04-18 02:00 | 3875.16 | 1.1842 | 85.216 | 59.8258 | 1135.6973
2036-04-19 03:00 | 4173.41 | 1.2886 | 84.8803 | 59.8258 | 1223.1057
2036-04-20 04:00 | 4412.74 | 1.4075 | 84.2791 | 59.8258 | 1293.2464
2036-04-21 05:00 | 5224.21 | 1.6798 | 84.1194 | 59.8258 | 1531.0648
2036-04-22 06:00 | 5331.34 | 1.6903 | 84.3821 | 59.8258 | 1562.4615
2036-04-23 07:00 | 5771.61 | 1.9084 | 83.815 | 59.8258 | 1691.4919
2036-04-24 08:00 | 5687.19 | 1.8111 | 84.4122 | 59.8258 | 1666.7509
2036-04-25 09:00 | 7001.09 | 2.3223 | 83.845 | 59.8258 | 2051.8169
2036-04-26 10:00 | 9107.85 | 3.0733 | 83.7675 | 59.8258 | 2669.2473
2036-04-27 11:00 | 10588.6 | 3.5236 | 84.3224 | 59.8258 | 3103.2123
2036-04-28 12:00 | 11694 | 3.7769 | 85.1361 | 59.8258 | 3427.1731
2036-04-29 13:00 | 12390.9 | 3.9875 | 85.5744 | 59.8258 | 3631.4143
2036-04-30 14:00 | 13278.6 | 4.3523 | 85.6857 | 59.8258 | 3891.5735
2036-05-01 15:00 | 15315 | 4.9435 | 86.2727 | 59.8258 | 4488.3834
2036-05-02 16:00 | 15667.1 | 5.0572 | 86.7833 | 59.8258 | 4591.5738
2036-05-03 17:00 | 15353.3 | 4.8702 | 87.417 | 59.8258 | 4499.6081
2036-05-04 18:00 | 13737.6 | 4.2828 | 87.9137 | 59.8258 | 4026.0931
2036-05-05 19:00 | 11844.2 | 3.7004 | 87.9051 | 59.8258 | 3471.1924
2036-05-06 20:00 | 9456.42 | 2.8726 | 88.1803 | 59.8258 | 2771.4031
2036-05-07 21:00 | 8170.94 | 2.4896 | 87.7709 | 59.8258 | 2394.6661
2036-05-08 22:00 | 6187.78 | 1.8158 | 87.9874 | 59.8258 | 1813.4593
2036-05-09 23:00 | 5480.23 | 1.6038 | 87.5645 | 59.8258 | 1606.0969
2036-05-11 | 4870.91 | 1.4675 | 86.7453 | 59.8258 | 1427.5228
2036-05-12 01:00 | 4469.97 | 1.3779 | 86.0942 | 59.8258 | 1310.0189
2036-05-13 02:00 | 4277.08 | 1.3165 | 85.8568 | 59.8258 | 1253.4884
2036-05-14 03:00 | 4544.28 | 1.4096 | 85.5013 | 59.8258 | 1331.797
2036-05-15 04:00 | 4714.63 | 1.4917 | 85.0743 | 59.8258 | 1381.7217
2036-05-16 05:00 | 5435.14 | 1.7644 | 84.5942 | 59.8258 | 1592.8823
2036-05-17 06:00 | 5643.7 | 1.7974 | 84.8623 | 59.8258 | 1654.0052
2036-05-18 07:00 | 6412.75 | 2.0639 | 84.7096 | 59.8258 | 1879.3915
2036-05-19 08:00 | 6840.21 | 2.1969 | 84.8404 | 59.8258 | 2004.6677
2036-05-20 09:00 | 8505.82 | 2.815 | 84.5188 | 59.8258 | 2492.8098
2036-05-21 10:00 | 9925.98 | 3.2555 | 84.9177 | 59.8258 | 2909.0176
2036-05-22 11:00 | 11786.4 | 3.9168 | 85.0661 | 59.8258 | 3454.2529
2036-05-23 12:00 | 13222.6 | 4.2806 | 85.869 | 59.8258 | 3875.1615
2036-05-24 13:00 | 12966.8 | 4.195 | 86.3476 | 59.8258 | 3800.194
2036-05-25 14:00 | 12774 | 4.1528 | 86.5541 | 59.8258 | 3743.6898
2036-05-26 15:00 | 12957.7 | 4.1927 | 86.7771 | 59.8258 | 3797.527
2036-05-27 16:00 | 12899.4 | 4.1159 | 87.1343 | 59.8258 | 3780.441
2036-05-28 17:00 | 12577.4 | 3.9304 | 87.5387 | 59.8258 | 3686.0721
2036-05-29 18:00 | 11201.6 | 3.4069 | 87.9816 | 59.8258 | 3282.8649
2036-05-30 19:00 | 9824.87 | 3.0432 | 87.5991 | 59.8258 | 2879.3852
2036-05-31 20:00 | 7805.79 | 2.3487 | 87.8467 | 59.8258 | 2287.6512
2036-06-01 21:00 | 6841.96 | 2.0759 | 87.3668 | 59.8258 | 2005.1805
2036-06-02 22:00 | 5032.36 | 1.4358 | 88.0057 | 59.8258 | 1474.8391
2036-06-03 23:00 | 4183.36 | 1.2853 | 86.4167 | 59.8258 | 1226.0218
2036-06-05 | 3635.63 | 1.1234 | 85.9309 | 59.8258 | 1065.498
2036-06-06 01:00 | 3350.64 | 1.04 | 85.5352 | 59.8258 | 981.9756
2036-06-07 02:00 | 3273.42 | 1 | 85.9143 | 59.8258 | 959.3447
2036-06-08 03:00 | 3511.92 | 1.08 | 85.1916 | 59.8258 | 1029.2422
2036-06-09 04:00 | 3757.35 | 1.2016 | 84.4903 | 59.8258 | 1101.1706
2036-06-10 05:00 | 4736.83 | 1.5146 | 84.3971 | 59.8258 | 1388.2278
2036-06-11 06:00 | 4899.55 | 1.5276 | 84.8042 | 59.8258 | 1435.9164
2036-06-12 07:00 | 5301.54 | 1.6869 | 84.5217 | 59.8258 | 1553.728
2036-06-13 08:00 | 5454.04 | 1.6962 | 84.9035 | 59.8258 | 1598.4213
2036-06-14 09:00 | 6762.53 | 2.3031 | 83.6527 | 59.8258 | 1981.9019
2036-06-15 10:00 | 8373.21 | 2.7689 | 84.2319 | 59.8258 | 2453.9456
2036-06-16 11:00 | 10263.8 | 3.4244 | 84.3928 | 59.8258 | 3008.0228
2036-06-17 12:00 | 11710.2 | 3.799 | 85.1783 | 59.8258 | 3431.9208
2036-06-18 13:00 | 12459.7 | 4.0149 | 85.7007 | 59.8258 | 3651.5776
2036-06-19 14:00 | 13593.6 | 4.3371 | 86.2177 | 59.8258 | 3983.8909
2036-06-20 15:00 | 15406.4 | 4.979 | 86.4295 | 59.8258 | 4515.1701
2036-06-21 16:00 | 15295.3 | 4.9212 | 87.0102 | 59.8258 | 4482.6099
2036-06-22 17:00 | 14857.2 | 4.713 | 87.5254 | 59.8258 | 4354.2155
2036-06-23 18:00 | 13271.5 | 4.1128 | 88.049 | 59.8258 | 3889.4927
2036-06-24 19:00 | 11608.1 | 3.5919 | 88.0618 | 59.8258 | 3401.9983
2036-06-25 20:00 | 9185.46 | 2.8054 | 88.1226 | 59.8258 | 2691.9926
2036-06-26 21:00 | 8052.41 | 2.4764 | 87.6537 | 59.8258 | 2359.9284
2036-06-27 22:00 | 6225.79 | 1.8139 | 88.1593 | 59.8258 | 1824.5989
2036-06-28 23:00 | 5514.99 | 1.6648 | 87.1866 | 59.8258 | 1616.284
2036-06-30 | 5086.6 | 1.5249 | 86.937 | 59.8258 | 1490.7353
2036-07-01 01:00 | 4555.96 | 1.3954 | 86.3374 | 59.8258 | 1335.2201
2036-07-02 02:00 | 4293.25 | 1.3244 | 85.973 | 59.8258 | 1258.2274
2036-07-03 03:00 | 4101.13 | 1.3048 | 85.2761 | 59.8258 | 1201.9226
2036-07-04 04:00 | 4258.37 | 1.3575 | 85.0481 | 59.8258 | 1248.0051
2036-07-05 05:00 | 4911.27 | 1.5735 | 84.8277 | 59.8258 | 1439.3512
2036-07-06 06:00 | 4952.11 | 1.5917 | 84.747 | 59.8258 | 1451.3202
2036-07-07 07:00 | 5741.59 | 1.901 | 84.2813 | 59.8258 | 1682.6939
2036-07-08 08:00 | 6440.59 | 2.1393 | 84.3018 | 59.8258 | 1887.5506
2036-07-09 09:00 | 8269.42 | 2.7201 | 84.5471 | 59.8258 | 2423.5278
2036-07-10 10:00 | 10317.8 | 3.3931 | 84.8422 | 59.8258 | 3023.8487
2036-07-11 11:00 | 12048.5 | 3.9215 | 85.4046 | 59.8258 | 3531.0668
2036-07-12 12:00 | 13590.2 | 4.2827 | 86.3292 | 59.8258 | 3982.8945
2036-07-13 13:00 | 13414.5 | 4.3684 | 86.3591 | 59.8258 | 3931.4019
2036-07-14 14:00 | 12501.7 | 4.0392 | 86.7831 | 59.8258 | 3663.8866
2036-07-15 15:00 | 12554.5 | 4.0499 | 86.8939 | 59.8258 | 3679.3607
2036-07-16 16:00 | 12299.1 | 3.912 | 87.1988 | 59.8258 | 3604.5104
2036-07-17 17:00 | 11898.6 | 3.7065 | 87.5576 | 59.8258 | 3487.1354
2036-07-18 18:00 | 10577.2 | 3.2133 | 87.9295 | 59.8258 | 3099.8713
2036-07-19 19:00 | 9308 | 2.854 | 87.6525 | 59.8258 | 2727.9055
2036-07-20 20:00 | 7228.87 | 2.0905 | 88.3671 | 59.8258 | 2118.5727
2036-07-21 21:00 | 6061 | 1.8032 | 87.5592 | 59.8258 | 1776.3038
2036-07-22 22:00 | 3807.76 | 1.155 | 86.9095 | 59.8258 | 1115.9443
2036-07-23 23:00 | 3237.76 | 1 | 88.033 | 59.8258 | 948.8938
2036-07-25 | 3195.88 | 1 | 90.9561 | 59.8258 | 936.62
2036-07-26 01:00 | 3130.32 | 1 | 94.6571 | 59.8258 | 917.4062
2036-07-27 02:00 | 3146.52 | 1 | 95.4983 | 59.8258 | 922.154
2036-07-28 03:00 | 3106.45 | 1 | 92.988 | 59.8258 | 910.4106
2036-07-29 04:00 | 3081.53 | 1 | 91.5066 | 59.8258 | 903.1073
2036-07-30 05:00 | 3145.19 | 1 | 85.0186 | 59.8258 | 921.7642
2036-07-31 06:00 | 3180.52 | 1 | 85.1282 | 59.8258 | 932.1184
2036-08-01 07:00 | 4024.7 | 1.247 | 84.4925 | 59.8258 | 1179.5231
2036-08-02 08:00 | 4277.75 | 1.298 | 84.8443 | 59.8258 | 1253.6848
2036-08-03 09:00 | 5864.88 | 1.8409 | 84.3573 | 59.8258 | 1718.8267
2036-08-04 10:00 | 7047.35 | 2.3628 | 83.626 | 59.8258 | 2065.3744
2036-08-05 11:00 | 9008.42 | 3.0303 | 83.8235 | 59.8258 | 2640.1073
2036-08-06 12:00 | 10577.1 | 3.5017 | 84.4153 | 59.8258 | 3099.842
2036-08-07 13:00 | 11793.8 | 3.8249 | 85.1182 | 59.8258 | 3456.4216
2036-08-08 14:00 | 12743.6 | 4.0086 | 85.9759 | 59.8258 | 3734.7805
2036-08-09 15:00 | 13682.8 | 4.3315 | 86.2649 | 59.8258 | 4010.0328
2036-08-10 16:00 | 13606.1 | 4.3929 | 86.377 | 59.8258 | 3987.5543
2036-08-11 17:00 | 12347.9 | 4.0372 | 86.4615 | 59.8258 | 3618.8123
2036-08-12 18:00 | 10636.3 | 3.4002 | 86.8237 | 59.8258 | 3117.1918
2036-08-13 19:00 | 9524.72 | 2.9584 | 87.1004 | 59.8258 | 2791.4199
2036-08-14 20:00 | 7503.01 | 2.2643 | 87.3828 | 59.8258 | 2198.9152
2036-08-15 21:00 | 6694.46 | 2.0323 | 86.9594 | 59.8258 | 1961.9526
2036-08-16 22:00 | 4946.73 | 1.4127 | 87.6337 | 59.8258 | 1449.7435
2036-08-17 23:00 | 3617.77 | 1.1115 | 86.1193 | 59.8258 | 1060.2637
2036-08-19 | 3245.71 | 1 | 87.7111 | 59.8258 | 951.2237
2036-08-20 01:00 | 3129.64 | 1 | 89.8176 | 59.8258 | 917.2069
2036-08-21 02:00 | 3184.26 | 1 | 95.5748 | 59.8258 | 933.2145
2036-08-22 03:00 | 3172.68 | 1 | 69.7887 | 59.8258 | 929.8207
2036-08-23 04:00 | 3114.25 | 1 | 69.6411 | 59.8258 | 912.6966
2036-08-24 05:00 | 3192.96 | 1 | 69.503 | 59.8258 | 935.7642
2036-08-25 06:00 | 3227.56 | 1 | 87.7144 | 59.8258 | 945.9045
2036-08-26 07:00 | 4629.91 | 1.4196 | 84.4938 | 59.8258 | 1356.8927
2036-08-27 08:00 | 4668.77 | 1.4618 | 84.3149 | 59.8258 | 1368.2814
2036-08-28 09:00 | 6233.35 | 2.1183 | 83.1992 | 59.8258 | 1826.8146
2036-08-29 10:00 | 8625.99 | 2.9177 | 83.4598 | 59.8258 | 2528.0281
2036-08-30 11:00 | 10534.1 | 3.5961 | 83.7632 | 59.8258 | 3087.24
2036-08-31 12:00 | 12183.1 | 3.961 | 84.9186 | 59.8258 | 3570.5142
2036-09-01 13:00 | 12878.5 | 4.1108 | 85.6661 | 59.8258 | 3774.3158
2036-09-02 14:00 | 13490.1 | 4.3026 | 86.0963 | 59.8258 | 3953.558
2036-09-03 15:00 | 13727.3 | 4.4533 | 86.2199 | 59.8258 | 4023.0745
2036-09-04 16:00 | 16154.8 | 5.1755 | 86.6729 | 59.8258 | 4734.5045
2036-09-05 17:00 | 14703.6 | 4.6966 | 87.2702 | 59.8258 | 4309.1998
2036-09-06 18:00 | 12855.1 | 4.0568 | 87.6365 | 59.8258 | 3767.4579
2036-09-07 19:00 | 11626.2 | 3.4878 | 88.3058 | 59.8258 | 3407.3029
2036-09-08 20:00 | 10366.7 | 3.1435 | 88.0562 | 59.8258 | 3038.1799
2036-09-09 21:00 | 9075.46 | 2.8064 | 87.6279 | 59.8258 | 2659.7548
2036-09-10 22:00 | 8222.42 | 2.5763 | 87.1724 | 59.8258 | 2409.7534
2036-09-11 23:00 | 5725.78 | 1.625 | 88.4567 | 59.8258 | 1678.0605
2036-09-13 | 4642.04 | 1.3887 | 87.1673 | 59.8258 | 1360.4476
2036-09-14 01:00 | 3850.8 | 1.1868 | 86.3062 | 59.8258 | 1128.5581
2036-09-15 02:00 | 3432.08 | 1.062 | 85.8914 | 59.8258 | 1005.8434
2036-09-16 03:00 | 3135.42 | 1 | 86.2343 | 59.8258 | 918.9009
2036-09-17 04:00 | 3214.55 | 1 | 90.1397 | 59.8258 | 942.0916
2036-09-18 05:00 | 3179.48 | 1 | 91.4226 | 59.8258 | 931.8136
2036-09-19 06:00 | 3976.59 | 1.2324 | 84.9015 | 59.8258 | 1165.4235
2036-09-20 07:00 | 5612.45 | 1.8091 | 84.318 | 59.8258 | 1644.8467
2036-09-21 08:00 | 5882.01 | 1.9169 | 84.3464 | 59.8258 | 1723.847
2036-09-22 09:00 | 7936.33 | 2.6885 | 83.9079 | 59.8258 | 2325.9087
2036-09-23 10:00 | 10195.4 | 3.5466 | 83.8445 | 59.8258 | 2987.9768
2036-09-24 11:00 | 12176.4 | 4.0603 | 84.8935 | 59.8258 | 3568.5506
2036-09-25 12:00 | 13201.3 | 4.2943 | 85.7703 | 59.8258 | 3868.9191
2036-09-26 13:00 | 14074.2 | 4.4314 | 86.6823 | 59.8258 | 4124.7409
2036-09-27 14:00 | 14295.7 | 4.6102 | 86.7723 | 59.8258 | 4189.6561
2036-09-28 15:00 | 14387.8 | 4.6965 | 86.9313 | 59.8258 | 4216.6479
2036-09-29 16:00 | 16566.1 | 5.3265 | 87.3653 | 59.8258 | 4855.0447
2036-09-30 17:00 | 15351.3 | 4.876 | 88.0301 | 59.8258 | 4499.0219
2036-10-01 18:00 | 13930.8 | 4.2217 | 88.9073 | 59.8258 | 4082.7145
2036-10-02 19:00 | 12139.7 | 3.699 | 88.7878 | 59.8258 | 3557.7949
2036-10-03 20:00 | 10767.5 | 3.3676 | 88.2518 | 59.8258 | 3155.6427
2036-10-04 21:00 | 9476.12 | 2.9769 | 87.9869 | 59.8258 | 2777.1766
2036-10-05 22:00 | 8589.41 | 2.6161 | 88.1434 | 59.8258 | 2517.3076
2036-10-06 23:00 | 5589.73 | 1.6045 | 88.7926 | 59.8258 | 1638.1882
2036-10-08 | 4712.77 | 1.4112 | 87.5723 | 59.8258 | 1381.1765
2036-10-09 01:00 | 3989.8 | 1.2214 | 86.7969 | 59.8258 | 1169.295
2036-10-10 02:00 | 3394.15 | 1.0671 | 86.0473 | 59.8258 | 994.7272
2036-10-11 03:00 | 3207.41 | 1 | 86.592 | 59.8258 | 939.9991
2036-10-12 04:00 | 3110.57 | 1 | 89.1678 | 59.8258 | 911.6181
2036-10-13 05:00 | 3144.67 | 1 | 90.2178 | 59.8258 | 921.6118
2036-10-14 06:00 | 4243.03 | 1.3192 | 85.1619 | 59.8258 | 1243.5093
2036-10-15 07:00 | 5416.69 | 1.6843 | 85.1707 | 59.8258 | 1587.4751
2036-10-16 08:00 | 5399.48 | 1.7085 | 85.0459 | 59.8258 | 1582.4314
2036-10-17 09:00 | 6315.72 | 1.9974 | 85.07 | 59.8258 | 1850.9548
2036-10-18 10:00 | 6674.98 | 2.1287 | 85.0434 | 59.8258 | 1956.2435
2036-10-19 11:00 | 8107.22 | 2.7126 | 84.4696 | 59.8258 | 2375.9916
2036-10-20 12:00 | 9397.15 | 3.1051 | 84.8554 | 59.8258 | 2754.0328
2036-10-21 13:00 | 9595.43 | 3.1378 | 85.2742 | 59.8258 | 2812.1429
2036-10-22 14:00 | 9870.51 | 3.1712 | 85.7069 | 59.8258 | 2892.7609
2036-10-23 15:00 | 10343.7 | 3.3002 | 85.9505 | 59.8258 | 3031.4392
2036-10-24 16:00 | 11822.4 | 3.9281 | 85.5353 | 59.8258 | 3464.8034
2036-10-25 17:00 | 10533.2 | 3.3455 | 86.4828 | 59.8258 | 3086.9762
2036-10-26 18:00 | 8584.44 | 2.7026 | 86.623 | 59.8258 | 2515.851
2036-10-27 19:00 | 7050.3 | 2.1959 | 86.5475 | 59.8258 | 2066.239
2036-10-28 20:00 | 5749.86 | 1.8171 | 86.0571 | 59.8258 | 1685.1176
2036-10-29 21:00 | 4434.55 | 1.478 | 84.9997 | 59.8258 | 1299.6383
2036-10-30 22:00 | 3556.72 | 1.1621 | 84.8849 | 59.8258 | 1042.3717
2036-10-31 23:00 | 2958.73 | 1 | 70.2898 | 59.8258 | 867.1182
2036-11-02 | 0 | 0 | 70.2601 | 59.8258 | 0
2036-11-03 01:00 | -349.861 | 1.3834 | 68.4987 | 59.8258 | -102.5341
2036-11-04 02:00 | -634.753 | 2.0562 | 67.8121 | 59.8258 | -186.0277
2036-11-05 03:00 | -792.123 | 2.4144 | 67.4015 | 59.8258 | -232.1483
2036-11-06 04:00 | -884.218 | 2.6315 | 67.053 | 59.8258 | -259.1387
2036-11-07 05:00 | -635.432 | 1.9767 | 66.8397 | 59.8258 | -186.2267
2036-11-08 06:00 | -582.481 | 1.8974 | 66.7527 | 59.8258 | -170.7083
2036-11-09 07:00 | -160.98 | 0.816 | 67.1085 | 59.8258 | -47.1786
2036-11-10 08:00 | 0 | 0 | 67.9334 | 59.8258 | 0
2036-11-11 09:00 | 2680.07 | 1 | 67.613 | 59.8258 | 785.451
2036-11-12 10:00 | 3695.89 | 1.1669 | 82.6127 | 59.8258 | 1083.1584
2036-11-13 11:00 | 5740.15 | 1.8796 | 82.2736 | 59.8258 | 1682.2719
2036-11-14 12:00 | 6915.18 | 2.2993 | 82.4305 | 59.8258 | 2026.6392
2036-11-15 13:00 | 7679.61 | 2.5159 | 83.0049 | 59.8258 | 2250.6715
2036-11-16 14:00 | 8796.02 | 2.8807 | 83.3381 | 59.8258 | 2577.859
2036-11-17 15:00 | 9553.06 | 3.241 | 83.1884 | 59.8258 | 2799.7255
2036-11-18 16:00 | 9750.86 | 3.3377 | 83.3828 | 59.8258 | 2857.695
2036-11-19 17:00 | 9223.3 | 3.1468 | 83.6519 | 59.8258 | 2703.0824
2036-11-20 18:00 | 7119.63 | 2.4009 | 83.9251 | 59.8258 | 2086.5576
2036-11-21 19:00 | 5769.12 | 1.9033 | 84.0683 | 59.8258 | 1690.7622
2036-11-22 20:00 | 3591.72 | 1.1094 | 84.8009 | 59.8258 | 1052.6292
2036-11-23 21:00 | 3044.83 | 1 | 89.3812 | 59.8258 | 892.3516
2036-11-24 22:00 | 0 | 0 | 69.3096 | 59.8258 | 0
2036-11-25 23:00 | -138.821 | 0.86223 | 67.9542 | 59.8258 | -40.6844
2036-11-27 | -482.745 | 1.725 | 67.0211 | 59.8258 | -141.4786
2036-11-28 01:00 | -821.795 | 2.5427 | 66.527 | 59.8258 | -240.8443
2036-11-29 02:00 | -1085.56 | 3.1738 | 66.163 | 59.8258 | -318.1462
2036-11-30 03:00 | -1190.97 | 3.4079 | 65.851 | 59.8258 | -349.0389
2036-12-01 04:00 | -1165.66 | 3.3288 | 65.6494 | 59.8258 | -341.6212
2036-12-02 05:00 | -865.247 | 2.5489 | 65.5242 | 59.8258 | -253.5789
2036-12-03 06:00 | -739.952 | 2.2885 | 65.496 | 59.8258 | -216.8585
2036-12-04 07:00 | -305.535 | 1.1701 | 65.6913 | 59.8258 | -89.5435
2036-12-05 08:00 | 1432.74 | 1 | 66.743 | 59.8258 | 419.8946
2036-12-06 09:00 | 3202.86 | 1 | 81.8092 | 59.8258 | 938.6656
2036-12-07 10:00 | 6090.68 | 1.954 | 81.5982 | 59.8258 | 1785.0021
2036-12-08 11:00 | 8266.8 | 2.7031 | 81.8563 | 59.8258 | 2422.7599
2036-12-09 12:00 | 9861.41 | 3.1449 | 82.7989 | 59.8258 | 2890.094
2036-12-10 13:00 | 10329.3 | 3.2839 | 83.4192 | 59.8258 | 3027.219
2036-12-11 14:00 | 11231.8 | 3.5884 | 83.7767 | 59.8258 | 3291.7156
2036-12-12 15:00 | 12773.4 | 4.0998 | 84.1321 | 59.8258 | 3743.514
2036-12-13 16:00 | 13123.3 | 4.1602 | 84.8043 | 59.8258 | 3846.0596
2036-12-14 17:00 | 12423.8 | 3.9545 | 85.1306 | 59.8258 | 3641.0564
2036-12-15 18:00 | 10503.1 | 3.2786 | 85.6195 | 59.8258 | 3078.1548
2036-12-16 19:00 | 8705.12 | 2.6831 | 85.7777 | 59.8258 | 2551.2188
2036-12-17 20:00 | 6218.21 | 1.8751 | 85.9474 | 59.8258 | 1822.3775
2036-12-18 21:00 | 4974.64 | 1.524 | 85.3291 | 59.8258 | 1457.9231
2036-12-19 22:00 | 3179.34 | 1 | 88.2868 | 59.8258 | 931.7726
2036-12-20 23:00 | 3144.04 | 1 | 69.3168 | 59.8258 | 921.4272
2036-12-22 | 3038.08 | 1 | 69.0509 | 59.8258 | 890.3734
2036-12-23 01:00 | 0 | 0 | 69.1315 | 59.8258 | 0
2036-12-24 02:00 | -65.5069 | 0.65385 | 68.1197 | 59.8258 | -19.1982
2036-12-25 03:00 | 331.493 | 1 | 68.1759 | 59.8258 | 97.151
2036-12-26 04:00 | 904.505 | 1 | 67.9506 | 59.8258 | 265.0842
2036-12-27 05:00 | 2133.64 | 1 | 67.7298 | 59.8258 | 625.3082
2036-12-28 06:00 | 2883.7 | 1 | 67.6959 | 59.8258 | 845.129
2036-12-29 07:00 | 3115.94 | 1 | 67.8047 | 59.8258 | 913.1919
2036-12-30 08:00 | 3126.05 | 1 | 86.1858 | 59.8258 | 916.1548
2036-12-31 09:00 | 5638.11 | 1.8266 | 82.2946 | 59.8258 | 1652.3669
2037-01-01 10:00 | 7414.83 | 2.5811 | 81.6745 | 59.8258 | 2173.0722
2037-01-02 11:00 | 9255.47 | 3.0921 | 82.6245 | 59.8258 | 2712.5105
2037-01-03 12:00 | 10529 | 3.4291 | 83.4093 | 59.8258 | 3085.7453
2037-01-04 13:00 | 10791.8 | 3.4359 | 84.1989 | 59.8258 | 3162.7644
2037-01-05 14:00 | 11828.9 | 3.7976 | 84.4356 | 59.8258 | 3466.7084
2037-01-06 15:00 | 13506.6 | 4.3406 | 84.7836 | 59.8258 | 3958.3937
2037-01-07 16:00 | 13687.6 | 4.3711 | 85.3511 | 59.8258 | 4011.4396
2037-01-08 17:00 | 13097.6 | 4.1449 | 85.8083 | 59.8258 | 3838.5276
2037-01-09 18:00 | 10997.3 | 3.4865 | 85.951 | 59.8258 | 3222.9905
2037-01-10 19:00 | 9270.4 | 2.8838 | 86.1443 | 59.8258 | 2716.886
2037-01-11 20:00 | 7092.34 | 2.1214 | 86.5554 | 59.8258 | 2078.5597
2037-01-12 21:00 | 5575.92 | 1.6877 | 86.0143 | 59.8258 | 1634.1408
2037-01-13 22:00 | 3452.84 | 1.0714 | 85.2597 | 59.8258 | 1011.9275
2037-01-14 23:00 | 3184.31 | 1 | 89.0635 | 59.8258 | 933.2291
2037-01-16 | 3175.93 | 1 | 69.3809 | 59.8258 | 930.7732
2037-01-17 01:00 | 3074.32 | 1 | 69.1891 | 59.8258 | 900.9943
2037-01-18 02:00 | 3127.54 | 1 | 69.0116 | 59.8258 | 916.5915
2037-01-19 03:00 | 3214.97 | 1 | 68.8581 | 59.8258 | 942.2147
2037-01-20 04:00 | 3130.25 | 1 | 68.7756 | 59.8258 | 917.3857
2037-01-21 05:00 | 3156.1 | 1 | 68.6687 | 59.8258 | 924.9616
2037-01-22 06:00 | 3208.47 | 1 | 68.5824 | 59.8258 | 940.3097
2037-01-23 07:00 | 3246.64 | 1 | 91.6318 | 59.8258 | 951.4963
2037-01-24 08:00 | 3259.81 | 1 | 86.345 | 59.8258 | 955.356
2037-01-25 09:00 | 5201.37 | 1.6721 | 82.9178 | 59.8258 | 1524.3711
2037-01-26 10:00 | 8067.87 | 2.6876 | 82.6356 | 59.8258 | 2364.4593
2037-01-27 11:00 | 10372 | 3.4397 | 83.1718 | 59.8258 | 3039.7331
2037-01-28 12:00 | 10660.4 | 3.521 | 83.7794 | 59.8258 | 3124.2548
2037-01-29 13:00 | 11537.6 | 3.7972 | 84.1847 | 59.8258 | 3381.3368
2037-01-30 14:00 | 12718.8 | 4.0952 | 84.8617 | 59.8258 | 3727.5123
2037-01-31 15:00 | 14350.4 | 4.5548 | 85.4743 | 59.8258 | 4205.6871
2037-02-01 16:00 | 14470.8 | 4.5805 | 85.9861 | 59.8258 | 4240.9728
2037-02-02 17:00 | 14013.5 | 4.4202 | 86.3508 | 59.8258 | 4106.9514
2037-02-03 18:00 | 11778.6 | 3.7136 | 86.5686 | 59.8258 | 3451.9669
2037-02-04 19:00 | 10317 | 3.1463 | 86.9815 | 59.8258 | 3023.6142
2037-02-05 20:00 | 7944.78 | 2.3849 | 87.0864 | 59.8258 | 2328.3852
2037-02-06 21:00 | 6567.94 | 1.9832 | 86.6514 | 59.8258 | 1924.8732
2037-02-07 22:00 | 4417.8 | 1.2987 | 86.7029 | 59.8258 | 1294.7294
2037-02-08 23:00 | 3085.1 | 1 | 88.0711 | 59.8258 | 904.1536
2037-02-10 | 3154.16 | 1 | 69.8993 | 59.8258 | 924.393
2037-02-11 01:00 | 3063.85 | 1 | 69.6304 | 59.8258 | 897.9258
2037-02-12 02:00 | 3140.2 | 1 | 69.41 | 59.8258 | 920.3018
2037-02-13 03:00 | 3129.83 | 1 | 69.2221 | 59.8258 | 917.2626
2037-02-14 04:00 | 0 | 0 | 69.3596 | 59.8258 | 0
2037-02-15 05:00 | 492.309 | 1 | 68.7712 | 59.8258 | 144.2815
2037-02-16 06:00 | 2041.65 | 1 | 82.0456 | 59.8258 | 598.3486
2037-02-17 07:00 | 2860.55 | 1.0213 | 81.3583 | 59.8258 | 838.3444
2037-02-18 08:00 | 2986.45 | 1 | 82.3413 | 59.8258 | 875.2421
2037-02-19 09:00 | 5411.75 | 1.789 | 82.4034 | 59.8258 | 1586.0274
2037-02-20 10:00 | 7745.5 | 2.5955 | 82.5444 | 59.8258 | 2269.982
2037-02-21 11:00 | 8800.18 | 2.918 | 83.1802 | 59.8258 | 2579.0782
2037-02-22 12:00 | 9219.91 | 3.0877 | 83.4213 | 59.8258 | 2702.0889
2037-02-23 13:00 | 10284.6 | 3.3744 | 83.9705 | 59.8258 | 3014.1187
2037-02-24 14:00 | 10630.2 | 3.4295 | 84.5457 | 59.8258 | 3115.4041
2037-02-25 15:00 | 11243.4 | 3.6556 | 84.6739 | 59.8258 | 3295.1153
2037-02-26 16:00 | 13248.6 | 4.2326 | 85.1629 | 59.8258 | 3882.7814
2037-02-27 17:00 | 12206.6 | 3.8519 | 85.7973 | 59.8258 | 3577.4013
2037-02-28 18:00 | 10645.6 | 3.296 | 86.2546 | 59.8258 | 3119.9174
2037-03-01 19:00 | 9301.28 | 2.7609 | 86.8282 | 59.8258 | 2725.9361
2037-03-02 20:00 | 8458.69 | 2.5869 | 86.268 | 59.8258 | 2478.9973
2037-03-03 21:00 | 7656.15 | 2.3674 | 85.9865 | 59.8258 | 2243.7961
2037-03-04 22:00 | 7125.07 | 2.2117 | 85.7467 | 59.8258 | 2088.1519
2037-03-05 23:00 | 4294.92 | 1.2577 | 86.4808 | 59.8258 | 1258.7168
2037-03-07 | 3261.67 | 1.0138 | 85.1231 | 59.8258 | 955.9011
2037-03-08 01:00 | 3342.87 | 1 | 90.0162 | 59.8258 | 979.6985
2037-03-09 02:00 | 3174.91 | 1 | 91.3053 | 59.8258 | 930.4743
2037-03-10 03:00 | 3272.45 | 1 | 95.0477 | 59.8258 | 959.0604
2037-03-11 04:00 | 3183.12 | 1 | 69.1487 | 59.8258 | 932.8804
2037-03-12 05:00 | 3187.78 | 1 | 69.0454 | 59.8258 | 934.2461
2037-03-13 06:00 | 3186 | 1 | 84.3171 | 59.8258 | 933.7244
2037-03-14 07:00 | 4166.09 | 1.2921 | 83.8994 | 59.8258 | 1220.9605
2037-03-15 08:00 | 3309.98 | 1.0027 | 84.3296 | 59.8258 | 970.0594
2037-03-16 09:00 | 3306.37 | 1.0299 | 83.7997 | 59.8258 | 969.0014
2037-03-17 10:00 | 4467.21 | 1.3568 | 84.0489 | 59.8258 | 1309.21
2037-03-18 11:00 | 4816.79 | 1.5063 | 83.696 | 59.8258 | 1411.6618
2037-03-19 12:00 | 4850.68 | 1.6196 | 82.8394 | 59.8258 | 1421.594
2037-03-20 13:00 | 7037.01 | 2.4117 | 82.4584 | 59.8258 | 2062.3441
2037-03-21 14:00 | 8255.26 | 2.8618 | 82.5805 | 59.8258 | 2419.3779
2037-03-22 15:00 | 8046.57 | 2.6236 | 83.7224 | 59.8258 | 2358.2169
2037-03-23 16:00 | 9968.27 | 3.3022 | 83.5858 | 59.8258 | 2921.4116
2037-03-24 17:00 | 9264.43 | 2.939 | 84.528 | 59.8258 | 2715.1364
2037-03-25 18:00 | 8280.84 | 2.3762 | 86.2008 | 59.8258 | 2426.8746
2037-03-26 19:00 | 6447.39 | 2.0513 | 84.5903 | 59.8258 | 1889.5435
2037-03-27 20:00 | 5697.53 | 1.7332 | 85.0295 | 59.8258 | 1669.7812
2037-03-28 21:00 | 5199.07 | 1.525 | 85.4137 | 59.8258 | 1523.697
2037-03-29 22:00 | 4615.71 | 1.4291 | 84.4159 | 59.8258 | 1352.7311
2037-03-30 23:00 | 3128.16 | 1 | 69.2218 | 59.8258 | 916.7732
2037-04-01 | 3164.97 | 1 | 68.9293 | 59.8258 | 927.5611
2037-04-02 01:00 | 3241.97 | 1 | 68.7584 | 59.8258 | 950.1276
2037-04-03 02:00 | 3182.8 | 1 | 68.6641 | 59.8258 | 932.7866
2037-04-04 03:00 | 3234.35 | 1 | 68.5588 | 59.8258 | 947.8944
2037-04-05 04:00 | 3161.45 | 1 | 68.4725 | 59.8258 | 926.5295
2037-04-06 05:00 | 3217.94 | 1 | 91.7853 | 59.8258 | 943.0851
2037-04-07 06:00 | 3223.17 | 1 | 89.6046 | 59.8258 | 944.6179
2037-04-08 07:00 | 3270.75 | 1 | 87.8276 | 59.8258 | 958.5622
2037-04-09 08:00 | 3219.51 | 1 | 68.277 | 59.8258 | 943.5452
2037-04-10 09:00 | 3360.44 | 1.0636 | 82.9948 | 59.8258 | 984.8477
2037-04-11 10:00 | 4492.55 | 1.4114 | 83.0276 | 59.8258 | 1316.6364
2037-04-12 11:00 | 6117.33 | 2.1436 | 81.6384 | 59.8258 | 1792.8124
2037-04-13 12:00 | 7917.48 | 2.585 | 82.8587 | 59.8258 | 2320.3843
2037-04-14 13:00 | 9226.24 | 3.1317 | 82.6839 | 59.8258 | 2703.944
2037-04-15 14:00 | 7946.66 | 2.4368 | 84.5092 | 59.8258 | 2328.9361
2037-04-16 15:00 | 9995.28 | 3.3897 | 83.131 | 59.8258 | 2929.3274
2037-04-17 16:00 | 10316.2 | 3.2767 | 84.3686 | 59.8258 | 3023.3798
2037-04-18 17:00 | 9738.59 | 3.0637 | 84.775 | 59.8258 | 2854.099
2037-04-19 18:00 | 8180.03 | 2.5751 | 84.8462 | 59.8258 | 2397.3301
2037-04-20 19:00 | 7003.7 | 2.0855 | 85.5524 | 59.8258 | 2052.5819
2037-04-21 20:00 | 4929.55 | 1.415 | 85.9933 | 59.8258 | 1444.7085
2037-04-22 21:00 | 3847.02 | 1.1975 | 84.4159 | 59.8258 | 1127.4503
2037-04-23 22:00 | 3122.51 | 1 | 69.1265 | 59.8258 | 915.1173
2037-04-24 23:00 | 3086.57 | 1 | 68.8411 | 59.8258 | 904.5844
2037-04-26 | 3047.05 | 1 | 68.6423 | 59.8258 | 893.0022
2037-04-27 01:00 | 3148.78 | 1 | 68.4645 | 59.8258 | 922.8163
2037-04-28 02:00 | 0 | 0 | 68.6603 | 59.8258 | 0
2037-04-29 03:00 | 3674.49 | 1 | 67.8062 | 59.8258 | 1076.8867
2037-04-30 04:00 | 3444.51 | 1 | 67.9966 | 59.8258 | 1009.4862
2037-05-01 05:00 | 3266.89 | 1 | 68.0571 | 59.8258 | 957.4309
2037-05-02 06:00 | 3283.22 | 1 | 67.9795 | 59.8258 | 962.2168
2037-05-03 07:00 | 3259.37 | 1 | 94.1073 | 59.8258 | 955.2271
2037-05-04 08:00 | 3264.33 | 1 | 89.4841 | 59.8258 | 956.6807
2037-05-05 09:00 | 3175.09 | 1 | 86.2576 | 59.8258 | 930.527
2037-05-06 10:00 | 3185.6 | 1 | 83.3543 | 59.8258 | 933.6072
2037-05-07 11:00 | 5907.22 | 1.9196 | 82.2082 | 59.8258 | 1731.2353
2037-05-08 12:00 | 7403.68 | 2.5015 | 81.9856 | 59.8258 | 2169.8044
2037-05-09 13:00 | 8505.3 | 2.8675 | 82.364 | 59.8258 | 2492.6574
2037-05-10 14:00 | 10023.6 | 3.3626 | 82.7873 | 59.8258 | 2937.6272
2037-05-11 15:00 | 11778.5 | 3.938 | 83.2276 | 59.8258 | 3451.9376
2037-05-12 16:00 | 11779 | 3.8173 | 84.1715 | 59.8258 | 3452.0841
2037-05-13 17:00 | 11462.8 | 3.6052 | 84.9078 | 59.8258 | 3359.4151
2037-05-14 18:00 | 9475.3 | 2.8836 | 85.5883 | 59.8258 | 2776.9363
2037-05-15 19:00 | 8135.68 | 2.4298 | 85.8021 | 59.8258 | 2384.3324
2037-05-16 20:00 | 5598.06 | 1.6584 | 85.7877 | 59.8258 | 1640.6294
2037-05-17 21:00 | 4426.08 | 1.3705 | 84.7444 | 59.8258 | 1297.156
2037-05-18 22:00 | 3158.69 | 1 | 93.3796 | 59.8258 | 925.7207
2037-05-19 23:00 | 3127.21 | 1 | 69.0007 | 59.8258 | 916.4948
2037-05-21 | 2918.57 | 1 | 68.7905 | 59.8258 | 855.3484
2037-05-22 01:00 | 207.365 | 1 | 68.8316 | 59.8258 | 60.7727
2037-05-23 02:00 | -54.415 | 0.66423 | 67.9721 | 59.8258 | -15.9475
2037-05-24 03:00 | 44.3455 | 1 | 67.9519 | 59.8258 | 12.9964
2037-05-25 04:00 | -16.83 | 0.56433 | 67.7354 | 59.8258 | -4.9324
2037-05-26 05:00 | 1991.75 | 1 | 67.306 | 59.8258 | 583.7243
2037-05-27 06:01 | 2718.74 | 1 | 67.3042 | 59.8258 | 796.784
2037-05-28 07:01 | 3127.01 | 1 | 67.3937 | 59.8258 | 916.4362
2037-05-29 08:01 | 3255.43 | 1 | 67.4886 | 59.8258 | 954.0724
2037-05-30 09:01 | 3612.42 | 1.1066 | 82.806 | 59.8258 | 1058.6958
2037-05-31 10:01 | 5602.92 | 1.8119 | 82.0855 | 59.8258 | 1642.0538
2037-06-01 11:01 | 7621.84 | 2.5966 | 81.6543 | 59.8258 | 2233.7408
2037-06-02 12:01 | 8425.8 | 2.812 | 82.3458 | 59.8258 | 2469.3582
2037-06-03 13:01 | 8995.56 | 2.9534 | 82.9191 | 59.8258 | 2636.3384
2037-06-04 14:01 | 9339.87 | 3.0182 | 83.4461 | 59.8258 | 2737.2457
2037-06-05 15:01 | 11738 | 3.8471 | 83.5024 | 59.8258 | 3440.0682
2037-06-06 16:01 | 11450.8 | 3.6943 | 84.2314 | 59.8258 | 3355.8982
2037-06-07 17:01 | 10996.6 | 3.51 | 84.6406 | 59.8258 | 3222.7853
2037-06-08 18:01 | 9348.59 | 2.9047 | 85.1598 | 59.8258 | 2739.8013
2037-06-09 19:01 | 7814.93 | 2.3356 | 85.6778 | 59.8258 | 2290.3299
2037-06-10 20:01 | 5621.56 | 1.6412 | 85.8919 | 59.8258 | 1647.5166
2037-06-11 21:01 | 4278.19 | 1.3461 | 84.41 | 59.8258 | 1253.8137
2037-06-12 22:01 | 3078.59 | 1 | 69.2582 | 59.8258 | 902.2457
2037-06-13 23:01 | 3098.69 | 1 | 68.8737 | 59.8258 | 908.1364
2037-06-15 00:01 | 1760.57 | 1 | 68.7549 | 59.8258 | 515.9721
2037-06-16 01:01 | 103.908 | 1 | 68.5651 | 59.8258 | 30.4524
2037-06-17 02:01 | -132.68 | 0.85742 | 67.4322 | 59.8258 | -38.8847
2037-06-18 03:01 | -90.5637 | 0.72316 | 67.2339 | 59.8258 | -26.5416
2037-06-19 04:01 | 119.274 | 1 | 67.5724 | 59.8258 | 34.9558
2037-06-20 05:01 | 1883.7 | 1 | 67.2165 | 59.8258 | 552.058
2037-06-21 06:01 | 2848.69 | 1 | 67.2052 | 59.8258 | 834.8686
2037-06-22 07:01 | 3140.86 | 1 | 67.3298 | 59.8258 | 920.4952
2037-06-23 08:01 | 3178.76 | 1 | 67.4312 | 59.8258 | 931.6026
2037-06-24 09:01 | 4379.76 | 1.3315 | 82.842 | 59.8258 | 1283.5809
2037-06-25 10:01 | 7458.76 | 2.5341 | 81.4209 | 59.8258 | 2185.9468
2037-06-26 11:01 | 9893.21 | 3.302 | 82.158 | 59.8258 | 2899.4136
2037-06-27 12:01 | 10741.3 | 3.6016 | 82.6936 | 59.8258 | 3147.9643
2037-06-28 13:01 | 11196.8 | 3.6626 | 83.5104 | 59.8258 | 3281.4582
2037-06-29 14:01 | 12642.4 | 4.0693 | 84.1311 | 59.8258 | 3705.1217
2037-06-30 15:01 | 13679.1 | 4.3836 | 84.6842 | 59.8258 | 4008.9485
2037-07-01 16:01 | 13438.2 | 4.3044 | 85.1575 | 59.8258 | 3938.3477
2037-07-02 17:01 | 12884.8 | 4.0466 | 85.6977 | 59.8258 | 3776.1621
2037-07-03 18:01 | 10583.9 | 3.3186 | 85.8759 | 59.8258 | 3101.8349
2037-07-04 19:01 | 8964.74 | 2.7345 | 86.1638 | 59.8258 | 2627.3059
2037-07-05 20:01 | 6665.56 | 1.9669 | 86.4706 | 59.8258 | 1953.4828
2037-07-06 21:01 | 5521.71 | 1.6629 | 85.788 | 59.8258 | 1618.2535
2037-07-07 22:01 | 3293.49 | 1 | 87.8698 | 59.8258 | 965.2266
2037-07-08 23:01 | 3231.62 | 1 | 69.449 | 59.8258 | 947.0943
2037-07-10 00:01 | 3095.27 | 1 | 69.1425 | 59.8258 | 907.1341
2037-07-11 01:01 | 3156.08 | 1 | 68.9236 | 59.8258 | 924.9557
2037-07-12 02:01 | 3105.83 | 1 | 68.7717 | 59.8258 | 910.2289
2037-07-13 03:01 | 3172.26 | 1 | 68.6168 | 59.8258 | 929.6976
2037-07-14 04:01 | 3155.37 | 1 | 68.5311 | 59.8258 | 924.7477
2037-07-15 05:01 | 3159.29 | 1 | 68.4296 | 59.8258 | 925.8965
2037-07-16 06:01 | 3194.84 | 1 | 68.3456 | 59.8258 | 936.3152
2037-07-17 07:01 | 3219.68 | 1 | 92.3329 | 59.8258 | 943.5951
2037-07-18 08:01 | 3264.31 | 1 | 89.0444 | 59.8258 | 956.6748
2037-07-19 09:01 | 5111.16 | 1.618 | 82.9089 | 59.8258 | 1497.9331
2037-07-20 10:01 | 6652.87 | 2.1949 | 82.5483 | 59.8258 | 1949.7637
2037-07-21 11:01 | 9298.05 | 3.1282 | 82.5677 | 59.8258 | 2724.9895
2037-07-22 12:01 | 10468.8 | 3.5539 | 82.9397 | 59.8258 | 3068.1024
2037-07-23 13:01 | 10523 | 3.3938 | 84.0948 | 59.8258 | 3083.9869
2037-07-24 14:01 | 11170.9 | 3.59 | 84.4286 | 59.8258 | 3273.8676
2037-07-25 15:01 | 12744.4 | 4.1591 | 84.4773 | 59.8258 | 3735.0149
2037-07-26 16:01 | 12934.9 | 4.119 | 85.2401 | 59.8258 | 3790.845
2037-07-27 17:01 | 12153.1 | 3.8603 | 85.555 | 59.8258 | 3561.722
2037-07-28 18:01 | 10136.1 | 3.1209 | 86.1186 | 59.8258 | 2970.5977
2037-07-29 19:01 | 8660.26 | 2.6719 | 85.9725 | 59.8258 | 2538.0717
2037-07-30 20:01 | 6293.09 | 1.8844 | 86.2602 | 59.8258 | 1844.3226
2037-07-31 21:01 | 4969.69 | 1.4915 | 85.8444 | 59.8258 | 1456.4724
2037-08-01 22:01 | 3183.85 | 1 | 88.2993 | 59.8258 | 933.0943
2037-08-02 23:01 | 3040.59 | 1 | 69.497 | 59.8258 | 891.109
2037-08-04 00:01 | 0 | 0 | 69.46 | 59.8258 | 0
2037-08-05 01:01 | -116.014 | 0.84035 | 68.1999 | 59.8258 | -34.0003
2037-08-06 02:01 | -255.45 | 1.1422 | 67.3943 | 59.8258 | -74.865
2037-08-07 03:01 | -509.212 | 1.7748 | 66.7905 | 59.8258 | -149.2353
2037-08-08 04:01 | -753.813 | 2.3674 | 66.3477 | 59.8258 | -220.9208
2037-08-09 05:01 | -947.702 | 2.8348 | 65.9691 | 59.8258 | -277.744
2037-08-10 06:01 | -305.55 | 1.1181 | 66.0249 | 59.8258 | -89.5479
2037-08-11 07:01 | 2289.84 | 1 | 66.9762 | 59.8258 | 671.0859
2037-08-12 08:01 | 3021.53 | 1 | 67.169 | 59.8258 | 885.523
2037-08-13 09:01 | 3166.99 | 1 | 82.1781 | 59.8258 | 928.1531
2037-08-14 10:01 | 5806.14 | 1.88 | 81.813 | 59.8258 | 1701.6117
2037-08-15 11:01 | 7547.81 | 2.6042 | 81.3305 | 59.8258 | 2212.0448
2037-08-16 12:01 | 8866.87 | 2.9963 | 82.0886 | 59.8258 | 2598.6231
2037-08-17 13:01 | 9563.17 | 3.1461 | 82.8657 | 59.8258 | 2802.6885
2037-08-18 14:01 | 10170.9 | 3.2572 | 83.5884 | 59.8258 | 2980.7965
2037-08-19 15:01 | 10218.7 | 3.2944 | 83.8224 | 59.8258 | 2994.8053
2037-08-20 16:01 | 12166.6 | 3.921 | 84.0384 | 59.8258 | 3565.6785
2037-08-21 17:01 | 10693.4 | 3.3684 | 84.805 | 59.8258 | 3133.9262
2037-08-22 18:01 | 8827.86 | 2.7572 | 85.0416 | 59.8258 | 2587.1904
2037-08-23 19:01 | 7367.74 | 2.2728 | 85.0681 | 59.8258 | 2159.2714
2037-08-24 20:01 | 6419.06 | 1.9703 | 84.9457 | 59.8258 | 1881.2408
2037-08-25 21:01 | 5557.14 | 1.6643 | 85.1481 | 59.8258 | 1628.637
2037-08-26 22:01 | 4416.17 | 1.3235 | 84.9032 | 59.8258 | 1294.2517
2037-08-27 23:01 | 3085.31 | 1 | 69.0972 | 59.8258 | 904.2151
2037-08-29 00:01 | 0 | 0 | 69.0421 | 59.8258 | 0
2037-08-30 01:01 | -113.037 | 0.77811 | 67.7591 | 59.8258 | -33.1279
2037-08-31 02:01 | -456.086 | 1.6676 | 66.7769 | 59.8258 | -133.6656
2037-09-01 03:01 | -569.417 | 1.8982 | 66.3462 | 59.8258 | -166.8796
2037-09-02 04:01 | -858.235 | 2.641 | 65.9387 | 59.8258 | -251.5238
2037-09-03 05:01 | -870.804 | 2.6205 | 65.6345 | 59.8258 | -255.2075
2037-09-04 06:01 | -222.638 | 0.92275 | 65.8829 | 59.8258 | -65.2488
2037-09-05 07:01 | 2196.48 | 1 | 66.728 | 59.8258 | 643.7247
2037-09-06 08:01 | 2942.99 | 1 | 66.905 | 59.8258 | 862.5052
2037-09-07 09:01 | 3532.66 | 1.1394 | 81.5541 | 59.8258 | 1035.3204
2037-09-08 10:01 | 6630.58 | 2.1637 | 81.477 | 59.8258 | 1943.2312
2037-09-09 11:01 | 8583.48 | 2.9236 | 81.3781 | 59.8258 | 2515.5697
2037-09-10 12:01 | 9878.84 | 3.3529 | 81.9962 | 59.8258 | 2895.2022
2037-09-11 13:01 | 10777.2 | 3.5116 | 83.0275 | 59.8258 | 3158.4855
2037-09-12 14:01 | 11535.2 | 3.7828 | 83.3704 | 59.8258 | 3380.6334
2037-09-13 15:01 | 11806.5 | 3.8173 | 83.9922 | 59.8258 | 3460.1436
2037-09-14 16:01 | 13833.7 | 4.3981 | 84.529 | 59.8258 | 4054.2573
2037-09-15 17:01 | 12013.5 | 3.7983 | 85.1276 | 59.8258 | 3520.8093
2037-09-16 18:01 | 10095.8 | 3.1134 | 85.6227 | 59.8258 | 2958.7869
2037-09-17 19:01 | 8345.66 | 2.5818 | 85.4455 | 59.8258 | 2445.8715
2037-09-18 20:01 | 7307.08 | 2.2638 | 85.2146 | 59.8258 | 2141.4938
2037-09-19 21:01 | 6194.59 | 1.9092 | 85.1038 | 59.8258 | 1815.4551
2037-09-20 22:01 | 5308.14 | 1.6508 | 84.6827 | 59.8258 | 1555.6623
2037-09-21 23:01 | 3299.92 | 1 | 90.8922 | 59.8258 | 967.1111
2037-09-23 00:01 | 3239.52 | 1 | 69.0177 | 59.8258 | 949.4096
2037-09-24 01:01 | 3154.55 | 1 | 68.791 | 59.8258 | 924.5073
2037-09-25 02:01 | 3220.83 | 1 | 68.621 | 59.8258 | 943.9321
2037-09-26 03:01 | 3195.87 | 1 | 68.4988 | 59.8258 | 936.617
2037-09-27 04:01 | 3112.96 | 1 | 68.3768 | 59.8258 | 912.3185
2037-09-28 05:01 | 3127.64 | 1 | 68.2983 | 59.8258 | 916.6208
2037-09-29 06:01 | 3169.91 | 1 | 68.2409 | 59.8258 | 929.0089
2037-09-30 07:01 | 3357.38 | 1 | 92.7127 | 59.8258 | 983.9509
2037-10-01 08:01 | 3241.7 | 1 | 85.0804 | 59.8258 | 950.0485
2037-10-02 09:01 | 5763.71 | 1.8293 | 82.7864 | 59.8258 | 1689.1767
2037-10-03 10:01 | 7772.07 | 2.5719 | 82.4773 | 59.8258 | 2277.7689
2037-10-04 11:01 | 8737.04 | 2.8174 | 83.2564 | 59.8258 | 2560.5737
2037-10-05 12:01 | 10334.7 | 3.4212 | 83.2192 | 59.8258 | 3028.8016
2037-10-06 13:01 | 11304.2 | 3.7034 | 83.7796 | 59.8258 | 3312.934
2037-10-07 14:01 | 11690.5 | 3.7656 | 84.4367 | 59.8258 | 3426.1473
2037-10-08 15:01 | 13092.7 | 4.1836 | 84.847 | 59.8258 | 3837.0916
2037-10-09 16:01 | 13337.3 | 4.2035 | 85.419 | 59.8258 | 3908.7768
2037-10-10 17:01 | 12629.2 | 3.9656 | 85.7859 | 59.8258 | 3701.2532
2037-10-11 18:01 | 11006.5 | 3.4291 | 86.044 | 59.8258 | 3225.6867
2037-10-12 19:01 | 9752.37 | 2.9672 | 86.3415 | 59.8258 | 2858.1375
2037-10-13 20:01 | 7661.01 | 2.2502 | 86.7806 | 59.8258 | 2245.2204
2037-10-14 21:01 | 6476.02 | 1.9495 | 86.0905 | 59.8258 | 1897.9341
2037-10-15 22:01 | 4512.68 | 1.3458 | 85.9119 | 59.8258 | 1322.536
2037-10-16 23:01 | 3960.09 | 1.2065 | 85.1518 | 59.8258 | 1160.5878
2037-10-18 00:01 | 3370.15 | 1 | 86.6847 | 59.8258 | 987.6935
2037-10-19 01:01 | 3171.09 | 1 | 87.5167 | 59.8258 | 929.3547
2037-10-20 02:01 | 3144.74 | 1 | 87.2052 | 59.8258 | 921.6323
2037-10-21 03:01 | 3288.25 | 1 | 86.5175 | 59.8258 | 963.6909
2037-10-22 04:01 | 3151.37 | 1 | 83.3996 | 59.8258 | 923.5754
2037-10-23 05:01 | 4039.28 | 1.2678 | 83.4308 | 59.8258 | 1183.7961
2037-10-24 06:01 | 4011.26 | 1.2464 | 83.6099 | 59.8258 | 1175.5843
2037-10-25 07:01 | 5067.05 | 1.604 | 83.3251 | 59.8258 | 1485.0058
2037-10-26 08:01 | 5240.4 | 1.6757 | 83.3099 | 59.8258 | 1535.8096
2037-10-27 09:01 | 6887.46 | 2.367 | 82.3936 | 59.8258 | 2018.5153
2037-10-28 10:01 | 9540.8 | 3.254 | 82.7493 | 59.8258 | 2796.1325
2037-10-29 11:01 | 10385.5 | 3.5258 | 83.3035 | 59.8258 | 3043.6896
2037-10-30 12:01 | 11975.1 | 4.0644 | 83.6952 | 59.8258 | 3509.5554
2037-10-31 13:01 | 13365.2 | 4.5456 | 84.1031 | 59.8258 | 3916.9535
2037-11-01 14:01 | 14032.7 | 4.5929 | 85.1302 | 59.8258 | 4112.5784
2037-11-02 15:01 | 15505.6 | 5.0145 | 85.7012 | 59.8258 | 4544.2428
2037-11-03 16:01 | 15328 | 4.8491 | 86.4748 | 59.8258 | 4492.1934
2037-11-04 17:01 | 14591.6 | 4.6103 | 86.8059 | 59.8258 | 4276.3758
2037-11-05 18:01 | 12205.5 | 3.8418 | 87.0247 | 59.8258 | 3577.0789
2037-11-06 19:01 | 10566.4 | 3.2023 | 87.439 | 59.8258 | 3096.7062
2037-11-07 20:01 | 8113.26 | 2.452 | 87.2788 | 59.8258 | 2377.7618
2037-11-08 21:01 | 6785.99 | 2.0299 | 87.0297 | 59.8258 | 1988.7774
2037-11-09 22:01 | 4428 | 1.2887 | 87.059 | 59.8258 | 1297.7187
2037-11-10 23:01 | 3364.32 | 1.0577 | 85.3472 | 59.8258 | 985.9849
2037-11-12 00:01 | 3208.58 | 1 | 89.6723 | 59.8258 | 940.342
2037-11-13 01:01 | 3097.81 | 1 | 69.7436 | 59.8258 | 907.8785
2037-11-14 02:01 | 3140.03 | 1 | 69.4991 | 59.8258 | 920.252
2037-11-15 03:01 | 3156.48 | 1 | 69.2775 | 59.8258 | 925.073
2037-11-16 04:01 | 3182.62 | 1 | 69.1161 | 59.8258 | 932.7338
2037-11-17 05:01 | 3136.9 | 1 | 93.0961 | 59.8258 | 919.3346
2037-11-18 06:01 | 3183.6 | 1 | 93.3897 | 59.8258 | 933.0211
2037-11-19 07:01 | 3220.12 | 1 | 83.7719 | 59.8258 | 943.724
2037-11-20 08:01 | 4488.85 | 1.3779 | 83.8787 | 59.8258 | 1315.5521
2037-11-21 09:01 | 7068.15 | 2.3269 | 82.966 | 59.8258 | 2071.4703
2037-11-22 10:01 | 9745.35 | 3.2477 | 83.173 | 59.8258 | 2856.0802
2037-11-23 11:01 | 11915.6 | 3.9104 | 83.9375 | 59.8258 | 3492.1176
2037-11-24 12:01 | 13094.6 | 4.2407 | 84.7187 | 59.8258 | 3837.6484
2037-11-25 13:01 | 13179.5 | 4.377 | 84.9021 | 59.8258 | 3862.5302
2037-11-26 14:01 | 13050.8 | 4.2048 | 85.6955 | 59.8258 | 3824.8119
2037-11-27 15:01 | 14893.1 | 4.7962 | 85.9254 | 59.8258 | 4364.7368
2037-11-28 16:01 | 15252.3 | 4.8594 | 86.501 | 59.8258 | 4470.0079
2037-11-29 17:01 | 14455.3 | 4.546 | 87.0254 | 59.8258 | 4236.4302
2037-11-30 18:01 | 12301.6 | 3.8343 | 87.3023 | 59.8258 | 3605.2431
2037-12-01 19:01 | 11020.3 | 3.4064 | 87.3205 | 59.8258 | 3229.7311
2037-12-02 20:01 | 8524.1 | 2.6389 | 87.1862 | 59.8258 | 2498.1671
2037-12-03 21:01 | 7371.23 | 2.2498 | 87.028 | 59.8258 | 2160.2943
2037-12-04 22:01 | 5201.04 | 1.5723 | 86.8189 | 59.8258 | 1524.2744
2037-12-05 23:01 | 4184.19 | 1.2609 | 86.3668 | 59.8258 | 1226.265
2037-12-07 00:01 | 3521.19 | 1.0917 | 85.5078 | 59.8258 | 1031.9589
2037-12-08 01:01 | 3212.22 | 1 | 86.6221 | 59.8258 | 941.4088
2037-12-09 02:01 | 3203.35 | 1 | 91.3699 | 59.8258 | 938.8092
2037-12-10 03:01 | 3183.2 | 1 | 89.6051 | 59.8258 | 932.9038
2037-12-11 04:01 | 3135.92 | 1 | 86.5325 | 59.8258 | 919.0474
2037-12-12 05:01 | 3576.61 | 1.1307 | 84.0252 | 59.8258 | 1048.2009
2037-12-13 06:01 | 3452.83 | 1.0831 | 84.0922 | 59.8258 | 1011.9246
2037-12-14 07:01 | 4694.6 | 1.4414 | 84.325 | 59.8258 | 1375.8514
2037-12-15 08:01 | 5693.63 | 1.8284 | 83.7703 | 59.8258 | 1668.6382
2037-12-16 09:01 | 8329.85 | 2.8011 | 83.2852 | 59.8258 | 2441.2381
2037-12-17 10:01 | 10765.1 | 3.5248 | 84.0648 | 59.8258 | 3154.9394
2037-12-18 11:01 | 12175.9 | 3.9477 | 84.7487 | 59.8258 | 3568.404
2037-12-19 12:01 | 13146.9 | 4.1924 | 85.4928 | 59.8258 | 3852.9761
2037-12-20 13:01 | 13406.9 | 4.3277 | 85.769 | 59.8258 | 3929.1745
2037-12-21 14:01 | 13331.5 | 4.1214 | 86.7514 | 59.8258 | 3907.077
2037-12-22 15:01 | 14364.2 | 4.5714 | 86.5447 | 59.8258 | 4209.7315
2037-12-23 16:01 | 14145.3 | 4.5215 | 86.7824 | 59.8258 | 4145.5782
2037-12-24 17:01 | 12694.8 | 4.0855 | 86.8779 | 59.8258 | 3720.4786
2037-12-25 18:01 | 11621.7 | 3.5759 | 87.5021 | 59.8258 | 3405.9841
2037-12-26 19:01 | 10235.5 | 3.2184 | 87.0963 | 59.8258 | 2999.7289
2037-12-27 20:01 | 8268.41 | 2.4861 | 87.6151 | 59.8258 | 2423.2318
2037-12-28 21:01 | 7306.21 | 2.176 | 87.4144 | 59.8258 | 2141.2388
2037-12-29 22:01 | 5522.49 | 1.596 | 87.5697 | 59.8258 | 1618.4821
2037-12-30 23:01 | 4347.39 | 1.3908 | 85.6339 | 59.8258 | 1274.0942
2038-01-01 00:01 | 3750.34 | 1.195 | 85.2759 | 59.8258 | 1099.1162
2038-01-02 01:01 | 3216.26 | 1.0042 | 85.2306 | 59.8258 | 942.5928
2038-01-03 02:01 | 3110.8 | 1 | 85.4874 | 59.8258 | 911.6855
2038-01-04 03:01 | 3201.06 | 1 | 86.1658 | 59.8258 | 938.1381
2038-01-05 04:01 | 3140.3 | 1 | 85.3824 | 59.8258 | 920.3311
2038-01-06 05:01 | 3655.26 | 1.183 | 83.8586 | 59.8258 | 1071.251
2038-01-07 06:01 | 3483.48 | 1.1071 | 84.0777 | 59.8258 | 1020.9072
2038-01-08 07:01 | 3529.85 | 1.179 | 83.3069 | 59.8258 | 1034.4969
2038-01-09 08:01 | 3230.3 | 1.0673 | 83.3989 | 59.8258 | 946.7075
2038-01-10 09:01 | 4111.52 | 1.3726 | 83.1347 | 59.8258 | 1204.9676
2038-01-11 10:01 | 6345.71 | 2.1102 | 83.1903 | 59.8258 | 1859.744
2038-01-12 11:01 | 8311.33 | 2.7478 | 83.522 | 59.8258 | 2435.8104
2038-01-13 12:01 | 9522.21 | 3.106 | 84.0743 | 59.8258 | 2790.6843
2038-01-14 13:01 | 9729.1 | 3.1408 | 84.5676 | 59.8258 | 2851.3177
2038-01-15 14:01 | 10554.3 | 3.4145 | 84.7806 | 59.8258 | 3093.16
2038-01-16 15:01 | 10427.8 | 3.3198 | 85.2812 | 59.8258 | 3056.0865
2038-01-17 16:01 | 11231.2 | 3.5801 | 85.4083 | 59.8258 | 3291.5398
2038-01-18 17:01 | 10214.4 | 3.2277 | 85.7381 | 59.8258 | 2993.5451
2038-01-19 18:01 | 8592.75 | 2.5892 | 86.4604 | 59.8258 | 2518.2864
2038-01-20 19:01 | 7143.57 | 2.2275 | 85.7859 | 59.8258 | 2093.5737
2038-01-21 20:01 | 4737.4 | 1.4661 | 85.6777 | 59.8258 | 1388.3949
2038-01-22 21:01 | 3451.11 | 1.1037 | 84.7887 | 59.8258 | 1011.4205
2038-01-23 22:01 | 3056.76 | 1 | 69.8075 | 59.8258 | 895.8479
2038-01-24 23:01 | 0 | 0 | 69.7732 | 59.8258 | 0
2038-01-26 00:01 | -180.933 | 0.94958 | 68.262 | 59.8258 | -53.0262
2038-01-27 01:01 | -452.539 | 1.6329 | 67.4263 | 59.8258 | -132.6261
2038-01-28 02:01 | -638.563 | 2.0656 | 66.9651 | 59.8258 | -187.1443
2038-01-29 03:01 | -886.663 | 2.6815 | 66.5786 | 59.8258 | -259.8553
2038-01-30 04:01 | -929.056 | 2.7504 | 66.2434 | 59.8258 | -272.2794
2038-01-31 05:01 | -1000.93 | 2.9396 | 66.0186 | 59.8258 | -293.3436
2038-02-01 06:01 | -308.237 | 1.1148 | 66.121 | 59.8258 | -90.3353
2038-02-02 07:01 | 1058.65 | 1 | 67.2229 | 59.8258 | 310.2597
2038-02-03 08:01 | 3130.6 | 1 | 67.1458 | 59.8258 | 917.4883
2038-02-04 09:01 | 3215.75 | 1 | 91.2487 | 59.8258 | 942.4433
2038-02-05 10:01 | 3233.5 | 1 | 83.9545 | 59.8258 | 947.6453
2038-02-06 11:01 | 3591.42 | 1.1344 | 82.3574 | 59.8258 | 1052.5413
2038-02-07 12:01 | 4018.46 | 1.2545 | 82.6116 | 59.8258 | 1177.6944
2038-02-08 13:01 | 4455.1 | 1.3869 | 82.7382 | 59.8258 | 1305.6609
2038-02-09 14:01 | 5036.35 | 1.5553 | 82.9131 | 59.8258 | 1476.0085
2038-02-10 15:01 | 5325.08 | 1.744 | 82.1615 | 59.8258 | 1560.6269
2038-02-11 16:01 | 7893.77 | 2.6681 | 81.7997 | 59.8258 | 2313.4356
2038-02-12 17:01 | 7441.22 | 2.3505 | 83.1501 | 59.8258 | 2180.8063
2038-02-13 18:01 | 6459.84 | 1.9952 | 83.6649 | 59.8258 | 1893.1922
2038-02-14 19:01 | 5592.8 | 1.7411 | 83.5299 | 59.8258 | 1639.0879
2038-02-15 20:01 | 5062.55 | 1.555 | 83.6515 | 59.8258 | 1483.6869
2038-02-16 21:01 | 4598.05 | 1.4308 | 83.398 | 59.8258 | 1347.5554
2038-02-17 22:01 | 4104.49 | 1.3151 | 82.8653 | 59.8258 | 1202.9073
2038-02-18 23:01 | 3047.34 | 1 | 68.2345 | 59.8258 | 893.0872
2038-02-20 00:01 | 3171.54 | 1 | 68.045 | 59.8258 | 929.4866
2038-02-21 01:01 | 3158.1 | 1 | 67.9744 | 59.8258 | 925.5477
2038-02-22 02:01 | 1489.04 | 1 | 68.0877 | 59.8258 | 436.3945
2038-02-23 03:01 | 690.367 | 1 | 67.8987 | 59.8258 | 202.3266
2038-02-24 04:01 | 100.635 | 1 | 67.6592 | 59.8258 | 29.4932
2038-02-25 05:01 | 85.0269 | 1 | 67.4188 | 59.8258 | 24.9189
2038-02-26 06:01 | 2207.39 | 1 | 67.0493 | 59.8258 | 646.9221
2038-02-27 07:01 | 2890.53 | 1 | 89.6653 | 59.8258 | 847.1307
2038-02-28 08:01 | 3042.78 | 1 | 67.2356 | 59.8258 | 891.7508
2038-03-01 09:01 | 3106.46 | 1 | 67.3005 | 59.8258 | 910.4136
2038-03-02 10:01 | 3163.79 | 1 | 89.8587 | 59.8258 | 927.2153
2038-03-03 11:01 | 3309.86 | 1.019 | 82.482 | 59.8258 | 970.0242
2038-03-04 12:01 | 3844.94 | 1.1858 | 82.4669 | 59.8258 | 1126.8407
2038-03-05 13:01 | 4782.74 | 1.4332 | 82.9362 | 59.8258 | 1401.6827
2038-03-06 14:01 | 7014.5 | 2.3533 | 81.4405 | 59.8258 | 2055.747
2038-03-07 15:01 | 7743.23 | 2.5721 | 81.9562 | 59.8258 | 2269.3167
2038-03-08 16:01 | 9626.65 | 3.1387 | 82.5125 | 59.8258 | 2821.2926
2038-03-09 17:01 | 8569.65 | 2.6555 | 83.6987 | 59.8258 | 2511.5165
2038-03-10 18:01 | 7533.13 | 2.18 | 84.8994 | 59.8258 | 2207.7425
2038-03-11 19:01 | 6265.31 | 1.8804 | 84.329 | 59.8258 | 1836.1811
2038-03-12 20:01 | 5450.2 | 1.6145 | 84.4105 | 59.8258 | 1597.2959
2038-03-13 21:01 | 4555.35 | 1.3955 | 83.7696 | 59.8258 | 1335.0413
2038-03-14 22:01 | 3934.51 | 1.2214 | 83.3736 | 59.8258 | 1153.0911
2038-03-15 23:01 | 3175.11 | 1 | 68.2101 | 59.8258 | 930.5329
2038-03-17 00:01 | 3053.89 | 1 | 68.0413 | 59.8258 | 895.0068
2038-03-18 01:01 | 0 | 0 | 68.198 | 59.8258 | 0
2038-03-19 02:01 | 165.257 | 1 | 67.6831 | 59.8258 | 48.432
2038-03-20 03:01 | 604.365 | 1 | 67.3615 | 59.8258 | 177.1219
2038-03-21 04:01 | 2079.3 | 1 | 67.1004 | 59.8258 | 609.3827
2038-03-22 05:01 | 2813.18 | 1 | 67.1055 | 59.8258 | 824.4617
2038-03-23 06:01 | 2971.87 | 1 | 67.1636 | 59.8258 | 870.9691
2038-03-24 07:01 | 3102.36 | 1 | 67.2257 | 59.8258 | 909.212
2038-03-25 08:01 | -40.7255 | 0.6517 | 67.2726 | 59.8258 | -11.9355
2038-03-26 09:01 | 84.582 | 1 | 67.1567 | 59.8258 | 24.7885
2038-03-27 10:01 | 2990.92 | 1 | 66.6579 | 59.8258 | 876.5521
2038-03-28 11:01 | 2116.49 | 1 | 66.9843 | 59.8258 | 620.282
2038-03-29 12:01 | 2879.78 | 1 | 66.8645 | 59.8258 | 843.9802
2038-03-30 13:01 | 3054.13 | 1 | 66.8756 | 59.8258 | 895.0771
2038-03-31 14:01 | 3224.57 | 1 | 66.9522 | 59.8258 | 945.0282
2038-04-01 15:01 | 3835.73 | 1.1719 | 82.2903 | 59.8258 | 1124.1415
2038-04-02 16:01 | 4824.64 | 1.4782 | 82.2307 | 59.8258 | 1413.9624
2038-04-03 17:01 | 5176.53 | 1.6529 | 81.7706 | 59.8258 | 1517.0912
2038-04-04 18:01 | 4335.72 | 1.3361 | 82.4036 | 59.8258 | 1270.6741
2038-04-05 19:01 | 3396.49 | 1.0678 | 82.0627 | 59.8258 | 995.413
2038-04-06 20:01 | 3018.91 | 1 | 67.1626 | 59.8258 | 884.7552
2038-04-07 21:01 | 3052 | 1 | 67.0895 | 59.8258 | 894.4529
2038-04-08 22:01 | 0 | 0 | 67.299 | 59.8258 | 0
2038-04-09 23:01 | -371.026 | 1.4921 | 65.7024 | 59.8258 | -108.737
2038-04-11 00:01 | -581.815 | 1.971 | 65.1655 | 59.8258 | -170.5131
2038-04-12 01:01 | -594.373 | 1.9686 | 64.9458 | 59.8258 | -174.1935
2038-04-13 02:01 | -492.454 | 1.7018 | 64.8478 | 59.8258 | -144.324
2038-04-14 03:01 | -241.598 | 1.062 | 64.9894 | 59.8258 | -70.8054
2038-04-15 04:01 | -230.8 | 1.0874 | 64.9987 | 59.8258 | -67.6408
2038-04-16 05:01 | 1069.27 | 1 | 65.7988 | 59.8258 | 313.3721
2038-04-17 06:01 | 774.832 | 1 | 65.9238 | 59.8258 | 227.0808
2038-04-18 07:01 | 1679.53 | 1 | 65.8345 | 59.8258 | 492.2217
2038-04-19 08:01 | -163.555 | 0.98994 | 65.3353 | 59.8258 | -47.9332
2038-04-20 09:01 | 1830.24 | 1 | 65.7327 | 59.8258 | 536.3904
2038-04-21 10:01 | 2847.75 | 1 | 65.8035 | 59.8258 | 834.5931
2038-04-22 11:01 | 3117.45 | 1 | 85.4903 | 59.8258 | 913.6344
2038-04-23 12:01 | 3207.41 | 1 | 81.9874 | 59.8258 | 939.9991
2038-04-24 13:01 | 4921.15 | 1.5666 | 80.8327 | 59.8258 | 1442.2467
2038-04-25 14:01 | 8010.28 | 2.7917 | 79.9034 | 59.8258 | 2347.5813
2038-04-26 15:01 | 9373.83 | 3.1636 | 80.9192 | 59.8258 | 2747.1984
2038-04-27 16:01 | 10149.3 | 3.384 | 81.5867 | 59.8258 | 2974.4662
2038-04-28 17:01 | 9655.8 | 3.0847 | 82.5994 | 59.8258 | 2829.8356
2038-04-29 18:01 | 8021.85 | 2.4089 | 83.7855 | 59.8258 | 2350.9722
2038-04-30 19:01 | 6673.22 | 2.0188 | 83.6868 | 59.8258 | 1955.7277
2038-05-01 20:01 | 4278.46 | 1.2552 | 84.0633 | 59.8258 | 1253.8929
2038-05-02 21:01 | 3274.7 | 1 | 83.8468 | 59.8258 | 959.7198
2038-05-03 22:01 | 3052.22 | 1 | 67.5676 | 59.8258 | 894.5174
2038-05-04 23:01 | 233.398 | 1 | 67.6444 | 59.8258 | 68.4022
2038-05-06 00:01 | -7.9905 | 0.5785 | 67.1882 | 59.8258 | -2.3418
2038-05-07 01:01 | -225.283 | 1.0947 | 65.9105 | 59.8258 | -66.0239
2038-05-08 02:01 | -363.465 | 1.4254 | 65.4567 | 59.8258 | -106.5211
2038-05-09 03:01 | -482.686 | 1.7166 | 65.1151 | 59.8258 | -141.4613
2038-05-10 04:01 | -462.66 | 1.6441 | 64.8832 | 59.8258 | -135.5923
2038-05-11 05:01 | -95.271 | 0.6801 | 65.3736 | 59.8258 | -27.9212
2038-05-12 06:01 | -142.763 | 0.88702 | 65.199 | 59.8258 | -41.8397
2038-05-13 07:01 | 2618.1 | 1 | 65.607 | 59.8258 | 767.2894
2038-05-14 08:01 | 644.517 | 1 | 66.1033 | 59.8258 | 188.8893
2038-05-15 09:01 | 3032.94 | 1 | 82.6152 | 59.8258 | 888.867
2038-05-16 10:01 | 5946.02 | 2.0174 | 79.723 | 59.8258 | 1742.6064
2038-05-17 11:01 | 7806.71 | 2.7681 | 79.716 | 59.8258 | 2287.9209
2038-05-18 12:01 | 9084.66 | 3.0417 | 81.0535 | 59.8258 | 2662.451
2038-05-19 13:01 | 9596.68 | 3.1475 | 81.8122 | 59.8258 | 2812.5093
2038-05-20 14:01 | 10088.7 | 3.3109 | 82.2398 | 59.8258 | 2956.7061
2038-05-21 15:01 | 11309.5 | 3.6542 | 82.8209 | 59.8258 | 3314.4873
2038-05-22 16:01 | 11116.4 | 3.542 | 83.4315 | 59.8258 | 3257.8952
2038-05-23 17:01 | 10444.1 | 3.2241 | 84.151 | 59.8258 | 3060.8636
2038-05-24 18:01 | 8098.96 | 2.4829 | 84.3845 | 59.8258 | 2373.5709
2038-05-25 19:01 | 6719.51 | 2.0811 | 84.0544 | 59.8258 | 1969.294
2038-05-26 20:01 | 4414.79 | 1.348 | 84.0886 | 59.8258 | 1293.8472
2038-05-27 21:01 | 3442.27 | 1.0829 | 83.2632 | 59.8258 | 1008.8298
2038-05-28 22:01 | 3141.79 | 1 | 68.1018 | 59.8258 | 920.7678
2038-05-29 23:01 | 2989.9 | 1 | 67.8676 | 59.8258 | 876.2532
2038-05-31 00:01 | 0 | 0 | 67.9533 | 59.8258 | 0
2038-06-01 01:01 | -68.0856 | 0.61445 | 66.8986 | 59.8258 | -19.9539
2038-06-02 02:01 | -178.789 | 0.97454 | 66.236 | 59.8258 | -52.3979
2038-06-03 03:01 | -89.1082 | 0.71557 | 66.2756 | 59.8258 | -26.115
2038-06-04 04:01 | 99.3655 | 1 | 66.6382 | 59.8258 | 29.1212
2038-06-05 05:01 | 1999.97 | 1 | 66.2983 | 59.8258 | 586.1333
2038-06-06 06:01 | 1954.16 | 1 | 66.4721 | 59.8258 | 572.7078
2038-06-07 07:01 | 3064.33 | 1 | 66.4187 | 59.8258 | 898.0665
2038-06-08 08:01 | 3091.71 | 1 | 84.2772 | 59.8258 | 906.0908
2038-06-09 09:01 | 5441.89 | 1.7237 | 81.3841 | 59.8258 | 1594.8605
2038-06-10 10:01 | 7876.7 | 2.6484 | 80.9111 | 59.8258 | 2308.4329
2038-06-11 11:01 | 9834.54 | 3.2684 | 81.5728 | 59.8258 | 2882.2192
2038-06-12 12:01 | 11033 | 3.5932 | 82.432 | 59.8258 | 3233.4531
2038-06-13 13:01 | 11665.9 | 3.7701 | 83.0559 | 59.8258 | 3418.9378
2038-06-14 14:01 | 12453.6 | 3.963 | 83.727 | 59.8258 | 3649.7899
2038-06-15 15:01 | 13351.4 | 4.3692 | 83.744 | 59.8258 | 3912.9091
2038-06-16 16:01 | 12847.7 | 4.0595 | 84.657 | 59.8258 | 3765.2892
2038-06-17 17:01 | 11517.2 | 3.6345 | 84.8866 | 59.8258 | 3375.3581
2038-06-18 18:01 | 9611.7 | 2.9327 | 85.4089 | 59.8258 | 2816.9112
2038-06-19 19:01 | 8419.12 | 2.6126 | 85.0009 | 59.8258 | 2467.4005
2038-06-20 20:01 | 6573.41 | 1.9111 | 85.8358 | 59.8258 | 1926.4763
2038-06-21 21:01 | 5364.17 | 1.4991 | 86.152 | 59.8258 | 1572.083
2038-06-22 22:01 | 3301.61 | 1 | 87.401 | 59.8258 | 967.6064
2038-06-23 23:01 | 3170.33 | 1 | 93.2089 | 59.8258 | 929.132
2038-06-25 00:01 | 3179 | 1 | 68.4098 | 59.8258 | 931.6729
2038-06-26 01:01 | 3078.51 | 1 | 68.2421 | 59.8258 | 902.2222
2038-06-27 02:01 | 3194.22 | 1 | 68.0698 | 59.8258 | 936.1335
2038-06-28 03:01 | 3187.33 | 1 | 67.9463 | 59.8258 | 934.1142
2038-06-29 04:01 | 3205.14 | 1 | 67.8661 | 59.8258 | 939.3338
2038-06-30 05:01 | 3196.32 | 1 | 90.8107 | 59.8258 | 936.7489
2038-07-01 06:01 | 3250.36 | 1 | 92.0281 | 59.8258 | 952.5865
2038-07-02 07:01 | 3194.75 | 1 | 89.8106 | 59.8258 | 936.2888
2038-07-03 08:01 | 3132.17 | 1 | 67.6514 | 59.8258 | 917.9484
2038-07-04 09:01 | 3113.58 | 1 | 67.6138 | 59.8258 | 912.5002
2038-07-05 10:01 | 3174.14 | 1 | 67.5571 | 59.8258 | 930.2486
2038-07-06 11:01 | 3170.57 | 1 | 89.3015 | 59.8258 | 929.2023
2038-07-07 12:01 | 3220.86 | 1.0069 | 82.3063 | 59.8258 | 943.9409
2038-07-08 13:01 | 3643.83 | 1.1529 | 82.0718 | 59.8258 | 1067.9012
2038-07-09 14:01 | 4085.88 | 1.2317 | 82.7637 | 59.8258 | 1197.4532
2038-07-10 15:01 | 5776.51 | 1.9013 | 81.4802 | 59.8258 | 1692.928
2038-07-11 16:01 | 6958.41 | 2.2725 | 81.7795 | 59.8258 | 2039.3087
2038-07-12 17:01 | 7124.27 | 2.3143 | 82.1075 | 59.8258 | 2087.9174
2038-07-13 18:01 | 6000.87 | 1.7848 | 83.5792 | 59.8258 | 1758.6814
2038-07-14 19:01 | 5125.42 | 1.5287 | 83.5092 | 59.8258 | 1502.1123
2038-07-15 20:01 | 3222.15 | 1 | 84.3463 | 59.8258 | 944.3189
2038-07-16 21:01 | 3108.48 | 1 | 91.524 | 59.8258 | 911.0056
2038-07-17 22:01 | 1814.78 | 1 | 67.5236 | 59.8258 | 531.8595
2038-07-18 23:01 | -102.642 | 0.82081 | 66.8494 | 59.8258 | -30.0814
2038-07-20 00:01 | -186.576 | 0.98137 | 66.1313 | 59.8258 | -54.68
2038-07-21 01:01 | -290.965 | 1.2426 | 65.6689 | 59.8258 | -85.2734
2038-07-22 02:01 | -663.31 | 2.203 | 65.1973 | 59.8258 | -194.397
2038-07-23 03:01 | -950.031 | 2.8928 | 64.8474 | 59.8258 | -278.4266
2038-07-24 04:01 | -1275.24 | 3.7113 | 64.5542 | 59.8258 | -373.736
2038-07-25 05:01 | -1462.3 | 4.1523 | 64.3089 | 59.8258 | -428.5578
2038-07-26 06:01 | -1011.57 | 2.9086 | 64.1375 | 59.8258 | -296.4619
2038-07-27 07:01 | -198.051 | 0.84413 | 64.5552 | 59.8258 | -58.043
2038-07-28 08:01 | 324.214 | 1 | 65.6299 | 59.8258 | 95.0177
2038-07-29 09:01 | 2434.21 | 1 | 82.8532 | 59.8258 | 713.3965
2038-07-30 10:01 | 3652.07 | 1.2676 | 79.1193 | 59.8258 | 1070.3161
2038-07-31 11:01 | 5792.1 | 1.9519 | 79.8326 | 59.8258 | 1697.4969
2038-08-01 12:01 | 6582.82 | 2.1658 | 80.6146 | 59.8258 | 1929.2341
2038-08-02 13:01 | 6461.92 | 2.1645 | 80.7452 | 59.8258 | 1893.8018
2038-08-03 14:01 | 7478.86 | 2.442 | 81.3184 | 59.8258 | 2191.8375
2038-08-04 15:01 | 7594.89 | 2.4625 | 81.6997 | 59.8258 | 2225.8425
2038-08-05 16:01 | 9570.72 | 3.0899 | 81.9663 | 59.8258 | 2804.9012
2038-08-06 17:01 | 7656.48 | 2.4055 | 82.7681 | 59.8258 | 2243.8928
2038-08-07 18:01 | 5381.64 | 1.6412 | 83.2345 | 59.8258 | 1577.203
2038-08-08 19:01 | 3931.1 | 1.2257 | 82.6652 | 59.8258 | 1152.0917
2038-08-09 20:01 | 3172.65 | 1 | 84.1053 | 59.8258 | 929.8119
2038-08-10 21:01 | 3140.17 | 1 | 90.2036 | 59.8258 | 920.293
2038-08-11 22:01 | 3151.87 | 1 | 67.0833 | 59.8258 | 923.7219
2038-08-12 23:01 | -618.363 | 2.1162 | 65.9304 | 59.8258 | -181.2243
2038-08-14 00:01 | -993.856 | 3.0055 | 65.1753 | 59.8258 | -291.2704
2038-08-15 01:01 | -1177.72 | 3.4332 | 64.7381 | 59.8258 | -345.1557
2038-08-16 02:01 | -1293.8 | 3.7171 | 64.4682 | 59.8258 | -379.1754
2038-08-17 03:01 | -1430.81 | 4.0717 | 64.215 | 59.8258 | -419.329
2038-08-18 04:01 | -1543.93 | 4.3594 | 63.9376 | 59.8258 | -452.4812
2038-08-19 05:01 | -1586.05 | 4.4564 | 63.7693 | 59.8258 | -464.8254
2038-08-20 06:01 | -940.346 | 2.7045 | 63.6798 | 59.8258 | -275.5882
2038-08-21 07:01 | 0 | 0 | 65.2534 | 59.8258 | 0
2038-08-22 08:01 | 97.1594 | 1 | 65.3297 | 59.8258 | 28.4746
2038-08-23 09:01 | 2813.29 | 1 | 65.096 | 59.8258 | 824.4939
2038-08-24 10:01 | 3992.77 | 1.2821 | 79.9417 | 59.8258 | 1170.1654
2038-08-25 11:01 | 5711.39 | 1.878 | 79.9251 | 59.8258 | 1673.8432
2038-08-26 12:01 | 7049.99 | 2.3028 | 80.4327 | 59.8258 | 2066.1481
2038-08-27 13:01 | 7717.18 | 2.5318 | 80.8123 | 59.8258 | 2261.6822
2038-08-28 14:01 | 8258.48 | 2.7128 | 81.1828 | 59.8258 | 2420.3216
2038-08-29 15:01 | 8092.15 | 2.6576 | 81.4992 | 59.8258 | 2371.5751
2038-08-30 16:01 | 9834.58 | 3.1744 | 81.9278 | 59.8258 | 2882.2309
2038-08-31 17:01 | 7903.75 | 2.5264 | 82.4714 | 59.8258 | 2316.3605
2038-09-01 18:01 | 6144.91 | 1.9522 | 82.5898 | 59.8258 | 1800.8953
2038-09-02 19:01 | 4899.89 | 1.5201 | 82.7624 | 59.8258 | 1436.016
2038-09-03 20:01 | 3653.01 | 1.1421 | 82.4719 | 59.8258 | 1070.5915
2038-09-04 21:01 | 3161.54 | 1 | 84.9718 | 59.8258 | 926.5559
2038-09-05 22:01 | 3146.32 | 1 | 92.0838 | 59.8258 | 922.0954
2038-09-06 23:01 | 0 | 0 | 67.2521 | 59.8258 | 0
2038-09-08 00:01 | -626.573 | 2.1431 | 65.4082 | 59.8258 | -183.6304
2038-09-09 01:01 | -963.109 | 2.9328 | 64.8545 | 59.8258 | -282.2594
2038-09-10 02:01 | -1197.57 | 3.5012 | 64.5266 | 59.8258 | -350.9731
2038-09-11 03:01 | -1211.61 | 3.4993 | 64.265 | 59.8258 | -355.0878
2038-09-12 04:01 | -1085.05 | 3.1684 | 64.0446 | 59.8258 | -317.9968
2038-09-13 05:01 | -953.469 | 2.8474 | 63.9599 | 59.8258 | -279.4342
2038-09-14 06:01 | -899.419 | 2.7326 | 63.9058 | 59.8258 | -263.5937
2038-09-15 07:01 | -426.461 | 1.4738 | 64.0126 | 59.8258 | -124.9834
2038-09-16 08:01 | 0 | 1 | 65.3393 | 59.8258 | 0
2038-09-17 09:01 | 3344.67 | 1.0779 | 79.561 | 59.8258 | 980.226
2038-09-18 10:01 | 6468.97 | 2.1735 | 79.339 | 59.8258 | 1895.868
2038-09-19 11:01 | 8703.62 | 2.9313 | 79.9414 | 59.8258 | 2550.7792
2038-09-20 12:01 | 10287 | 3.349 | 81.053 | 59.8258 | 3014.8221
2038-09-21 13:01 | 10933.6 | 3.4824 | 81.9801 | 59.8258 | 3204.3219
2038-09-22 14:01 | 11478.4 | 3.7333 | 82.2062 | 59.8258 | 3363.987
2038-09-23 15:01 | 10950 | 3.5104 | 82.846 | 59.8258 | 3209.1282
2038-09-24 16:01 | 11607.8 | 3.7192 | 83.0681 | 59.8258 | 3401.9104
2038-09-25 17:01 | 10411.7 | 3.2653 | 83.6686 | 59.8258 | 3051.3681
2038-09-26 18:01 | 8627.56 | 2.6529 | 84.0545 | 59.8258 | 2528.4882
2038-09-27 19:01 | 7243.95 | 2.1953 | 84.1622 | 59.8258 | 2122.9922
2038-09-28 20:01 | 4978.2 | 1.4586 | 84.5228 | 59.8258 | 1458.9664
2038-09-29 21:01 | 3524.83 | 1.0806 | 83.4821 | 59.8258 | 1033.0257
2038-09-30 22:01 | 3193.98 | 1 | 67.8745 | 59.8258 | 936.0631
2038-10-01 23:01 | 2790.28 | 1 | 67.6391 | 59.8258 | 817.7503
2038-10-03 00:01 | 0 | 0 | 67.654 | 59.8258 | 0
2038-10-04 01:01 | -225.692 | 0.97192 | 66.0348 | 59.8258 | -66.1438
2038-10-05 02:01 | -292.634 | 1.2477 | 65.6581 | 59.8258 | -85.7626
2038-10-06 03:01 | -267.564 | 1.1631 | 65.4514 | 59.8258 | -78.4153
2038-10-07 04:01 | -331.093 | 1.3396 | 65.1597 | 59.8258 | -97.0338
2038-10-08 05:01 | 937.892 | 1 | 66.009 | 59.8258 | 274.869
2038-10-09 06:01 | 207.863 | 1 | 66.1323 | 59.8258 | 60.9186
2038-10-10 07:01 | 2246.75 | 1 | 65.8524 | 59.8258 | 658.4574
2038-10-11 08:01 | 2980.84 | 1 | 82.6214 | 59.8258 | 873.598
2038-10-12 09:01 | 5224.56 | 1.732 | 80.227 | 59.8258 | 1531.1674
2038-10-13 10:01 | 7668.85 | 2.6577 | 80.0019 | 59.8258 | 2247.5181
2038-10-14 11:01 | 9234.3 | 3.0891 | 80.9884 | 59.8258 | 2706.3062
2038-10-15 12:01 | 10725.7 | 3.5197 | 81.796 | 59.8258 | 3143.3924
2038-10-16 13:01 | 11491.4 | 3.7344 | 82.4588 | 59.8258 | 3367.7969
2038-10-17 14:01 | 12496.2 | 4.068 | 82.9045 | 59.8258 | 3662.2747
2038-10-18 15:01 | 11815.2 | 3.6803 | 84.0076 | 59.8258 | 3462.6933
2038-10-19 16:01 | 12651.7 | 4.0245 | 83.9207 | 59.8258 | 3707.8473
2038-10-20 17:01 | 11271.4 | 3.5377 | 84.4263 | 59.8258 | 3303.3213
2038-10-21 18:01 | 9027.91 | 2.7563 | 84.9289 | 59.8258 | 2645.8192
2038-10-22 19:01 | 7744.54 | 2.3551 | 84.7948 | 59.8258 | 2269.7006
2038-10-23 20:01 | 5621.32 | 1.6343 | 85.2849 | 59.8258 | 1647.4463
2038-10-24 21:01 | 4355.77 | 1.314 | 84.3704 | 59.8258 | 1276.5502
2038-10-25 22:01 | 3208.86 | 1 | 88.4578 | 59.8258 | 940.424
2038-10-26 23:01 | 3199.28 | 1 | 68.1681 | 59.8258 | 937.6164
2038-10-28 00:01 | 3171.07 | 1 | 67.9567 | 59.8258 | 929.3489
2038-10-29 01:01 | 3143.12 | 1 | 67.7964 | 59.8258 | 921.1575
2038-10-30 02:01 | 3190.59 | 1 | 67.6658 | 59.8258 | 935.0696
2038-10-31 03:01 | 3173.44 | 1 | 67.5868 | 59.8258 | 930.0435
2038-11-01 04:01 | 3229.85 | 1 | 67.5142 | 59.8258 | 946.5756
2038-11-02 05:01 | 3206.22 | 1 | 67.4636 | 59.8258 | 939.6503
2038-11-03 06:01 | 3267.29 | 1 | 67.4291 | 59.8258 | 957.5482
2038-11-04 07:01 | 3277.45 | 1 | 89.7798 | 59.8258 | 960.5258
2038-11-05 08:01 | 3292.79 | 1 | 93.9626 | 59.8258 | 965.0215
2038-11-06 09:01 | 3272.72 | 1 | 85.4803 | 59.8258 | 959.1396
2038-11-07 10:01 | 6840.98 | 2.2818 | 81.3076 | 59.8258 | 2004.8933
2038-11-08 11:01 | 7357.27 | 2.3803 | 82.1708 | 59.8258 | 2156.203
2038-11-09 12:01 | 6499.61 | 2.021 | 83.0301 | 59.8258 | 1904.8477
2038-11-10 13:01 | 6860.25 | 2.1489 | 82.9276 | 59.8258 | 2010.5408
2038-11-11 14:01 | 6639.21 | 2.0364 | 83.3149 | 59.8258 | 1945.7604
2038-11-12 15:01 | 7950.16 | 2.5856 | 82.5197 | 59.8258 | 2329.9619
2038-11-13 16:01 | 9022.06 | 3.0684 | 82.0482 | 59.8258 | 2644.1048
2038-11-14 17:01 | 8291.18 | 2.6292 | 83.2558 | 59.8258 | 2429.905
2038-11-15 18:01 | 7221.76 | 2.1982 | 83.9264 | 59.8258 | 2116.4889
2038-11-16 19:01 | 6481.13 | 1.9412 | 84.1035 | 59.8258 | 1899.4317
2038-11-17 20:01 | 4305.52 | 1.274 | 84.2418 | 59.8258 | 1261.8234
2038-11-18 21:01 | 3297.2 | 1.0405 | 82.992 | 59.8258 | 966.3139
2038-11-19 22:01 | 3103.03 | 1 | 67.9033 | 59.8258 | 909.4083
2038-11-20 23:01 | 3076.66 | 1 | 67.6995 | 59.8258 | 901.68
2038-11-22 00:01 | 3143.88 | 1 | 67.5667 | 59.8258 | 921.3803
2038-11-23 01:01 | 1562.2 | 1 | 67.6143 | 59.8258 | 457.8356
2038-11-24 02:01 | 688.885 | 1 | 67.4307 | 59.8258 | 201.8923
2038-11-25 03:01 | 3243.75 | 1 | 66.9148 | 59.8258 | 950.6493
2038-11-26 04:01 | 3270.19 | 1 | 67.0728 | 59.8258 | 958.3981
2038-11-27 05:01 | 3262.48 | 1 | 67.1272 | 59.8258 | 956.1385
2038-11-28 06:01 | 3233.47 | 1 | 67.1042 | 59.8258 | 947.6365
2038-11-29 07:01 | 3173.18 | 1 | 67.1142 | 59.8258 | 929.9673
2038-11-30 08:01 | 3116.77 | 1 | 67.1611 | 59.8258 | 913.4351
2038-12-01 09:01 | 3220.73 | 1 | 67.1306 | 59.8258 | 943.9028
2038-12-02 10:01 | 3212.34 | 1 | 67.0986 | 59.8258 | 941.4439
2038-12-03 11:01 | 3214.44 | 1 | 91.9011 | 59.8258 | 942.0594
2038-12-04 12:01 | 5009.44 | 1.575 | 81.7776 | 59.8258 | 1468.1219
2038-12-05 13:01 | 4232.72 | 1.2516 | 82.9237 | 59.8258 | 1240.4878
2038-12-06 14:01 | 4040.61 | 1.2333 | 82.4439 | 59.8258 | 1184.1859
2038-12-07 15:01 | 5590.58 | 1.8166 | 81.4508 | 59.8258 | 1638.4373
2038-12-08 16:01 | 5902.33 | 1.8863 | 81.8462 | 59.8258 | 1729.8022
2038-12-09 17:01 | 6054.74 | 1.917 | 82.1115 | 59.8258 | 1774.4691
2038-12-10 18:01 | 5039.49 | 1.5284 | 82.8092 | 59.8258 | 1476.9287
2038-12-11 19:01 | 4346.88 | 1.3357 | 82.5472 | 59.8258 | 1273.9448
2038-12-12 20:01 | 3120.94 | 1 | 87.3312 | 59.8258 | 914.6572
2038-12-13 21:01 | 3149.49 | 1 | 67.1192 | 59.8258 | 923.0244
2038-12-14 22:01 | 0 | 0 | 67.3061 | 59.8258 | 0
2038-12-15 23:01 | -143.229 | 0.85726 | 66.0474 | 59.8258 | -41.9763
2038-12-17 00:01 | -240.037 | 1.1233 | 65.5051 | 59.8258 | -70.3479
2038-12-18 01:01 | -323.988 | 1.3242 | 65.1723 | 59.8258 | -94.9515
2038-12-19 02:01 | -210.383 | 1.0105 | 65.1827 | 59.8258 | -61.6572
2038-12-20 03:01 | -49.6992 | 0.61452 | 65.6006 | 59.8258 | -14.5654
2038-12-21 04:01 | 2105.63 | 1 | 65.7035 | 59.8258 | 617.0992
2038-12-22 05:01 | 3056.87 | 1 | 65.8203 | 59.8258 | 895.8802
2038-12-23 06:01 | 3406.08 | 1 | 86.8413 | 59.8258 | 998.2235
2038-12-24 07:01 | 3660.47 | 1.0521 | 82.3335 | 59.8258 | 1072.7779
2038-12-25 08:01 | 3403.71 | 1 | 87.9364 | 59.8258 | 997.5289
2038-12-26 09:01 | 3487.61 | 1 | 85.0303 | 59.8258 | 1022.1176
2038-12-27 10:01 | 3601.2 | 1 | 86.9489 | 59.8258 | 1055.4075
2038-12-28 11:01 | 3675.15 | 1 | 87.316 | 59.8258 | 1077.0801
2038-12-29 12:01 | 3379.78 | 1 | 85.8611 | 59.8258 | 990.5157
2038-12-30 13:01 | 3184.65 | 1 | 83.1929 | 59.8258 | 933.3288
2038-12-31 14:01 | 3378.43 | 1.0834 | 80.9618 | 59.8258 | 990.1201
2039-01-01 15:01 | 5432.36 | 1.7417 | 80.9573 | 59.8258 | 1592.0676
2039-01-02 16:01 | 6231.63 | 2.0915 | 80.5571 | 59.8258 | 1826.3105
2039-01-03 17:01 | 6862.01 | 2.2484 | 81.1051 | 59.8258 | 2011.0566
2039-01-04 18:01 | 5622.49 | 1.7515 | 82.0389 | 59.8258 | 1647.7892
2039-01-05 19:01 | 5060.72 | 1.5313 | 82.4573 | 59.8258 | 1483.1506
2039-01-06 20:01 | 3166.04 | 1 | 84.4915 | 59.8258 | 927.8747
2039-01-07 21:01 | 3068.31 | 1 | 90.3377 | 59.8258 | 899.2329
2039-01-08 22:01 | 0 | 0 | 66.9612 | 59.8258 | 0
2039-01-09 23:01 | -321.39 | 1.337 | 65.3612 | 59.8258 | -94.1901
2039-01-11 00:01 | -386.23 | 1.4738 | 64.9339 | 59.8258 | -113.1928
2039-01-12 01:01 | -399.659 | 1.5012 | 64.7225 | 59.8258 | -117.1285
2039-01-13 02:01 | -533.488 | 1.8569 | 64.49 | 59.8258 | -156.3499
2039-01-14 03:01 | -517.67 | 1.789 | 64.2994 | 59.8258 | -151.7141
2039-01-15 04:01 | -654.947 | 2.1643 | 64.1171 | 59.8258 | -191.946
2039-01-16 05:01 | -739.159 | 2.3623 | 63.9257 | 59.8258 | -216.6261
2039-01-17 06:01 | 13.4547 | 1 | 65.2232 | 59.8258 | 3.9432
2039-01-18 07:01 | 1790.81 | 1 | 65.0447 | 59.8258 | 524.8346
2039-01-19 08:01 | 2652.43 | 1 | 80.623 | 59.8258 | 777.3505
2039-01-20 09:01 | 2915.01 | 1 | 84.2596 | 59.8258 | 854.3051
2039-01-21 10:01 | 4431.09 | 1.4375 | 79.8254 | 59.8258 | 1298.6243
2039-01-22 11:01 | 5872.63 | 1.9201 | 80.0359 | 59.8258 | 1721.098
2039-01-23 12:01 | 6317.56 | 1.9943 | 80.9308 | 59.8258 | 1851.4941
2039-01-24 13:01 | 8174.15 | 2.6552 | 80.7973 | 59.8258 | 2395.6069
2039-01-25 14:01 | 8995.01 | 2.9139 | 81.2759 | 59.8258 | 2636.1772
2039-01-26 15:01 | 8793.64 | 2.9005 | 81.4365 | 59.8258 | 2577.1615
2039-01-27 16:01 | 10654.5 | 3.5213 | 81.6333 | 59.8258 | 3122.5257
2039-01-28 17:01 | 8863.32 | 2.7292 | 83.0925 | 59.8258 | 2597.5827
2039-01-29 18:01 | 6805.21 | 2.0445 | 83.56 | 59.8258 | 1994.4102
2039-01-30 19:01 | 5272.6 | 1.7576 | 81.8575 | 59.8258 | 1545.2465
2039-01-31 20:01 | 4170.01 | 1.4011 | 81.5101 | 59.8258 | 1222.1093
2039-02-01 21:01 | 3177.86 | 1.0174 | 81.9533 | 59.8258 | 931.3388
2039-02-02 22:01 | 3043.82 | 1 | 89.2948 | 59.8258 | 892.0556
2039-02-03 23:01 | 0 | 0 | 67.2223 | 59.8258 | 0
2039-02-05 00:01 | -853.055 | 2.6921 | 65.2595 | 59.8258 | -250.0057
2039-02-06 01:01 | -1233.65 | 3.6111 | 64.7099 | 59.8258 | -361.5471
2039-02-07 02:01 | -1513.34 | 4.2969 | 64.3429 | 59.8258 | -443.5162
2039-02-08 03:01 | -1651.1 | 4.6234 | 64.0384 | 59.8258 | -483.8896
2039-02-09 04:01 | -1930.54 | 5.3714 | 63.7335 | 59.8258 | -565.7854
2039-02-10 05:01 | -2161.06 | 5.9499 | 63.4882 | 59.8258 | -633.3442
2039-02-11 06:01 | -1573.3 | 4.3017 | 63.2712 | 59.8258 | -461.0887
2039-02-12 07:01 | -985.597 | 2.8544 | 63.2775 | 59.8258 | -288.85
2039-02-13 08:01 | -682.248 | 2.162 | 63.3969 | 59.8258 | -199.9472
2039-02-14 09:01 | 2288.15 | 1 | 64.621 | 59.8258 | 670.5906
2039-02-15 10:01 | 3034.18 | 1 | 64.8966 | 59.8258 | 889.2304
2039-02-16 11:01 | 3142.41 | 1 | 84.0298 | 59.8258 | 920.9495
2039-02-17 12:01 | 4656.48 | 1.461 | 80.1629 | 59.8258 | 1364.6796
2039-02-18 13:01 | 4060.68 | 1.3381 | 79.7913 | 59.8258 | 1190.0678
2039-02-19 14:01 | 4566.34 | 1.4536 | 80.4101 | 59.8258 | 1338.2621
2039-02-20 15:01 | 5666.79 | 1.8411 | 80.2244 | 59.8258 | 1660.7722
2039-02-21 16:01 | 7695.77 | 2.5237 | 80.3078 | 59.8258 | 2255.4075
2039-02-22 17:01 | 5818.83 | 1.8461 | 81.2165 | 59.8258 | 1705.3307
2039-02-23 18:01 | 3906.65 | 1.2483 | 81.1219 | 59.8258 | 1144.9261
2039-02-24 19:01 | 3111.79 | 1 | 86.7297 | 59.8258 | 911.9756
2039-02-25 20:01 | 3155.27 | 1 | 66.1999 | 59.8258 | 924.7184
2039-02-26 21:01 | 2995.9 | 1 | 66.151 | 59.8258 | 878.0116
2039-02-27 22:01 | -51.4516 | 0.69241 | 65.9661 | 59.8258 | -15.079
2039-02-28 23:01 | -1600.15 | 4.7526 | 64.3105 | 59.8258 | -468.9577
2039-03-02 00:01 | -2284.56 | 6.108 | 63.6815 | 59.8258 | -669.5384
2039-03-03 01:01 | -2605.73 | 6.108 | 63.1107 | 59.8258 | -763.6641
2039-03-04 02:01 | -2774.55 | 6.108 | 62.6985 | 59.8258 | -813.1403
2039-03-05 03:01 | -3028.39 | 6.108 | 62.2298 | 59.8258 | -887.5335
2039-03-06 04:01 | -3272.1 | 6.108 | 61.8029 | 59.8258 | -958.9578
2039-03-07 05:01 | -3402.92 | 6.108 | 61.5053 | 59.8258 | -997.2974
2039-03-08 06:01 | -2658.53 | 6.108 | 61.8978 | 59.8258 | -779.1382
2039-03-09 07:01 | -1820.72 | 5.0518 | 62.1986 | 59.8258 | -533.6004
2039-03-10 08:01 | -1520.1 | 4.2928 | 62.2623 | 59.8258 | -445.4973
2039-03-11 09:01 | -563.339 | 1.73 | 62.3796 | 59.8258 | -165.0984
2039-03-12 10:01 | 2670.36 | 1 | 63.7408 | 59.8258 | 782.6053
2039-03-13 11:01 | 3180.59 | 1 | 81.0462 | 59.8258 | 932.1389
2039-03-14 12:01 | 4317.05 | 1.3505 | 79.3987 | 59.8258 | 1265.2025
2039-03-15 13:01 | 5240.86 | 1.6703 | 79.4546 | 59.8258 | 1535.9444
2039-03-16 14:01 | 6118.59 | 1.9479 | 79.8261 | 59.8258 | 1793.1817
2039-03-17 15:01 | 6061.37 | 1.9693 | 79.8982 | 59.8258 | 1776.4122
2039-03-18 16:01 | 7936.79 | 2.568 | 80.1285 | 59.8258 | 2326.0435
2039-03-19 17:01 | 5910.14 | 1.8436 | 81.0813 | 59.8258 | 1732.0911
2039-03-20 18:01 | 3766 | 1.2001 | 80.8024 | 59.8258 | 1103.7056
2039-03-21 19:01 | 3120.54 | 1 | 87.514 | 59.8258 | 914.54
2039-03-22 20:01 | 3162.9 | 1 | 65.7877 | 59.8258 | 926.9545
2039-03-23 21:01 | 3001.35 | 1 | 65.7688 | 59.8258 | 879.6089
2039-03-24 22:01 | -94.2675 | 0.80621 | 65.4004 | 59.8258 | -27.6271
2039-03-25 23:01 | -1354.19 | 4.111 | 63.9745 | 59.8258 | -396.8739
2039-03-27 00:01 | -1771.11 | 5.0021 | 63.4582 | 59.8258 | -519.0611
2039-03-28 01:01 | -2016.98 | 5.6126 | 63.1591 | 59.8258 | -591.1185
2039-03-29 02:01 | -2155.2 | 5.9557 | 62.8971 | 59.8258 | -631.6268
2039-03-30 03:01 | -2506.41 | 6.108 | 62.4407 | 59.8258 | -734.5563
2039-03-31 04:01 | -2413.04 | 6.108 | 62.2916 | 59.8258 | -707.1922
2039-04-01 05:01 | -1957.85 | 5.414 | 62.3137 | 59.8258 | -573.7892
2039-04-02 06:01 | -1925.42 | 5.3803 | 62.2973 | 59.8258 | -564.2849
2039-04-03 07:01 | -1280.7 | 3.6016 | 62.2519 | 59.8258 | -375.3361
2039-04-04 08:01 | -638.193 | 1.9975 | 62.4327 | 59.8258 | -187.0359
2039-04-05 09:01 | 2535.7 | 1 | 80.3901 | 59.8258 | 743.1403
2039-04-06 10:01 | 5031.71 | 1.6413 | 78.3956 | 59.8258 | 1474.6486
2039-04-07 11:01 | 7394.55 | 2.4524 | 78.7425 | 59.8258 | 2167.1287
2039-04-08 12:01 | 8740.04 | 2.9594 | 79.1007 | 59.8258 | 2561.4529
2039-04-09 13:01 | 9608.34 | 3.1535 | 80.1198 | 59.8258 | 2815.9265
2039-04-10 14:01 | 10478.9 | 3.3692 | 80.9384 | 59.8258 | 3071.0624
2039-04-11 15:01 | 11619.2 | 3.7358 | 81.4162 | 59.8258 | 3405.2514
2039-04-12 16:01 | 10993.1 | 3.4935 | 82.0696 | 59.8258 | 3221.7596
2039-04-13 17:01 | 9476.41 | 2.9463 | 82.6561 | 59.8258 | 2777.2616
2039-04-14 18:01 | 7002.58 | 2.1725 | 82.7397 | 59.8258 | 2052.2536
2039-04-15 19:01 | 5243.74 | 1.5753 | 83.0221 | 59.8258 | 1536.7885
2039-04-16 20:01 | 3240.9 | 1 | 85.5602 | 59.8258 | 949.814
2039-04-17 21:01 | 3118.01 | 1 | 66.8419 | 59.8258 | 913.7985
2039-04-18 22:01 | 0 | 0 | 66.879 | 59.8258 | 0
2039-04-19 23:01 | -589.381 | 1.8949 | 64.8732 | 59.8258 | -172.7305
2039-04-21 00:01 | -820.635 | 2.5886 | 64.4141 | 59.8258 | -240.5044
2039-04-22 01:01 | -1208.6 | 3.582 | 64.0327 | 59.8258 | -354.2057
2039-04-23 02:01 | -1473.92 | 4.226 | 63.7097 | 59.8258 | -431.9633
2039-04-24 03:01 | -1294.4 | 3.6944 | 63.4154 | 59.8258 | -379.3512
2039-04-25 04:01 | -1415.98 | 4.0803 | 63.2771 | 59.8258 | -414.9828
2039-04-26 05:01 | -1150.32 | 3.3277 | 63.1374 | 59.8258 | -337.1255
2039-04-27 06:01 | -1181.53 | 3.4832 | 63.09 | 59.8258 | -346.2723
2039-04-28 07:01 | -914.291 | 2.7437 | 63.0423 | 59.8258 | -267.9522
2039-04-29 08:01 | -143.82 | 0.72144 | 63.6326 | 59.8258 | -42.1495
2039-04-30 09:01 | 2754.71 | 1.1796 | 75.2914 | 59.8258 | 807.3258
2039-05-01 10:01 | 5780.73 | 2.0503 | 77.8634 | 59.8258 | 1694.1647
2039-05-02 11:01 | 8065.62 | 2.7601 | 78.9191 | 59.8258 | 2363.7999
2039-05-03 12:01 | 9330.56 | 3.1187 | 79.8632 | 59.8258 | 2734.5172
2039-05-04 13:01 | 10215.4 | 3.3313 | 80.7587 | 59.8258 | 2993.8382
2039-05-05 14:01 | 10984.5 | 3.5292 | 81.4701 | 59.8258 | 3219.2392
2039-05-06 15:01 | 11802.5 | 3.8229 | 81.7943 | 59.8258 | 3458.9713
2039-05-07 16:01 | 11083 | 3.5189 | 82.4898 | 59.8258 | 3248.1067
2039-05-08 17:01 | 9326.95 | 2.9614 | 82.6964 | 59.8258 | 2733.4592
2039-05-09 18:01 | 7224.74 | 2.2212 | 83.1465 | 59.8258 | 2117.3623
2039-05-10 19:01 | 5841.54 | 1.7341 | 83.4805 | 59.8258 | 1711.9864
2039-05-11 20:01 | 3302.85 | 1 | 84.4377 | 59.8258 | 967.9698
2039-05-12 21:01 | 3143.38 | 1 | 67.1342 | 59.8258 | 921.2337
2039-05-13 22:01 | 0 | 0 | 67.1381 | 59.8258 | 0
2039-05-14 23:01 | -490.714 | 1.6966 | 65.2196 | 59.8258 | -143.8141
2039-05-16 00:01 | -759.234 | 2.4343 | 64.6777 | 59.8258 | -222.5095
2039-05-17 01:01 | -1037.42 | 3.1263 | 64.2727 | 59.8258 | -304.0378
2039-05-18 02:01 | -1047.77 | 3.1042 | 63.9773 | 59.8258 | -307.0711
2039-05-19 03:01 | -1257.11 | 3.6816 | 63.7091 | 59.8258 | -368.4226
2039-05-20 04:01 | -1452.75 | 4.1708 | 63.4897 | 59.8258 | -425.759
2039-05-21 05:01 | -1047.94 | 3.0339 | 63.3259 | 59.8258 | -307.1209
2039-05-22 06:01 | -1219.25 | 3.6038 | 63.2872 | 59.8258 | -357.3269
2039-05-23 07:01 | -798.652 | 2.4133 | 63.2246 | 59.8258 | -234.0618
2039-05-24 08:01 | -236.811 | 1.0005 | 63.637 | 59.8258 | -69.4025
2039-05-25 09:01 | 2383.4 | 1.0242 | 75.404 | 59.8258 | 698.5056
2039-05-26 10:01 | 5751.23 | 1.9188 | 78.7686 | 59.8258 | 1685.5191
2039-05-27 11:01 | 7782.78 | 2.6772 | 78.9474 | 59.8258 | 2280.9077
2039-05-28 12:01 | 9123.55 | 3.093 | 79.736 | 59.8258 | 2673.8486
2039-05-29 13:01 | 10105.7 | 3.3033 | 80.7681 | 59.8258 | 2961.6883
2039-05-30 14:01 | 10904.4 | 3.5388 | 81.3676 | 59.8258 | 3195.7642
2039-05-31 15:01 | 11737.7 | 3.8586 | 81.626 | 59.8258 | 3439.9803
2039-06-01 16:01 | 11207.4 | 3.5956 | 82.3756 | 59.8258 | 3284.5647
2039-06-02 17:01 | 9559.17 | 3.0501 | 82.6848 | 59.8258 | 2801.5162
2039-06-03 18:01 | 7340.03 | 2.2447 | 83.3106 | 59.8258 | 2151.1504
2039-06-04 19:01 | 5983.82 | 1.7927 | 83.4183 | 59.8258 | 1753.6845
2039-06-05 20:01 | 3451.9 | 1.0355 | 83.1969 | 59.8258 | 1011.652
2039-06-06 21:01 | 3198.48 | 1 | 87.4303 | 59.8258 | 937.382
2039-06-07 22:01 | 0 | 0 | 67.2373 | 59.8258 | 0
2039-06-08 23:01 | -148.872 | 0.81278 | 65.7932 | 59.8258 | -43.6301
2039-06-10 00:01 | -702.395 | 2.3468 | 64.8673 | 59.8258 | -205.8517
2039-06-11 01:01 | -897.439 | 2.7551 | 64.418 | 59.8258 | -263.0134
2039-06-12 02:01 | -905.724 | 2.7505 | 64.1333 | 59.8258 | -265.4415
2039-06-13 03:01 | -1078.67 | 3.2248 | 63.8665 | 59.8258 | -316.127
2039-06-14 04:01 | -965.607 | 2.8845 | 63.6853 | 59.8258 | -282.9915
2039-06-15 05:01 | -614.785 | 1.9715 | 63.6543 | 59.8258 | -180.1757
2039-06-16 06:01 | -815.653 | 2.5937 | 63.5939 | 59.8258 | -239.0443
2039-06-17 07:01 | -317.435 | 1.199 | 63.7338 | 59.8258 | -93.031
2039-06-18 08:01 | -102.745 | 0.74529 | 64.321 | 59.8258 | -30.1116
2039-06-19 09:01 | 2457.96 | 1.017 | 76.0224 | 59.8258 | 720.357
2039-06-20 10:01 | 6273.32 | 2.2001 | 78.2803 | 59.8258 | 1838.5286
2039-06-21 11:01 | 8590.21 | 2.9024 | 79.4183 | 59.8258 | 2517.542
2039-06-22 12:01 | 9960.07 | 3.3213 | 80.2552 | 59.8258 | 2919.0084
2039-06-23 13:01 | 10530.5 | 3.5307 | 80.7492 | 59.8258 | 3086.1849
2039-06-24 14:01 | 11354.9 | 3.7389 | 81.4735 | 59.8258 | 3327.7927
2039-06-25 15:01 | 12607.1 | 4.018 | 82.3747 | 59.8258 | 3694.7763
2039-06-26 16:01 | 12021.8 | 3.7994 | 82.9634 | 59.8258 | 3523.2418
2039-06-27 17:01 | 10388 | 3.2502 | 83.3645 | 59.8258 | 3044.4223
2039-06-28 18:01 | 8254.02 | 2.482 | 83.9746 | 59.8258 | 2419.0145
2039-06-29 19:01 | 6999.99 | 2.1403 | 83.5536 | 59.8258 | 2051.4946
2039-06-30 20:01 | 4853.53 | 1.4356 | 83.9026 | 59.8258 | 1422.4292
2039-07-01 21:01 | 3240.67 | 1 | 83.7334 | 59.8258 | 949.7466
2039-07-02 22:01 | 3067.65 | 1 | 67.4018 | 59.8258 | 899.0395
2039-07-03 23:01 | 0 | 0 | 67.42 | 59.8258 | 0
2039-07-05 00:01 | -192.187 | 0.99794 | 65.9572 | 59.8258 | -56.3244
2039-07-06 01:01 | -425.563 | 1.5982 | 65.2184 | 59.8258 | -124.7202
2039-07-07 02:01 | -547.906 | 1.88 | 64.8266 | 59.8258 | -160.5754
2039-07-08 03:01 | -824.869 | 2.5998 | 64.4594 | 59.8258 | -241.7452
2039-07-09 04:01 | -892.377 | 2.7279 | 64.1505 | 59.8258 | -261.5299
2039-07-10 05:01 | -926.515 | 2.8139 | 63.9711 | 59.8258 | -271.5347
2039-07-11 06:01 | -222.409 | 0.92006 | 64.2387 | 59.8258 | -65.1816
2039-07-12 07:01 | 1879.63 | 1 | 65.163 | 59.8258 | 550.8652
2039-07-13 08:01 | -201.918 | 1.095 | 64.742 | 59.8258 | -59.1763
2039-07-14 09:01 | 2212.88 | 1 | 65.2142 | 59.8258 | 648.5311
2039-07-15 10:01 | 3090.61 | 1.0299 | 79.3261 | 59.8258 | 905.7684
2039-07-16 11:01 | 3112.76 | 1 | 82.6946 | 59.8258 | 912.2599
2039-07-17 12:01 | 3218.79 | 1 | 84.3553 | 59.8258 | 943.3342
2039-07-18 13:01 | 3216.75 | 1 | 84.2329 | 59.8258 | 942.7364
2039-07-19 14:01 | 4411.99 | 1.3404 | 80.9586 | 59.8258 | 1293.0266
2039-07-20 15:01 | 3865 | 1.2249 | 80.4813 | 59.8258 | 1132.7197
2039-07-21 16:01 | 6411.34 | 2.15 | 79.6563 | 59.8258 | 1878.9783
2039-07-22 17:01 | 5651.44 | 1.7797 | 80.8781 | 59.8258 | 1656.2736
2039-07-23 18:01 | 4900.8 | 1.4742 | 81.6763 | 59.8258 | 1436.2827
2039-07-24 19:01 | 3990.7 | 1.2238 | 81.349 | 59.8258 | 1169.5587
2039-07-25 20:01 | 3331.85 | 1.0279 | 81.1891 | 59.8258 | 976.4688
2039-07-26 21:01 | 3195.72 | 1 | 83.2014 | 59.8258 | 936.5731
2039-07-27 22:01 | 3173.38 | 1 | 85.533 | 59.8258 | 930.0259
2039-07-28 23:01 | 0 | 0 | 66.1788 | 59.8258 | 0
2039-07-30 00:01 | -273.749 | 1.2089 | 64.7044 | 59.8258 | -80.2279
2039-07-31 01:01 | -352.638 | 1.4052 | 64.3231 | 59.8258 | -103.348
2039-08-01 02:01 | -478.169 | 1.7268 | 64.0521 | 59.8258 | -140.1375
2039-08-02 03:01 | -478.926 | 1.705 | 63.8893 | 59.8258 | -140.3594
2039-08-03 04:01 | -510.151 | 1.7938 | 63.7104 | 59.8258 | -149.5105
2039-08-04 05:01 | -465.791 | 1.6686 | 63.651 | 59.8258 | -136.5099
2039-08-05 06:01 | 1084.09 | 1 | 64.769 | 59.8258 | 317.7154
2039-08-06 07:01 | 2679.91 | 1 | 64.7687 | 59.8258 | 785.4041
2039-08-07 08:01 | 0 | 0 | 65.3 | 59.8258 | 0
2039-08-08 09:01 | -177.223 | 0.94292 | 64.1947 | 59.8258 | -51.9389
2039-08-09 10:01 | -30.7259 | 0.57575 | 64.8909 | 59.8258 | -9.0049
2039-08-10 11:01 | 359.293 | 1 | 64.7886 | 59.8258 | 105.2984
2039-08-11 12:01 | -31.8892 | 0.63526 | 64.5575 | 59.8258 | -9.3458
2039-08-12 13:01 | -458.185 | 1.7442 | 63.4303 | 59.8258 | -134.2808
2039-08-13 14:01 | -549.636 | 1.9085 | 63.1624 | 59.8258 | -161.0824
2039-08-14 15:01 | -442.293 | 1.6057 | 63.0943 | 59.8258 | -129.6233
2039-08-15 16:01 | 2536.78 | 1 | 64.0233 | 59.8258 | 743.4568
2039-08-16 17:01 | 2925.56 | 1 | 64.2887 | 59.8258 | 857.397
2039-08-17 18:01 | -42.4148 | 0.67324 | 64.4496 | 59.8258 | -12.4306
2039-08-18 19:01 | -528.494 | 1.9363 | 63.1492 | 59.8258 | -154.8863
2039-08-19 20:01 | -980.015 | 3.0716 | 62.7374 | 59.8258 | -287.214
2039-08-20 21:01 | -1252.28 | 3.7249 | 62.5323 | 59.8258 | -367.007
2039-08-21 22:01 | -1314.12 | 3.8452 | 62.3209 | 59.8258 | -385.1306
2039-08-22 23:01 | -2405.2 | 6.108 | 61.9408 | 59.8258 | -704.8945
2039-08-24 00:01 | -2895.95 | 6.108 | 61.3667 | 59.8258 | -848.7192
2039-08-25 01:01 | -3267.41 | 6.108 | 60.8967 | 59.8258 | -957.5833
2039-08-26 02:01 | -3184.1 | 6.108 | 60.7942 | 59.8258 | -933.1676
2039-08-27 03:01 | -3136.43 | 6.108 | 60.7209 | 59.8258 | -919.1969
2039-08-28 04:01 | -3244.19 | 6.108 | 60.5146 | 59.8258 | -950.7782
2039-08-29 05:01 | -2679.55 | 6.108 | 60.8101 | 59.8258 | -785.2986
2039-08-30 06:01 | -2886.06 | 6.108 | 60.6449 | 59.8258 | -845.8207
2039-08-31 07:01 | -2059.4 | 5.8133 | 61.114 | 59.8258 | -603.5506
2039-09-01 08:01 | -1641.72 | 4.621 | 61.166 | 59.8258 | -481.1406
2039-09-02 09:01 | 0 | 0 | 62.8553 | 59.8258 | 0
2039-09-03 10:01 | 2663.39 | 1 | 76.4696 | 59.8258 | 780.5626
2039-09-04 11:01 | 4790.23 | 1.5578 | 77.6119 | 59.8258 | 1403.8778
2039-09-05 12:01 | 5500.95 | 1.8498 | 77.7158 | 59.8258 | 1612.1693
2039-09-06 13:01 | 5655.27 | 1.9394 | 77.8948 | 59.8258 | 1657.396
2039-09-07 14:01 | 6176.88 | 2.118 | 78.2296 | 59.8258 | 1810.2648
2039-09-08 15:01 | 6891.06 | 2.3626 | 78.562 | 59.8258 | 2019.5703
2039-09-09 16:01 | 6013.6 | 2.0885 | 78.7072 | 59.8258 | 1762.4122
2039-09-10 17:01 | 4379.89 | 1.4968 | 79.012 | 59.8258 | 1283.619
2039-09-11 18:01 | 2933.85 | 1 | 83.7945 | 59.8258 | 859.8266
2039-09-12 19:01 | 2792.72 | 1 | 65.1055 | 59.8258 | 818.4654
2039-09-13 20:01 | -805.976 | 2.6899 | 63.9198 | 59.8258 | -236.2082
2039-09-14 21:01 | -1273.05 | 3.7855 | 63.2141 | 59.8258 | -373.0941
2039-09-15 22:01 | -2203.92 | 6.108 | 62.7096 | 59.8258 | -645.9052
2039-09-16 23:01 | -2763.43 | 6.108 | 61.9493 | 59.8258 | -809.8814
2039-09-18 00:01 | -3117.39 | 6.108 | 61.3648 | 59.8258 | -913.6168
2039-09-19 01:01 | -3299.01 | 6.108 | 60.9288 | 59.8258 | -966.8444
2039-09-20 02:01 | -3431.51 | 6.108 | 60.6207 | 59.8258 | -1005.6763
2039-09-21 03:01 | -3316.02 | 6.108 | 60.505 | 59.8258 | -971.8295
2039-09-22 04:01 | -3325.29 | 6.108 | 60.3577 | 59.8258 | -974.5463
2039-09-23 05:01 | -3088.44 | 6.108 | 60.4187 | 59.8258 | -905.1324
2039-09-24 06:01 | -3158.9 | 6.108 | 60.2999 | 59.8258 | -925.7822
2039-09-25 07:01 | -2548.23 | 6.108 | 60.6623 | 59.8258 | -746.8125
2039-09-26 08:01 | -1646.22 | 4.6334 | 60.9768 | 59.8258 | -482.4595
2039-09-27 09:01 | 0 | 0 | 62.7147 | 59.8258 | 0
2039-09-28 10:01 | 2722.97 | 1 | 78.1059 | 59.8258 | 798.0237
2039-09-29 11:01 | 4877.75 | 1.5569 | 77.7572 | 59.8258 | 1429.5274
2039-09-30 12:01 | 6514.43 | 2.1071 | 78.1272 | 59.8258 | 1909.191
2039-10-01 13:01 | 7321.47 | 2.3872 | 78.5707 | 59.8258 | 2145.711
2039-10-02 14:01 | 8025.94 | 2.5902 | 79.1912 | 59.8258 | 2352.1708
2039-10-03 15:01 | 9135.33 | 2.9707 | 79.5066 | 59.8258 | 2677.3009
2039-10-04 16:01 | 8539.75 | 2.7627 | 80.0278 | 59.8258 | 2502.7537
2039-10-05 17:01 | 6703.11 | 2.1506 | 80.392 | 59.8258 | 1964.4876
2039-10-06 18:01 | 3982.16 | 1.28 | 80.3471 | 59.8258 | 1167.0559
2039-10-07 19:01 | 3068.96 | 1 | 90.5978 | 59.8258 | 899.4234
2039-10-08 20:01 | 0 | 0 | 65.6358 | 59.8258 | 0
2039-10-09 21:01 | -554.469 | 1.9708 | 63.8284 | 59.8258 | -162.4988
2039-10-10 22:01 | -1936.81 | 5.6612 | 63.1577 | 59.8258 | -567.623
2039-10-11 23:01 | -2494.28 | 6.108 | 62.4362 | 59.8258 | -731.0013
2039-10-13 00:01 | -3201.76 | 6.108 | 61.5571 | 59.8258 | -938.3432
2039-10-14 01:01 | -3619.16 | 6.108 | 60.8912 | 59.8258 | -1060.6711
2039-10-15 02:01 | -3888.05 | 6.108 | 60.4016 | 59.8258 | -1139.475
2039-10-16 03:01 | -4182.12 | 6.108 | 59.9044 | 59.8258 | -1225.6584
2039-10-17 04:01 | -4117.37 | 6.108 | 59.7037 | 59.8258 | -1206.682
2039-10-18 05:01 | -3758.57 | 6.108 | 59.7884 | 59.8258 | -1101.5281
2039-10-19 06:01 | -3608.91 | 6.108 | 59.8195 | 59.8258 | -1057.6671
2039-10-20 07:01 | -3078.45 | 6.108 | 60.143 | 59.8258 | -902.2046
2039-10-21 08:01 | -2551 | 6.108 | 60.5532 | 59.8258 | -747.6243
2039-10-22 09:01 | -1064.2 | 2.9968 | 60.8781 | 59.8258 | -311.8862
2039-10-23 10:01 | 2783.49 | 1 | 62.4433 | 59.8258 | 815.7604
2039-10-24 11:01 | 4608.19 | 1.4347 | 77.9907 | 59.8258 | 1350.5272
2039-10-25 12:01 | 6190.52 | 2.0295 | 77.7573 | 59.8258 | 1814.2623
2039-10-26 13:01 | 7626.92 | 2.4209 | 78.7336 | 59.8258 | 2235.2296
2039-10-27 14:01 | 8297.83 | 2.6614 | 79.1304 | 59.8258 | 2431.8539
2039-10-28 15:01 | 9212.07 | 2.964 | 79.5488 | 59.8258 | 2699.7912
2039-10-29 16:01 | 8324.59 | 2.6616 | 80.0619 | 59.8258 | 2439.6965
2039-10-30 17:01 | 6404.36 | 1.9981 | 80.6192 | 59.8258 | 1876.9326
2039-10-31 18:01 | 4478.16 | 1.3896 | 80.6441 | 59.8258 | 1312.4191
2039-11-01 19:01 | 3134.37 | 1 | 81.7659 | 59.8258 | 918.5932
2039-11-02 20:01 | 2442.07 | 1 | 65.2763 | 59.8258 | 715.7001
2039-11-03 21:01 | -372.295 | 1.55 | 64.201 | 59.8258 | -109.1089
2039-11-04 22:01 | -1465.02 | 4.3984 | 63.2702 | 59.8258 | -429.355
2039-11-05 23:01 | -1841.89 | 5.2156 | 62.7379 | 59.8258 | -539.8047
2039-11-07 00:01 | -2449.05 | 6.108 | 62.2199 | 59.8258 | -717.7457
2039-11-08 01:01 | -3023.79 | 6.108 | 61.4826 | 59.8258 | -886.1854
2039-11-09 02:01 | -3316.6 | 6.108 | 60.9351 | 59.8258 | -971.9995
2039-11-10 03:01 | -3226.21 | 6.108 | 60.7427 | 59.8258 | -945.5088
2039-11-11 04:01 | -3164.68 | 6.108 | 60.6127 | 59.8258 | -927.4762
2039-11-12 05:01 | -2615.27 | 6.108 | 60.8879 | 59.8258 | -766.46
2039-11-13 06:01 | -3018.9 | 6.108 | 60.5524 | 59.8258 | -884.7523
2039-11-14 07:01 | -2648.99 | 6.108 | 60.7263 | 59.8258 | -776.3423
2039-11-15 08:01 | -1857.24 | 5.2311 | 61.0481 | 59.8258 | -544.3033
2039-11-16 09:01 | 0 | 1 | 62.75 | 59.8258 | 0
2039-11-17 10:01 | 3220.51 | 1 | 80.7866 | 59.8258 | 943.8383
2039-11-18 11:01 | 6045.7 | 1.9025 | 78.0353 | 59.8258 | 1771.8198
2039-11-19 12:01 | 7688.19 | 2.4644 | 78.4422 | 59.8258 | 2253.1861
2039-11-20 13:01 | 8454.39 | 2.7188 | 79.0061 | 59.8258 | 2477.7371
2039-11-21 14:01 | 9006.36 | 2.8912 | 79.5349 | 59.8258 | 2639.5036
2039-11-22 15:01 | 10124.3 | 3.2557 | 79.9346 | 59.8258 | 2967.1394
2039-11-23 16:01 | 9301.29 | 2.9599 | 80.5406 | 59.8258 | 2725.939
2039-11-24 17:01 | 7264.69 | 2.2837 | 80.9319 | 59.8258 | 2129.0705
2039-11-25 18:01 | 5311.13 | 1.6639 | 80.9183 | 59.8258 | 1556.5386
2039-11-26 19:01 | 3199.87 | 1 | 81.2576 | 59.8258 | 937.7893
2039-11-27 20:01 | 3164.65 | 1 | 65.5382 | 59.8258 | 927.4674
2039-11-28 21:01 | 0 | 0 | 65.6663 | 59.8258 | 0
2039-11-29 22:01 | -999.48 | 3.0877 | 63.6592 | 59.8258 | -292.9187
2039-11-30 23:01 | -1558.86 | 4.5345 | 63.108 | 59.8258 | -456.8568
2039-12-02 00:01 | -2091.28 | 5.893 | 62.7196 | 59.8258 | -612.8937
2039-12-03 01:01 | -2359.64 | 6.108 | 62.2747 | 59.8258 | -691.5422
2039-12-04 02:01 | -2433.95 | 6.108 | 61.927 | 59.8258 | -713.3203
2039-12-05 03:01 | -2357.58 | 6.108 | 61.7753 | 59.8258 | -690.9385
2039-12-06 04:01 | -2710.63 | 6.108 | 61.3586 | 59.8258 | -794.4072
2039-12-07 05:01 | -2173.21 | 6.0893 | 61.5828 | 59.8258 | -636.905
2039-12-08 06:01 | -2439.82 | 6.108 | 61.3441 | 59.8258 | -715.0407
2039-12-09 07:01 | -1871.25 | 5.2322 | 61.4588 | 59.8258 | -548.4092
2039-12-10 08:01 | -1464.79 | 4.1638 | 61.4787 | 59.8258 | -429.2876
2039-12-11 09:01 | 0 | 1 | 63.1301 | 59.8258 | 0
2039-12-12 10:01 | 3835.57 | 1.18 | 78.2051 | 59.8258 | 1124.0946
2039-12-13 11:01 | 6835.5 | 2.2096 | 78.0059 | 59.8258 | 2003.2873
2039-12-14 12:01 | 8627.23 | 2.8267 | 78.5242 | 59.8258 | 2528.3915
2039-12-15 13:01 | 9400.04 | 3.0233 | 79.42 | 59.8258 | 2754.8798
2039-12-16 14:01 | 10053.7 | 3.2255 | 79.9753 | 59.8258 | 2946.4486
2039-12-17 15:01 | 10771.4 | 3.4798 | 80.3356 | 59.8258 | 3156.7857
2039-12-18 16:01 | 9807.34 | 3.1158 | 81.0004 | 59.8258 | 2874.2476
2039-12-19 17:01 | 8100.75 | 2.5482 | 81.3243 | 59.8258 | 2374.0955
2039-12-20 18:01 | 6181.15 | 1.9069 | 81.5713 | 59.8258 | 1811.5162
2039-12-21 19:01 | 4448.66 | 1.3451 | 81.6941 | 59.8258 | 1303.7735
2039-12-22 20:01 | 3148.97 | 1 | 66.0437 | 59.8258 | 922.872
2039-12-23 21:01 | 3038.34 | 1 | 65.7778 | 59.8258 | 890.4496
2039-12-24 22:01 | -595.389 | 2.1143 | 64.5878 | 59.8258 | -174.4913
2039-12-25 23:01 | -1278.97 | 3.8265 | 63.7393 | 59.8258 | -374.8291
2039-12-27 00:01 | -1659.57 | 4.738 | 63.2036 | 59.8258 | -486.372
2039-12-28 01:01 | -1835.82 | 5.1588 | 62.862 | 59.8258 | -538.0257
2039-12-29 02:01 | -2112.32 | 5.9033 | 62.5826 | 59.8258 | -619.0599
2039-12-30 03:01 | -2366.24 | 6.108 | 62.1541 | 59.8258 | -693.4765
2039-12-31 04:01 | -2401.85 | 6.108 | 61.9164 | 59.8258 | -703.9127
2040-01-01 05:01 | -2728.24 | 6.108 | 61.5101 | 59.8258 | -799.5682
2040-01-02 06:01 | -2052.7 | 5.7371 | 61.7522 | 59.8258 | -601.587
2040-01-03 07:01 | -1664.76 | 4.6605 | 61.7207 | 59.8258 | -487.893
2040-01-04 08:01 | -2049.09 | 5.835 | 61.7589 | 59.8258 | -600.529
2040-01-05 09:01 | -1214.72 | 3.4031 | 61.6278 | 59.8258 | -355.9993
2040-01-06 10:01 | -1134.38 | 3.403 | 61.7619 | 59.8258 | -332.454
2040-01-07 11:01 | -1384.18 | 4.0979 | 61.7306 | 59.8258 | -405.6631
2040-01-08 12:01 | -1344.11 | 3.9285 | 61.6004 | 59.8258 | -393.9198
2040-01-09 13:01 | -904.969 | 2.7267 | 61.5374 | 59.8258 | -265.2202
2040-01-10 14:01 | -655.28 | 2.1451 | 61.6209 | 59.8258 | -192.0436
2040-01-11 15:01 | 2462.49 | 1 | 62.7464 | 59.8258 | 721.6846
2040-01-12 16:01 | 2995.69 | 1 | 79.6449 | 59.8258 | 877.9501
2040-01-13 17:01 | 2805.39 | 1 | 63.3228 | 59.8258 | 822.1786
2040-01-14 18:01 | -212.333 | 1.1287 | 62.8331 | 59.8258 | -62.2287
2040-01-15 19:01 | -587.701 | 2.0867 | 62.1047 | 59.8258 | -172.2382
2040-01-16 20:01 | -1444.91 | 4.3845 | 61.7279 | 59.8258 | -423.4613
2040-01-17 21:01 | -1991.22 | 5.7239 | 61.4247 | 59.8258 | -583.569
2040-01-18 22:01 | -2459.77 | 6.108 | 60.9547 | 59.8258 | -720.8874
2040-01-19 23:01 | -4306.03 | 6.108 | 59.3664 | 59.8258 | -1261.9728
2040-01-21 00:01 | -4754.33 | 6.108 | 58.6877 | 59.8258 | -1393.3566
2040-01-22 01:01 | -5065.23 | 6.108 | 58.1785 | 59.8258 | -1484.4724
2040-01-23 02:01 | -5292.8 | 6.108 | 57.7972 | 59.8258 | -1551.1666
2040-01-24 03:01 | -5294 | 6.108 | 57.5661 | 59.8258 | -1551.5182
2040-01-25 04:01 | -5550.74 | 6.108 | 57.1724 | 59.8258 | -1626.7613
2040-01-26 05:01 | -5677.52 | 6.108 | 56.8924 | 59.8258 | -1663.9169
2040-01-27 06:01 | -5032.65 | 6.108 | 57.2282 | 59.8258 | -1474.9241
2040-01-28 07:01 | -4275.47 | 6.108 | 57.7584 | 59.8258 | -1253.0166
2040-01-29 08:01 | -3902.36 | 6.108 | 58.0889 | 59.8258 | -1143.6688
2040-01-30 09:01 | -3446.26 | 6.108 | 58.4599 | 59.8258 | -1009.9991
2040-01-31 10:01 | -2402.6 | 6.108 | 59.2785 | 59.8258 | -704.1326
2040-02-01 11:01 | -1578.87 | 4.5159 | 59.6314 | 59.8258 | -462.7211
2040-02-02 12:01 | -1803.5 | 5.2893 | 59.8478 | 59.8258 | -528.5537
2040-02-03 13:01 | -1508.68 | 4.3699 | 59.8681 | 59.8258 | -442.1505
2040-02-04 14:01 | -1211.79 | 3.6078 | 59.9647 | 59.8258 | -355.1406
2040-02-05 15:01 | 0 | 1 | 61.5568 | 59.8258 | 0
2040-02-06 16:01 | 2933.23 | 1 | 61.4666 | 59.8258 | 859.6449
2040-02-07 17:01 | 0 | 0 | 62.2127 | 59.8258 | 0
2040-02-08 18:01 | -742.948 | 2.3838 | 60.684 | 59.8258 | -217.7366
2040-02-09 19:01 | -1326 | 4.0915 | 60.4885 | 59.8258 | -388.6122
2040-02-10 20:01 | -1804.43 | 5.2997 | 60.3378 | 59.8258 | -528.8262
2040-02-11 21:01 | -2147.24 | 6.108 | 60.1792 | 59.8258 | -629.2939
2040-02-12 22:01 | -2731.32 | 6.108 | 59.5708 | 59.8258 | -800.4709
2040-02-13 23:01 | -3909.1 | 6.108 | 58.5475 | 59.8258 | -1145.6441
2040-02-15 00:01 | -4135.61 | 6.108 | 58.1432 | 59.8258 | -1212.0276
2040-02-16 01:01 | -4451.8 | 6.108 | 57.7417 | 59.8258 | -1304.6938
2040-02-17 02:01 | -4503.4 | 6.108 | 57.5584 | 59.8258 | -1319.8163
2040-02-18 03:01 | -4559.16 | 6.108 | 57.3856 | 59.8258 | -1336.1579
2040-02-19 04:01 | -4455.14 | 6.108 | 57.3199 | 59.8258 | -1305.6726
2040-02-20 05:01 | -4192.75 | 6.108 | 57.4533 | 59.8258 | -1228.7737
2040-02-21 06:01 | -4775.36 | 6.108 | 56.9935 | 59.8258 | -1399.5199
2040-02-22 07:01 | -3555.62 | 6.108 | 57.7897 | 59.8258 | -1042.0494
2040-02-23 08:01 | -2792.77 | 6.108 | 58.4419 | 59.8258 | -818.4801
2040-02-24 09:01 | -837.003 | 2.4175 | 59.0762 | 59.8258 | -245.3014
2040-02-25 10:01 | 2718.56 | 1 | 60.7305 | 59.8258 | 796.7313
2040-02-26 11:01 | 4515.96 | 1.4133 | 76.2696 | 59.8258 | 1323.4972
2040-02-27 12:01 | 6081.86 | 1.9812 | 76.287 | 59.8258 | 1782.4172
2040-02-28 13:01 | 7500.69 | 2.3893 | 77.2049 | 59.8258 | 2198.2352
2040-02-29 14:01 | 8351.43 | 2.6878 | 77.6813 | 59.8258 | 2447.5625
2040-03-01 15:01 | 9469.74 | 3.0717 | 78.1144 | 59.8258 | 2775.3068
2040-03-02 16:01 | 8768.26 | 2.8198 | 78.7421 | 59.8258 | 2569.7233
2040-03-03 17:01 | 6596.87 | 2.1085 | 79.1304 | 59.8258 | 1933.3517
2040-03-04 18:01 | 4022.43 | 1.2774 | 79.2204 | 59.8258 | 1178.8579
2040-03-05 19:01 | 3106.94 | 1 | 83.8913 | 59.8258 | 910.5542
2040-03-06 20:01 | 0 | 0 | 64.3995 | 59.8258 | 0
2040-03-07 21:01 | -726.932 | 2.3499 | 62.476 | 59.8258 | -213.0427
2040-03-08 22:01 | -1986.19 | 5.8562 | 61.9291 | 59.8258 | -582.0948
2040-03-09 23:01 | -2555.62 | 6.108 | 61.1719 | 59.8258 | -748.9783
2040-03-11 00:01 | -3319.16 | 6.108 | 60.2689 | 59.8258 | -972.7498
2040-03-12 01:01 | -3351.79 | 6.108 | 59.8915 | 59.8258 | -982.3127
2040-03-13 02:01 | -3642.18 | 6.108 | 59.4427 | 59.8258 | -1067.4176
2040-03-14 03:01 | -4026.59 | 6.108 | 58.9157 | 59.8258 | -1180.077
2040-03-15 04:01 | -3680.05 | 6.108 | 58.9381 | 59.8258 | -1078.5162
2040-03-16 05:01 | -3223.01 | 6.108 | 59.1584 | 59.8258 | -944.571
2040-03-17 06:01 | -3455.22 | 6.108 | 58.9678 | 59.8258 | -1012.625
2040-03-18 07:01 | -2777.32 | 6.108 | 59.3883 | 59.8258 | -813.9521
2040-03-19 08:01 | -1707.66 | 4.8862 | 59.9067 | 59.8258 | -500.4657
2040-03-20 09:01 | 0 | 1 | 61.6603 | 59.8258 | 0
2040-03-21 10:01 | 3486.06 | 1.0668 | 76.9189 | 59.8258 | 1021.6633
2040-03-22 11:01 | 6007.05 | 1.9377 | 76.6933 | 59.8258 | 1760.4926
2040-03-23 12:01 | 7421.82 | 2.3998 | 77.3426 | 59.8258 | 2175.1207
2040-03-24 13:01 | 8482.92 | 2.7068 | 78.1202 | 59.8258 | 2486.0984
2040-03-25 14:01 | 8940.82 | 2.9147 | 78.3577 | 59.8258 | 2620.2957
2040-03-26 15:01 | 10178.2 | 3.2394 | 79.1443 | 59.8258 | 2982.936
2040-03-27 16:01 | 9339.34 | 2.9888 | 79.5395 | 59.8258 | 2737.0904
2040-03-28 17:01 | 7295.83 | 2.2699 | 80.191 | 59.8258 | 2138.1967
2040-03-29 18:01 | 4655.28 | 1.4864 | 79.7771 | 59.8258 | 1364.3279
2040-03-30 19:01 | 3117.33 | 1 | 80.1163 | 59.8258 | 913.5992
2040-03-31 20:01 | 3019.18 | 1 | 64.6398 | 59.8258 | 884.8343
2040-04-01 21:01 | 3087.6 | 1 | 64.488 | 59.8258 | 904.8862
2040-04-02 22:01 | -451.858 | 1.7712 | 63.5065 | 59.8258 | -132.4265
2040-04-03 23:01 | -761.849 | 2.4923 | 62.7282 | 59.8258 | -223.2759
2040-04-05 00:01 | -910.787 | 2.8483 | 62.3238 | 59.8258 | -266.9253
2040-04-06 01:01 | -1430.19 | 4.2591 | 62.056 | 59.8258 | -419.1473
2040-04-07 02:01 | -1595.49 | 4.6054 | 61.7586 | 59.8258 | -467.592
2040-04-08 03:01 | -1625.09 | 4.6705 | 61.5018 | 59.8258 | -476.2669
2040-04-09 04:01 | -1593.9 | 4.5849 | 61.3644 | 59.8258 | -467.126
2040-04-10 05:01 | -1251.33 | 3.6389 | 61.2805 | 59.8258 | -366.7286
2040-04-11 06:01 | -1042.29 | 3.1431 | 61.3177 | 59.8258 | -305.465
2040-04-12 07:01 | -1154.74 | 3.5017 | 61.337 | 59.8258 | -338.4209
2040-04-13 08:01 | -1302.85 | 3.8846 | 61.279 | 59.8258 | -381.8276
2040-04-14 09:01 | -842.762 | 2.5676 | 61.2374 | 59.8258 | -246.9892
2040-04-15 10:01 | -384.957 | 1.4166 | 61.5039 | 59.8258 | -112.8198
2040-04-16 11:01 | 0 | 1 | 62.7757 | 59.8258 | 0
2040-04-17 12:01 | -296.997 | 1.3431 | 61.7803 | 59.8258 | -87.0412
2040-04-18 13:01 | -297.189 | 1.2839 | 61.6696 | 59.8258 | -87.0975
2040-04-19 14:01 | 2337.86 | 1 | 62.4634 | 59.8258 | 685.1591
2040-04-20 15:01 | 4576.64 | 1.6343 | 75.7832 | 59.8258 | 1341.2808
2040-04-21 16:01 | 4715.25 | 1.6937 | 76.1087 | 59.8258 | 1381.9034
2040-04-22 17:01 | 3379.58 | 1.1349 | 77.2454 | 59.8258 | 990.4571
2040-04-23 18:01 | 3032.34 | 1 | 86.2961 | 59.8258 | 888.6911
2040-04-24 19:01 | 2884.9 | 1 | 63.4304 | 59.8258 | 845.4807
2040-04-25 20:01 | -631.208 | 2.2558 | 62.4647 | 59.8258 | -184.9888
2040-04-26 21:01 | -1140.52 | 3.5233 | 61.8002 | 59.8258 | -334.2534
2040-04-27 22:01 | -2437.87 | 6.108 | 61.1485 | 59.8258 | -714.4692
2040-04-28 23:01 | -3192.27 | 6.108 | 60.2787 | 59.8258 | -935.562
2040-04-30 00:01 | -3479.01 | 6.108 | 59.762 | 59.8258 | -1019.5972
2040-05-01 01:01 | -3836.32 | 6.108 | 59.2482 | 59.8258 | -1124.3144
2040-05-02 02:01 | -3791.8 | 6.108 | 59.0812 | 59.8258 | -1111.2669
2040-05-03 03:01 | -4335.98 | 6.108 | 58.4981 | 59.8258 | -1270.7503
2040-05-04 04:01 | -4155.88 | 6.108 | 58.4189 | 59.8258 | -1217.9682
2040-05-05 05:01 | -3505.57 | 6.108 | 58.7751 | 59.8258 | -1027.3812
2040-05-06 06:01 | -4170.46 | 6.108 | 58.2536 | 59.8258 | -1222.2412
2040-05-07 07:01 | -3438.34 | 6.108 | 58.6489 | 59.8258 | -1007.678
2040-05-08 08:01 | -2421.79 | 6.108 | 59.4091 | 59.8258 | -709.7566
2040-05-09 09:01 | -1034.13 | 2.951 | 59.7424 | 59.8258 | -303.0736
2040-05-10 10:01 | 2381.13 | 1 | 61.3644 | 59.8258 | 697.8403
2040-05-11 11:01 | 3344.04 | 1.0704 | 76.4576 | 59.8258 | 980.0414
2040-05-12 12:01 | 4929.49 | 1.5745 | 76.9035 | 59.8258 | 1444.6909
2040-05-13 13:01 | 5839.04 | 1.8924 | 77.1841 | 59.8258 | 1711.2537
2040-05-14 14:01 | 6758.07 | 2.1746 | 77.7336 | 59.8258 | 1980.5948
2040-05-15 15:01 | 6847.55 | 2.1877 | 78.261 | 59.8258 | 2006.8188
2040-05-16 16:01 | 6648.92 | 2.1019 | 78.6882 | 59.8258 | 1948.6061
2040-05-17 17:01 | 4963.58 | 1.6021 | 78.5976 | 59.8258 | 1454.6817
2040-05-18 18:01 | 3096.69 | 1 | 80.9837 | 59.8258 | 907.5503
2040-05-19 19:01 | 2999.94 | 1 | 63.9291 | 59.8258 | 879.1956
2040-05-20 20:01 | -244.464 | 1.2048 | 63.204 | 59.8258 | -71.6453
2040-05-21 21:01 | -1083.96 | 3.4326 | 62.2324 | 59.8258 | -317.6773
2040-05-22 22:01 | -2273.86 | 6.108 | 61.5802 | 59.8258 | -666.4026
2040-05-23 23:01 | -2702.91 | 6.108 | 60.8929 | 59.8258 | -792.1447
2040-05-25 00:01 | -2884.73 | 6.108 | 60.4557 | 59.8258 | -845.4309
2040-05-26 01:01 | -3170.06 | 6.108 | 59.9785 | 59.8258 | -929.0529
2040-05-27 02:01 | -3211.73 | 6.108 | 59.7337 | 59.8258 | -941.2651
2040-05-28 03:01 | -3004.02 | 6.108 | 59.7135 | 59.8258 | -880.3914
2040-05-29 04:01 | -2932.72 | 6.108 | 59.6599 | 59.8258 | -859.4954
2040-05-30 05:01 | -2462.12 | 6.108 | 59.9276 | 59.8258 | -721.5761
2040-05-31 06:01 | -2872.11 | 6.108 | 59.6198 | 59.8258 | -841.7324
2040-06-01 07:01 | -2323 | 6.108 | 59.9451 | 59.8258 | -680.8041
2040-06-02 08:01 | -1820.38 | 5.1749 | 60.1026 | 59.8258 | -533.5007
2040-06-03 09:01 | 0 | 0 | 61.781 | 59.8258 | 0
2040-06-04 10:01 | 2814.32 | 1.0565 | 74.2482 | 59.8258 | 824.7958
2040-06-05 11:01 | 5097.07 | 1.6743 | 76.444 | 59.8258 | 1493.8038
2040-06-06 12:01 | 6673.75 | 2.1535 | 77.2713 | 59.8258 | 1955.8831
2040-06-07 13:01 | 6721.3 | 2.1395 | 78.0249 | 59.8258 | 1969.8186
2040-06-08 14:01 | 5549 | 1.7827 | 78.2709 | 59.8258 | 1626.2514
2040-06-09 15:01 | 6428.21 | 2.1034 | 78.1107 | 59.8258 | 1883.9224
2040-06-10 16:01 | 6035.83 | 1.8655 | 79.1582 | 59.8258 | 1768.9272
2040-06-11 17:01 | 5036.52 | 1.6079 | 78.8124 | 59.8258 | 1476.0583
2040-06-12 18:01 | 3931.85 | 1.2377 | 78.9866 | 59.8258 | 1152.3115
2040-06-13 19:01 | 3159.93 | 1 | 83.6123 | 59.8258 | 926.0841
2040-06-14 20:01 | 3079.79 | 1 | 64.003 | 59.8258 | 902.5974
2040-06-15 21:01 | -62.1064 | 0.72298 | 63.8606 | 59.8258 | -18.2016
2040-06-16 22:01 | -998.507 | 3.2251 | 62.3984 | 59.8258 | -292.6335
2040-06-17 23:01 | -1623.12 | 4.7719 | 61.8773 | 59.8258 | -475.6895
2040-06-19 00:01 | -2088.16 | 5.9518 | 61.5336 | 59.8258 | -611.9793
2040-06-20 01:01 | -2286.8 | 6.108 | 61.1538 | 59.8258 | -670.1949
2040-06-21 02:01 | -2570.93 | 6.108 | 60.7054 | 59.8258 | -753.4652
2040-06-22 03:01 | -2600.85 | 6.108 | 60.498 | 59.8258 | -762.2339
2040-06-23 04:01 | -2849.3 | 6.108 | 60.1708 | 59.8258 | -835.0474
2040-06-24 05:01 | -2975.2 | 6.108 | 59.9323 | 59.8258 | -871.945
2040-06-25 06:01 | -2236.35 | 6.108 | 60.3664 | 59.8258 | -655.4095
2040-06-26 07:01 | -1261.58 | 3.5632 | 60.4225 | 59.8258 | -369.7326
2040-06-27 08:01 | -1737.5 | 5.1412 | 60.5996 | 59.8258 | -509.211
2040-06-28 09:01 | -2035.97 | 5.8453 | 60.5253 | 59.8258 | -596.6839
2040-06-29 10:01 | -1737.31 | 4.9351 | 60.4125 | 59.8258 | -509.1553
2040-06-30 11:01 | -1319.87 | 3.8388 | 60.4158 | 59.8258 | -386.8157
2040-07-01 12:01 | -1360.39 | 4.0566 | 60.444 | 59.8258 | -398.691
2040-07-02 13:01 | -1239.28 | 3.6973 | 60.3681 | 59.8258 | -363.1971
2040-07-03 14:01 | -1039.1 | 3.1669 | 60.3443 | 59.8258 | -304.5301
2040-07-04 15:01 | -812.187 | 2.577 | 60.3681 | 59.8258 | -238.0285
2040-07-05 16:01 | 2123.46 | 1 | 61.6059 | 59.8258 | 622.3247
2040-07-06 17:01 | 94.391 | 1 | 62.1565 | 59.8258 | 27.6633
2040-07-07 18:01 | -30.2836 | 0.66561 | 61.885 | 59.8258 | -8.8752
2040-07-08 19:01 | -463.508 | 1.8099 | 60.8408 | 59.8258 | -135.8408
2040-07-09 20:01 | -614.235 | 2.1395 | 60.651 | 59.8258 | -180.0145
2040-07-10 21:01 | -890.63 | 2.8866 | 60.5331 | 59.8258 | -261.0179
2040-07-11 22:01 | -1049.77 | 3.2715 | 60.3893 | 59.8258 | -307.6572
2040-07-12 23:01 | -2440.58 | 6.108 | 59.9937 | 59.8258 | -715.2634
2040-07-14 00:01 | -2792.51 | 6.108 | 59.5251 | 59.8258 | -818.4039
2040-07-15 01:01 | -2743.95 | 6.108 | 59.404 | 59.8258 | -804.1724
2040-07-16 02:01 | -2866.64 | 6.108 | 59.2328 | 59.8258 | -840.1293
2040-07-17 03:01 | -2874.52 | 6.108 | 59.1436 | 59.8258 | -842.4387
2040-07-18 04:01 | -3021.7 | 6.108 | 58.9258 | 59.8258 | -885.5729
2040-07-19 05:01 | -3124.57 | 6.108 | 58.7794 | 59.8258 | -915.7211
2040-07-20 06:01 | -3160.24 | 6.108 | 58.6835 | 59.8258 | -926.1749
2040-07-21 07:01 | -2365.8 | 6.108 | 59.2103 | 59.8258 | -693.3475
2040-07-22 08:01 | -1987.81 | 5.7073 | 59.4418 | 59.8258 | -582.5696
2040-07-23 09:01 | -2396.97 | 6.108 | 59.2994 | 59.8258 | -702.4826
2040-07-24 10:01 | -1964.98 | 5.6432 | 59.4468 | 59.8258 | -575.8788
2040-07-25 11:01 | -1687.65 | 4.8716 | 59.4769 | 59.8258 | -494.6014
2040-07-26 12:01 | -1017.12 | 3.0217 | 59.5698 | 59.8258 | -298.0884
2040-07-27 13:01 | -264.489 | 1.0584 | 60.0567 | 59.8258 | -77.5141
2040-07-28 14:01 | -381.145 | 1.5624 | 60.2225 | 59.8258 | -111.7026
2040-07-29 15:01 | -662.903 | 2.3123 | 60.0828 | 59.8258 | -194.2777
2040-07-30 16:01 | -321.846 | 1.2845 | 60.2202 | 59.8258 | -94.3238
2040-07-31 17:01 | 2678.8 | 1 | 61.1845 | 59.8258 | 785.0788
2040-08-01 18:01 | -261.936 | 1.2971 | 60.9419 | 59.8258 | -76.7659
2040-08-02 19:01 | -816.281 | 2.7562 | 60.3524 | 59.8258 | -239.2283
2040-08-03 20:01 | -1298.49 | 4.0025 | 60.0599 | 59.8258 | -380.5499
2040-08-04 21:01 | -2021.93 | 5.9607 | 59.9208 | 59.8258 | -592.5692
2040-08-05 22:01 | -2553.46 | 6.108 | 59.4271 | 59.8258 | -748.3453
2040-08-06 23:01 | -3134.51 | 6.108 | 58.7855 | 59.8258 | -918.6342
2040-08-08 00:01 | -4311.78 | 6.108 | 57.7373 | 59.8258 | -1263.658
2040-08-09 01:01 | -4744.56 | 6.108 | 57.1407 | 59.8258 | -1390.4933
2040-08-10 02:01 | -4896.18 | 6.108 | 56.7967 | 59.8258 | -1434.9287
2040-08-11 03:01 | -5412.35 | 6.108 | 56.2451 | 59.8258 | -1586.2032
2040-08-12 04:01 | -5194.87 | 6.108 | 56.2049 | 59.8258 | -1522.4661
2040-08-13 05:01 | -4975.02 | 6.108 | 56.2105 | 59.8258 | -1458.0344
2040-08-14 06:01 | -4640.06 | 6.108 | 56.3965 | 59.8258 | -1359.8673
2040-08-15 07:01 | -3585.06 | 6.108 | 57.1539 | 59.8258 | -1050.6774
2040-08-16 08:01 | -1691.3 | 4.9786 | 58.3753 | 59.8258 | -495.6711
2040-08-17 09:01 | -913.728 | 2.7453 | 58.7034 | 59.8258 | -267.7872
2040-08-18 10:01 | 0 | 0 | 60.4824 | 59.8258 | 0
2040-08-19 11:01 | 3091.54 | 1 | 81.3241 | 59.8258 | 906.0409
2040-08-20 12:01 | 3535.96 | 1.1931 | 74.887 | 59.8258 | 1036.2876
2040-08-21 13:01 | 4339.47 | 1.4354 | 75.6079 | 59.8258 | 1271.7731
2040-08-22 14:01 | 4436.53 | 1.4746 | 75.9118 | 59.8258 | 1300.2186
2040-08-23 15:01 | 4087.81 | 1.3601 | 76.2113 | 59.8258 | 1198.0189
2040-08-24 16:01 | 4750.62 | 1.5362 | 76.8002 | 59.8258 | 1392.2693
2040-08-25 17:01 | 3010.97 | 1 | 77.216 | 59.8258 | 882.4282
2040-08-26 18:01 | 3015.93 | 1 | 62.5887 | 59.8258 | 883.8818
2040-08-27 19:01 | 0 | 0 | 62.8827 | 59.8258 | 0
2040-08-28 20:01 | -702.222 | 2.3237 | 61.1481 | 59.8258 | -205.801
2040-08-29 21:01 | -1854.62 | 5.5752 | 60.7446 | 59.8258 | -543.5355
2040-08-30 22:01 | -2683.48 | 6.108 | 59.9558 | 59.8258 | -786.4504
2040-08-31 23:01 | -3549.65 | 6.108 | 58.9961 | 59.8258 | -1040.2997
2040-09-02 00:01 | -4207.15 | 6.108 | 58.1633 | 59.8258 | -1232.994
2040-09-03 01:01 | -4552.81 | 6.108 | 57.6142 | 59.8258 | -1334.2969
2040-09-04 02:01 | -4891.88 | 6.108 | 57.1064 | 59.8258 | -1433.6685
2040-09-05 03:01 | -4856 | 6.108 | 56.908 | 59.8258 | -1423.1531
2040-09-06 04:01 | -4908.24 | 6.108 | 56.6905 | 59.8258 | -1438.4631
2040-09-07 05:01 | -4543.5 | 6.108 | 56.8253 | 59.8258 | -1331.5684
2040-09-08 06:01 | -4060.23 | 6.108 | 57.1145 | 59.8258 | -1189.936
2040-09-09 07:01 | -3567.66 | 6.108 | 57.4897 | 59.8258 | -1045.5779
2040-09-10 08:01 | -2310.31 | 6.108 | 58.468 | 59.8258 | -677.085
2040-09-11 09:01 | -1303.19 | 3.7629 | 58.7802 | 59.8258 | -381.9273
2040-09-12 10:01 | 2251.6 | 1 | 60.3834 | 59.8258 | 659.8788
2040-09-13 11:01 | 3126.06 | 1 | 60.8855 | 59.8258 | 916.1577
2040-09-14 12:01 | 4055.07 | 1.3182 | 75.7153 | 59.8258 | 1188.4237
2040-09-15 13:01 | 4996.8 | 1.6048 | 76.2305 | 59.8258 | 1464.4175
2040-09-16 14:01 | 3991.18 | 1.2825 | 76.6406 | 59.8258 | 1169.6994
2040-09-17 15:01 | 4237.07 | 1.3304 | 77.1396 | 59.8258 | 1241.7626
2040-09-18 16:01 | 4399.35 | 1.3747 | 77.3483 | 59.8258 | 1289.3222
2040-09-19 17:01 | 3112.75 | 1 | 78.9326 | 59.8258 | 912.257
2040-09-20 18:01 | 3086.47 | 1 | 82.3114 | 59.8258 | 904.5551
2040-09-21 19:01 | 3155.88 | 1 | 62.5742 | 59.8258 | 924.8971
2040-09-22 20:01 | 0 | 0 | 62.9512 | 59.8258 | 0
2040-09-23 21:01 | -715.254 | 2.3596 | 61.2104 | 59.8258 | -209.6203
2040-09-24 22:01 | -1008.43 | 3.1853 | 60.8418 | 59.8258 | -295.5417
2040-09-25 23:01 | -1934.36 | 5.7368 | 60.5809 | 59.8258 | -566.905
2040-09-27 00:01 | -2143 | 6.108 | 60.2614 | 59.8258 | -628.0513
2040-09-28 01:01 | -2323.92 | 6.108 | 59.8941 | 59.8258 | -681.0737
2040-09-29 02:01 | -2637.04 | 6.108 | 59.5333 | 59.8258 | -772.8401
2040-09-30 03:01 | -2782.6 | 6.108 | 59.2874 | 59.8258 | -815.4996
2040-10-01 04:01 | -2465.72 | 6.108 | 59.3963 | 59.8258 | -722.6312
2040-10-02 05:01 | -2585.56 | 6.108 | 59.2739 | 59.8258 | -757.7528
2040-10-03 06:01 | -2104.29 | 6.0485 | 59.5564 | 59.8258 | -616.7065
2040-10-04 07:01 | -1874.48 | 5.3652 | 59.5437 | 59.8258 | -549.3559
2040-10-05 08:01 | -2048.4 | 5.9303 | 59.5962 | 59.8258 | -600.3268
2040-10-06 09:01 | -2113.98 | 6.0669 | 59.5642 | 59.8258 | -619.5464
2040-10-07 10:01 | -1843.86 | 5.2786 | 59.5025 | 59.8258 | -540.382
2040-10-08 11:01 | -1530.39 | 4.4532 | 59.513 | 59.8258 | -448.513
2040-10-09 12:01 | -1033.19 | 3.1083 | 59.5617 | 59.8258 | -302.7981
2040-10-10 13:01 | -1011.64 | 3.1721 | 59.6518 | 59.8258 | -296.4824
2040-10-11 14:01 | -1082.85 | 3.3692 | 59.645 | 59.8258 | -317.352
2040-10-12 15:01 | -1226.08 | 3.7611 | 59.6018 | 59.8258 | -359.3286
2040-10-13 16:01 | -536.128 | 1.7602 | 59.6417 | 59.8258 | -157.1236
2040-10-14 17:01 | -297.596 | 1.2705 | 60.0256 | 59.8258 | -87.2168
2040-10-15 18:01 | 0 | 0 | 61.1472 | 59.8258 | 0
2040-10-16 19:01 | -392.34 | 1.636 | 60.1046 | 59.8258 | -114.9835
2040-10-17 20:01 | -619.341 | 2.1884 | 59.9108 | 59.8258 | -181.5109
2040-10-18 21:01 | -1238.78 | 3.8991 | 59.7512 | 59.8258 | -363.0506
2040-10-19 22:01 | -1322.44 | 3.9856 | 59.6139 | 59.8258 | -387.5689
2040-10-20 23:01 | -1820.1 | 5.4088 | 59.5552 | 59.8258 | -533.4187
2040-10-22 00:01 | -1988.56 | 5.7664 | 59.4277 | 59.8258 | -582.7894
2040-10-23 01:01 | -1868.45 | 5.3899 | 59.3482 | 59.8258 | -547.5886
2040-10-24 02:01 | -1655.64 | 4.813 | 59.3411 | 59.8258 | -485.2202
2040-10-25 03:01 | -1355.04 | 4.0019 | 59.3908 | 59.8258 | -397.123
2040-10-26 04:01 | -1085.98 | 3.3059 | 59.4798 | 59.8258 | -318.2693
2040-10-27 05:01 | -888.044 | 2.8038 | 59.5972 | 59.8258 | -260.26
2040-10-28 06:01 | -467.65 | 1.6547 | 59.8138 | 59.8258 | -137.0547
2040-10-29 07:01 | 4.0801 | 1 | 61.2064 | 59.8258 | 1.1958
2040-10-30 08:01 | 2259.6 | 1 | 77.1058 | 59.8258 | 662.2234
2040-10-31 09:01 | 3134.84 | 1.0461 | 75.4131 | 59.8258 | 918.7309
2040-11-01 10:01 | 4058.23 | 1.3195 | 76.119 | 59.8258 | 1189.3498
2040-11-02 11:01 | 4151.31 | 1.339 | 76.569 | 59.8258 | 1216.6289
2040-11-03 12:01 | 5763.53 | 1.9051 | 76.4715 | 59.8258 | 1689.1239
2040-11-04 13:01 | 5827.83 | 1.8132 | 77.7559 | 59.8258 | 1707.9684
2040-11-05 14:01 | 5540.44 | 1.6503 | 78.6907 | 59.8258 | 1623.7427
2040-11-06 15:01 | 5639.82 | 1.7425 | 78.2954 | 59.8258 | 1652.8681
2040-11-07 16:01 | 5348.64 | 1.6878 | 78.1465 | 59.8258 | 1567.5316
2040-11-08 17:01 | 4157.81 | 1.3247 | 78.1306 | 59.8258 | 1218.5338
2040-11-09 18:01 | 2995.27 | 1 | 79.4877 | 59.8258 | 877.827
2040-11-10 19:01 | 2993.7 | 1 | 63.2967 | 59.8258 | 877.3669
2040-11-11 20:01 | 2968.23 | 1 | 63.2545 | 59.8258 | 869.9023
2040-11-12 21:01 | -598.456 | 2.1908 | 62.2482 | 59.8258 | -175.3901
2040-11-13 22:01 | -1016.53 | 3.1965 | 61.5368 | 59.8258 | -297.9155
2040-11-14 23:01 | -1929.34 | 5.6824 | 61.1153 | 59.8258 | -565.4337
2040-11-16 00:01 | -2293.1 | 6.108 | 60.6589 | 59.8258 | -672.0413
2040-11-17 01:01 | -2616.32 | 6.108 | 60.1408 | 59.8258 | -766.7677
2040-11-18 02:01 | -2793.45 | 6.108 | 59.7435 | 59.8258 | -818.6794
2040-11-19 03:01 | -2948.39 | 6.108 | 59.4497 | 59.8258 | -864.0878
2040-11-20 04:01 | -2844.83 | 6.108 | 59.3592 | 59.8258 | -833.7374
2040-11-21 05:01 | -2671.04 | 6.108 | 59.3831 | 59.8258 | -782.8046
2040-11-22 06:01 | -2206.03 | 6.108 | 59.6658 | 59.8258 | -646.5236
2040-11-23 07:01 | -2080.92 | 5.947 | 59.7039 | 59.8258 | -609.8575
2040-11-24 08:01 | -1930.87 | 5.5294 | 59.6661 | 59.8258 | -565.8821
2040-11-25 09:01 | -2123.27 | 6.108 | 59.6673 | 59.8258 | -622.269
2040-11-26 10:01 | -1834.58 | 5.2414 | 59.5993 | 59.8258 | -537.6623
2040-11-27 11:01 | -1468.52 | 4.2737 | 59.6153 | 59.8258 | -430.3807
2040-11-28 12:01 | -1105.33 | 3.3268 | 59.6746 | 59.8258 | -323.9402
2040-11-29 13:01 | -892.591 | 2.8089 | 59.766 | 59.8258 | -261.5926
2040-11-30 14:01 | -906.213 | 2.8949 | 59.8088 | 59.8258 | -265.5848
2040-12-01 15:01 | -727.252 | 2.3789 | 59.8423 | 59.8258 | -213.1365
2040-12-02 16:01 | 63.9833 | 1 | 61.2481 | 59.8258 | 18.7517
2040-12-03 17:01 | -125.105 | 0.90804 | 60.7303 | 59.8258 | -36.6647
2040-12-04 18:01 | -449.02 | 1.7651 | 60.2224 | 59.8258 | -131.5948
2040-12-05 19:01 | -1062.07 | 3.4259 | 59.9353 | 59.8258 | -311.262
2040-12-06 20:01 | -1538.07 | 4.6401 | 59.7492 | 59.8258 | -450.7638
2040-12-07 21:01 | -2602.98 | 6.108 | 59.2341 | 59.8258 | -762.8581
2040-12-08 22:01 | -3126.65 | 6.108 | 58.6436 | 59.8258 | -916.3307
2040-12-09 23:01 | -4099.09 | 6.108 | 57.731 | 59.8258 | -1201.3247
2040-12-11 00:01 | -4738.11 | 6.108 | 57.0081 | 59.8258 | -1388.603
2040-12-12 01:01 | -4874.09 | 6.108 | 56.6616 | 59.8258 | -1428.4548
2040-12-13 02:01 | -5045.66 | 6.108 | 56.3522 | 59.8258 | -1478.737
2040-12-14 03:01 | -5050.55 | 6.108 | 56.1959 | 59.8258 | -1480.1701
2040-12-15 04:01 | -5270.84 | 6.108 | 55.8938 | 59.8258 | -1544.7307
2040-12-16 05:01 | -5447.26 | 6.108 | 55.6218 | 59.8258 | -1596.4343
2040-12-17 06:01 | -5680.44 | 6.108 | 55.3102 | 59.8258 | -1664.7726
2040-12-18 07:01 | -4389.34 | 6.108 | 56.1324 | 59.8258 | -1286.3886
2040-12-19 08:01 | -2581.46 | 6.108 | 57.5383 | 59.8258 | -756.5512
2040-12-20 09:01 | -1780.82 | 5.2092 | 58.147 | 59.8258 | -521.9068
2040-12-21 10:01 | -732.592 | 2.2104 | 58.3907 | 59.8258 | -214.7015
2040-12-22 11:01 | 2114.51 | 1 | 59.9686 | 59.8258 | 619.7017
2040-12-23 12:01 | 2930.04 | 1 | 60.4451 | 59.8258 | 858.71
2040-12-24 13:01 | 2930.68 | 1 | 83.7019 | 59.8258 | 858.8975
2040-12-25 14:01 | 2799.81 | 1 | 79.2137 | 59.8258 | 820.5433
2040-12-26 15:01 | 2836.62 | 1 | 81.3455 | 59.8258 | 831.3313
2040-12-27 16:01 | 2754.51 | 1 | 61.4907 | 59.8258 | 807.2672
2040-12-28 17:01 | 2923.51 | 1 | 61.5917 | 59.8258 | 856.7962
2040-12-29 18:01 | -297.747 | 1.3789 | 60.987 | 59.8258 | -87.261
2040-12-30 19:01 | -1114.23 | 3.5918 | 60.2257 | 59.8258 | -326.5486
2040-12-31 20:01 | -1812.55 | 5.4055 | 59.8375 | 59.8258 | -531.206
2041-01-01 21:01 | -2461.8 | 6.108 | 59.326 | 59.8258 | -721.4824
2041-01-02 22:01 | -3141.76 | 6.108 | 58.5889 | 59.8258 | -920.759
2041-01-03 23:01 | -3716.75 | 6.108 | 57.8718 | 59.8258 | -1089.2719
2041-01-05 00:01 | -5533.41 | 6.108 | 56.2772 | 59.8258 | -1621.6824
2041-01-06 01:01 | -5822.84 | 6.108 | 55.652 | 59.8258 | -1706.5059
2041-01-07 02:01 | -6080.48 | 6.108 | 55.1552 | 59.8258 | -1782.0128
2041-01-08 03:01 | -6113.17 | 6.108 | 54.8859 | 59.8258 | -1791.5933
2041-01-09 04:01 | -6290.98 | 6.108 | 54.5455 | 59.8258 | -1843.7042
2041-01-10 05:01 | -6401.3 | 6.108 | 54.2536 | 59.8258 | -1876.0358
2041-01-11 06:01 | -6553.08 | 6.108 | 54.0041 | 59.8258 | -1920.5182
2041-01-12 07:01 | -4959.77 | 6.108 | 55.0609 | 59.8258 | -1453.5651
2041-01-13 08:01 | -3136.12 | 6.108 | 56.5258 | 59.8258 | -919.106
2041-01-14 09:01 | -2257.66 | 6.108 | 57.4497 | 59.8258 | -661.6548
2041-01-15 10:01 | -1016.56 | 2.9699 | 57.7991 | 59.8258 | -297.9243
2041-01-16 11:01 | 1964.76 | 1 | 59.4709 | 59.8258 | 575.8143
2041-01-17 12:01 | 2932.77 | 1 | 82.9354 | 59.8258 | 859.51
2041-01-18 13:01 | 2854.89 | 1 | 74.7553 | 59.8258 | 836.6857
2041-01-19 14:01 | 2912.34 | 1 | 74.8399 | 59.8258 | 853.5226
2041-01-20 15:01 | 2907.13 | 1 | 75.4632 | 59.8258 | 851.9957
2041-01-21 16:01 | 2871.32 | 1 | 61.1925 | 59.8258 | 841.5008
2041-01-22 17:01 | 2921.16 | 1 | 85.1002 | 59.8258 | 856.1075
2041-01-23 18:01 | 0 | 0 | 61.7301 | 59.8258 | 0
2041-01-24 19:01 | -843.494 | 2.7519 | 60.0581 | 59.8258 | -247.2037
2041-01-25 20:01 | -1707.3 | 5.1888 | 59.7246 | 59.8258 | -500.3602
2041-01-26 21:01 | -2485.62 | 6.108 | 59.1647 | 59.8258 | -728.4633
2041-01-27 22:01 | -3009.07 | 6.108 | 58.5328 | 59.8258 | -881.8714
2041-01-28 23:01 | -3370.4 | 6.108 | 57.9975 | 59.8258 | -987.7667
2041-01-30 00:01 | -4711.16 | 6.108 | 56.8048 | 59.8258 | -1380.7047
2041-01-31 01:01 | -5171.92 | 6.108 | 56.1468 | 59.8258 | -1515.7401
2041-02-01 02:01 | -5433.87 | 6.108 | 55.685 | 59.8258 | -1592.5101
2041-02-02 03:01 | -5632.71 | 6.108 | 55.3244 | 59.8258 | -1650.7843
2041-02-03 04:01 | -5544.41 | 6.108 | 55.1963 | 59.8258 | -1624.9062
2041-02-04 05:01 | -5351.29 | 6.108 | 55.1881 | 59.8258 | -1568.3083
2041-02-05 06:01 | -4942.63 | 6.108 | 55.4345 | 59.8258 | -1448.5419
2041-02-06 07:01 | -4280.97 | 6.108 | 55.9183 | 59.8258 | -1254.6285
2041-02-07 08:01 | -2813.32 | 6.108 | 57.0634 | 59.8258 | -824.5027
2041-02-08 09:01 | -1630.93 | 4.7997 | 57.8138 | 59.8258 | -477.9784
2041-02-09 10:01 | 0 | 1 | 59.6159 | 59.8258 | 0
2041-02-10 11:01 | 2986.42 | 1 | 77.9037 | 59.8258 | 875.2333
2041-02-11 12:01 | 4486.51 | 1.4519 | 74.6516 | 59.8258 | 1314.8663
2041-02-12 13:01 | 5619.26 | 1.8077 | 75.3037 | 59.8258 | 1646.8425
2041-02-13 14:01 | 5827.46 | 1.8766 | 75.7902 | 59.8258 | 1707.8599
2041-02-14 15:01 | 6019.31 | 1.918 | 76.3283 | 59.8258 | 1764.0856
2041-02-15 16:01 | 5537.58 | 1.7846 | 76.4948 | 59.8258 | 1622.9045
2041-02-16 17:01 | 3691.65 | 1.1939 | 76.6242 | 59.8258 | 1081.9158
2041-02-17 18:01 | 3004.28 | 1 | 81.2007 | 59.8258 | 880.4676
2041-02-18 19:01 | 3010.36 | 1 | 62.0845 | 59.8258 | 882.2494
2041-02-19 20:01 | 0 | 0 | 62.3846 | 59.8258 | 0
2041-02-20 21:01 | -1267.75 | 3.8927 | 60.5233 | 59.8258 | -371.5408
2041-02-21 22:01 | -1939.02 | 5.7208 | 60.0909 | 59.8258 | -568.2707
2041-02-22 23:01 | -3238.76 | 6.108 | 58.9414 | 59.8258 | -949.1869
2041-02-24 00:01 | -3867.6 | 6.108 | 58.1109 | 59.8258 | -1133.4817
2041-02-25 01:01 | -4274.85 | 6.108 | 57.4485 | 59.8258 | -1252.8349
2041-02-26 02:01 | -4460.57 | 6.108 | 57.0458 | 59.8258 | -1307.264
2041-02-27 03:01 | -4661.73 | 6.108 | 56.6796 | 59.8258 | -1366.2182
2041-02-28 04:01 | -4680.27 | 6.108 | 56.4674 | 59.8258 | -1371.6517
2041-03-01 05:01 | -4589.75 | 6.108 | 56.4018 | 59.8258 | -1345.1229
2041-03-02 06:01 | -4309.23 | 6.108 | 56.5179 | 59.8258 | -1262.9106
2041-03-03 07:01 | -3700.44 | 6.108 | 56.9134 | 59.8258 | -1084.4919
2041-03-04 08:01 | -2245.55 | 6.108 | 58.03 | 59.8258 | -658.1057
2041-03-05 09:01 | -1809.25 | 5.2626 | 58.3295 | 59.8258 | -530.2388
2041-03-06 10:01 | -827.958 | 2.4771 | 58.5099 | 59.8258 | -242.6505
2041-03-07 11:01 | -512.833 | 1.8317 | 58.9424 | 59.8258 | -150.2965
2041-03-08 12:01 | -177.104 | 0.93105 | 59.4989 | 59.8258 | -51.9041
2041-03-09 13:01 | 44.3044 | 1 | 60.4916 | 59.8258 | 12.9843
2041-03-10 14:01 | 30.6016 | 1 | 60.5835 | 59.8258 | 8.9684
2041-03-11 15:01 | 2802.34 | 1 | 60.3927 | 59.8258 | 821.2848
2041-03-12 16:01 | 3163.05 | 1 | 60.7658 | 59.8258 | 926.9984
2041-03-13 17:01 | 3074.13 | 1 | 61.0761 | 59.8258 | 900.9386
2041-03-14 18:01 | 2930.83 | 1 | 61.2658 | 59.8258 | 858.9415
2041-03-15 19:01 | -202.562 | 1.1432 | 60.8572 | 59.8258 | -59.3651
2041-03-16 20:01 | -627.022 | 2.2451 | 60.1212 | 59.8258 | -183.762
2041-03-17 21:01 | -1575.44 | 4.8572 | 59.7184 | 59.8258 | -461.7159
2041-03-18 22:01 | -2018.52 | 5.907 | 59.431 | 59.8258 | -591.5698
2041-03-19 23:01 | -3045.26 | 6.108 | 58.5225 | 59.8258 | -892.4776
2041-03-21 00:01 | -3399.86 | 6.108 | 57.9902 | 59.8258 | -996.4006
2041-03-22 01:01 | -3657.55 | 6.108 | 57.629 | 59.8258 | -1071.9221
2041-03-23 02:01 | -3835.56 | 6.108 | 57.3599 | 59.8258 | -1124.0917
2041-03-24 03:01 | -3961.68 | 6.108 | 57.1239 | 59.8258 | -1161.0538
2041-03-25 04:01 | -4060.11 | 6.108 | 56.9165 | 59.8258 | -1189.9008
2041-03-26 05:01 | -4189.5 | 6.108 | 56.7091 | 59.8258 | -1227.8212
2041-03-27 06:01 | -4046.56 | 6.108 | 56.7048 | 59.8258 | -1185.9297
2041-03-28 07:01 | -3638.23 | 6.108 | 56.963 | 59.8258 | -1066.26
2041-03-29 08:01 | -2210.17 | 6.108 | 58.0293 | 59.8258 | -647.7369
2041-03-30 09:01 | -1394.61 | 4.0511 | 58.2765 | 59.8258 | -408.7198
2041-03-31 10:01 | 0 | 1 | 60.03 | 59.8258 | 0
2041-04-01 11:01 | 3036.33 | 1 | 60.0319 | 59.8258 | 889.8605
2041-04-02 12:01 | 3379.6 | 1.1193 | 74.7176 | 59.8258 | 990.463
2041-04-03 13:01 | 4236.24 | 1.3999 | 75.0866 | 59.8258 | 1241.5194
2041-04-04 14:01 | 4253.26 | 1.4172 | 75.319 | 59.8258 | 1246.5075
2041-04-05 15:01 | 3966.66 | 1.3298 | 75.4922 | 59.8258 | 1162.5133
2041-04-06 16:01 | 3617.05 | 1.2194 | 75.5712 | 59.8258 | 1060.0527
2041-04-07 17:01 | 2940.34 | 1 | 61.8096 | 59.8258 | 861.7286
2041-04-08 18:01 | 2896.92 | 1 | 61.8183 | 59.8258 | 849.0034
2041-04-09 19:01 | -382.557 | 1.6228 | 61.0335 | 59.8258 | -112.1164
2041-04-10 20:01 | -1058.43 | 3.4121 | 60.3087 | 59.8258 | -310.1952
2041-04-11 21:01 | -2406 | 6.108 | 59.6481 | 59.8258 | -705.129
2041-04-12 22:01 | -3071.92 | 6.108 | 58.8331 | 59.8258 | -900.2909
2041-04-13 23:01 | -4095.01 | 6.108 | 57.7519 | 59.8258 | -1200.129
2041-04-15 00:01 | -4482.9 | 6.108 | 57.0936 | 59.8258 | -1313.8083
2041-04-16 01:01 | -4915.33 | 6.108 | 56.4987 | 59.8258 | -1440.541
2041-04-17 02:01 | -5193.59 | 6.108 | 56.0347 | 59.8258 | -1522.091
2041-04-18 03:01 | -5444.13 | 6.108 | 55.6271 | 59.8258 | -1595.517
2041-04-19 04:01 | -5149.94 | 6.108 | 55.6436 | 59.8258 | -1509.2984
2041-04-20 05:01 | -4808.82 | 6.108 | 55.7917 | 59.8258 | -1409.326
2041-04-21 06:01 | -4146.22 | 6.108 | 56.2268 | 59.8258 | -1215.1371
2041-04-22 07:01 | -4023.22 | 6.108 | 56.3596 | 59.8258 | -1179.0894
2041-04-23 08:01 | -3500.55 | 6.108 | 56.7573 | 59.8258 | -1025.9099
2041-04-24 09:01 | -3861.44 | 6.108 | 56.5482 | 59.8258 | -1131.6764
2041-04-25 10:01 | -3201.06 | 6.108 | 57.0061 | 59.8258 | -938.1381
2041-04-26 11:01 | -1875.58 | 5.542 | 57.8911 | 59.8258 | -549.6782
2041-04-27 12:01 | 0 | 0 | 59.6158 | 59.8258 | 0
2041-04-28 13:01 | 2862.28 | 1 | 59.6944 | 59.8258 | 838.8515
2041-04-29 14:01 | 3079.34 | 1 | 60.2369 | 59.8258 | 902.4655
2041-04-30 15:01 | -137.315 | 0.96254 | 60.224 | 59.8258 | -40.2431
2041-05-01 16:01 | 880.835 | 1 | 60.6007 | 59.8258 | 258.1473
2041-05-02 17:01 | 264.895 | 1 | 60.7401 | 59.8258 | 77.6331
2041-05-03 18:01 | -73.8096 | 0.76855 | 60.3321 | 59.8258 | -21.6315
2041-05-04 19:01 | -654.037 | 2.3702 | 59.4343 | 59.8258 | -191.6793
2041-05-05 20:01 | -1053.9 | 3.3829 | 59.1556 | 59.8258 | -308.8676
2041-05-06 21:01 | -2018.45 | 6.08 | 59.0289 | 59.8258 | -591.5493
2041-05-07 22:01 | -2449.83 | 6.108 | 58.5638 | 59.8258 | -717.9743
2041-05-08 23:01 | -3385.9 | 6.108 | 57.7324 | 59.8258 | -992.3093
2041-05-10 00:01 | -3639.47 | 6.108 | 57.3324 | 59.8258 | -1066.6234
2041-05-11 01:01 | -3848.9 | 6.108 | 56.9841 | 59.8258 | -1128.0012
2041-05-12 02:01 | -4071.36 | 6.108 | 56.6531 | 59.8258 | -1193.1978
2041-05-13 03:01 | -4176.23 | 6.108 | 56.4608 | 59.8258 | -1223.9322
2041-05-14 04:01 | -4115.01 | 6.108 | 56.395 | 59.8258 | -1205.9904
2041-05-15 05:01 | -4020.12 | 6.108 | 56.4028 | 59.8258 | -1178.1809
2041-05-16 06:01 | -3608.56 | 6.108 | 56.6651 | 59.8258 | -1057.5645
2041-05-17 07:01 | -3215.55 | 6.108 | 56.9707 | 59.8258 | -942.3847
2041-05-18 08:01 | -2802.47 | 6.108 | 57.3172 | 59.8258 | -821.3229
2041-05-19 09:01 | -2242.48 | 6.108 | 57.8038 | 59.8258 | -657.206
2041-05-20 10:01 | -2037.76 | 5.959 | 58.0176 | 59.8258 | -597.2085
2041-05-21 11:01 | -1401.71 | 4.0926 | 58.0805 | 59.8258 | -410.8006
2041-05-22 12:01 | -895.179 | 2.7943 | 58.2827 | 59.8258 | -262.3511
2041-05-23 13:01 | -670.71 | 2.2653 | 58.495 | 59.8258 | -196.5657
2041-05-24 14:01 | -762.955 | 2.5788 | 58.5686 | 59.8258 | -223.6
2041-05-25 15:01 | -929.488 | 3.0298 | 58.5546 | 59.8258 | -272.406
2041-05-26 16:01 | -223.628 | 0.95447 | 58.8852 | 59.8258 | -65.5389
2041-05-27 17:01 | 405.704 | 1 | 60.0296 | 59.8258 | 118.9001
2041-05-28 18:01 | 2210.91 | 1 | 60.0138 | 59.8258 | 647.9538
2041-05-29 19:01 | 174.107 | 1 | 60.5289 | 59.8258 | 51.0257
2041-05-30 20:01 | -79.2097 | 0.78045 | 60.0174 | 59.8258 | -23.2141
2041-05-31 21:01 | -753.933 | 2.6603 | 59.1539 | 59.8258 | -220.956
2041-06-01 22:01 | -1058.29 | 3.3767 | 58.9673 | 59.8258 | -310.1542
2041-06-02 23:01 | -1832.46 | 5.5543 | 58.8402 | 59.8258 | -537.041
2041-06-04 00:01 | -2355.24 | 6.108 | 58.4234 | 59.8258 | -690.2527
2041-06-05 01:01 | -2456.92 | 6.108 | 58.2142 | 59.8258 | -720.0522
2041-06-06 02:01 | -2580.96 | 6.108 | 58.0401 | 59.8258 | -756.4047
2041-06-07 03:01 | -2602.79 | 6.108 | 57.9686 | 59.8258 | -762.8025
2041-06-08 04:01 | -2604.58 | 6.108 | 57.9173 | 59.8258 | -763.327
2041-06-09 05:01 | -2599.16 | 6.108 | 57.8851 | 59.8258 | -761.7386
2041-06-10 06:01 | -2556.87 | 6.108 | 57.8686 | 59.8258 | -749.3446
2041-06-11 07:01 | -1847.51 | 5.401 | 58.1962 | 59.8258 | -541.4517
2041-06-12 08:01 | -1348.02 | 3.9806 | 58.2826 | 59.8258 | -395.0657
2041-06-13 09:01 | -1758.17 | 5.3092 | 58.4226 | 59.8258 | -515.2688
2041-06-14 10:01 | -1559.93 | 4.6027 | 58.3775 | 59.8258 | -457.1704
2041-06-15 11:01 | -988.184 | 3.0075 | 58.4467 | 59.8258 | -289.6081
2041-06-16 12:01 | -557.277 | 1.9132 | 58.717 | 59.8258 | -163.3218
2041-06-17 13:01 | -448.778 | 1.7022 | 58.9384 | 59.8258 | -131.5238
2041-06-18 14:01 | -608.303 | 2.1768 | 58.9214 | 59.8258 | -178.276
2041-06-19 15:01 | -737.448 | 2.504 | 58.88 | 59.8258 | -216.1247
2041-06-20 16:01 | -924.834 | 3.013 | 58.826 | 59.8258 | -271.0421
2041-06-21 17:01 | 0 | 1 | 60.2086 | 59.8258 | 0
2041-06-22 18:01 | -502.266 | 1.9725 | 59.1407 | 59.8258 | -147.1996
2041-06-23 19:01 | -948.329 | 3.1267 | 58.9117 | 59.8258 | -277.9278
2041-06-24 20:01 | -1398.92 | 4.3255 | 58.7531 | 59.8258 | -409.983
2041-06-25 21:01 | -1657.26 | 4.967 | 58.6369 | 59.8258 | -485.695
2041-06-26 22:01 | -1838.66 | 5.4382 | 58.5597 | 59.8258 | -538.8581
2041-06-27 23:01 | -1952.49 | 5.7306 | 58.4781 | 59.8258 | -572.2183
2041-06-29 00:01 | -3354 | 6.108 | 57.4712 | 59.8258 | -982.9604
2041-06-30 01:01 | -3749.8 | 6.108 | 56.9505 | 59.8258 | -1098.9579
2041-07-01 02:01 | -3931.55 | 6.108 | 56.6337 | 59.8258 | -1152.2236
2041-07-02 03:01 | -4144.64 | 6.108 | 56.3475 | 59.8258 | -1214.6741
2041-07-03 04:01 | -4254.32 | 6.108 | 56.1401 | 59.8258 | -1246.8181
2041-07-04 05:01 | -4339.36 | 6.108 | 55.9464 | 59.8258 | -1271.7409
2041-07-05 06:01 | -4400.87 | 6.108 | 55.8084 | 59.8258 | -1289.7677
2041-07-06 07:01 | -3639.32 | 6.108 | 56.2943 | 59.8258 | -1066.5794
2041-07-07 08:01 | -3080.61 | 6.108 | 56.7411 | 59.8258 | -902.8377
2041-07-08 09:01 | -3608.14 | 6.108 | 56.4153 | 59.8258 | -1057.4415
2041-07-09 10:01 | -3355.55 | 6.108 | 56.5409 | 59.8258 | -983.4146
2041-07-10 11:01 | -2987.85 | 6.108 | 56.789 | 59.8258 | -875.6524
2041-07-11 12:01 | -2644.62 | 6.108 | 57.0845 | 59.8258 | -775.0616
2041-07-12 13:01 | -2600.93 | 6.108 | 57.1575 | 59.8258 | -762.2573
2041-07-13 14:01 | -2684.57 | 6.108 | 57.0997 | 59.8258 | -786.7698
2041-07-14 15:01 | -2910.19 | 6.108 | 56.9253 | 59.8258 | -852.8925
2041-07-15 16:01 | -2990.07 | 6.108 | 56.8274 | 59.8258 | -876.303
2041-07-16 17:01 | -1813.09 | 5.3748 | 57.4759 | 59.8258 | -531.3642
2041-07-17 18:01 | -2302.24 | 6.108 | 57.4177 | 59.8258 | -674.7199
2041-07-18 19:01 | -2762.11 | 6.108 | 57.0682 | 59.8258 | -809.4945
2041-07-19 20:01 | -3214.73 | 6.108 | 56.6491 | 59.8258 | -942.1444
2041-07-20 21:01 | -3478.2 | 6.108 | 56.3707 | 59.8258 | -1019.3598
2041-07-21 22:01 | -3634.3 | 6.108 | 56.1814 | 59.8258 | -1065.1082
2041-07-22 23:01 | -3671.57 | 6.108 | 56.0647 | 59.8258 | -1076.0309
2041-07-24 00:01 | -5031.06 | 6.108 | 54.9897 | 59.8258 | -1474.4581
2041-07-25 01:01 | -5246.22 | 6.108 | 54.6048 | 59.8258 | -1537.5153
2041-07-26 02:01 | -5436.19 | 6.108 | 54.3025 | 59.8258 | -1593.19
2041-07-27 03:01 | -5505.76 | 6.108 | 54.1338 | 59.8258 | -1613.579
2041-07-28 04:01 | -5527.5 | 6.108 | 54.0147 | 59.8258 | -1619.9503
2041-07-29 05:01 | -5565.36 | 6.108 | 53.8785 | 59.8258 | -1631.046
2041-07-30 06:01 | -5538.6 | 6.108 | 53.825 | 59.8258 | -1623.2034
2041-07-31 07:01 | -4600.82 | 6.108 | 54.4629 | 59.8258 | -1348.3672
2041-08-01 08:01 | -3943.11 | 6.108 | 55.0229 | 59.8258 | -1155.6115
2041-08-02 09:01 | -4305.8 | 6.108 | 54.8621 | 59.8258 | -1261.9054
2041-08-03 10:01 | -3912.26 | 6.108 | 55.1451 | 59.8258 | -1146.5702
2041-08-04 11:01 | -3157.85 | 6.108 | 55.7438 | 59.8258 | -925.4745
2041-08-05 12:01 | -2656.86 | 6.108 | 56.2542 | 59.8258 | -778.6488
2041-08-06 13:01 | -2340.85 | 6.108 | 56.614 | 59.8258 | -686.0354
2041-08-07 14:01 | -2183.83 | 6.108 | 56.8309 | 59.8258 | -640.0174
2041-08-08 15:01 | -2053.71 | 6.0853 | 57.023 | 59.8258 | -601.883
2041-08-09 16:01 | -2042.49 | 6.0394 | 57.1079 | 59.8258 | -598.5947
2041-08-10 17:01 | -858.308 | 2.5308 | 57.1507 | 59.8258 | -251.5452
2041-08-11 18:01 | -1131.54 | 3.6671 | 57.498 | 59.8258 | -331.6216
2041-08-12 19:01 | -1424.08 | 4.4169 | 57.524 | 59.8258 | -417.3566
2041-08-13 20:01 | -1628.67 | 4.9477 | 57.5114 | 59.8258 | -477.3161
2041-08-14 21:01 | -1745.66 | 5.2406 | 57.5151 | 59.8258 | -511.6024
2041-08-15 22:01 | -1887.3 | 5.6297 | 57.5313 | 59.8258 | -553.113
2041-08-16 23:01 | -2051.31 | 6.0794 | 57.5088 | 59.8258 | -601.1796
2041-08-18 00:01 | -3223.16 | 6.108 | 56.6294 | 59.8258 | -944.6149
2041-08-19 01:01 | -3510.01 | 6.108 | 56.2639 | 59.8258 | -1028.6824
2041-08-20 02:01 | -3744.63 | 6.108 | 55.9761 | 59.8258 | -1097.4427
2041-08-21 03:01 | -3807.7 | 6.108 | 55.8438 | 59.8258 | -1115.9267
2041-08-22 04:01 | -3633.98 | 6.108 | 55.907 | 59.8258 | -1065.0144
2041-08-23 05:01 | -3483.41 | 6.108 | 55.9788 | 59.8258 | -1020.8867
2041-08-24 06:01 | -3000.22 | 6.108 | 56.3417 | 59.8258 | -879.2777
2041-08-25 07:01 | -2915.4 | 6.108 | 56.4589 | 59.8258 | -854.4194
2041-08-26 08:01 | -2740.79 | 6.108 | 56.6227 | 59.8258 | -803.2463
2041-08-27 09:01 | -2908.64 | 6.108 | 56.5368 | 59.8258 | -852.4382
2041-08-28 10:01 | -2377.41 | 6.108 | 56.9305 | 59.8258 | -696.7501
2041-08-29 11:01 | -1852.07 | 5.4771 | 57.2249 | 59.8258 | -542.7881
2041-08-30 12:01 | -1406.61 | 4.1952 | 57.3413 | 59.8258 | -412.2367
2041-08-31 13:01 | 0 | 0 | 58.9925 | 59.8258 | 0
2041-09-01 14:01 | 2797.92 | 1 | 59.0084 | 59.8258 | 819.9894
2041-09-02 15:01 | 3102.31 | 1 | 59.5355 | 59.8258 | 909.1973
2041-09-03 16:01 | 3040.46 | 1 | 59.9152 | 59.8258 | 891.0709
2041-09-04 17:01 | 0 | 0 | 60.4128 | 59.8258 | 0
2041-09-05 18:01 | -622.55 | 2.0152 | 58.7873 | 59.8258 | -182.4514
2041-09-06 19:01 | -1290 | 4.119 | 58.6258 | 59.8258 | -378.0617
2041-09-07 20:01 | -1814.72 | 5.4644 | 58.3848 | 59.8258 | -531.8419
2041-09-08 21:01 | -3082.54 | 6.108 | 57.4271 | 59.8258 | -903.4033
2041-09-09 22:01 | -3662.58 | 6.108 | 56.6994 | 59.8258 | -1073.3962
2041-09-10 23:01 | -4715.17 | 6.108 | 55.6959 | 59.8258 | -1381.8799
2041-09-12 00:01 | -5174.52 | 6.108 | 55.0897 | 59.8258 | -1516.5021
2041-09-13 01:01 | -5462.16 | 6.108 | 54.6315 | 59.8258 | -1600.8011
2041-09-14 02:01 | -5700.85 | 6.108 | 54.2156 | 59.8258 | -1670.7542
2041-09-15 03:01 | -5811.55 | 6.108 | 53.9213 | 59.8258 | -1703.1972
2041-09-16 04:01 | -6039.9 | 6.108 | 53.5602 | 59.8258 | -1770.12
2041-09-17 05:01 | -6118.6 | 6.108 | 53.3523 | 59.8258 | -1793.1846
2041-09-18 06:01 | -6074.52 | 6.108 | 53.2569 | 59.8258 | -1780.2661
2041-09-19 07:01 | -5560.2 | 6.108 | 53.5414 | 59.8258 | -1629.5338
2041-09-20 08:01 | -4186.87 | 6.108 | 54.5476 | 59.8258 | -1227.0505
2041-09-21 09:01 | -3085.17 | 6.108 | 55.5262 | 59.8258 | -904.1741
2041-09-22 10:01 | -1655.35 | 4.9725 | 56.526 | 59.8258 | -485.1352
2041-09-23 11:01 | -642.641 | 2.0105 | 56.888 | 59.8258 | -188.3395
2041-09-24 12:01 | 937.873 | 1 | 58.5965 | 59.8258 | 274.8634
2041-09-25 13:01 | 2927.6 | 1 | 58.8353 | 59.8258 | 857.9949
2041-09-26 14:01 | 2915.11 | 1 | 59.3538 | 59.8258 | 854.3344
2041-09-27 15:01 | 2897.73 | 1 | 59.6758 | 59.8258 | 849.2408
2041-09-28 16:01 | 2883.97 | 1 | 59.897 | 59.8258 | 845.2082
2041-09-29 17:01 | -422.095 | 1.7654 | 59.2666 | 59.8258 | -123.7038
2041-09-30 18:01 | -903.531 | 3.0236 | 58.7224 | 59.8258 | -264.7988
2041-10-01 19:01 | -1689.28 | 5.2008 | 58.4151 | 59.8258 | -495.0791
2041-10-02 20:01 | -2407.01 | 6.108 | 57.9321 | 59.8258 | -705.425
2041-10-03 21:01 | -3717.38 | 6.108 | 56.7434 | 59.8258 | -1089.4565
2041-10-04 22:01 | -4364.59 | 6.108 | 55.9271 | 59.8258 | -1279.1351
2041-10-05 23:01 | -5533.85 | 6.108 | 54.8026 | 59.8258 | -1621.8113
2041-10-07 00:01 | -6051.16 | 6.108 | 54.0887 | 59.8258 | -1773.4199
2041-10-08 01:01 | -6284.03 | 6.108 | 53.6053 | 59.8258 | -1841.6674
2041-10-09 02:01 | -6449.24 | 6.108 | 53.2299 | 59.8258 | -1890.0857
2041-10-10 03:01 | -6510.3 | 6.108 | 52.9724 | 59.8258 | -1907.9806
2041-10-11 04:01 | -6505.02 | 6.108 | 52.79 | 59.8258 | -1906.4332
2041-10-12 05:01 | -6391.66 | 6.108 | 52.7629 | 59.8258 | -1873.2106
2041-10-13 06:01 | -6086.13 | 6.108 | 52.9127 | 59.8258 | -1783.6686
2041-10-14 07:01 | -5585.74 | 6.108 | 53.2532 | 59.8258 | -1637.0188
2041-10-15 08:01 | -4503.44 | 6.108 | 54.0792 | 59.8258 | -1319.828
2041-10-16 09:01 | -3528.38 | 6.108 | 54.9445 | 59.8258 | -1034.0661
2041-10-17 10:01 | -1994.51 | 6.0529 | 56.2635 | 59.8258 | -584.5332
2041-10-18 11:01 | -1042.76 | 3.0965 | 56.5268 | 59.8258 | -305.6028
2041-10-19 12:01 | 61.6458 | 1 | 58.3632 | 59.8258 | 18.0666
2041-10-20 13:01 | 2865.58 | 1 | 58.432 | 59.8258 | 839.8186
2041-10-21 14:01 | 2888.49 | 1 | 59.0044 | 59.8258 | 846.5329
2041-10-22 15:01 | -248.677 | 1.2976 | 58.7382 | 59.8258 | -72.88
2041-10-23 16:01 | -273.278 | 1.2668 | 58.4231 | 59.8258 | -80.0899
2041-10-24 17:01 | -579.996 | 2.1539 | 58.1519 | 59.8258 | -169.98
2041-10-25 18:01 | -808.544 | 2.7381 | 58.0517 | 59.8258 | -236.9609
2041-10-26 19:01 | -1405.71 | 4.4307 | 57.8988 | 59.8258 | -411.9729
2041-10-27 20:01 | -1780.68 | 5.3814 | 57.7203 | 59.8258 | -521.8658
2041-10-28 21:01 | -2874.67 | 6.108 | 57.0291 | 59.8258 | -842.4826
2041-10-29 22:01 | -3330.88 | 6.108 | 56.5149 | 59.8258 | -976.1846
2041-10-30 23:01 | -4196.94 | 6.108 | 55.7137 | 59.8258 | -1230.0017
2041-11-01 00:01 | -4525.27 | 6.108 | 55.259 | 59.8258 | -1326.2257
2041-11-02 01:01 | -4697.38 | 6.108 | 54.9264 | 59.8258 | -1376.6662
2041-11-03 02:01 | -4957.4 | 6.108 | 54.5636 | 59.8258 | -1452.8705
2041-11-04 03:01 | -5025.85 | 6.108 | 54.3914 | 59.8258 | -1472.9312
2041-11-05 04:01 | -4894.43 | 6.108 | 54.3916 | 59.8258 | -1434.4158
2041-11-06 05:01 | -4870.92 | 6.108 | 54.3644 | 59.8258 | -1427.5257
2041-11-07 06:01 | -4424.01 | 6.108 | 54.66 | 59.8258 | -1296.5493
2041-11-08 07:01 | -4031.7 | 6.108 | 54.9752 | 59.8258 | -1181.5746
2041-11-09 08:01 | -3012.08 | 6.108 | 55.7864 | 59.8258 | -882.7535
2041-11-10 09:01 | -1948.89 | 5.848 | 56.6726 | 59.8258 | -571.1633
2041-11-11 10:01 | -652.357 | 1.9512 | 56.8783 | 59.8258 | -191.187
2041-11-12 11:01 | 2799.03 | 1 | 58.463 | 59.8258 | 820.3147
2041-11-13 12:01 | 3056.48 | 1 | 75.3174 | 59.8258 | 895.7659
2041-11-14 13:01 | 3829.7 | 1.2162 | 74.1416 | 59.8258 | 1122.3743
2041-11-15 14:01 | 3670.5 | 1.1823 | 74.2954 | 59.8258 | 1075.7174
2041-11-16 15:01 | 3734.17 | 1.2025 | 74.5741 | 59.8258 | 1094.3772
2041-11-17 16:01 | 3236.89 | 1.0487 | 74.7242 | 59.8258 | 948.6388
2041-11-18 17:01 | 3040.71 | 1 | 60.4365 | 59.8258 | 891.1441
2041-11-19 18:01 | 2965.67 | 1 | 60.5417 | 59.8258 | 869.1521
2041-11-20 19:01 | -237.262 | 1.2343 | 60.017 | 59.8258 | -69.5346
2041-11-21 20:01 | -1028.92 | 3.4066 | 59.1802 | 59.8258 | -301.5467
2041-11-22 21:01 | -2438.64 | 6.108 | 58.478 | 59.8258 | -714.6948
2041-11-23 22:01 | -2989.21 | 6.108 | 57.7684 | 59.8258 | -876.051
2041-11-24 23:01 | -4022.29 | 6.108 | 56.7042 | 59.8258 | -1178.8168
2041-11-26 00:01 | -4539.45 | 6.108 | 55.9677 | 59.8258 | -1330.3815
2041-11-27 01:01 | -4889.02 | 6.108 | 55.4304 | 59.8258 | -1432.8303
2041-11-28 02:01 | -5218.18 | 6.108 | 54.9478 | 59.8258 | -1529.2976
2041-11-29 03:01 | -5449.81 | 6.108 | 54.5629 | 59.8258 | -1597.1816
2041-11-30 04:01 | -5666.76 | 6.108 | 54.2051 | 59.8258 | -1660.7634
2041-12-01 05:01 | -5786.17 | 6.108 | 53.9403 | 59.8258 | -1695.759
2041-12-02 06:01 | -5921.8 | 6.108 | 53.6755 | 59.8258 | -1735.5083
2041-12-03 07:01 | -4808 | 6.108 | 54.3831 | 59.8258 | -1409.0857
2041-12-04 08:01 | -3098.25 | 6.108 | 55.7088 | 59.8258 | -908.0074
2041-12-05 09:01 | -2251.02 | 6.108 | 56.5749 | 59.8258 | -659.7088
2041-12-06 10:01 | -896.923 | 2.6501 | 56.9159 | 59.8258 | -262.8622
2041-12-07 11:01 | 2612.12 | 1 | 58.5155 | 59.8258 | 765.5368
2041-12-08 12:01 | 3118.16 | 1 | 77.0252 | 59.8258 | 913.8425
2041-12-09 13:01 | 3644.99 | 1.1667 | 74.1142 | 59.8258 | 1068.2411
2041-12-10 14:01 | 3785.1 | 1.2169 | 74.3826 | 59.8258 | 1109.3033
2041-12-11 15:01 | 3662.02 | 1.181 | 74.626 | 59.8258 | 1073.2321
2041-12-12 16:01 | 3090.18 | 1 | 80.4002 | 59.8258 | 905.6424
2041-12-13 17:01 | 3224.19 | 1.0324 | 75.0042 | 59.8258 | 944.9168
2041-12-14 18:01 | 3011.59 | 1 | 60.5852 | 59.8258 | 882.6099
2041-12-15 19:01 | 2822.93 | 1 | 60.7076 | 59.8258 | 827.3191
2041-12-16 20:01 | -298.565 | 1.4204 | 60.0588 | 59.8258 | -87.5008
2041-12-17 21:01 | -887.491 | 2.9841 | 59.3242 | 59.8258 | -260.0979
2041-12-18 22:01 | -1498.91 | 4.6159 | 58.972 | 59.8258 | -439.2872
2041-12-19 23:01 | -2001.67 | 5.9376 | 58.7131 | 59.8258 | -586.6316
2041-12-21 00:01 | -3977.44 | 6.108 | 57.0646 | 59.8258 | -1165.6726
2041-12-22 01:01 | -4520.45 | 6.108 | 56.2236 | 59.8258 | -1324.8131
2041-12-23 02:01 | -5044.19 | 6.108 | 55.5258 | 59.8258 | -1478.3062
2041-12-24 03:01 | -5368.32 | 6.108 | 55.0213 | 59.8258 | -1573.2993
2041-12-25 04:01 | -5632.72 | 6.108 | 54.5874 | 59.8258 | -1650.7873
2041-12-26 05:01 | -5743.25 | 6.108 | 54.2797 | 59.8258 | -1683.1804
2041-12-27 06:01 | -5931.2 | 6.108 | 53.9718 | 59.8258 | -1738.2631
2041-12-28 07:01 | -4615.67 | 6.108 | 54.7858 | 59.8258 | -1352.7193
2041-12-29 08:01 | -2737.24 | 6.108 | 56.2497 | 59.8258 | -802.2059
2041-12-30 09:01 | -2123.46 | 6.108 | 56.9594 | 59.8258 | -622.3247
2041-12-31 10:01 | -1064.11 | 3.1309 | 57.1698 | 59.8258 | -311.8599
2042-01-01 11:01 | 2397.4 | 1 | 58.7175 | 59.8258 | 702.6086
2042-01-02 12:01 | 3103.4 | 1 | 77.7062 | 59.8258 | 909.5168
2042-01-03 13:01 | 3407.31 | 1.0897 | 74.2714 | 59.8258 | 998.584
2042-01-04 14:01 | 3786.18 | 1.2124 | 74.5497 | 59.8258 | 1109.6198
2042-01-05 15:01 | 4130.66 | 1.341 | 74.6423 | 59.8258 | 1210.5769
2042-01-06 16:01 | 3249.7 | 1.0472 | 75.0389 | 59.8258 | 952.3931
2042-01-07 17:01 | 3712.64 | 1.2086 | 74.9546 | 59.8258 | 1088.0674
2042-01-08 18:01 | 2961.11 | 1 | 60.7973 | 59.8258 | 867.8157
2042-01-09 19:01 | 2748.96 | 1 | 60.8668 | 59.8258 | 805.6406
2042-01-10 20:01 | -535.477 | 2.0783 | 59.963 | 59.8258 | -156.9328
2042-01-11 21:01 | -1344.97 | 4.2366 | 59.3085 | 59.8258 | -394.1718
2042-01-12 22:01 | -1868.69 | 5.5699 | 58.9428 | 59.8258 | -547.659
2042-01-13 23:01 | -2349.96 | 6.108 | 58.479 | 59.8258 | -688.7053
2042-01-15 00:01 | -3831 | 6.108 | 57.1471 | 59.8258 | -1122.7553
2042-01-16 01:01 | -4330.85 | 6.108 | 56.3969 | 59.8258 | -1269.2468
2042-01-17 02:01 | -4710.86 | 6.108 | 55.8444 | 59.8258 | -1380.6168
2042-01-18 03:01 | -4878.45 | 6.108 | 55.4957 | 59.8258 | -1429.7326
2042-01-19 04:01 | -4882.01 | 6.108 | 55.3103 | 59.8258 | -1430.7759
2042-01-20 05:01 | -4849.15 | 6.108 | 55.1809 | 59.8258 | -1421.1456
2042-01-21 06:01 | -4519.19 | 6.108 | 55.3282 | 59.8258 | -1324.4438
2042-01-22 07:01 | -4149.42 | 6.108 | 55.5502 | 59.8258 | -1216.075
2042-01-23 08:01 | -2717.77 | 6.108 | 56.626 | 59.8258 | -796.4998
2042-01-24 09:01 | -1799.66 | 5.334 | 57.2896 | 59.8258 | -527.4283
2042-01-25 10:01 | 0 | 0 | 59.0295 | 59.8258 | 0
2042-01-26 11:01 | 2879.37 | 1 | 75.8282 | 59.8258 | 843.86
2042-01-27 12:01 | 5116.9 | 1.5867 | 74.6466 | 59.8258 | 1499.6154
2042-01-28 13:01 | 6018.54 | 1.9477 | 74.6739 | 59.8258 | 1763.86
2042-01-29 14:01 | 6340.16 | 2.0467 | 75.2189 | 59.8258 | 1858.1175
2042-01-30 15:01 | 6087.6 | 1.9825 | 75.5056 | 59.8258 | 1784.0994
2042-01-31 16:01 | 5880.76 | 1.8738 | 76.108 | 59.8258 | 1723.4806
2042-02-01 17:01 | 4068.06 | 1.3079 | 76.185 | 59.8258 | 1192.2307
2042-02-02 18:01 | 3276.02 | 1.0603 | 76.018 | 59.8258 | 960.1067
2042-02-03 19:01 | 3057.77 | 1 | 61.5217 | 59.8258 | 896.1439
2042-02-04 20:01 | 2964.71 | 1 | 61.5235 | 59.8258 | 868.8707
2042-02-05 21:01 | -763.714 | 2.6901 | 60.5044 | 59.8258 | -223.8225
2042-02-06 22:01 | -1444.51 | 4.438 | 59.8262 | 59.8258 | -423.3441
2042-02-07 23:01 | -2741.68 | 6.108 | 58.9117 | 59.8258 | -803.5071
2042-02-09 00:01 | -3423.75 | 6.108 | 58.046 | 59.8258 | -1003.4021
2042-02-10 01:01 | -3640.27 | 6.108 | 57.5318 | 59.8258 | -1066.8578
2042-02-11 02:01 | -3665.06 | 6.108 | 57.218 | 59.8258 | -1074.1231
2042-02-12 03:01 | -3628.99 | 6.108 | 57.0723 | 59.8258 | -1063.552
2042-02-13 04:01 | -3410.26 | 6.108 | 57.0959 | 59.8258 | -999.4485
2042-02-14 05:01 | -3145.9 | 6.108 | 57.2328 | 59.8258 | -921.9723
2042-02-15 06:01 | -2552.35 | 6.108 | 57.6614 | 59.8258 | -748.0199
2042-02-16 07:01 | -2326.42 | 6.108 | 57.8733 | 59.8258 | -681.8064
2042-02-17 08:01 | -1228.16 | 3.5799 | 58.0582 | 59.8258 | -359.9382
2042-02-18 09:01 | -259.118 | 1.005 | 58.6115 | 59.8258 | -75.94
2042-02-19 10:01 | 2821.2 | 1 | 78.1701 | 59.8258 | 826.8121
2042-02-20 11:01 | 4605.52 | 1.4114 | 75.4294 | 59.8258 | 1349.7447
2042-02-21 12:01 | 6247.14 | 1.9777 | 75.4837 | 59.8258 | 1830.856
2042-02-22 13:01 | 6963.01 | 2.1768 | 76.2018 | 59.8258 | 2040.6568
2042-02-23 14:01 | 6890.87 | 2.1626 | 76.5982 | 59.8258 | 2019.5146
2042-02-24 15:01 | 6430.26 | 1.9979 | 77.0714 | 59.8258 | 1884.5232
2042-02-25 16:01 | 6435.31 | 2.012 | 77.1516 | 59.8258 | 1886.0032
2042-02-26 17:01 | 5146.22 | 1.5694 | 77.6943 | 59.8258 | 1508.2082
2042-02-27 18:01 | 4070.94 | 1.3095 | 76.8906 | 59.8258 | 1193.0747
2042-02-28 19:01 | 3148.57 | 1 | 79.3517 | 59.8258 | 922.7548
2042-03-01 20:01 | 3174.18 | 1 | 62.1494 | 59.8258 | 930.2603
2042-03-02 21:01 | 0 | 0 | 62.4244 | 59.8258 | 0
2042-03-03 22:01 | -439.108 | 1.6305 | 60.7411 | 59.8258 | -128.6899
2042-03-04 23:01 | -1307.29 | 4.117 | 60.2145 | 59.8258 | -383.1289
2042-03-06 00:01 | -1771.51 | 5.2373 | 59.8438 | 59.8258 | -519.1783
2042-03-07 01:01 | -2078.2 | 6.0324 | 59.5564 | 59.8258 | -609.0603
2042-03-08 02:01 | -2496.45 | 6.108 | 59.0196 | 59.8258 | -731.6373
2042-03-09 03:01 | -2721.3 | 6.108 | 58.6623 | 59.8258 | -797.5343
2042-03-10 04:01 | -2637.95 | 6.108 | 58.548 | 59.8258 | -773.1068
2042-03-11 05:01 | -2429.05 | 6.108 | 58.5993 | 59.8258 | -711.8843
2042-03-12 06:01 | -1974.98 | 5.724 | 58.7841 | 59.8258 | -578.8095
2042-03-13 07:01 | -1821 | 5.2949 | 58.7939 | 59.8258 | -533.6824
2042-03-14 08:01 | -1351.32 | 3.9744 | 58.7989 | 59.8258 | -396.0328
2042-03-15 09:01 | -914.697 | 2.8388 | 58.9391 | 59.8258 | -268.0712
2042-03-16 10:01 | -396.387 | 1.4599 | 59.2353 | 59.8258 | -116.1696
2042-03-17 11:01 | 2092.14 | 1 | 60.3722 | 59.8258 | 613.1457
2042-03-18 12:01 | 2979.17 | 1 | 60.6419 | 59.8258 | 873.1085
2042-03-19 13:01 | 4009.95 | 1.2681 | 75.7038 | 59.8258 | 1175.2003
2042-03-20 14:01 | 4139.62 | 1.3187 | 75.8515 | 59.8258 | 1213.2029
2042-03-21 15:01 | 4046.06 | 1.2901 | 76.0593 | 59.8258 | 1185.7831
2042-03-22 16:01 | 4338.25 | 1.3734 | 76.3165 | 59.8258 | 1271.4156
2042-03-23 17:01 | 3701.15 | 1.1761 | 76.4169 | 59.8258 | 1084.7
2042-03-24 18:01 | 3219.85 | 1.0411 | 76.2075 | 59.8258 | 943.6449
2042-03-25 19:01 | 3076.03 | 1 | 86.7375 | 59.8258 | 901.4954
2042-03-26 20:01 | 3080.93 | 1 | 61.7726 | 59.8258 | 902.9315
2042-03-27 21:01 | -487.809 | 1.908 | 60.9453 | 59.8258 | -142.9627
2042-03-28 22:01 | -1017.12 | 3.2737 | 60.2641 | 59.8258 | -298.0884
2042-03-29 23:01 | -2055.07 | 6.108 | 59.8474 | 59.8258 | -602.2816
2042-03-31 00:01 | -2911.77 | 6.108 | 58.9233 | 59.8258 | -853.3555
2042-04-01 01:01 | -3216.89 | 6.108 | 58.3664 | 59.8258 | -942.7774
2042-04-02 02:01 | -3394.28 | 6.108 | 57.9497 | 59.8258 | -994.7653
2042-04-03 03:01 | -3571 | 6.108 | 57.6405 | 59.8258 | -1046.5568
2042-04-04 04:01 | -3756.07 | 6.108 | 57.3297 | 59.8258 | -1100.7955
2042-04-05 05:01 | -3881.7 | 6.108 | 57.0833 | 59.8258 | -1137.614
2042-04-06 06:01 | -3970.95 | 6.108 | 56.8844 | 59.8258 | -1163.7706
2042-04-07 07:01 | -2951.33 | 6.108 | 57.5214 | 59.8258 | -864.9494
2042-04-08 08:01 | -1964.1 | 5.7681 | 58.1902 | 59.8258 | -575.6209
2042-04-09 09:01 | -2014.22 | 5.8898 | 58.3182 | 59.8258 | -590.3096
2042-04-10 10:01 | -662.311 | 1.9417 | 58.3473 | 59.8258 | -194.1042
2042-04-11 11:01 | 1127.65 | 1 | 59.9875 | 59.8258 | 330.4816
2042-04-12 12:01 | 2994.65 | 1 | 60.1656 | 59.8258 | 877.6453
2042-04-13 13:01 | 3146 | 1 | 80.5676 | 59.8258 | 922.0016
2042-04-14 14:01 | 3773.02 | 1.1959 | 75.512 | 59.8258 | 1105.763
2042-04-15 15:01 | 3058.37 | 1 | 78.2257 | 59.8258 | 896.3198
2042-04-16 16:01 | 3090.32 | 1 | 83.8906 | 59.8258 | 905.6834
2042-04-17 17:01 | 3889.98 | 1.2301 | 76.0019 | 59.8258 | 1140.0406
2042-04-18 18:01 | 3040.05 | 1 | 79.6475 | 59.8258 | 890.9507
2042-04-19 19:01 | 3134.73 | 1 | 61.4951 | 59.8258 | 918.6987
2042-04-20 20:01 | 3071.49 | 1 | 61.5435 | 59.8258 | 900.1649
2042-04-21 21:01 | 3156.27 | 1 | 61.634 | 59.8258 | 925.0114
2042-04-22 22:01 | 3111.24 | 1 | 61.7381 | 59.8258 | 911.8144
2042-04-23 23:01 | 3168.55 | 1 | 61.7961 | 59.8258 | 928.6103
2042-04-25 00:01 | -490.757 | 1.9244 | 60.9868 | 59.8258 | -143.8267
2042-04-26 01:01 | -692.184 | 2.3548 | 60.3833 | 59.8258 | -202.8591
2042-04-27 02:01 | -797.898 | 2.6214 | 60.0862 | 59.8258 | -233.8408
2042-04-28 03:01 | -775.935 | 2.5387 | 59.9619 | 59.8258 | -227.4041
2042-04-29 04:01 | -710.361 | 2.3634 | 59.884 | 59.8258 | -208.1863
2042-04-30 05:01 | -626.804 | 2.1453 | 59.8222 | 59.8258 | -183.6981
2042-05-01 06:01 | -349.238 | 1.3802 | 59.9994 | 59.8258 | -102.3516
2042-05-02 07:01 | -112.994 | 0.78467 | 60.525 | 59.8258 | -33.1153
2042-05-03 08:01 | 2446.92 | 1 | 61.0012 | 59.8258 | 717.1215
2042-05-04 09:01 | 3058.87 | 1 | 61.3 | 59.8258 | 896.4663
2042-05-05 10:01 | 3345.91 | 1.0657 | 76.2336 | 59.8258 | 980.5894
2042-05-06 11:01 | 3857.68 | 1.2599 | 75.9902 | 59.8258 | 1130.5744
2042-05-07 12:01 | 4704.42 | 1.5794 | 75.8152 | 59.8258 | 1378.7294
2042-05-08 13:01 | 5050.56 | 1.5916 | 76.9794 | 59.8258 | 1480.173
2042-05-09 14:01 | 3685.85 | 1.1597 | 77.2016 | 59.8258 | 1080.216
2042-05-10 15:01 | 3132.02 | 1.0195 | 76.6707 | 59.8258 | 917.9045
2042-05-11 16:01 | 4746.13 | 1.4673 | 77.3416 | 59.8258 | 1390.9534
2042-05-12 17:01 | 4885.96 | 1.5227 | 77.4431 | 59.8258 | 1431.9335
2042-05-13 18:01 | 4920.05 | 1.5932 | 77.0453 | 59.8258 | 1441.9243
2042-05-14 19:01 | 4080.8 | 1.2362 | 78.1109 | 59.8258 | 1195.9644
2042-05-15 20:01 | 3322.75 | 1 | 79.649 | 59.8258 | 973.8019
2042-05-16 21:01 | 3199.32 | 1 | 62.6384 | 59.8258 | 937.6281
2042-05-17 22:01 | 0 | 0 | 62.8842 | 59.8258 | 0
2042-05-18 23:01 | -603.184 | 2.1126 | 61.1198 | 59.8258 | -176.7758
2042-05-20 00:01 | -1031.08 | 3.2786 | 60.6507 | 59.8258 | -302.1797
2042-05-21 01:01 | -1410.13 | 4.2559 | 60.341 | 59.8258 | -413.2683
2042-05-22 02:01 | -1815.71 | 5.333 | 60.0943 | 59.8258 | -532.1321
2042-05-23 03:01 | -2254.8 | 6.108 | 59.7485 | 59.8258 | -660.8166
2042-05-24 04:01 | -2570.73 | 6.108 | 59.3262 | 59.8258 | -753.4066
2042-05-25 05:01 | -2823.19 | 6.108 | 58.9584 | 59.8258 | -827.3953
2042-05-26 06:01 | -3024.28 | 6.108 | 58.6341 | 59.8258 | -886.329
2042-05-27 07:01 | -2305.92 | 6.108 | 59.0086 | 59.8258 | -675.7984
2042-05-28 08:01 | -1956.63 | 5.6394 | 59.1012 | 59.8258 | -573.4316
2042-05-29 09:01 | -2509.96 | 6.108 | 58.7829 | 59.8258 | -735.5967
2042-05-30 10:01 | -2211.2 | 6.108 | 58.8907 | 59.8258 | -648.0387
2042-05-31 11:01 | -1832.92 | 5.2891 | 58.9034 | 59.8258 | -537.1758
2042-06-01 12:01 | -1312.1 | 3.8553 | 58.9224 | 59.8258 | -384.5386
2042-06-02 13:01 | -1083.81 | 3.3337 | 59.0065 | 59.8258 | -317.6334
2042-06-03 14:01 | -999.836 | 3.1412 | 59.0437 | 59.8258 | -293.023
2042-06-04 15:01 | -910.222 | 2.9014 | 59.0757 | 59.8258 | -266.7597
2042-06-05 16:01 | -955.275 | 3.0532 | 59.0782 | 59.8258 | -279.9635
2042-06-06 17:01 | 1638.91 | 1 | 60.3453 | 59.8258 | 480.3171
2042-06-07 18:01 | -89.8245 | 0.83566 | 60.3244 | 59.8258 | -26.325
2042-06-08 19:01 | -411.963 | 1.6795 | 59.6332 | 59.8258 | -120.7344
2042-06-09 20:01 | -737.087 | 2.5341 | 59.3299 | 59.8258 | -216.0189
2042-06-10 21:01 | -915.063 | 2.9682 | 59.1996 | 59.8258 | -268.1785
2042-06-11 22:01 | -1039.67 | 3.2866 | 59.1353 | 59.8258 | -304.6972
2042-06-12 23:01 | -1112.97 | 3.4711 | 59.0347 | 59.8258 | -326.1793
2042-06-14 00:01 | -2340.33 | 6.108 | 58.7227 | 59.8258 | -685.883
2042-06-15 01:01 | -2693.59 | 6.108 | 58.2766 | 59.8258 | -789.4133
2042-06-16 02:01 | -2930.88 | 6.108 | 57.9512 | 59.8258 | -858.9561
2042-06-17 03:01 | -3029.49 | 6.108 | 57.7655 | 59.8258 | -887.8559
2042-06-18 04:01 | -3028.12 | 6.108 | 57.6719 | 59.8258 | -887.4544
2042-06-19 05:01 | -2987.65 | 6.108 | 57.5945 | 59.8258 | -875.5938
2042-06-20 06:01 | -2915.55 | 6.108 | 57.5969 | 59.8258 | -854.4634
2042-06-21 07:01 | -2016.78 | 5.9229 | 58.1837 | 59.8258 | -591.0599
2042-06-22 08:01 | -1183.41 | 3.4511 | 58.2459 | 59.8258 | -346.8232
2042-06-23 09:01 | -825.132 | 2.6459 | 58.5286 | 59.8258 | -241.8223
2042-06-24 10:01 | -170.021 | 0.83657 | 59.1342 | 59.8258 | -49.8282
2042-06-25 11:01 | 2278.49 | 1 | 60.0059 | 59.8258 | 667.7595
2042-06-26 12:01 | 2934.65 | 1 | 81.7996 | 59.8258 | 860.061
2042-06-27 13:01 | 3205.91 | 1 | 60.6806 | 59.8258 | 939.5595
2042-06-28 14:01 | 3187.36 | 1 | 60.9319 | 59.8258 | 934.123
2042-06-29 15:01 | 3228.29 | 1 | 61.1212 | 59.8258 | 946.1184
2042-06-30 16:01 | 3239.58 | 1 | 61.2904 | 59.8258 | 949.4272
2042-07-01 17:01 | 3299.33 | 1 | 77.6036 | 59.8258 | 966.9382
2042-07-02 18:01 | 3193.31 | 1 | 86.4083 | 59.8258 | 935.8668
2042-07-03 19:01 | 3062.62 | 1 | 61.5659 | 59.8258 | 897.5653
2042-07-04 20:01 | 2969.28 | 1 | 61.6398 | 59.8258 | 870.2101
2042-07-05 21:01 | 2946.62 | 1 | 61.6972 | 59.8258 | 863.5691
2042-07-06 22:01 | 0 | 0 | 62.0251 | 59.8258 | 0
2042-07-07 23:01 | 0 | 1 | 61.6673 | 59.8258 | 0
2042-07-09 00:01 | -966.517 | 3.2245 | 60.1115 | 59.8258 | -283.2582
2042-07-10 01:01 | -1520.82 | 4.6104 | 59.7645 | 59.8258 | -445.7083
2042-07-11 02:01 | -1961.33 | 5.7609 | 59.4921 | 59.8258 | -574.8091
2042-07-12 03:01 | -2470.72 | 6.108 | 58.9812 | 59.8258 | -724.0966
2042-07-13 04:01 | -2595.36 | 6.108 | 58.7118 | 59.8258 | -760.6249
2042-07-14 05:01 | -2773.47 | 6.108 | 58.4296 | 59.8258 | -812.8238
2042-07-15 06:01 | -2507.9 | 6.108 | 58.503 | 59.8258 | -734.9929
2042-07-16 07:01 | -2436.19 | 6.108 | 58.4865 | 59.8258 | -713.9768
2042-07-17 08:01 | -2155.24 | 6.108 | 58.6296 | 59.8258 | -631.6385
2042-07-18 09:01 | -2033.62 | 5.892 | 58.6335 | 59.8258 | -595.9952
2042-07-19 10:01 | -1155.74 | 3.3577 | 58.6294 | 59.8258 | -338.714
2042-07-20 11:01 | 0 | 1 | 60.2892 | 59.8258 | 0
2042-07-21 12:01 | 2913.91 | 1 | 60.2137 | 59.8258 | 853.9827
2042-07-22 13:01 | 3000.34 | 1 | 60.6936 | 59.8258 | 879.3129
2042-07-23 14:01 | 3075.89 | 1 | 60.9779 | 59.8258 | 901.4544
2042-07-24 15:01 | 3057.39 | 1 | 61.1788 | 59.8258 | 896.0326
2042-07-25 16:01 | 3136.42 | 1 | 61.3432 | 59.8258 | 919.194
2042-07-26 17:01 | 2983.35 | 1 | 61.5041 | 59.8258 | 874.3336
2042-07-27 18:01 | 0 | 0 | 61.8304 | 59.8258 | 0
2042-07-28 19:01 | -426.856 | 1.7265 | 60.3545 | 59.8258 | -125.0991
2042-07-29 20:01 | -917.862 | 3.0245 | 59.8719 | 59.8258 | -268.9988
2042-07-30 21:01 | -1866.9 | 5.6326 | 59.582 | 59.8258 | -547.1344
2042-07-31 22:01 | -2446.15 | 6.108 | 59.0203 | 59.8258 | -716.8958
2042-08-01 23:01 | -3501.3 | 6.108 | 57.9664 | 59.8258 | -1026.1297
2042-08-03 00:01 | -3932.3 | 6.108 | 57.3506 | 59.8258 | -1152.4434
2042-08-04 01:01 | -4225.08 | 6.108 | 56.8735 | 59.8258 | -1238.2487
2042-08-05 02:01 | -4330.34 | 6.108 | 56.5716 | 59.8258 | -1269.0974
2042-08-06 03:01 | -4447.1 | 6.108 | 56.3034 | 59.8258 | -1303.3164
2042-08-07 04:01 | -4403.69 | 6.108 | 56.1681 | 59.8258 | -1290.5941
2042-08-08 05:01 | -4401.8 | 6.108 | 56.0445 | 59.8258 | -1290.0402
2042-08-09 06:01 | -4100.22 | 6.108 | 56.1888 | 59.8258 | -1201.6559
2042-08-10 07:01 | -3494.68 | 6.108 | 56.6081 | 59.8258 | -1024.1896
2042-08-11 08:01 | -2082.43 | 6.108 | 57.6965 | 59.8258 | -610.3
2042-08-12 09:01 | -1352.84 | 3.9454 | 57.874 | 59.8258 | -396.4783
2042-08-13 10:01 | -329.969 | 1.1759 | 58.3398 | 59.8258 | -96.7044
2042-08-14 11:01 | 2791.04 | 1 | 59.6111 | 59.8258 | 817.9731
2042-08-15 12:01 | 3071.88 | 1 | 75.3726 | 59.8258 | 900.2792
2042-08-16 13:01 | 3639.99 | 1.1324 | 75.46 | 59.8258 | 1066.7758
2042-08-17 14:01 | 3226.88 | 1 | 79.2644 | 59.8258 | 945.7052
2042-08-18 15:01 | 3214.03 | 1 | 78.7126 | 59.8258 | 941.9392
2042-08-19 16:01 | 3144.38 | 1 | 77.553 | 59.8258 | 921.5268
2042-08-20 17:01 | 3111.58 | 1 | 61.1818 | 59.8258 | 911.9141
2042-08-21 18:01 | 3002.13 | 1 | 61.2935 | 59.8258 | 879.8375
2042-08-22 19:01 | 0 | 0 | 61.6283 | 59.8258 | 0
2042-08-23 20:01 | -337.88 | 1.3853 | 60.1713 | 59.8258 | -99.0229
2042-08-24 21:01 | -1233.77 | 3.9558 | 59.6544 | 59.8258 | -361.5823
2042-08-25 22:01 | -1523.26 | 4.5709 | 59.3558 | 59.8258 | -446.4234
2042-08-26 23:01 | -2048.88 | 6.0467 | 59.127 | 59.8258 | -600.4675
2042-08-28 00:01 | -2001.08 | 5.7825 | 58.8696 | 59.8258 | -586.4587
2042-08-29 01:01 | -1987.32 | 5.7762 | 58.7673 | 59.8258 | -582.426
2042-08-30 02:01 | -2053.71 | 5.9767 | 58.6905 | 59.8258 | -601.883
2042-08-31 03:01 | -2031.19 | 5.8965 | 58.6192 | 59.8258 | -595.283
2042-09-01 04:01 | -2126.75 | 6.108 | 58.5495 | 59.8258 | -623.2889
2042-09-02 05:01 | -2321.69 | 6.108 | 58.3513 | 59.8258 | -680.4202
2042-09-03 06:01 | -2318.74 | 6.108 | 58.2766 | 59.8258 | -679.5556
2042-09-04 07:01 | -2528.07 | 6.108 | 58.0863 | 59.8258 | -740.9042
2042-09-05 08:01 | -2688.17 | 6.108 | 57.9059 | 59.8258 | -787.8249
2042-09-06 09:01 | -3117.16 | 6.108 | 57.5193 | 59.8258 | -913.5494
2042-09-07 10:01 | -2939.88 | 6.108 | 57.538 | 59.8258 | -861.5938
2042-09-08 11:01 | -2984.61 | 6.108 | 57.4321 | 59.8258 | -874.7028
2042-09-09 12:01 | -2732.75 | 6.108 | 57.534 | 59.8258 | -800.89
2042-09-10 13:01 | -2044.69 | 6.0125 | 57.9689 | 59.8258 | -599.2395
2042-09-11 14:01 | -1824.1 | 5.3313 | 57.9904 | 59.8258 | -534.5909
2042-09-12 15:01 | -601.992 | 1.829 | 58.0684 | 59.8258 | -176.4264
2042-09-13 16:01 | -312.94 | 1.3274 | 58.6482 | 59.8258 | -91.7137
2042-09-14 17:01 | -1113.94 | 3.6752 | 58.4576 | 59.8258 | -326.4636
2042-09-15 18:01 | -1667.55 | 5.083 | 58.2992 | 59.8258 | -488.7107
2042-09-16 19:01 | -2405.39 | 6.108 | 57.9205 | 59.8258 | -704.9502
2042-09-17 20:01 | -3023.8 | 6.108 | 57.3368 | 59.8258 | -886.1883
2042-09-18 21:01 | -4155.63 | 6.108 | 56.3324 | 59.8258 | -1217.8949
2042-09-19 22:01 | -4649.36 | 6.108 | 55.7057 | 59.8258 | -1362.5929
2042-09-20 23:01 | -5648.34 | 6.108 | 54.745 | 59.8258 | -1655.365
2042-09-22 00:01 | -6062.65 | 6.108 | 54.1648 | 59.8258 | -1776.7873
2042-09-23 01:01 | -6375.07 | 6.108 | 53.6893 | 59.8258 | -1868.3486
2042-09-24 02:01 | -6466.08 | 6.108 | 53.408 | 59.8258 | -1895.021
2042-09-25 03:01 | -6572.07 | 6.108 | 53.1479 | 59.8258 | -1926.0836
2042-09-26 04:01 | -6510.23 | 6.108 | 53.0233 | 59.8258 | -1907.9601
2042-09-27 05:01 | -6327.73 | 6.108 | 53.0398 | 59.8258 | -1854.4746
2042-09-28 06:01 | -5925.11 | 6.108 | 53.2611 | 59.8258 | -1736.4783
2042-09-29 07:01 | -6103.53 | 6.108 | 53.1029 | 59.8258 | -1788.7681
2042-09-30 08:01 | -5859.8 | 6.108 | 53.2112 | 59.8258 | -1717.3379
2042-10-01 09:01 | -5927.16 | 6.108 | 53.1313 | 59.8258 | -1737.0791
2042-10-02 10:01 | -4758.69 | 6.108 | 53.959 | 59.8258 | -1394.6344
2042-10-03 11:01 | -5056.89 | 6.108 | 53.8368 | 59.8258 | -1482.0282
2042-10-04 12:01 | -5498.71 | 6.108 | 53.4916 | 59.8258 | -1611.5128
2042-10-05 13:01 | -5370.24 | 6.108 | 53.4902 | 59.8258 | -1573.862
2042-10-06 14:01 | -4693.35 | 6.108 | 53.9478 | 59.8258 | -1375.4851
2042-10-07 15:01 | -4400.73 | 6.108 | 54.2142 | 59.8258 | -1289.7266
2042-10-08 16:01 | -4219.29 | 6.108 | 54.3649 | 59.8258 | -1236.5518
2042-10-09 17:01 | -4741.42 | 6.108 | 53.9836 | 59.8258 | -1389.573
2042-10-10 18:01 | -4947.33 | 6.108 | 53.757 | 59.8258 | -1449.9193
2042-10-11 19:01 | -5565.5 | 6.108 | 53.2296 | 59.8258 | -1631.087
2042-10-12 20:01 | -5912.79 | 6.108 | 52.8366 | 59.8258 | -1732.8677
2042-10-13 21:01 | -6876.4 | 6.108 | 51.9827 | 59.8258 | -2015.2739
2042-10-14 22:01 | -7154.11 | 6.108 | 51.5421 | 59.8258 | -2096.6627
2042-10-15 23:01 | -8153.94 | 6.108 | 50.6131 | 59.8258 | -2389.6839
2042-10-17 00:01 | -8397.49 | 6.108 | 50.1765 | 59.8258 | -2461.0614
2042-10-18 01:01 | -8689.55 | 6.108 | 49.7536 | 59.8258 | -2546.6557
2042-10-19 02:01 | -8971.97 | 6.108 | 49.3479 | 59.8258 | -2629.4248
2042-10-20 03:01 | -9164.01 | 6.108 | 49.0164 | 59.8258 | -2685.7062
2042-10-21 04:01 | -9272.86 | 6.108 | 48.752 | 59.8258 | -2717.607
2042-10-22 05:01 | -9181.01 | 6.108 | 48.6729 | 59.8258 | -2690.6884
2042-10-23 06:01 | -8979.98 | 6.108 | 48.7071 | 59.8258 | -2631.7723
2042-10-24 07:01 | -8684.26 | 6.108 | 48.8528 | 59.8258 | -2545.1054
2042-10-25 08:01 | -7708.94 | 6.108 | 49.5429 | 59.8258 | -2259.2673
2042-10-26 09:01 | -8041.41 | 6.108 | 49.3778 | 59.8258 | -2356.7046
2042-10-27 10:01 | -6616.6 | 6.108 | 50.4141 | 59.8258 | -1939.134
2042-10-28 11:01 | -4820.57 | 6.108 | 51.9189 | 59.8258 | -1412.7696
2042-10-29 12:01 | -3661.12 | 6.108 | 53.1152 | 59.8258 | -1072.9684
2042-10-30 13:01 | -2836.1 | 6.108 | 54.0593 | 59.8258 | -831.1789
2042-10-31 14:01 | -2448.55 | 6.108 | 54.6359 | 59.8258 | -717.5992
2042-11-01 15:01 | -2172.12 | 6.108 | 55.1002 | 59.8258 | -636.5855
2042-11-02 16:01 | -2060.57 | 6.108 | 55.395 | 59.8258 | -603.8935
2042-11-03 17:01 | -3211.32 | 6.108 | 54.695 | 59.8258 | -941.145
2042-11-04 18:01 | -3706.73 | 6.108 | 54.2907 | 59.8258 | -1086.3353
2042-11-05 19:01 | -4487.45 | 6.108 | 53.6515 | 59.8258 | -1315.1418
2042-11-06 20:01 | -4942.11 | 6.108 | 53.2022 | 59.8258 | -1448.3895
2042-11-07 21:01 | -5874.79 | 6.108 | 52.4021 | 59.8258 | -1721.731
2042-11-08 22:01 | -5982.81 | 6.108 | 52.1301 | 59.8258 | -1753.3885
2042-11-09 23:01 | -6646.06 | 6.108 | 51.5131 | 59.8258 | -1947.7679
2042-11-11 00:01 | -6923.12 | 6.108 | 51.1363 | 59.8258 | -2028.9662
2042-11-12 01:01 | -6807.77 | 6.108 | 51.0698 | 59.8258 | -1995.1604
2042-11-13 02:01 | -6587.72 | 6.108 | 51.1452 | 59.8258 | -1930.6701
2042-11-14 03:01 | -6217.71 | 6.108 | 51.3862 | 59.8258 | -1822.2309
2042-11-15 04:01 | -6014.14 | 6.108 | 51.5382 | 59.8258 | -1762.5704
2042-11-16 05:01 | -6542.53 | 6.108 | 51.167 | 59.8258 | -1917.4263
2042-11-17 06:01 | -6808.27 | 6.108 | 50.9039 | 59.8258 | -1995.307
2042-11-18 07:01 | -6112.14 | 6.108 | 51.3534 | 59.8258 | -1791.2914
2042-11-19 08:01 | -5012.14 | 6.108 | 52.2255 | 59.8258 | -1468.9132
2042-11-20 09:01 | -4452.54 | 6.108 | 52.8147 | 59.8258 | -1304.9107
2042-11-21 10:01 | -4719.6 | 6.108 | 52.7556 | 59.8258 | -1383.1782
2042-11-22 11:01 | -2626.86 | 6.108 | 54.3633 | 59.8258 | -769.8567
2042-11-23 12:01 | -1770.63 | 5.4005 | 55.1548 | 59.8258 | -518.9204
2042-11-24 13:01 | -1719.64 | 5.2607 | 55.4659 | 59.8258 | -503.9767
2042-11-25 14:01 | -809.013 | 2.5116 | 55.6464 | 59.8258 | -237.0983
2042-11-26 15:01 | -925.343 | 3.1243 | 56.0033 | 59.8258 | -271.1913
2042-11-27 16:01 | -1401.63 | 4.4875 | 56.0999 | 59.8258 | -410.7772
2042-11-28 17:01 | -1441.85 | 4.4722 | 56.0992 | 59.8258 | -422.5645
2042-11-29 18:01 | -2238.9 | 6.108 | 55.9581 | 59.8258 | -656.1568
2042-11-30 19:01 | -3341.17 | 6.108 | 55.1027 | 59.8258 | -979.2003
2042-12-01 20:01 | -3760.47 | 6.108 | 54.626 | 59.8258 | -1102.085
2042-12-02 21:01 | -4576.81 | 6.108 | 53.891 | 59.8258 | -1341.3306
2042-12-03 22:01 | -5060.37 | 6.108 | 53.3732 | 59.8258 | -1483.0481
2042-12-04 23:01 | -5434.65 | 6.108 | 52.9176 | 59.8258 | -1592.7387
2042-12-06 00:01 | -7140.53 | 6.108 | 51.4789 | 59.8258 | -2092.6828
2042-12-07 01:01 | -7189.05 | 6.108 | 51.1099 | 59.8258 | -2106.9026
2042-12-08 02:01 | -7560.09 | 6.108 | 50.6042 | 59.8258 | -2215.6437
2042-12-09 03:01 | -7753.64 | 6.108 | 50.2605 | 59.8258 | -2272.3676
2042-12-10 04:01 | -7775.14 | 6.108 | 50.0586 | 59.8258 | -2278.6686
2042-12-11 05:01 | -8454.34 | 6.108 | 49.3961 | 59.8258 | -2477.7225
2042-12-12 06:01 | -8602.19 | 6.108 | 49.0948 | 59.8258 | -2521.053
2042-12-13 07:01 | -7832.41 | 6.108 | 49.5116 | 59.8258 | -2295.4528
2042-12-14 08:01 | -6943.9 | 6.108 | 50.1606 | 59.8258 | -2035.0562
2042-12-15 09:01 | -7475.47 | 6.108 | 49.838 | 59.8258 | -2190.844
2042-12-16 10:01 | -6991 | 6.108 | 50.1282 | 59.8258 | -2048.8599
2042-12-17 11:01 | -6473.9 | 6.108 | 50.5117 | 59.8258 | -1897.3128
2042-12-18 12:01 | -3638.3 | 6.108 | 52.7103 | 59.8258 | -1066.2805
2042-12-19 13:01 | -1925.52 | 6.009 | 54.3635 | 59.8258 | -564.3142
2042-12-20 14:01 | -1196.88 | 3.6444 | 54.7477 | 59.8258 | -350.7709
2042-12-21 15:01 | -1396.64 | 4.4768 | 55.165 | 59.8258 | -409.3148
2042-12-22 16:01 | -2112.95 | 6.108 | 55.2159 | 59.8258 | -619.2445
2042-12-23 17:01 | -1978.73 | 5.9957 | 55.3793 | 59.8258 | -579.9085
2042-12-24 18:01 | -2464.5 | 6.108 | 55.1456 | 59.8258 | -722.2737
2042-12-25 19:01 | -3240.62 | 6.108 | 54.5801 | 59.8258 | -949.732
2042-12-26 20:01 | -3942.71 | 6.108 | 53.9647 | 59.8258 | -1155.4942
2042-12-27 21:01 | -4450.23 | 6.108 | 53.4799 | 59.8258 | -1304.2337
2042-12-28 22:01 | -4318.7 | 6.108 | 53.4862 | 59.8258 | -1265.686
2042-12-29 23:01 | -5150.26 | 6.108 | 52.8397 | 59.8258 | -1509.3922
2042-12-31 00:01 | -6472.03 | 6.108 | 51.7113 | 59.8258 | -1896.7648
2043-01-01 01:01 | -7355.26 | 6.108 | 50.7708 | 59.8258 | -2155.6139
2043-01-02 02:01 | -6844.27 | 6.108 | 50.8695 | 59.8258 | -2005.8575
2043-01-03 03:01 | -7349.17 | 6.108 | 50.388 | 59.8258 | -2153.8291
2043-01-04 04:01 | -7182.87 | 6.108 | 50.3455 | 59.8258 | -2105.0914
2043-01-05 05:01 | -7347.92 | 6.108 | 50.1119 | 59.8258 | -2153.4628
2043-01-06 06:01 | -6624.29 | 6.108 | 50.567 | 59.8258 | -1941.3878
2043-01-07 07:01 | -6645.33 | 6.108 | 50.589 | 59.8258 | -1947.554
2043-01-08 08:01 | -4575.75 | 6.108 | 52.1267 | 59.8258 | -1341.0199
2043-01-09 09:01 | -3156.43 | 6.108 | 53.4553 | 59.8258 | -925.0583
2043-01-10 10:01 | -1480.25 | 4.5622 | 54.6634 | 59.8258 | -433.8185
2043-01-11 11:01 | -494.027 | 1.6479 | 55.1812 | 59.8258 | -144.785
2043-01-12 12:01 | 2519.56 | 1 | 56.7161 | 59.8258 | 738.4101
2043-01-13 13:01 | 2915.75 | 1 | 57.3576 | 59.8258 | 854.522
2043-01-14 14:01 | 2900.04 | 1 | 57.8241 | 59.8258 | 849.9178
2043-01-15 15:01 | 2831.86 | 1 | 58.1413 | 59.8258 | 829.9362
2043-01-16 16:01 | 872.007 | 1 | 58.5689 | 59.8258 | 255.56
2043-01-17 17:01 | -1063.81 | 3.6677 | 57.2872 | 59.8258 | -311.7719
2043-01-18 18:01 | -1575.8 | 4.9075 | 56.8939 | 59.8258 | -461.8214
2043-01-19 19:01 | -2278.44 | 6.108 | 56.5135 | 59.8258 | -667.7448
2043-01-20 20:01 | -3100.23 | 6.108 | 55.7367 | 59.8258 | -908.5877
2043-01-21 21:01 | -4232.57 | 6.108 | 54.6647 | 59.8258 | -1240.4438
2043-01-22 22:01 | -4795.11 | 6.108 | 53.9636 | 59.8258 | -1405.308
2043-01-23 23:01 | -6323.11 | 6.108 | 52.5954 | 59.8258 | -1853.1206
2043-01-25 00:01 | -6287.24 | 6.108 | 52.2511 | 59.8258 | -1842.6082
2043-01-26 01:01 | -6421 | 6.108 | 51.9108 | 59.8258 | -1881.8093
2043-01-27 02:01 | -6703.74 | 6.108 | 51.5089 | 59.8258 | -1964.6723
2043-01-28 03:01 | -7047.21 | 6.108 | 51.0596 | 59.8258 | -2065.3334
2043-01-29 04:01 | -6891.53 | 6.108 | 50.993 | 59.8258 | -2019.7081
2043-01-30 05:01 | -6946.99 | 6.108 | 50.8794 | 59.8258 | -2035.9618
2043-01-31 06:01 | -6248.07 | 6.108 | 51.3278 | 59.8258 | -1831.1286
2043-02-01 07:01 | -6348.59 | 6.108 | 51.279 | 59.8258 | -1860.5881
2043-02-02 08:01 | -4667.37 | 6.108 | 52.5134 | 59.8258 | -1367.8711
2043-02-03 09:01 | -3544.52 | 6.108 | 53.5562 | 59.8258 | -1038.7963
2043-02-04 10:01 | -2043.8 | 6.108 | 54.9309 | 59.8258 | -598.9787
2043-02-05 11:01 | -705.607 | 2.1249 | 55.2765 | 59.8258 | -206.793
2043-02-06 12:01 | -207.096 | 1.0228 | 56.2236 | 59.8258 | -60.6938
2043-02-07 13:01 | 2111.89 | 1 | 57.2572 | 59.8258 | 618.9339
2043-02-08 14:01 | 2915.75 | 1 | 57.6794 | 59.8258 | 854.522
2043-02-09 15:01 | 2899.52 | 1 | 58.1139 | 59.8258 | 849.7654
2043-02-10 16:01 | 93.1272 | 1 | 58.6442 | 59.8258 | 27.2929
2043-02-11 17:01 | -1139.12 | 3.848 | 57.151 | 59.8258 | -333.8431
2043-02-12 18:01 | -1563.88 | 4.8559 | 56.8664 | 59.8258 | -458.328
2043-02-13 19:01 | -2475.94 | 6.108 | 56.3861 | 59.8258 | -725.6264
2043-02-14 20:01 | -2908.94 | 6.108 | 55.8737 | 59.8258 | -852.5262
2043-02-15 21:01 | -3947.93 | 6.108 | 54.9128 | 59.8258 | -1157.0241
2043-02-16 22:01 | -4467.9 | 6.108 | 54.3042 | 59.8258 | -1309.4122
2043-02-17 23:01 | -5569.9 | 6.108 | 53.2884 | 59.8258 | -1632.3766
2043-02-19 00:01 | -6169.67 | 6.108 | 52.5715 | 59.8258 | -1808.1518
2043-02-20 01:01 | -6287.43 | 6.108 | 52.2127 | 59.8258 | -1842.6638
2043-02-21 02:01 | -6547.2 | 6.108 | 51.8048 | 59.8258 | -1918.7949
2043-02-22 03:01 | -6594.99 | 6.108 | 51.5745 | 59.8258 | -1932.8008
2043-02-23 04:01 | -6978.79 | 6.108 | 51.1469 | 59.8258 | -2045.2815
2043-02-24 05:01 | -6574.37 | 6.108 | 51.3101 | 59.8258 | -1926.7577
2043-02-25 06:01 | -6561.96 | 6.108 | 51.2718 | 59.8258 | -1923.1206
2043-02-26 07:01 | -6553.81 | 6.108 | 51.2335 | 59.8258 | -1920.7321
2043-02-27 08:01 | -4894.29 | 6.108 | 52.4126 | 59.8258 | -1434.3748
2043-02-28 09:01 | -3737.52 | 6.108 | 53.4427 | 59.8258 | -1095.359
2043-03-01 10:01 | -1672.6 | 5.169 | 54.9864 | 59.8258 | -490.1907
2043-03-02 11:01 | -420.342 | 1.36 | 55.4182 | 59.8258 | -123.1901
2043-03-03 12:01 | 2933.76 | 1 | 56.9577 | 59.8258 | 859.8002
2043-03-04 13:01 | 2973.11 | 1 | 81.2049 | 59.8258 | 871.3325
2043-03-05 14:01 | 2920.09 | 1 | 58.0373 | 59.8258 | 855.7939
2043-03-06 15:01 | 3051.73 | 1 | 58.2964 | 59.8258 | 894.3738
2043-03-07 16:01 | 2929.02 | 1 | 58.5667 | 59.8258 | 858.411
2043-03-08 17:01 | -16.035 | 0.64185 | 58.9279 | 59.8258 | -4.6994
2043-03-09 18:01 | -203.52 | 1.13 | 57.9618 | 59.8258 | -59.6458
2043-03-10 19:01 | -792.517 | 2.8032 | 57.3949 | 59.8258 | -232.2638
2043-03-11 20:01 | -1416.17 | 4.4986 | 57.1722 | 59.8258 | -415.0385
2043-03-12 21:01 | -2365.67 | 6.108 | 56.7162 | 59.8258 | -693.3094
2043-03-13 22:01 | -3006.35 | 6.108 | 56.0205 | 59.8258 | -881.0742
2043-03-14 23:01 | -3735.53 | 6.108 | 55.311 | 59.8258 | -1094.7758
2043-03-16 00:01 | -3981.97 | 6.108 | 54.9042 | 59.8258 | -1167.0002
2043-03-17 01:01 | -4406.28 | 6.108 | 54.4086 | 59.8258 | -1291.3532
2043-03-18 02:01 | -4479.78 | 6.108 | 54.1743 | 59.8258 | -1312.8939
2043-03-19 03:01 | -4459.18 | 6.108 | 54.0552 | 59.8258 | -1306.8567
2043-03-20 04:01 | -4082.85 | 6.108 | 54.2422 | 59.8258 | -1196.5652
2043-03-21 05:01 | -4167.19 | 6.108 | 54.1863 | 59.8258 | -1221.2828
2043-03-22 06:01 | -3563.25 | 6.108 | 54.6178 | 59.8258 | -1044.2855
2043-03-23 07:01 | -3471.98 | 6.108 | 54.7555 | 59.8258 | -1017.5369
2043-03-24 08:01 | -3504.76 | 6.108 | 54.7736 | 59.8258 | -1027.1438
2043-03-25 09:01 | -4051.78 | 6.108 | 54.3769 | 59.8258 | -1187.4595
2043-03-26 10:01 | -3959.22 | 6.108 | 54.3628 | 59.8258 | -1160.3328
2043-03-27 11:01 | -3824.25 | 6.108 | 54.4232 | 59.8258 | -1120.777
2043-03-28 12:01 | -3553.71 | 6.108 | 54.5808 | 59.8258 | -1041.4896
2043-03-29 13:01 | -3423.51 | 6.108 | 54.6522 | 59.8258 | -1003.3317
2043-03-30 14:01 | -3553.36 | 6.108 | 54.5248 | 59.8258 | -1041.387
2043-03-31 15:01 | -3290.79 | 6.108 | 54.6677 | 59.8258 | -964.4353
2043-04-01 16:01 | -2356 | 6.108 | 55.3563 | 59.8258 | -690.4754
2043-04-02 17:01 | -2018.63 | 6.0995 | 55.7321 | 59.8258 | -591.6021
2043-04-03 18:01 | -1754.46 | 5.2693 | 55.822 | 59.8258 | -514.1815
2043-04-04 19:01 | -1862.29 | 5.674 | 55.9336 | 59.8258 | -545.7833
2043-04-05 20:01 | -2143.53 | 6.108 | 55.8882 | 59.8258 | -628.2066
2043-04-06 21:01 | -2892.18 | 6.108 | 55.3556 | 59.8258 | -847.6143
2043-04-07 22:01 | -3250.4 | 6.108 | 55.0153 | 59.8258 | -952.5982
2043-04-08 23:01 | -3998.51 | 6.108 | 54.3866 | 59.8258 | -1171.8476
2043-04-10 00:01 | -4218.9 | 6.108 | 54.0931 | 59.8258 | -1236.4375
2043-04-11 01:01 | -3945.55 | 6.108 | 54.2002 | 59.8258 | -1156.3266
2043-04-12 02:01 | -4069.18 | 6.108 | 54.0947 | 59.8258 | -1192.5589
2043-04-13 03:01 | -4059.93 | 6.108 | 54.0784 | 59.8258 | -1189.848
2043-04-14 04:01 | -3929.54 | 6.108 | 54.148 | 59.8258 | -1151.6345
2043-04-15 05:01 | -3522.55 | 6.108 | 54.459 | 59.8258 | -1032.3575
2043-04-16 06:01 | -3023.99 | 6.108 | 54.8838 | 59.8258 | -886.244
2043-04-17 07:01 | -2119.62 | 6.108 | 55.6476 | 59.8258 | -621.1993
2043-04-18 08:01 | -1851.98 | 5.5656 | 55.8779 | 59.8258 | -542.7618
2043-04-19 09:01 | -2114.68 | 6.108 | 55.9565 | 59.8258 | -619.7515
2043-04-20 10:01 | -1708.4 | 5.1176 | 56.0593 | 59.8258 | -500.6826
2043-04-21 11:01 | 1985.24 | 1 | 57.5145 | 59.8258 | 581.8164
2043-04-22 12:01 | 3060.21 | 1.0024 | 72.2669 | 59.8258 | 896.859
2043-04-23 13:01 | 3851.67 | 1.3549 | 71.7203 | 59.8258 | 1128.813
2043-04-24 14:01 | 2835.68 | 1 | 58.8467 | 59.8258 | 831.0558
2043-04-25 15:01 | 3156.84 | 1 | 58.9885 | 59.8258 | 925.1785
2043-04-26 16:01 | 3204.86 | 1 | 76.1854 | 59.8258 | 939.2517
2043-04-27 17:01 | 2870.78 | 1 | 59.4008 | 59.8258 | 841.3426
2043-04-28 18:01 | 2942.07 | 1 | 59.4828 | 59.8258 | 862.2356
2043-04-29 19:01 | 2864.63 | 1 | 59.5726 | 59.8258 | 839.5402
2043-04-30 20:01 | -198.84 | 1.1558 | 59.1421 | 59.8258 | -58.2743
2043-05-01 21:01 | -1105.48 | 3.6737 | 58.2484 | 59.8258 | -323.9842
2043-05-02 22:01 | -1788.74 | 5.4689 | 57.8781 | 59.8258 | -524.2279
2043-05-03 23:01 | -2654.24 | 6.108 | 57.1737 | 59.8258 | -777.881
2043-05-05 00:01 | -3366.29 | 6.108 | 56.3665 | 59.8258 | -986.5622
2043-05-06 01:01 | -3775.58 | 6.108 | 55.7537 | 59.8258 | -1106.5133
2043-05-07 02:01 | -4125.5 | 6.108 | 55.2829 | 59.8258 | -1209.0647
2043-05-08 03:01 | -4478.28 | 6.108 | 54.8275 | 59.8258 | -1312.4543
2043-05-09 04:01 | -4320.81 | 6.108 | 54.753 | 59.8258 | -1266.3044
2043-05-10 05:01 | -4940.44 | 6.108 | 54.1719 | 59.8258 | -1447.9
2043-05-11 06:01 | -5130.98 | 6.108 | 53.8394 | 59.8258 | -1503.7418
2043-05-12 07:01 | -4272.37 | 6.108 | 54.3015 | 59.8258 | -1252.108
2043-05-13 08:01 | -2433.58 | 6.108 | 55.6865 | 59.8258 | -713.2119
2043-05-14 09:01 | -1495.19 | 4.4775 | 56.2159 | 59.8258 | -438.1969
2043-05-15 10:01 | -834.34 | 2.6378 | 56.5223 | 59.8258 | -244.5209
2043-05-16 11:01 | 2317.35 | 1 | 57.9702 | 59.8258 | 679.1482
2043-05-17 12:01 | 3180.84 | 1 | 83.0977 | 59.8258 | 932.2122
2043-05-18 13:01 | 3176.9 | 1 | 74.1978 | 59.8258 | 931.0575
2043-05-19 14:01 | 3293.76 | 1.0628 | 73.6319 | 59.8258 | 965.3058
2043-05-20 15:01 | 3042.01 | 1 | 81.5854 | 59.8258 | 891.5251
2043-05-21 16:01 | 3109.97 | 1 | 59.585 | 59.8258 | 911.4422
2043-05-22 17:01 | 3063.55 | 1 | 59.7326 | 59.8258 | 897.8379
2043-05-23 18:01 | 411.744 | 1 | 60.0819 | 59.8258 | 120.6703
2043-05-24 19:01 | -748.679 | 2.7118 | 58.598 | 59.8258 | -219.4162
2043-05-25 20:01 | -1211.62 | 3.8537 | 58.1578 | 59.8258 | -355.0908
2043-05-26 21:01 | -1618.68 | 4.9463 | 57.9334 | 59.8258 | -474.3883
2043-05-27 22:01 | -1953.36 | 5.839 | 57.7419 | 59.8258 | -572.4733
2043-05-28 23:01 | -2881.48 | 6.108 | 56.9234 | 59.8258 | -844.4784
2043-05-30 00:01 | -4233.58 | 6.108 | 55.6827 | 59.8258 | -1240.7398
2043-05-31 01:01 | -4619.29 | 6.108 | 55.0719 | 59.8258 | -1353.7803
2043-06-01 02:01 | -4745.03 | 6.108 | 54.7245 | 59.8258 | -1390.631
2043-06-02 03:01 | -4713.23 | 6.108 | 54.5607 | 59.8258 | -1381.3114
2043-06-03 04:01 | -4698.32 | 6.108 | 54.4152 | 59.8258 | -1376.9417
2043-06-04 05:01 | -4879.73 | 6.108 | 54.1511 | 59.8258 | -1430.1077
2043-06-05 06:01 | -5031.97 | 6.108 | 53.9426 | 59.8258 | -1474.7248
2043-06-06 07:01 | -4131.34 | 6.108 | 54.5259 | 59.8258 | -1210.7762
2043-06-07 08:01 | -3933.72 | 6.108 | 54.714 | 59.8258 | -1152.8595
2043-06-08 09:01 | -4742.27 | 6.108 | 54.1256 | 59.8258 | -1389.8221
2043-06-09 10:01 | -4849.86 | 6.108 | 53.9036 | 59.8258 | -1421.3537
2043-06-10 11:01 | -4758.16 | 6.108 | 53.8381 | 59.8258 | -1394.479
2043-06-11 12:01 | -4530.39 | 6.108 | 53.9264 | 59.8258 | -1327.7262
2043-06-12 13:01 | -4472.82 | 6.108 | 53.8981 | 59.8258 | -1310.8541
2043-06-13 14:01 | -4172.7 | 6.108 | 54.0421 | 59.8258 | -1222.8977
2043-06-14 15:01 | -3727.82 | 6.108 | 54.3435 | 59.8258 | -1092.5162
2043-06-15 16:01 | -3506.98 | 6.108 | 54.5205 | 59.8258 | -1027.7944
2043-06-16 17:01 | -1947.93 | 5.9589 | 55.6635 | 59.8258 | -570.8819
2043-06-17 18:01 | -2054.74 | 6.108 | 55.8305 | 59.8258 | -602.1849
2043-06-18 19:01 | -2404.4 | 6.108 | 55.6655 | 59.8258 | -704.6601
2043-06-19 20:01 | -2469.11 | 6.108 | 55.6221 | 59.8258 | -723.6247
2043-06-20 21:01 | -2746.53 | 6.108 | 55.4406 | 59.8258 | -804.9285
2043-06-21 22:01 | -2779.05 | 6.108 | 55.4227 | 59.8258 | -814.4592
2043-06-22 23:01 | -2654.25 | 6.108 | 55.5095 | 59.8258 | -777.8839
2043-06-24 00:01 | -3742.39 | 6.108 | 54.728 | 59.8258 | -1096.7862
2043-06-25 01:01 | -3935.06 | 6.108 | 54.4726 | 59.8258 | -1153.2522
2043-06-26 02:01 | -3966.35 | 6.108 | 54.3704 | 59.8258 | -1162.4224
2043-06-27 03:01 | -3952.35 | 6.108 | 54.3487 | 59.8258 | -1158.3194
2043-06-28 04:01 | -3737.8 | 6.108 | 54.485 | 59.8258 | -1095.441
2043-06-29 05:01 | -3672.09 | 6.108 | 54.5224 | 59.8258 | -1076.1833
2043-06-30 06:01 | -3087.68 | 6.108 | 54.9713 | 59.8258 | -904.9097
2043-07-01 07:01 | -2822.53 | 6.108 | 55.2499 | 59.8258 | -827.2019
2043-07-02 08:01 | -2844.29 | 6.108 | 55.3085 | 59.8258 | -833.5791
2043-07-03 09:01 | -3532.18 | 6.108 | 54.8358 | 59.8258 | -1035.1798
2043-07-04 10:01 | -3348.73 | 6.108 | 54.9064 | 59.8258 | -981.4159
2043-07-05 11:01 | -2489.36 | 6.108 | 55.5355 | 59.8258 | -729.5594
2043-07-06 12:01 | -594.046 | 1.7803 | 55.9755 | 59.8258 | -174.0977
2043-07-07 13:01 | 2291.34 | 1 | 57.6133 | 59.8258 | 671.5255
2043-07-08 14:01 | -544.671 | 2.1703 | 57.2259 | 59.8258 | -159.6273
2043-07-09 15:01 | -1402.09 | 4.5317 | 56.9197 | 59.8258 | -410.912
2043-07-10 16:01 | -1482.34 | 4.5509 | 56.7389 | 59.8258 | -434.431
2043-07-11 17:01 | -1594.38 | 4.8834 | 56.735 | 59.8258 | -467.2667
2043-07-12 18:01 | -1688.65 | 5.1341 | 56.7014 | 59.8258 | -494.8945
2043-07-13 19:01 | -2179.61 | 6.108 | 56.4859 | 59.8258 | -638.7806
2043-07-14 20:01 | -2607.95 | 6.108 | 56.0857 | 59.8258 | -764.3147
2043-07-15 21:01 | -3878.12 | 6.108 | 55.0594 | 59.8258 | -1136.5648
2043-07-16 22:01 | -4121.6 | 6.108 | 54.6699 | 59.8258 | -1207.9217
2043-07-17 23:01 | -5027.67 | 6.108 | 53.835 | 59.8258 | -1473.4646
2043-07-19 00:01 | -5349.82 | 6.108 | 53.3626 | 59.8258 | -1567.8775
2043-07-20 01:01 | -5502.97 | 6.108 | 53.0141 | 59.8258 | -1612.7613
2043-07-21 02:01 | -5673.74 | 6.108 | 52.7239 | 59.8258 | -1662.8091
2043-07-22 03:01 | -5808.51 | 6.108 | 52.496 | 59.8258 | -1702.3062
2043-07-23 04:01 | -5453.58 | 6.108 | 52.6368 | 59.8258 | -1598.2865
2043-07-24 05:01 | -5585.51 | 6.108 | 52.497 | 59.8258 | -1636.9514
2043-07-25 06:01 | -5098.82 | 6.108 | 52.7911 | 59.8258 | -1494.3166
2043-07-26 07:01 | -5187.51 | 6.108 | 52.7196 | 59.8258 | -1520.3091
2043-07-27 08:01 | -4644.4 | 6.108 | 53.092 | 59.8258 | -1361.1393
2043-07-28 09:01 | -5579.14 | 6.108 | 52.4426 | 59.8258 | -1635.0845
2043-07-29 10:01 | -5505.93 | 6.108 | 52.3829 | 59.8258 | -1613.6288
2043-07-30 11:01 | -5272.29 | 6.108 | 52.4902 | 59.8258 | -1545.1557
2043-07-31 12:01 | -5147.81 | 6.108 | 52.5529 | 59.8258 | -1508.6742
2043-08-01 13:01 | -5036.65 | 6.108 | 52.5922 | 59.8258 | -1476.0964
2043-08-02 14:01 | -5285.03 | 6.108 | 52.3681 | 59.8258 | -1548.8894
2043-08-03 15:01 | -5151.41 | 6.108 | 52.4115 | 59.8258 | -1509.7292
2043-08-04 16:01 | -3931.41 | 6.108 | 53.2937 | 59.8258 | -1152.1825
2043-08-05 17:01 | -3956.72 | 6.108 | 53.4053 | 59.8258 | -1159.6002
2043-08-06 18:01 | -3814.16 | 6.108 | 53.557 | 59.8258 | -1117.82
2043-08-07 19:01 | -4296.74 | 6.108 | 53.2225 | 59.8258 | -1259.2502
2043-08-08 20:01 | -4483.3 | 6.108 | 53.0433 | 59.8258 | -1313.9255
2043-08-09 21:01 | -5526.15 | 6.108 | 52.2372 | 59.8258 | -1619.5547
2043-08-10 22:01 | -5799.4 | 6.108 | 51.8668 | 59.8258 | -1699.6364
2043-08-11 23:01 | -6543.51 | 6.108 | 51.1776 | 59.8258 | -1917.7135
2043-08-13 00:01 | -6712.74 | 6.108 | 50.8702 | 59.8258 | -1967.3099
2043-08-14 01:01 | -6841.5 | 6.108 | 50.6347 | 59.8258 | -2005.0457
2043-08-15 02:01 | -6869.51 | 6.108 | 50.5016 | 59.8258 | -2013.2546
2043-08-16 03:01 | -6783.23 | 6.108 | 50.4878 | 59.8258 | -1987.9685
2043-08-17 04:01 | -6898.75 | 6.108 | 50.33 | 59.8258 | -2021.824
2043-08-18 05:01 | -6528.11 | 6.108 | 50.5357 | 59.8258 | -1913.2002
2043-08-19 06:01 | -6213.05 | 6.108 | 50.7524 | 59.8258 | -1820.8652
2043-08-20 07:01 | -6207.85 | 6.108 | 50.7692 | 59.8258 | -1819.3412
2043-08-21 08:01 | -6214.9 | 6.108 | 50.742 | 59.8258 | -1821.4074
2043-08-22 09:01 | -6644.54 | 6.108 | 50.4004 | 59.8258 | -1947.3224
2043-08-23 10:01 | -6274.97 | 6.108 | 50.6014 | 59.8258 | -1839.0122
2043-08-24 11:01 | -4119.98 | 6.108 | 52.2091 | 59.8258 | -1207.4469
2043-08-25 12:01 | -4924.76 | 6.108 | 51.8721 | 59.8258 | -1443.3047
2043-08-26 13:01 | -5266.4 | 6.108 | 51.6246 | 59.8258 | -1543.4295
2043-08-27 14:01 | -5279.99 | 6.108 | 51.5574 | 59.8258 | -1547.4123
2043-08-28 15:01 | -5220.77 | 6.108 | 51.6013 | 59.8258 | -1530.0567
2043-08-29 16:01 | -4211.85 | 6.108 | 52.3664 | 59.8258 | -1234.3714
2043-08-30 17:01 | -3940.99 | 6.108 | 52.662 | 59.8258 | -1154.9902
2043-08-31 18:01 | -3584.16 | 6.108 | 53.0188 | 59.8258 | -1050.4136
2043-09-01 19:01 | -3789.57 | 6.108 | 52.9674 | 59.8258 | -1110.6133
2043-09-02 20:01 | -3927.4 | 6.108 | 52.9127 | 59.8258 | -1151.0073
2043-09-03 21:01 | -4677.45 | 6.108 | 52.3945 | 59.8258 | -1370.8253
2043-09-04 22:01 | -4742.25 | 6.108 | 52.2779 | 59.8258 | -1389.8163
2043-09-05 23:01 | -5487.81 | 6.108 | 51.6685 | 59.8258 | -1608.3183
2043-09-07 00:01 | -5496.73 | 6.108 | 51.5439 | 59.8258 | -1610.9325
2043-09-08 01:01 | -5391.38 | 6.108 | 51.56 | 59.8258 | -1580.0575
2043-09-09 02:01 | -5378.88 | 6.108 | 51.5517 | 59.8258 | -1576.3941
2043-09-10 03:01 | -5463.78 | 6.108 | 51.4826 | 59.8258 | -1601.2759
2043-09-11 04:01 | -5294.16 | 6.108 | 51.5783 | 59.8258 | -1551.5651
2043-09-12 05:01 | -5404.82 | 6.108 | 51.5037 | 59.8258 | -1583.9964
2043-09-13 06:01 | -4983.58 | 6.108 | 51.799 | 59.8258 | -1460.5431
2043-09-14 07:01 | -5415.55 | 6.108 | 51.5114 | 59.8258 | -1587.141
2043-09-15 08:01 | -5101.26 | 6.108 | 51.7009 | 59.8258 | -1495.0317
2043-09-16 09:01 | -4343.37 | 6.108 | 52.2926 | 59.8258 | -1272.9161
2043-09-17 10:01 | -3460.67 | 6.108 | 53.0714 | 59.8258 | -1014.2223
2043-09-18 11:01 | -3931.03 | 6.108 | 52.8982 | 59.8258 | -1152.0712
2043-09-19 12:01 | -4409.39 | 6.108 | 52.5687 | 59.8258 | -1292.2646
2043-09-20 13:01 | -2993.91 | 6.108 | 53.5998 | 59.8258 | -877.4284
2043-09-21 14:01 | -4507.57 | 6.108 | 52.6671 | 59.8258 | -1321.0384
2043-09-22 15:01 | -3672.94 | 6.108 | 53.2029 | 59.8258 | -1076.4325
2043-09-23 16:01 | -4477.02 | 6.108 | 52.6324 | 59.8258 | -1312.085
2043-09-24 17:01 | -4572.55 | 6.108 | 52.4965 | 59.8258 | -1340.0821
2043-09-25 18:01 | -4460.11 | 6.108 | 52.5255 | 59.8258 | -1307.1292
2043-09-26 19:01 | -5010.43 | 6.108 | 52.0837 | 59.8258 | -1468.4121
2043-09-27 20:01 | -5116.22 | 6.108 | 51.9294 | 59.8258 | -1499.4161
2043-09-28 21:01 | -6339.71 | 6.108 | 50.931 | 59.8258 | -1857.9856
2043-09-29 22:01 | -6728.32 | 6.108 | 50.4248 | 59.8258 | -1971.8759
2043-09-30 23:01 | -7888.26 | 6.108 | 49.375 | 59.8258 | -2311.8208
2043-10-02 00:01 | -8000.92 | 6.108 | 49.0205 | 59.8258 | -2344.8382
2043-10-03 01:01 | -8086.4 | 6.108 | 48.7491 | 59.8258 | -2369.8899
2043-10-04 02:01 | -8330.85 | 6.108 | 48.413 | 59.8258 | -2441.5311
2043-10-05 03:01 | -8341.46 | 6.108 | 48.2461 | 59.8258 | -2444.6406
2043-10-06 04:01 | -8320.21 | 6.108 | 48.136 | 59.8258 | -2438.4128
2043-10-07 05:01 | -8096.87 | 6.108 | 48.2171 | 59.8258 | -2372.9584
2043-10-08 06:01 | -8090.01 | 6.108 | 48.1624 | 59.8258 | -2370.9479
2043-10-09 07:01 | -8194.66 | 6.108 | 48.0211 | 59.8258 | -2401.6178
2043-10-10 08:01 | -7649.58 | 6.108 | 48.3503 | 59.8258 | -2241.8706
2043-10-11 09:01 | -7915.66 | 6.108 | 48.1642 | 59.8258 | -2319.8509
2043-10-12 10:01 | -7668.02 | 6.108 | 48.2956 | 59.8258 | -2247.2748
2043-10-13 11:01 | -7462.62 | 6.108 | 48.4295 | 59.8258 | -2187.078
2043-10-14 12:01 | -7535.75 | 6.108 | 48.3802 | 59.8258 | -2208.5103
2043-10-15 13:01 | -7544.76 | 6.108 | 48.34 | 59.8258 | -2211.1509
2043-10-16 14:01 | -7765.85 | 6.108 | 48.1392 | 59.8258 | -2275.946
2043-10-17 15:01 | -6773.58 | 6.108 | 48.8244 | 59.8258 | -1985.1403
2043-10-18 16:01 | -6451.81 | 6.108 | 49.1519 | 59.8258 | -1890.8389
2043-10-19 17:01 | -6319.36 | 6.108 | 49.3239 | 59.8258 | -1852.0216
2043-10-20 18:01 | -6098.52 | 6.108 | 49.5279 | 59.8258 | -1787.2998
2043-10-21 19:01 | -6763.83 | 6.108 | 49.0847 | 59.8258 | -1982.2829
2043-10-22 20:01 | -7040.16 | 6.108 | 48.8249 | 59.8258 | -2063.2672
2043-10-23 21:01 | -7655.25 | 6.108 | 48.2958 | 59.8258 | -2243.5323
2043-10-24 22:01 | -8127.34 | 6.108 | 47.821 | 59.8258 | -2381.8882
2043-10-25 23:01 | -9125.08 | 6.108 | 46.9365 | 59.8258 | -2674.297
2043-10-27 00:01 | -9570.16 | 6.108 | 46.3745 | 59.8258 | -2804.737
2043-10-28 01:01 | -9797.55 | 6.108 | 46.0051 | 59.8258 | -2871.3785
2043-10-29 02:01 | -9949.64 | 6.108 | 45.7323 | 59.8258 | -2915.9516
2043-10-30 03:01 | -10045.4 | 6.108 | 45.5128 | 59.8258 | -2944.0161
2043-10-31 04:01 | -9847.36 | 6.108 | 45.524 | 59.8258 | -2885.9763
2043-11-01 05:01 | -10335.5 | 6.108 | 45.0774 | 59.8258 | -3029.036
2043-11-02 06:01 | -10007.8 | 6.108 | 45.1732 | 59.8258 | -2932.9967
2043-11-03 07:01 | -9439.13 | 6.108 | 45.5329 | 59.8258 | -2766.3359
2043-11-04 08:01 | -8398.29 | 6.108 | 46.3263 | 59.8258 | -2461.2958
2043-11-05 09:01 | -8007.68 | 6.108 | 46.7401 | 59.8258 | -2346.8193
2043-11-06 10:01 | -6488.08 | 6.108 | 47.9715 | 59.8258 | -1901.4685
2043-11-07 11:01 | -5321.35 | 6.108 | 49.1082 | 59.8258 | -1559.5337
2043-11-08 12:01 | -4264.8 | 6.108 | 50.2188 | 59.8258 | -1249.8895
2043-11-09 13:01 | -3342.77 | 6.108 | 51.2379 | 59.8258 | -979.6692
2043-11-10 14:01 | -2568.03 | 6.108 | 52.1554 | 59.8258 | -752.6153
2043-11-11 15:01 | -2975.51 | 6.108 | 52.1868 | 59.8258 | -872.0359
2043-11-12 16:01 | -3757 | 6.108 | 51.767 | 59.8258 | -1101.068
2043-11-13 17:01 | -3608.14 | 6.108 | 51.9134 | 59.8258 | -1057.4415
2043-11-14 18:01 | -4549.42 | 6.108 | 51.2927 | 59.8258 | -1333.3034
2043-11-15 19:01 | -5510.25 | 6.108 | 50.5245 | 59.8258 | -1614.8949
2043-11-16 20:01 | -5912.42 | 6.108 | 50.0669 | 59.8258 | -1732.7593
2043-11-17 21:01 | -6414.72 | 6.108 | 49.5814 | 59.8258 | -1879.9689
2043-11-18 22:01 | -6828.1 | 6.108 | 49.155 | 59.8258 | -2001.1186
2043-11-19 23:01 | -7037.66 | 6.108 | 48.8623 | 59.8258 | -2062.5345
2043-11-21 00:01 | -8557.9 | 6.108 | 47.6105 | 59.8258 | -2508.0729
2043-11-22 01:01 | -8937.36 | 6.108 | 47.0438 | 59.8258 | -2619.2817
2043-11-23 02:01 | -9297.93 | 6.108 | 46.5377 | 59.8258 | -2724.9543
2043-11-24 03:01 | -9417.52 | 6.108 | 46.2545 | 59.8258 | -2760.0027
2043-11-25 04:01 | -10022.6 | 6.108 | 45.641 | 59.8258 | -2937.3341
2043-11-26 05:01 | -9728.26 | 6.108 | 45.6444 | 59.8258 | -2851.0716
2043-11-27 06:01 | -10220.3 | 6.108 | 45.1807 | 59.8258 | -2995.2743
2043-11-28 07:01 | -9380.03 | 6.108 | 45.67 | 59.8258 | -2749.0154
2043-11-29 08:01 | -7727.7 | 6.108 | 46.9109 | 59.8258 | -2264.7653
2043-11-30 09:01 | -7354.02 | 6.108 | 47.393 | 59.8258 | -2155.2505
2043-12-01 10:01 | -5392.33 | 6.108 | 49.0012 | 59.8258 | -1580.3359
2043-12-02 11:01 | -4210.66 | 6.108 | 50.1968 | 59.8258 | -1234.0226
2043-12-03 12:01 | -3128.99 | 6.108 | 51.3752 | 59.8258 | -917.0164
2043-12-04 13:01 | -2686.85 | 6.108 | 52.066 | 59.8258 | -787.438
2043-12-05 14:01 | -2111.11 | 6.108 | 52.7769 | 59.8258 | -618.7053
2043-12-06 15:01 | -2249.2 | 6.108 | 52.9613 | 59.8258 | -659.1755
2043-12-07 16:01 | -2687.38 | 6.108 | 52.8175 | 59.8258 | -787.5933
2043-12-08 17:01 | -2824.3 | 6.108 | 52.7965 | 59.8258 | -827.7206
2043-12-09 18:01 | -3726.33 | 6.108 | 52.2004 | 59.8258 | -1092.0795
2043-12-10 19:01 | -4533.41 | 6.108 | 51.5634 | 59.8258 | -1328.6113
2043-12-11 20:01 | -5019.6 | 6.108 | 51.0842 | 59.8258 | -1471.0995
2043-12-12 21:01 | -5562.46 | 6.108 | 50.5785 | 59.8258 | -1630.1961
2043-12-13 22:01 | -5935.51 | 6.108 | 50.1729 | 59.8258 | -1739.5263
2043-12-14 23:01 | -5574.8 | 6.108 | 50.3111 | 59.8258 | -1633.8126
2043-12-16 00:01 | -6724.93 | 6.108 | 49.4249 | 59.8258 | -1970.8824
2043-12-17 01:01 | -6679.55 | 6.108 | 49.2847 | 59.8258 | -1957.5829
2043-12-18 02:01 | -6921.3 | 6.108 | 48.9972 | 59.8258 | -2028.4328
2043-12-19 03:01 | -6736.98 | 6.108 | 49.0481 | 59.8258 | -1974.4139
2043-12-20 04:01 | -6340.34 | 6.108 | 49.3129 | 59.8258 | -1858.1702
2043-12-21 05:01 | -6307.6 | 6.108 | 49.3503 | 59.8258 | -1848.5751
2043-12-22 06:01 | -6030.48 | 6.108 | 49.5841 | 59.8258 | -1767.3592
2043-12-23 07:01 | -6198.71 | 6.108 | 49.5074 | 59.8258 | -1816.6626
2043-12-24 08:01 | -4758.65 | 6.108 | 50.5956 | 59.8258 | -1394.6226
2043-12-25 09:01 | -3559.94 | 6.108 | 51.6989 | 59.8258 | -1043.3154
2043-12-26 10:01 | -1760.69 | 5.5774 | 53.1911 | 59.8258 | -516.0073
2043-12-27 11:01 | -690.119 | 2.1785 | 53.5634 | 59.8258 | -202.2539
2043-12-28 12:01 | 2346.35 | 1 | 55.1962 | 59.8258 | 687.6473
2043-12-29 13:01 | 2936.12 | 1 | 55.8141 | 59.8258 | 860.4918
2043-12-30 14:01 | 2898.38 | 1 | 56.325 | 59.8258 | 849.4313
2043-12-31 15:01 | 2908.17 | 1 | 56.6601 | 59.8258 | 852.3005
2044-01-01 16:01 | 2878.2 | 1 | 56.9419 | 59.8258 | 843.5172
2044-01-02 17:01 | -465.233 | 1.9503 | 56.3507 | 59.8258 | -136.3463
2044-01-03 18:01 | -1211.82 | 4.0469 | 55.8037 | 59.8258 | -355.1494
2044-01-04 19:01 | -1969.12 | 6.108 | 55.518 | 59.8258 | -577.0921
2044-01-05 20:01 | -2898.33 | 6.108 | 54.6813 | 59.8258 | -849.4167
2044-01-06 21:01 | -4257.43 | 6.108 | 53.4564 | 59.8258 | -1247.7296
2044-01-07 22:01 | -5226.32 | 6.108 | 52.3997 | 59.8258 | -1531.6832
2044-01-08 23:01 | -6067.41 | 6.108 | 51.4797 | 59.8258 | -1778.1823
2044-01-10 00:01 | -6687.04 | 6.108 | 50.7071 | 59.8258 | -1959.778
2044-01-11 01:01 | -6925.28 | 6.108 | 50.2288 | 59.8258 | -2029.5992
2044-01-12 02:01 | -7306.31 | 6.108 | 49.7001 | 59.8258 | -2141.2681
2044-01-13 03:01 | -7172.49 | 6.108 | 49.5707 | 59.8258 | -2102.0493
2044-01-14 04:01 | -7351.55 | 6.108 | 49.2772 | 59.8258 | -2154.5266
2044-01-15 05:01 | -7269.22 | 6.108 | 49.2167 | 59.8258 | -2130.3981
2044-01-16 06:01 | -6897.46 | 6.108 | 49.4131 | 59.8258 | -2021.446
2044-01-17 07:01 | -7382.08 | 6.108 | 49.0314 | 59.8258 | -2163.4741
2044-01-18 08:01 | -5795.04 | 6.108 | 50.1189 | 59.8258 | -1698.3586
2044-01-19 09:01 | -4805.54 | 6.108 | 50.9978 | 59.8258 | -1408.3647
2044-01-20 10:01 | -3173.09 | 6.108 | 52.4176 | 59.8258 | -929.9409
2044-01-21 11:01 | -1624.25 | 5.0859 | 53.6364 | 59.8258 | -476.0207
2044-01-22 12:01 | -767.615 | 2.4552 | 54.0275 | 59.8258 | -224.9657
2044-01-23 13:01 | -253.078 | 1.144 | 54.789 | 59.8258 | -74.1698
2044-01-24 14:01 | 262.835 | 1 | 56.0633 | 59.8258 | 77.0293
2044-01-25 15:01 | -168.457 | 1.088 | 55.6418 | 59.8258 | -49.3699
2044-01-26 16:01 | -399.754 | 1.7065 | 55.4046 | 59.8258 | -117.1563
2044-01-27 17:01 | -1757.8 | 5.7631 | 55.1708 | 59.8258 | -515.1603
2044-01-28 18:01 | -2279.1 | 6.108 | 54.7704 | 59.8258 | -667.9383
2044-01-29 19:01 | -3234.84 | 6.108 | 53.9816 | 59.8258 | -948.038
2044-01-30 20:01 | -3413.88 | 6.108 | 53.6979 | 59.8258 | -1000.5095
2044-01-31 21:01 | -4359.51 | 6.108 | 52.8982 | 59.8258 | -1277.6463
2044-02-01 22:01 | -4636.87 | 6.108 | 52.5063 | 59.8258 | -1358.9325
2044-02-02 23:01 | -5536.29 | 6.108 | 51.6901 | 59.8258 | -1622.5264
2044-02-04 00:01 | -5598.35 | 6.108 | 51.4365 | 59.8258 | -1640.7144
2044-02-05 01:01 | -5690.71 | 6.108 | 51.2315 | 59.8258 | -1667.7825
2044-02-06 02:01 | -5786.29 | 6.108 | 51.0472 | 59.8258 | -1695.7942
2044-02-07 03:01 | -6005.79 | 6.108 | 50.7898 | 59.8258 | -1760.1233
2044-02-08 04:01 | -6074.22 | 6.108 | 50.6325 | 59.8258 | -1780.1782
2044-02-09 05:01 | -5959.15 | 6.108 | 50.6559 | 59.8258 | -1746.4545
2044-02-10 06:01 | -5684.31 | 6.108 | 50.8302 | 59.8258 | -1665.9068
2044-02-11 07:01 | -5717 | 6.108 | 50.8226 | 59.8258 | -1675.4873
2044-02-12 08:01 | -5640.12 | 6.108 | 50.8607 | 59.8258 | -1652.956
2044-02-13 09:01 | -6525.12 | 6.108 | 50.1859 | 59.8258 | -1912.3239
2044-02-14 10:01 | -6479.99 | 6.108 | 50.07 | 59.8258 | -1899.0976
2044-02-15 11:01 | -6569.9 | 6.108 | 49.9007 | 59.8258 | -1925.4476
2044-02-16 12:01 | -6632.98 | 6.108 | 49.7448 | 59.8258 | -1943.9345
2044-02-17 13:01 | -6961.54 | 6.108 | 49.38 | 59.8258 | -2040.226
2044-02-18 14:01 | -7609.5 | 6.108 | 48.7319 | 59.8258 | -2230.1243
2044-02-19 15:01 | -7498.97 | 6.108 | 48.6104 | 59.8258 | -2197.7312
2044-02-20 16:01 | -7074.41 | 6.108 | 48.792 | 59.8258 | -2073.3049
2044-02-21 17:01 | -7417.39 | 6.108 | 48.4905 | 59.8258 | -2173.8224
2044-02-22 18:01 | -6832.75 | 6.108 | 48.8147 | 59.8258 | -2002.4814
2044-02-23 19:01 | -8011.47 | 6.108 | 47.9184 | 59.8258 | -2347.9301
2044-02-24 20:01 | -7985.13 | 6.108 | 47.7604 | 59.8258 | -2340.2106
2044-02-25 21:01 | -9114.5 | 6.108 | 46.8054 | 59.8258 | -2671.1963
2044-02-26 22:01 | -9414.86 | 6.108 | 46.3503 | 59.8258 | -2759.2231
2044-02-27 23:01 | -10745.8 | 6.108 | 45.1615 | 59.8258 | -3149.2831
2044-02-29 00:01 | -10943.5 | 6.108 | 44.6875 | 59.8258 | -3207.2233
2044-03-01 01:01 | -11199.5 | 6.108 | 44.265 | 59.8258 | -3282.2494
2044-03-02 02:01 | -11380.8 | 6.108 | 43.9297 | 59.8258 | -3335.3832
2044-03-03 03:01 | -10810.3 | 6.108 | 44.1837 | 59.8258 | -3168.1862
2044-03-04 04:01 | -11203.3 | 6.108 | 43.8157 | 59.8258 | -3283.3631
2044-03-05 05:01 | -10772.3 | 6.108 | 44.0179 | 59.8258 | -3157.0495
2044-03-06 06:01 | -9916.75 | 6.108 | 44.6002 | 59.8258 | -2906.3125
2044-03-07 07:01 | -11020.3 | 6.108 | 43.8336 | 59.8258 | -3229.7311
2044-03-08 08:01 | -10480 | 6.108 | 44.0793 | 59.8258 | -3071.3848
2044-03-09 09:01 | -8595.43 | 6.108 | 45.452 | 59.8258 | -2519.0719
2044-03-10 10:01 | -7608.76 | 6.108 | 46.42 | 59.8258 | -2229.9074
2044-03-11 11:01 | -5805.49 | 6.108 | 48.005 | 59.8258 | -1701.4212
2044-03-12 12:01 | -5103.95 | 6.108 | 48.8666 | 59.8258 | -1495.8201
2044-03-13 13:01 | -5818.4 | 6.108 | 48.6493 | 59.8258 | -1705.2047
2044-03-14 14:01 | -4499.06 | 6.108 | 49.7482 | 59.8258 | -1318.5443
2044-03-15 15:01 | -4496.05 | 6.108 | 50.0092 | 59.8258 | -1317.6622
2044-03-16 16:01 | -4231.67 | 6.108 | 50.3961 | 59.8258 | -1240.1801
2044-03-17 17:01 | -5352.56 | 6.108 | 49.6945 | 59.8258 | -1568.6805
2044-03-18 18:01 | -5533.44 | 6.108 | 49.5016 | 59.8258 | -1621.6912
2044-03-19 19:01 | -6629.73 | 6.108 | 48.6926 | 59.8258 | -1942.9821
2044-03-20 20:01 | -6852.67 | 6.108 | 48.4022 | 59.8258 | -2008.3193
2044-03-21 21:01 | -8384.82 | 6.108 | 47.1568 | 59.8258 | -2457.3482
2044-03-22 22:01 | -8580.36 | 6.108 | 46.7393 | 59.8258 | -2514.6553
2044-03-23 23:01 | -9493.24 | 6.108 | 45.8689 | 59.8258 | -2782.194
2044-03-25 00:01 | -10118 | 6.108 | 45.1511 | 59.8258 | -2965.2931
2044-03-26 01:01 | -10282.6 | 6.108 | 44.7884 | 59.8258 | -3013.5326
2044-03-27 02:01 | -10522.8 | 6.108 | 44.4064 | 59.8258 | -3083.9283
2044-03-28 03:01 | -10339.1 | 6.108 | 44.3737 | 59.8258 | -3030.0911
2044-03-29 04:01 | -9908.95 | 6.108 | 44.5761 | 59.8258 | -2904.0266
2044-03-30 05:01 | -9575.53 | 6.108 | 44.794 | 59.8258 | -2806.3108
2044-03-31 06:01 | -8877.8 | 6.108 | 45.3108 | 59.8258 | -2601.8263
2044-04-01 07:01 | -8495.86 | 6.108 | 45.6757 | 59.8258 | -2489.8908
2044-04-02 08:01 | -8204.62 | 6.108 | 45.974 | 59.8258 | -2404.5368
2044-04-03 09:01 | -8327.31 | 6.108 | 45.9566 | 59.8258 | -2440.4937
2044-04-04 10:01 | -7424.06 | 6.108 | 46.6457 | 59.8258 | -2175.7772
2044-04-05 11:01 | -7170.09 | 6.108 | 46.9594 | 59.8258 | -2101.3459
2044-04-06 12:01 | -6657.14 | 6.108 | 47.4356 | 59.8258 | -1951.0151
2044-04-07 13:01 | -5741.72 | 6.108 | 48.2354 | 59.8258 | -1682.732
2044-04-08 14:01 | -5407.78 | 6.108 | 48.6774 | 59.8258 | -1584.8639
2044-04-09 15:01 | -3312.66 | 6.108 | 50.4166 | 59.8258 | -970.8448
2044-04-10 16:01 | -3130.06 | 6.108 | 50.9295 | 59.8258 | -917.33
2044-04-11 17:01 | -3497.5 | 6.108 | 50.9267 | 59.8258 | -1025.0161
2044-04-12 18:01 | -3302.89 | 6.108 | 51.1933 | 59.8258 | -967.9815
2044-04-13 19:01 | -4177.13 | 6.108 | 50.6861 | 59.8258 | -1224.196
2044-04-14 20:01 | -4867.21 | 6.108 | 50.1898 | 59.8258 | -1426.4384
2044-04-15 21:01 | -6058.56 | 6.108 | 49.2351 | 59.8258 | -1775.5887
2044-04-16 22:01 | -6454.15 | 6.108 | 48.7722 | 59.8258 | -1891.5246
2044-04-17 23:01 | -7330.76 | 6.108 | 48.0035 | 59.8258 | -2148.4337
2044-04-19 00:01 | -8042.39 | 6.108 | 47.2959 | 59.8258 | -2356.9918
2044-04-20 01:01 | -8435.28 | 6.108 | 46.8056 | 59.8258 | -2472.1365
2044-04-21 02:01 | -8677.5 | 6.108 | 46.4606 | 59.8258 | -2543.1242
2044-04-22 03:01 | -8625.32 | 6.108 | 46.3516 | 59.8258 | -2527.8318
2044-04-23 04:01 | -8841.98 | 6.108 | 46.0813 | 59.8258 | -2591.3285
2044-04-24 05:01 | -8721.11 | 6.108 | 46.0607 | 59.8258 | -2555.905
2044-04-25 06:01 | -9036.38 | 6.108 | 45.7467 | 59.8258 | -2648.3016
2044-04-26 07:01 | -8349.92 | 6.108 | 46.1633 | 59.8258 | -2447.12
2044-04-27 08:01 | -7174.79 | 6.108 | 47.0651 | 59.8258 | -2102.7234
2044-04-28 09:01 | -6156.22 | 6.108 | 47.9888 | 59.8258 | -1804.21
2044-04-29 10:01 | -4956.78 | 6.108 | 49.0943 | 59.8258 | -1452.6888
2044-04-30 11:01 | -3846.15 | 6.108 | 50.1959 | 59.8258 | -1127.1953
2044-05-01 12:01 | -2238.45 | 6.108 | 51.7268 | 59.8258 | -656.0249
2044-05-02 13:01 | -3111.6 | 6.108 | 51.4966 | 59.8258 | -911.9199
2044-05-03 14:01 | -3317.84 | 6.108 | 51.4855 | 59.8258 | -972.3629
2044-05-04 15:01 | -3196.16 | 6.108 | 51.6507 | 59.8258 | -936.702
2044-05-05 16:01 | -3142.51 | 6.108 | 51.7967 | 59.8258 | -920.9788
2044-05-06 17:01 | -1591.22 | 5.0402 | 52.7994 | 59.8258 | -466.3405
2044-05-07 18:01 | -1757.02 | 5.5944 | 53.0745 | 59.8258 | -514.9317
2044-05-08 19:01 | -1865.15 | 5.8653 | 53.2328 | 59.8258 | -546.6215
2044-05-09 20:01 | -2104.24 | 6.108 | 53.2255 | 59.8258 | -616.6919
2044-05-10 21:01 | -2332.43 | 6.108 | 53.1466 | 59.8258 | -683.5678
2044-05-11 22:01 | -2251.45 | 6.108 | 53.2747 | 59.8258 | -659.8349
2044-05-12 23:01 | -2122.39 | 6.108 | 53.4333 | 59.8258 | -622.0111
2044-05-14 00:01 | -3315.49 | 6.108 | 52.6139 | 59.8258 | -971.6742
2044-05-15 01:01 | -3213.15 | 6.108 | 52.6064 | 59.8258 | -941.6813
2044-05-16 02:01 | -3623.05 | 6.108 | 52.3034 | 59.8258 | -1061.8111
2044-05-17 03:01 | -3627 | 6.108 | 52.287 | 59.8258 | -1062.9688
2044-05-18 04:01 | -3639.68 | 6.108 | 52.2812 | 59.8258 | -1066.6849
2044-05-19 05:01 | -4468.08 | 6.108 | 51.654 | 59.8258 | -1309.465
2044-05-20 06:01 | -5607.17 | 6.108 | 50.7078 | 59.8258 | -1643.2993
2044-05-21 07:01 | -5547.9 | 6.108 | 50.5444 | 59.8258 | -1625.929
2044-05-22 08:01 | -5776.61 | 6.108 | 50.2715 | 59.8258 | -1692.9573
2044-05-23 09:01 | -7245.59 | 6.108 | 49.0697 | 59.8258 | -2123.4728
2044-05-24 10:01 | -7599.93 | 6.108 | 48.5 | 59.8258 | -2227.3196
2044-05-25 11:01 | -7248.14 | 6.108 | 48.5137 | 59.8258 | -2124.2201
2044-05-26 12:01 | -6929.82 | 6.108 | 48.6506 | 59.8258 | -2030.9298
2044-05-27 13:01 | -5702 | 6.108 | 49.5056 | 59.8258 | -1671.0912
2044-05-28 14:01 | -7105.98 | 6.108 | 48.5338 | 59.8258 | -2082.5572
2044-05-29 15:01 | -7276.02 | 6.108 | 48.2376 | 59.8258 | -2132.391
2044-05-30 16:01 | -7249.74 | 6.108 | 48.1125 | 59.8258 | -2124.6891
2044-05-31 17:01 | -6049.78 | 6.108 | 48.9258 | 59.8258 | -1773.0155
2044-06-01 18:01 | -6690.13 | 6.108 | 48.5335 | 59.8258 | -1960.6836
2044-06-02 19:01 | -7107.53 | 6.108 | 48.1254 | 59.8258 | -2083.0114
2044-06-03 20:01 | -7498.92 | 6.108 | 47.7144 | 59.8258 | -2197.7165
2044-06-04 21:01 | -7874.82 | 6.108 | 47.3356 | 59.8258 | -2307.8819
2044-06-05 22:01 | -8075.9 | 6.108 | 47.0785 | 59.8258 | -2366.8127
2044-06-06 23:01 | -8105.67 | 6.108 | 46.9309 | 59.8258 | -2375.5374
2044-06-08 00:01 | -9079.68 | 6.108 | 46.1155 | 59.8258 | -2660.9915
2044-06-09 01:01 | -9427.38 | 6.108 | 45.6405 | 59.8258 | -2762.8923
2044-06-10 02:01 | -9577.23 | 6.108 | 45.3535 | 59.8258 | -2806.809
2044-06-11 03:01 | -9710.8 | 6.108 | 45.1219 | 59.8258 | -2845.9545
2044-06-12 04:01 | -9325.3 | 6.108 | 45.2894 | 59.8258 | -2732.9756
2044-06-13 05:01 | -9328.94 | 6.108 | 45.2219 | 59.8258 | -2734.0424
2044-06-14 06:01 | -8705.01 | 6.108 | 45.6441 | 59.8258 | -2551.1866
2044-06-15 07:01 | -8815.95 | 6.108 | 45.5981 | 59.8258 | -2583.6999
2044-06-16 08:01 | -8642.3 | 6.108 | 45.7169 | 59.8258 | -2532.8081
2044-06-17 09:01 | -9005.4 | 6.108 | 45.4504 | 59.8258 | -2639.2222
2044-06-18 10:01 | -8726.28 | 6.108 | 45.5987 | 59.8258 | -2557.4202
2044-06-19 11:01 | -8113.42 | 6.108 | 46.043 | 59.8258 | -2377.8087
2044-06-20 12:01 | -7369.39 | 6.108 | 46.6555 | 59.8258 | -2159.755
2044-06-21 13:01 | -6694.4 | 6.108 | 47.276 | 59.8258 | -1961.935
2044-06-22 14:01 | -6061.16 | 6.108 | 47.8975 | 59.8258 | -1776.3506
2044-06-23 15:01 | -5017.03 | 6.108 | 48.8607 | 59.8258 | -1470.3464
2044-06-24 16:01 | -5110.81 | 6.108 | 49.0415 | 59.8258 | -1497.8306
2044-06-25 17:01 | -5980.62 | 6.108 | 48.5204 | 59.8258 | -1752.7467
2044-06-26 18:01 | -6115.6 | 6.108 | 48.3822 | 59.8258 | -1792.3054
2044-06-27 19:01 | -6889.05 | 6.108 | 47.7907 | 59.8258 | -2018.9813
2044-06-28 20:01 | -7395.97 | 6.108 | 47.3172 | 59.8258 | -2167.5448
2044-06-29 21:01 | -8406.53 | 6.108 | 46.43 | 59.8258 | -2463.7107
2044-06-30 22:01 | -8443.85 | 6.108 | 46.191 | 59.8258 | -2474.6482
2044-07-01 23:01 | -9650.21 | 6.108 | 45.1585 | 59.8258 | -2828.1974
2044-07-03 00:01 | -10147.1 | 6.108 | 44.5341 | 59.8258 | -2973.8215
2044-07-04 01:01 | -10059.2 | 6.108 | 44.3659 | 59.8258 | -2948.0605
2044-07-05 02:01 | -10653.4 | 6.108 | 43.7745 | 59.8258 | -3122.2033
2044-07-06 03:01 | -10960.2 | 6.108 | 43.3394 | 59.8258 | -3212.1175
2044-07-07 04:01 | -10945.6 | 6.108 | 43.1349 | 59.8258 | -3207.8387
2044-07-08 05:01 | -11138.5 | 6.108 | 42.8547 | 59.8258 | -3264.3721
2044-07-09 06:01 | -10889.7 | 6.108 | 42.9015 | 59.8258 | -3191.456
2044-07-10 07:01 | -10668.3 | 6.108 | 42.9804 | 59.8258 | -3126.5701
2044-07-11 08:01 | -9408.44 | 6.108 | 43.8824 | 59.8258 | -2757.3416
2044-07-12 09:01 | -8916.03 | 6.108 | 44.3843 | 59.8258 | -2613.0305
2044-07-13 10:01 | -7606.46 | 6.108 | 45.4838 | 59.8258 | -2229.2334
2044-07-14 11:01 | -5884.1 | 6.108 | 47.0149 | 59.8258 | -1724.4595
2044-07-15 12:01 | -4247.35 | 6.108 | 48.6162 | 59.8258 | -1244.7754
2044-07-16 13:01 | -3229.11 | 6.108 | 49.8164 | 59.8258 | -946.3587
2044-07-17 14:01 | -2939.79 | 6.108 | 50.433 | 59.8258 | -861.5674
2044-07-18 15:01 | -3506.22 | 6.108 | 50.3157 | 59.8258 | -1027.5716
2044-07-19 16:01 | -4429.82 | 6.108 | 49.7703 | 59.8258 | -1298.2521
2044-07-20 17:01 | -3601.35 | 6.108 | 50.402 | 59.8258 | -1055.4515
2044-07-21 18:01 | -4468.84 | 6.108 | 49.911 | 59.8258 | -1309.6877
2044-07-22 19:01 | -5370.05 | 6.108 | 49.2407 | 59.8258 | -1573.8063
2044-07-23 20:01 | -5997.55 | 6.108 | 48.6578 | 59.8258 | -1757.7084
2044-07-24 21:01 | -6640.05 | 6.108 | 48.0759 | 59.8258 | -1946.0066
2044-07-25 22:01 | -6860.41 | 6.108 | 47.7986 | 59.8258 | -2010.5877
2044-07-26 23:01 | -7199.17 | 6.108 | 47.4314 | 59.8258 | -2109.8685
2044-07-28 00:01 | -8541.27 | 6.108 | 46.3063 | 59.8258 | -2503.1991
2044-07-29 01:01 | -8828.55 | 6.108 | 45.8246 | 59.8258 | -2587.3926
2044-07-30 02:01 | -8777.61 | 6.108 | 45.6642 | 59.8258 | -2572.4636
2044-07-31 03:01 | -9136.81 | 6.108 | 45.289 | 59.8258 | -2677.7347
2044-08-01 04:01 | -9136.06 | 6.108 | 45.1561 | 59.8258 | -2677.5149
2044-08-02 05:01 | -9043.72 | 6.108 | 45.111 | 59.8258 | -2650.4527
2044-08-03 06:01 | -8821.08 | 6.108 | 45.2269 | 59.8258 | -2585.2034
2044-08-04 07:01 | -8700.12 | 6.108 | 45.3067 | 59.8258 | -2549.7535
2044-08-05 08:01 | -7642.63 | 6.108 | 46.0874 | 59.8258 | -2239.8338
2044-08-06 09:01 | -6522.17 | 6.108 | 47.0593 | 59.8258 | -1911.4593
2044-08-07 10:01 | -5254.97 | 6.108 | 48.2206 | 59.8258 | -1540.0797
2044-08-08 11:01 | -4500.64 | 6.108 | 49.0559 | 59.8258 | -1319.0074
2044-08-09 12:01 | -3959.79 | 6.108 | 49.7172 | 59.8258 | -1160.4999
2044-08-10 13:01 | -2479.39 | 6.108 | 51.0632 | 59.8258 | -726.6375
2044-08-11 14:01 | -1896.45 | 6.064 | 51.8438 | 59.8258 | -555.7946
2044-08-12 15:01 | -1503.62 | 4.7486 | 52.1331 | 59.8258 | -440.6675
2044-08-13 16:01 | -1435.21 | 4.6541 | 52.4263 | 59.8258 | -420.6185
2044-08-14 17:01 | -3032.27 | 6.108 | 51.7676 | 59.8258 | -888.6706
2044-08-15 18:01 | -3583.95 | 6.108 | 51.3089 | 59.8258 | -1050.3521
2044-08-16 19:01 | -4465.89 | 6.108 | 50.5891 | 59.8258 | -1308.8232
2044-08-17 20:01 | -4880.08 | 6.108 | 50.1655 | 59.8258 | -1430.2103
2044-08-18 21:01 | -6110.6 | 6.108 | 49.1282 | 59.8258 | -1790.8401
2044-08-19 22:01 | -6972.02 | 6.108 | 48.2372 | 59.8258 | -2043.2974
2044-08-20 23:01 | -7712.8 | 6.108 | 47.437 | 59.8258 | -2260.3985
2044-08-22 00:01 | -8115.86 | 6.108 | 46.8982 | 59.8258 | -2378.5238
2044-08-23 01:01 | -8144.95 | 6.108 | 46.6625 | 59.8258 | -2387.0492
2044-08-24 02:01 | -8368.08 | 6.108 | 46.3312 | 59.8258 | -2452.4422
2044-08-25 03:01 | -8455.32 | 6.108 | 46.1134 | 59.8258 | -2478.0097
2044-08-26 04:01 | -8645.55 | 6.108 | 45.8389 | 59.8258 | -2533.7606
2044-08-27 05:01 | -8722.65 | 6.108 | 45.6722 | 59.8258 | -2556.3564
2044-08-28 06:01 | -8511.74 | 6.108 | 45.7405 | 59.8258 | -2494.5447
2044-08-29 07:01 | -8586.65 | 6.108 | 45.6435 | 59.8258 | -2516.4987
2044-08-30 08:01 | -7773.29 | 6.108 | 46.1949 | 59.8258 | -2278.1264
2044-08-31 09:01 | -7123.86 | 6.108 | 46.7444 | 59.8258 | -2087.7973
2044-09-01 10:01 | -5602.13 | 6.108 | 47.9979 | 59.8258 | -1641.8222
2044-09-02 11:01 | -4300.68 | 6.108 | 49.2294 | 59.8258 | -1260.4049
2044-09-03 12:01 | -3040.2 | 6.108 | 50.4892 | 59.8258 | -890.9947
2044-09-04 13:01 | -2526.51 | 6.108 | 51.2228 | 59.8258 | -740.447
2044-09-05 14:01 | -1888.9 | 6.0315 | 51.9664 | 59.8258 | -553.5819
2044-09-06 15:01 | -1972.63 | 6.108 | 52.2052 | 59.8258 | -578.1208
2044-09-07 16:01 | -2111.63 | 6.108 | 52.2876 | 59.8258 | -618.8577
2044-09-08 17:01 | -3647.28 | 6.108 | 51.2633 | 59.8258 | -1068.9123
2044-09-09 18:01 | -4230.75 | 6.108 | 50.7268 | 59.8258 | -1239.9104
2044-09-10 19:01 | -4888.39 | 6.108 | 50.1458 | 59.8258 | -1432.6457
2044-09-11 20:01 | -5890.68 | 6.108 | 49.283 | 59.8258 | -1726.3879
2044-09-12 21:01 | -6816.72 | 6.108 | 48.4017 | 59.8258 | -1997.7834
2044-09-13 22:01 | -7356.23 | 6.108 | 47.7556 | 59.8258 | -2155.8982
2044-09-14 23:01 | -8215.61 | 6.108 | 46.9095 | 59.8258 | -2407.7576
2044-09-16 00:01 | -8685.99 | 6.108 | 46.3063 | 59.8258 | -2545.6124
2044-09-17 01:01 | -8606.25 | 6.108 | 46.1318 | 59.8258 | -2522.2429
2044-09-18 02:01 | -8772.8 | 6.108 | 45.8579 | 59.8258 | -2571.0539
2044-09-19 03:01 | -8913.63 | 6.108 | 45.6151 | 59.8258 | -2612.3271
2044-09-20 04:01 | -8744.68 | 6.108 | 45.6077 | 59.8258 | -2562.8127
2044-09-21 05:01 | -8883.3 | 6.108 | 45.4436 | 59.8258 | -2603.4382
2044-09-22 06:01 | -8473.7 | 6.108 | 45.6816 | 59.8258 | -2483.3963
2044-09-23 07:01 | -8421.06 | 6.108 | 45.7171 | 59.8258 | -2467.9691
2044-09-24 08:01 | -7072.7 | 6.108 | 46.7224 | 59.8258 | -2072.8038
2044-09-25 09:01 | -6145.48 | 6.108 | 47.5867 | 59.8258 | -1801.0624
2044-09-26 10:01 | -3996.12 | 6.108 | 49.4046 | 59.8258 | -1171.1472
2044-09-27 11:01 | -2433.61 | 6.108 | 50.976 | 59.8258 | -713.2207
2044-09-28 12:01 | -1105.24 | 3.511 | 51.7978 | 59.8258 | -323.9139
2044-09-29 13:01 | -418.93 | 1.5807 | 52.4749 | 59.8258 | -122.7763
2044-09-30 14:01 | -172.45 | 1.005 | 53.2835 | 59.8258 | -50.5401
2044-10-01 15:01 | 0 | 0 | 54.3793 | 59.8258 | 0
2044-10-02 16:01 | -300.609 | 1.49 | 53.6934 | 59.8258 | -88.0998
2044-10-03 17:01 | -1398.68 | 4.7994 | 53.4486 | 59.8258 | -409.9126
2044-10-04 18:01 | -1889.04 | 6.017 | 53.3419 | 59.8258 | -553.623
2044-10-05 19:01 | -2934.61 | 6.108 | 52.5725 | 59.8258 | -860.0493
2044-10-06 20:01 | -3342.15 | 6.108 | 52.1689 | 59.8258 | -979.4875
2044-10-07 21:01 | -4810.69 | 6.108 | 50.9875 | 59.8258 | -1409.8741
2044-10-08 22:01 | -5346.44 | 6.108 | 50.3505 | 59.8258 | -1566.8869
2044-10-09 23:01 | -5977.4 | 6.108 | 49.6841 | 59.8258 | -1751.803
2044-10-11 00:01 | -6729.36 | 6.108 | 48.9221 | 59.8258 | -1972.1807
2044-10-12 01:01 | -6965.65 | 6.108 | 48.5139 | 59.8258 | -2041.4305
2044-10-13 02:01 | -7115.56 | 6.108 | 48.2128 | 59.8258 | -2085.3648
2044-10-14 03:01 | -7196.23 | 6.108 | 48.0156 | 59.8258 | -2109.0068
2044-10-15 04:01 | -7718.78 | 6.108 | 47.507 | 59.8258 | -2262.1511
2044-10-16 05:01 | -8157.56 | 6.108 | 47.0263 | 59.8258 | -2390.7448
2044-10-17 06:01 | -8503.29 | 6.108 | 46.6067 | 59.8258 | -2492.0683
2044-10-18 07:01 | -7400.68 | 6.108 | 47.289 | 59.8258 | -2168.9252
2044-10-19 08:01 | -6727.11 | 6.108 | 47.8331 | 59.8258 | -1971.5213
2044-10-20 09:01 | -6295.31 | 6.108 | 48.2461 | 59.8258 | -1844.9732
2044-10-21 10:01 | -6241.48 | 6.108 | 48.3555 | 59.8258 | -1829.1972
2044-10-22 11:01 | -5590.77 | 6.108 | 48.8735 | 59.8258 | -1638.4929
2044-10-23 12:01 | -5316.7 | 6.108 | 49.1831 | 59.8258 | -1558.171
2044-10-24 13:01 | -5094.4 | 6.108 | 49.4213 | 59.8258 | -1493.0213
2044-10-25 14:01 | -4998.82 | 6.108 | 49.5398 | 59.8258 | -1465.0095
2044-10-26 15:01 | -4736.06 | 6.108 | 49.7638 | 59.8258 | -1388.0022
2044-10-27 16:01 | -4460.48 | 6.108 | 50.0289 | 59.8258 | -1307.2376
2044-10-28 17:01 | -2860.83 | 6.108 | 51.3072 | 59.8258 | -838.4265
2044-10-29 18:01 | -3253.64 | 6.108 | 51.289 | 59.8258 | -953.5478
2044-10-30 19:01 | -3386.79 | 6.108 | 51.3028 | 59.8258 | -992.5702
2044-10-31 20:01 | -3614.5 | 6.108 | 51.1917 | 59.8258 | -1059.3054
2044-11-01 21:01 | -3729.23 | 6.108 | 51.1579 | 59.8258 | -1092.9294
2044-11-02 22:01 | -3915.41 | 6.108 | 51.0709 | 59.8258 | -1147.4934
2044-11-03 23:01 | -4016.41 | 6.108 | 51.0007 | 59.8258 | -1177.0936
2044-11-05 00:01 | -5389.07 | 6.108 | 49.991 | 59.8258 | -1579.3805
2044-11-06 01:01 | -5597.35 | 6.108 | 49.6796 | 59.8258 | -1640.4214
2044-11-07 02:01 | -5670.88 | 6.108 | 49.5295 | 59.8258 | -1661.9709
2044-11-08 03:01 | -5713.48 | 6.108 | 49.453 | 59.8258 | -1674.4557
2044-11-09 04:01 | -5943.99 | 6.108 | 49.2447 | 59.8258 | -1742.0115
2044-11-10 05:01 | -5719.25 | 6.108 | 49.3381 | 59.8258 | -1676.1467
2044-11-11 06:01 | -5667.89 | 6.108 | 49.3838 | 59.8258 | -1661.0946
2044-11-12 07:01 | -4977.06 | 6.108 | 49.9108 | 59.8258 | -1458.6323
2044-11-13 08:01 | -4354.13 | 6.108 | 50.4655 | 59.8258 | -1276.0695
2044-11-14 09:01 | -4744.18 | 6.108 | 50.2989 | 59.8258 | -1390.3819
2044-11-15 10:01 | -3810.41 | 6.108 | 51.0102 | 59.8258 | -1116.7209
2044-11-16 11:01 | -3382.92 | 6.108 | 51.457 | 59.8258 | -991.436
2044-11-17 12:01 | -2889.61 | 6.108 | 51.9788 | 59.8258 | -846.8611
2044-11-18 13:01 | -2252.1 | 6.108 | 52.6013 | 59.8258 | -660.0254
2044-11-19 14:01 | -2085.27 | 6.108 | 52.9 | 59.8258 | -611.1323
2044-11-20 15:01 | -1321.84 | 4.1127 | 53.1378 | 59.8258 | -387.3931
2044-11-21 16:01 | -1471.98 | 4.7732 | 53.4007 | 59.8258 | -431.3948
2044-11-22 17:01 | -498.412 | 1.6726 | 53.5598 | 59.8258 | -146.0701
2044-11-23 18:01 | -1040.44 | 3.6498 | 53.846 | 59.8258 | -304.9229
2044-11-24 19:01 | -1400.81 | 4.572 | 53.8321 | 59.8258 | -410.5369
2044-11-25 20:01 | -2146.17 | 6.108 | 53.6516 | 59.8258 | -628.9803
2044-11-26 21:01 | -2519.57 | 6.108 | 53.3263 | 59.8258 | -738.4131
2044-11-27 22:01 | -2784.61 | 6.108 | 53.0825 | 59.8258 | -816.0886
2044-11-28 23:01 | -3299.64 | 6.108 | 52.639 | 59.8258 | -967.029
2044-11-30 00:01 | -4583.98 | 6.108 | 51.5941 | 59.8258 | -1343.4319
2044-12-01 01:01 | -4642.03 | 6.108 | 51.3331 | 59.8258 | -1360.4447
2044-12-02 02:01 | -4694.83 | 6.108 | 51.1768 | 59.8258 | -1375.9189
2044-12-03 03:01 | -4625.39 | 6.108 | 51.153 | 59.8258 | -1355.568
2044-12-04 04:01 | -4480.3 | 6.108 | 51.2115 | 59.8258 | -1313.0463
2044-12-05 05:01 | -3988.42 | 6.108 | 51.5494 | 59.8258 | -1168.8905
2044-12-06 06:01 | -3777.61 | 6.108 | 51.77 | 59.8258 | -1107.1082
2044-12-07 07:01 | -4072.17 | 6.108 | 51.6053 | 59.8258 | -1193.4352
2044-12-08 08:01 | -2988.39 | 6.108 | 52.4074 | 59.8258 | -875.8107
2044-12-09 09:01 | -3611.54 | 6.108 | 52.092 | 59.8258 | -1058.4379
2044-12-10 10:01 | -3101.22 | 6.108 | 52.4798 | 59.8258 | -908.8779
2044-12-11 11:01 | -2335.12 | 6.108 | 53.1157 | 59.8258 | -684.3561
2044-12-12 12:01 | -1202.97 | 3.7276 | 53.5478 | 59.8258 | -352.5557
2044-12-13 13:01 | -1022.11 | 3.3862 | 53.9007 | 59.8258 | -299.5509
2044-12-14 14:01 | -1342.37 | 4.4037 | 54.0544 | 59.8258 | -393.4098
2044-12-15 15:01 | 0 | 1 | 55.5329 | 59.8258 | 0
2044-12-16 16:01 | 2875.95 | 1 | 55.5448 | 59.8258 | 842.8577
2044-12-17 17:01 | 0 | 0 | 56.3576 | 59.8258 | 0
2044-12-18 18:01 | -154.526 | 0.94808 | 55.5435 | 59.8258 | -45.2871
2044-12-19 19:01 | -698.194 | 2.6195 | 55.0514 | 59.8258 | -204.6205
2044-12-20 20:01 | -1052.01 | 3.5435 | 54.9303 | 59.8258 | -308.3137
2044-12-21 21:01 | -2299.71 | 6.108 | 54.5556 | 59.8258 | -673.9785
2044-12-22 22:01 | -2633.25 | 6.108 | 54.0911 | 59.8258 | -771.7294
2044-12-23 23:01 | -3504.78 | 6.108 | 53.3227 | 59.8258 | -1027.1496
[5 empty] | 2505779.7385 | 286.0479

## Atlanta
| Property | Soil |  |  |  |  | Property | Soil
| Thermal conductivity [W/m K] | 1.72 |  | W/M-K | 0.57779 | BTU/HR-FT-R | Thermal conductivity [Btu/Hr-ft-R] | 0.99379
| Specific heat [J/kg K] | 1900
| Density [kg/m3] | 1300
| Volumeric specific heat [MJ/K-M3] | 2.47
| Thermal diffusivity [m2/hr] | 0.0025069 |  | m2/hr | 10.7639 | ft2/hr | Thermal diffusivity [ft2/hr] | 0.026984
VBGHE design and performance
| Borehole number | 2
| Borehole depth | 240 | ft | 73 | m
| Annual Max. LFT | 94.6 | F
| Annual Min. LFT | 47.5 | F
Time | Thermal load | Fluid flow | Outlet temperature | Far field ground temperature | Load
| Btu/hr | GPM | F | F | W
2020-01-01 | -4775.44 | 6.4446 | 61.2579 | 64.1561 | -1399.5433
2020-01-02 01:00 | -4508.17 | 6.4446 | 60.8744 | 64.1561 | -1321.2142
2020-01-03 02:00 | -4554.44 | 6.4446 | 60.558 | 64.1561 | -1334.7746
2020-01-04 03:00 | -4535.18 | 6.4446 | 60.4005 | 64.1561 | -1329.1301
2020-01-05 04:00 | -4517.4 | 6.4446 | 60.2389 | 64.1561 | -1323.9193
2020-01-06 05:00 | -4554.31 | 6.4446 | 60.0464 | 64.1561 | -1334.7365
2020-01-07 06:00 | -4536.61 | 6.4446 | 59.9724 | 64.1561 | -1329.5491
2020-01-08 07:00 | -3771.35 | 6.4446 | 60.3506 | 64.1561 | -1105.2736
2020-01-09 08:00 | -3230.99 | 6.4446 | 60.6809 | 64.1561 | -946.9097
2020-01-10 09:00 | -3576.56 | 6.4446 | 60.4977 | 64.1561 | -1048.1863
2020-01-11 10:00 | -3522.52 | 6.4446 | 60.4695 | 64.1561 | -1032.3487
2020-01-12 11:00 | -2770.21 | 6.4446 | 60.8731 | 64.1561 | -811.8684
2020-01-13 12:00 | -2541.36 | 6.4446 | 61.0974 | 64.1561 | -744.7991
2020-01-14 13:00 | -2689 | 6.4446 | 61.0648 | 64.1561 | -788.0681
2020-01-15 14:00 | -2658.69 | 6.4446 | 61.0809 | 64.1561 | -779.1851
2020-01-16 15:00 | -3438.36 | 6.4446 | 60.6157 | 64.1561 | -1007.6838
2020-01-17 16:00 | -3868.38 | 6.4446 | 60.275 | 64.1561 | -1133.7103
2020-01-18 17:00 | -2680.06 | 6.4446 | 60.8902 | 64.1561 | -785.4481
2020-01-19 18:00 | -3229.08 | 6.4446 | 60.6248 | 64.1561 | -946.3499
2020-01-20 19:00 | -3602.66 | 6.4446 | 60.3543 | 64.1561 | -1055.8354
2020-01-21 20:00 | -4058.6 | 6.4446 | 59.9773 | 64.1561 | -1189.4582
2020-01-22 21:00 | -4388.4 | 6.4446 | 59.6764 | 64.1561 | -1286.1131
2020-01-23 22:00 | -4670.33 | 6.4446 | 59.4069 | 64.1561 | -1368.7386
2020-01-24 23:00 | -4903.81 | 6.4446 | 59.1336 | 64.1561 | -1437.1648
2020-01-26 | -6111.8 | 6.4446 | 58.2954 | 64.1561 | -1791.1918
2020-01-27 01:00 | -6521.59 | 6.4446 | 57.8297 | 64.1561 | -1911.2894
2020-01-28 02:00 | -6622.43 | 6.4446 | 57.5782 | 64.1561 | -1940.8426
2020-01-29 03:00 | -6578.79 | 6.4446 | 57.4709 | 64.1561 | -1928.053
2020-01-30 04:00 | -6543.77 | 6.4446 | 57.3894 | 64.1561 | -1917.7897
2020-01-31 05:00 | -6281.91 | 6.4446 | 57.4439 | 64.1561 | -1841.0461
2020-02-01 06:00 | -5867.07 | 6.4446 | 57.6467 | 64.1561 | -1719.4685
2020-02-02 07:00 | -5925.67 | 6.4446 | 57.6035 | 64.1561 | -1736.6424
2020-02-03 08:00 | -5730.25 | 6.4446 | 57.6842 | 64.1561 | -1679.3705
2020-02-04 09:00 | -5781.87 | 6.4446 | 57.632 | 64.1561 | -1694.4988
2020-02-05 10:00 | -5473.13 | 6.4446 | 57.787 | 64.1561 | -1604.0161
2020-02-06 11:00 | -4610.56 | 6.4446 | 58.3045 | 64.1561 | -1351.2218
2020-02-07 12:00 | -2322.89 | 6.4446 | 59.7758 | 64.1561 | -680.7719
2020-02-08 13:00 | -1524.11 | 4.3218 | 60.1027 | 64.1561 | -446.6725
2020-02-09 14:00 | -2468.4 | 6.4446 | 60.2392 | 64.1561 | -723.4166
2020-02-10 15:00 | -3269.28 | 6.4446 | 59.7989 | 64.1561 | -958.1314
2020-02-11 16:00 | -2624.97 | 6.4446 | 60.1622 | 64.1561 | -769.3028
2020-02-12 17:00 | -2708.93 | 6.4446 | 60.1978 | 64.1561 | -793.909
2020-02-13 18:00 | -2656.76 | 6.4446 | 60.2538 | 64.1561 | -778.6195
2020-02-14 19:00 | -3345 | 6.4446 | 59.8389 | 64.1561 | -980.3227
2020-02-15 20:00 | -3876.76 | 6.4446 | 59.4583 | 64.1561 | -1136.1662
2020-02-16 21:00 | -4740.19 | 6.4446 | 58.8639 | 64.1561 | -1389.2126
2020-02-17 22:00 | -5207.76 | 6.4446 | 58.4422 | 64.1561 | -1526.2438
2020-02-18 23:00 | -6178.24 | 6.4446 | 57.7123 | 64.1561 | -1810.6634
2020-02-20 | -6381.13 | 6.4446 | 57.3789 | 64.1561 | -1870.1246
2020-02-21 01:00 | -6470.24 | 6.4446 | 57.1582 | 64.1561 | -1896.2402
2020-02-22 02:00 | -6592.59 | 6.4446 | 56.9645 | 64.1561 | -1932.0974
2020-02-23 03:00 | -6833.62 | 6.4446 | 56.7184 | 64.1561 | -2002.7363
2020-02-24 04:00 | -6623.72 | 6.4446 | 56.7298 | 64.1561 | -1941.2207
2020-02-25 05:00 | -6574.31 | 6.4446 | 56.701 | 64.1561 | -1926.7401
2020-02-26 06:00 | -6248.45 | 6.4446 | 56.8441 | 64.1561 | -1831.2399
2020-02-27 07:00 | -6277.75 | 6.4446 | 56.8071 | 64.1561 | -1839.8269
2020-02-28 08:00 | -6612.2 | 6.4446 | 56.5692 | 64.1561 | -1937.8445
2020-02-29 09:00 | -7487.43 | 6.4446 | 55.9698 | 64.1561 | -2194.3491
2020-03-01 10:00 | -7234.9 | 6.4446 | 55.9714 | 64.1561 | -2120.3399
2020-03-02 11:00 | -6766.33 | 6.4446 | 56.1877 | 64.1561 | -1983.0156
2020-03-03 12:00 | -6770.11 | 6.4446 | 56.1679 | 64.1561 | -1984.1234
2020-03-04 13:00 | -6507.68 | 6.4446 | 56.2776 | 64.1561 | -1907.2127
2020-03-05 14:00 | -6496.34 | 6.4446 | 56.2635 | 64.1561 | -1903.8893
2020-03-06 15:00 | -5904.06 | 6.4446 | 56.6161 | 64.1561 | -1730.3092
2020-03-07 16:00 | -5109.01 | 6.4446 | 57.1431 | 64.1561 | -1497.303
2020-03-08 17:00 | -5120.26 | 6.4446 | 57.2304 | 64.1561 | -1500.6001
2020-03-09 18:00 | -4809.54 | 6.4446 | 57.4549 | 64.1561 | -1409.537
2020-03-10 19:00 | -5218.89 | 6.4446 | 57.2546 | 64.1561 | -1529.5057
2020-03-11 20:00 | -5325.13 | 6.4446 | 57.1836 | 64.1561 | -1560.6415
2020-03-12 21:00 | -6034.25 | 6.4446 | 56.7465 | 64.1561 | -1768.4641
2020-03-13 22:00 | -6160.32 | 6.4446 | 56.5846 | 64.1561 | -1805.4116
2020-03-14 23:00 | -6417.02 | 6.4446 | 56.3668 | 64.1561 | -1880.6429
2020-03-16 | -6831.17 | 6.4446 | 56.0482 | 64.1561 | -2002.0183
2020-03-17 01:00 | -7139.68 | 6.4446 | 55.7688 | 64.1561 | -2092.4337
2020-03-18 02:00 | -7169.12 | 6.4446 | 55.6537 | 64.1561 | -2101.0617
2020-03-19 03:00 | -7059.67 | 6.4446 | 55.6554 | 64.1561 | -2068.985
2020-03-20 04:00 | -6985.34 | 6.4446 | 55.6524 | 64.1561 | -2047.2011
2020-03-21 05:00 | -6781.94 | 6.4446 | 55.7362 | 64.1561 | -1987.5904
2020-03-22 06:00 | -6147.84 | 6.4446 | 56.101 | 64.1561 | -1801.754
2020-03-23 07:00 | -6139.82 | 6.4446 | 56.156 | 64.1561 | -1799.4036
2020-03-24 08:00 | -6310.6 | 6.4446 | 56.0694 | 64.1561 | -1849.4543
2020-03-25 09:00 | -5358.88 | 6.4446 | 56.6363 | 64.1561 | -1570.5327
2020-03-26 10:00 | -4305.12 | 6.4446 | 57.3801 | 64.1561 | -1261.7061
2020-03-27 11:00 | -3010.51 | 6.4446 | 58.3444 | 64.1561 | -882.2934
2020-03-28 12:00 | -2013.47 | 5.8298 | 59.0548 | 64.1561 | -590.0898
2020-03-29 13:00 | -2031.64 | 5.8872 | 59.3119 | 64.1561 | -595.4149
2020-03-30 14:00 | -1798.28 | 5.1966 | 59.4824 | 64.1561 | -527.0238
2020-03-31 15:00 | -2487.52 | 6.4446 | 59.4811 | 64.1561 | -729.0201
2020-04-01 16:00 | -2800.53 | 6.4446 | 59.3294 | 64.1561 | -820.7543
2020-04-02 17:00 | -3205.46 | 6.4446 | 59.0858 | 64.1561 | -939.4276
2020-04-03 18:00 | -3514.84 | 6.4446 | 58.8619 | 64.1561 | -1030.0979
2020-04-04 19:00 | -4432.83 | 6.4446 | 58.265 | 64.1561 | -1299.1342
2020-04-05 20:00 | -4934.54 | 6.4446 | 57.841 | 64.1561 | -1446.1709
2020-04-06 21:00 | -5977.15 | 6.4446 | 57.093 | 64.1561 | -1751.7297
2020-04-07 22:00 | -6401.82 | 6.4446 | 56.6487 | 64.1561 | -1876.1882
2020-04-08 23:00 | -7410.13 | 6.4446 | 55.864 | 64.1561 | -2171.6947
2020-04-10 | -8075.73 | 6.4446 | 55.2265 | 64.1561 | -2366.7628
2020-04-11 01:00 | -8546.9 | 6.4446 | 54.7103 | 64.1561 | -2504.8491
2020-04-12 02:00 | -8737.09 | 6.4446 | 54.3798 | 64.1561 | -2560.5883
2020-04-13 03:00 | -8882.71 | 6.4446 | 54.1229 | 64.1561 | -2603.2653
2020-04-14 04:00 | -9143.68 | 6.4446 | 53.8119 | 64.1561 | -2679.7481
2020-04-15 05:00 | -8910.46 | 6.4446 | 53.8061 | 64.1561 | -2611.398
2020-04-16 06:00 | -8571.6 | 6.4446 | 53.9204 | 64.1561 | -2512.088
2020-04-17 07:00 | -8708.68 | 6.4446 | 53.797 | 64.1561 | -2552.2622
2020-04-18 08:00 | -8315.68 | 6.4446 | 53.9667 | 64.1561 | -2437.0852
2020-04-19 09:00 | -7553.1 | 6.4446 | 54.4142 | 64.1561 | -2213.5951
2020-04-20 10:00 | -6129.24 | 6.4446 | 55.3402 | 64.1561 | -1796.3029
2020-04-21 11:00 | -4418.87 | 6.4446 | 56.5524 | 64.1561 | -1295.043
2020-04-22 12:00 | -3539.49 | 6.4446 | 57.3595 | 64.1561 | -1037.3221
2020-04-23 13:00 | -2627.89 | 6.4446 | 58.1705 | 64.1561 | -770.1585
2020-04-24 14:00 | -2417.9 | 6.4446 | 58.5614 | 64.1561 | -708.6165
2020-04-25 15:00 | -3641.74 | 6.4446 | 58.0263 | 64.1561 | -1067.2886
2020-04-26 16:00 | -3791.73 | 6.4446 | 57.9427 | 64.1561 | -1111.2464
2020-04-27 17:00 | -4255.66 | 6.4446 | 57.6693 | 64.1561 | -1247.2108
2020-04-28 18:00 | -4882.04 | 6.4446 | 57.2677 | 64.1561 | -1430.7847
2020-04-29 19:00 | -5818.04 | 6.4446 | 56.6222 | 64.1561 | -1705.0992
2020-04-30 20:00 | -6510.65 | 6.4446 | 56.0557 | 64.1561 | -1908.0832
2020-05-01 21:00 | -7731.56 | 6.4446 | 55.1743 | 64.1561 | -2265.8966
2020-05-02 22:00 | -8198.38 | 6.4446 | 54.6629 | 64.1561 | -2402.708
2020-05-03 23:00 | -9118.01 | 6.4446 | 53.8992 | 64.1561 | -2672.2249
2020-05-05 | -9599.88 | 6.4446 | 53.3626 | 64.1561 | -2813.4471
2020-05-06 01:00 | -9888.1 | 6.4446 | 52.9588 | 64.1561 | -2897.916
2020-05-07 02:00 | -10088.9 | 6.4446 | 52.6371 | 64.1561 | -2956.7647
2020-05-08 03:00 | -10247.9 | 6.4446 | 52.3808 | 64.1561 | -3003.363
2020-05-09 04:00 | -10139 | 6.4446 | 52.2987 | 64.1561 | -2971.4476
2020-05-10 05:00 | -10586.7 | 6.4446 | 51.9238 | 64.1561 | -3102.6555
2020-05-11 06:00 | -10419.5 | 6.4446 | 51.8825 | 64.1561 | -3053.654
2020-05-12 07:00 | -9650.6 | 6.4446 | 52.261 | 64.1561 | -2828.3117
2020-05-13 08:00 | -9043.73 | 6.4446 | 52.6431 | 64.1561 | -2650.4556
2020-05-14 09:00 | -9304.94 | 6.4446 | 52.533 | 64.1561 | -2727.0087
2020-05-15 10:00 | -8901.24 | 6.4446 | 52.7388 | 64.1561 | -2608.6959
2020-05-16 11:00 | -8353.46 | 6.4446 | 53.0793 | 64.1561 | -2448.1575
2020-05-17 12:00 | -8135.57 | 6.4446 | 53.262 | 64.1561 | -2384.3002
2020-05-18 13:00 | -7956.55 | 6.4446 | 53.3908 | 64.1561 | -2331.8346
2020-05-19 14:00 | -7109.97 | 6.4446 | 53.9103 | 64.1561 | -2083.7265
2020-05-20 15:00 | -7380.04 | 6.4446 | 53.8475 | 64.1561 | -2162.8762
2020-05-21 16:00 | -7398.29 | 6.4446 | 53.8527 | 64.1561 | -2168.2248
2020-05-22 17:00 | -5959.06 | 6.4446 | 54.7287 | 64.1561 | -1746.4281
2020-05-23 18:00 | -6555.68 | 6.4446 | 54.5378 | 64.1561 | -1921.2802
2020-05-24 19:00 | -6873.15 | 6.4446 | 54.376 | 64.1561 | -2014.3214
2020-05-25 20:00 | -7181.59 | 6.4446 | 54.1538 | 64.1561 | -2104.7163
2020-05-26 21:00 | -7342.3 | 6.4446 | 54.0354 | 64.1561 | -2151.8157
2020-05-27 22:00 | -7574.38 | 6.4446 | 53.8793 | 64.1561 | -2219.8317
2020-05-28 23:00 | -7765.83 | 6.4446 | 53.7132 | 64.1561 | -2275.9401
2020-05-30 | -9177.52 | 6.4446 | 52.8113 | 64.1561 | -2689.6656
2020-05-31 01:00 | -9250.04 | 6.4446 | 52.5845 | 64.1561 | -2710.9191
2020-06-01 02:00 | -9468.95 | 6.4446 | 52.3337 | 64.1561 | -2775.0753
2020-06-02 03:00 | -9460.43 | 6.4446 | 52.2473 | 64.1561 | -2772.5783
2020-06-03 04:00 | -9868.61 | 6.4446 | 51.9252 | 64.1561 | -2892.2041
2020-06-04 05:00 | -9874.5 | 6.4446 | 51.7983 | 64.1561 | -2893.9303
2020-06-05 06:00 | -9990.93 | 6.4446 | 51.6536 | 64.1561 | -2928.0525
2020-06-06 07:00 | -9592.54 | 6.4446 | 51.8224 | 64.1561 | -2811.296
2020-06-07 08:00 | -9422.22 | 6.4446 | 51.9077 | 64.1561 | -2761.3801
2020-06-08 09:00 | -10374.3 | 6.4446 | 51.3146 | 64.1561 | -3040.4072
2020-06-09 10:00 | -9943.34 | 6.4446 | 51.4386 | 64.1561 | -2914.1053
2020-06-10 11:00 | -9902.15 | 6.4446 | 51.4114 | 64.1561 | -2902.0337
2020-06-11 12:00 | -9321.54 | 6.4446 | 51.7365 | 64.1561 | -2731.8737
2020-06-12 13:00 | -9366.38 | 6.4446 | 51.723 | 64.1561 | -2745.015
2020-06-13 14:00 | -9032.2 | 6.4446 | 51.9 | 64.1561 | -2647.0765
2020-06-14 15:00 | -9322.99 | 6.4446 | 51.7419 | 64.1561 | -2732.2987
2020-06-15 16:00 | -9693.71 | 6.4446 | 51.4816 | 64.1561 | -2840.946
2020-06-16 17:00 | -8490.69 | 6.4446 | 52.1355 | 64.1561 | -2488.3756
2020-06-17 18:00 | -9041.42 | 6.4446 | 51.8803 | 64.1561 | -2649.7786
2020-06-18 19:00 | -9026.39 | 6.4446 | 51.8595 | 64.1561 | -2645.3738
2020-06-19 20:00 | -9507.35 | 6.4446 | 51.5257 | 64.1561 | -2786.3292
2020-06-20 21:00 | -9630.75 | 6.4446 | 51.3884 | 64.1561 | -2822.4942
2020-06-21 22:00 | -9730.36 | 6.4446 | 51.2796 | 64.1561 | -2851.687
2020-06-22 23:00 | -9752.4 | 6.4446 | 51.2065 | 64.1561 | -2858.1463
2020-06-24 | -11007 | 6.4446 | 50.4013 | 64.1561 | -3225.8333
2020-06-25 01:00 | -11059.4 | 6.4446 | 50.1888 | 64.1561 | -3241.1902
2020-06-26 02:00 | -11029.5 | 6.4446 | 50.0902 | 64.1561 | -3232.4274
2020-06-27 03:00 | -10687.3 | 6.4446 | 50.2296 | 64.1561 | -3132.1384
2020-06-28 04:00 | -10391.6 | 6.4446 | 50.3873 | 64.1561 | -3045.4773
2020-06-29 05:00 | -10044.3 | 6.4446 | 50.583 | 64.1561 | -2943.6937
2020-06-30 06:00 | -9608.75 | 6.4446 | 50.8768 | 64.1561 | -2816.0466
2020-07-01 07:00 | -9437.63 | 6.4446 | 51.0315 | 64.1561 | -2765.8963
2020-07-02 08:00 | -9018.06 | 6.4446 | 51.328 | 64.1561 | -2642.9325
2020-07-03 09:00 | -8816.69 | 6.4446 | 51.5179 | 64.1561 | -2583.9168
2020-07-04 10:00 | -8099.86 | 6.4446 | 52.0107 | 64.1561 | -2373.8346
2020-07-05 11:00 | -7348.89 | 6.4446 | 52.5756 | 64.1561 | -2153.7471
2020-07-06 12:00 | -6601.19 | 6.4446 | 53.1836 | 64.1561 | -1934.6178
2020-07-07 13:00 | -6516.78 | 6.4446 | 53.4137 | 64.1561 | -1909.8797
2020-07-08 14:00 | -6353.84 | 6.4446 | 53.6315 | 64.1561 | -1862.1267
2020-07-09 15:00 | -6331.47 | 6.4446 | 53.7526 | 64.1561 | -1855.5707
2020-07-10 16:00 | -5747.42 | 6.4446 | 54.1936 | 64.1561 | -1684.4025
2020-07-11 17:00 | -5920.62 | 6.4446 | 54.2089 | 64.1561 | -1735.1624
2020-07-12 18:00 | -5982.16 | 6.4446 | 54.2294 | 64.1561 | -1753.198
2020-07-13 19:00 | -6417.45 | 6.4446 | 54.0055 | 64.1561 | -1880.7689
2020-07-14 20:00 | -6645.77 | 6.4446 | 53.8619 | 64.1561 | -1947.6829
2020-07-15 21:00 | -7459.59 | 6.4446 | 53.3583 | 64.1561 | -2186.19
2020-07-16 22:00 | -7704.98 | 6.4446 | 53.114 | 64.1561 | -2258.1067
2020-07-17 23:00 | -8552.11 | 6.4446 | 52.5187 | 64.1561 | -2506.376
2020-07-19 | -8843.37 | 6.4446 | 52.2064 | 64.1561 | -2591.7359
2020-07-20 01:00 | -8848.61 | 6.4446 | 52.0912 | 64.1561 | -2593.2716
2020-07-21 02:00 | -9068.23 | 6.4446 | 51.8868 | 64.1561 | -2657.6359
2020-07-22 03:00 | -9239.82 | 6.4446 | 51.7087 | 64.1561 | -2707.9239
2020-07-23 04:00 | -9267.94 | 6.4446 | 51.6079 | 64.1561 | -2716.1651
2020-07-24 05:00 | -9074.33 | 6.4446 | 51.6696 | 64.1561 | -2659.4236
2020-07-25 06:00 | -8847.99 | 6.4446 | 51.7839 | 64.1561 | -2593.0899
2020-07-26 07:00 | -8895.92 | 6.4446 | 51.7507 | 64.1561 | -2607.1368
2020-07-27 08:00 | -8590.54 | 6.4446 | 51.9139 | 64.1561 | -2517.6387
2020-07-28 09:00 | -8574.99 | 6.4446 | 51.9432 | 64.1561 | -2513.0815
2020-07-29 10:00 | -7108.23 | 6.4446 | 52.8416 | 64.1561 | -2083.2166
2020-07-30 11:00 | -6287.76 | 6.4446 | 53.5037 | 64.1561 | -1842.7606
2020-07-31 12:00 | -4843.64 | 6.4446 | 54.5605 | 64.1561 | -1419.5308
2020-08-01 13:00 | -4940.91 | 6.4446 | 54.7629 | 64.1561 | -1448.0378
2020-08-02 14:00 | -3633.95 | 6.4446 | 55.7098 | 64.1561 | -1065.0056
2020-08-03 15:00 | -3315.45 | 6.4446 | 56.1722 | 64.1561 | -971.6625
2020-08-04 16:00 | -3202.08 | 6.4446 | 56.4574 | 64.1561 | -938.437
2020-08-05 17:00 | -4113 | 6.4446 | 56.0606 | 64.1561 | -1205.4013
2020-08-06 18:00 | -4592.83 | 6.4446 | 55.7798 | 64.1561 | -1346.0256
2020-08-07 19:00 | -5325.92 | 6.4446 | 55.3359 | 64.1561 | -1560.8731
2020-08-08 20:00 | -5906.71 | 6.4446 | 54.9251 | 64.1561 | -1731.0858
2020-08-09 21:00 | -6895.38 | 6.4446 | 54.2479 | 64.1561 | -2020.8364
2020-08-10 22:00 | -7488.66 | 6.4446 | 53.7324 | 64.1561 | -2194.7096
2020-08-11 23:00 | -8395.32 | 6.4446 | 53.0368 | 64.1561 | -2460.4254
2020-08-13 | -8823.97 | 6.4446 | 52.5858 | 64.1561 | -2586.0503
2020-08-14 01:00 | -8798.52 | 6.4446 | 52.4384 | 64.1561 | -2578.5917
2020-08-15 02:00 | -8895.9 | 6.4446 | 52.266 | 64.1561 | -2607.1309
2020-08-16 03:00 | -9095.69 | 6.4446 | 52.047 | 64.1561 | -2665.6836
2020-08-17 04:00 | -9168.24 | 6.4446 | 51.896 | 64.1561 | -2686.9459
2020-08-18 05:00 | -9179.01 | 6.4446 | 51.8113 | 64.1561 | -2690.1023
2020-08-19 06:00 | -8861.21 | 6.4446 | 51.945 | 64.1561 | -2596.9643
2020-08-20 07:00 | -8991.99 | 6.4446 | 51.8502 | 64.1561 | -2635.2921
2020-08-21 08:00 | -8729.76 | 6.4446 | 51.9686 | 64.1561 | -2558.4401
2020-08-22 09:00 | -8726.64 | 6.4446 | 51.9697 | 64.1561 | -2557.5257
2020-08-23 10:00 | -8185.89 | 6.4446 | 52.2874 | 64.1561 | -2399.0475
2020-08-24 11:00 | -5078.22 | 6.4446 | 54.225 | 64.1561 | -1488.2794
2020-08-25 12:00 | -2463.07 | 6.4446 | 56.1792 | 64.1561 | -721.8546
2020-08-26 13:00 | -1920.87 | 5.7034 | 56.8557 | 64.1561 | -562.9514
2020-08-27 14:00 | -1201.49 | 3.6064 | 57.2043 | 64.1561 | -352.122
2020-08-28 15:00 | -668.256 | 2.2353 | 57.656 | 64.1561 | -195.8465
2020-08-29 16:00 | -728.011 | 2.5309 | 58.0186 | 64.1561 | -213.359
2020-08-30 17:00 | -2048.81 | 6.354 | 58.0948 | 64.1561 | -600.4469
2020-08-31 18:00 | -3467.78 | 6.4446 | 57.2467 | 64.1561 | -1016.306
2020-09-01 19:00 | -4764.55 | 6.4446 | 56.353 | 64.1561 | -1396.3518
2020-09-02 20:00 | -5204.87 | 6.4446 | 55.9243 | 64.1561 | -1525.3968
2020-09-03 21:00 | -6524.52 | 6.4446 | 55.0104 | 64.1561 | -1912.1481
2020-09-04 22:00 | -7114.5 | 6.4446 | 54.4466 | 64.1561 | -2085.0541
2020-09-05 23:00 | -8215.84 | 6.4446 | 53.5825 | 64.1561 | -2407.825
2020-09-07 | -8569.84 | 6.4446 | 53.1192 | 64.1561 | -2511.5722
2020-09-08 01:00 | -8800.28 | 6.4446 | 52.7802 | 64.1561 | -2579.1075
2020-09-09 02:00 | -8984.52 | 6.4446 | 52.4943 | 64.1561 | -2633.1029
2020-09-10 03:00 | -8856.75 | 6.4446 | 52.4202 | 64.1561 | -2595.6572
2020-09-11 04:00 | -8915.76 | 6.4446 | 52.2753 | 64.1561 | -2612.9513
2020-09-12 05:00 | -8800.09 | 6.4446 | 52.2622 | 64.1561 | -2579.0518
2020-09-13 06:00 | -8732.71 | 6.4446 | 52.2503 | 64.1561 | -2559.3047
2020-09-14 07:00 | -8387.74 | 6.4446 | 52.4285 | 64.1561 | -2458.2039
2020-09-15 08:00 | -6971.42 | 6.4446 | 53.298 | 64.1561 | -2043.1215
2020-09-16 09:00 | -5793.42 | 6.4446 | 54.1782 | 64.1561 | -1697.8838
2020-09-17 10:00 | -3753.13 | 6.4446 | 55.6397 | 64.1561 | -1099.9338
2020-09-18 11:00 | -1633.45 | 4.8862 | 56.958 | 64.1561 | -478.7169
2020-09-19 12:00 | -1042.68 | 3.2101 | 57.4377 | 64.1561 | -305.5793
2020-09-20 13:00 | -217.609 | 0.9597 | 58.1664 | 64.1561 | -63.7749
2020-09-21 14:00 | 1115.13 | 1 | 59.1117 | 64.1561 | 326.8123
2020-09-22 15:00 | 2793.86 | 1 | 59.1002 | 64.1561 | 818.7995
2020-09-23 16:00 | 1934.32 | 1 | 59.7584 | 64.1561 | 566.8932
2020-09-24 17:00 | -605.704 | 2.334 | 59.4026 | 64.1561 | -177.5143
2020-09-25 18:00 | -1949.69 | 6.005 | 59.0529 | 64.1561 | -571.3977
2020-09-26 19:00 | -3331.93 | 6.4446 | 58.184 | 64.1561 | -976.4923
2020-09-27 20:00 | -4130.84 | 6.4446 | 57.5259 | 64.1561 | -1210.6297
2020-09-28 21:00 | -5667.26 | 6.4446 | 56.3983 | 64.1561 | -1660.91
2020-09-29 22:00 | -5921.82 | 6.4446 | 55.9526 | 64.1561 | -1735.5141
2020-09-30 23:00 | -7497.94 | 6.4446 | 54.8062 | 64.1561 | -2197.4293
2020-10-02 | -7550.93 | 6.4446 | 54.4856 | 64.1561 | -2212.9591
2020-10-03 01:00 | -8287.08 | 6.4446 | 53.8463 | 64.1561 | -2428.7034
2020-10-04 02:00 | -8683.59 | 6.4446 | 53.3801 | 64.1561 | -2544.909
2020-10-05 03:00 | -8701.22 | 6.4446 | 53.1488 | 64.1561 | -2550.0759
2020-10-06 04:00 | -8646.19 | 6.4446 | 53.0132 | 64.1561 | -2533.9482
2020-10-07 05:00 | -8624.1 | 6.4446 | 52.9293 | 64.1561 | -2527.4742
2020-10-08 06:00 | -8489.85 | 6.4446 | 52.926 | 64.1561 | -2488.1294
2020-10-09 07:00 | -8192.91 | 6.4446 | 53.0602 | 64.1561 | -2401.1049
2020-10-10 08:00 | -7713.13 | 6.4446 | 53.3403 | 64.1561 | -2260.4953
2020-10-11 09:00 | -6879.47 | 6.4446 | 53.8813 | 64.1561 | -2016.1736
2020-10-12 10:00 | -5151.6 | 6.4446 | 55.0195 | 64.1561 | -1509.7849
2020-10-13 11:00 | -3653.29 | 6.4446 | 56.1572 | 64.1561 | -1070.6736
2020-10-14 12:00 | -2330.14 | 6.4446 | 57.2401 | 64.1561 | -682.8966
2020-10-15 13:00 | -1625.21 | 4.7638 | 57.623 | 64.1561 | -476.302
2020-10-16 14:00 | -1531.83 | 4.6327 | 57.9293 | 64.1561 | -448.9351
2020-10-17 15:00 | -1897.69 | 5.7078 | 58.1032 | 64.1561 | -556.158
2020-10-18 16:00 | -1326.63 | 3.9264 | 58.1642 | 64.1561 | -388.7969
2020-10-19 17:00 | -1907.94 | 5.7882 | 58.349 | 64.1561 | -559.162
2020-10-20 18:00 | -2416.42 | 6.4446 | 58.2235 | 64.1561 | -708.1828
2020-10-21 19:00 | -2927.21 | 6.4446 | 57.912 | 64.1561 | -857.8806
2020-10-22 20:00 | -3536.84 | 6.4446 | 57.5219 | 64.1561 | -1036.5455
2020-10-23 21:00 | -4487.06 | 6.4446 | 56.905 | 64.1561 | -1315.0275
2020-10-24 22:00 | -4759.45 | 6.4446 | 56.6106 | 64.1561 | -1394.8571
2020-10-25 23:00 | -5482.45 | 6.4446 | 56.0825 | 64.1561 | -1606.7475
2020-10-27 | -5981.1 | 6.4446 | 55.6469 | 64.1561 | -1752.8874
2020-10-28 01:00 | -6221.73 | 6.4446 | 55.3609 | 64.1561 | -1823.4091
2020-10-29 02:00 | -6303.43 | 6.4446 | 55.202 | 64.1561 | -1847.353
2020-10-30 03:00 | -6668.18 | 6.4446 | 54.9091 | 64.1561 | -1954.2506
2020-10-31 04:00 | -6701.69 | 6.4446 | 54.7864 | 64.1561 | -1964.0715
2020-11-01 05:00 | -6827.78 | 6.4446 | 54.6421 | 64.1561 | -2001.0248
2020-11-02 06:00 | -6812.85 | 6.4446 | 54.5942 | 64.1561 | -1996.6492
2020-11-03 07:00 | -6006.26 | 6.4446 | 55.0441 | 64.1561 | -1760.261
2020-11-04 08:00 | -5696.43 | 6.4446 | 55.2884 | 64.1561 | -1669.4588
2020-11-05 09:00 | -6132.17 | 6.4446 | 55.0843 | 64.1561 | -1797.1616
2020-11-06 10:00 | -5870.53 | 6.4446 | 55.2038 | 64.1561 | -1720.4825
2020-11-07 11:00 | -4188.37 | 6.4446 | 56.2247 | 64.1561 | -1227.4901
2020-11-08 12:00 | -2807.52 | 6.4446 | 57.2491 | 64.1561 | -822.8029
2020-11-09 13:00 | -2359 | 6.4446 | 57.7578 | 64.1561 | -691.3547
2020-11-10 14:00 | -2212.51 | 6.4446 | 58.0097 | 64.1561 | -648.4227
2020-11-11 15:00 | -2160.28 | 6.2973 | 58.139 | 64.1561 | -633.1156
2020-11-12 16:00 | -2942.6 | 6.4446 | 57.8037 | 64.1561 | -862.3909
2020-11-13 17:00 | -2554.22 | 6.4446 | 58.032 | 64.1561 | -748.568
2020-11-14 18:00 | -4121.38 | 6.4446 | 57.1325 | 64.1561 | -1207.8572
2020-11-15 19:00 | -5089.12 | 6.4446 | 56.4121 | 64.1561 | -1491.4738
2020-11-16 20:00 | -5906.76 | 6.4446 | 55.7358 | 64.1561 | -1731.1005
2020-11-17 21:00 | -6753.57 | 6.4446 | 55.0522 | 64.1561 | -1979.276
2020-11-18 22:00 | -7282.24 | 6.4446 | 54.5471 | 64.1561 | -2134.2139
2020-11-19 23:00 | -7719.61 | 6.4446 | 54.0863 | 64.1561 | -2262.3944
2020-11-21 | -9449.54 | 6.4446 | 52.858 | 64.1561 | -2769.3868
2020-11-22 01:00 | -9945.73 | 6.4446 | 52.2342 | 64.1561 | -2914.8057
2020-11-23 02:00 | -10412.1 | 6.4446 | 51.6836 | 64.1561 | -3051.4853
2020-11-24 03:00 | -10815.4 | 6.4446 | 51.2091 | 64.1561 | -3169.6809
2020-11-25 04:00 | -10767.9 | 6.4446 | 51.0172 | 64.1561 | -3155.76
2020-11-26 05:00 | -11026.7 | 6.4446 | 50.6828 | 64.1561 | -3231.6068
2020-11-27 06:00 | -11375.8 | 6.4446 | 50.3195 | 64.1561 | -3333.9179
2020-11-28 07:00 | -10420.9 | 6.4446 | 50.7362 | 64.1561 | -3054.0643
2020-11-29 08:00 | -8923.54 | 6.4446 | 51.632 | 64.1561 | -2615.2314
2020-11-30 09:00 | -7973.42 | 6.4446 | 52.3462 | 64.1561 | -2336.7787
2020-12-01 10:00 | -6844.06 | 6.4446 | 53.1765 | 64.1561 | -2005.796
2020-12-02 11:00 | -5355.31 | 6.4446 | 54.2596 | 64.1561 | -1569.4864
2020-12-03 12:00 | -4432.41 | 6.4446 | 55.0971 | 64.1561 | -1299.0111
2020-12-04 13:00 | -3727.55 | 6.4446 | 55.7857 | 64.1561 | -1092.4371
2020-12-05 14:00 | -4145.18 | 6.4446 | 55.759 | 64.1561 | -1214.8323
2020-12-06 15:00 | -3634.49 | 6.4446 | 56.1747 | 64.1561 | -1065.1639
2020-12-07 16:00 | -3433.57 | 6.4446 | 56.4407 | 64.1561 | -1006.28
2020-12-08 17:00 | -3183.01 | 6.4446 | 56.7218 | 64.1561 | -932.8481
2020-12-09 18:00 | -4258.41 | 6.4446 | 56.1978 | 64.1561 | -1248.0168
2020-12-10 19:00 | -5237.69 | 6.4446 | 55.5761 | 64.1561 | -1535.0154
2020-12-11 20:00 | -6042.78 | 6.4446 | 54.9917 | 64.1561 | -1770.964
2020-12-12 21:00 | -6289.35 | 6.4446 | 54.7216 | 64.1561 | -1843.2265
2020-12-13 22:00 | -6676.11 | 6.4446 | 54.3941 | 64.1561 | -1956.5747
2020-12-14 23:00 | -6845.04 | 6.4446 | 54.1759 | 64.1561 | -2006.0832
2020-12-16 | -8408.33 | 6.4446 | 53.1377 | 64.1561 | -2464.2383
2020-12-17 01:00 | -8969.84 | 6.4446 | 52.5631 | 64.1561 | -2628.8006
2020-12-18 02:00 | -9234.81 | 6.4446 | 52.207 | 64.1561 | -2706.4556
2020-12-19 03:00 | -9447.74 | 6.4446 | 51.9267 | 64.1561 | -2768.8593
2020-12-20 04:00 | -9670.36 | 6.4446 | 51.6505 | 64.1561 | -2834.1028
2020-12-21 05:00 | -9737.96 | 6.4446 | 51.4632 | 64.1561 | -2853.9144
2020-12-22 06:00 | -9958.55 | 6.4446 | 51.2335 | 64.1561 | -2918.5629
2020-12-23 07:00 | -9171.46 | 6.4446 | 51.6151 | 64.1561 | -2687.8896
2020-12-24 08:00 | -7899.18 | 6.4446 | 52.3989 | 64.1561 | -2315.0211
2020-12-25 09:00 | -7251.12 | 6.4446 | 52.9191 | 64.1561 | -2125.0935
2020-12-26 10:00 | -5674.94 | 6.4446 | 53.9938 | 64.1561 | -1663.1607
2020-12-27 11:00 | -4046.12 | 6.4446 | 55.2024 | 64.1561 | -1185.8007
2020-12-28 12:00 | -2733.25 | 6.4446 | 56.3209 | 64.1561 | -801.0365
2020-12-29 13:00 | -1833.78 | 5.4437 | 56.9938 | 64.1561 | -537.4279
2020-12-30 14:00 | -1261.32 | 3.8034 | 57.3164 | 64.1561 | -369.6564
2020-12-31 15:00 | -660.088 | 2.1907 | 57.7078 | 64.1561 | -193.4527
2021-01-01 16:00 | -1129.35 | 3.703 | 57.9585 | 64.1561 | -330.9798
2021-01-02 17:00 | -983.966 | 3.1313 | 58.0568 | 64.1561 | -288.372
2021-01-03 18:00 | -2606.83 | 6.4446 | 57.8509 | 64.1561 | -763.9865
2021-01-04 19:00 | -3550.53 | 6.4446 | 57.2272 | 64.1561 | -1040.5576
2021-01-05 20:00 | -4565.01 | 6.4446 | 56.5091 | 64.1561 | -1337.8724
2021-01-06 21:00 | -5105.87 | 6.4446 | 56.0416 | 64.1561 | -1496.3828
2021-01-07 22:00 | -5810.32 | 6.4446 | 55.4856 | 64.1561 | -1702.8367
2021-01-08 23:00 | -6159.76 | 6.4446 | 55.105 | 64.1561 | -1805.2475
2021-01-10 | -7759.71 | 6.4446 | 54.0035 | 64.1561 | -2274.1465
2021-01-11 01:00 | -8055.87 | 6.4446 | 53.562 | 64.1561 | -2360.9424
2021-01-12 02:00 | -8559.43 | 6.4446 | 53.0642 | 64.1561 | -2508.5213
2021-01-13 03:00 | -8424.18 | 6.4446 | 52.964 | 64.1561 | -2468.8834
2021-01-14 04:00 | -8552.58 | 6.4446 | 52.7704 | 64.1561 | -2506.5138
2021-01-15 05:00 | -8736.41 | 6.4446 | 52.5421 | 64.1561 | -2560.389
2021-01-16 06:00 | -8251.25 | 6.4446 | 52.7498 | 64.1561 | -2418.2027
2021-01-17 07:00 | -8310.05 | 6.4446 | 52.703 | 64.1561 | -2435.4352
2021-01-18 08:00 | -6880.06 | 6.4446 | 53.5466 | 64.1561 | -2016.3465
2021-01-19 09:00 | -5913.14 | 6.4446 | 54.2575 | 64.1561 | -1732.9703
2021-01-20 10:00 | -4441.59 | 6.4446 | 55.3156 | 64.1561 | -1301.7015
2021-01-21 11:00 | -2715.61 | 6.4446 | 56.6023 | 64.1561 | -795.8667
2021-01-22 12:00 | -1540.45 | 4.5498 | 57.2566 | 64.1561 | -451.4613
2021-01-23 13:00 | -926.085 | 2.8937 | 57.6664 | 64.1561 | -271.4087
2021-01-24 14:00 | -426.819 | 1.5938 | 58.1495 | 64.1561 | -125.0883
2021-01-25 15:00 | -219.401 | 1.1151 | 58.6781 | 64.1561 | -64.3001
2021-01-26 16:00 | -62.1927 | 0.70763 | 59.3119 | 64.1561 | -18.2269
2021-01-27 17:00 | -1067.78 | 3.6073 | 58.6647 | 64.1561 | -312.9354
2021-01-28 18:00 | -1781.37 | 5.4344 | 58.5656 | 64.1561 | -522.068
2021-01-29 19:00 | -2389.49 | 6.4446 | 58.3806 | 64.1561 | -700.2904
2021-01-30 20:00 | -3176.12 | 6.4446 | 57.8627 | 64.1561 | -930.8289
2021-01-31 21:00 | -4247.67 | 6.4446 | 57.1225 | 64.1561 | -1244.8692
2021-02-01 22:00 | -4775.45 | 6.4446 | 56.6325 | 64.1561 | -1399.5462
2021-02-02 23:00 | -5748.06 | 6.4446 | 55.8914 | 64.1561 | -1684.5901
2021-02-04 | -5875.18 | 6.4446 | 55.6246 | 64.1561 | -1721.8453
2021-02-05 01:00 | -6091.02 | 6.4446 | 55.3599 | 64.1561 | -1785.1017
2021-02-06 02:00 | -6213.1 | 6.4446 | 55.175 | 64.1561 | -1820.8799
2021-02-07 03:00 | -6404.88 | 6.4446 | 54.9664 | 64.1561 | -1877.085
2021-02-08 04:00 | -6316.15 | 6.4446 | 54.9283 | 64.1561 | -1851.0808
2021-02-09 05:00 | -6069.16 | 6.4446 | 55.0386 | 64.1561 | -1778.6952
2021-02-10 06:00 | -5907.03 | 6.4446 | 55.1341 | 64.1561 | -1731.1796
2021-02-11 07:00 | -6215.15 | 6.4446 | 54.955 | 64.1561 | -1821.4807
2021-02-12 08:00 | -6390.62 | 6.4446 | 54.8054 | 64.1561 | -1872.9058
2021-02-13 09:00 | -6811.58 | 6.4446 | 54.5048 | 64.1561 | -1996.277
2021-02-14 10:00 | -6781.43 | 6.4446 | 54.4389 | 64.1561 | -1987.4409
2021-02-15 11:00 | -6285.41 | 6.4446 | 54.6751 | 64.1561 | -1842.0718
2021-02-16 12:00 | -6179.54 | 6.4446 | 54.7284 | 64.1561 | -1811.0444
2021-02-17 13:00 | -5635.91 | 6.4446 | 55.0379 | 64.1561 | -1651.7222
2021-02-18 14:00 | -5652.5 | 6.4446 | 55.0494 | 64.1561 | -1656.5842
2021-02-19 15:00 | -5476.14 | 6.4446 | 55.1547 | 64.1561 | -1604.8982
2021-02-20 16:00 | -4692.82 | 6.4446 | 55.6345 | 64.1561 | -1375.3298
2021-02-21 17:00 | -4382.57 | 6.4446 | 55.9007 | 64.1561 | -1284.4045
2021-02-22 18:00 | -4187.26 | 6.4446 | 56.0961 | 64.1561 | -1227.1648
2021-02-23 19:00 | -4536.75 | 6.4446 | 55.9445 | 64.1561 | -1329.5902
2021-02-24 20:00 | -4788.94 | 6.4446 | 55.8034 | 64.1561 | -1403.4998
2021-02-25 21:00 | -5377.07 | 6.4446 | 55.4489 | 64.1561 | -1575.8637
2021-02-26 22:00 | -5680.93 | 6.4446 | 55.2118 | 64.1561 | -1664.9162
2021-02-27 23:00 | -6340.21 | 6.4446 | 54.7551 | 64.1561 | -1858.1321
2021-03-01 | -6438.48 | 6.4446 | 54.5977 | 64.1561 | -1886.9322
2021-03-02 01:00 | -6455.27 | 6.4446 | 54.523 | 64.1561 | -1891.8529
2021-03-03 02:00 | -6455.95 | 6.4446 | 54.4872 | 64.1561 | -1892.0522
2021-03-04 03:00 | -6379.58 | 6.4446 | 54.5125 | 64.1561 | -1869.6703
2021-03-05 04:00 | -6168.05 | 6.4446 | 54.6276 | 64.1561 | -1807.677
2021-03-06 05:00 | -5798.63 | 6.4446 | 54.8685 | 64.1561 | -1699.4107
2021-03-07 06:00 | -5303.83 | 6.4446 | 55.214 | 64.1561 | -1554.3991
2021-03-08 07:00 | -5122.56 | 6.4446 | 55.4058 | 64.1561 | -1501.2741
2021-03-09 08:00 | -4912.62 | 6.4446 | 55.5993 | 64.1561 | -1439.7468
2021-03-10 09:00 | -5205.88 | 6.4446 | 55.4907 | 64.1561 | -1525.6928
2021-03-11 10:00 | -4736.65 | 6.4446 | 55.7904 | 64.1561 | -1388.1751
2021-03-12 11:00 | -4069.86 | 6.4446 | 56.2609 | 64.1561 | -1192.7582
2021-03-13 12:00 | -3729.95 | 6.4446 | 56.5799 | 64.1561 | -1093.1404
2021-03-14 13:00 | -3677.83 | 6.4446 | 56.7088 | 64.1561 | -1077.8656
2021-03-15 14:00 | -3579.42 | 6.4446 | 56.8315 | 64.1561 | -1049.0244
2021-03-16 15:00 | -3089.17 | 6.4446 | 57.1944 | 64.1561 | -905.3464
2021-03-17 16:00 | -2059.18 | 6.0663 | 57.8412 | 64.1561 | -603.4861
2021-03-18 17:00 | -1871.85 | 5.4955 | 58.0122 | 64.1561 | -548.5851
2021-03-19 18:00 | -1753.96 | 5.1973 | 58.1502 | 64.1561 | -514.0349
2021-03-20 19:00 | -2177.15 | 6.4446 | 58.2537 | 64.1561 | -638.0597
2021-03-21 20:00 | -2325.69 | 6.4446 | 58.2083 | 64.1561 | -681.5925
2021-03-22 21:00 | -3098.26 | 6.4446 | 57.7837 | 64.1561 | -908.0104
2021-03-23 22:00 | -3322.46 | 6.4446 | 57.6025 | 64.1561 | -973.7169
2021-03-24 23:00 | -4131.68 | 6.4446 | 57.078 | 64.1561 | -1210.8759
2021-03-26 | -4244.4 | 6.4446 | 56.9142 | 64.1561 | -1243.9108
2021-03-27 01:00 | -4387.64 | 6.4446 | 56.7732 | 64.1561 | -1285.8903
2021-03-28 02:00 | -4285.43 | 6.4446 | 56.7962 | 64.1561 | -1255.9356
2021-03-29 03:00 | -4212.66 | 6.4446 | 56.8335 | 64.1561 | -1234.6088
2021-03-30 04:00 | -3883.55 | 6.4446 | 57.0276 | 64.1561 | -1138.1562
2021-03-31 05:00 | -3516.74 | 6.4446 | 57.2873 | 64.1561 | -1030.6548
2021-04-01 06:00 | -2950.68 | 6.4446 | 57.6906 | 64.1561 | -864.7589
2021-04-02 07:00 | -2904.48 | 6.4446 | 57.8212 | 64.1561 | -851.2191
2021-04-03 08:00 | -2559.54 | 6.4446 | 58.0978 | 64.1561 | -750.1271
2021-04-04 09:00 | -2680.64 | 6.4446 | 58.1194 | 64.1561 | -785.618
2021-04-05 10:00 | -2486.25 | 6.4446 | 58.2914 | 64.1561 | -728.6479
2021-04-06 11:00 | -1653.61 | 4.7958 | 58.5153 | 64.1561 | -484.6253
2021-04-07 12:00 | -1077.89 | 3.2696 | 58.7141 | 64.1561 | -315.8984
2021-04-08 13:00 | -790.778 | 2.5833 | 58.9647 | 64.1561 | -231.7542
2021-04-09 14:00 | -673.759 | 2.3086 | 59.1515 | 64.1561 | -197.4593
2021-04-10 15:00 | -495.377 | 1.8223 | 59.3409 | 64.1561 | -145.1807
2021-04-11 16:00 | 940.791 | 1 | 60.2901 | 64.1561 | 275.7186
2021-04-12 17:00 | 2277.42 | 1 | 60.2098 | 64.1561 | 667.4459
2021-04-13 18:00 | 2938.94 | 1 | 60.3544 | 64.1561 | 861.3183
2021-04-14 19:00 | 0 | 0 | 61.3246 | 64.1561 | 0
2021-04-15 20:00 | 0 | 0 | 61.1891 | 64.1561 | 0
2021-04-16 21:00 | -725.335 | 2.5998 | 60.0838 | 64.1561 | -212.5747
2021-04-17 22:00 | -984.709 | 3.1653 | 59.9227 | 64.1561 | -288.5897
2021-04-18 23:00 | -1614.2 | 4.9101 | 59.7978 | 64.1561 | -473.0753
2021-04-20 | -2326.69 | 6.4446 | 59.5617 | 64.1561 | -681.8855
2021-04-21 01:00 | -2595.99 | 6.4446 | 59.2977 | 64.1561 | -760.8096
2021-04-22 02:00 | -2828.05 | 6.4446 | 59.0765 | 64.1561 | -828.8196
2021-04-23 03:00 | -3096.29 | 6.4446 | 58.8515 | 64.1561 | -907.433
2021-04-24 04:00 | -3241.7 | 6.4446 | 58.6785 | 64.1561 | -950.0485
2021-04-25 05:00 | -3409.87 | 6.4446 | 58.4912 | 64.1561 | -999.3342
2021-04-26 06:00 | -3492.41 | 6.4446 | 58.3539 | 64.1561 | -1023.5243
2021-04-27 07:00 | -2805.92 | 6.4446 | 58.7189 | 64.1561 | -822.334
2021-04-28 08:00 | -2356.8 | 6.4446 | 59.0273 | 64.1561 | -690.7099
2021-04-29 09:00 | -2766.68 | 6.4446 | 58.8463 | 64.1561 | -810.8339
2021-04-30 10:00 | -2381.53 | 6.4446 | 59.0603 | 64.1561 | -697.9575
2021-05-01 11:00 | -1997.59 | 5.7458 | 59.1763 | 64.1561 | -585.4358
2021-05-02 12:00 | -1051.02 | 3.0775 | 59.2685 | 64.1561 | -308.0236
2021-05-03 13:00 | -690.771 | 2.2986 | 59.565 | 64.1561 | -202.445
2021-05-04 14:00 | -305.171 | 1.2757 | 59.9187 | 64.1561 | -89.4368
2021-05-05 15:00 | -72.4345 | 0.71347 | 60.5813 | 64.1561 | -21.2285
2021-05-06 16:00 | -44.4206 | 0.6851 | 60.8297 | 64.1561 | -13.0184
2021-05-07 17:00 | 2634.04 | 1 | 60.5331 | 64.1561 | 771.9609
2021-05-08 18:00 | 0 | 0 | 61.5116 | 64.1561 | 0
2021-05-09 19:00 | -536.7 | 2.0647 | 60.4189 | 64.1561 | -157.2912
2021-05-10 20:00 | -1080.6 | 3.4767 | 60.1245 | 64.1561 | -316.6926
2021-05-11 21:00 | -1550.1 | 4.6856 | 59.9972 | 64.1561 | -454.2895
2021-05-12 22:00 | -2003.24 | 5.8731 | 59.8943 | 64.1561 | -587.0917
2021-05-13 23:00 | -2402.8 | 6.4446 | 59.6451 | 64.1561 | -704.1912
2021-05-15 | -4141.42 | 6.4446 | 58.4983 | 64.1561 | -1213.7304
2021-05-16 01:00 | -4693.67 | 6.4446 | 57.9136 | 64.1561 | -1375.5789
2021-05-17 02:00 | -5132.01 | 6.4446 | 57.4371 | 64.1561 | -1504.0437
2021-05-18 03:00 | -5349.5 | 6.4446 | 57.1292 | 64.1561 | -1567.7837
2021-05-19 04:00 | -5588.89 | 6.4446 | 56.8282 | 64.1561 | -1637.942
2021-05-20 05:00 | -6061.52 | 6.4446 | 56.3626 | 64.1561 | -1776.4562
2021-05-21 06:00 | -6232.82 | 6.4446 | 56.1005 | 64.1561 | -1826.6592
2021-05-22 07:00 | -5427.47 | 6.4446 | 56.4545 | 64.1561 | -1590.6344
2021-05-23 08:00 | -5022.61 | 6.4446 | 56.6897 | 64.1561 | -1471.9817
2021-05-24 09:00 | -5406.37 | 6.4446 | 56.4695 | 64.1561 | -1584.4506
2021-05-25 10:00 | -4973.3 | 6.4446 | 56.6652 | 64.1561 | -1457.5304
2021-05-26 11:00 | -4878.61 | 6.4446 | 56.7186 | 64.1561 | -1429.7795
2021-05-27 12:00 | -4446.41 | 6.4446 | 56.9911 | 64.1561 | -1303.1141
2021-05-28 13:00 | -3502.9 | 6.4446 | 57.5932 | 64.1561 | -1026.5987
2021-05-29 14:00 | -2765.42 | 6.4446 | 58.1488 | 64.1561 | -810.4646
2021-05-30 15:00 | -3223.74 | 6.4446 | 58.0127 | 64.1561 | -944.7849
2021-05-31 16:00 | -2624 | 6.4446 | 58.3948 | 64.1561 | -769.0185
2021-06-01 17:00 | -1688.4 | 4.89 | 58.7089 | 64.1561 | -494.8212
2021-06-02 18:00 | -2724.5 | 6.4446 | 58.5771 | 64.1561 | -798.4721
2021-06-03 19:00 | -3536.44 | 6.4446 | 58.059 | 64.1561 | -1036.4283
2021-06-04 20:00 | -4361.17 | 6.4446 | 57.4481 | 64.1561 | -1278.1328
2021-06-05 21:00 | -4559.71 | 6.4446 | 57.2095 | 64.1561 | -1336.3191
2021-06-06 22:00 | -4954.27 | 6.4446 | 56.8798 | 64.1561 | -1451.9532
2021-06-07 23:00 | -5203.51 | 6.4446 | 56.6124 | 64.1561 | -1524.9982
2021-06-09 | -6649.39 | 6.4446 | 55.6402 | 64.1561 | -1948.7438
2021-06-10 01:00 | -7093.71 | 6.4446 | 55.144 | 64.1561 | -2078.9612
2021-06-11 02:00 | -7363.14 | 6.4446 | 54.7915 | 64.1561 | -2157.9233
2021-06-12 03:00 | -7594.05 | 6.4446 | 54.5044 | 64.1561 | -2225.5964
2021-06-13 04:00 | -7579.37 | 6.4446 | 54.3689 | 64.1561 | -2221.2941
2021-06-14 05:00 | -7565.95 | 6.4446 | 54.2517 | 64.1561 | -2217.3611
2021-06-15 06:00 | -7277.62 | 6.4446 | 54.3472 | 64.1561 | -2132.8599
2021-06-16 07:00 | -7204.15 | 6.4446 | 54.3537 | 64.1561 | -2111.3279
2021-06-17 08:00 | -6244.88 | 6.4446 | 54.9022 | 64.1561 | -1830.1937
2021-06-18 09:00 | -5963.48 | 6.4446 | 55.1455 | 64.1561 | -1747.7235
2021-06-19 10:00 | -5287.43 | 6.4446 | 55.612 | 64.1561 | -1549.5928
2021-06-20 11:00 | -3534.99 | 6.4446 | 56.7685 | 64.1561 | -1036.0033
2021-06-21 12:00 | -3345.49 | 6.4446 | 57.1375 | 64.1561 | -980.4663
2021-06-22 13:00 | -3544.4 | 6.4446 | 57.186 | 64.1561 | -1038.7611
2021-06-23 14:00 | -3103.99 | 6.4446 | 57.5205 | 64.1561 | -909.6897
2021-06-24 15:00 | -2316.26 | 6.4446 | 58.1183 | 64.1561 | -678.8288
2021-06-25 16:00 | -1889.72 | 5.4905 | 58.3536 | 64.1561 | -553.8223
2021-06-26 17:00 | -2411.82 | 6.4446 | 58.3669 | 64.1561 | -706.8347
2021-06-27 18:00 | -3710.01 | 6.4446 | 57.6113 | 64.1561 | -1087.2966
2021-06-28 19:00 | -4519.5 | 6.4446 | 57.0256 | 64.1561 | -1324.5347
2021-06-29 20:00 | -5214.4 | 6.4446 | 56.4821 | 64.1561 | -1528.1898
2021-06-30 21:00 | -6295.03 | 6.4446 | 55.6857 | 64.1561 | -1844.8912
2021-07-01 22:00 | -6880.38 | 6.4446 | 55.1117 | 64.1561 | -2016.4403
2021-07-02 23:00 | -7776.46 | 6.4446 | 54.3496 | 64.1561 | -2279.0555
2021-07-04 | -8361.27 | 6.4446 | 53.7683 | 64.1561 | -2450.4463
2021-07-05 01:00 | -8629.61 | 6.4446 | 53.3935 | 64.1561 | -2529.089
2021-07-06 02:00 | -8686.43 | 6.4446 | 53.1821 | 64.1561 | -2545.7413
2021-07-07 03:00 | -8614.09 | 6.4446 | 53.0874 | 64.1561 | -2524.5406
2021-07-08 04:00 | -8632.14 | 6.4446 | 52.964 | 64.1561 | -2529.8305
2021-07-09 05:00 | -8491.78 | 6.4446 | 52.9558 | 64.1561 | -2488.6951
2021-07-10 06:00 | -8060.68 | 6.4446 | 53.1616 | 64.1561 | -2362.3521
2021-07-11 07:00 | -7928.51 | 6.4446 | 53.2388 | 64.1561 | -2323.6169
2021-07-12 08:00 | -6572.28 | 6.4446 | 54.0524 | 64.1561 | -1926.1451
2021-07-13 09:00 | -5426.3 | 6.4446 | 54.8836 | 64.1561 | -1590.2915
2021-07-14 10:00 | -4043.37 | 6.4446 | 55.9213 | 64.1561 | -1184.9948
2021-07-15 11:00 | -2317.77 | 6.4446 | 57.2267 | 64.1561 | -679.2713
2021-07-16 12:00 | -1357.07 | 3.9726 | 57.6432 | 64.1561 | -397.718
2021-07-17 13:00 | -697.835 | 2.2727 | 58.1113 | 64.1561 | -204.5153
2021-07-18 14:00 | -278.6 | 1.2194 | 58.7036 | 64.1561 | -81.6496
2021-07-19 15:00 | -170.137 | 1.0041 | 59.1833 | 64.1561 | -49.8622
2021-07-20 16:00 | 2128.64 | 1 | 59.5342 | 64.1561 | 623.8428
2021-07-21 17:00 | -608.434 | 2.3459 | 59.4211 | 64.1561 | -178.3144
2021-07-22 18:00 | -1682.03 | 5.2235 | 59.1397 | 64.1561 | -492.9543
2021-07-23 19:00 | -2681.31 | 6.4446 | 58.6717 | 64.1561 | -785.8144
2021-07-24 20:00 | -3247.99 | 6.4446 | 58.2269 | 64.1561 | -951.8919
2021-07-25 21:00 | -4637.77 | 6.4446 | 57.2892 | 64.1561 | -1359.1962
2021-07-26 22:00 | -5148.11 | 6.4446 | 56.7297 | 64.1561 | -1508.7621
2021-07-27 23:00 | -6153.48 | 6.4446 | 55.9348 | 64.1561 | -1803.407
2021-07-29 | -6610.37 | 6.4446 | 55.4418 | 64.1561 | -1937.3082
2021-07-30 01:00 | -6777.11 | 6.4446 | 55.1514 | 64.1561 | -1986.1749
2021-07-31 02:00 | -6991.9 | 6.4446 | 54.8718 | 64.1561 | -2049.1236
2021-08-01 03:00 | -7346.04 | 6.4446 | 54.5295 | 64.1561 | -2152.9118
2021-08-02 04:00 | -7511.94 | 6.4446 | 54.2642 | 64.1561 | -2201.5323
2021-08-03 05:00 | -7429.07 | 6.4446 | 54.1992 | 64.1561 | -2177.2455
2021-08-04 06:00 | -7024.62 | 6.4446 | 54.3736 | 64.1561 | -2058.7129
2021-08-05 07:00 | -6866.91 | 6.4446 | 54.4562 | 64.1561 | -2012.4927
2021-08-06 08:00 | -5899.67 | 6.4446 | 55.0268 | 64.1561 | -1729.0226
2021-08-07 09:00 | -4882.44 | 6.4446 | 55.7333 | 64.1561 | -1430.9019
2021-08-08 10:00 | -3023.61 | 6.4446 | 57.0152 | 64.1561 | -886.1326
2021-08-09 11:00 | -1338.54 | 3.9312 | 57.7985 | 64.1561 | -392.2874
2021-08-10 12:00 | -1744.58 | 5.32 | 58.195 | 64.1561 | -511.2859
2021-08-11 13:00 | -1315.5 | 3.9242 | 58.3263 | 64.1561 | -385.535
2021-08-12 14:00 | -1915.56 | 5.7986 | 58.5081 | 64.1561 | -561.3952
2021-08-13 15:00 | -2082.42 | 6.1008 | 58.5303 | 64.1561 | -610.2971
2021-08-14 16:00 | -1357.97 | 3.9597 | 58.5379 | 64.1561 | -397.9817
2021-08-15 17:00 | -1465.59 | 4.4729 | 58.701 | 64.1561 | -429.522
2021-08-16 18:00 | -1467.89 | 4.4262 | 58.7619 | 64.1561 | -430.1961
2021-08-17 19:00 | -1899.34 | 5.6798 | 58.8109 | 64.1561 | -556.6416
2021-08-18 20:00 | -2291.38 | 6.4446 | 58.7493 | 64.1561 | -671.5372
2021-08-19 21:00 | -3382.12 | 6.4446 | 58.0869 | 64.1561 | -991.2015
2021-08-20 22:00 | -3771.83 | 6.4446 | 57.7297 | 64.1561 | -1105.4143
2021-08-21 23:00 | -4651.72 | 6.4446 | 57.0874 | 64.1561 | -1363.2846
2021-08-23 | -4968.52 | 6.4446 | 56.7461 | 64.1561 | -1456.1295
2021-08-24 01:00 | -5355.84 | 6.4446 | 56.3851 | 64.1561 | -1569.6418
2021-08-25 02:00 | -5500.99 | 6.4446 | 56.1824 | 64.1561 | -1612.181
2021-08-26 03:00 | -5711.23 | 6.4446 | 55.9754 | 64.1561 | -1673.7963
2021-08-27 04:00 | -5696.15 | 6.4446 | 55.901 | 64.1561 | -1669.3768
2021-08-28 05:00 | -5475.36 | 6.4446 | 55.9851 | 64.1561 | -1604.6696
2021-08-29 06:00 | -4978.05 | 6.4446 | 56.2712 | 64.1561 | -1458.9224
2021-08-30 07:00 | -5103.16 | 6.4446 | 56.2344 | 64.1561 | -1495.5886
2021-08-31 08:00 | -5168.32 | 6.4446 | 56.1878 | 64.1561 | -1514.6851
2021-09-01 09:00 | -5431.45 | 6.4446 | 56.0125 | 64.1561 | -1591.8009
2021-09-02 10:00 | -5523.02 | 6.4446 | 55.9083 | 64.1561 | -1618.6374
2021-09-03 11:00 | -3650.52 | 6.4446 | 56.994 | 64.1561 | -1069.8618
2021-09-04 12:00 | -2361.25 | 6.4446 | 57.9432 | 64.1561 | -692.0141
2021-09-05 13:00 | -1735 | 5.0461 | 58.2575 | 64.1561 | -508.4783
2021-09-06 14:00 | -1398.06 | 4.183 | 58.4811 | 64.1561 | -409.7309
2021-09-07 15:00 | -1173.97 | 3.6084 | 58.6818 | 64.1561 | -344.0566
2021-09-08 16:00 | -1622.3 | 4.9534 | 58.8241 | 64.1561 | -475.4492
2021-09-09 17:00 | -2111.33 | 6.2443 | 58.8301 | 64.1561 | -618.7697
2021-09-10 18:00 | -2706.62 | 6.4446 | 58.4898 | 64.1561 | -793.232
2021-09-11 19:00 | -4165.49 | 6.4446 | 57.5464 | 64.1561 | -1220.7846
2021-09-12 20:00 | -4380.92 | 6.4446 | 57.2323 | 64.1561 | -1283.9209
2021-09-13 21:00 | -5726.48 | 6.4446 | 56.301 | 64.1561 | -1678.2656
2021-09-14 22:00 | -6257.11 | 6.4446 | 55.7759 | 64.1561 | -1833.7779
2021-09-15 23:00 | -7612.37 | 6.4446 | 54.7579 | 64.1561 | -2230.9654
2021-09-17 | -8171.63 | 6.4446 | 54.1356 | 64.1561 | -2394.8683
2021-09-18 01:00 | -8721.46 | 6.4446 | 53.5598 | 64.1561 | -2556.0076
2021-09-19 02:00 | -9102.39 | 6.4446 | 53.0918 | 64.1561 | -2667.6472
2021-09-20 03:00 | -9268.81 | 6.4446 | 52.7788 | 64.1561 | -2716.4201
2021-09-21 04:00 | -9375.16 | 6.4446 | 52.5321 | 64.1561 | -2747.5882
2021-09-22 05:00 | -9349.84 | 6.4446 | 52.4013 | 64.1561 | -2740.1676
2021-09-23 06:00 | -9021.51 | 6.4446 | 52.4803 | 64.1561 | -2643.9436
2021-09-24 07:00 | -8851.08 | 6.4446 | 52.5273 | 64.1561 | -2593.9955
2021-09-25 08:00 | -7922.66 | 6.4446 | 53.045 | 64.1561 | -2321.9024
2021-09-26 09:00 | -7344 | 6.4446 | 53.4535 | 64.1561 | -2152.3139
2021-09-27 10:00 | -6075.26 | 6.4446 | 54.3006 | 64.1561 | -1780.4829
2021-09-28 11:00 | -4723.46 | 6.4446 | 55.2852 | 64.1561 | -1384.3095
2021-09-29 12:00 | -3223.29 | 6.4446 | 56.4296 | 64.1561 | -944.653
2021-09-30 13:00 | -2892.49 | 6.4446 | 56.9313 | 64.1561 | -847.7051
2021-10-01 14:00 | -2480.61 | 6.4446 | 57.3946 | 64.1561 | -726.995
2021-10-02 15:00 | -2619.34 | 6.4446 | 57.5001 | 64.1561 | -767.6528
2021-10-03 16:00 | -2265.67 | 6.4446 | 57.8359 | 64.1561 | -664.0023
2021-10-04 17:00 | -3309.81 | 6.4446 | 57.3352 | 64.1561 | -970.0096
2021-10-05 18:00 | -4516.4 | 6.4446 | 56.5762 | 64.1561 | -1323.6262
2021-10-06 19:00 | -5377.27 | 6.4446 | 55.9301 | 64.1561 | -1575.9223
2021-10-07 20:00 | -5988.81 | 6.4446 | 55.4107 | 64.1561 | -1755.147
2021-10-08 21:00 | -7198.07 | 6.4446 | 54.5416 | 64.1561 | -2109.5461
2021-10-09 22:00 | -7798.75 | 6.4446 | 53.9431 | 64.1561 | -2285.588
2021-10-10 23:00 | -8908.71 | 6.4446 | 53.0587 | 64.1561 | -2610.8852
2021-10-12 | -9564.3 | 6.4446 | 52.3993 | 64.1561 | -2803.0196
2021-10-13 01:00 | -9937.27 | 6.4446 | 51.9246 | 64.1561 | -2912.3264
2021-10-14 02:00 | -10242.4 | 6.4446 | 51.5219 | 64.1561 | -3001.7511
2021-10-15 03:00 | -10536.8 | 6.4446 | 51.1529 | 64.1561 | -3088.0313
2021-10-16 04:00 | -10544.9 | 6.4446 | 50.9583 | 64.1561 | -3090.4051
2021-10-17 05:00 | -10848.9 | 6.4446 | 50.6356 | 64.1561 | -3179.4987
2021-10-18 06:00 | -11097.9 | 6.4446 | 50.3404 | 64.1561 | -3252.4734
2021-10-19 07:00 | -10225.7 | 6.4446 | 50.7297 | 64.1561 | -2996.8568
2021-10-20 08:00 | -8762.98 | 6.4446 | 51.6061 | 64.1561 | -2568.1759
2021-10-21 09:00 | -8231.54 | 6.4446 | 52.0614 | 64.1561 | -2412.4262
2021-10-22 10:00 | -6955.48 | 6.4446 | 52.9328 | 64.1561 | -2038.45
2021-10-23 11:00 | -5582.14 | 6.4446 | 53.9445 | 64.1561 | -1635.9637
2021-10-24 12:00 | -4368.47 | 6.4446 | 54.9385 | 64.1561 | -1280.2722
2021-10-25 13:00 | -3298.12 | 6.4446 | 55.8642 | 64.1561 | -966.5836
2021-10-26 14:00 | -2350.39 | 6.4446 | 56.7113 | 64.1561 | -688.8313
2021-10-27 15:00 | -2364.84 | 6.4446 | 56.9879 | 64.1561 | -693.0662
2021-10-28 16:00 | -2797.03 | 6.4446 | 56.905 | 64.1561 | -819.7286
2021-10-29 17:00 | -2165.24 | 6.4084 | 57.3713 | 64.1561 | -634.5692
2021-10-30 18:00 | -4147.78 | 6.4446 | 56.3448 | 64.1561 | -1215.5943
2021-10-31 19:00 | -4747.05 | 6.4446 | 55.8886 | 64.1561 | -1391.223
2021-11-01 20:00 | -5512.78 | 6.4446 | 55.3114 | 64.1561 | -1615.6363
2021-11-02 21:00 | -6170.76 | 6.4446 | 54.8041 | 64.1561 | -1808.4712
2021-11-03 22:00 | -6579.27 | 6.4446 | 54.4279 | 64.1561 | -1928.1937
2021-11-04 23:00 | -7139.83 | 6.4446 | 53.9513 | 64.1561 | -2092.4776
2021-11-06 | -8572.23 | 6.4446 | 52.9495 | 64.1561 | -2512.2726
2021-11-07 01:00 | -9006.61 | 6.4446 | 52.4334 | 64.1561 | -2639.5768
2021-11-08 02:00 | -9249.5 | 6.4446 | 52.0779 | 64.1561 | -2710.7609
2021-11-09 03:00 | -9581.79 | 6.4446 | 51.7172 | 64.1561 | -2808.1454
2021-11-10 04:00 | -9692.81 | 6.4446 | 51.4896 | 64.1561 | -2840.6822
2021-11-11 05:00 | -9867.63 | 6.4446 | 51.2395 | 64.1561 | -2891.9169
2021-11-12 06:00 | -9849.66 | 6.4446 | 51.1478 | 64.1561 | -2886.6504
2021-11-13 07:00 | -9351.78 | 6.4446 | 51.3712 | 64.1561 | -2740.7362
2021-11-14 08:00 | -7553.69 | 6.4446 | 52.4497 | 64.1561 | -2213.768
2021-11-15 09:00 | -6567.13 | 6.4446 | 53.2234 | 64.1561 | -1924.6358
2021-11-16 10:00 | -4765.5 | 6.4446 | 54.499 | 64.1561 | -1396.6302
2021-11-17 11:00 | -3111.38 | 6.4446 | 55.7878 | 64.1561 | -911.8555
2021-11-18 12:00 | -1706.91 | 5.0978 | 56.7268 | 64.1561 | -500.2459
2021-11-19 13:00 | -805.307 | 2.5026 | 57.1538 | 64.1561 | -236.0122
2021-11-20 14:00 | 109.225 | 1 | 58.7216 | 64.1561 | 32.0107
2021-11-21 15:00 | 809.687 | 1 | 58.8916 | 64.1561 | 237.2958
2021-11-22 16:00 | -103.519 | 0.91266 | 58.9517 | 64.1561 | -30.3384
2021-11-23 17:00 | 2533.99 | 1 | 58.9145 | 64.1561 | 742.6392
2021-11-24 18:00 | -1126.31 | 3.8408 | 58.7958 | 64.1561 | -330.0889
2021-11-25 19:00 | -1963.99 | 5.9459 | 58.5497 | 64.1561 | -575.5887
2021-11-26 20:00 | -2978.54 | 6.4446 | 57.905 | 64.1561 | -872.9239
2021-11-27 21:00 | -3703.3 | 6.4446 | 57.3495 | 64.1561 | -1085.3301
2021-11-28 22:00 | -4136.68 | 6.4446 | 56.9648 | 64.1561 | -1212.3412
2021-11-29 23:00 | -4498.53 | 6.4446 | 56.5785 | 64.1561 | -1318.389
2021-12-01 | -5850.39 | 6.4446 | 55.6565 | 64.1561 | -1714.5801
2021-12-02 01:00 | -6138.14 | 6.4446 | 55.267 | 64.1561 | -1798.9113
2021-12-03 02:00 | -6835.92 | 6.4446 | 54.6833 | 64.1561 | -2003.4104
2021-12-04 03:00 | -6904.42 | 6.4446 | 54.4647 | 64.1561 | -2023.4858
2021-12-05 04:00 | -6885.64 | 6.4446 | 54.3509 | 64.1561 | -2017.9819
2021-12-06 05:00 | -6817.13 | 6.4446 | 54.2764 | 64.1561 | -1997.9036
2021-12-07 06:00 | -6465.22 | 6.4446 | 54.4438 | 64.1561 | -1894.7689
2021-12-08 07:00 | -6147.97 | 6.4446 | 54.6352 | 64.1561 | -1801.7921
2021-12-09 08:00 | -4651.52 | 6.4446 | 55.5722 | 64.1561 | -1363.2259
2021-12-10 09:00 | -3175.36 | 6.4446 | 56.6457 | 64.1561 | -930.6062
2021-12-11 10:00 | -1319.66 | 3.8953 | 57.502 | 64.1561 | -386.7542
2021-12-12 11:00 | 0 | 1 | 59.1736 | 64.1561 | 0
2021-12-13 12:00 | 2847.27 | 1 | 76.8158 | 64.1561 | 834.4525
2021-12-14 13:00 | 2870.39 | 1 | 72.6992 | 64.1561 | 841.2283
2021-12-15 14:00 | 2866.48 | 1 | 73.8779 | 64.1561 | 840.0824
2021-12-16 15:00 | 3381.83 | 1.1691 | 71.9999 | 64.1561 | 991.1165
2021-12-17 16:00 | 3125.05 | 1.0819 | 72.2575 | 64.1561 | 915.8617
2021-12-18 17:00 | 2826.1 | 1 | 60.4514 | 64.1561 | 828.2482
2021-12-19 18:00 | 2616.47 | 1 | 60.6116 | 64.1561 | 766.8117
2021-12-20 19:00 | -458.269 | 1.9005 | 60.3947 | 64.1561 | -134.3054
2021-12-21 20:00 | -1270.45 | 4.0402 | 59.8779 | 64.1561 | -372.3321
2021-12-22 21:00 | -2508.75 | 6.4446 | 59.3984 | 64.1561 | -735.242
2021-12-23 22:00 | -3294.16 | 6.4446 | 58.7091 | 64.1561 | -965.423
2021-12-24 23:00 | -4406.79 | 6.4446 | 57.8112 | 64.1561 | -1291.5027
2021-12-26 | -5017.83 | 6.4446 | 57.1521 | 64.1561 | -1470.5808
2021-12-27 01:00 | -5284.74 | 6.4446 | 56.7696 | 64.1561 | -1548.8044
2021-12-28 02:00 | -5749.27 | 6.4446 | 56.3177 | 64.1561 | -1684.9447
2021-12-29 03:00 | -5729.63 | 6.4446 | 56.1573 | 64.1561 | -1679.1888
2021-12-30 04:00 | -5611.04 | 6.4446 | 56.1071 | 64.1561 | -1644.4335
2021-12-31 05:00 | -5725.57 | 6.4446 | 55.9653 | 64.1561 | -1677.9989
2022-01-01 06:00 | -5323.37 | 6.4446 | 56.1298 | 64.1561 | -1560.1257
2022-01-02 07:00 | -5145.04 | 6.4446 | 56.2375 | 64.1561 | -1507.8624
2022-01-03 08:00 | -4219.42 | 6.4446 | 56.8072 | 64.1561 | -1236.5899
2022-01-04 09:00 | -3728.37 | 6.4446 | 57.1994 | 64.1561 | -1092.6774
2022-01-05 10:00 | -2123.95 | 6.2581 | 58.2262 | 64.1561 | -622.4683
2022-01-06 11:00 | 0 | 0 | 59.7782 | 64.1561 | 0
2022-01-07 12:00 | 2749.02 | 1 | 59.4796 | 64.1561 | 805.6582
2022-01-08 13:00 | -297.01 | 1.4564 | 59.8491 | 64.1561 | -87.045
2022-01-09 14:00 | -82.7838 | 0.72835 | 60.1664 | 64.1561 | -24.2615
2022-01-10 15:00 | -221.425 | 1.1829 | 59.9164 | 64.1561 | -64.8933
2022-01-11 16:00 | 2551.7 | 1 | 60.1167 | 64.1561 | 747.8294
2022-01-12 17:00 | 3021.07 | 1 | 60.3502 | 64.1561 | 885.3882
2022-01-13 18:00 | 0 | 0 | 61.2956 | 64.1561 | 0
2022-01-14 19:00 | -374.039 | 1.488 | 60.1642 | 64.1561 | -109.62
2022-01-15 20:00 | -740.316 | 2.5725 | 59.9595 | 64.1561 | -216.9652
2022-01-16 21:00 | -1663.61 | 5.1043 | 59.8199 | 64.1561 | -487.556
2022-01-17 22:00 | -2249.94 | 6.4446 | 59.5988 | 64.1561 | -659.3923
2022-01-18 23:00 | -3171.82 | 6.4446 | 58.8735 | 64.1561 | -929.5687
2022-01-20 | -3586.04 | 6.4446 | 58.4444 | 64.1561 | -1050.9646
2022-01-21 01:00 | -3800.25 | 6.4446 | 58.1888 | 64.1561 | -1113.7433
2022-01-22 02:00 | -3936.74 | 6.4446 | 58.0115 | 64.1561 | -1153.7446
2022-01-23 03:00 | -4016.7 | 6.4446 | 57.8944 | 64.1561 | -1177.1786
2022-01-24 04:00 | -3824.97 | 6.4446 | 57.9301 | 64.1561 | -1120.9881
2022-01-25 05:00 | -3646.69 | 6.4446 | 58.0012 | 64.1561 | -1068.7393
2022-01-26 06:00 | -3238.24 | 6.4446 | 58.2596 | 64.1561 | -949.0345
2022-01-27 07:00 | -3020.44 | 6.4446 | 58.4396 | 64.1561 | -885.2036
2022-01-28 08:00 | -2948.39 | 6.4446 | 58.5265 | 64.1561 | -864.0878
2022-01-29 09:00 | -3272.11 | 6.4446 | 58.3621 | 64.1561 | -958.9608
2022-01-30 10:00 | -1300.74 | 3.7683 | 58.9685 | 64.1561 | -381.2093
2022-01-31 11:00 | 0 | 1 | 60.5223 | 64.1561 | 0
2022-02-01 12:00 | 2500.98 | 1 | 74.9094 | 64.1561 | 732.9649
2022-02-02 13:00 | 2972.24 | 1 | 60.4644 | 64.1561 | 871.0776
2022-02-03 14:00 | 2950.66 | 1 | 60.786 | 64.1561 | 864.7531
2022-02-04 15:00 | 3109.2 | 1 | 60.9688 | 64.1561 | 911.2166
2022-02-05 16:00 | 3178.42 | 1 | 79.9672 | 64.1561 | 931.503
2022-02-06 17:00 | 3174.95 | 1 | 81.7469 | 64.1561 | 930.486
2022-02-07 18:00 | 3111.15 | 1 | 61.3881 | 64.1561 | 911.7881
2022-02-08 19:00 | 3048.43 | 1 | 61.507 | 64.1561 | 893.4066
2022-02-09 20:00 | 2972 | 1 | 61.6228 | 64.1561 | 871.0072
2022-02-10 21:00 | -720.076 | 2.5971 | 61.3449 | 64.1561 | -211.0334
2022-02-11 22:00 | -1459.35 | 4.462 | 60.8237 | 64.1561 | -427.6933
2022-02-12 23:00 | -2842.38 | 6.4446 | 60.1408 | 64.1561 | -833.0193
2022-02-14 | -3991.25 | 6.4446 | 59.1707 | 64.1561 | -1169.7199
2022-02-15 01:00 | -4905.31 | 6.4446 | 58.2974 | 64.1561 | -1437.6045
2022-02-16 02:00 | -5780.48 | 6.4446 | 57.4411 | 64.1561 | -1694.0915
2022-02-17 03:00 | -6601.05 | 6.4446 | 56.6638 | 64.1561 | -1934.5768
2022-02-18 04:00 | -6650.54 | 6.4446 | 56.3417 | 64.1561 | -1949.0809
2022-02-19 05:00 | -6673.27 | 6.4446 | 56.1209 | 64.1561 | -1955.7424
2022-02-20 06:00 | -6764.92 | 6.4446 | 55.9007 | 64.1561 | -1982.6023
2022-02-21 07:00 | -7007.28 | 6.4446 | 55.5966 | 64.1561 | -2053.631
2022-02-22 08:00 | -7383.07 | 6.4446 | 55.2002 | 64.1561 | -2163.7642
2022-02-23 09:00 | -7657.21 | 6.4446 | 54.8857 | 64.1561 | -2244.1067
2022-02-24 10:00 | -7496.99 | 6.4446 | 54.8202 | 64.1561 | -2197.1509
2022-02-25 11:00 | -7408.83 | 6.4446 | 54.7523 | 64.1561 | -2171.3137
2022-02-26 12:00 | -7086.09 | 6.4446 | 54.8298 | 64.1561 | -2076.728
2022-02-27 13:00 | -6467.85 | 6.4446 | 55.1322 | 64.1561 | -1895.5397
2022-02-28 14:00 | -5288.22 | 6.4446 | 55.8433 | 64.1561 | -1549.8243
2022-03-01 15:00 | -4899.31 | 6.4446 | 56.1815 | 64.1561 | -1435.846
2022-03-02 16:00 | -3064.08 | 6.4446 | 57.3603 | 64.1561 | -897.9932
2022-03-03 17:00 | -3055.66 | 6.4446 | 57.5806 | 64.1561 | -895.5255
2022-03-04 18:00 | -1846.49 | 5.4047 | 58.2226 | 64.1561 | -541.1528
2022-03-05 19:00 | -1700.52 | 5.0302 | 58.4388 | 64.1561 | -498.3732
2022-03-06 20:00 | -2763.44 | 6.4446 | 58.2303 | 64.1561 | -809.8843
2022-03-07 21:00 | -3554.01 | 6.4446 | 57.749 | 64.1561 | -1041.5775
2022-03-08 22:00 | -4053.78 | 6.4446 | 57.3696 | 64.1561 | -1188.0456
2022-03-09 23:00 | -5014.8 | 6.4446 | 56.7297 | 64.1561 | -1469.6928
2022-03-11 | -5401.73 | 6.4446 | 56.3579 | 64.1561 | -1583.0908
2022-03-12 01:00 | -6217.53 | 6.4446 | 55.7381 | 64.1561 | -1822.1782
2022-03-13 02:00 | -6987.17 | 6.4446 | 55.1131 | 64.1561 | -2047.7374
2022-03-14 03:00 | -7102.27 | 6.4446 | 54.8637 | 64.1561 | -2081.4699
2022-03-15 04:00 | -7230.05 | 6.4446 | 54.6457 | 64.1561 | -2118.9185
2022-03-16 05:00 | -7130.96 | 6.4446 | 54.5964 | 64.1561 | -2089.8781
2022-03-17 06:00 | -7184.07 | 6.4446 | 54.4699 | 64.1561 | -2105.4431
2022-03-18 07:00 | -7566.34 | 6.4446 | 54.1503 | 64.1561 | -2217.4754
2022-03-19 08:00 | -6962.72 | 6.4446 | 54.411 | 64.1561 | -2040.5718
2022-03-20 09:00 | -6489.38 | 6.4446 | 54.6923 | 64.1561 | -1901.8495
2022-03-21 10:00 | -4930.19 | 6.4446 | 55.67 | 64.1561 | -1444.8961
2022-03-22 11:00 | -3757.39 | 6.4446 | 56.5519 | 64.1561 | -1101.1823
2022-03-23 12:00 | -3016.46 | 6.4446 | 57.21 | 64.1561 | -884.0372
2022-03-24 13:00 | -2630.04 | 6.4446 | 57.6469 | 64.1561 | -770.7886
2022-03-25 14:00 | -2822.23 | 6.4446 | 57.6974 | 64.1561 | -827.114
2022-03-26 15:00 | -3017.53 | 6.4446 | 57.6735 | 64.1561 | -884.3507
2022-03-27 16:00 | -3065.01 | 6.4446 | 57.6782 | 64.1561 | -898.2658
2022-03-28 17:00 | -4332.03 | 6.4446 | 56.9282 | 64.1561 | -1269.5927
2022-03-29 18:00 | -5129.08 | 6.4446 | 56.3077 | 64.1561 | -1503.185
2022-03-30 19:00 | -6249.34 | 6.4446 | 55.4614 | 64.1561 | -1831.5008
2022-03-31 20:00 | -6707.88 | 6.4446 | 54.9677 | 64.1561 | -1965.8856
2022-04-01 21:00 | -7995.42 | 6.4446 | 54.0078 | 64.1561 | -2343.2263
2022-04-02 22:00 | -8439.39 | 6.4446 | 53.4584 | 64.1561 | -2473.3411
2022-04-03 23:00 | -9661.48 | 6.4446 | 52.4827 | 64.1561 | -2831.5003
2022-04-05 | -10844.7 | 6.4446 | 51.4614 | 64.1561 | -3178.2678
2022-04-06 01:00 | -10799.9 | 6.4446 | 51.1479 | 64.1561 | -3165.1382
2022-04-07 02:00 | -11265.4 | 6.4446 | 50.6388 | 64.1561 | -3301.5628
2022-04-08 03:00 | -11420.3 | 6.4446 | 50.3257 | 64.1561 | -3346.9595
2022-04-09 04:00 | -11594.8 | 6.4446 | 50.0138 | 64.1561 | -3398.1004
2022-04-10 05:00 | -11928.4 | 6.4446 | 49.6405 | 64.1561 | -3495.869
2022-04-11 06:00 | -11978.7 | 6.4446 | 49.444 | 64.1561 | -3510.6104
2022-04-12 07:00 | -11466.9 | 6.4446 | 49.6179 | 64.1561 | -3360.6167
2022-04-13 08:00 | -10186.1 | 6.4446 | 50.3421 | 64.1561 | -2985.2512
2022-04-14 09:00 | -9361.04 | 6.4446 | 50.9254 | 64.1561 | -2743.45
2022-04-15 10:00 | -7805.2 | 6.4446 | 51.9688 | 64.1561 | -2287.4783
2022-04-16 11:00 | -6599.31 | 6.4446 | 52.9094 | 64.1561 | -1934.0668
2022-04-17 12:00 | -5785.43 | 6.4446 | 53.6538 | 64.1561 | -1695.5422
2022-04-18 13:00 | -5069.99 | 6.4446 | 54.3186 | 64.1561 | -1485.8674
2022-04-19 14:00 | -4600.9 | 6.4446 | 54.8194 | 64.1561 | -1348.3907
2022-04-20 15:00 | -4257.06 | 6.4446 | 55.2261 | 64.1561 | -1247.6211
2022-04-21 16:00 | -4308.87 | 6.4446 | 55.3524 | 64.1561 | -1262.8051
2022-04-22 17:00 | -3902.08 | 6.4446 | 55.708 | 64.1561 | -1143.5868
2022-04-23 18:00 | -5437.1 | 6.4446 | 54.9121 | 64.1561 | -1593.4567
2022-04-24 19:00 | -6269.49 | 6.4446 | 54.3367 | 64.1561 | -1837.4061
2022-04-25 20:00 | -6848.94 | 6.4446 | 53.8659 | 64.1561 | -2007.2262
2022-04-26 21:00 | -7499.81 | 6.4446 | 53.3649 | 64.1561 | -2197.9773
2022-04-27 22:00 | -7953.9 | 6.4446 | 52.9512 | 64.1561 | -2331.058
2022-04-28 23:00 | -8441.49 | 6.4446 | 52.5037 | 64.1561 | -2473.9565
2022-04-30 | -10162 | 6.4446 | 51.3186 | 64.1561 | -2978.1882
2022-05-01 01:00 | -10444.7 | 6.4446 | 50.858 | 64.1561 | -3061.0394
2022-05-02 02:00 | -10872.2 | 6.4446 | 50.3854 | 64.1561 | -3186.3273
2022-05-03 03:00 | -10928.9 | 6.4446 | 50.163 | 64.1561 | -3202.9444
2022-05-04 04:00 | -10942.3 | 6.4446 | 49.9996 | 64.1561 | -3206.8716
2022-05-05 05:00 | -11137.8 | 6.4446 | 49.7453 | 64.1561 | -3264.167
2022-05-06 06:00 | -11039.2 | 6.4446 | 49.6971 | 64.1561 | -3235.2702
2022-05-07 07:00 | -10371.8 | 6.4446 | 50.0284 | 64.1561 | -3039.6745
2022-05-08 08:00 | -9293.82 | 6.4446 | 50.6932 | 64.1561 | -2723.7498
2022-05-09 09:00 | -8287.11 | 6.4446 | 51.4059 | 64.1561 | -2428.7122
2022-05-10 10:00 | -6882.96 | 6.4446 | 52.3952 | 64.1561 | -2017.1965
2022-05-11 11:00 | -5434.26 | 6.4446 | 53.4901 | 64.1561 | -1592.6244
2022-05-12 12:00 | -3927.02 | 6.4446 | 54.6946 | 64.1561 | -1150.896
2022-05-13 13:00 | -2970.08 | 6.4446 | 55.611 | 64.1561 | -870.4445
2022-05-14 14:00 | -3028.31 | 6.4446 | 55.887 | 64.1561 | -887.5101
2022-05-15 15:00 | -2473.2 | 6.4446 | 56.42 | 64.1561 | -724.8234
2022-05-16 16:00 | -2641.78 | 6.4446 | 56.5254 | 64.1561 | -774.2293
2022-05-17 17:00 | -2285.14 | 6.4446 | 56.8805 | 64.1561 | -669.7084
2022-05-18 18:00 | -3804.69 | 6.4446 | 56.1087 | 64.1561 | -1115.0446
2022-05-19 19:00 | -5048.81 | 6.4446 | 55.3011 | 64.1561 | -1479.6601
2022-05-20 20:00 | -5988.18 | 6.4446 | 54.5935 | 64.1561 | -1754.9623
2022-05-21 21:00 | -6476 | 6.4446 | 54.147 | 64.1561 | -1897.9282
2022-05-22 22:00 | -6929.35 | 6.4446 | 53.7405 | 64.1561 | -2030.792
2022-05-23 23:00 | -7285.52 | 6.4446 | 53.3783 | 64.1561 | -2135.1751
2022-05-25 | -8599.03 | 6.4446 | 52.4561 | 64.1561 | -2520.1269
2022-05-26 01:00 | -9368.53 | 6.4446 | 51.7608 | 64.1561 | -2745.6451
2022-05-27 02:00 | -9724.26 | 6.4446 | 51.3254 | 64.1561 | -2849.8993
2022-05-28 03:00 | -10013 | 6.4446 | 50.9708 | 64.1561 | -2934.5206
2022-05-29 04:00 | -10181.5 | 6.4446 | 50.7063 | 64.1561 | -2983.9031
2022-05-30 05:00 | -10138.4 | 6.4446 | 50.5811 | 64.1561 | -2971.2717
2022-05-31 06:00 | -9688.36 | 6.4446 | 50.7646 | 64.1561 | -2839.378
2022-06-01 07:00 | -9915.26 | 6.4446 | 50.6122 | 64.1561 | -2905.8759
2022-06-02 08:00 | -8178.58 | 6.4446 | 51.6142 | 64.1561 | -2396.9052
2022-06-03 09:00 | -6988.09 | 6.4446 | 52.4845 | 64.1561 | -2048.007
2022-06-04 10:00 | -5638.45 | 6.4446 | 53.5062 | 64.1561 | -1652.4666
2022-06-05 11:00 | -4214.96 | 6.4446 | 54.6114 | 64.1561 | -1235.2828
2022-06-06 12:00 | -2304.29 | 6.4446 | 56.0697 | 64.1561 | -675.3207
2022-06-07 13:00 | -1794.93 | 5.3406 | 56.5644 | 64.1561 | -526.0421
2022-06-08 14:00 | -2580.55 | 6.4446 | 56.6188 | 64.1561 | -756.2845
2022-06-09 15:00 | -3045.99 | 6.4446 | 56.4482 | 64.1561 | -892.6915
2022-06-10 16:00 | -2969.59 | 6.4446 | 56.5517 | 64.1561 | -870.3009
2022-06-11 17:00 | -3326.27 | 6.4446 | 56.4129 | 64.1561 | -974.8335
2022-06-12 18:00 | -3851.14 | 6.4446 | 56.1126 | 64.1561 | -1128.6577
2022-06-13 19:00 | -4348.32 | 6.4446 | 55.7847 | 64.1561 | -1274.3668
2022-06-14 20:00 | -4861.78 | 6.4446 | 55.4316 | 64.1561 | -1424.8471
2022-06-15 21:00 | -5939.27 | 6.4446 | 54.7184 | 64.1561 | -1740.6282
2022-06-16 22:00 | -6226.96 | 6.4446 | 54.3905 | 64.1561 | -1824.9418
2022-06-17 23:00 | -7313.55 | 6.4446 | 53.6077 | 64.1561 | -2143.3899
2022-06-19 | -7353.36 | 6.4446 | 53.3855 | 64.1561 | -2155.0571
2022-06-20 01:00 | -7516.33 | 6.4446 | 53.155 | 64.1561 | -2202.8189
2022-06-21 02:00 | -7690.66 | 6.4446 | 52.9534 | 64.1561 | -2253.91
2022-06-22 03:00 | -7590.35 | 6.4446 | 52.9346 | 64.1561 | -2224.512
2022-06-23 04:00 | -7565.59 | 6.4446 | 52.9004 | 64.1561 | -2217.2556
2022-06-24 05:00 | -7513.09 | 6.4446 | 52.9104 | 64.1561 | -2201.8693
2022-06-25 06:00 | -7116.95 | 6.4446 | 53.1348 | 64.1561 | -2085.7722
2022-06-26 07:00 | -7022.67 | 6.4446 | 53.2252 | 64.1561 | -2058.1414
2022-06-27 08:00 | -7007 | 6.4446 | 53.2535 | 64.1561 | -2053.549
2022-06-28 09:00 | -7699.3 | 6.4446 | 52.8355 | 64.1561 | -2256.4421
2022-06-29 10:00 | -7360.19 | 6.4446 | 52.9514 | 64.1561 | -2157.0588
2022-06-30 11:00 | -6658.58 | 6.4446 | 53.3568 | 64.1561 | -1951.4372
2022-07-01 12:00 | -5937.71 | 6.4446 | 53.8355 | 64.1561 | -1740.171
2022-07-02 13:00 | -5083.13 | 6.4446 | 54.4288 | 64.1561 | -1489.7183
2022-07-03 14:00 | -3399.01 | 6.4446 | 55.5751 | 64.1561 | -996.1515
2022-07-04 15:00 | -2452.29 | 6.4446 | 56.4169 | 64.1561 | -718.6953
2022-07-05 16:00 | -1842.74 | 5.4691 | 56.8496 | 64.1561 | -540.0538
2022-07-06 17:00 | -2662.01 | 6.4446 | 56.7799 | 64.1561 | -780.1581
2022-07-07 18:00 | -3060.38 | 6.4446 | 56.6055 | 64.1561 | -896.9088
2022-07-08 19:00 | -3828.56 | 6.4446 | 56.174 | 64.1561 | -1122.0402
2022-07-09 20:00 | -3990.17 | 6.4446 | 56.0394 | 64.1561 | -1169.4034
2022-07-10 21:00 | -4952.3 | 6.4446 | 55.4451 | 64.1561 | -1451.3759
2022-07-11 22:00 | -5530.74 | 6.4446 | 54.9922 | 64.1561 | -1620.8999
2022-07-12 23:00 | -6399.18 | 6.4446 | 54.3644 | 64.1561 | -1875.4145
2022-07-14 | -6823.52 | 6.4446 | 53.9686 | 64.1561 | -1999.7763
2022-07-15 01:00 | -7102.94 | 6.4446 | 53.6799 | 64.1561 | -2081.6662
2022-07-16 02:00 | -7110.89 | 6.4446 | 53.5594 | 64.1561 | -2083.9961
2022-07-17 03:00 | -7341.5 | 6.4446 | 53.3379 | 64.1561 | -2151.5813
2022-07-18 04:00 | -7095.4 | 6.4446 | 53.3941 | 64.1561 | -2079.4565
2022-07-19 05:00 | -6946.53 | 6.4446 | 53.4554 | 64.1561 | -2035.827
2022-07-20 06:00 | -6516 | 6.4446 | 53.7086 | 64.1561 | -1909.6511
2022-07-21 07:00 | -6198.91 | 6.4446 | 53.9399 | 64.1561 | -1816.7212
2022-07-22 08:00 | -6475.83 | 6.4446 | 53.8161 | 64.1561 | -1897.8784
2022-07-23 09:00 | -6767.94 | 6.4446 | 53.6362 | 64.1561 | -1983.4874
2022-07-24 10:00 | -6621.28 | 6.4446 | 53.6869 | 64.1561 | -1940.5056
2022-07-25 11:00 | -6177.2 | 6.4446 | 53.953 | 64.1561 | -1810.3586
2022-07-26 12:00 | -5879.3 | 6.4446 | 54.1677 | 64.1561 | -1723.0527
2022-07-27 13:00 | -5957.88 | 6.4446 | 54.1542 | 64.1561 | -1746.0823
2022-07-28 14:00 | -5979.89 | 6.4446 | 54.1373 | 64.1561 | -1752.5328
2022-07-29 15:00 | -5520.74 | 6.4446 | 54.4097 | 64.1561 | -1617.9692
2022-07-30 16:00 | -4656.73 | 6.4446 | 54.9745 | 64.1561 | -1364.7528
2022-07-31 17:00 | -4195.88 | 6.4446 | 55.3657 | 64.1561 | -1229.691
2022-08-01 18:00 | -4038.59 | 6.4446 | 55.568 | 64.1561 | -1183.5939
2022-08-02 19:00 | -4359.4 | 6.4446 | 55.4554 | 64.1561 | -1277.614
2022-08-03 20:00 | -4578.77 | 6.4446 | 55.3532 | 64.1561 | -1341.905
2022-08-04 21:00 | -5485.39 | 6.4446 | 54.8214 | 64.1561 | -1607.6091
2022-08-05 22:00 | -5753.47 | 6.4446 | 54.5803 | 64.1561 | -1686.1756
2022-08-06 23:00 | -6200.28 | 6.4446 | 54.2446 | 64.1561 | -1817.1227
2022-08-08 | -6368.74 | 6.4446 | 54.0648 | 64.1561 | -1866.4934
2022-08-09 01:00 | -6298.09 | 6.4446 | 54.0495 | 64.1561 | -1845.788
2022-08-10 02:00 | -6398.42 | 6.4446 | 53.9647 | 64.1561 | -1875.1918
2022-08-11 03:00 | -6328.3 | 6.4446 | 53.9874 | 64.1561 | -1854.6417
2022-08-12 04:00 | -5971.52 | 6.4446 | 54.1911 | 64.1561 | -1750.0798
2022-08-13 05:00 | -5727.55 | 6.4446 | 54.3699 | 64.1561 | -1678.5792
2022-08-14 06:00 | -5069.57 | 6.4446 | 54.8078 | 64.1561 | -1485.7443
2022-08-15 07:00 | -4846.91 | 6.4446 | 55.0333 | 64.1561 | -1420.4891
2022-08-16 08:00 | -4648.53 | 6.4446 | 55.2344 | 64.1561 | -1362.3497
2022-08-17 09:00 | -5158.89 | 6.4446 | 55.0067 | 64.1561 | -1511.9214
2022-08-18 10:00 | -4269.05 | 6.4446 | 55.5472 | 64.1561 | -1251.1351
2022-08-19 11:00 | -4337.78 | 6.4446 | 55.6183 | 64.1561 | -1271.2778
2022-08-20 12:00 | -2196.44 | 6.4446 | 56.9798 | 64.1561 | -643.713
2022-08-21 13:00 | -1403.81 | 4.1275 | 57.2541 | 64.1561 | -411.4161
2022-08-22 14:00 | -766.721 | 2.4719 | 57.6276 | 64.1561 | -224.7037
2022-08-23 15:00 | -396.378 | 1.5483 | 58.0746 | 64.1561 | -116.1669
2022-08-24 16:00 | -179.353 | 1.0062 | 58.5779 | 64.1561 | -52.5632
2022-08-25 17:00 | -1085.92 | 3.6573 | 58.2997 | 64.1561 | -318.2517
2022-08-26 18:00 | -1995.56 | 6.0843 | 58.1968 | 64.1561 | -584.8409
2022-08-27 19:00 | -3264.7 | 6.4446 | 57.4356 | 64.1561 | -956.7891
2022-08-28 20:00 | -4060.59 | 6.4446 | 56.8023 | 64.1561 | -1190.0415
2022-08-29 21:00 | -5555.12 | 6.4446 | 55.7472 | 64.1561 | -1628.045
2022-08-30 22:00 | -6346.56 | 6.4446 | 55.0133 | 64.1561 | -1859.9931
2022-08-31 23:00 | -7510.77 | 6.4446 | 54.0797 | 64.1561 | -2201.1894
2022-09-02 | -8259.59 | 6.4446 | 53.3469 | 64.1561 | -2420.6469
2022-09-03 01:00 | -8326.07 | 6.4446 | 53.0406 | 64.1561 | -2440.1302
2022-09-04 02:00 | -8955.64 | 6.4446 | 52.464 | 64.1561 | -2624.639
2022-09-05 03:00 | -8892.96 | 6.4446 | 52.2872 | 64.1561 | -2606.2693
2022-09-06 04:00 | -9300.16 | 6.4446 | 51.8748 | 64.1561 | -2725.6078
2022-09-07 05:00 | -9175.49 | 6.4446 | 51.7836 | 64.1561 | -2689.0707
2022-09-08 06:00 | -9021.04 | 6.4446 | 51.7611 | 64.1561 | -2643.8058
2022-09-09 07:00 | -8966.52 | 6.4446 | 51.7131 | 64.1561 | -2627.8276
2022-09-10 08:00 | -7056.11 | 6.4446 | 52.8081 | 64.1561 | -2067.9417
2022-09-11 09:00 | -5714.01 | 6.4446 | 53.784 | 64.1561 | -1674.611
2022-09-12 10:00 | -3620.78 | 6.4446 | 55.285 | 64.1561 | -1061.1459
2022-09-13 11:00 | -1830.44 | 5.5073 | 56.5366 | 64.1561 | -536.449
2022-09-14 12:00 | -845.535 | 2.5858 | 56.9651 | 64.1561 | -247.8018
2022-09-15 13:00 | -236.815 | 1.0806 | 57.7598 | 64.1561 | -69.4036
2022-09-16 14:00 | -998.958 | 3.4243 | 57.7871 | 64.1561 | -292.7657
2022-09-17 15:00 | -1149.88 | 3.6521 | 57.8342 | 64.1561 | -336.9966
2022-09-18 16:00 | -963.604 | 3.0816 | 57.9409 | 64.1561 | -282.4045
2022-09-19 17:00 | -1319.77 | 4.1703 | 58.0445 | 64.1561 | -386.7864
2022-09-20 18:00 | -1596.95 | 4.8744 | 58.0574 | 64.1561 | -468.0198
2022-09-21 19:00 | -2274.74 | 6.4446 | 57.9909 | 64.1561 | -666.6605
2022-09-22 20:00 | -2876.84 | 6.4446 | 57.6044 | 64.1561 | -843.1186
2022-09-23 21:00 | -4027.76 | 6.4446 | 56.857 | 64.1561 | -1180.4199
2022-09-24 22:00 | -4542.75 | 6.4446 | 56.3939 | 64.1561 | -1331.3486
2022-09-25 23:00 | -5597.93 | 6.4446 | 55.6142 | 64.1561 | -1640.5913
2022-09-27 | -6383.03 | 6.4446 | 54.9352 | 64.1561 | -1870.6814
2022-09-28 01:00 | -6486.37 | 6.4446 | 54.6543 | 64.1561 | -1900.9674
2022-09-29 02:00 | -6798.24 | 6.4446 | 54.3254 | 64.1561 | -1992.3675
2022-09-30 03:00 | -7027.28 | 6.4446 | 54.0615 | 64.1561 | -2059.4925
2022-10-01 04:00 | -7102.39 | 6.4446 | 53.892 | 64.1561 | -2081.505
2022-10-02 05:00 | -6713.65 | 6.4446 | 54.0384 | 64.1561 | -1967.5766
2022-10-03 06:00 | -6801.07 | 6.4446 | 53.9646 | 64.1561 | -1993.1969
2022-10-04 07:00 | -6171.56 | 6.4446 | 54.3082 | 64.1561 | -1808.7057
2022-10-05 08:00 | -6078.61 | 6.4446 | 54.3924 | 64.1561 | -1781.4647
2022-10-06 09:00 | -6736.92 | 6.4446 | 54.0131 | 64.1561 | -1974.3964
2022-10-07 10:00 | -7091.59 | 6.4446 | 53.7129 | 64.1561 | -2078.3399
2022-10-08 11:00 | -6619.17 | 6.4446 | 53.8965 | 64.1561 | -1939.8872
2022-10-09 12:00 | -5899.88 | 6.4446 | 54.3182 | 64.1561 | -1729.0841
2022-10-10 13:00 | -5954.93 | 6.4446 | 54.3215 | 64.1561 | -1745.2177
2022-10-11 14:00 | -5616.55 | 6.4446 | 54.5108 | 64.1561 | -1646.0483
2022-10-12 15:00 | -5535.75 | 6.4446 | 54.5776 | 64.1561 | -1622.3682
2022-10-13 16:00 | -5256.75 | 6.4446 | 54.7651 | 64.1561 | -1540.6013
2022-10-14 17:00 | -3796.46 | 6.4446 | 55.6828 | 64.1561 | -1112.6326
2022-10-15 18:00 | -4171.07 | 6.4446 | 55.6278 | 64.1561 | -1222.4199
2022-10-16 19:00 | -4309.07 | 6.4446 | 55.5993 | 64.1561 | -1262.8638
2022-10-17 20:00 | -4270.81 | 6.4446 | 55.6362 | 64.1561 | -1251.6509
2022-10-18 21:00 | -4414.8 | 6.4446 | 55.6003 | 64.1561 | -1293.8502
2022-10-19 22:00 | -4198.5 | 6.4446 | 55.7726 | 64.1561 | -1230.4589
2022-10-20 23:00 | -4166.09 | 6.4446 | 55.8415 | 64.1561 | -1220.9605
2022-10-22 | -5530.14 | 6.4446 | 55.0659 | 64.1561 | -1620.724
2022-10-23 01:00 | -5255.37 | 6.4446 | 55.1269 | 64.1561 | -1540.1969
2022-10-24 02:00 | -5036.62 | 6.4446 | 55.2493 | 64.1561 | -1476.0876
2022-10-25 03:00 | -5025.96 | 6.4446 | 55.2997 | 64.1561 | -1472.9635
2022-10-26 04:00 | -4988.82 | 6.4446 | 55.3434 | 64.1561 | -1462.0788
2022-10-27 05:00 | -4975.35 | 6.4446 | 55.3535 | 64.1561 | -1458.1311
2022-10-28 06:00 | -4757.66 | 6.4446 | 55.5162 | 64.1561 | -1394.3325
2022-10-29 07:00 | -3874.63 | 6.4446 | 56.0991 | 64.1561 | -1135.542
2022-10-30 08:00 | -4236.92 | 6.4446 | 56.0048 | 64.1561 | -1241.7187
2022-10-31 09:00 | -5588.2 | 6.4446 | 55.2198 | 64.1561 | -1637.7398
2022-11-01 10:00 | -6301.54 | 6.4446 | 54.6516 | 64.1561 | -1846.7991
2022-11-02 11:00 | -7265.01 | 6.4446 | 53.9153 | 64.1561 | -2129.1643
2022-11-03 12:00 | -6892.3 | 6.4446 | 53.9558 | 64.1561 | -2019.9337
2022-11-04 13:00 | -6008.45 | 6.4446 | 54.3963 | 64.1561 | -1760.9029
2022-11-05 14:00 | -6209.33 | 6.4446 | 54.2924 | 64.1561 | -1819.775
2022-11-06 15:00 | -7142.12 | 6.4446 | 53.6915 | 64.1561 | -2093.1488
2022-11-07 16:00 | -7646.86 | 6.4446 | 53.2383 | 64.1561 | -2241.0734
2022-11-08 17:00 | -6596.83 | 6.4446 | 53.7361 | 64.1561 | -1933.34
2022-11-09 18:00 | -8117.71 | 6.4446 | 52.8355 | 64.1561 | -2379.066
2022-11-10 19:00 | -8577.79 | 6.4446 | 52.3472 | 64.1561 | -2513.9021
2022-11-11 20:00 | -9200.97 | 6.4446 | 51.7593 | 64.1561 | -2696.5381
2022-11-12 21:00 | -9848.72 | 6.4446 | 51.1864 | 64.1561 | -2886.3749
2022-11-13 22:00 | -10033.4 | 6.4446 | 50.8818 | 64.1561 | -2940.4993
2022-11-14 23:00 | -10848 | 6.4446 | 50.2141 | 64.1561 | -3179.235
2022-11-16 | -12323.3 | 6.4446 | 49.1116 | 64.1561 | -3611.6027
2022-11-17 01:00 | -12462.8 | 6.4446 | 48.697 | 64.1561 | -3652.4861
2022-11-18 02:00 | -12577 | 6.4446 | 48.3918 | 64.1561 | -3685.9548
2022-11-19 03:00 | -12863.1 | 6.4446 | 48.0395 | 64.1561 | -3769.8025
2022-11-20 04:00 | -12842.5 | 6.4446 | 47.8587 | 64.1561 | -3763.7652
2022-11-21 05:00 | -12936.8 | 6.4446 | 47.6321 | 64.1561 | -3791.4018
2022-11-22 06:00 | -12878.3 | 6.4446 | 47.536 | 64.1561 | -3774.2572
2022-11-23 07:00 | -12618.5 | 6.4446 | 47.5742 | 64.1561 | -3698.1173
2022-11-24 08:00 | -11501.7 | 6.4446 | 48.1739 | 64.1561 | -3370.8155
2022-11-25 09:00 | -9771.65 | 6.4446 | 49.2823 | 64.1561 | -2863.7879
2022-11-26 10:00 | -8300.31 | 6.4446 | 50.3729 | 64.1561 | -2432.5807
2022-11-27 11:00 | -6057.56 | 6.4446 | 51.9977 | 64.1561 | -1775.2956
2022-11-28 12:00 | -4593.67 | 6.4446 | 53.2892 | 64.1561 | -1346.2718
2022-11-29 13:00 | -3546.31 | 6.4446 | 54.3344 | 64.1561 | -1039.3209
2022-11-30 14:00 | -2937.92 | 6.4446 | 55.0764 | 64.1561 | -861.0194
2022-12-01 15:00 | -2142.55 | 6.4446 | 55.8825 | 64.1561 | -627.9194
2022-12-02 16:00 | -2297.01 | 6.4446 | 56.1165 | 64.1561 | -673.1872
2022-12-03 17:00 | -3240.36 | 6.4446 | 55.7487 | 64.1561 | -949.6558
2022-12-04 18:00 | -4531.12 | 6.4446 | 55.0286 | 64.1561 | -1327.9402
2022-12-05 19:00 | -5623.25 | 6.4446 | 54.313 | 64.1561 | -1648.0119
2022-12-06 20:00 | -6206.02 | 6.4446 | 53.8533 | 64.1561 | -1818.8049
2022-12-07 21:00 | -7688.91 | 6.4446 | 52.8424 | 64.1561 | -2253.3971
2022-12-08 22:00 | -8273.17 | 6.4446 | 52.2575 | 64.1561 | -2424.6268
2022-12-09 23:00 | -9242.26 | 6.4446 | 51.4616 | 64.1561 | -2708.639
2022-12-11 | -9776.87 | 6.4446 | 50.9122 | 64.1561 | -2865.3178
2022-12-12 01:00 | -9999.5 | 6.4446 | 50.5666 | 64.1561 | -2930.5642
2022-12-13 02:00 | -10259.6 | 6.4446 | 50.2329 | 64.1561 | -3006.7919
2022-12-14 03:00 | -10927.7 | 6.4446 | 49.6686 | 64.1561 | -3202.5927
2022-12-15 04:00 | -10617.9 | 6.4446 | 49.6554 | 64.1561 | -3111.7993
2022-12-16 05:00 | -10640.1 | 6.4446 | 49.5437 | 64.1561 | -3118.3055
2022-12-17 06:00 | -10312.9 | 6.4446 | 49.6677 | 64.1561 | -3022.4126
2022-12-18 07:00 | -10263 | 6.4446 | 49.6639 | 64.1561 | -3007.7884
2022-12-19 08:00 | -9224.7 | 6.4446 | 50.2555 | 64.1561 | -2703.4927
2022-12-20 09:00 | -8125.95 | 6.4446 | 51.0111 | 64.1561 | -2381.4809
2022-12-21 10:00 | -6647.41 | 6.4446 | 52.0628 | 64.1561 | -1948.1636
2022-12-22 11:00 | -4695.73 | 6.4446 | 53.4865 | 64.1561 | -1376.1826
2022-12-23 12:00 | -3291.94 | 6.4446 | 54.6851 | 64.1561 | -964.7724
2022-12-24 13:00 | -2340.5 | 6.4446 | 55.6253 | 64.1561 | -685.9328
2022-12-25 14:00 | -2058.74 | 6.1776 | 56.0709 | 64.1561 | -603.3571
2022-12-26 15:00 | -2009.56 | 6.0248 | 56.329 | 64.1561 | -588.9439
2022-12-27 16:00 | -2761.45 | 6.4446 | 56.1525 | 64.1561 | -809.3011
2022-12-28 17:00 | -3283.94 | 6.4446 | 55.8985 | 64.1561 | -962.4278
2022-12-29 18:00 | -3631.25 | 6.4446 | 55.7073 | 64.1561 | -1064.2143
2022-12-30 19:00 | -4372.23 | 6.4446 | 55.2725 | 64.1561 | -1281.3741
2022-12-31 20:00 | -4901.21 | 6.4446 | 54.9037 | 64.1561 | -1436.4029
2023-01-01 21:00 | -5810.04 | 6.4446 | 54.288 | 64.1561 | -1702.7546
2023-01-02 22:00 | -6277.94 | 6.4446 | 53.8871 | 64.1561 | -1839.8826
2023-01-03 23:00 | -7138.94 | 6.4446 | 53.252 | 64.1561 | -2092.2168
2023-01-05 | -7600.67 | 6.4446 | 52.81 | 64.1561 | -2227.5365
2023-01-06 01:00 | -7618.93 | 6.4446 | 52.6468 | 64.1561 | -2232.888
2023-01-07 02:00 | -8004.33 | 6.4446 | 52.3145 | 64.1561 | -2345.8376
2023-01-08 03:00 | -7985.53 | 6.4446 | 52.2191 | 64.1561 | -2340.3278
2023-01-09 04:00 | -7950.92 | 6.4446 | 52.1693 | 64.1561 | -2330.1846
2023-01-10 05:00 | -7830.89 | 6.4446 | 52.207 | 64.1561 | -2295.0073
2023-01-11 06:00 | -7419.14 | 6.4446 | 52.4441 | 64.1561 | -2174.3353
2023-01-12 07:00 | -7448.64 | 6.4446 | 52.4586 | 64.1561 | -2182.9809
2023-01-13 08:00 | -6555.52 | 6.4446 | 53.0124 | 64.1561 | -1921.2333
2023-01-14 09:00 | -5214.53 | 6.4446 | 53.9309 | 64.1561 | -1528.2279
2023-01-15 10:00 | -3704.75 | 6.4446 | 55.0562 | 64.1561 | -1085.755
2023-01-16 11:00 | -1842.68 | 5.5673 | 56.2904 | 64.1561 | -540.0362
2023-01-17 12:00 | -907.527 | 2.7729 | 56.6677 | 64.1561 | -265.9699
2023-01-18 13:00 | -385.481 | 1.5012 | 57.2771 | 64.1561 | -112.9733
2023-01-19 14:00 | 0 | 0 | 58.5638 | 64.1561 | 0
2023-01-20 15:00 | 1499.71 | 1 | 58.4496 | 64.1561 | 439.5216
2023-01-21 16:00 | 2913.93 | 1 | 58.4672 | 64.1561 | 853.9886
2023-01-22 17:00 | -82.3674 | 0.85945 | 59.182 | 64.1561 | -24.1395
2023-01-23 18:00 | -849.389 | 2.9869 | 58.3748 | 64.1561 | -248.9313
2023-01-24 19:00 | -1745.12 | 5.4155 | 58.172 | 64.1561 | -511.4442
2023-01-25 20:00 | -2504.89 | 6.4446 | 57.8653 | 64.1561 | -734.1108
2023-01-26 21:00 | -3731.97 | 6.4446 | 57.0176 | 64.1561 | -1093.7324
2023-01-27 22:00 | -4506.15 | 6.4446 | 56.3289 | 64.1561 | -1320.6222
2023-01-28 23:00 | -5579.63 | 6.4446 | 55.4963 | 64.1561 | -1635.2281
2023-01-30 | -5931.66 | 6.4446 | 55.0628 | 64.1561 | -1738.3979
2023-01-31 01:00 | -6328.58 | 6.4446 | 54.648 | 64.1561 | -1854.7237
2023-02-01 02:00 | -6442.75 | 6.4446 | 54.4206 | 64.1561 | -1888.1836
2023-02-02 03:00 | -6563.51 | 6.4446 | 54.216 | 64.1561 | -1923.5749
2023-02-03 04:00 | -6608.69 | 6.4446 | 54.0605 | 64.1561 | -1936.8158
2023-02-04 05:00 | -6406.7 | 6.4446 | 54.1079 | 64.1561 | -1877.6184
2023-02-05 06:00 | -5940.9 | 6.4446 | 54.3553 | 64.1561 | -1741.1059
2023-02-06 07:00 | -5854.13 | 6.4446 | 54.4318 | 64.1561 | -1715.6761
2023-02-07 08:00 | -5646.22 | 6.4446 | 54.5666 | 64.1561 | -1654.7437
2023-02-08 09:00 | -5416.45 | 6.4446 | 54.7275 | 64.1561 | -1587.4048
2023-02-09 10:00 | -4228.88 | 6.4446 | 55.4826 | 64.1561 | -1239.3624
2023-02-10 11:00 | -3498.13 | 6.4446 | 56.0717 | 64.1561 | -1025.2007
2023-02-11 12:00 | -2597.07 | 6.4446 | 56.7695 | 64.1561 | -761.1261
2023-02-12 13:00 | -1962.6 | 5.8067 | 57.2048 | 64.1561 | -575.1813
2023-02-13 14:00 | -1425.07 | 4.2457 | 57.3971 | 64.1561 | -417.6468
2023-02-14 15:00 | -910.438 | 2.8789 | 57.6524 | 64.1561 | -266.823
2023-02-15 16:00 | 28.4421 | 1 | 59.0546 | 64.1561 | 8.3356
2023-02-16 17:00 | -93.3745 | 0.89772 | 58.8854 | 64.1561 | -27.3654
2023-02-17 18:00 | -342.221 | 1.5297 | 58.5607 | 64.1561 | -100.2951
2023-02-18 19:00 | -903.227 | 3.0885 | 58.3818 | 64.1561 | -264.7097
2023-02-19 20:00 | -1348.9 | 4.2398 | 58.3168 | 64.1561 | -395.3236
2023-02-20 21:00 | -2250.74 | 6.4446 | 58.2124 | 64.1561 | -659.6268
2023-02-21 22:00 | -2718.88 | 6.4446 | 57.8539 | 64.1561 | -796.8251
2023-02-22 23:00 | -3577.81 | 6.4446 | 57.264 | 64.1561 | -1048.5526
2023-02-24 | -3925.13 | 6.4446 | 56.9358 | 64.1561 | -1150.342
2023-02-25 01:00 | -4124.9 | 6.4446 | 56.7188 | 64.1561 | -1208.8889
2023-02-26 02:00 | -4279.36 | 6.4446 | 56.5528 | 64.1561 | -1254.1566
2023-02-27 03:00 | -4330.15 | 6.4446 | 56.4648 | 64.1561 | -1269.0417
2023-02-28 04:00 | -4145.59 | 6.4446 | 56.5271 | 64.1561 | -1214.9525
2023-03-01 05:00 | -4017.71 | 6.4446 | 56.5991 | 64.1561 | -1177.4746
2023-03-02 06:00 | -3588.73 | 6.4446 | 56.8667 | 64.1561 | -1051.7529
2023-03-03 07:00 | -3586.74 | 6.4446 | 56.9206 | 64.1561 | -1051.1697
2023-03-04 08:00 | -3507.49 | 6.4446 | 56.9999 | 64.1561 | -1027.9438
2023-03-05 09:00 | -3590.3 | 6.4446 | 56.9809 | 64.1561 | -1052.2131
2023-03-06 10:00 | -2691.41 | 6.4446 | 57.5339 | 64.1561 | -788.7744
2023-03-07 11:00 | -1693 | 4.957 | 57.9361 | 64.1561 | -496.1693
2023-03-08 12:00 | -993.846 | 3.0327 | 58.1526 | 64.1561 | -291.2675
2023-03-09 13:00 | -302.655 | 1.2159 | 58.6268 | 64.1561 | -88.6994
2023-03-10 14:00 | 856.697 | 1 | 59.5803 | 64.1561 | 251.0731
2023-03-11 15:00 | 2355.85 | 1 | 59.4769 | 64.1561 | 690.4315
2023-03-12 16:00 | 3031.32 | 1 | 59.6387 | 64.1561 | 888.3922
2023-03-13 17:00 | 3089 | 1 | 59.9093 | 64.1561 | 905.2965
2023-03-14 18:00 | 3061.75 | 1 | 60.1196 | 64.1561 | 897.3103
2023-03-15 19:00 | 2938.27 | 1 | 60.3214 | 64.1561 | 861.1219
2023-03-16 20:00 | -73.2199 | 0.82556 | 60.8116 | 64.1561 | -21.4586
2023-03-17 21:00 | -940.419 | 3.1936 | 59.7921 | 64.1561 | -275.6096
2023-03-18 22:00 | -1419.85 | 4.37 | 59.4918 | 64.1561 | -416.117
2023-03-19 23:00 | -2326 | 6.4446 | 59.2422 | 64.1561 | -681.6833
2023-03-21 | -2995.94 | 6.4446 | 58.6668 | 64.1561 | -878.0233
2023-03-22 01:00 | -3266.39 | 6.4446 | 58.3124 | 64.1561 | -957.2844
2023-03-23 02:00 | -3467.77 | 6.4446 | 58.0752 | 64.1561 | -1016.3031
2023-03-24 03:00 | -3524.72 | 6.4446 | 57.9386 | 64.1561 | -1032.9935
2023-03-25 04:00 | -3538.71 | 6.4446 | 57.8409 | 64.1561 | -1037.0935
2023-03-26 05:00 | -3703.14 | 6.4446 | 57.6742 | 64.1561 | -1085.2832
2023-03-27 06:00 | -3774.47 | 6.4446 | 57.5568 | 64.1561 | -1106.188
2023-03-28 07:00 | -2971.06 | 6.4446 | 57.9772 | 64.1561 | -870.7317
2023-03-29 08:00 | -2603.82 | 6.4446 | 58.2618 | 64.1561 | -763.1043
2023-03-30 09:00 | -3337.88 | 6.4446 | 57.89 | 64.1561 | -978.2361
2023-03-31 10:00 | -3524.07 | 6.4446 | 57.7209 | 64.1561 | -1032.803
2023-04-01 11:00 | -3082.24 | 6.4446 | 57.9382 | 64.1561 | -903.3154
2023-04-02 12:00 | -3062.94 | 6.4446 | 57.9791 | 64.1561 | -897.6591
2023-04-03 13:00 | -3003.13 | 6.4446 | 58.0117 | 64.1561 | -880.1305
2023-04-04 14:00 | -2953.64 | 6.4446 | 58.0192 | 64.1561 | -865.6264
2023-04-05 15:00 | -2662.19 | 6.4446 | 58.1819 | 64.1561 | -780.2109
2023-04-06 16:00 | -2348.96 | 6.4446 | 58.3856 | 64.1561 | -688.4122
2023-04-07 17:00 | -857.04 | 2.4809 | 58.4843 | 64.1561 | -251.1736
2023-04-08 18:00 | -1014.59 | 3.3059 | 58.8128 | 64.1561 | -297.347
2023-04-09 19:00 | -1200.97 | 3.7637 | 58.8386 | 64.1561 | -351.9696
2023-04-10 20:00 | -1546.44 | 4.7181 | 58.8344 | 64.1561 | -453.2168
2023-04-11 21:00 | -1780.55 | 5.3056 | 58.817 | 64.1561 | -521.8277
2023-04-12 22:00 | -1880.76 | 5.5397 | 58.8099 | 64.1561 | -551.1963
2023-04-13 23:00 | -1943.62 | 5.7005 | 58.7978 | 64.1561 | -569.6188
2023-04-15 | -3363.55 | 6.4446 | 58.0958 | 64.1561 | -985.7592
2023-04-16 01:00 | -3657.69 | 6.4446 | 57.7711 | 64.1561 | -1071.9631
2023-04-17 02:00 | -3738.25 | 6.4446 | 57.6204 | 64.1561 | -1095.5729
2023-04-18 03:00 | -3790.4 | 6.4446 | 57.5349 | 64.1561 | -1110.8566
2023-04-19 04:00 | -3733.64 | 6.4446 | 57.5204 | 64.1561 | -1094.2219
2023-04-20 05:00 | -3701.67 | 6.4446 | 57.4892 | 64.1561 | -1084.8524
2023-04-21 06:00 | -3530.75 | 6.4446 | 57.5723 | 64.1561 | -1034.7607
2023-04-22 07:00 | -2724.57 | 6.4446 | 58.0612 | 64.1561 | -798.4926
2023-04-23 08:00 | -2270.55 | 6.4446 | 58.4208 | 64.1561 | -665.4325
2023-04-24 09:00 | -2733.84 | 6.4446 | 58.2374 | 64.1561 | -801.2094
2023-04-25 10:00 | -2740.88 | 6.4446 | 58.2299 | 64.1561 | -803.2726
2023-04-26 11:00 | -2603.09 | 6.4446 | 58.3112 | 64.1561 | -762.8904
2023-04-27 12:00 | -2374.06 | 6.4446 | 58.4841 | 64.1561 | -695.7683
2023-04-28 13:00 | -2413.25 | 6.4446 | 58.4987 | 64.1561 | -707.2538
2023-04-29 14:00 | -2332.88 | 6.4446 | 58.555 | 64.1561 | -683.6996
2023-04-30 15:00 | -1996.88 | 5.7833 | 58.6344 | 64.1561 | -585.2278
2023-05-01 16:00 | -1832.28 | 5.3598 | 58.6922 | 64.1561 | -536.9883
2023-05-02 17:00 | -379.098 | 1.2052 | 58.8337 | 64.1561 | -111.1027
2023-05-03 18:00 | -606.901 | 2.2414 | 59.1894 | 64.1561 | -177.8651
2023-05-04 19:00 | -894.403 | 2.9707 | 59.1499 | 64.1561 | -262.1236
2023-05-05 20:00 | -1212.66 | 3.8163 | 59.1045 | 64.1561 | -355.3956
2023-05-06 21:00 | -1427.14 | 4.3545 | 59.0722 | 64.1561 | -418.2534
2023-05-07 22:00 | -1650.89 | 4.9494 | 59.0546 | 64.1561 | -483.8281
2023-05-08 23:00 | -1758.74 | 5.2064 | 59.0118 | 64.1561 | -515.4358
2023-05-10 | -3146.3 | 6.4446 | 58.4145 | 64.1561 | -922.0895
2023-05-11 01:00 | -3478.71 | 6.4446 | 58.0637 | 64.1561 | -1019.5093
2023-05-12 02:00 | -3550.04 | 6.4446 | 57.909 | 64.1561 | -1040.414
2023-05-13 03:00 | -3367.48 | 6.4446 | 57.9575 | 64.1561 | -986.911
2023-05-14 04:00 | -3628.44 | 6.4446 | 57.7729 | 64.1561 | -1063.3908
2023-05-15 05:00 | -3725.08 | 6.4446 | 57.6398 | 64.1561 | -1091.7132
2023-05-16 06:00 | -3625.3 | 6.4446 | 57.6495 | 64.1561 | -1062.4706
2023-05-17 07:00 | -2913.66 | 6.4446 | 58.057 | 64.1561 | -853.9095
2023-05-18 08:00 | -2322.44 | 6.4446 | 58.4716 | 64.1561 | -680.64
2023-05-19 09:00 | -3213.78 | 6.4446 | 58.0192 | 64.1561 | -941.8659
2023-05-20 10:00 | -3217.91 | 6.4446 | 57.9612 | 64.1561 | -943.0763
2023-05-21 11:00 | -2924.32 | 6.4446 | 58.1096 | 64.1561 | -857.0336
2023-05-22 12:00 | -2025.12 | 5.8976 | 58.5792 | 64.1561 | -593.5041
2023-05-23 13:00 | -1501.54 | 4.3871 | 58.6972 | 64.1561 | -440.0579
2023-05-24 14:00 | 0 | 0 | 60.1507 | 64.1561 | 0
2023-05-25 15:00 | -162.721 | 1.0304 | 59.7756 | 64.1561 | -47.6888
2023-05-26 16:00 | 1318.76 | 1 | 60.2236 | 64.1561 | 386.4904
2023-05-27 17:00 | 2967.09 | 1 | 74.2581 | 64.1561 | 869.5682
2023-05-28 18:00 | 2906.57 | 1 | 60.4653 | 64.1561 | 851.8316
2023-05-29 19:00 | 0 | 0 | 61.386 | 64.1561 | 0
2023-05-30 20:00 | -696.644 | 2.4462 | 60.0867 | 64.1561 | -204.1662
2023-05-31 21:00 | -979.237 | 3.1652 | 59.8837 | 64.1561 | -286.986
2023-06-01 22:00 | -1361.38 | 4.1896 | 59.7746 | 64.1561 | -398.9811
2023-06-02 23:00 | -1604.85 | 4.7956 | 59.6463 | 64.1561 | -470.3351
2023-06-04 | -2918.46 | 6.4446 | 59.0972 | 64.1561 | -855.3162
2023-06-05 01:00 | -3421.39 | 6.4446 | 58.6291 | 64.1561 | -1002.7104
2023-06-06 02:00 | -3618.96 | 6.4446 | 58.3581 | 64.1561 | -1060.6125
2023-06-07 03:00 | -3675.02 | 6.4446 | 58.2186 | 64.1561 | -1077.042
2023-06-08 04:00 | -3538.23 | 6.4446 | 58.2078 | 64.1561 | -1036.9529
2023-06-09 05:00 | -3464.03 | 6.4446 | 58.1722 | 64.1561 | -1015.207
2023-06-10 06:00 | -3110.94 | 6.4446 | 58.3337 | 64.1561 | -911.7265
2023-06-11 07:00 | -3005.38 | 6.4446 | 58.4093 | 64.1561 | -880.7899
2023-06-12 08:00 | -2194.36 | 6.3721 | 58.8966 | 64.1561 | -643.1034
2023-06-13 09:00 | -1503.61 | 4.3303 | 58.9788 | 64.1561 | -440.6646
2023-06-14 10:00 | 0 | 1 | 60.4711 | 64.1561 | 0
2023-06-15 11:00 | 2829.55 | 1 | 60.0417 | 64.1561 | 829.2592
2023-06-16 12:00 | 2945.73 | 1.0341 | 72.3662 | 64.1561 | 863.3082
2023-06-17 13:00 | 3600.99 | 1.2236 | 73.0137 | 64.1561 | 1055.346
2023-06-18 14:00 | 4087.4 | 1.3342 | 73.7562 | 64.1561 | 1197.8987
2023-06-19 15:00 | 4522.64 | 1.509 | 73.7732 | 64.1561 | 1325.4549
2023-06-20 16:00 | 5076.99 | 1.6888 | 74.0563 | 64.1561 | 1487.9189
2023-06-21 17:00 | 4146.75 | 1.3726 | 74.329 | 64.1561 | 1215.2925
2023-06-22 18:00 | 3028.3 | 1 | 79.8237 | 64.1561 | 887.5071
2023-06-23 19:00 | 2839.76 | 1 | 61.8594 | 64.1561 | 832.2515
2023-06-24 20:00 | -431.868 | 1.8001 | 61.6157 | 64.1561 | -126.568
2023-06-25 21:00 | -1792.29 | 5.4592 | 60.9454 | 64.1561 | -525.2683
2023-06-26 22:00 | -2344.87 | 6.4446 | 60.4641 | 64.1561 | -687.2136
2023-06-27 23:00 | -3462.2 | 6.4446 | 59.532 | 64.1561 | -1014.6707
2023-06-29 | -3861.71 | 6.4446 | 59.0043 | 64.1561 | -1131.7555
2023-06-30 01:00 | -4424.01 | 6.4446 | 58.4023 | 64.1561 | -1296.5493
2023-07-01 02:00 | -4696.78 | 6.4446 | 58.0221 | 64.1561 | -1376.4903
2023-07-02 03:00 | -4989.17 | 6.4446 | 57.6593 | 64.1561 | -1462.1814
2023-07-03 04:00 | -4995.05 | 6.4446 | 57.4713 | 64.1561 | -1463.9046
2023-07-04 05:00 | -5067.15 | 6.4446 | 57.2945 | 64.1561 | -1485.0351
2023-07-05 06:00 | -4717.11 | 6.4446 | 57.3908 | 64.1561 | -1382.4485
2023-07-06 07:00 | -4404.28 | 6.4446 | 57.5176 | 64.1561 | -1290.7671
2023-07-07 08:00 | -3148.66 | 6.4446 | 58.2679 | 64.1561 | -922.7812
2023-07-08 09:00 | -1909.64 | 5.5403 | 58.9536 | 64.1561 | -559.6602
2023-07-09 10:00 | 0 | 0 | 60.4965 | 64.1561 | 0
2023-07-10 11:00 | 2818.12 | 1 | 76.1606 | 64.1561 | 825.9094
2023-07-11 12:00 | 4471.68 | 1.4935 | 73.0153 | 64.1561 | 1310.52
2023-07-12 13:00 | 5309.49 | 1.7775 | 73.4868 | 64.1561 | 1556.0579
2023-07-13 14:00 | 6787.63 | 2.2315 | 74.0991 | 64.1561 | 1989.258
2023-07-14 15:00 | 6256.07 | 2.0661 | 74.5079 | 64.1561 | 1833.4731
2023-07-15 16:00 | 5998.72 | 2.0295 | 74.4913 | 64.1561 | 1758.0513
2023-07-16 17:00 | 4474.49 | 1.4872 | 74.8676 | 64.1561 | 1311.3436
2023-07-17 18:00 | 3376.1 | 1.1286 | 74.7926 | 64.1561 | 989.4372
2023-07-18 19:00 | 3016.41 | 1 | 82.3072 | 64.1561 | 884.0225
2023-07-19 20:00 | 2934.53 | 1 | 62.2847 | 64.1561 | 860.0258
2023-07-20 21:00 | -385.23 | 1.6405 | 62.0806 | 64.1561 | -112.8998
2023-07-21 22:00 | -976.829 | 3.169 | 61.4325 | 64.1561 | -286.2803
2023-07-22 23:00 | -1857.25 | 5.5152 | 61.0629 | 64.1561 | -544.3062
2023-07-24 | -2009.22 | 5.7433 | 60.7871 | 64.1561 | -588.8443
2023-07-25 01:00 | -2026.54 | 5.7839 | 60.6049 | 64.1561 | -593.9202
2023-07-26 02:00 | -2286.44 | 6.4446 | 60.4283 | 64.1561 | -670.0894
2023-07-27 03:00 | -2648.59 | 6.4446 | 60.0937 | 64.1561 | -776.2251
2023-07-28 04:00 | -2422.8 | 6.4446 | 60.1008 | 64.1561 | -710.0526
2023-07-29 05:00 | -2661.24 | 6.4446 | 59.908 | 64.1561 | -779.9325
2023-07-30 06:00 | -2465.53 | 6.4446 | 59.9614 | 64.1561 | -722.5755
2023-07-31 07:00 | -2502.42 | 6.4446 | 59.9018 | 64.1561 | -733.3869
2023-08-01 08:00 | -2310.53 | 6.4446 | 59.9711 | 64.1561 | -677.1495
2023-08-02 09:00 | -2714.42 | 6.4446 | 59.7277 | 64.1561 | -795.518
2023-08-03 10:00 | -1998.57 | 5.7051 | 59.9395 | 64.1561 | -585.723
2023-08-04 11:00 | 0 | 0 | 61.333 | 64.1561 | 0
2023-08-05 12:00 | 2889.77 | 1 | 60.8623 | 64.1561 | 846.908
2023-08-06 13:00 | 3066.03 | 1 | 61.2454 | 64.1561 | 898.5647
2023-08-07 14:00 | 3041.16 | 1 | 61.492 | 64.1561 | 891.276
2023-08-08 15:00 | -331.826 | 1.525 | 61.5189 | 64.1561 | -97.2486
2023-08-09 16:00 | 0 | 0 | 62.1249 | 64.1561 | 0
2023-08-10 17:00 | -45.4833 | 0.70341 | 61.7951 | 64.1561 | -13.3298
2023-08-11 18:00 | -36.5826 | 0.65896 | 61.7831 | 64.1561 | -10.7213
2023-08-12 19:00 | -421.704 | 1.7242 | 60.9874 | 64.1561 | -123.5892
2023-08-13 20:00 | -654.56 | 2.2897 | 60.7365 | 64.1561 | -191.8326
2023-08-14 21:00 | -1461.6 | 4.5092 | 60.5789 | 64.1561 | -428.3527
2023-08-15 22:00 | -1868.51 | 5.4664 | 60.4231 | 64.1561 | -547.6062
2023-08-16 23:00 | -3195.06 | 6.4446 | 59.7224 | 64.1561 | -936.3797
2023-08-18 | -3881.14 | 6.4446 | 59.0734 | 64.1561 | -1137.4499
2023-08-19 01:00 | -4112.25 | 6.4446 | 58.7047 | 64.1561 | -1205.1815
2023-08-20 02:00 | -4571.05 | 6.4446 | 58.2489 | 64.1561 | -1339.6425
2023-08-21 03:00 | -4810.8 | 6.4446 | 57.9541 | 64.1561 | -1409.9063
2023-08-22 04:00 | -4984.19 | 6.4446 | 57.7044 | 64.1561 | -1460.7219
2023-08-23 05:00 | -5034.24 | 6.4446 | 57.5615 | 64.1561 | -1475.3901
2023-08-24 06:00 | -4855.32 | 6.4446 | 57.5778 | 64.1561 | -1422.9538
2023-08-25 07:00 | -4694.69 | 6.4446 | 57.6174 | 64.1561 | -1375.8778
2023-08-26 08:00 | -3906.22 | 6.4446 | 58.0561 | 64.1561 | -1144.8001
2023-08-27 09:00 | -3204.99 | 6.4446 | 58.5313 | 64.1561 | -939.2898
2023-08-28 10:00 | -1805.75 | 5.221 | 59.2085 | 64.1561 | -529.2131
2023-08-29 11:00 | -662.472 | 2.0144 | 59.4576 | 64.1561 | -194.1514
2023-08-30 12:00 | -238.535 | 1.1128 | 60.1197 | 64.1561 | -69.9077
2023-08-31 13:00 | 2888.97 | 1 | 60.4376 | 64.1561 | 846.6735
2023-09-01 14:00 | 0 | 0 | 61.5743 | 64.1561 | 0
2023-09-02 15:00 | 2735.71 | 1 | 60.8901 | 64.1561 | 801.7575
2023-09-03 16:00 | 2862.88 | 1 | 61.1567 | 64.1561 | 839.0273
2023-09-04 17:00 | 2785.02 | 1 | 61.4204 | 64.1561 | 816.2088
2023-09-05 18:00 | 0 | 0 | 62.2274 | 64.1561 | 0
2023-09-06 19:00 | -920.754 | 2.9671 | 60.7833 | 64.1561 | -269.8464
2023-09-07 20:00 | -1685.65 | 5.0832 | 60.5538 | 64.1561 | -494.0152
2023-09-08 21:00 | -2874.5 | 6.4446 | 59.9499 | 64.1561 | -842.4328
2023-09-09 22:00 | -3594.78 | 6.4446 | 59.2704 | 64.1561 | -1053.526
2023-09-10 23:00 | -4738.61 | 6.4446 | 58.3294 | 64.1561 | -1388.7495
2023-09-12 | -5482.25 | 6.4446 | 57.6233 | 64.1561 | -1606.6889
2023-09-13 01:00 | -5883.13 | 6.4446 | 57.105 | 64.1561 | -1724.1752
2023-09-14 02:00 | -6197.85 | 6.4446 | 56.7068 | 64.1561 | -1816.4105
2023-09-15 03:00 | -6381.97 | 6.4446 | 56.3912 | 64.1561 | -1870.3708
2023-09-16 04:00 | -6691.63 | 6.4446 | 56.017 | 64.1561 | -1961.1232
2023-09-17 05:00 | -6889.59 | 6.4446 | 55.7162 | 64.1561 | -2019.1395
2023-09-18 06:00 | -7106.77 | 6.4446 | 55.4394 | 64.1561 | -2082.7887
2023-09-19 07:00 | -5995.53 | 6.4446 | 55.9798 | 64.1561 | -1757.1164
2023-09-20 08:00 | -4548.35 | 6.4446 | 56.876 | 64.1561 | -1332.9898
2023-09-21 09:00 | -3843 | 6.4446 | 57.4512 | 64.1561 | -1126.2721
2023-09-22 10:00 | -2584.88 | 6.4446 | 58.3435 | 64.1561 | -757.5535
2023-09-23 11:00 | -1212.65 | 3.5043 | 58.7526 | 64.1561 | -355.3926
2023-09-24 12:00 | 0 | 0 | 60.384 | 64.1561 | 0
2023-09-25 13:00 | 2717.8 | 1 | 60.0154 | 64.1561 | 796.5086
2023-09-26 14:00 | 2847.74 | 1 | 60.4623 | 64.1561 | 834.5902
2023-09-27 15:00 | 2838.93 | 1 | 60.7754 | 64.1561 | 832.0083
2023-09-28 16:00 | 2831.47 | 1 | 60.9792 | 64.1561 | 829.8219
2023-09-29 17:00 | 2853.41 | 1 | 74.9451 | 64.1561 | 836.2519
2023-09-30 18:00 | 0 | 0 | 62.0011 | 64.1561 | 0
2023-10-01 19:00 | -827.537 | 2.666 | 60.5739 | 64.1561 | -242.5272
2023-10-02 20:00 | -1638.62 | 4.9915 | 60.3305 | 64.1561 | -480.2321
2023-10-03 21:00 | -2490.55 | 6.4446 | 59.9611 | 64.1561 | -729.9082
2023-10-04 22:00 | -3095.3 | 6.4446 | 59.4094 | 64.1561 | -907.1429
2023-10-05 23:00 | -3433.74 | 6.4446 | 59.0114 | 64.1561 | -1006.3299
2023-10-07 | -4997.19 | 6.4446 | 57.9328 | 64.1561 | -1464.5318
2023-10-08 01:00 | -5801.3 | 6.4446 | 57.1626 | 64.1561 | -1700.1932
2023-10-09 02:00 | -5925.87 | 6.4446 | 56.8151 | 64.1561 | -1736.7011
2023-10-10 03:00 | -6098.09 | 6.4446 | 56.5261 | 64.1561 | -1787.1738
2023-10-11 04:00 | -6711.32 | 6.4446 | 55.9917 | 64.1561 | -1966.8937
2023-10-12 05:00 | -7012.77 | 6.4446 | 55.5957 | 64.1561 | -2055.24
2023-10-13 06:00 | -7222.49 | 6.4446 | 55.3124 | 64.1561 | -2116.7029
2023-10-14 07:00 | -6138.3 | 6.4446 | 55.8408 | 64.1561 | -1798.9581
2023-10-15 08:00 | -4153.87 | 6.4446 | 57.0589 | 64.1561 | -1217.3791
2023-10-16 09:00 | -3216.41 | 6.4446 | 57.8261 | 64.1561 | -942.6367
2023-10-17 10:00 | -1565.35 | 4.5579 | 58.6174 | 64.1561 | -458.7588
2023-10-18 11:00 | 0 | 1 | 60.2293 | 64.1561 | 0
2023-10-19 12:00 | 2846.99 | 1 | 59.9018 | 64.1561 | 834.3704
2023-10-20 13:00 | 2841.69 | 1 | 75.4154 | 64.1561 | 832.8171
2023-10-21 14:00 | 2897.15 | 1 | 73.9456 | 64.1561 | 849.0709
2023-10-22 15:00 | 2900.35 | 1 | 75.1554 | 64.1561 | 850.0087
2023-10-23 16:00 | 2881.58 | 1 | 80.6342 | 64.1561 | 844.5077
2023-10-24 17:00 | 3210.7 | 1.1162 | 73.1833 | 64.1561 | 940.9633
2023-10-25 18:00 | 2880.36 | 1 | 61.4094 | 64.1561 | 844.1502
2023-10-26 19:00 | 0 | 0 | 62.2009 | 64.1561 | 0
2023-10-27 20:00 | -733.41 | 2.4236 | 60.7799 | 64.1561 | -214.9413
2023-10-28 21:00 | -1209.36 | 3.7881 | 60.5467 | 64.1561 | -354.4284
2023-10-29 22:00 | -1850.14 | 5.4868 | 60.3622 | 64.1561 | -542.2225
2023-10-30 23:00 | -2140.83 | 6.1689 | 60.1638 | 64.1561 | -627.4153
2023-11-01 | -3676.07 | 6.4446 | 59.1298 | 64.1561 | -1077.3498
2023-11-02 01:00 | -4190.05 | 6.4446 | 58.5738 | 64.1561 | -1227.9824
2023-11-03 02:00 | -4384.05 | 6.4446 | 58.2501 | 64.1561 | -1284.8382
2023-11-04 03:00 | -4540.33 | 6.4446 | 58.0066 | 64.1561 | -1330.6394
2023-11-05 04:00 | -4663.4 | 6.4446 | 57.8052 | 64.1561 | -1366.7076
2023-11-06 05:00 | -4470.79 | 6.4446 | 57.7989 | 64.1561 | -1310.2592
2023-11-07 06:00 | -4079.26 | 6.4446 | 57.9795 | 64.1561 | -1195.5131
2023-11-08 07:00 | -3611.81 | 6.4446 | 58.2742 | 64.1561 | -1058.517
2023-11-09 08:00 | -2315.62 | 6.4446 | 59.0989 | 64.1561 | -678.6412
2023-11-10 09:00 | -1372.87 | 3.9328 | 59.2907 | 64.1561 | -402.3485
2023-11-11 10:00 | 2333.31 | 1 | 60.2888 | 64.1561 | 683.8257
2023-11-12 11:00 | 3176.86 | 1.0527 | 73.1958 | 64.1561 | 931.0458
2023-11-13 12:00 | 5214.58 | 1.7049 | 73.7074 | 64.1561 | 1528.2425
2023-11-14 13:00 | 6333.79 | 2.0596 | 74.2344 | 64.1561 | 1856.2506
2023-11-15 14:00 | 7104.66 | 2.3115 | 74.6737 | 64.1561 | 2082.1703
2023-11-16 15:00 | 7188.7 | 2.3734 | 74.9103 | 64.1561 | 2106.8
2023-11-17 16:00 | 8020.46 | 2.603 | 75.3973 | 64.1561 | 2350.5648
2023-11-18 17:00 | 6990 | 2.2673 | 75.738 | 64.1561 | 2048.5668
2023-11-19 18:00 | 5099.63 | 1.6443 | 75.9547 | 64.1561 | 1494.554
2023-11-20 19:00 | 3548.86 | 1.1484 | 75.8546 | 64.1561 | 1040.0682
2023-11-21 20:00 | 3011.97 | 1 | 62.906 | 64.1561 | 882.7213
2023-11-22 21:00 | 0 | 0 | 63.5495 | 64.1561 | 0
2023-11-23 22:00 | -565.953 | 1.95 | 62.0131 | 64.1561 | -165.8645
2023-11-24 23:00 | -1593.27 | 4.8481 | 61.5764 | 64.1561 | -466.9413
2023-11-26 | -2166.95 | 6.2186 | 61.2371 | 64.1561 | -635.0704
2023-11-27 01:00 | -2571.95 | 6.4446 | 60.7994 | 64.1561 | -753.7641
2023-11-28 02:00 | -2857.27 | 6.4446 | 60.4015 | 64.1561 | -837.3832
2023-11-29 03:00 | -3167.98 | 6.4446 | 60.0489 | 64.1561 | -928.4433
2023-11-30 04:00 | -3039.75 | 6.4446 | 59.9579 | 64.1561 | -890.8628
2023-12-01 05:00 | -3270.52 | 6.4446 | 59.7158 | 64.1561 | -958.4948
2023-12-02 06:00 | -3132.59 | 6.4446 | 59.7011 | 64.1561 | -918.0715
2023-12-03 07:00 | -2943.99 | 6.4446 | 59.7571 | 64.1561 | -862.7983
2023-12-04 08:00 | -2059.38 | 5.8753 | 60.134 | 64.1561 | -603.5447
2023-12-05 09:00 | -1292.78 | 3.7123 | 60.2182 | 64.1561 | -378.8764
2023-12-06 10:00 | 1441.35 | 1 | 61.3382 | 64.1561 | 422.418
2023-12-07 11:00 | 2863.11 | 1 | 76.8478 | 64.1561 | 839.0947
2023-12-08 12:00 | 4335.36 | 1.4867 | 73.7831 | 64.1561 | 1270.5686
2023-12-09 13:00 | 4882.08 | 1.6105 | 74.5996 | 64.1561 | 1430.7964
2023-12-10 14:00 | 5124.41 | 1.6318 | 75.3211 | 64.1561 | 1501.8163
2023-12-11 15:00 | 6871.6 | 2.1972 | 75.506 | 64.1561 | 2013.8672
2023-12-12 16:00 | 7942.76 | 2.5848 | 75.6452 | 64.1561 | 2327.7932
2023-12-13 17:00 | 7019.74 | 2.3056 | 75.9037 | 64.1561 | 2057.2827
2023-12-14 18:00 | 5260.98 | 1.7038 | 76.2222 | 64.1561 | 1541.841
2023-12-15 19:00 | 3376.52 | 1.1148 | 75.9593 | 64.1561 | 989.5603
2023-12-16 20:00 | 3049.37 | 1 | 82.6772 | 64.1561 | 893.6821
2023-12-17 21:00 | 0 | 0 | 63.8917 | 64.1561 | 0
2023-12-18 22:00 | -670.769 | 2.2711 | 62.3435 | 64.1561 | -196.583
2023-12-19 23:00 | -1623.65 | 4.8859 | 61.8999 | 64.1561 | -475.8448
2023-12-21 | -2061.16 | 5.8914 | 61.5697 | 64.1561 | -604.0664
2023-12-22 01:00 | -2566.94 | 6.4446 | 61.1674 | 64.1561 | -752.2959
2023-12-23 02:00 | -2821.07 | 6.4446 | 60.7964 | 64.1561 | -826.774
2023-12-24 03:00 | -3155.17 | 6.4446 | 60.4279 | 64.1561 | -924.689
2023-12-25 04:00 | -3296.09 | 6.4446 | 60.1677 | 64.1561 | -965.9886
2023-12-26 05:00 | -3222.77 | 6.4446 | 60.0724 | 64.1561 | -944.5007
2023-12-27 06:00 | -2688.58 | 6.4446 | 60.3053 | 64.1561 | -787.945
2023-12-28 07:00 | -2589.19 | 6.4446 | 60.3597 | 64.1561 | -758.8167
2023-12-29 08:00 | -2198.11 | 6.225 | 60.5257 | 64.1561 | -644.2024
2023-12-30 09:00 | -1241.81 | 3.5197 | 60.5522 | 64.1561 | -363.9386
2023-12-31 10:00 | 2581.36 | 1 | 61.4219 | 64.1561 | 756.5219
2024-01-01 11:00 | 2964.16 | 1 | 61.8049 | 64.1561 | 868.7095
2024-01-02 12:00 | 3712.65 | 1.229 | 74.6482 | 64.1561 | 1088.0703
2024-01-03 13:00 | 4626.54 | 1.4796 | 75.27 | 64.1561 | 1355.905
2024-01-04 14:00 | 3959.1 | 1.2895 | 75.3389 | 64.1561 | 1160.2977
2024-01-05 15:00 | 5475.24 | 1.7747 | 75.5176 | 64.1561 | 1604.6344
2024-01-06 16:00 | 6421.77 | 2.117 | 75.5366 | 64.1561 | 1882.035
2024-01-07 17:00 | 5117.43 | 1.6509 | 76.079 | 64.1561 | 1499.7707
2024-01-08 18:00 | 4464.34 | 1.4251 | 76.2494 | 64.1561 | 1308.3689
2024-01-09 19:00 | 3082.17 | 1.0094 | 75.9401 | 64.1561 | 903.2949
2024-01-10 20:00 | 3058.48 | 1 | 80.1611 | 64.1561 | 896.352
2024-01-11 21:00 | 2806.73 | 1 | 63.2341 | 64.1561 | 822.5714
2024-01-12 22:00 | -149.909 | 1.0094 | 63.278 | 64.1561 | -43.934
2024-01-13 23:00 | -1259.12 | 3.954 | 62.2716 | 64.1561 | -369.0116
2024-01-15 | -1886.12 | 5.4684 | 61.8592 | 64.1561 | -552.7672
2024-01-16 01:00 | -2403.69 | 6.4446 | 61.5285 | 64.1561 | -704.452
2024-01-17 02:00 | -2939.81 | 6.4446 | 60.9929 | 64.1561 | -861.5733
2024-01-18 03:00 | -3366.54 | 6.4446 | 60.498 | 64.1561 | -986.6355
2024-01-19 04:00 | -3460.16 | 6.4446 | 60.2453 | 64.1561 | -1014.0728
2024-01-20 05:00 | -3581.07 | 6.4446 | 60.0351 | 64.1561 | -1049.508
2024-01-21 06:00 | -3230.58 | 6.4446 | 60.1293 | 64.1561 | -946.7895
2024-01-22 07:00 | -3108.98 | 6.4446 | 60.1536 | 64.1561 | -911.1521
2024-01-23 08:00 | -3108.03 | 6.4446 | 60.1082 | 64.1561 | -910.8737
2024-01-24 09:00 | -3457.45 | 6.4446 | 59.8359 | 64.1561 | -1013.2786
2024-01-25 10:00 | -3337.68 | 6.4446 | 59.8065 | 64.1561 | -978.1774
2024-01-26 11:00 | -2957.81 | 6.4446 | 59.9687 | 64.1561 | -866.8485
2024-01-27 12:00 | -2658.17 | 6.4446 | 60.1173 | 64.1561 | -779.0327
2024-01-28 13:00 | -2067.22 | 5.8698 | 60.328 | 64.1561 | -605.8424
2024-01-29 14:00 | -1866.04 | 5.3323 | 60.3604 | 64.1561 | -546.8823
2024-01-30 15:00 | -1789.55 | 5.1653 | 60.3839 | 64.1561 | -524.4653
2024-01-31 16:00 | -974.165 | 2.8739 | 60.3954 | 64.1561 | -285.4996
2024-02-01 17:00 | -754.982 | 2.4691 | 60.5959 | 64.1561 | -221.2634
2024-02-02 18:00 | -827.798 | 2.7087 | 60.6515 | 64.1561 | -242.6036
2024-02-03 19:00 | -1351.74 | 4.1609 | 60.5926 | 64.1561 | -396.1559
2024-02-04 20:00 | -1662.48 | 4.9099 | 60.4904 | 64.1561 | -487.2248
2024-02-05 21:00 | -2458.21 | 6.4446 | 60.2798 | 64.1561 | -720.4302
2024-02-06 22:00 | -2870.75 | 6.4446 | 59.9241 | 64.1561 | -841.3338
2024-02-07 23:00 | -3783.97 | 6.4446 | 59.2647 | 64.1561 | -1108.9721
2024-02-09 | -4011.58 | 6.4446 | 58.9643 | 64.1561 | -1175.678
2024-02-10 01:00 | -4103.22 | 6.4446 | 58.7846 | 64.1561 | -1202.5351
2024-02-11 02:00 | -4287.4 | 6.4446 | 58.583 | 64.1561 | -1256.5129
2024-02-12 03:00 | -4328.31 | 6.4446 | 58.476 | 64.1561 | -1268.5024
2024-02-13 04:00 | -4204.97 | 6.4446 | 58.4763 | 64.1561 | -1232.3551
2024-02-14 05:00 | -4133.81 | 6.4446 | 58.4819 | 64.1561 | -1211.5001
2024-02-15 06:00 | -3604.95 | 6.4446 | 58.7704 | 64.1561 | -1056.5066
2024-02-16 07:00 | -3564.47 | 6.4446 | 58.8211 | 64.1561 | -1044.643
2024-02-17 08:00 | -3229.71 | 6.4446 | 59.0312 | 64.1561 | -946.5346
2024-02-18 09:00 | -2147.08 | 6.1799 | 59.667 | 64.1561 | -629.247
2024-02-19 10:00 | -604.447 | 1.7495 | 59.7975 | 64.1561 | -177.1459
2024-02-20 11:00 | 2496.61 | 1 | 60.8048 | 64.1561 | 731.6842
2024-02-21 12:00 | 3001.67 | 1 | 61.1618 | 64.1561 | 879.7026
2024-02-22 13:00 | 3103.81 | 1 | 75.8947 | 64.1561 | 909.6369
2024-02-23 14:00 | 3025.37 | 1 | 61.7194 | 64.1561 | 886.6484
2024-02-24 15:00 | 3023.63 | 1 | 61.9053 | 64.1561 | 886.1385
2024-02-25 16:00 | 3012.7 | 1 | 62.0504 | 64.1561 | 882.9352
2024-02-26 17:00 | 3072.66 | 1 | 62.1244 | 64.1561 | 900.5078
2024-02-27 18:00 | 3020.61 | 1 | 62.2222 | 64.1561 | 885.2534
2024-02-28 19:00 | -230.195 | 1.2307 | 62.2897 | 64.1561 | -67.4635
2024-02-29 20:00 | -893.143 | 2.9651 | 61.557 | 64.1561 | -261.7544
2024-03-01 21:00 | -2046.09 | 6.0551 | 61.2084 | 64.1561 | -599.6498
2024-03-02 22:00 | -2692.12 | 6.4446 | 60.678 | 64.1561 | -788.9825
2024-03-03 23:00 | -3974.68 | 6.4446 | 59.6593 | 64.1561 | -1164.8637
2024-03-05 | -4348.46 | 6.4446 | 59.1092 | 64.1561 | -1274.4078
2024-03-06 01:00 | -4785.05 | 6.4446 | 58.6212 | 64.1561 | -1402.3597
2024-03-07 02:00 | -5029.76 | 6.4446 | 58.2707 | 64.1561 | -1474.0771
2024-03-08 03:00 | -5180.15 | 6.4446 | 58.0047 | 64.1561 | -1518.1521
2024-03-09 04:00 | -5347.93 | 6.4446 | 57.7472 | 64.1561 | -1567.3236
2024-03-10 05:00 | -5639.04 | 6.4446 | 57.4337 | 64.1561 | -1652.6395
2024-03-11 06:00 | -5781.32 | 6.4446 | 57.1934 | 64.1561 | -1694.3376
2024-03-12 07:00 | -4781.56 | 6.4446 | 57.6882 | 64.1561 | -1401.3369
2024-03-13 08:00 | -3403.44 | 6.4446 | 58.5503 | 64.1561 | -997.4498
2024-03-14 09:00 | -3000.74 | 6.4446 | 58.9416 | 64.1561 | -879.4301
2024-03-15 10:00 | -2253.18 | 6.4446 | 59.491 | 64.1561 | -660.3419
2024-03-16 11:00 | -538.3 | 1.5406 | 59.6081 | 64.1561 | -157.7602
2024-03-17 12:00 | 2695.56 | 1 | 60.6101 | 64.1561 | 789.9907
2024-03-18 13:00 | 3072.5 | 1 | 61.0375 | 64.1561 | 900.4609
2024-03-19 14:00 | 3002.95 | 1 | 78.3362 | 64.1561 | 880.0778
2024-03-20 15:00 | 3116.52 | 1 | 75.3315 | 64.1561 | 913.3619
2024-03-21 16:00 | 3114.89 | 1 | 77.532 | 64.1561 | 912.8841
2024-03-22 17:00 | 4025.35 | 1.3247 | 74.5483 | 64.1561 | 1179.7136
2024-03-23 18:00 | 3121.65 | 1 | 81.5529 | 64.1561 | 914.8653
2024-03-24 19:00 | 2993 | 1 | 62.2202 | 64.1561 | 877.1617
2024-03-25 20:00 | -87.9728 | 0.84199 | 62.5881 | 64.1561 | -25.7823
2024-03-26 21:00 | -626.799 | 2.2603 | 61.6566 | 64.1561 | -183.6967
2024-03-27 22:00 | -1086.68 | 3.4245 | 61.3331 | 64.1561 | -318.4745
2024-03-28 23:00 | -1497.54 | 4.4755 | 61.1372 | 64.1561 | -438.8857
2024-03-30 | -3010.76 | 6.4446 | 60.4716 | 64.1561 | -882.3667
2024-03-31 01:00 | -3580.23 | 6.4446 | 59.8387 | 64.1561 | -1049.2618
2024-04-01 02:00 | -4038.94 | 6.4446 | 59.353 | 64.1561 | -1183.6965
2024-04-02 03:00 | -4250.48 | 6.4446 | 59.0459 | 64.1561 | -1245.6927
2024-04-03 04:00 | -4365.57 | 6.4446 | 58.821 | 64.1561 | -1279.4223
2024-04-04 05:00 | -4614.45 | 6.4446 | 58.5253 | 64.1561 | -1352.3618
2024-04-05 06:00 | -4505.55 | 6.4446 | 58.4661 | 64.1561 | -1320.4464
2024-04-06 07:00 | -3634.42 | 6.4446 | 58.9041 | 64.1561 | -1065.1434
2024-04-07 08:00 | -2835.03 | 6.4446 | 59.4295 | 64.1561 | -830.8653
2024-04-08 09:00 | -3093.39 | 6.4446 | 59.3624 | 64.1561 | -906.5831
2024-04-09 10:00 | -2687.35 | 6.4446 | 59.5995 | 64.1561 | -787.5845
2024-04-10 11:00 | -1917.08 | 5.4741 | 59.8776 | 64.1561 | -561.8407
2024-04-11 12:00 | -1019.41 | 2.9861 | 59.9971 | 64.1561 | -298.7596
2024-04-12 13:00 | 2321.4 | 1 | 60.9103 | 64.1561 | 680.3352
2024-04-13 14:00 | 3013.05 | 1 | 77.1728 | 64.1561 | 883.0378
2024-04-14 15:00 | 3403.73 | 1.1041 | 74.2805 | 64.1561 | 997.5348
2024-04-15 16:00 | 3127.62 | 1.0152 | 74.5186 | 64.1561 | 916.6149
2024-04-16 17:00 | 5477.52 | 1.7892 | 74.5895 | 64.1561 | 1605.3026
2024-04-17 18:00 | 3593.9 | 1.1588 | 75.1634 | 64.1561 | 1053.2681
2024-04-18 19:00 | 3147.68 | 1 | 80.586 | 64.1561 | 922.4939
2024-04-19 20:00 | 3132.59 | 1 | 62.312 | 64.1561 | 918.0715
2024-04-20 21:00 | 3089.61 | 1 | 62.4051 | 64.1561 | 905.4753
2024-04-21 22:00 | 592.499 | 1 | 63.0934 | 64.1561 | 173.6443
2024-04-22 23:00 | 353.176 | 1 | 62.9169 | 64.1561 | 103.5057
2024-04-24 | -1155.39 | 3.7344 | 61.685 | 64.1561 | -338.6114
2024-04-25 01:00 | -1885.85 | 5.5244 | 61.3498 | 64.1561 | -552.6881
2024-04-26 02:00 | -2295.92 | 6.4446 | 61.0737 | 64.1561 | -672.8677
2024-04-27 03:00 | -2617.33 | 6.4446 | 60.69 | 64.1561 | -767.0637
2024-04-28 04:00 | -2921.22 | 6.4446 | 60.3722 | 64.1561 | -856.1251
2024-04-29 05:00 | -2843.19 | 6.4446 | 60.263 | 64.1561 | -833.2567
2024-04-30 06:00 | -2501.73 | 6.4446 | 60.3927 | 64.1561 | -733.1847
2024-05-01 07:00 | -2454.05 | 6.4446 | 60.3986 | 64.1561 | -719.2111
2024-05-02 08:00 | -2220.44 | 6.2869 | 60.47 | 64.1561 | -650.7467
2024-05-03 09:00 | -2465.28 | 6.4446 | 60.3404 | 64.1561 | -722.5022
2024-05-04 10:00 | -1168.43 | 3.3021 | 60.4189 | 64.1561 | -342.433
2024-05-05 11:00 | 0 | 1 | 61.9203 | 64.1561 | 0
2024-05-06 12:00 | 2693.02 | 1 | 61.4664 | 64.1561 | 789.2463
2024-05-07 13:00 | 2975.74 | 1 | 74.9985 | 64.1561 | 872.1033
2024-05-08 14:00 | 3589.28 | 1.196 | 74.4933 | 64.1561 | 1051.9141
2024-05-09 15:00 | 3644.32 | 1.2475 | 74.4231 | 64.1561 | 1068.0448
2024-05-10 16:00 | 4247.19 | 1.4536 | 74.6125 | 64.1561 | 1244.7285
2024-05-11 17:00 | 3355.46 | 1.1617 | 74.6841 | 64.1561 | 983.3883
2024-05-12 18:00 | 2858.51 | 1 | 62.724 | 64.1561 | 837.7466
2024-05-13 19:00 | 0 | 0 | 63.4005 | 64.1561 | 0
2024-05-14 20:00 | -497.725 | 1.7776 | 62.0116 | 64.1561 | -145.8688
2024-05-15 21:00 | -1828.51 | 5.5145 | 61.6194 | 64.1561 | -535.8834
2024-05-16 22:00 | -2631.41 | 6.4446 | 61.0707 | 64.1561 | -771.1901
2024-05-17 23:00 | -3926.53 | 6.4446 | 60.03 | 64.1561 | -1150.7523
2024-05-19 | -4515.75 | 6.4446 | 59.3422 | 64.1561 | -1323.4357
2024-05-20 01:00 | -4991.13 | 6.4446 | 58.798 | 64.1561 | -1462.7558
2024-05-21 02:00 | -5350.65 | 6.4446 | 58.3422 | 64.1561 | -1568.1207
2024-05-22 03:00 | -5659.42 | 6.4446 | 57.9426 | 64.1561 | -1658.6123
2024-05-23 04:00 | -5799.12 | 6.4446 | 57.6524 | 64.1561 | -1699.5543
2024-05-24 05:00 | -5895.75 | 6.4446 | 57.4305 | 64.1561 | -1727.8738
2024-05-25 06:00 | -5427.68 | 6.4446 | 57.5697 | 64.1561 | -1590.696
2024-05-26 07:00 | -5525.26 | 6.4446 | 57.4607 | 64.1561 | -1619.2939
2024-05-27 08:00 | -4672.03 | 6.4446 | 57.906 | 64.1561 | -1369.2368
2024-05-28 09:00 | -3251.64 | 6.4446 | 58.8034 | 64.1561 | -952.9616
2024-05-29 10:00 | -1717.76 | 4.9425 | 59.5744 | 64.1561 | -503.4258
2024-05-30 11:00 | 0 | 1 | 61.1789 | 64.1561 | 0
2024-05-31 12:00 | 2854.32 | 1 | 76.2924 | 64.1561 | 836.5186
2024-06-01 13:00 | 3874 | 1.3177 | 73.4833 | 64.1561 | 1135.3573
2024-06-02 14:00 | 4231.97 | 1.4423 | 73.8806 | 64.1561 | 1240.268
2024-06-03 15:00 | 4916.28 | 1.6425 | 74.4102 | 64.1561 | 1440.8194
2024-06-04 16:00 | 5248.09 | 1.7873 | 74.4877 | 64.1561 | 1538.0634
2024-06-05 17:00 | 4286.12 | 1.4563 | 74.782 | 64.1561 | 1256.1378
2024-06-06 18:00 | 2892.93 | 1 | 76.5034 | 64.1561 | 847.8341
2024-06-07 19:00 | 2827.65 | 1 | 62.6085 | 64.1561 | 828.7024
2024-06-08 20:00 | 0 | 0 | 63.3083 | 64.1561 | 0
2024-06-09 21:00 | -1235.86 | 3.8595 | 61.7797 | 64.1561 | -362.1948
2024-06-10 22:00 | -1998.3 | 5.8236 | 61.4027 | 64.1561 | -585.6439
2024-06-11 23:00 | -3293.41 | 6.4446 | 60.5211 | 64.1561 | -965.2032
2024-06-13 | -3897.24 | 6.4446 | 59.8597 | 64.1561 | -1142.1683
2024-06-14 01:00 | -4400.69 | 6.4446 | 59.27 | 64.1561 | -1289.7149
2024-06-15 02:00 | -4824.98 | 6.4446 | 58.7903 | 64.1561 | -1414.0621
2024-06-16 03:00 | -5136.09 | 6.4446 | 58.3916 | 64.1561 | -1505.2394
2024-06-17 04:00 | -5274.56 | 6.4446 | 58.1099 | 64.1561 | -1545.8209
2024-06-18 05:00 | -5389.81 | 6.4446 | 57.8881 | 64.1561 | -1579.5974
2024-06-19 06:00 | -5075.02 | 6.4446 | 57.9518 | 64.1561 | -1487.3415
2024-06-20 07:00 | -4967.55 | 6.4446 | 57.944 | 64.1561 | -1455.8452
2024-06-21 08:00 | -4167.77 | 6.4446 | 58.3854 | 64.1561 | -1221.4528
2024-06-22 09:00 | -3355.32 | 6.4446 | 58.9226 | 64.1561 | -983.3472
2024-06-23 10:00 | -2027.66 | 5.8369 | 59.6922 | 64.1561 | -594.2485
2024-06-24 11:00 | -1806.53 | 5.1981 | 59.8734 | 64.1561 | -529.4417
2024-06-25 12:00 | -762.359 | 2.2851 | 60.0208 | 64.1561 | -223.4254
2024-06-26 13:00 | -383.135 | 1.4867 | 60.4806 | 64.1561 | -112.2858
2024-06-27 14:00 | 1428.43 | 1 | 61.2882 | 64.1561 | 418.6315
2024-06-28 15:00 | 2875.95 | 1 | 61.2205 | 64.1561 | 842.8577
2024-06-29 16:00 | 2957.05 | 1 | 75.5673 | 64.1561 | 866.6258
2024-06-30 17:00 | 3025.09 | 1 | 61.705 | 64.1561 | 886.5664
2024-07-01 18:00 | 2923.35 | 1 | 61.8924 | 64.1561 | 856.7493
2024-07-02 19:00 | 0 | 0 | 62.7296 | 64.1561 | 0
2024-07-03 20:00 | -623.76 | 1.9943 | 61.2903 | 64.1561 | -182.806
2024-07-04 21:00 | -1496.9 | 4.6045 | 61.0792 | 64.1561 | -438.6981
2024-07-05 22:00 | -1994.45 | 5.7842 | 60.8441 | 64.1561 | -584.5156
2024-07-06 23:00 | -3040.57 | 6.4446 | 60.1985 | 64.1561 | -891.1031
2024-07-08 | -3531.88 | 6.4446 | 59.6788 | 64.1561 | -1035.0919
2024-07-09 01:00 | -3810.91 | 6.4446 | 59.3525 | 64.1561 | -1116.8675
2024-07-10 02:00 | -3949.57 | 6.4446 | 59.1313 | 64.1561 | -1157.5047
2024-07-11 03:00 | -4102.12 | 6.4446 | 58.9187 | 64.1561 | -1202.2127
2024-07-12 04:00 | -4073.91 | 6.4446 | 58.823 | 64.1561 | -1193.9452
2024-07-13 05:00 | -4115.42 | 6.4446 | 58.7197 | 64.1561 | -1206.1105
2024-07-14 06:00 | -3788.02 | 6.4446 | 58.8459 | 64.1561 | -1110.1591
2024-07-15 07:00 | -3586.14 | 6.4446 | 58.9662 | 64.1561 | -1050.9939
2024-07-16 08:00 | -2243.19 | 6.4446 | 59.7895 | 64.1561 | -657.4141
2024-07-17 09:00 | -1357.59 | 3.8554 | 59.9164 | 64.1561 | -397.8704
2024-07-18 10:00 | 2243.97 | 1 | 60.9314 | 64.1561 | 657.6427
2024-07-19 11:00 | 3266.09 | 1 | 75.4282 | 64.1561 | 957.1965
2024-07-20 12:00 | 5147.47 | 1.6392 | 74.6522 | 64.1561 | 1508.5745
2024-07-21 13:00 | 6033.04 | 1.934 | 75.029 | 64.1561 | 1768.1095
2024-07-22 14:00 | 6620.41 | 2.1383 | 75.3431 | 64.1561 | 1940.2506
2024-07-23 15:00 | 6887.84 | 2.2501 | 75.5583 | 64.1561 | 2018.6266
2024-07-24 16:00 | 7622.48 | 2.4869 | 75.8316 | 64.1561 | 2233.9284
2024-07-25 17:00 | 6638.43 | 2.1348 | 76.3037 | 64.1561 | 1945.5318
2024-07-26 18:00 | 5426.39 | 1.7227 | 76.5737 | 64.1561 | 1590.3179
2024-07-27 19:00 | 3672.93 | 1.1654 | 76.5784 | 64.1561 | 1076.4295
2024-07-28 20:00 | 3155.76 | 1 | 80.821 | 64.1561 | 924.862
2024-07-29 21:00 | 2795.16 | 1 | 63.3654 | 64.1561 | 819.1805
2024-07-30 22:00 | -121.486 | 0.93422 | 63.4393 | 64.1561 | -35.604
2024-07-31 23:00 | -1103.55 | 3.5314 | 62.3563 | 64.1561 | -323.4186
2024-08-02 | -1410.01 | 4.1787 | 61.9378 | 64.1561 | -413.2331
2024-08-03 01:00 | -1549.73 | 4.5181 | 61.7192 | 64.1561 | -454.181
2024-08-04 02:00 | -1756.05 | 5.0727 | 61.5439 | 64.1561 | -514.6475
2024-08-05 03:00 | -1868.97 | 5.3485 | 61.3665 | 64.1561 | -547.741
2024-08-06 04:00 | -1830.45 | 5.2221 | 61.2471 | 64.1561 | -536.4519
2024-08-07 05:00 | -1792.43 | 5.1315 | 61.181 | 64.1561 | -525.3094
2024-08-08 06:00 | -1570.49 | 4.5193 | 61.1366 | 64.1561 | -460.2652
2024-08-09 07:00 | -1277.09 | 3.7543 | 61.1542 | 64.1561 | -374.2781
2024-08-10 08:00 | -826.988 | 2.5681 | 61.2353 | 64.1561 | -242.3663
2024-08-11 09:00 | 0 | 1 | 62.54 | 64.1561 | 0
2024-08-12 10:00 | 2282.07 | 1.0308 | 71.3361 | 64.1561 | 668.8087
2024-08-13 11:00 | 2803.59 | 1 | 76.1169 | 64.1561 | 821.6511
2024-08-14 12:00 | 3102.96 | 1.0248 | 75.0435 | 64.1561 | 909.3878
2024-08-15 13:00 | 3986.33 | 1.2831 | 75.5156 | 64.1561 | 1168.278
2024-08-16 14:00 | 3725.45 | 1.1897 | 75.8318 | 64.1561 | 1091.8216
2024-08-17 15:00 | 5388.27 | 1.7458 | 75.7713 | 64.1561 | 1579.1461
2024-08-18 16:00 | 5666.42 | 1.8916 | 75.6641 | 64.1561 | 1660.6638
2024-08-19 17:00 | 4780.28 | 1.5569 | 76.1645 | 64.1561 | 1400.9618
2024-08-20 18:00 | 3519.86 | 1.1841 | 75.8271 | 64.1561 | 1031.5691
2024-08-21 19:00 | 2955.06 | 1 | 63.425 | 64.1561 | 866.0426
2024-08-22 20:00 | 2922.66 | 1 | 63.3956 | 64.1561 | 856.5471
2024-08-23 21:00 | -613.897 | 2.2544 | 63.0087 | 64.1561 | -179.9155
2024-08-24 22:00 | -1219.7 | 3.746 | 62.3898 | 64.1561 | -357.4588
2024-08-25 23:00 | -2358.02 | 6.4446 | 61.9445 | 64.1561 | -691.0674
2024-08-27 | -3222.32 | 6.4446 | 61.1547 | 64.1561 | -944.3688
2024-08-28 01:00 | -3709.13 | 6.4446 | 60.5707 | 64.1561 | -1087.0387
2024-08-29 02:00 | -4244.27 | 6.4446 | 59.9804 | 64.1561 | -1243.8728
2024-08-30 03:00 | -4462.38 | 6.4446 | 59.6222 | 64.1561 | -1307.7945
2024-08-31 04:00 | -4633.45 | 6.4446 | 59.3159 | 64.1561 | -1357.9301
2024-09-01 05:00 | -4781.88 | 6.4446 | 59.0596 | 64.1561 | -1401.4307
2024-09-02 06:00 | -4744.1 | 6.4446 | 58.9394 | 64.1561 | -1390.3585
2024-09-03 07:00 | -3665.77 | 6.4446 | 59.4806 | 64.1561 | -1074.3311
2024-09-04 08:00 | -2488.38 | 6.4446 | 60.2117 | 64.1561 | -729.2722
2024-09-05 09:00 | -1863.08 | 5.2698 | 60.4657 | 64.1561 | -546.0148
2024-09-06 10:00 | -1134.47 | 3.3069 | 60.6033 | 64.1561 | -332.4803
2024-09-07 11:00 | 2407.15 | 1 | 61.4988 | 64.1561 | 705.466
2024-09-08 12:00 | 2856.01 | 1 | 77.9035 | 64.1561 | 837.0139
2024-09-09 13:00 | 3786.32 | 1.3128 | 74.1282 | 64.1561 | 1109.6609
2024-09-10 14:00 | 4251.01 | 1.4599 | 74.5168 | 64.1561 | 1245.848
2024-09-11 15:00 | 4519.87 | 1.5609 | 74.7044 | 64.1561 | 1324.6431
2024-09-12 16:00 | 3220.85 | 1.1243 | 74.8054 | 64.1561 | 943.938
2024-09-13 17:00 | 4893.93 | 1.6728 | 75.0256 | 64.1561 | 1434.2693
2024-09-14 18:00 | 3153.26 | 1.09 | 75.1343 | 64.1561 | 924.1293
2024-09-15 19:00 | 2869.16 | 1 | 81.8919 | 64.1561 | 840.8678
2024-09-16 20:00 | 2776.73 | 1 | 63.0838 | 64.1561 | 813.7792
2024-09-17 21:00 | 0 | 0 | 63.7733 | 64.1561 | 0
2024-09-18 22:00 | -346.398 | 1.3799 | 62.5356 | 64.1561 | -101.5192
2024-09-19 23:00 | -805.538 | 2.6932 | 62.1354 | 64.1561 | -236.0799
2024-09-21 | -2305.3 | 6.4446 | 61.7752 | 64.1561 | -675.6167
2024-09-22 01:00 | -2848.59 | 6.4446 | 61.172 | 64.1561 | -834.8393
2024-09-23 02:00 | -3058.08 | 6.4446 | 60.7948 | 64.1561 | -896.2348
2024-09-24 03:00 | -3271.37 | 6.4446 | 60.5123 | 64.1561 | -958.7439
2024-09-25 04:00 | -3375.17 | 6.4446 | 60.3173 | 64.1561 | -989.1647
2024-09-26 05:00 | -3605.84 | 6.4446 | 60.0434 | 64.1561 | -1056.7674
2024-09-27 06:00 | -3776.77 | 6.4446 | 59.8344 | 64.1561 | -1106.862
2024-09-28 07:00 | -2899.01 | 6.4446 | 60.2631 | 64.1561 | -849.616
2024-09-29 08:00 | -2317.09 | 6.4446 | 60.6235 | 64.1561 | -679.072
2024-09-30 09:00 | -1962.83 | 5.5295 | 60.7012 | 64.1561 | -575.2487
2024-10-01 10:00 | -924.52 | 2.6864 | 60.7831 | 64.1561 | -270.9501
2024-10-02 11:00 | 2612.24 | 1 | 61.6284 | 64.1561 | 765.572
2024-10-03 12:00 | 3588.22 | 1.151 | 74.9488 | 64.1561 | 1051.6035
2024-10-04 13:00 | 4407.04 | 1.369 | 75.6778 | 64.1561 | 1291.5759
2024-10-05 14:00 | 5065.47 | 1.5903 | 75.842 | 64.1561 | 1484.5427
2024-10-06 15:00 | 5293.17 | 1.7541 | 75.4801 | 64.1561 | 1551.275
2024-10-07 16:00 | 4809.54 | 1.5245 | 76.2731 | 64.1561 | 1409.537
2024-10-08 17:00 | 6603.38 | 2.218 | 75.6684 | 64.1561 | 1935.2596
2024-10-09 18:00 | 5004.45 | 1.5818 | 76.717 | 64.1561 | 1466.6595
2024-10-10 19:00 | 3710 | 1.1652 | 76.8409 | 64.1561 | 1087.2937
2024-10-11 20:00 | 3145.39 | 1 | 79.6347 | 64.1561 | 921.8228
2024-10-12 21:00 | 3160.83 | 1 | 63.4984 | 64.1561 | 926.3478
2024-10-13 22:00 | 3208.61 | 1 | 63.5253 | 64.1561 | 940.3508
2024-10-14 23:00 | 3045.65 | 1 | 63.5566 | 64.1561 | 892.5919
2024-10-16 | -812.888 | 2.7928 | 63.144 | 64.1561 | -238.234
2024-10-17 01:00 | -1224.54 | 3.7032 | 62.58 | 64.1561 | -358.8772
2024-10-18 02:00 | -1462.66 | 4.2901 | 62.2787 | 64.1561 | -428.6633
2024-10-19 03:00 | -1648.1 | 4.7589 | 62.099 | 64.1561 | -483.0104
2024-10-20 04:00 | -1638.42 | 4.6979 | 61.9369 | 64.1561 | -480.1735
2024-10-21 05:00 | -1424.82 | 4.1178 | 61.799 | 64.1561 | -417.5735
2024-10-22 06:00 | -927.641 | 2.794 | 61.8227 | 64.1561 | -271.8647
2024-10-23 07:00 | -781.374 | 2.5097 | 61.9322 | 64.1561 | -228.9981
2024-10-24 08:00 | -315.954 | 1.2549 | 62.1823 | 64.1561 | -92.597
2024-10-25 09:00 | -1279.23 | 4.0088 | 61.9692 | 64.1561 | -374.9053
2024-10-26 10:00 | -416.093 | 1.3934 | 61.9473 | 64.1561 | -121.9448
2024-10-27 11:00 | 2560.94 | 1 | 62.5114 | 64.1561 | 750.5374
2024-10-28 12:00 | 3046.58 | 1.0203 | 75.1775 | 64.1561 | 892.8645
2024-10-29 13:00 | 3578.37 | 1.1998 | 75.3589 | 64.1561 | 1048.7167
2024-10-30 14:00 | 3700.09 | 1.2657 | 75.2936 | 64.1561 | 1084.3893
2024-10-31 15:00 | 3944.77 | 1.3667 | 75.3069 | 64.1561 | 1156.098
2024-11-01 16:00 | 3829.32 | 1.3301 | 75.4325 | 64.1561 | 1122.2629
2024-11-02 17:00 | 3470.27 | 1.2047 | 75.494 | 64.1561 | 1017.0357
2024-11-03 18:00 | 2855.77 | 1 | 81.571 | 64.1561 | 836.9436
2024-11-04 19:00 | 2626.32 | 1 | 63.5698 | 64.1561 | 769.6984
2024-11-05 20:00 | -261.069 | 1.3058 | 63.3878 | 64.1561 | -76.5118
2024-11-06 21:00 | -1412.48 | 4.3401 | 62.5809 | 64.1561 | -413.957
2024-11-07 22:00 | -2125.6 | 6.0763 | 62.1817 | 64.1561 | -622.9519
2024-11-08 23:00 | -3295.13 | 6.4446 | 61.2831 | 64.1561 | -965.7073
2024-11-10 | -3773.53 | 6.4446 | 60.6892 | 64.1561 | -1105.9125
2024-11-11 01:00 | -4116.7 | 6.4446 | 60.2022 | 64.1561 | -1206.4857
2024-11-12 02:00 | -4381 | 6.4446 | 59.8362 | 64.1561 | -1283.9444
2024-11-13 03:00 | -4590.06 | 6.4446 | 59.5249 | 64.1561 | -1345.2138
2024-11-14 04:00 | -4631.87 | 6.4446 | 59.3289 | 64.1561 | -1357.4671
2024-11-15 05:00 | -4568.39 | 6.4446 | 59.2348 | 64.1561 | -1338.8629
2024-11-16 06:00 | -4345.03 | 6.4446 | 59.2658 | 64.1561 | -1273.4026
2024-11-17 07:00 | -3718.57 | 6.4446 | 59.5705 | 64.1561 | -1089.8053
2024-11-18 08:00 | -2189.33 | 6.2591 | 60.4705 | 64.1561 | -641.6293
2024-11-19 09:00 | -1356.64 | 3.8363 | 60.6196 | 64.1561 | -397.5919
2024-11-20 10:00 | 2084.61 | 1 | 61.6779 | 64.1561 | 610.9389
2024-11-21 11:00 | 3017.31 | 1.0438 | 73.976 | 64.1561 | 884.2863
2024-11-22 12:00 | 5055.85 | 1.6689 | 74.8587 | 64.1561 | 1481.7234
2024-11-23 13:00 | 6373.89 | 2.0473 | 75.6307 | 64.1561 | 1868.0028
2024-11-24 14:00 | 7152.23 | 2.2806 | 76.1638 | 64.1561 | 2096.1117
2024-11-25 15:00 | 7709.02 | 2.4301 | 76.701 | 64.1561 | 2259.2907
2024-11-26 16:00 | 9007.42 | 2.8252 | 77.0817 | 64.1561 | 2639.8142
2024-11-27 17:00 | 8171.52 | 2.5868 | 77.3715 | 64.1561 | 2394.8361
2024-11-28 18:00 | 6827.32 | 2.1162 | 77.8365 | 64.1561 | 2000.89
2024-11-29 19:00 | 5323.05 | 1.646 | 77.8938 | 64.1561 | 1560.032
2024-11-30 20:00 | 4012.34 | 1.2687 | 77.5445 | 64.1561 | 1175.9008
2024-12-01 21:00 | 3113.07 | 1 | 64.311 | 64.1561 | 912.3508
2024-12-02 22:00 | 3023.36 | 1 | 64.1657 | 64.1561 | 886.0594
2024-12-03 23:00 | -492.705 | 1.9088 | 63.7872 | 64.1561 | -144.3976
2024-12-05 | -1074.55 | 3.3483 | 63.1042 | 64.1561 | -314.9195
2024-12-06 01:00 | -1508.89 | 4.4264 | 62.7116 | 64.1561 | -442.212
2024-12-07 02:00 | -1847.96 | 5.2771 | 62.4599 | 64.1561 | -541.5836
2024-12-08 03:00 | -2049.04 | 5.7708 | 62.2375 | 64.1561 | -600.5143
2024-12-09 04:00 | -2172.19 | 6.0836 | 62.0217 | 64.1561 | -636.606
2024-12-10 05:00 | -2151.77 | 6.007 | 61.8881 | 64.1561 | -630.6215
2024-12-11 06:00 | -1712.82 | 4.7954 | 61.797 | 64.1561 | -501.978
2024-12-12 07:00 | -1517.44 | 4.3652 | 61.8106 | 64.1561 | -444.7178
2024-12-13 08:00 | -636.594 | 1.9668 | 61.888 | 64.1561 | -186.5673
2024-12-14 09:00 | 1848.19 | 1 | 62.7918 | 64.1561 | 541.651
2024-12-15 10:00 | 3058.44 | 1 | 79.877 | 64.1561 | 896.3403
2024-12-16 11:00 | 5398.67 | 1.7328 | 75.9985 | 64.1561 | 1582.194
2024-12-17 12:00 | 6481.26 | 2.1871 | 75.831 | 64.1561 | 1899.4698
2024-12-18 13:00 | 5155.62 | 1.641 | 76.9259 | 64.1561 | 1510.9631
2024-12-19 14:00 | 4730.73 | 1.5388 | 76.7664 | 64.1561 | 1386.4401
2024-12-20 15:00 | 5091.79 | 1.6645 | 76.7443 | 64.1561 | 1492.2563
2024-12-21 16:00 | 6366.55 | 2.125 | 76.6053 | 64.1561 | 1865.8516
2024-12-22 17:00 | 5009.28 | 1.6409 | 77.0419 | 64.1561 | 1468.075
2024-12-23 18:00 | 3078.12 | 1.0477 | 76.5692 | 64.1561 | 902.1079
2024-12-24 19:00 | 2787.82 | 1 | 64.2211 | 64.1561 | 817.0294
2024-12-25 20:00 | 0 | 0 | 64.8119 | 64.1561 | 0
2024-12-26 21:00 | -1329.56 | 4.0765 | 63.1903 | 64.1561 | -389.6556
2024-12-27 22:00 | -1998.17 | 5.7079 | 62.7096 | 64.1561 | -585.6058
2024-12-28 23:00 | -3447.06 | 6.4446 | 61.6906 | 64.1561 | -1010.2336
2024-12-30 | -3972.63 | 6.4446 | 61.0114 | 64.1561 | -1164.2629
2024-12-31 01:00 | -4269.69 | 6.4446 | 60.521 | 64.1561 | -1251.3226
2025-01-01 02:00 | -4491.76 | 6.4446 | 60.1686 | 64.1561 | -1316.4049
2025-01-02 03:00 | -4529.54 | 6.4446 | 59.9558 | 64.1561 | -1327.4771
2025-01-03 04:00 | -4424.01 | 6.4446 | 59.8464 | 64.1561 | -1296.5493
2025-01-04 05:00 | -4369.06 | 6.4446 | 59.7671 | 64.1561 | -1280.4451
2025-01-05 06:00 | -4061.26 | 6.4446 | 59.8695 | 64.1561 | -1190.2378
2025-01-06 07:00 | -3787.83 | 6.4446 | 59.9853 | 64.1561 | -1110.1034
2025-01-07 08:00 | -2858.25 | 6.4446 | 60.5361 | 64.1561 | -837.6704
2025-01-08 09:00 | -2137 | 6.0289 | 60.9535 | 64.1561 | -626.2929
2025-01-09 10:00 | -941.226 | 2.6766 | 61.0485 | 64.1561 | -275.8461
2025-01-10 11:00 | 2594.89 | 1 | 61.9684 | 64.1561 | 760.4872
2025-01-11 12:00 | 2864.36 | 1 | 74.7068 | 64.1561 | 839.4611
2025-01-12 13:00 | 4860.86 | 1.5773 | 75.4069 | 64.1561 | 1424.5774
2025-01-13 14:00 | 5623.33 | 1.8422 | 75.6829 | 64.1561 | 1648.0353
2025-01-14 15:00 | 5593.97 | 1.8785 | 75.752 | 64.1561 | 1639.4308
2025-01-15 16:00 | 6379.89 | 2.132 | 76.0385 | 64.1561 | 1869.7612
2025-01-16 17:00 | 5324.04 | 1.8127 | 76.0644 | 64.1561 | 1560.3221
2025-01-17 18:00 | 3881.6 | 1.3373 | 76.0238 | 64.1561 | 1137.5847
2025-01-18 19:00 | 2897.85 | 1 | 82.0965 | 64.1561 | 849.276
2025-01-19 20:00 | 2832.58 | 1 | 63.8152 | 64.1561 | 830.1473
2025-01-20 21:00 | -769.677 | 2.6611 | 63.348 | 64.1561 | -225.5701
2025-01-21 22:00 | -1463.44 | 4.3613 | 62.752 | 64.1561 | -428.8919
2025-01-22 23:00 | -2517.57 | 6.4446 | 62.219 | 64.1561 | -737.8269
2025-01-24 | -3135.4 | 6.4446 | 61.5744 | 64.1561 | -918.895
2025-01-25 01:00 | -3451.38 | 6.4446 | 61.1152 | 64.1561 | -1011.4996
2025-01-26 02:00 | -3808.86 | 6.4446 | 60.6506 | 64.1561 | -1116.2667
2025-01-27 03:00 | -4008.29 | 6.4446 | 60.3437 | 64.1561 | -1174.7138
2025-01-28 04:00 | -4130.47 | 6.4446 | 60.0926 | 64.1561 | -1210.5213
2025-01-29 05:00 | -4104.93 | 6.4446 | 59.9665 | 64.1561 | -1203.0362
2025-01-30 06:00 | -3718.72 | 6.4446 | 60.096 | 64.1561 | -1089.8492
2025-01-31 07:00 | -3741.05 | 6.4446 | 60.0371 | 64.1561 | -1096.3935
2025-02-01 08:00 | -3438.09 | 6.4446 | 60.1532 | 64.1561 | -1007.6047
2025-02-02 09:00 | -3423.87 | 6.4446 | 60.1474 | 64.1561 | -1003.4372
2025-02-03 10:00 | -2912.33 | 6.4446 | 60.4271 | 64.1561 | -853.5197
2025-02-04 11:00 | -2191.45 | 6.1979 | 60.8122 | 64.1561 | -642.2506
2025-02-05 12:00 | -2051.21 | 5.7903 | 60.86 | 64.1561 | -601.1503
2025-02-06 13:00 | -1963 | 5.5787 | 60.8824 | 64.1561 | -575.2985
2025-02-07 14:00 | -1858.33 | 5.3034 | 60.8784 | 64.1561 | -544.6228
2025-02-08 15:00 | -1592.69 | 4.58 | 60.8822 | 64.1561 | -466.7714
2025-02-09 16:00 | -885.485 | 2.6626 | 60.9409 | 64.1561 | -259.51
2025-02-10 17:00 | -738.709 | 2.428 | 61.114 | 64.1561 | -216.4942
2025-02-11 18:00 | -923.084 | 2.9618 | 61.1303 | 64.1561 | -270.5292
2025-02-12 19:00 | -1428.34 | 4.3281 | 61.062 | 64.1561 | -418.6051
2025-02-13 20:00 | -1914.44 | 5.575 | 60.9659 | 64.1561 | -561.067
2025-02-14 21:00 | -2877.94 | 6.4446 | 60.5091 | 64.1561 | -843.441
2025-02-15 22:00 | -3321.04 | 6.4446 | 60.1036 | 64.1561 | -973.3007
2025-02-16 23:00 | -4140.22 | 6.4446 | 59.48 | 64.1561 | -1213.3787
2025-02-18 | -4518.94 | 6.4446 | 59.0862 | 64.1561 | -1324.3706
2025-02-19 01:00 | -4710.9 | 6.4446 | 58.8259 | 64.1561 | -1380.6285
2025-02-20 02:00 | -5008.94 | 6.4446 | 58.532 | 64.1561 | -1467.9754
2025-02-21 03:00 | -5094.55 | 6.4446 | 58.3704 | 64.1561 | -1493.0652
2025-02-22 04:00 | -5065.4 | 6.4446 | 58.2906 | 64.1561 | -1484.5222
2025-02-23 05:00 | -5266.71 | 6.4446 | 58.1006 | 64.1561 | -1543.5203
2025-02-24 06:00 | -5225.34 | 6.4446 | 58.0419 | 64.1561 | -1531.396
2025-02-25 07:00 | -4386.29 | 6.4446 | 58.4885 | 64.1561 | -1285.4947
2025-02-26 08:00 | -3327.41 | 6.4446 | 59.1729 | 64.1561 | -975.1676
2025-02-27 09:00 | -3331.18 | 6.4446 | 59.2989 | 64.1561 | -976.2725
2025-02-28 10:00 | -3288.97 | 6.4446 | 59.3705 | 64.1561 | -963.902
2025-03-01 11:00 | -2986.65 | 6.4446 | 59.5724 | 64.1561 | -875.3007
2025-03-02 12:00 | -1698.13 | 4.8445 | 60.0623 | 64.1561 | -497.6728
2025-03-03 13:00 | -951.132 | 2.8434 | 60.2826 | 64.1561 | -278.7493
2025-03-04 14:00 | -270.359 | 1.1158 | 60.7974 | 64.1561 | -79.2344
2025-03-05 15:00 | 0 | 1 | 61.9067 | 64.1561 | 0
2025-03-06 16:00 | 806.23 | 1 | 61.8418 | 64.1561 | 236.2827
2025-03-07 17:00 | 2867.37 | 1 | 61.5371 | 64.1561 | 840.3432
2025-03-08 18:00 | 0 | 0 | 62.5758 | 64.1561 | 0
2025-03-09 19:00 | -1228.78 | 3.6649 | 61.1556 | 64.1561 | -360.1199
2025-03-10 20:00 | -1992.61 | 5.8592 | 60.9504 | 64.1561 | -583.9763
2025-03-11 21:00 | -2513.21 | 6.4446 | 60.6323 | 64.1561 | -736.5491
2025-03-12 22:00 | -3244.63 | 6.4446 | 60.0654 | 64.1561 | -950.9072
2025-03-13 23:00 | -3828.03 | 6.4446 | 59.5208 | 64.1561 | -1121.8848
2025-03-15 | -5336.97 | 6.4446 | 58.4438 | 64.1561 | -1564.1115
2025-03-16 01:00 | -5862.22 | 6.4446 | 57.8587 | 64.1561 | -1718.0471
2025-03-17 02:00 | -6587.03 | 6.4446 | 57.1922 | 64.1561 | -1930.4679
2025-03-18 03:00 | -6891.51 | 6.4446 | 56.775 | 64.1561 | -2019.7022
2025-03-19 04:00 | -7083.8 | 6.4446 | 56.4475 | 64.1561 | -2076.0568
2025-03-20 05:00 | -7265.28 | 6.4446 | 56.1325 | 64.1561 | -2129.2434
2025-03-21 06:00 | -7631.04 | 6.4446 | 55.7566 | 64.1561 | -2236.4371
2025-03-22 07:00 | -6664.91 | 6.4446 | 56.1799 | 64.1561 | -1953.2923
2025-03-23 08:00 | -5463.63 | 6.4446 | 56.8933 | 64.1561 | -1601.2319
2025-03-24 09:00 | -4840.97 | 6.4446 | 57.3637 | 64.1561 | -1418.7483
2025-03-25 10:00 | -3500.66 | 6.4446 | 58.2627 | 64.1561 | -1025.9422
2025-03-26 11:00 | -2192.43 | 6.3641 | 59.2137 | 64.1561 | -642.5378
2025-03-27 12:00 | -1392.05 | 3.9849 | 59.4462 | 64.1561 | -407.9696
2025-03-28 13:00 | -898.571 | 2.7947 | 59.7823 | 64.1561 | -263.3452
2025-03-29 14:00 | -590.467 | 2.0282 | 60.0907 | 64.1561 | -173.0488
2025-03-30 15:00 | -433.477 | 1.6532 | 60.3708 | 64.1561 | -127.0396
2025-03-31 16:00 | -608.045 | 2.1738 | 60.4284 | 64.1561 | -178.2004
2025-04-01 17:00 | 1844.41 | 1 | 61.1453 | 64.1561 | 540.5432
2025-04-02 18:00 | -830.228 | 2.9221 | 60.8161 | 64.1561 | -243.3158
2025-04-03 19:00 | -1805.74 | 5.4283 | 60.5486 | 64.1561 | -529.2102
2025-04-04 20:00 | -2531.96 | 6.4446 | 60.1707 | 64.1561 | -742.0442
2025-04-05 21:00 | -3312.64 | 6.4446 | 59.5932 | 64.1561 | -970.8389
2025-04-06 22:00 | -4133.26 | 6.4446 | 58.9609 | 64.1561 | -1211.3389
2025-04-07 23:00 | -4437.37 | 6.4446 | 58.5544 | 64.1561 | -1300.4648
2025-04-09 | -5871.37 | 6.4446 | 57.5413 | 64.1561 | -1720.7287
2025-04-10 01:00 | -6327.74 | 6.4446 | 57.0132 | 64.1561 | -1854.4775
2025-04-11 02:00 | -6452.27 | 6.4446 | 56.7275 | 64.1561 | -1890.9737
2025-04-12 03:00 | -6837.89 | 6.4446 | 56.3473 | 64.1561 | -2003.9877
2025-04-13 04:00 | -6471.48 | 6.4446 | 56.4172 | 64.1561 | -1896.6036
2025-04-14 05:00 | -6518.21 | 6.4446 | 56.2841 | 64.1561 | -1910.2988
2025-04-15 06:00 | -6204.09 | 6.4446 | 56.4126 | 64.1561 | -1818.2393
2025-04-16 07:00 | -5719.53 | 6.4446 | 56.6828 | 64.1561 | -1676.2288
2025-04-17 08:00 | -4415.05 | 6.4446 | 57.4924 | 64.1561 | -1293.9234
2025-04-18 09:00 | -3530.05 | 6.4446 | 58.1745 | 64.1561 | -1034.5555
2025-04-19 10:00 | -1786.12 | 5.1823 | 59.1296 | 64.1561 | -523.4601
2025-04-20 11:00 | -385.618 | 1.2316 | 59.5204 | 64.1561 | -113.0135
2025-04-21 12:00 | 2788.08 | 1 | 60.4086 | 64.1561 | 817.1056
2025-04-22 13:00 | 3149.42 | 1.1019 | 72.8405 | 64.1561 | 923.0039
2025-04-23 14:00 | 3650.67 | 1.2684 | 73.2654 | 64.1561 | 1069.9058
2025-04-24 15:00 | 4238.44 | 1.4788 | 73.527 | 64.1561 | 1242.1641
2025-04-25 16:00 | 4884.03 | 1.6887 | 73.932 | 64.1561 | 1431.3679
2025-04-26 17:00 | 4012.4 | 1.4016 | 74.1125 | 64.1561 | 1175.9184
2025-04-27 18:00 | 2836.72 | 1 | 76.0609 | 64.1561 | 831.3606
2025-04-28 19:00 | 2724.36 | 1 | 62.3604 | 64.1561 | 798.4311
2025-04-29 20:00 | -199.934 | 1.1441 | 62.373 | 64.1561 | -58.5949
2025-04-30 21:00 | -1421.12 | 4.4304 | 61.5441 | 64.1561 | -416.4892
2025-05-01 22:00 | -2227.22 | 6.4344 | 61.1679 | 64.1561 | -652.7337
2025-05-02 23:00 | -3622.49 | 6.4446 | 60.102 | 64.1561 | -1061.647
2025-05-04 | -4182.4 | 6.4446 | 59.4605 | 64.1561 | -1225.7404
2025-05-05 01:00 | -4433.1 | 6.4446 | 59.0354 | 64.1561 | -1299.2134
2025-05-06 02:00 | -4830.69 | 6.4446 | 58.613 | 64.1561 | -1415.7355
2025-05-07 03:00 | -5057.2 | 6.4446 | 58.2977 | 64.1561 | -1482.119
2025-05-08 04:00 | -5199.03 | 6.4446 | 58.0421 | 64.1561 | -1523.6853
2025-05-09 05:00 | -5180.01 | 6.4446 | 57.9257 | 64.1561 | -1518.1111
2025-05-10 06:00 | -4838.73 | 6.4446 | 58.0411 | 64.1561 | -1418.0918
2025-05-11 07:00 | -4421.7 | 6.4446 | 58.2456 | 64.1561 | -1295.8724
2025-05-12 08:00 | -3139.4 | 6.4446 | 59.0321 | 64.1561 | -920.0673
2025-05-13 09:00 | -2003.4 | 5.7554 | 59.711 | 64.1561 | -587.1386
2025-05-14 10:00 | -472.22 | 1.4146 | 59.9522 | 64.1561 | -138.394
2025-05-15 11:00 | 2773.65 | 1 | 60.8774 | 64.1561 | 812.8766
2025-05-16 12:00 | 3105.68 | 1.0887 | 73.2483 | 64.1561 | 910.185
2025-05-17 13:00 | 4293.96 | 1.4702 | 73.8321 | 64.1561 | 1258.4355
2025-05-18 14:00 | 4817.37 | 1.647 | 74.1978 | 64.1561 | 1411.8318
2025-05-19 15:00 | 4488.03 | 1.5461 | 74.4338 | 64.1561 | 1315.3118
2025-05-20 16:00 | 4554.01 | 1.5676 | 74.6373 | 64.1561 | 1334.6486
2025-05-21 17:00 | 3757.43 | 1.2974 | 74.7424 | 64.1561 | 1101.194
2025-05-22 18:00 | 2896.41 | 1 | 75.3692 | 64.1561 | 848.854
2025-05-23 19:00 | 2930.22 | 1 | 62.7415 | 64.1561 | 858.7627
2025-05-24 20:00 | 2814.04 | 1 | 62.8099 | 64.1561 | 824.7137
2025-05-25 21:00 | -515.911 | 2.0015 | 62.5197 | 64.1561 | -151.1986
2025-05-26 22:00 | -1003.29 | 3.1907 | 61.9658 | 64.1561 | -294.0353
2025-05-27 23:00 | -1891.87 | 5.5697 | 61.6356 | 64.1561 | -554.4524
2025-05-29 | -2235.64 | 6.3312 | 61.3882 | 64.1561 | -655.2014
2025-05-30 01:00 | -2549.36 | 6.4446 | 61.0346 | 64.1561 | -747.1437
2025-05-31 02:00 | -2715.02 | 6.4446 | 60.7524 | 64.1561 | -795.6938
2025-06-01 03:00 | -2798.73 | 6.4446 | 60.5946 | 64.1561 | -820.2268
2025-06-02 04:00 | -2961.6 | 6.4446 | 60.4047 | 64.1561 | -867.9593
2025-06-03 05:00 | -2980.82 | 6.4446 | 60.3167 | 64.1561 | -873.5921
2025-06-04 06:00 | -2736.06 | 6.4446 | 60.4091 | 64.1561 | -801.86
2025-06-05 07:00 | -2808.59 | 6.4446 | 60.3434 | 64.1561 | -823.1165
2025-06-06 08:00 | -2878.48 | 6.4446 | 60.2526 | 64.1561 | -843.5992
2025-06-07 09:00 | -3407.72 | 6.4446 | 59.8967 | 64.1561 | -998.7041
2025-06-08 10:00 | -2836.52 | 6.4446 | 60.1476 | 64.1561 | -831.302
2025-06-09 11:00 | -2151.49 | 6.1075 | 60.4765 | 64.1561 | -630.5395
2025-06-10 12:00 | -2018.56 | 5.7322 | 60.5141 | 64.1561 | -591.5815
2025-06-11 13:00 | -2087.12 | 5.9634 | 60.5225 | 64.1561 | -611.6745
2025-06-12 14:00 | -2081.24 | 5.9275 | 60.4817 | 64.1561 | -609.9512
2025-06-13 15:00 | -2229.41 | 6.3553 | 60.4574 | 64.1561 | -653.3756
2025-06-14 16:00 | -1668.81 | 4.7232 | 60.3916 | 64.1561 | -489.0799
2025-06-15 17:00 | -1499.69 | 4.3977 | 60.4473 | 64.1561 | -439.5158
2025-06-16 18:00 | -1419.29 | 4.2001 | 60.4704 | 64.1561 | -415.9528
2025-06-17 19:00 | -1867.98 | 5.4911 | 60.4644 | 64.1561 | -547.4509
2025-06-18 20:00 | -2145.42 | 6.1637 | 60.3858 | 64.1561 | -628.7605
2025-06-19 21:00 | -3258.79 | 6.4446 | 59.7367 | 64.1561 | -955.0571
2025-06-20 22:00 | -3882.59 | 6.4446 | 59.213 | 64.1561 | -1137.8748
2025-06-21 23:00 | -4924.61 | 6.4446 | 58.4257 | 64.1561 | -1443.2607
2025-06-23 | -5244.12 | 6.4446 | 58.0223 | 64.1561 | -1536.8999
2025-06-24 01:00 | -5286.25 | 6.4446 | 57.831 | 64.1561 | -1549.2469
2025-06-25 02:00 | -5785.02 | 6.4446 | 57.4107 | 64.1561 | -1695.422
2025-06-26 03:00 | -5874.99 | 6.4446 | 57.2168 | 64.1561 | -1721.7896
2025-06-27 04:00 | -5881.54 | 6.4446 | 57.0966 | 64.1561 | -1723.7092
2025-06-28 05:00 | -5811.71 | 6.4446 | 57.0591 | 64.1561 | -1703.2441
2025-06-29 06:00 | -5347.34 | 6.4446 | 57.2758 | 64.1561 | -1567.1507
2025-06-30 07:00 | -5188.57 | 6.4446 | 57.3599 | 64.1561 | -1520.6198
2025-07-01 08:00 | -5332.15 | 6.4446 | 57.2613 | 64.1561 | -1562.6989
2025-07-02 09:00 | -5822.37 | 6.4446 | 56.9241 | 64.1561 | -1706.3682
2025-07-03 10:00 | -5725.14 | 6.4446 | 56.887 | 64.1561 | -1677.8729
2025-07-04 11:00 | -5534.7 | 6.4446 | 56.9395 | 64.1561 | -1622.0605
2025-07-05 12:00 | -4511.35 | 6.4446 | 57.5199 | 64.1561 | -1322.1462
2025-07-06 13:00 | -4417.07 | 6.4446 | 57.6357 | 64.1561 | -1294.5154
2025-07-07 14:00 | -4148.28 | 6.4446 | 57.8198 | 64.1561 | -1215.7409
2025-07-08 15:00 | -3805.27 | 6.4446 | 58.057 | 64.1561 | -1115.2146
2025-07-09 16:00 | -3036.45 | 6.4446 | 58.5712 | 64.1561 | -889.8957
2025-07-10 17:00 | -2866.56 | 6.4446 | 58.7801 | 64.1561 | -840.1058
2025-07-11 18:00 | -3003.48 | 6.4446 | 58.7581 | 64.1561 | -880.2331
2025-07-12 19:00 | -3591.26 | 6.4446 | 58.4165 | 64.1561 | -1052.4944
2025-07-13 20:00 | -3906.67 | 6.4446 | 58.176 | 64.1561 | -1144.932
2025-07-14 21:00 | -4853.27 | 6.4446 | 57.5612 | 64.1561 | -1422.353
2025-07-15 22:00 | -5097.77 | 6.4446 | 57.2866 | 64.1561 | -1494.0089
2025-07-16 23:00 | -6027.8 | 6.4446 | 56.6253 | 64.1561 | -1766.5738
2025-07-18 | -6105.38 | 6.4446 | 56.4119 | 64.1561 | -1789.3102
2025-07-19 01:00 | -6160.09 | 6.4446 | 56.2674 | 64.1561 | -1805.3442
2025-07-20 02:00 | -6215.25 | 6.4446 | 56.1534 | 64.1561 | -1821.51
2025-07-21 03:00 | -5940.34 | 6.4446 | 56.2546 | 64.1561 | -1740.9418
2025-07-22 04:00 | -5746.38 | 6.4446 | 56.3396 | 64.1561 | -1684.0977
2025-07-23 05:00 | -5571.48 | 6.4446 | 56.4396 | 64.1561 | -1632.8396
2025-07-24 06:00 | -5092.92 | 6.4446 | 56.7264 | 64.1561 | -1492.5875
2025-07-25 07:00 | -4842.71 | 6.4446 | 56.9205 | 64.1561 | -1419.2582
2025-07-26 08:00 | -4201.88 | 6.4446 | 57.3551 | 64.1561 | -1231.4495
2025-07-27 09:00 | -4207.3 | 6.4446 | 57.4504 | 64.1561 | -1233.0379
2025-07-28 10:00 | -2148.97 | 6.3134 | 58.7278 | 64.1561 | -629.8009
2025-07-29 11:00 | -1077.3 | 3.108 | 58.9703 | 64.1561 | -315.7255
2025-07-30 12:00 | -741.354 | 2.4436 | 59.416 | 64.1561 | -217.2694
2025-07-31 13:00 | 167.528 | 1 | 60.7657 | 64.1561 | 49.0976
2025-08-01 14:00 | 2574.42 | 1 | 60.4346 | 64.1561 | 754.488
2025-08-02 15:00 | 3098.58 | 1 | 60.7678 | 64.1561 | 908.1042
2025-08-03 16:00 | 3114.93 | 1.0071 | 73.9705 | 64.1561 | 912.8959
2025-08-04 17:00 | 3126.46 | 1 | 75.6623 | 64.1561 | 916.275
2025-08-05 18:00 | 3035.77 | 1 | 61.517 | 64.1561 | 889.6964
2025-08-06 19:00 | 2909.88 | 1 | 61.7207 | 64.1561 | 852.8016
2025-08-07 20:00 | -47.6446 | 0.74261 | 62.2728 | 64.1561 | -13.9633
2025-08-08 21:00 | -1108.29 | 3.6111 | 61.1064 | 64.1561 | -324.8077
2025-08-09 22:00 | -1595.48 | 4.7549 | 60.7863 | 64.1561 | -467.589
2025-08-10 23:00 | -2532.79 | 6.4446 | 60.4332 | 64.1561 | -742.2875
2025-08-12 | -3278.85 | 6.4446 | 59.7978 | 64.1561 | -960.9361
2025-08-13 01:00 | -3539.27 | 6.4446 | 59.4251 | 64.1561 | -1037.2576
2025-08-14 02:00 | -3889.52 | 6.4446 | 59.066 | 64.1561 | -1139.9058
2025-08-15 03:00 | -4055.97 | 6.4446 | 58.8268 | 64.1561 | -1188.6875
2025-08-16 04:00 | -4146.5 | 6.4446 | 58.6473 | 64.1561 | -1215.2192
2025-08-17 05:00 | -4334.11 | 6.4446 | 58.4331 | 64.1561 | -1270.2023
2025-08-18 06:00 | -4508.92 | 6.4446 | 58.2251 | 64.1561 | -1321.434
2025-08-19 07:00 | -3471.44 | 6.4446 | 58.7493 | 64.1561 | -1017.3786
2025-08-20 08:00 | -2214.12 | 6.3963 | 59.5592 | 64.1561 | -648.8945
2025-08-21 09:00 | -1840.17 | 5.2511 | 59.7095 | 64.1561 | -539.3006
2025-08-22 10:00 | -2101.21 | 6.103 | 59.8486 | 64.1561 | -615.8039
2025-08-23 11:00 | -1036.53 | 2.979 | 59.8637 | 64.1561 | -303.777
2025-08-24 12:00 | 0 | 1 | 61.3895 | 64.1561 | 0
2025-08-25 13:00 | -174.09 | 1.0652 | 60.9603 | 64.1561 | -51.0207
2025-08-26 14:00 | 83.7307 | 1 | 61.6616 | 64.1561 | 24.539
2025-08-27 15:00 | 2747.49 | 1 | 61.1068 | 64.1561 | 805.2098
2025-08-28 16:00 | 2817.51 | 1 | 61.4686 | 64.1561 | 825.7307
2025-08-29 17:00 | 2862.31 | 1 | 79.4934 | 64.1561 | 838.8603
2025-08-30 18:00 | 2788.7 | 1 | 61.8492 | 64.1561 | 817.2873
2025-08-31 19:00 | -315.708 | 1.4723 | 61.8051 | 64.1561 | -92.5249
2025-09-01 20:00 | -951.282 | 3.1196 | 61.2268 | 64.1561 | -278.7932
2025-09-02 21:00 | -1463.74 | 4.4204 | 60.9353 | 64.1561 | -428.9798
2025-09-03 22:00 | -1974.09 | 5.7497 | 60.7656 | 64.1561 | -578.5487
2025-09-04 23:00 | -2488.39 | 6.4446 | 60.4576 | 64.1561 | -729.2751
2025-09-06 | -4289.4 | 6.4446 | 59.199 | 64.1561 | -1257.099
2025-09-07 01:00 | -4914.82 | 6.4446 | 58.5494 | 64.1561 | -1440.3916
2025-09-08 02:00 | -5413.28 | 6.4446 | 58.0179 | 64.1561 | -1586.4758
2025-09-09 03:00 | -5690.3 | 6.4446 | 57.6302 | 64.1561 | -1667.6623
2025-09-10 04:00 | -6049.04 | 6.4446 | 57.2121 | 64.1561 | -1772.7986
2025-09-11 05:00 | -6270.01 | 6.4446 | 56.874 | 64.1561 | -1837.5585
2025-09-12 06:00 | -6321.84 | 6.4446 | 56.6729 | 64.1561 | -1852.7484
2025-09-13 07:00 | -4897.11 | 6.4446 | 57.4199 | 64.1561 | -1435.2013
2025-09-14 08:00 | -3366.7 | 6.4446 | 58.4103 | 64.1561 | -986.6824
2025-09-15 09:00 | -2982.3 | 6.4446 | 58.8211 | 64.1561 | -874.0259
2025-09-16 10:00 | -1951.67 | 5.623 | 59.3867 | 64.1561 | -571.978
2025-09-17 11:00 | -826.516 | 2.4381 | 59.5843 | 64.1561 | -242.2279
2025-09-18 12:00 | 4.7792 | 1 | 61.162 | 64.1561 | 1.4006
2025-09-19 13:00 | 2855.04 | 1 | 60.7216 | 64.1561 | 836.7296
2025-09-20 14:00 | 2836.41 | 1 | 61.1848 | 64.1561 | 831.2697
2025-09-21 15:00 | 2846.91 | 1 | 77.3343 | 64.1561 | 834.347
2025-09-22 16:00 | 2884.41 | 1 | 79.3134 | 64.1561 | 845.3371
2025-09-23 17:00 | 3699.47 | 1.2883 | 73.7091 | 64.1561 | 1084.2076
2025-09-24 18:00 | 2861.92 | 1 | 62.0425 | 64.1561 | 838.746
2025-09-25 19:00 | 0 | 0 | 62.7844 | 64.1561 | 0
2025-09-26 20:00 | -670.826 | 2.1425 | 61.2994 | 64.1561 | -196.5997
2025-09-27 21:00 | -1275.53 | 3.9715 | 61.1001 | 64.1561 | -373.8209
2025-09-28 22:00 | -1838.8 | 5.4 | 60.8959 | 64.1561 | -538.8991
2025-09-29 23:00 | -2488.27 | 6.4446 | 60.553 | 64.1561 | -729.24
2025-10-01 | -3862.85 | 6.4446 | 59.5426 | 64.1561 | -1132.0896
2025-10-02 01:00 | -4391.96 | 6.4446 | 58.9664 | 64.1561 | -1287.1564
2025-10-03 02:00 | -4642.38 | 6.4446 | 58.6006 | 64.1561 | -1360.5473
2025-10-04 03:00 | -4830.32 | 6.4446 | 58.3223 | 64.1561 | -1415.6271
2025-10-05 04:00 | -4924.01 | 6.4446 | 58.1194 | 64.1561 | -1443.0849
2025-10-06 05:00 | -4950.17 | 6.4446 | 57.9691 | 64.1561 | -1450.7516
2025-10-07 06:00 | -4488.97 | 6.4446 | 58.1564 | 64.1561 | -1315.5872
2025-10-08 07:00 | -3925.9 | 6.4446 | 58.4893 | 64.1561 | -1150.5677
2025-10-09 08:00 | -2985.61 | 6.4446 | 59.0945 | 64.1561 | -874.9959
2025-10-10 09:00 | -1755.41 | 5.0361 | 59.6502 | 64.1561 | -514.4599
2025-10-11 10:00 | 0 | 1 | 61.2047 | 64.1561 | 0
2025-10-12 11:00 | 2801.04 | 1 | 80.0402 | 64.1561 | 820.9038
2025-10-13 12:00 | 3500.29 | 1.1983 | 73.4198 | 64.1561 | 1025.8337
2025-10-14 13:00 | 4060.82 | 1.3836 | 73.8597 | 64.1561 | 1190.1089
2025-10-15 14:00 | 4501.81 | 1.5403 | 74.1177 | 64.1561 | 1319.3503
2025-10-16 15:00 | 4631.46 | 1.5823 | 74.4175 | 64.1561 | 1357.3469
2025-10-17 16:00 | 5213.1 | 1.7804 | 74.6476 | 64.1561 | 1527.8088
2025-10-18 17:00 | 4858.86 | 1.669 | 74.7992 | 64.1561 | 1423.9913
2025-10-19 18:00 | 3863.03 | 1.3054 | 75.1232 | 64.1561 | 1132.1423
2025-10-20 19:00 | 2896.84 | 1 | 80.0758 | 64.1561 | 848.98
2025-10-21 20:00 | 2831.64 | 1 | 62.8561 | 64.1561 | 829.8718
2025-10-22 21:00 | -512.463 | 1.976 | 62.5396 | 64.1561 | -150.1881
2025-10-23 22:00 | -1173.71 | 3.6633 | 61.9492 | 64.1561 | -343.9804
2025-10-24 23:00 | -2223.42 | 6.4446 | 61.5739 | 64.1561 | -651.6201
2025-10-26 | -2904.53 | 6.4446 | 60.9112 | 64.1561 | -851.2337
2025-10-27 01:00 | -3216.99 | 6.4446 | 60.4806 | 64.1561 | -942.8067
2025-10-28 02:00 | -3594.25 | 6.4446 | 60.0371 | 64.1561 | -1053.3707
2025-10-29 03:00 | -3802.42 | 6.4446 | 59.7515 | 64.1561 | -1114.3793
2025-10-30 04:00 | -3819.62 | 6.4446 | 59.593 | 64.1561 | -1119.4201
2025-10-31 05:00 | -3699.72 | 6.4446 | 59.5605 | 64.1561 | -1084.2809
2025-11-01 06:00 | -3343.14 | 6.4446 | 59.7118 | 64.1561 | -979.7776
2025-11-02 07:00 | -2927.03 | 6.4446 | 59.9431 | 64.1561 | -857.8278
2025-11-03 08:00 | -1875.8 | 5.3321 | 60.3463 | 64.1561 | -549.7427
2025-11-04 09:00 | -1218.82 | 3.5429 | 60.4968 | 64.1561 | -357.2009
2025-11-05 10:00 | 0 | 1 | 61.9723 | 64.1561 | 0
2025-11-06 11:00 | 2986.77 | 1 | 61.4548 | 64.1561 | 875.3359
2025-11-07 12:00 | 2974.29 | 1 | 74.9885 | 64.1561 | 871.6784
2025-11-08 13:00 | 3132.39 | 1.0123 | 74.9748 | 64.1561 | 918.0129
2025-11-09 14:00 | 3194.92 | 1 | 75.5972 | 64.1561 | 936.3386
2025-11-10 15:00 | 3273.04 | 1 | 77.139 | 64.1561 | 959.2333
2025-11-11 16:00 | 3721.36 | 1.1866 | 75.5799 | 64.1561 | 1090.623
2025-11-12 17:00 | 3373.25 | 1.0529 | 75.9652 | 64.1561 | 988.602
2025-11-13 18:00 | 3355.61 | 1.0356 | 76.1645 | 64.1561 | 983.4322
2025-11-14 19:00 | 3159.72 | 1 | 84.4721 | 64.1561 | 926.0225
2025-11-15 20:00 | 3119.54 | 1 | 62.855 | 64.1561 | 914.2469
2025-11-16 21:00 | 0 | 0 | 63.6716 | 64.1561 | 0
2025-11-17 22:00 | -406.098 | 1.5321 | 62.3354 | 64.1561 | -119.0156
2025-11-18 23:00 | -1125.41 | 3.5669 | 61.9326 | 64.1561 | -329.8251
2025-11-20 | -1478.06 | 4.378 | 61.6763 | 64.1561 | -433.1766
2025-11-21 01:00 | -1666.59 | 4.839 | 61.4908 | 64.1561 | -488.4293
2025-11-22 02:00 | -1789.98 | 5.1508 | 61.3388 | 64.1561 | -524.5914
2025-11-23 03:00 | -1820.21 | 5.2114 | 61.2573 | 64.1561 | -533.4509
2025-11-24 04:00 | -1734.12 | 4.9678 | 61.1949 | 64.1561 | -508.2204
2025-11-25 05:00 | -1580.94 | 4.5621 | 61.173 | 64.1561 | -463.3278
2025-11-26 06:00 | -1256.34 | 3.6909 | 61.183 | 64.1561 | -368.1969
2025-11-27 07:00 | -1089.23 | 3.3039 | 61.2392 | 64.1561 | -319.2218
2025-11-28 08:00 | -836.353 | 2.6344 | 61.2931 | 64.1561 | -245.1109
2025-11-29 09:00 | -847.658 | 2.7254 | 61.3599 | 64.1561 | -248.424
2025-11-30 10:00 | -471.806 | 1.674 | 61.4881 | 64.1561 | -138.2727
2025-12-01 11:00 | 1878.51 | 1 | 62.1772 | 64.1561 | 550.5369
2025-12-02 12:00 | 3001.37 | 1 | 62.1835 | 64.1561 | 879.6147
2025-12-03 13:00 | 2988.2 | 1 | 77.0252 | 64.1561 | 875.755
2025-12-04 14:00 | 3096.8 | 1 | 77.5007 | 64.1561 | 907.5825
2025-12-05 15:00 | 3561.58 | 1.1444 | 75.615 | 64.1561 | 1043.7961
2025-12-06 16:00 | 5257.58 | 1.6395 | 76.1464 | 64.1561 | 1540.8446
2025-12-07 17:00 | 5461.41 | 1.7686 | 75.966 | 64.1561 | 1600.5813
2025-12-08 18:00 | 5565.15 | 1.764 | 76.4235 | 64.1561 | 1630.9845
2025-12-09 19:00 | 4488.95 | 1.3959 | 76.8196 | 64.1561 | 1315.5814
2025-12-10 20:00 | 3481.38 | 1.1131 | 76.4963 | 64.1561 | 1020.2918
2025-12-11 21:00 | 3038.68 | 1 | 63.5054 | 64.1561 | 890.5492
2025-12-12 22:00 | 2957.94 | 1 | 63.4959 | 64.1561 | 866.8866
2025-12-13 23:00 | -550.704 | 2.085 | 63.1527 | 64.1561 | -161.3954
2025-12-15 | -962.656 | 3.05 | 62.5494 | 64.1561 | -282.1266
2025-12-16 01:00 | -1297.69 | 3.8973 | 62.2251 | 64.1561 | -380.3154
2025-12-17 02:00 | -1381.65 | 4.0604 | 62.0419 | 64.1561 | -404.9216
2025-12-18 03:00 | -1372.12 | 4.0256 | 61.9082 | 64.1561 | -402.1287
2025-12-19 04:00 | -1251.09 | 3.6991 | 61.7871 | 64.1561 | -366.6583
2025-12-20 05:00 | -1135.93 | 3.4116 | 61.7563 | 64.1561 | -332.9082
2025-12-21 06:00 | -715.226 | 2.2748 | 61.7882 | 64.1561 | -209.612
2025-12-22 07:00 | -512.177 | 1.8175 | 61.928 | 64.1561 | -150.1043
2025-12-23 08:00 | 0 | 1 | 63.0507 | 64.1561 | 0
2025-12-24 09:00 | -109.801 | 0.8693 | 62.6105 | 64.1561 | -32.1795
2025-12-25 10:00 | 2187.17 | 1 | 62.5901 | 64.1561 | 640.9963
2025-12-26 11:00 | 2745.39 | 1 | 62.724 | 64.1561 | 804.5944
2025-12-27 12:00 | 3478.58 | 1.1379 | 75.5797 | 64.1561 | 1019.4712
2025-12-28 13:00 | 4275.26 | 1.3886 | 75.8325 | 64.1561 | 1252.955
2025-12-29 14:00 | 5844.51 | 1.9548 | 75.7095 | 64.1561 | 1712.8568
2025-12-30 15:00 | 7097.8 | 2.3403 | 76.2245 | 64.1561 | 2080.1598
2025-12-31 16:00 | 8133.98 | 2.6948 | 76.5052 | 64.1561 | 2383.8342
2026-01-01 17:00 | 8199.92 | 2.6596 | 77.1002 | 64.1561 | 2403.1593
2026-01-02 18:00 | 7533.45 | 2.3892 | 77.6226 | 64.1561 | 2207.8363
2026-01-03 19:00 | 5931.3 | 1.8359 | 78.0622 | 64.1561 | 1738.2924
2026-01-04 20:00 | 4929.34 | 1.5018 | 78.2161 | 64.1561 | 1444.6469
2026-01-05 21:00 | 3127.92 | 1 | 81.7011 | 64.1561 | 916.7029
2026-01-06 22:00 | 3073.09 | 1 | 64.3364 | 64.1561 | 900.6338
2026-01-07 23:00 | 0 | 0 | 64.9651 | 64.1561 | 0
2026-01-09 | -513.029 | 1.8524 | 63.4842 | 64.1561 | -150.354
2026-01-10 01:00 | -767.905 | 2.5221 | 63.0963 | 64.1561 | -225.0507
2026-01-11 02:00 | -1025.71 | 3.1728 | 62.8317 | 64.1561 | -300.6059
2026-01-12 03:00 | -1190.68 | 3.5738 | 62.6221 | 64.1561 | -348.9539
2026-01-13 04:00 | -1068.73 | 3.2102 | 62.4428 | 64.1561 | -313.2138
2026-01-14 05:00 | -912.648 | 2.8178 | 62.3838 | 64.1561 | -267.4707
2026-01-15 06:00 | -460.709 | 1.6168 | 62.4705 | 64.1561 | -135.0205
2026-01-16 07:00 | 0 | 0 | 63.5823 | 64.1561 | 0
2026-01-17 08:00 | 1951.56 | 1 | 63.1482 | 64.1561 | 571.9458
2026-01-18 09:00 | 2714.73 | 1 | 63.2032 | 64.1561 | 795.6088
2026-01-19 10:00 | 3120.11 | 1.0274 | 75.9606 | 64.1561 | 914.414
2026-01-20 11:00 | 5690.29 | 1.908 | 75.8793 | 64.1561 | 1667.6594
2026-01-21 12:00 | 7480.13 | 2.5778 | 75.9682 | 64.1561 | 2192.2097
2026-01-22 13:00 | 8560.32 | 2.9352 | 76.4919 | 64.1561 | 2508.7821
2026-01-23 14:00 | 8685.43 | 2.9101 | 77.1486 | 64.1561 | 2545.4483
2026-01-24 15:00 | 8856.28 | 2.8916 | 77.7351 | 64.1561 | 2595.5195
2026-01-25 16:00 | 9970.8 | 3.166 | 78.3152 | 64.1561 | 2922.153
2026-01-26 17:00 | 9455.34 | 2.9892 | 78.6803 | 64.1561 | 2771.0866
2026-01-27 18:00 | 8274.27 | 2.6305 | 78.7756 | 64.1561 | 2424.9492
2026-01-28 19:00 | 6789.34 | 2.0929 | 79.1708 | 64.1561 | 1989.7591
2026-01-29 20:00 | 5700.64 | 1.7819 | 78.893 | 64.1561 | 1670.6927
2026-01-30 21:00 | 3477.52 | 1.0759 | 78.9085 | 64.1561 | 1019.1605
2026-01-31 22:00 | 3039.71 | 1 | 83.2371 | 64.1561 | 890.8511
2026-02-01 23:00 | 0 | 0 | 65.7611 | 64.1561 | 0
2026-02-03 | -567.649 | 1.9571 | 64.1653 | 64.1561 | -166.3615
2026-02-04 01:00 | -948.289 | 2.9798 | 63.7094 | 64.1561 | -277.9161
2026-02-05 02:00 | -1264.94 | 3.7596 | 63.3847 | 64.1561 | -370.7173
2026-02-06 03:00 | -1502.2 | 4.3476 | 63.1356 | 64.1561 | -440.2514
2026-02-07 04:00 | -1778.7 | 5.0652 | 62.8956 | 64.1561 | -521.2855
2026-02-08 05:00 | -1862.94 | 5.2424 | 62.711 | 64.1561 | -545.9738
2026-02-09 06:00 | -1796.55 | 5.0518 | 62.5697 | 64.1561 | -526.5168
2026-02-10 07:00 | -866.212 | 2.5162 | 62.5091 | 64.1561 | -253.8617
2026-02-11 08:00 | 196.133 | 1 | 63.8191 | 64.1561 | 57.4809
2026-02-12 09:00 | -322.259 | 1.4509 | 63.0974 | 64.1561 | -94.4448
2026-02-13 10:00 | 0 | 1 | 63.9342 | 64.1561 | 0
2026-02-14 11:00 | -637.357 | 2.2665 | 62.8393 | 64.1561 | -186.7909
2026-02-15 12:00 | -1110.28 | 3.436 | 62.6034 | 64.1561 | -325.3909
2026-02-16 13:00 | -714.492 | 2.2517 | 62.4974 | 64.1561 | -209.3969
2026-02-17 14:00 | -486.229 | 1.7357 | 62.5777 | 64.1561 | -142.4997
2026-02-18 15:00 | 2321.44 | 1 | 63.0881 | 64.1561 | 680.3469
2026-02-19 16:00 | 2911.65 | 1 | 63.1967 | 64.1561 | 853.3204
2026-02-20 17:00 | 2839.02 | 1.0426 | 74.7628 | 64.1561 | 832.0346
2026-02-21 18:00 | 2860.04 | 1 | 63.4911 | 64.1561 | 838.195
2026-02-22 19:00 | 0 | 0 | 64.253 | 64.1561 | 0
2026-02-23 20:00 | -568.841 | 1.9811 | 62.8738 | 64.1561 | -166.7108
2026-02-24 21:00 | -973.92 | 3.0892 | 62.5536 | 64.1561 | -285.4278
2026-02-25 22:00 | -1392.25 | 4.1499 | 62.3163 | 64.1561 | -408.0282
2026-02-26 23:00 | -1681.04 | 4.861 | 62.1365 | 64.1561 | -492.6642
2026-02-28 | -3138.74 | 6.4446 | 61.4534 | 64.1561 | -919.8739
2026-03-01 01:00 | -3475.6 | 6.4446 | 61.0292 | 64.1561 | -1018.5978
2026-03-02 02:00 | -3667.68 | 6.4446 | 60.7432 | 64.1561 | -1074.8909
2026-03-03 03:00 | -3751.83 | 6.4446 | 60.5414 | 64.1561 | -1099.5528
2026-03-04 04:00 | -3673.76 | 6.4446 | 60.4507 | 64.1561 | -1076.6728
2026-03-05 05:00 | -3355.13 | 6.4446 | 60.5308 | 64.1561 | -983.2915
2026-03-06 06:00 | -2535.92 | 6.4446 | 60.9756 | 64.1561 | -743.2048
2026-03-07 07:00 | -2365.85 | 6.4446 | 61.1297 | 64.1561 | -693.3622
2026-03-08 08:00 | -2966.18 | 6.4446 | 60.7855 | 64.1561 | -869.3015
2026-03-09 09:00 | -2907.23 | 6.4446 | 60.747 | 64.1561 | -852.025
2026-03-10 10:00 | -2636.12 | 6.4446 | 60.8666 | 64.1561 | -772.5705
2026-03-11 11:00 | -1724.3 | 4.8427 | 61.0627 | 64.1561 | -505.3424
2026-03-12 12:00 | -798.995 | 2.3881 | 61.2184 | 64.1561 | -234.1623
2026-03-13 13:00 | -500.421 | 1.7826 | 61.5532 | 64.1561 | -146.6589
2026-03-14 14:00 | 2026.39 | 1 | 62.2727 | 64.1561 | 593.8763
2026-03-15 15:00 | 1193.03 | 1 | 62.8016 | 64.1561 | 349.6426
2026-03-16 16:00 | 3169.9 | 1 | 77.2335 | 64.1561 | 929.006
2026-03-17 17:00 | 3064.81 | 1 | 62.7112 | 64.1561 | 898.2071
2026-03-18 18:00 | 3020.52 | 1 | 62.89 | 64.1561 | 885.227
2026-03-19 19:00 | 0 | 0 | 63.7282 | 64.1561 | 0
2026-03-20 20:00 | -397.316 | 1.5213 | 62.448 | 64.1561 | -116.4418
2026-03-21 21:00 | -664.618 | 2.2945 | 62.2041 | 64.1561 | -194.7803
2026-03-22 22:00 | -977.353 | 3.0918 | 62.0073 | 64.1561 | -286.4339
2026-03-23 23:00 | -1996.67 | 5.8583 | 61.8144 | 64.1561 | -585.1662
2026-03-25 | -2356.32 | 6.4446 | 61.5279 | 64.1561 | -690.5692
2026-03-26 01:00 | -2429.43 | 6.4446 | 61.3677 | 64.1561 | -711.9956
2026-03-27 02:00 | -2334.76 | 6.4446 | 61.3331 | 64.1561 | -684.2506
2026-03-28 03:00 | -2389.74 | 6.4446 | 61.2465 | 64.1561 | -700.3637
2026-03-29 04:00 | -2291.65 | 6.4227 | 61.2269 | 64.1561 | -671.6163
2026-03-30 05:00 | -1902.49 | 5.3264 | 61.1802 | 64.1561 | -557.5648
2026-03-31 06:00 | -1893.83 | 5.4051 | 61.2067 | 64.1561 | -555.0268
2026-04-01 07:00 | -1793.48 | 5.1151 | 61.2108 | 64.1561 | -525.6171
2026-04-02 08:00 | -2006.73 | 5.7421 | 61.2214 | 64.1561 | -588.1145
2026-04-03 09:00 | -1383.93 | 3.9354 | 61.1917 | 64.1561 | -405.5898
2026-04-04 10:00 | 88.9528 | 1 | 62.6031 | 64.1561 | 26.0695
2026-04-05 11:00 | 2370.63 | 1.1217 | 71.1119 | 64.1561 | 694.7631
2026-04-06 12:00 | 2773.09 | 1 | 79.0266 | 64.1561 | 812.7125
2026-04-07 13:00 | 3726.73 | 1.2412 | 75.1836 | 64.1561 | 1092.1967
2026-04-08 14:00 | 4277.48 | 1.3863 | 75.7837 | 64.1561 | 1253.6056
2026-04-09 15:00 | 5592.83 | 1.8647 | 75.7012 | 64.1561 | 1639.0967
2026-04-10 16:00 | 6498.63 | 2.149 | 76.1111 | 64.1561 | 1904.5604
2026-04-11 17:00 | 6373.45 | 2.0875 | 76.5174 | 64.1561 | 1867.8738
2026-04-12 18:00 | 5300.01 | 1.6594 | 77.2629 | 64.1561 | 1553.2796
2026-04-13 19:00 | 4025.81 | 1.257 | 77.3561 | 64.1561 | 1179.8484
2026-04-14 20:00 | 3116.58 | 1 | 64.0476 | 64.1561 | 913.3794
2026-04-15 21:00 | 3279.54 | 1 | 63.9373 | 64.1561 | 961.1383
2026-04-16 22:00 | 0 | 0 | 64.7121 | 64.1561 | 0
2026-04-17 23:00 | -349.658 | 1.4173 | 63.3728 | 64.1561 | -102.4746
2026-04-19 | -477.519 | 1.7758 | 63.0491 | 64.1561 | -139.947
2026-04-20 01:00 | -519.977 | 1.8632 | 62.8856 | 64.1561 | -152.3902
2026-04-21 02:00 | -567.773 | 1.9878 | 62.7604 | 64.1561 | -166.3978
2026-04-22 03:00 | -441.806 | 1.6363 | 62.7074 | 64.1561 | -129.4806
2026-04-23 04:00 | -516.671 | 1.8715 | 62.6406 | 64.1561 | -151.4213
2026-04-24 05:00 | -481.259 | 1.7557 | 62.597 | 64.1561 | -141.0431
2026-04-25 06:00 | -589.584 | 2.0621 | 62.5135 | 64.1561 | -172.79
2026-04-26 07:00 | -815.194 | 2.654 | 62.3923 | 64.1561 | -238.9098
2026-04-27 08:00 | -1166.15 | 3.5688 | 62.2647 | 64.1561 | -341.7648
2026-04-28 09:00 | -1025.04 | 3.1014 | 62.1628 | 64.1561 | -300.4096
2026-04-29 10:00 | -547.923 | 1.8329 | 62.2606 | 64.1561 | -160.5804
2026-04-30 11:00 | -197.542 | 0.98876 | 62.6661 | 64.1561 | -57.8938
2026-05-01 12:00 | 1961.47 | 1 | 63.0102 | 64.1561 | 574.8501
2026-05-02 13:00 | 2812.22 | 1 | 63.0473 | 64.1561 | 824.1803
2026-05-03 14:00 | 2948.26 | 1 | 63.2376 | 64.1561 | 864.0497
2026-05-04 15:00 | 3043.88 | 1 | 76.1961 | 64.1561 | 892.0732
2026-05-05 16:00 | 3629.58 | 1.1463 | 76.5404 | 64.1561 | 1063.7249
2026-05-06 17:00 | 4097.22 | 1.284 | 76.7747 | 64.1561 | 1200.7766
2026-05-07 18:00 | 3147.99 | 1 | 83.008 | 64.1561 | 922.5848
2026-05-08 19:00 | 3021.56 | 1 | 63.6893 | 64.1561 | 885.5318
2026-05-09 20:00 | -502.661 | 1.9413 | 63.4116 | 64.1561 | -147.3154
2026-05-10 21:00 | -985.923 | 3.1152 | 62.8316 | 64.1561 | -288.9455
2026-05-11 22:00 | -1948.02 | 5.6718 | 62.4905 | 64.1561 | -570.9083
2026-05-12 23:00 | -2256.26 | 6.3128 | 62.2094 | 64.1561 | -661.2445
2026-05-14 | -2435.41 | 6.4446 | 61.9272 | 64.1561 | -713.7482
2026-05-15 01:00 | -2446.9 | 6.4446 | 61.7353 | 64.1561 | -717.1156
2026-05-16 02:00 | -2337.28 | 6.4446 | 61.6994 | 64.1561 | -684.9892
2026-05-17 03:00 | -2021.12 | 5.6266 | 61.6363 | 64.1561 | -592.3318
2026-05-18 04:00 | -1907.19 | 5.3853 | 61.6244 | 64.1561 | -558.9422
2026-05-19 05:00 | -1458.69 | 4.1574 | 61.5997 | 64.1561 | -427.4998
2026-05-20 06:00 | -1195.23 | 3.5373 | 61.663 | 64.1561 | -350.2873
2026-05-21 07:00 | -829.672 | 2.5801 | 61.7453 | 64.1561 | -243.1529
2026-05-22 08:00 | -635.961 | 2.1303 | 61.9018 | 64.1561 | -186.3818
2026-05-23 09:00 | 0 | 1 | 63.1332 | 64.1561 | 0
2026-05-24 10:00 | 1971.07 | 1 | 75.7312 | 64.1561 | 577.6636
2026-05-25 11:00 | 2630 | 1 | 76.2534 | 64.1561 | 770.7769
2026-05-26 12:00 | 3162.72 | 1.0544 | 75.5007 | 64.1561 | 926.9017
2026-05-27 13:00 | 5206.11 | 1.6877 | 76.0245 | 64.1561 | 1525.7602
2026-05-28 14:00 | 5048.96 | 1.5816 | 76.8206 | 64.1561 | 1479.7041
2026-05-29 15:00 | 6492.72 | 2.275 | 75.7149 | 64.1561 | 1902.8284
2026-05-30 16:00 | 6955.52 | 2.2247 | 77.075 | 64.1561 | 2038.4617
2026-05-31 17:00 | 7016.11 | 2.1129 | 78.0949 | 64.1561 | 2056.2189
2026-06-01 18:00 | 5901.63 | 1.7082 | 78.8226 | 64.1561 | 1729.597
2026-06-02 19:00 | 5009.49 | 1.4532 | 78.8176 | 64.1561 | 1468.1366
2026-06-03 20:00 | 3391.26 | 1 | 64.5253 | 64.1561 | 993.8802
2026-06-04 21:00 | 2998.04 | 1 | 64.4804 | 64.1561 | 878.6388
2026-06-05 22:00 | -738.9 | 2.5705 | 63.9669 | 64.1561 | -216.5502
2026-06-06 23:00 | -1332.63 | 3.9833 | 63.3172 | 64.1561 | -390.5553
2026-06-08 | -1757.97 | 5.0394 | 62.9363 | 64.1561 | -515.2101
2026-06-09 01:00 | -2217.99 | 6.2292 | 62.6685 | 64.1561 | -650.0287
2026-06-10 02:00 | -2459.23 | 6.4446 | 62.3452 | 64.1561 | -720.7292
2026-06-11 03:00 | -2541.02 | 6.4446 | 62.0706 | 64.1561 | -744.6995
2026-06-12 04:00 | -2669.36 | 6.4446 | 61.8491 | 64.1561 | -782.3122
2026-06-13 05:00 | -2432.56 | 6.4446 | 61.8535 | 64.1561 | -712.913
2026-06-14 06:00 | -2665.24 | 6.4446 | 61.6249 | 64.1561 | -781.1047
2026-06-15 07:00 | -2716.24 | 6.4446 | 61.4877 | 64.1561 | -796.0514
2026-06-16 08:00 | -2988.1 | 6.4446 | 61.2349 | 64.1561 | -875.7257
2026-06-17 09:00 | -2775.03 | 6.4446 | 61.2561 | 64.1561 | -813.281
2026-06-18 10:00 | -2785.3 | 6.4446 | 61.2067 | 64.1561 | -816.2909
2026-06-19 11:00 | -1435.04 | 4.0129 | 61.4428 | 64.1561 | -420.5687
2026-06-20 12:00 | -944.315 | 2.8559 | 61.6413 | 64.1561 | -276.7514
2026-06-21 13:00 | -569.945 | 1.9246 | 61.8546 | 64.1561 | -167.0344
2026-06-22 14:00 | -131.829 | 0.80422 | 62.4367 | 64.1561 | -38.6353
2026-06-23 15:00 | 2729.72 | 1 | 62.5035 | 64.1561 | 800.002
2026-06-24 16:00 | 2821.64 | 1 | 62.8434 | 64.1561 | 826.9411
2026-06-25 17:00 | 130.113 | 1 | 63.6788 | 64.1561 | 38.1324
2026-06-26 18:00 | -973.609 | 3.1986 | 62.3193 | 64.1561 | -285.3366
2026-06-27 19:00 | -1996.5 | 5.8377 | 61.9774 | 64.1561 | -585.1164
2026-06-28 20:00 | -3696.19 | 6.4446 | 60.9 | 64.1561 | -1083.2464
2026-06-29 21:00 | -4412.11 | 6.4446 | 60.1269 | 64.1561 | -1293.0618
2026-06-30 22:00 | -5836.83 | 6.4446 | 58.9709 | 64.1561 | -1710.606
2026-07-01 23:00 | -6313.95 | 6.4446 | 58.3554 | 64.1561 | -1850.4361
2026-07-03 | -6631.47 | 6.4446 | 57.8909 | 64.1561 | -1943.492
2026-07-04 01:00 | -6924.49 | 6.4446 | 57.4873 | 64.1561 | -2029.3677
2026-07-05 02:00 | -7116.66 | 6.4446 | 57.1695 | 64.1561 | -2085.6872
2026-07-06 03:00 | -6992.68 | 6.4446 | 57.0313 | 64.1561 | -2049.3522
2026-07-07 04:00 | -7095.21 | 6.4446 | 56.8137 | 64.1561 | -2079.4008
2026-07-08 05:00 | -6636.07 | 6.4446 | 56.9575 | 64.1561 | -1944.8401
2026-07-09 06:00 | -6513.64 | 6.4446 | 56.9673 | 64.1561 | -1908.9594
2026-07-10 07:00 | -5600.79 | 6.4446 | 57.4671 | 64.1561 | -1641.4295
2026-07-11 08:00 | -5015.05 | 6.4446 | 57.8742 | 64.1561 | -1469.7661
2026-07-12 09:00 | -3245.19 | 6.4446 | 59.0222 | 64.1561 | -951.0713
2026-07-13 10:00 | -1842.15 | 5.2829 | 59.8552 | 64.1561 | -539.8809
2026-07-14 11:00 | -636.359 | 1.9175 | 60.1893 | 64.1561 | -186.4984
2026-07-15 12:00 | 1093.37 | 1 | 61.5196 | 64.1561 | 320.4351
2026-07-16 13:00 | 2842.64 | 1 | 61.4675 | 64.1561 | 833.0955
2026-07-17 14:00 | 2853.88 | 1 | 61.8991 | 64.1561 | 836.3897
2026-07-18 15:00 | 2859.05 | 1 | 74.7096 | 64.1561 | 837.9048
2026-07-19 16:00 | 2907.02 | 1.0091 | 74.2682 | 64.1561 | 851.9635
2026-07-20 17:00 | 2879.86 | 1 | 77.7318 | 64.1561 | 844.0037
2026-07-21 18:00 | 2634.59 | 1 | 62.6552 | 64.1561 | 772.1221
2026-07-22 19:00 | -405.999 | 1.7107 | 62.4258 | 64.1561 | -118.9866
2026-07-23 20:00 | -1829.56 | 5.5103 | 61.8013 | 64.1561 | -536.1911
2026-07-24 21:00 | -3099.57 | 6.4446 | 60.9407 | 64.1561 | -908.3943
2026-07-25 22:00 | -4398.73 | 6.4446 | 59.8882 | 64.1561 | -1289.1405
2026-07-26 23:00 | -5346.4 | 6.4446 | 58.9968 | 64.1561 | -1566.8752
2026-07-28 | -5993.92 | 6.4446 | 58.2688 | 64.1561 | -1756.6445
2026-07-29 01:00 | -6217.93 | 6.4446 | 57.8506 | 64.1561 | -1822.2954
2026-07-30 02:00 | -6200.77 | 6.4446 | 57.6405 | 64.1561 | -1817.2663
2026-07-31 03:00 | -6489.64 | 6.4446 | 57.2995 | 64.1561 | -1901.9257
2026-08-01 04:00 | -6611.34 | 6.4446 | 57.0576 | 64.1561 | -1937.5925
2026-08-02 05:00 | -6948.8 | 6.4446 | 56.6994 | 64.1561 | -2036.4923
2026-08-03 06:00 | -6086.33 | 6.4446 | 57.0604 | 64.1561 | -1783.7272
2026-08-04 07:00 | -4684.58 | 6.4446 | 57.897 | 64.1561 | -1372.9149
2026-08-05 08:00 | -3912.09 | 6.4446 | 58.4901 | 64.1561 | -1146.5204
2026-08-06 09:00 | -2636.3 | 6.4446 | 59.3933 | 64.1561 | -772.6233
2026-08-07 10:00 | -1119.88 | 3.1929 | 59.8221 | 64.1561 | -328.2044
2026-08-08 11:00 | 817.709 | 1 | 61.3016 | 64.1561 | 239.6469
2026-08-09 12:00 | 3057.01 | 1 | 61.1555 | 64.1561 | 895.9212
2026-08-10 13:00 | 3099.88 | 1 | 76.4127 | 64.1561 | 908.4851
2026-08-11 14:00 | 3875.01 | 1.2858 | 74.4369 | 64.1561 | 1135.6533
2026-08-12 15:00 | 4530.49 | 1.423 | 75.3957 | 64.1561 | 1327.7556
2026-08-13 16:00 | 6744.32 | 2.2254 | 75.0869 | 64.1561 | 1976.5651
2026-08-14 17:00 | 5641.26 | 1.8242 | 75.803 | 64.1561 | 1653.2901
2026-08-15 18:00 | 4053.36 | 1.296 | 76.1198 | 64.1561 | 1187.9226
2026-08-16 19:00 | 3100.71 | 1 | 63.1324 | 64.1561 | 908.7284
2026-08-17 20:00 | 2993.69 | 1 | 63.1428 | 64.1561 | 877.3639
2026-08-18 21:00 | -130.038 | 0.94984 | 63.3619 | 64.1561 | -38.1104
2026-08-19 22:00 | -721.988 | 2.489 | 62.4366 | 64.1561 | -211.5938
2026-08-20 23:00 | -2332.49 | 6.4446 | 61.9277 | 64.1561 | -683.5853
2026-08-22 | -3038.06 | 6.4446 | 61.2158 | 64.1561 | -890.3675
2026-08-23 01:00 | -3520.25 | 6.4446 | 60.672 | 64.1561 | -1031.6834
2026-08-24 02:00 | -3447.74 | 6.4446 | 60.4847 | 64.1561 | -1010.4329
2026-08-25 03:00 | -3609.75 | 6.4446 | 60.2606 | 64.1561 | -1057.9133
2026-08-26 04:00 | -3820.98 | 6.4446 | 59.9894 | 64.1561 | -1119.8187
2026-08-27 05:00 | -4260.88 | 6.4446 | 59.602 | 64.1561 | -1248.7407
2026-08-28 06:00 | -3461.97 | 6.4446 | 59.955 | 64.1561 | -1014.6033
2026-08-29 07:00 | -2177.03 | 6.1942 | 60.6761 | 64.1561 | -638.0245
2026-08-30 08:00 | -1835.47 | 5.1856 | 60.7747 | 64.1561 | -537.9232
2026-08-31 09:00 | -503.327 | 1.5395 | 60.9632 | 64.1561 | -147.5106
2026-09-01 10:00 | 2387.08 | 1 | 78.2607 | 64.1561 | 699.5841
2026-09-02 11:00 | 3818.99 | 1.2957 | 74.3985 | 64.1561 | 1119.2355
2026-09-03 12:00 | 5073.82 | 1.7081 | 74.9056 | 64.1561 | 1486.9899
2026-09-04 13:00 | 5701.42 | 1.9606 | 75.0362 | 64.1561 | 1670.9213
2026-09-05 14:00 | 6208.87 | 2.0899 | 75.6173 | 64.1561 | 1819.6402
2026-09-06 15:00 | 6657.74 | 2.1728 | 76.2785 | 64.1561 | 1951.191
2026-09-07 16:00 | 8820.19 | 2.896 | 76.4423 | 64.1561 | 2584.9425
2026-09-08 17:00 | 7370.19 | 2.4491 | 76.7397 | 64.1561 | 2159.9895
2026-09-09 18:00 | 5462.66 | 1.8153 | 76.8781 | 64.1561 | 1600.9476
2026-09-10 19:00 | 3418.71 | 1.1833 | 76.3275 | 64.1561 | 1001.925
2026-09-11 20:00 | 2878.31 | 1 | 82.5589 | 64.1561 | 843.5494
2026-09-12 21:00 | 2802.79 | 1 | 64.0561 | 64.1561 | 821.4167
2026-09-13 22:00 | 0 | 0 | 64.6414 | 64.1561 | 0
2026-09-14 23:00 | -1502.99 | 4.5573 | 62.987 | 64.1561 | -440.4829
2026-09-16 | -2245.69 | 6.3625 | 62.529 | 64.1561 | -658.1468
2026-09-17 01:00 | -2783.71 | 6.4446 | 61.9548 | 64.1561 | -815.8249
2026-09-18 02:00 | -3021.66 | 6.4446 | 61.5673 | 64.1561 | -885.5611
2026-09-19 03:00 | -3355.94 | 6.4446 | 61.1399 | 64.1561 | -983.5289
2026-09-20 04:00 | -3581.19 | 6.4446 | 60.8014 | 64.1561 | -1049.5432
2026-09-21 05:00 | -3585.24 | 6.4446 | 60.639 | 64.1561 | -1050.7301
2026-09-22 06:00 | -3277.76 | 6.4446 | 60.7118 | 64.1561 | -960.6166
2026-09-23 07:00 | -2706.52 | 6.4446 | 61.0065 | 64.1561 | -793.2027
2026-09-24 08:00 | -2202.98 | 6.1843 | 61.2604 | 64.1561 | -645.6297
2026-09-25 09:00 | -872.764 | 2.4638 | 61.2879 | 64.1561 | -255.7819
2026-09-26 10:00 | 2457.34 | 1 | 62.2411 | 64.1561 | 720.1753
2026-09-27 11:00 | 2883.73 | 1 | 74.8934 | 64.1561 | 845.1378
2026-09-28 12:00 | 4690.7 | 1.5391 | 75.4871 | 64.1561 | 1374.7085
2026-09-29 13:00 | 6307.71 | 2.0066 | 76.2274 | 64.1561 | 1848.6073
2026-09-30 14:00 | 7443.18 | 2.3992 | 76.5069 | 64.1561 | 2181.3807
2026-10-01 15:00 | 8851.95 | 2.9272 | 76.6125 | 64.1561 | 2594.2505
2026-10-02 16:00 | 8956.16 | 2.9514 | 77.052 | 64.1561 | 2624.7914
2026-10-03 17:00 | 8293.03 | 2.7122 | 77.4601 | 64.1561 | 2430.4472
2026-10-04 18:00 | 5727.1 | 1.855 | 77.7554 | 64.1561 | 1678.4473
2026-10-05 19:00 | 3016.03 | 1 | 77.8071 | 64.1561 | 883.9111
2026-10-06 20:00 | 2728.36 | 1 | 64.6214 | 64.1561 | 799.6034
2026-10-07 21:00 | -513.531 | 1.9666 | 64.0889 | 64.1561 | -150.5011
2026-10-08 22:00 | -1619.78 | 4.8139 | 63.3384 | 64.1561 | -474.7107
2026-10-09 23:00 | -2227.55 | 6.2615 | 62.8634 | 64.1561 | -652.8305
2026-10-11 | -2638.28 | 6.4446 | 62.3671 | 64.1561 | -773.2035
2026-10-12 01:00 | -2971.1 | 6.4446 | 61.9325 | 64.1561 | -870.7435
2026-10-13 02:00 | -3114.14 | 6.4446 | 61.6079 | 64.1561 | -912.6643
2026-10-14 03:00 | -3321.68 | 6.4446 | 61.3058 | 64.1561 | -973.4883
2026-10-15 04:00 | -3276.63 | 6.4446 | 61.1714 | 64.1561 | -960.2855
2026-10-16 05:00 | -2984.39 | 6.4446 | 61.2244 | 64.1561 | -874.6384
2026-10-17 06:00 | -3069.53 | 6.4446 | 61.1143 | 64.1561 | -899.5904
2026-10-18 07:00 | -2056.49 | 5.766 | 61.5229 | 64.1561 | -602.6977
2026-10-19 08:00 | -1536.21 | 4.3375 | 61.5851 | 64.1561 | -450.2187
2026-10-20 09:00 | -311.057 | 1.0748 | 61.9261 | 64.1561 | -91.1618
2026-10-21 10:00 | 2839.7 | 1 | 81.0214 | 64.1561 | 832.2339
2026-10-22 11:00 | 4590.61 | 1.4529 | 76.0048 | 64.1561 | 1345.375
2026-10-23 12:00 | 6093.53 | 1.9711 | 76.1884 | 64.1561 | 1785.8374
2026-10-24 13:00 | 7401.99 | 2.3671 | 76.7368 | 64.1561 | 2169.3091
2026-10-25 14:00 | 8458.22 | 2.7499 | 76.9578 | 64.1561 | 2478.8596
2026-10-26 15:00 | 10070.3 | 3.2836 | 77.3289 | 64.1561 | 2951.3136
2026-10-27 16:00 | 10467.3 | 3.2967 | 78.1912 | 64.1561 | 3067.6628
2026-10-28 17:00 | 9559.29 | 3.0726 | 78.2924 | 64.1561 | 2801.5513
2026-10-29 18:00 | 6940.12 | 2.1929 | 78.6816 | 64.1561 | 2033.9484
2026-10-30 19:00 | 4906.75 | 1.5411 | 78.6551 | 64.1561 | 1438.0265
2026-10-31 20:00 | 3026.21 | 1 | 84.0381 | 64.1561 | 886.8946
2026-11-01 21:00 | 2821.31 | 1 | 65.0472 | 64.1561 | 826.8443
2026-11-02 22:00 | -960.933 | 3.1472 | 64.3551 | 64.1561 | -281.6217
2026-11-03 23:00 | -1586.03 | 4.602 | 63.6693 | 64.1561 | -464.8195
2026-11-05 | -2114.19 | 5.9391 | 63.2475 | 64.1561 | -619.6079
2026-11-06 01:00 | -2392.06 | 6.4446 | 62.9174 | 64.1561 | -701.0436
2026-11-07 02:00 | -2413.78 | 6.4446 | 62.6715 | 64.1561 | -707.4091
2026-11-08 03:00 | -2615.06 | 6.4446 | 62.3331 | 64.1561 | -766.3984
2026-11-09 04:00 | -2668.18 | 6.4446 | 62.1394 | 64.1561 | -781.9664
2026-11-10 05:00 | -2285.84 | 6.3377 | 62.2101 | 64.1561 | -669.9136
2026-11-11 06:00 | -1984.6 | 5.4968 | 62.1555 | 64.1561 | -581.6288
2026-11-12 07:00 | -1148.98 | 3.2625 | 62.1699 | 64.1561 | -336.7328
2026-11-13 08:00 | -624.65 | 2.0243 | 62.4054 | 64.1561 | -183.0668
2026-11-14 09:00 | 2396.89 | 1 | 63.1178 | 64.1561 | 702.4591
2026-11-15 10:00 | 3952.13 | 1.2952 | 76.0312 | 64.1561 | 1158.255
2026-11-16 11:00 | 6613.04 | 2.1584 | 76.4257 | 64.1561 | 1938.0907
2026-11-17 12:00 | 7981.57 | 2.6375 | 76.7837 | 64.1561 | 2339.1673
2026-11-18 13:00 | 8660.73 | 2.8524 | 77.2923 | 64.1561 | 2538.2094
2026-11-19 14:00 | 9844.76 | 3.1836 | 77.8965 | 64.1561 | 2885.2143
2026-11-20 15:00 | 11027.1 | 3.6376 | 78.0388 | 64.1561 | 3231.724
2026-11-21 16:00 | 11311.2 | 3.6532 | 78.7016 | 64.1561 | 3314.9855
2026-11-22 17:00 | 10554.2 | 3.4171 | 78.9785 | 64.1561 | 3093.1307
2026-11-23 18:00 | 8239.99 | 2.5938 | 79.4943 | 64.1561 | 2414.9027
2026-11-24 19:00 | 6180.82 | 1.9523 | 79.3816 | 64.1561 | 1811.4195
2026-11-25 20:00 | 3645.16 | 1.1602 | 79.1012 | 64.1561 | 1068.2909
2026-11-26 21:00 | 3102.72 | 1 | 65.7178 | 64.1561 | 909.3175
2026-11-27 22:00 | -320.12 | 1.3945 | 65.3245 | 64.1561 | -93.8179
2026-11-28 23:00 | -869.607 | 2.789 | 64.4698 | 64.1561 | -254.8567
2026-11-30 | -1272.82 | 3.7703 | 63.9871 | 64.1561 | -373.0267
2026-12-01 01:00 | -1687.75 | 4.8216 | 63.6708 | 64.1561 | -494.6307
2026-12-02 02:00 | -1865.96 | 5.2281 | 63.4007 | 64.1561 | -546.8589
2026-12-03 03:00 | -1785.15 | 4.9845 | 63.1635 | 64.1561 | -523.1758
2026-12-04 04:00 | -1753.17 | 4.9274 | 63.0328 | 64.1561 | -513.8034
2026-12-05 05:00 | -1346.17 | 3.824 | 62.927 | 64.1561 | -394.5235
2026-12-06 06:00 | -1093.9 | 3.2367 | 62.932 | 64.1561 | -320.5904
2026-12-07 07:00 | -496.454 | 1.6644 | 63.0643 | 64.1561 | -145.4963
2026-12-08 08:00 | -248.009 | 1.1314 | 63.4197 | 64.1561 | -72.6843
2026-12-09 09:00 | 2408.02 | 1 | 78.7306 | 64.1561 | 705.721
2026-12-10 10:00 | 4616.11 | 1.5324 | 76.3843 | 64.1561 | 1352.8483
2026-12-11 11:00 | 6422.44 | 2.1883 | 76.485 | 64.1561 | 1882.2314
2026-12-12 12:00 | 7970.06 | 2.7106 | 76.918 | 64.1561 | 2335.794
2026-12-13 13:00 | 9000.16 | 2.9753 | 77.6735 | 64.1561 | 2637.6865
2026-12-14 14:00 | 9792.67 | 3.2226 | 78.1327 | 64.1561 | 2869.9483
2026-12-15 15:00 | 11083 | 3.6454 | 78.4781 | 64.1561 | 3248.1067
2026-12-16 16:00 | 11374.1 | 3.6841 | 79.0367 | 64.1561 | 3333.4197
2026-12-17 17:00 | 10421 | 3.3147 | 79.5547 | 64.1561 | 3054.0936
2026-12-18 18:00 | 8522.88 | 2.6662 | 79.8899 | 64.1561 | 2497.8096
2026-12-19 19:00 | 6257.17 | 2.0044 | 79.5398 | 64.1561 | 1833.7955
2026-12-20 20:00 | 3437.94 | 1.0952 | 79.4126 | 64.1561 | 1007.5608
2026-12-21 21:00 | 3158.48 | 1 | 65.9742 | 64.1561 | 925.6591
2026-12-22 22:00 | 0 | 0 | 66.4941 | 64.1561 | 0
2026-12-23 23:00 | -543.029 | 1.6401 | 64.6992 | 64.1561 | -159.1461
2026-12-25 | -801.672 | 2.5906 | 64.4105 | 64.1561 | -234.9469
2026-12-26 01:00 | -1262.95 | 3.7577 | 64.0565 | 64.1561 | -370.1341
2026-12-27 02:00 | -1443.97 | 4.1554 | 63.7843 | 64.1561 | -423.1858
2026-12-28 03:00 | -1513.68 | 4.3206 | 63.5476 | 64.1561 | -443.6158
2026-12-29 04:00 | -1503.09 | 4.2849 | 63.3916 | 64.1561 | -440.5122
2026-12-30 05:00 | -1185.76 | 3.4304 | 63.2826 | 64.1561 | -347.512
2026-12-31 06:00 | -1220.17 | 3.6036 | 63.2405 | 64.1561 | -357.5965
2027-01-01 07:00 | -669.393 | 2.0945 | 63.2492 | 64.1561 | -196.1797
2027-01-02 08:00 | -201.669 | 0.96605 | 63.7015 | 64.1561 | -59.1033
2027-01-03 09:00 | 2371.54 | 1 | 78.1919 | 64.1561 | 695.0298
2027-01-04 10:00 | 4765.15 | 1.6001 | 76.4861 | 64.1561 | 1396.5276
2027-01-05 11:00 | 6997.86 | 2.4493 | 76.4253 | 64.1561 | 2050.8703
2027-01-06 12:00 | 8156.07 | 2.8347 | 76.9732 | 64.1561 | 2390.3082
2027-01-07 13:00 | 8161.44 | 2.7599 | 77.7003 | 64.1561 | 2391.882
2027-01-08 14:00 | 8896.29 | 2.9374 | 78.258 | 64.1561 | 2607.2452
2027-01-09 15:00 | 10598 | 3.4939 | 78.5416 | 64.1561 | 3105.9672
2027-01-10 16:00 | 10604.3 | 3.4089 | 79.2258 | 64.1561 | 3107.8135
2027-01-11 17:00 | 10090.2 | 3.1827 | 79.7034 | 64.1561 | 2957.1457
2027-01-12 18:00 | 7867.5 | 2.4709 | 79.8955 | 64.1561 | 2305.7366
2027-01-13 19:00 | 5828.69 | 1.8127 | 79.9425 | 64.1561 | 1708.2204
2027-01-14 20:00 | 3130.1 | 1 | 80.0297 | 64.1561 | 917.3418
2027-01-15 21:00 | 3068.83 | 1 | 66.0638 | 64.1561 | 899.3853
2027-01-16 22:00 | 0 | 0 | 66.5939 | 64.1561 | 0
2027-01-17 23:00 | -861.611 | 2.7353 | 64.8784 | 64.1561 | -252.5133
2027-01-19 | -1366.85 | 4.0091 | 64.3798 | 64.1561 | -400.5842
2027-01-20 01:00 | -1798.52 | 5.0777 | 64.0447 | 64.1561 | -527.0942
2027-01-21 02:00 | -2013.53 | 5.5815 | 63.7807 | 64.1561 | -590.1074
2027-01-22 03:00 | -2220.78 | 6.1192 | 63.5297 | 64.1561 | -650.8464
2027-01-23 04:00 | -2542.24 | 6.4446 | 63.2206 | 64.1561 | -745.057
2027-01-24 05:00 | -2924.8 | 6.4446 | 62.7999 | 64.1561 | -857.1743
2027-01-25 06:00 | -2144.97 | 5.8974 | 62.9708 | 64.1561 | -628.6287
2027-01-26 07:00 | -1102.66 | 3.0682 | 62.9422 | 64.1561 | -323.1577
2027-01-27 08:00 | -641.118 | 2.0678 | 63.2103 | 64.1561 | -187.8931
2027-01-28 09:00 | 2232.5 | 1 | 63.9349 | 64.1561 | 654.2812
2027-01-29 10:00 | 3238.23 | 1.0664 | 76.7011 | 64.1561 | 949.0315
2027-01-30 11:00 | 5629.5 | 1.8527 | 76.9635 | 64.1561 | 1649.8436
2027-01-31 12:00 | 6911.07 | 2.3234 | 77.1205 | 64.1561 | 2025.4347
2027-02-01 13:00 | 7885.2 | 2.62 | 77.6485 | 64.1561 | 2310.924
2027-02-02 14:00 | 8740.5 | 2.8307 | 78.313 | 64.1561 | 2561.5877
2027-02-03 15:00 | 8789.53 | 2.8903 | 78.4394 | 64.1561 | 2575.957
2027-02-04 16:00 | 10872.2 | 3.5266 | 78.8273 | 64.1561 | 3186.3273
2027-02-05 17:00 | 9607.27 | 3.0548 | 79.4774 | 64.1561 | 2815.6129
2027-02-06 18:00 | 7533.17 | 2.3748 | 79.736 | 64.1561 | 2207.7542
2027-02-07 19:00 | 5506.76 | 1.7392 | 79.6216 | 64.1561 | 1613.872
2027-02-08 20:00 | 3986.76 | 1.279 | 79.242 | 64.1561 | 1168.404
2027-02-09 21:00 | 3086.11 | 1 | 83.1884 | 64.1561 | 904.4496
2027-02-10 22:00 | 3091.04 | 1 | 65.8509 | 64.1561 | 905.8944
2027-02-11 23:00 | -840.359 | 2.7647 | 65.2697 | 64.1561 | -246.2849
2027-02-13 | -1438.31 | 4.1879 | 64.5919 | 64.1561 | -421.5271
2027-02-14 01:00 | -2078.47 | 5.8121 | 64.1645 | 64.1561 | -609.1394
2027-02-15 02:00 | -2175.62 | 5.9504 | 63.8504 | 64.1561 | -637.6113
2027-02-16 03:00 | -2721.21 | 6.4446 | 63.4014 | 64.1561 | -797.5079
2027-02-17 04:00 | -2948.14 | 6.4446 | 62.9778 | 64.1561 | -864.0145
2027-02-18 05:00 | -2980.64 | 6.4446 | 62.7626 | 64.1561 | -873.5394
2027-02-19 06:00 | -2107.88 | 5.7949 | 63.0018 | 64.1561 | -617.7586
2027-02-20 07:00 | -1026.26 | 2.8674 | 63.0062 | 64.1561 | -300.7671
2027-02-21 08:00 | -672.944 | 2.1704 | 63.2719 | 64.1561 | -197.2204
2027-02-22 09:00 | 2373.84 | 1 | 63.9597 | 64.1561 | 695.7038
2027-02-23 10:00 | 3174.02 | 1.0214 | 77.0365 | 64.1561 | 930.2134
2027-02-24 11:00 | 5641.65 | 1.807 | 77.336 | 64.1561 | 1653.4044
2027-02-25 12:00 | 7016.01 | 2.2839 | 77.5478 | 64.1561 | 2056.1896
2027-02-26 13:00 | 7631.42 | 2.5319 | 77.7288 | 64.1561 | 2236.5484
2027-02-27 14:00 | 8395.66 | 2.7051 | 78.4073 | 64.1561 | 2460.5251
2027-02-28 15:00 | 8803.81 | 2.8193 | 78.7696 | 64.1561 | 2580.142
2027-03-01 16:00 | 10708.3 | 3.4569 | 78.9231 | 64.1561 | 3138.2929
2027-03-02 17:00 | 9271.73 | 2.935 | 79.5629 | 64.1561 | 2717.2758
2027-03-03 18:00 | 7460.02 | 2.3143 | 79.9346 | 64.1561 | 2186.316
2027-03-04 19:00 | 5396.68 | 1.7217 | 79.5102 | 64.1561 | 1581.6108
2027-03-05 20:00 | 3753.39 | 1.2189 | 79.1093 | 64.1561 | 1100.01
2027-03-06 21:00 | 3087.44 | 1 | 80.6428 | 64.1561 | 904.8393
2027-03-07 22:00 | 3074.93 | 1 | 86.848 | 64.1561 | 901.173
2027-03-08 23:00 | 0 | 0 | 66.463 | 64.1561 | 0
2027-03-10 | -663.049 | 2.1187 | 64.8082 | 64.1561 | -194.3205
2027-03-11 01:00 | -836.029 | 2.6401 | 64.4748 | 64.1561 | -245.0159
2027-03-12 02:00 | -1124.46 | 3.3746 | 64.2165 | 64.1561 | -329.5467
2027-03-13 03:00 | -1198.84 | 3.5183 | 63.9993 | 64.1561 | -351.3453
2027-03-14 04:00 | -1316.82 | 3.8327 | 63.7949 | 64.1561 | -385.9218
2027-03-15 05:00 | -1178.09 | 3.4346 | 63.6746 | 64.1561 | -345.2641
2027-03-16 06:00 | -1178.3 | 3.4737 | 63.6138 | 64.1561 | -345.3256
2027-03-17 07:00 | -397.452 | 1.3651 | 63.7349 | 64.1561 | -116.4817
2027-03-18 08:00 | 736.35 | 1 | 64.7392 | 64.1561 | 215.8029
2027-03-19 09:00 | 2401.28 | 1 | 75.8966 | 64.1561 | 703.7457
2027-03-20 10:00 | 5134.66 | 1.7624 | 76.6352 | 64.1561 | 1504.8203
2027-03-21 11:00 | 7042.61 | 2.4296 | 76.9934 | 64.1561 | 2063.9852
2027-03-22 12:00 | 8616.82 | 2.8531 | 77.9218 | 64.1561 | 2525.3407
2027-03-23 13:00 | 9605.78 | 3.1627 | 78.4322 | 64.1561 | 2815.1762
2027-03-24 14:00 | 10085.8 | 3.2683 | 79.027 | 64.1561 | 2955.8562
2027-03-25 15:00 | 11549.5 | 3.6978 | 79.5011 | 64.1561 | 3384.8243
2027-03-26 16:00 | 11201.8 | 3.6268 | 79.7477 | 64.1561 | 3282.9235
2027-03-27 17:00 | 10487.7 | 3.3122 | 80.2878 | 64.1561 | 3073.6415
2027-03-28 18:00 | 8225.2 | 2.5386 | 80.6956 | 64.1561 | 2410.5682
2027-03-29 19:00 | 6489.63 | 2.0831 | 80.1063 | 64.1561 | 1901.9228
2027-03-30 20:00 | 4199.56 | 1.2981 | 80.4006 | 64.1561 | 1230.7695
2027-03-31 21:00 | 3128.69 | 1 | 82.9186 | 64.1561 | 916.9285
2027-04-01 22:00 | 89.382 | 1 | 67.0913 | 64.1561 | 26.1953
2027-04-02 23:00 | -387.549 | 1.5959 | 65.6412 | 64.1561 | -113.5794
2027-04-04 | -825.708 | 2.6404 | 65.0025 | 64.1561 | -241.9911
2027-04-05 01:00 | -1252.69 | 3.7004 | 64.6238 | 64.1561 | -367.1272
2027-04-06 02:00 | -1439.88 | 4.1221 | 64.3302 | 64.1561 | -421.9872
2027-04-07 03:00 | -1551.92 | 4.3985 | 64.0849 | 64.1561 | -454.8229
2027-04-08 04:00 | -1475.8 | 4.1764 | 63.9213 | 64.1561 | -432.5143
2027-04-09 05:00 | -1325.94 | 3.797 | 63.8103 | 64.1561 | -388.5947
2027-04-10 06:00 | -1061.56 | 3.1198 | 63.7617 | 64.1561 | -311.1125
2027-04-11 07:00 | -386.889 | 1.3659 | 63.939 | 64.1561 | -113.386
2027-04-12 08:00 | 58.1105 | 1 | 65.0702 | 64.1561 | 17.0305
2027-04-13 09:00 | 2430.17 | 1 | 76.248 | 64.1561 | 712.2125
2027-04-14 10:00 | 4927.21 | 1.6406 | 77.14 | 64.1561 | 1444.0227
2027-04-15 11:00 | 6933.6 | 2.3702 | 77.2462 | 64.1561 | 2032.0376
2027-04-16 12:00 | 8358.08 | 2.8249 | 77.8193 | 64.1561 | 2449.5114
2027-04-17 13:00 | 9381.15 | 3.1186 | 78.435 | 64.1561 | 2749.3437
2027-04-18 14:00 | 10211.6 | 3.3942 | 78.8382 | 64.1561 | 2992.7245
2027-04-19 15:00 | 11819.4 | 3.8687 | 79.3709 | 64.1561 | 3463.9242
2027-04-20 16:00 | 12092.4 | 3.8664 | 80.0708 | 64.1561 | 3543.9326
2027-04-21 17:00 | 11646 | 3.7169 | 80.4113 | 64.1561 | 3413.1057
2027-04-22 18:00 | 9639.43 | 3.0283 | 80.8097 | 64.1561 | 2825.0381
2027-04-23 19:00 | 7731.86 | 2.4034 | 80.9218 | 64.1561 | 2265.9845
2027-04-24 20:00 | 4668.55 | 1.4563 | 80.7502 | 64.1561 | 1368.2169
2027-04-25 21:00 | 3559.61 | 1.1276 | 80.1804 | 64.1561 | 1043.2187
2027-04-26 22:00 | 3043.97 | 1 | 66.7916 | 64.1561 | 892.0995
2027-04-27 23:00 | 693.323 | 1 | 67.1203 | 64.1561 | 203.1929
2027-04-29 | -190.834 | 1.0839 | 66.176 | 64.1561 | -55.9279
2027-04-30 01:00 | -528.733 | 1.8895 | 65.4053 | 64.1561 | -154.9563
2027-05-01 02:00 | -712.611 | 2.316 | 65.0553 | 64.1561 | -208.8457
2027-05-02 03:00 | -736.367 | 2.3485 | 64.8187 | 64.1561 | -215.8079
2027-05-03 04:00 | -916.81 | 2.8316 | 64.5885 | 64.1561 | -268.6905
2027-05-04 05:00 | -798.161 | 2.4781 | 64.4381 | 64.1561 | -233.9179
2027-05-05 06:00 | -828.272 | 2.5921 | 64.3481 | 64.1561 | -242.7426
2027-05-06 07:00 | 115.463 | 1 | 65.4866 | 64.1561 | 33.8389
2027-05-07 08:00 | 2129.11 | 1 | 65.0529 | 64.1561 | 623.9805
2027-05-08 09:00 | 2789.09 | 1 | 77.157 | 64.1561 | 817.4016
2027-05-09 10:00 | 4946.65 | 1.6321 | 77.7947 | 64.1561 | 1449.72
2027-05-10 11:00 | 6852.26 | 2.3458 | 77.6794 | 64.1561 | 2008.1992
2027-05-11 12:00 | 8189.94 | 2.7887 | 78.1498 | 64.1561 | 2400.2345
2027-05-12 13:00 | 7908.66 | 2.6085 | 78.9105 | 64.1561 | 2317.7994
2027-05-13 14:00 | 7809.85 | 2.4576 | 79.6757 | 64.1561 | 2288.8411
2027-05-14 15:00 | 8661.71 | 2.7831 | 79.5496 | 64.1561 | 2538.4966
2027-05-15 16:00 | 8841.54 | 2.8418 | 79.7465 | 64.1561 | 2591.1996
2027-05-16 17:00 | 8684.61 | 2.7245 | 80.1977 | 64.1561 | 2545.2079
2027-05-17 18:00 | 6882.69 | 2.1968 | 80.0847 | 64.1561 | 2017.1173
2027-05-18 19:00 | 5730.98 | 1.7281 | 80.712 | 64.1561 | 1679.5844
2027-05-19 20:00 | 3201.59 | 1 | 80.9866 | 64.1561 | 938.2934
2027-05-20 21:00 | 3009.13 | 1 | 66.5783 | 64.1561 | 881.8889
2027-05-21 22:00 | 0 | 0 | 67.0958 | 64.1561 | 0
2027-05-22 23:00 | -271.579 | 1.1279 | 65.6876 | 64.1561 | -79.5919
2027-05-24 | -651.791 | 2.2137 | 65.1594 | 64.1561 | -191.0211
2027-05-25 01:00 | -864.985 | 2.6982 | 64.8227 | 64.1561 | -253.5021
2027-05-26 02:00 | -1002.33 | 3.0285 | 64.5998 | 64.1561 | -293.7539
2027-05-27 03:00 | -945.31 | 2.8537 | 64.418 | 64.1561 | -277.043
2027-05-28 04:00 | -870.276 | 2.6715 | 64.3347 | 64.1561 | -255.0527
2027-05-29 05:00 | -539.626 | 1.8061 | 64.3503 | 64.1561 | -158.1488
2027-05-30 06:00 | -454.945 | 1.6559 | 64.4103 | 64.1561 | -133.3312
2027-05-31 07:00 | -106.648 | 0.74312 | 64.8894 | 64.1561 | -31.2554
2027-06-01 08:00 | -71.607 | 0.72859 | 65.0731 | 64.1561 | -20.9859
2027-06-02 09:00 | 2192.42 | 1 | 77.0243 | 64.1561 | 642.5349
2027-06-03 10:00 | 4656.73 | 1.6472 | 76.7215 | 64.1561 | 1364.7528
2027-06-04 11:00 | 6958.08 | 2.4327 | 77.2287 | 64.1561 | 2039.212
2027-06-05 12:00 | 7749.73 | 2.5898 | 78.1953 | 64.1561 | 2271.2217
2027-06-06 13:00 | 7914.47 | 2.6326 | 78.6044 | 64.1561 | 2319.5022
2027-06-07 14:00 | 9030.98 | 2.9451 | 79.1049 | 64.1561 | 2646.719
2027-06-08 15:00 | 8948.87 | 2.9842 | 79.1528 | 64.1561 | 2622.6549
2027-06-09 16:00 | 9602.18 | 3.133 | 79.6042 | 64.1561 | 2814.1212
2027-06-10 17:00 | 8837.4 | 2.885 | 79.7968 | 64.1561 | 2589.9863
2027-06-11 18:00 | 7391.68 | 2.2731 | 80.6215 | 64.1561 | 2166.2876
2027-06-12 19:00 | 5846.55 | 1.6915 | 81.3685 | 64.1561 | 1713.4547
2027-06-13 20:00 | 3281.01 | 1 | 83.3981 | 64.1561 | 961.5691
2027-06-14 21:00 | 3116.23 | 1 | 66.6432 | 64.1561 | 913.2769
2027-06-15 22:00 | -389.729 | 1.5727 | 66.2167 | 64.1561 | -114.2183
2027-06-16 23:00 | -860.552 | 2.7204 | 65.4305 | 64.1561 | -252.2029
2027-06-18 | -1145.35 | 3.393 | 64.9716 | 64.1561 | -335.669
2027-06-19 01:00 | -1369.46 | 3.9437 | 64.6785 | 64.1561 | -401.3491
2027-06-20 02:00 | -1594.95 | 4.5111 | 64.4399 | 64.1561 | -467.4337
2027-06-21 03:00 | -1581.48 | 4.4361 | 64.2105 | 64.1561 | -463.486
2027-06-22 04:00 | -1588.21 | 4.4684 | 64.0762 | 64.1561 | -465.4584
2027-06-23 05:00 | -1235.37 | 3.5188 | 63.9727 | 64.1561 | -362.0512
2027-06-24 06:00 | -1032.34 | 3.0588 | 63.9645 | 64.1561 | -302.549
2027-06-25 07:00 | -697.089 | 2.1996 | 64.0037 | 64.1561 | -204.2966
2027-06-26 08:00 | -753.607 | 2.4263 | 64.0285 | 64.1561 | -220.8604
2027-06-27 09:00 | 1679.72 | 1 | 64.8031 | 64.1561 | 492.2773
2027-06-28 10:00 | 3089.88 | 1.0771 | 76.6879 | 64.1561 | 905.5544
2027-06-29 11:00 | 5604.6 | 1.9287 | 77.0644 | 64.1561 | 1642.5461
2027-06-30 12:00 | 5915.79 | 1.9648 | 77.8761 | 64.1561 | 1733.7469
2027-07-01 13:00 | 6516.43 | 2.0832 | 78.6038 | 64.1561 | 1909.7771
2027-07-02 14:00 | 6870.77 | 2.2067 | 78.7953 | 64.1561 | 2013.6239
2027-07-03 15:00 | 8149.44 | 2.6263 | 78.9529 | 64.1561 | 2388.3651
2027-07-04 16:00 | 7537.32 | 2.4598 | 79.0861 | 64.1561 | 2208.9704
2027-07-05 17:00 | 7076.77 | 2.2544 | 79.4784 | 64.1561 | 2073.9966
2027-07-06 18:00 | 5816.98 | 1.7974 | 79.9067 | 64.1561 | 1704.7886
2027-07-07 19:00 | 4229.7 | 1.3346 | 79.5885 | 64.1561 | 1239.6027
2027-07-08 20:00 | 3122.74 | 1 | 66.3019 | 64.1561 | 915.1848
2027-07-09 21:00 | 3139.77 | 1 | 66.0925 | 64.1561 | 920.1758
2027-07-10 22:00 | -384.87 | 1.5808 | 65.8053 | 64.1561 | -112.7943
2027-07-11 23:00 | -931.045 | 2.918 | 65.0465 | 64.1561 | -272.8624
2027-07-13 | -1318.09 | 3.8511 | 64.6213 | 64.1561 | -386.294
2027-07-14 01:00 | -1627.94 | 4.6129 | 64.3551 | 64.1561 | -477.1021
2027-07-15 02:00 | -1896.69 | 5.2835 | 64.125 | 64.1561 | -555.865
2027-07-16 03:00 | -1999.61 | 5.5173 | 63.8875 | 64.1561 | -586.0278
2027-07-17 04:00 | -2127.34 | 5.8537 | 63.7422 | 64.1561 | -623.4618
2027-07-18 05:00 | -2252.29 | 6.1742 | 63.6052 | 64.1561 | -660.081
2027-07-19 06:00 | -1625.16 | 4.4413 | 63.4798 | 64.1561 | -476.2874
2027-07-20 07:00 | -960.033 | 2.7947 | 63.5451 | 64.1561 | -281.3579
2027-07-21 08:00 | -1206.24 | 3.6058 | 63.6251 | 64.1561 | -353.514
2027-07-22 09:00 | -847.745 | 2.5666 | 63.5873 | 64.1561 | -248.4495
2027-07-23 10:00 | -261.242 | 1.0804 | 63.932 | 64.1561 | -76.5625
2027-07-24 11:00 | 1896.94 | 1 | 64.4707 | 64.1561 | 555.9382
2027-07-25 12:00 | 2948.22 | 1 | 64.4552 | 64.1561 | 864.038
2027-07-26 13:00 | 3040.19 | 1 | 64.6548 | 64.1561 | 890.9917
2027-07-27 14:00 | 3210.4 | 1 | 80.4447 | 64.1561 | 940.8754
2027-07-28 15:00 | 3112.58 | 1 | 79.0136 | 64.1561 | 912.2072
2027-07-29 16:00 | 6111.68 | 1.9251 | 78.0559 | 64.1561 | 1791.1566
2027-07-30 17:00 | 5371.04 | 1.6713 | 78.5795 | 64.1561 | 1574.0964
2027-07-31 18:00 | 4298.76 | 1.3662 | 78.4507 | 64.1561 | 1259.8422
2027-08-01 19:00 | 3040.63 | 1 | 79.0608 | 64.1561 | 891.1207
2027-08-02 20:00 | 3112.39 | 1 | 86.5326 | 64.1561 | 912.1515
2027-08-03 21:00 | 3116.93 | 1 | 65.2866 | 64.1561 | 913.482
2027-08-04 22:00 | 3010.73 | 1 | 65.3273 | 64.1561 | 882.3579
2027-08-05 23:00 | -777.896 | 2.6267 | 64.8793 | 64.1561 | -227.9788
2027-08-07 | -1209.2 | 3.5996 | 64.3061 | 64.1561 | -354.3815
2027-08-08 01:00 | -1464.05 | 4.2128 | 64.0025 | 64.1561 | -429.0707
2027-08-09 02:00 | -1568.73 | 4.4498 | 63.8237 | 64.1561 | -459.7494
2027-08-10 03:00 | -1652.51 | 4.664 | 63.6715 | 64.1561 | -484.3029
2027-08-11 04:00 | -1737.24 | 4.8852 | 63.4985 | 64.1561 | -509.1348
2027-08-12 05:00 | -1818.56 | 5.0926 | 63.4009 | 64.1561 | -532.9673
2027-08-13 06:00 | -1187.44 | 3.3585 | 63.3326 | 64.1561 | -348.0043
2027-08-14 07:00 | -603.922 | 1.9344 | 63.5021 | 64.1561 | -176.9921
2027-08-15 08:00 | -825.749 | 2.6567 | 63.5557 | 64.1561 | -242.0031
2027-08-16 09:00 | -361.723 | 1.3441 | 63.6857 | 64.1561 | -106.0105
2027-08-17 10:00 | 1757.24 | 1 | 64.3305 | 64.1561 | 514.9962
2027-08-18 11:00 | 2909.29 | 1 | 64.3062 | 64.1561 | 852.6287
2027-08-19 12:00 | 3048.58 | 1 | 81.4348 | 64.1561 | 893.4506
2027-08-20 13:00 | 3164.48 | 1 | 79.8383 | 64.1561 | 927.4175
2027-08-21 14:00 | 3697.06 | 1.1732 | 77.8272 | 64.1561 | 1083.5013
2027-08-22 15:00 | 4050.03 | 1.2735 | 78.1003 | 64.1561 | 1186.9466
2027-08-23 16:00 | 6899.36 | 2.2936 | 77.5332 | 64.1561 | 2022.0028
2027-08-24 17:00 | 5827.56 | 1.8642 | 78.3906 | 64.1561 | 1707.8892
2027-08-25 18:00 | 4961.18 | 1.5573 | 78.7535 | 64.1561 | 1453.9783
2027-08-26 19:00 | 3457.95 | 1.0934 | 78.67 | 64.1561 | 1013.4251
2027-08-27 20:00 | 3137.98 | 1 | 82.0329 | 64.1561 | 919.6512
2027-08-28 21:00 | 3205.5 | 1 | 65.3901 | 64.1561 | 939.4393
2027-08-29 22:00 | 3133.02 | 1 | 65.3702 | 64.1561 | 918.1975
2027-08-30 23:00 | -582.833 | 2.1165 | 65.024 | 64.1561 | -170.8115
2027-09-01 | -928.028 | 2.8872 | 64.4272 | 64.1561 | -271.9782
2027-09-02 01:00 | -1137.99 | 3.393 | 64.1251 | 64.1561 | -333.5119
2027-09-03 02:00 | -1265.62 | 3.6985 | 63.9524 | 64.1561 | -370.9166
2027-09-04 03:00 | -1169.31 | 3.4176 | 63.8076 | 64.1561 | -342.6909
2027-09-05 04:00 | -1000.63 | 2.9925 | 63.6911 | 64.1561 | -293.2557
2027-09-06 05:00 | -648.626 | 2.0824 | 63.7331 | 64.1561 | -190.0935
2027-09-07 06:00 | -558.115 | 1.919 | 63.8059 | 64.1561 | -163.5674
2027-09-08 07:00 | -287.865 | 1.2084 | 64.0048 | 64.1561 | -84.3649
2027-09-09 08:00 | -646.496 | 2.2279 | 63.8179 | 64.1561 | -189.4693
2027-09-10 09:00 | -143.532 | 0.7949 | 64.1963 | 64.1561 | -42.0651
2027-09-11 10:00 | 1940.26 | 1 | 64.4414 | 64.1561 | 568.6341
2027-09-12 11:00 | 2965.96 | 1.0909 | 75.7982 | 64.1561 | 869.2371
2027-09-13 12:00 | 5215.44 | 1.7826 | 76.8134 | 64.1561 | 1528.4946
2027-09-14 13:00 | 6292.63 | 2.1499 | 77.1917 | 64.1561 | 1844.1878
2027-09-15 14:00 | 6650.09 | 2.2554 | 77.6433 | 64.1561 | 1948.949
2027-09-16 15:00 | 8350.35 | 2.8144 | 77.9917 | 64.1561 | 2447.246
2027-09-17 16:00 | 9054.35 | 2.9721 | 78.663 | 64.1561 | 2653.568
2027-09-18 17:00 | 8836.08 | 2.8307 | 79.2949 | 64.1561 | 2589.5994
2027-09-19 18:00 | 6708.79 | 2.0018 | 80.397 | 64.1561 | 1966.1523
2027-09-20 19:00 | 5189.06 | 1.5578 | 80.2566 | 64.1561 | 1520.7634
2027-09-21 20:00 | 3294.67 | 1 | 85.2348 | 64.1561 | 965.5725
2027-09-22 21:00 | 2933.87 | 1 | 66.1601 | 64.1561 | 859.8324
2027-09-23 22:00 | -470.781 | 1.8078 | 65.6617 | 64.1561 | -137.9723
2027-09-24 23:00 | -878.623 | 2.7641 | 64.9613 | 64.1561 | -257.499
2027-09-26 | -1178.34 | 3.4941 | 64.558 | 64.1561 | -345.3374
2027-09-27 01:00 | -1318.6 | 3.8162 | 64.3016 | 64.1561 | -386.4435
2027-09-28 02:00 | -1505.49 | 4.2999 | 64.1035 | 64.1561 | -441.2156
2027-09-29 03:00 | -1673.95 | 4.7232 | 63.891 | 64.1561 | -490.5863
2027-09-30 04:00 | -1677.42 | 4.7029 | 63.7372 | 64.1561 | -491.6033
2027-10-01 05:00 | -1440.25 | 4.0674 | 63.6227 | 64.1561 | -422.0956
2027-10-02 06:00 | -1381.93 | 3.9695 | 63.5775 | 64.1561 | -405.0037
2027-10-03 07:00 | -928.041 | 2.7511 | 63.5588 | 64.1561 | -271.982
2027-10-04 08:00 | -1133.01 | 3.4135 | 63.586 | 64.1561 | -332.0525
2027-10-05 09:00 | -451.503 | 1.5165 | 63.6759 | 64.1561 | -132.3225
2027-10-06 10:00 | 659.354 | 1 | 64.7322 | 64.1561 | 193.2376
2027-10-07 11:00 | 3026.09 | 1 | 80.8831 | 64.1561 | 886.8594
2027-10-08 12:00 | 3551.32 | 1.1483 | 77.4277 | 64.1561 | 1040.7892
2027-10-09 13:00 | 3219.36 | 1.0631 | 77.4043 | 64.1561 | 943.5013
2027-10-10 14:00 | 3993.45 | 1.3241 | 77.4455 | 64.1561 | 1170.3647
2027-10-11 15:00 | 5835.93 | 1.9212 | 77.6819 | 64.1561 | 1710.3422
2027-10-12 16:00 | 6256.41 | 2.0435 | 78.0831 | 64.1561 | 1833.5728
2027-10-13 17:00 | 6244.72 | 2.0034 | 78.5054 | 64.1561 | 1830.1468
2027-10-14 18:00 | 4387.64 | 1.401 | 78.7043 | 64.1561 | 1285.8903
2027-10-15 19:00 | 3067.55 | 1 | 82.8497 | 64.1561 | 899.0102
2027-10-16 20:00 | 0 | 0 | 66.2592 | 64.1561 | 0
2027-10-17 21:00 | -796.532 | 2.6091 | 64.6574 | 64.1561 | -233.4405
2027-10-18 22:00 | -1920.64 | 5.5228 | 64.1852 | 64.1561 | -562.884
2027-10-19 23:00 | -2370.41 | 6.4446 | 63.7868 | 64.1561 | -694.6986
2027-10-21 | -2824.38 | 6.4446 | 63.2489 | 64.1561 | -827.7441
2027-10-22 01:00 | -3003.36 | 6.4446 | 62.9098 | 64.1561 | -880.1979
2027-10-23 02:00 | -3309.12 | 6.4446 | 62.5606 | 64.1561 | -969.8073
2027-10-24 03:00 | -3351.62 | 6.4446 | 62.3562 | 64.1561 | -982.2629
2027-10-25 04:00 | -3299.63 | 6.4446 | 62.2412 | 64.1561 | -967.0261
2027-10-26 05:00 | -2981.23 | 6.4446 | 62.3114 | 64.1561 | -873.7123
2027-10-27 06:00 | -2946.22 | 6.4446 | 62.2697 | 64.1561 | -863.4518
2027-10-28 07:00 | -2159.45 | 5.9687 | 62.5781 | 64.1561 | -632.8723
2027-10-29 08:00 | -2047.63 | 5.6726 | 62.6325 | 64.1561 | -600.1011
2027-10-30 09:00 | -960.217 | 2.7097 | 62.6828 | 64.1561 | -281.4118
2027-10-31 10:00 | 475.778 | 1 | 64.0788 | 64.1561 | 139.4368
2027-11-01 11:00 | 2693.99 | 1 | 63.7597 | 64.1561 | 789.5305
2027-11-02 12:00 | 3020.46 | 1 | 80.2552 | 64.1561 | 885.2094
2027-11-03 13:00 | 3580.68 | 1.1576 | 77.0792 | 64.1561 | 1049.3937
2027-11-04 14:00 | 3970.39 | 1.302 | 77.1246 | 64.1561 | 1163.6064
2027-11-05 15:00 | 4959.25 | 1.6605 | 77.0609 | 64.1561 | 1453.4127
2027-11-06 16:00 | 4771.84 | 1.5777 | 77.4381 | 64.1561 | 1398.4883
2027-11-07 17:00 | 4182.47 | 1.3994 | 77.405 | 64.1561 | 1225.761
2027-11-08 18:00 | 2945.9 | 1 | 84.0304 | 64.1561 | 863.3581
2027-11-09 19:00 | 2747.92 | 1 | 65.0062 | 64.1561 | 805.3359
2027-11-10 20:00 | -942.615 | 3.0907 | 64.4549 | 64.1561 | -276.2532
2027-11-11 21:00 | -1805.55 | 5.1904 | 63.8729 | 64.1561 | -529.1545
2027-11-12 22:00 | -3029.12 | 6.4446 | 63.0668 | 64.1561 | -887.7474
2027-11-13 23:00 | -3810.87 | 6.4446 | 62.2692 | 64.1561 | -1116.8557
2027-11-15 | -4491.21 | 6.4446 | 61.5512 | 64.1561 | -1316.2437
2027-11-16 01:00 | -4914.56 | 6.4446 | 60.9839 | 64.1561 | -1440.3154
2027-11-17 02:00 | -5224.27 | 6.4446 | 60.5609 | 64.1561 | -1531.0824
2027-11-18 03:00 | -5255.91 | 6.4446 | 60.3188 | 64.1561 | -1540.3552
2027-11-19 04:00 | -5553.75 | 6.4446 | 59.9635 | 64.1561 | -1627.6435
2027-11-20 05:00 | -5325.36 | 6.4446 | 59.9223 | 64.1561 | -1560.709
2027-11-21 06:00 | -4947.82 | 6.4446 | 60.0369 | 64.1561 | -1450.0629
2027-11-22 07:00 | -3893.31 | 6.4446 | 60.6069 | 64.1561 | -1141.0165
2027-11-23 08:00 | -3240.82 | 6.4446 | 61.0683 | 64.1561 | -949.7906
2027-11-24 09:00 | -2068.28 | 5.7922 | 61.7174 | 64.1561 | -606.153
2027-11-25 10:00 | -965.437 | 2.7386 | 61.8868 | 64.1561 | -282.9417
2027-11-26 11:00 | 52.4517 | 1 | 63.4464 | 64.1561 | 15.3721
2027-11-27 12:00 | 2778.92 | 1 | 63.012 | 64.1561 | 814.4211
2027-11-28 13:00 | 2855.48 | 1 | 63.4209 | 64.1561 | 836.8586
2027-11-29 14:00 | 2853.31 | 1 | 63.6846 | 64.1561 | 836.2226
2027-11-30 15:00 | 2875.03 | 1 | 78.0173 | 64.1561 | 842.5881
2027-12-01 16:00 | 3079.2 | 1.0621 | 75.977 | 64.1561 | 902.4244
2027-12-02 17:00 | 3009.71 | 1.0369 | 76.1276 | 64.1561 | 882.0589
2027-12-03 18:00 | 2900.6 | 1 | 64.1498 | 64.1561 | 850.0819
2027-12-04 19:00 | 0 | 0 | 64.898 | 64.1561 | 0
2027-12-05 20:00 | -1444.43 | 4.285 | 63.329 | 64.1561 | -423.3206
2027-12-06 21:00 | -2262.22 | 6.3958 | 62.9874 | 64.1561 | -662.9912
2027-12-07 22:00 | -3831.16 | 6.4446 | 61.8229 | 64.1561 | -1122.8022
2027-12-08 23:00 | -4533.93 | 6.4446 | 61.0752 | 64.1561 | -1328.7637
2027-12-10 | -4948.59 | 6.4446 | 60.5016 | 64.1561 | -1450.2886
2027-12-11 01:00 | -5224.85 | 6.4446 | 60.1005 | 64.1561 | -1531.2524
2027-12-12 02:00 | -5360.61 | 6.4446 | 59.8232 | 64.1561 | -1571.0397
2027-12-13 03:00 | -5307.64 | 6.4446 | 59.6857 | 64.1561 | -1555.5157
2027-12-14 04:00 | -5257.83 | 6.4446 | 59.5958 | 64.1561 | -1540.9179
2027-12-15 05:00 | -4943.57 | 6.4446 | 59.685 | 64.1561 | -1448.8173
2027-12-16 06:00 | -4602.27 | 6.4446 | 59.8295 | 64.1561 | -1348.7922
2027-12-17 07:00 | -3549.9 | 6.4446 | 60.4537 | 64.1561 | -1040.373
2027-12-18 08:00 | -2858.37 | 6.4446 | 60.9667 | 64.1561 | -837.7056
2027-12-19 09:00 | -1542.47 | 4.3181 | 61.41 | 64.1561 | -452.0533
2027-12-20 10:00 | 0 | 0 | 63.0048 | 64.1561 | 0
2027-12-21 11:00 | 2800.79 | 1 | 62.6141 | 64.1561 | 820.8305
2027-12-22 12:00 | 3006.15 | 1 | 76.7573 | 64.1561 | 881.0156
2027-12-23 13:00 | 3782.07 | 1.2242 | 76.1163 | 64.1561 | 1108.4153
2027-12-24 14:00 | 4489.44 | 1.4445 | 76.4627 | 64.1561 | 1315.725
2027-12-25 15:00 | 6280.19 | 2.0245 | 76.7158 | 64.1561 | 1840.542
2027-12-26 16:00 | 6796.83 | 2.1953 | 77.0888 | 64.1561 | 1991.9542
2027-12-27 17:00 | 6509.9 | 2.1031 | 77.3857 | 64.1561 | 1907.8634
2027-12-28 18:00 | 4328.92 | 1.3865 | 77.6874 | 64.1561 | 1268.6812
2027-12-29 19:00 | 3093.29 | 1 | 83.6044 | 64.1561 | 906.5538
2027-12-30 20:00 | 0 | 0 | 65.3195 | 64.1561 | 0
2027-12-31 21:00 | -824.827 | 2.4432 | 63.6297 | 64.1561 | -241.7329
2028-01-01 22:00 | -2073.35 | 6.0136 | 63.3197 | 64.1561 | -607.6389
2028-01-02 23:00 | -2867.52 | 6.4446 | 62.6137 | 64.1561 | -840.3872
2028-01-04 | -3260.12 | 6.4446 | 62.0967 | 64.1561 | -955.4469
2028-01-05 01:00 | -3581.91 | 6.4446 | 61.6703 | 64.1561 | -1049.7542
2028-01-06 02:00 | -3817.85 | 6.4446 | 61.3547 | 64.1561 | -1118.9014
2028-01-07 03:00 | -4270.48 | 6.4446 | 60.9058 | 64.1561 | -1251.5541
2028-01-08 04:00 | -4536.4 | 6.4446 | 60.5581 | 64.1561 | -1329.4876
2028-01-09 05:00 | -4705.62 | 6.4446 | 60.2823 | 64.1561 | -1379.0811
2028-01-10 06:00 | -3419.77 | 6.4446 | 60.9219 | 64.1561 | -1002.2357
2028-01-11 07:00 | -2140.52 | 6.0108 | 61.6353 | 64.1561 | -627.3245
2028-01-12 08:00 | -1757.42 | 4.9194 | 61.7795 | 64.1561 | -515.049
2028-01-13 09:00 | -1018.31 | 2.9653 | 61.9317 | 64.1561 | -298.4372
2028-01-14 10:00 | 544.371 | 1 | 63.282 | 64.1561 | 159.5394
2028-01-15 11:00 | 2843.1 | 1 | 79.0165 | 64.1561 | 833.2304
2028-01-16 12:00 | 3521.6 | 1.1027 | 76.5443 | 64.1561 | 1032.0791
2028-01-17 13:00 | 4270.41 | 1.407 | 76.2178 | 64.1561 | 1251.5336
2028-01-18 14:00 | 5559.22 | 1.7155 | 77.2868 | 64.1561 | 1629.2466
2028-01-19 15:00 | 5822.37 | 1.8744 | 77.0969 | 64.1561 | 1706.3682
2028-01-20 16:00 | 8027.44 | 2.6553 | 77.0218 | 64.1561 | 2352.6104
2028-01-21 17:00 | 7009.74 | 2.2662 | 77.7167 | 64.1561 | 2054.352
2028-01-22 18:00 | 5408.98 | 1.7051 | 78.208 | 64.1561 | 1585.2156
2028-01-23 19:00 | 3560.41 | 1.101 | 78.4253 | 64.1561 | 1043.4532
2028-01-24 20:00 | 3141.24 | 1 | 86.1646 | 64.1561 | 920.6066
2028-01-25 21:00 | 3050.22 | 1 | 64.8482 | 64.1561 | 893.9312
2028-01-26 22:00 | 779.438 | 1 | 65.3576 | 64.1561 | 228.4307
2028-01-27 23:00 | -1147.11 | 3.6349 | 64.03 | 64.1561 | -336.1848
2028-01-29 | -1779.42 | 5.0926 | 63.5393 | 64.1561 | -521.4965
2028-01-30 01:00 | -2189.88 | 6.1006 | 63.2589 | 64.1561 | -641.7905
2028-01-31 02:00 | -2506.48 | 6.4446 | 62.9341 | 64.1561 | -734.5768
2028-02-01 03:00 | -2698.43 | 6.4446 | 62.6126 | 64.1561 | -790.8318
2028-02-02 04:00 | -2934.52 | 6.4446 | 62.2925 | 64.1561 | -860.0229
2028-02-03 05:00 | -2824.98 | 6.4446 | 62.2194 | 64.1561 | -827.9199
2028-02-04 06:00 | -1946.72 | 5.3827 | 62.4278 | 64.1561 | -570.5273
2028-02-05 07:00 | -1344.36 | 3.7972 | 62.4827 | 64.1561 | -393.993
2028-02-06 08:00 | -1705.88 | 4.9351 | 62.5735 | 64.1561 | -499.9441
2028-02-07 09:00 | -1230.17 | 3.524 | 62.516 | 64.1561 | -360.5272
2028-02-08 10:00 | 0 | 1 | 63.9073 | 64.1561 | 0
2028-02-09 11:00 | 2390.76 | 1 | 76.5543 | 64.1561 | 700.6626
2028-02-10 12:00 | 2863.98 | 1 | 78.3836 | 64.1561 | 839.3497
2028-02-11 13:00 | 3120.01 | 1 | 77.368 | 64.1561 | 914.3847
2028-02-12 14:00 | 4450.24 | 1.3978 | 77.2127 | 64.1561 | 1304.2366
2028-02-13 15:00 | 5214.41 | 1.7015 | 77.0172 | 64.1561 | 1528.1927
2028-02-14 16:00 | 7956.66 | 2.6631 | 76.9638 | 64.1561 | 2331.8669
2028-02-15 17:00 | 6574.24 | 2.091 | 78.0329 | 64.1561 | 1926.7196
2028-02-16 18:00 | 5488.8 | 1.6784 | 78.67 | 64.1561 | 1608.6085
2028-02-17 19:00 | 3589.94 | 1.1238 | 78.3862 | 64.1561 | 1052.1076
2028-02-18 20:00 | 3163.84 | 1 | 83.4743 | 64.1561 | 927.23
2028-02-19 21:00 | 3098.24 | 1 | 64.9606 | 64.1561 | 908.0045
2028-02-20 22:00 | 3037.86 | 1 | 64.9335 | 64.1561 | 890.3089
2028-02-21 23:00 | -986.138 | 3.2086 | 64.4327 | 64.1561 | -289.0085
2028-02-23 | -1600.34 | 4.6263 | 63.8291 | 64.1561 | -469.0134
2028-02-24 01:00 | -2018.75 | 5.6574 | 63.4932 | 64.1561 | -591.6372
2028-02-25 02:00 | -2144.49 | 5.9223 | 63.2737 | 64.1561 | -628.488
2028-02-26 03:00 | -2108.8 | 5.813 | 63.091 | 64.1561 | -618.0283
2028-02-27 04:00 | -2018.07 | 5.5861 | 62.9161 | 64.1561 | -591.4379
2028-02-28 05:00 | -1672.09 | 4.6601 | 62.8459 | 64.1561 | -490.0412
2028-02-29 06:00 | -1583.09 | 4.502 | 62.8428 | 64.1561 | -463.9579
2028-03-01 07:00 | -1321.19 | 3.7993 | 62.8356 | 64.1561 | -387.2026
2028-03-02 08:00 | -1547.2 | 4.4825 | 62.8466 | 64.1561 | -453.4396
2028-03-03 09:00 | -878.765 | 2.5937 | 62.8224 | 64.1561 | -257.5406
2028-03-04 10:00 | 94.1134 | 1 | 64.1466 | 64.1561 | 27.5819
2028-03-05 11:00 | 2115.86 | 1 | 73.9322 | 64.1561 | 620.0974
2028-03-06 12:00 | 2991.51 | 1.0559 | 75.6486 | 64.1561 | 876.725
2028-03-07 13:00 | 4714.75 | 1.501 | 77.0955 | 64.1561 | 1381.7568
2028-03-08 14:00 | 5865.05 | 1.9398 | 76.9701 | 64.1561 | 1718.8765
2028-03-09 15:00 | 7440.95 | 2.4756 | 77.2448 | 64.1561 | 2180.7272
2028-03-10 16:00 | 7260.59 | 2.3245 | 78.0891 | 64.1561 | 2127.8689
2028-03-11 17:00 | 6389.41 | 2.0137 | 78.5078 | 64.1561 | 1872.5512
2028-03-12 18:00 | 4791.04 | 1.4664 | 78.9614 | 64.1561 | 1404.1152
2028-03-13 19:00 | 3239.35 | 1 | 78.8356 | 64.1561 | 949.3598
2028-03-14 20:00 | 3063.47 | 1 | 65.2218 | 64.1561 | 897.8144
2028-03-15 21:00 | 0 | 0 | 65.8596 | 64.1561 | 0
2028-03-16 22:00 | -915.914 | 2.8345 | 64.2016 | 64.1561 | -268.4279
2028-03-17 23:00 | -1200.13 | 3.577 | 63.8333 | 64.1561 | -351.7234
2028-03-19 | -1155.5 | 3.399 | 63.6218 | 64.1561 | -338.6436
2028-03-20 01:00 | -1215.11 | 3.5818 | 63.4924 | 64.1561 | -356.1136
2028-03-21 02:00 | -1279.05 | 3.7453 | 63.3448 | 64.1561 | -374.8526
2028-03-22 03:00 | -1161.66 | 3.4157 | 63.249 | 64.1561 | -340.4489
2028-03-23 04:00 | -1045.87 | 3.1327 | 63.2094 | 64.1561 | -306.5142
2028-03-24 05:00 | -630.392 | 2.0318 | 63.2578 | 64.1561 | -184.7497
2028-03-25 06:00 | -638.902 | 2.1518 | 63.3168 | 64.1561 | -187.2437
2028-03-26 07:00 | -348.055 | 1.356 | 63.4679 | 64.1561 | -102.0049
2028-03-27 08:00 | -418.834 | 1.6149 | 63.4769 | 64.1561 | -122.7481
2028-03-28 09:00 | 197.366 | 1 | 64.4647 | 64.1561 | 57.8423
2028-03-29 10:00 | 2081.04 | 1 | 64.0941 | 64.1561 | 609.8926
2028-03-30 11:00 | 2843.66 | 1 | 80.1576 | 64.1561 | 833.3945
2028-03-31 12:00 | 3269.86 | 1.091 | 76.7578 | 64.1561 | 958.3014
2028-04-01 13:00 | 4874.13 | 1.5928 | 77.1605 | 64.1561 | 1428.4665
2028-04-02 14:00 | 5853.8 | 1.9394 | 77.281 | 64.1561 | 1715.5794
2028-04-03 15:00 | 7913.44 | 2.7207 | 77.1318 | 64.1561 | 2319.2003
2028-04-04 16:00 | 8930.45 | 2.9863 | 77.8331 | 64.1561 | 2617.2565
2028-04-05 17:00 | 8797.74 | 2.803 | 78.776 | 64.1561 | 2578.3631
2028-04-06 18:00 | 7282.8 | 2.2327 | 79.5094 | 64.1561 | 2134.378
2028-04-07 19:00 | 5584.14 | 1.6591 | 79.9546 | 64.1561 | 1636.5499
2028-04-08 20:00 | 3282 | 1 | 83.2023 | 64.1561 | 961.8593
2028-04-09 21:00 | 3185.3 | 1 | 65.6826 | 64.1561 | 933.5193
2028-04-10 22:00 | -253.176 | 1.2298 | 65.4971 | 64.1561 | -74.1986
2028-04-11 23:00 | -648.392 | 2.209 | 64.6979 | 64.1561 | -190.0249
2028-04-13 | -915.416 | 2.8504 | 64.2814 | 64.1561 | -268.2819
2028-04-14 01:00 | -1070.26 | 3.2179 | 64.0342 | 64.1561 | -313.6622
2028-04-15 02:00 | -1117.06 | 3.318 | 63.8575 | 64.1561 | -327.378
2028-04-16 03:00 | -1144.17 | 3.3891 | 63.6851 | 64.1561 | -335.3231
2028-04-17 04:00 | -995.652 | 2.9852 | 63.5908 | 64.1561 | -291.7968
2028-04-18 05:00 | -536.464 | 1.784 | 63.6342 | 64.1561 | -157.2221
2028-04-19 06:00 | -686.428 | 2.2932 | 63.6196 | 64.1561 | -201.1722
2028-04-20 07:00 | -246.025 | 1.0654 | 63.8384 | 64.1561 | -72.1028
2028-04-21 08:00 | -251.033 | 1.1845 | 63.9313 | 64.1561 | -73.5705
2028-04-22 09:00 | 2072.86 | 1 | 64.266 | 64.1561 | 607.4953
2028-04-23 10:00 | 3178.88 | 1.1223 | 76.1278 | 64.1561 | 931.6378
2028-04-24 11:00 | 5739.24 | 1.9818 | 76.6064 | 64.1561 | 1682.0052
2028-04-25 12:00 | 6889.98 | 2.4006 | 76.935 | 64.1561 | 2019.2538
2028-04-26 13:00 | 7179.6 | 2.3347 | 78.1292 | 64.1561 | 2104.1331
2028-04-27 14:00 | 7657.58 | 2.5092 | 78.3239 | 64.1561 | 2244.2152
2028-04-28 15:00 | 8842.01 | 2.892 | 78.5796 | 64.1561 | 2591.3373
2028-04-29 16:00 | 8894.77 | 2.8719 | 79.0461 | 64.1561 | 2606.7998
2028-04-30 17:00 | 8779.7 | 2.7821 | 79.4737 | 64.1561 | 2573.0761
2028-05-01 18:00 | 7143.17 | 2.1988 | 79.9849 | 64.1561 | 2093.4565
2028-05-02 19:00 | 5873.58 | 1.7554 | 80.3358 | 64.1561 | 1721.3764
2028-05-03 20:00 | 3226 | 1.0037 | 79.7353 | 64.1561 | 945.4473
2028-05-04 21:00 | 3188.71 | 1 | 66.0838 | 64.1561 | 934.5187
2028-05-05 22:00 | 0 | 0 | 66.6957 | 64.1561 | 0
2028-05-06 23:00 | -152.311 | 0.75549 | 65.4489 | 64.1561 | -44.6379
2028-05-08 | -275.222 | 1.2591 | 65.0842 | 64.1561 | -80.6596
2028-05-09 01:00 | -460.276 | 1.7105 | 64.6958 | 64.1561 | -134.8936
2028-05-10 02:00 | -663.464 | 2.2173 | 64.4234 | 64.1561 | -194.4421
2028-05-11 03:00 | -697.833 | 2.2708 | 64.2159 | 64.1561 | -204.5147
2028-05-12 04:00 | -646.64 | 2.1318 | 64.1259 | 64.1561 | -189.5115
2028-05-13 05:00 | -267.927 | 1.1329 | 64.2956 | 64.1561 | -78.5217
2028-05-14 06:00 | -160.888 | 0.93416 | 64.5151 | 64.1561 | -47.1516
2028-05-15 07:00 | 809.23 | 1 | 64.97 | 64.1561 | 237.1619
2028-05-16 08:00 | 2851.62 | 1 | 64.5791 | 64.1561 | 835.7273
2028-05-17 09:00 | 3425.51 | 1.1351 | 77.3548 | 64.1561 | 1003.9179
2028-05-18 10:00 | 5610.68 | 1.8436 | 77.6434 | 64.1561 | 1644.328
2028-05-19 11:00 | 7140.35 | 2.4124 | 77.6741 | 64.1561 | 2092.63
2028-05-20 12:00 | 7803.73 | 2.5877 | 78.2987 | 64.1561 | 2287.0475
2028-05-21 13:00 | 8320.63 | 2.6545 | 79.087 | 64.1561 | 2438.5359
2028-05-22 14:00 | 9398.48 | 2.9863 | 79.3977 | 64.1561 | 2754.4226
2028-05-23 15:00 | 10969.1 | 3.6743 | 79.0814 | 64.1561 | 3214.7259
2028-05-24 16:00 | 10956.5 | 3.5958 | 79.7103 | 64.1561 | 3211.0332
2028-05-25 17:00 | 10733.3 | 3.4285 | 80.2871 | 64.1561 | 3145.6197
2028-05-26 18:00 | 8337.32 | 2.6106 | 80.7204 | 64.1561 | 2443.4273
2028-05-27 19:00 | 6855.47 | 2.098 | 80.9267 | 64.1561 | 2009.1399
2028-05-28 20:00 | 4437.46 | 1.3242 | 81.1051 | 64.1561 | 1300.4912
2028-05-29 21:00 | 3409.95 | 1.0713 | 80.1257 | 64.1561 | 999.3577
2028-05-30 22:00 | 3102.43 | 1 | 66.6588 | 64.1561 | 909.2325
2028-05-31 23:00 | 3144.69 | 1 | 66.4525 | 64.1561 | 921.6177
2028-06-02 | 98.9663 | 1 | 67.0689 | 64.1561 | 29.0042
2028-06-03 01:00 | -422.131 | 1.6469 | 65.6625 | 64.1561 | -123.7144
2028-06-04 02:00 | -661.164 | 2.1976 | 65.1837 | 64.1561 | -193.768
2028-06-05 03:00 | -739.239 | 2.3635 | 64.9223 | 64.1561 | -216.6496
2028-06-06 04:00 | -717.319 | 2.2962 | 64.7319 | 64.1561 | -210.2254
2028-06-07 05:00 | -361.574 | 1.3606 | 64.7331 | 64.1561 | -105.9669
2028-06-08 06:00 | -258.083 | 1.1673 | 64.8492 | 64.1561 | -75.6367
2028-06-09 07:00 | 0 | 1 | 65.669 | 64.1561 | 0
2028-06-10 08:00 | 3003.94 | 1 | 64.937 | 64.1561 | 880.3679
2028-06-11 09:00 | 3383.19 | 1.0817 | 78.2253 | 64.1561 | 991.5151
2028-06-12 10:00 | 5774.86 | 1.8862 | 78.1236 | 64.1561 | 1692.4444
2028-06-13 11:00 | 7528.8 | 2.549 | 78.033 | 64.1561 | 2206.4735
2028-06-14 12:00 | 7709.44 | 2.5754 | 78.6193 | 64.1561 | 2259.4138
2028-06-15 13:00 | 7818.52 | 2.5503 | 79.1952 | 64.1561 | 2291.382
2028-06-16 14:00 | 8640.8 | 2.8142 | 79.396 | 64.1561 | 2532.3685
2028-06-17 15:00 | 10411.4 | 3.4411 | 79.4654 | 64.1561 | 3051.2801
2028-06-18 16:00 | 10712.4 | 3.5185 | 79.9027 | 64.1561 | 3139.4945
2028-06-19 17:00 | 10460.6 | 3.362 | 80.4211 | 64.1561 | 3065.6992
2028-06-20 18:00 | 8617.53 | 2.6861 | 80.9804 | 64.1561 | 2525.5487
2028-06-21 19:00 | 6723.94 | 2.0771 | 81.0778 | 64.1561 | 1970.5923
2028-06-22 20:00 | 4334.75 | 1.321 | 81.0912 | 64.1561 | 1270.3898
2028-06-23 21:00 | 3096.43 | 1 | 81.8655 | 64.1561 | 907.4741
2028-06-24 22:00 | 2861.79 | 1 | 66.9414 | 64.1561 | 838.7079
2028-06-25 23:00 | -311.734 | 1.3913 | 66.5252 | 64.1561 | -91.3602
2028-06-27 | -648.202 | 2.1701 | 65.7415 | 64.1561 | -189.9693
2028-06-28 01:00 | -1008.86 | 3.0666 | 65.2886 | 64.1561 | -295.6677
2028-06-29 02:00 | -1242.32 | 3.6189 | 65.0035 | 64.1561 | -364.0881
2028-06-30 03:00 | -1564.26 | 4.4411 | 64.7468 | 64.1561 | -458.4394
2028-07-01 04:00 | -1755.21 | 4.8947 | 64.4857 | 64.1561 | -514.4013
2028-07-02 05:00 | -1815.88 | 5.0283 | 64.2988 | 64.1561 | -532.1819
2028-07-03 06:00 | -941.772 | 2.6712 | 64.1872 | 64.1561 | -276.0061
2028-07-04 07:00 | 523.951 | 1 | 65.43 | 64.1561 | 153.5549
2028-07-05 08:00 | 3038.47 | 1 | 64.9516 | 64.1561 | 890.4877
2028-07-06 09:00 | 3114.74 | 1 | 82.3583 | 64.1561 | 912.8402
2028-07-07 10:00 | 4789.79 | 1.5395 | 78.3139 | 64.1561 | 1403.7489
2028-07-08 11:00 | 6483.83 | 2.1491 | 78.2371 | 64.1561 | 1900.223
2028-07-09 12:00 | 7417.83 | 2.4493 | 78.6635 | 64.1561 | 2173.9514
2028-07-10 13:00 | 8041.65 | 2.5991 | 79.2506 | 64.1561 | 2356.775
2028-07-11 14:00 | 8819.45 | 2.8805 | 79.3794 | 64.1561 | 2584.7256
2028-07-12 15:00 | 9532.34 | 3.1079 | 79.6746 | 64.1561 | 2793.6531
2028-07-13 16:00 | 12124.2 | 4.0521 | 79.6426 | 64.1561 | 3553.2523
2028-07-14 17:00 | 11035.6 | 3.5908 | 80.443 | 64.1561 | 3234.2151
2028-07-15 18:00 | 9550.1 | 3.0133 | 81.0261 | 64.1561 | 2798.858
2028-07-16 19:00 | 7532.9 | 2.3382 | 81.2384 | 64.1561 | 2207.6751
2028-07-17 20:00 | 6256.12 | 1.9013 | 81.3688 | 64.1561 | 1833.4878
2028-07-18 21:00 | 4968.48 | 1.5189 | 81.1427 | 64.1561 | 1456.1177
2028-07-19 22:00 | 3589.76 | 1.1656 | 80.1585 | 64.1561 | 1052.0548
2028-07-20 23:00 | 1225.64 | 1 | 67.5485 | 64.1561 | 359.1996
2028-07-22 | -170.21 | 1.0272 | 66.775 | 64.1561 | -49.8836
2028-07-23 01:00 | -537.968 | 1.9064 | 65.9292 | 64.1561 | -157.6629
2028-07-24 02:00 | -920.975 | 2.8502 | 65.4908 | 64.1561 | -269.9111
2028-07-25 03:00 | -1055.49 | 3.1349 | 65.1926 | 64.1561 | -309.3336
2028-07-26 04:00 | -1297.96 | 3.764 | 64.9318 | 64.1561 | -380.3945
2028-07-27 05:00 | -1092.87 | 3.1698 | 64.7459 | 64.1561 | -320.2886
2028-07-28 06:00 | -168.923 | 0.77072 | 65.1252 | 64.1561 | -49.5064
2028-07-29 07:00 | 2272.47 | 1 | 80.1806 | 64.1561 | 665.9952
2028-07-30 08:00 | 2924.21 | 1 | 82.9065 | 64.1561 | 857.0014
2028-07-31 09:00 | 4079.53 | 1.3316 | 78.3789 | 64.1561 | 1195.5922
2028-08-01 10:00 | 6107.35 | 2.0379 | 78.331 | 64.1561 | 1789.8876
2028-08-02 11:00 | 7668.63 | 2.6387 | 78.3416 | 64.1561 | 2247.4536
2028-08-03 12:00 | 8730.52 | 2.9274 | 79.0435 | 64.1561 | 2558.6628
2028-08-04 13:00 | 9082.84 | 2.9715 | 79.6806 | 64.1561 | 2661.9176
2028-08-05 14:00 | 9879.26 | 3.1726 | 80.1795 | 64.1561 | 2895.3253
2028-08-06 15:00 | 10425 | 3.3875 | 80.326 | 64.1561 | 3055.2659
2028-08-07 16:00 | 12338.5 | 4.0873 | 80.3458 | 64.1561 | 3616.0574
2028-08-08 17:00 | 11590.9 | 3.6315 | 81.4241 | 64.1561 | 3396.9575
2028-08-09 18:00 | 10187.5 | 3.173 | 81.6944 | 64.1561 | 2985.6615
2028-08-10 19:00 | 8082.19 | 2.5106 | 81.7361 | 64.1561 | 2368.6561
2028-08-11 20:00 | 6851.16 | 2.086 | 81.8387 | 64.1561 | 2007.8768
2028-08-12 21:00 | 5735.22 | 1.7646 | 81.5398 | 64.1561 | 1680.8271
2028-08-13 22:00 | 4711.91 | 1.4642 | 81.1998 | 64.1561 | 1380.9245
2028-08-14 23:00 | 3112.6 | 1 | 67.6512 | 64.1561 | 912.213
2028-08-16 | 3046.37 | 1 | 67.3672 | 64.1561 | 892.8029
2028-08-17 01:00 | 0 | 0 | 67.9271 | 64.1561 | 0
2028-08-18 02:00 | -155.027 | 0.92928 | 66.8262 | 64.1561 | -45.4339
2028-08-19 03:00 | -261.987 | 1.195 | 66.3203 | 64.1561 | -76.7808
2028-08-20 04:00 | -323.686 | 1.3368 | 66.0157 | 64.1561 | -94.863
2028-08-21 05:00 | 83.7565 | 1 | 66.769 | 64.1561 | 24.5466
2028-08-22 06:00 | 2090.07 | 1 | 66.1743 | 64.1561 | 612.5391
2028-08-23 07:00 | 2867.86 | 1 | 82.8311 | 64.1561 | 840.4868
2028-08-24 08:00 | 3160.47 | 1 | 79.3914 | 64.1561 | 926.2423
2028-08-25 09:00 | 5103.94 | 1.6137 | 79.4168 | 64.1561 | 1495.8172
2028-08-26 10:00 | 7001.95 | 2.3665 | 78.8784 | 64.1561 | 2052.069
2028-08-27 11:00 | 8610.09 | 2.9419 | 79.1226 | 64.1561 | 2523.3683
2028-08-28 12:00 | 9227.42 | 3.0747 | 79.7757 | 64.1561 | 2704.2899
2028-08-29 13:00 | 6818.97 | 2.1195 | 80.9416 | 64.1561 | 1998.4428
2028-08-30 14:00 | 7159.84 | 2.1196 | 81.5196 | 64.1561 | 2098.342
2028-08-31 15:00 | 8308.86 | 2.6422 | 80.6482 | 64.1561 | 2435.0865
2028-09-01 16:00 | 9106.83 | 3.0681 | 80.133 | 64.1561 | 2668.9484
2028-09-02 17:00 | 9032.8 | 2.9548 | 80.657 | 64.1561 | 2647.2524
2028-09-03 18:00 | 7652.14 | 2.3782 | 81.3678 | 64.1561 | 2242.6209
2028-09-04 19:00 | 6811.38 | 2.0336 | 81.8445 | 64.1561 | 1996.2184
2028-09-05 20:00 | 4510.17 | 1.3559 | 81.6944 | 64.1561 | 1321.8003
2028-09-06 21:00 | 3300.87 | 1.0466 | 80.7449 | 64.1561 | 967.3895
2028-09-07 22:00 | 2935.88 | 1 | 67.405 | 64.1561 | 860.4215
2028-09-08 23:00 | 50.9005 | 1 | 67.8737 | 64.1561 | 14.9175
2028-09-10 | -259.585 | 1.213 | 66.5741 | 64.1561 | -76.0769
2028-09-11 01:00 | -539.96 | 1.8967 | 65.9915 | 64.1561 | -158.2467
2028-09-12 02:00 | -696.587 | 2.2563 | 65.6998 | 64.1561 | -204.1495
2028-09-13 03:00 | -563.94 | 1.8818 | 65.5545 | 64.1561 | -165.2745
2028-09-14 04:00 | -430.561 | 1.5659 | 65.5016 | 64.1561 | -126.185
2028-09-15 05:00 | -110.426 | 0.75374 | 65.9214 | 64.1561 | -32.3627
2028-09-16 06:00 | 43.0534 | 1 | 66.4356 | 64.1561 | 12.6177
2028-09-17 07:00 | 1914.09 | 1 | 65.941 | 64.1561 | 560.9644
2028-09-18 08:00 | 2760.98 | 1 | 84.3971 | 64.1561 | 809.1634
2028-09-19 09:00 | 4483.98 | 1.5233 | 78.2261 | 64.1561 | 1314.1248
2028-09-20 10:00 | 6388.46 | 2.2363 | 78.1428 | 64.1561 | 1872.2728
2028-09-21 11:00 | 7782.83 | 2.716 | 78.5422 | 64.1561 | 2280.9223
2028-09-22 12:00 | 9114.86 | 3.0351 | 79.4575 | 64.1561 | 2671.3018
2028-09-23 13:00 | 9565.61 | 3.1332 | 80.039 | 64.1561 | 2803.4036
2028-09-24 14:00 | 10723 | 3.4256 | 80.6542 | 64.1561 | 3142.6011
2028-09-25 15:00 | 11959.6 | 3.9915 | 80.4718 | 64.1561 | 3505.0128
2028-09-26 16:00 | 12344.4 | 4.0113 | 81.1608 | 64.1561 | 3617.7865
2028-09-27 17:00 | 11871.5 | 3.82 | 81.5775 | 64.1561 | 3479.1932
2028-09-28 18:00 | 9985.41 | 3.0926 | 82.2329 | 64.1561 | 2926.4348
2028-09-29 19:00 | 8128.57 | 2.5089 | 82.2411 | 64.1561 | 2382.2487
2028-09-30 20:00 | 5334.94 | 1.5853 | 82.5784 | 64.1561 | 1563.5166
2028-10-01 21:00 | 3731.77 | 1.1796 | 81.4279 | 64.1561 | 1093.6738
2028-10-02 22:00 | 2953.52 | 1 | 67.9735 | 64.1561 | 865.5913
2028-10-03 23:00 | 0 | 0 | 68.3847 | 64.1561 | 0
2028-10-05 | -238.2 | 1.1257 | 67.0288 | 64.1561 | -69.8095
2028-10-06 01:00 | -539.813 | 1.8942 | 66.3904 | 64.1561 | -158.2036
2028-10-07 02:00 | -777.283 | 2.4587 | 66.0227 | 64.1561 | -227.7992
2028-10-08 03:00 | -751.97 | 2.3515 | 65.7751 | 64.1561 | -220.3807
2028-10-09 04:00 | -684.068 | 2.1873 | 65.603 | 64.1561 | -200.4805
2028-10-10 05:00 | -369.028 | 1.3763 | 65.649 | 64.1561 | -108.1514
2028-10-11 06:00 | -312.401 | 1.2975 | 65.6757 | 64.1561 | -91.5557
2028-10-12 07:00 | 312.59 | 1 | 66.4651 | 64.1561 | 91.6111
2028-10-13 08:00 | 2168.61 | 1 | 66.025 | 64.1561 | 635.5569
2028-10-14 09:00 | 2666.84 | 1 | 66.0903 | 64.1561 | 781.5737
2028-10-15 10:00 | 3128.62 | 1.0519 | 78.5067 | 64.1561 | 916.908
2028-10-16 11:00 | 4848.35 | 1.5586 | 79.1164 | 64.1561 | 1420.9111
2028-10-17 12:00 | 6075.6 | 1.942 | 79.4394 | 64.1561 | 1780.5826
2028-10-18 13:00 | 6346.77 | 2.0866 | 79.395 | 64.1561 | 1860.0547
2028-10-19 14:00 | 6926.02 | 2.2583 | 79.6711 | 64.1561 | 2029.8161
2028-10-20 15:00 | 8524.21 | 2.7924 | 79.7863 | 64.1561 | 2498.1993
2028-10-21 16:00 | 8321.74 | 2.7949 | 79.7978 | 64.1561 | 2438.8612
2028-10-22 17:00 | 7602.8 | 2.6013 | 79.7444 | 64.1561 | 2228.1607
2028-10-23 18:00 | 5289.82 | 1.8465 | 79.5569 | 64.1561 | 1550.2932
2028-10-24 19:00 | 3129.26 | 1.0998 | 79.2999 | 64.1561 | 917.0956
2028-10-25 20:00 | 2632.51 | 1 | 67.2335 | 64.1561 | 771.5125
2028-10-26 21:00 | -502.078 | 1.876 | 66.595 | 64.1561 | -147.1445
2028-10-27 22:00 | -1531.86 | 4.4462 | 65.8115 | 64.1561 | -448.9438
2028-10-28 23:00 | -2165.92 | 5.9409 | 65.3171 | 64.1561 | -634.7685
2028-10-30 | -2665.33 | 6.4446 | 64.8113 | 64.1561 | -781.1311
2028-10-31 01:00 | -2924.51 | 6.4446 | 64.3831 | 64.1561 | -857.0893
2028-11-01 02:00 | -3177.76 | 6.4446 | 63.9768 | 64.1561 | -931.3095
2028-11-02 03:00 | -3326.18 | 6.4446 | 63.676 | 64.1561 | -974.8071
2028-11-03 04:00 | -3201.67 | 6.4446 | 63.5644 | 64.1561 | -938.3169
2028-11-04 05:00 | -2765.53 | 6.4446 | 63.6866 | 64.1561 | -810.4968
2028-11-05 06:00 | -2584.61 | 6.4446 | 63.7318 | 64.1561 | -757.4744
2028-11-06 07:00 | -2055.78 | 5.5768 | 63.804 | 64.1561 | -602.4896
2028-11-07 08:00 | -1645.17 | 4.5326 | 63.8087 | 64.1561 | -482.1517
2028-11-08 09:00 | -670.862 | 1.9975 | 63.9355 | 64.1561 | -196.6102
2028-11-09 10:00 | 2503.85 | 1 | 64.7527 | 64.1561 | 733.806
2028-11-10 11:00 | 3030.67 | 1 | 84.099 | 64.1561 | 888.2017
2028-11-11 12:00 | 4006.43 | 1.2578 | 78.4282 | 64.1561 | 1174.1687
2028-11-12 13:00 | 5199.45 | 1.6223 | 78.751 | 64.1561 | 1523.8084
2028-11-13 14:00 | 6003.16 | 1.9541 | 78.5295 | 64.1561 | 1759.3525
2028-11-14 15:00 | 7797.58 | 2.5535 | 78.7313 | 64.1561 | 2285.2451
2028-11-15 16:00 | 8163.05 | 2.6989 | 78.9631 | 64.1561 | 2392.3538
2028-11-16 17:00 | 7800.8 | 2.6038 | 79.1236 | 64.1561 | 2286.1888
2028-11-17 18:00 | 5910.01 | 2.0156 | 79.0396 | 64.1561 | 1732.053
2028-11-18 19:00 | 3697.54 | 1.2509 | 79.0823 | 64.1561 | 1083.642
2028-11-19 20:00 | 2897.02 | 1 | 66.6159 | 64.1561 | 849.0328
2028-11-20 21:00 | 0 | 0 | 67.1395 | 64.1561 | 0
2028-11-21 22:00 | -1252.21 | 3.7824 | 65.4168 | 64.1561 | -366.9865
2028-11-22 23:00 | -1942.58 | 5.4302 | 64.9187 | 64.1561 | -569.314
2028-11-24 | -2465.72 | 6.4446 | 64.5212 | 64.1561 | -722.6312
2028-11-25 01:00 | -2860.73 | 6.4446 | 64.0257 | 64.1561 | -838.3972
2028-11-26 02:00 | -3065.18 | 6.4446 | 63.6551 | 64.1561 | -898.3156
2028-11-27 03:00 | -3153.99 | 6.4446 | 63.4039 | 64.1561 | -924.3432
2028-11-28 04:00 | -3235.36 | 6.4446 | 63.1878 | 64.1561 | -948.1904
2028-11-29 05:00 | -3025.66 | 6.4446 | 63.1621 | 64.1561 | -886.7334
2028-11-30 06:00 | -2411.97 | 6.4446 | 63.4364 | 64.1561 | -706.8786
2028-12-01 07:00 | -1877.74 | 5.1082 | 63.4482 | 64.1561 | -550.3113
2028-12-02 08:00 | -1299.27 | 3.6529 | 63.5095 | 64.1561 | -380.7784
2028-12-03 09:00 | 181.818 | 1 | 64.919 | 64.1561 | 53.2856
2028-12-04 10:00 | 2459.92 | 1 | 75.1021 | 64.1561 | 720.9314
2028-12-05 11:00 | 4354.77 | 1.4959 | 76.87 | 64.1561 | 1276.2571
2028-12-06 12:00 | 5487.04 | 1.8536 | 77.4484 | 64.1561 | 1608.0927
2028-12-07 13:00 | 6297.34 | 2.0947 | 77.9824 | 64.1561 | 1845.5682
2028-12-08 14:00 | 6967.35 | 2.3171 | 78.3076 | 64.1561 | 2041.9287
2028-12-09 15:00 | 8792.13 | 2.8432 | 78.9249 | 64.1561 | 2576.7189
2028-12-10 16:00 | 9435.03 | 3.052 | 79.3153 | 64.1561 | 2765.1343
2028-12-11 17:00 | 9179.75 | 2.9979 | 79.5315 | 64.1561 | 2690.3192
2028-12-12 18:00 | 7091.75 | 2.2766 | 79.9545 | 64.1561 | 2078.3868
2028-12-13 19:00 | 5453.12 | 1.686 | 80.3886 | 64.1561 | 1598.1517
2028-12-14 20:00 | 3084.17 | 1 | 83.1692 | 64.1561 | 903.881
2028-12-15 21:00 | 3078.67 | 1 | 66.6026 | 64.1561 | 902.2691
2028-12-16 22:00 | -256.139 | 1.2266 | 66.3748 | 64.1561 | -75.0669
2028-12-17 23:00 | -853.407 | 2.7254 | 65.5017 | 64.1561 | -250.1089
2028-12-19 | -1308.46 | 3.8227 | 65.048 | 64.1561 | -383.4718
2028-12-20 01:00 | -1661.44 | 4.6825 | 64.7584 | 64.1561 | -486.92
2028-12-21 02:00 | -2134.21 | 5.8915 | 64.5282 | 64.1561 | -625.4752
2028-12-22 03:00 | -2468.48 | 6.4446 | 64.2046 | 64.1561 | -723.4401
2028-12-23 04:00 | -2651.32 | 6.4446 | 63.9024 | 64.1561 | -777.0252
2028-12-24 05:00 | -2789.57 | 6.4446 | 63.6468 | 64.1561 | -817.5423
2028-12-25 06:00 | -1810.17 | 4.9183 | 63.7541 | 64.1561 | -530.5085
2028-12-26 07:00 | -848.113 | 2.4406 | 63.8269 | 64.1561 | -248.5574
2028-12-27 08:00 | -734.167 | 2.3525 | 64.0526 | 64.1561 | -215.1631
2028-12-28 09:00 | 1949.21 | 1 | 64.8324 | 64.1561 | 571.2571
2028-12-29 10:00 | 3108.04 | 1 | 84.9622 | 64.1561 | 910.8766
2028-12-30 11:00 | 3893.29 | 1.2431 | 78.1372 | 64.1561 | 1141.0107
2028-12-31 12:00 | 5331.99 | 1.7378 | 78.1314 | 64.1561 | 1562.652
2029-01-01 13:00 | 6163.41 | 2.0035 | 78.4673 | 64.1561 | 1806.3172
2029-01-02 14:00 | 6827.63 | 2.2285 | 78.7216 | 64.1561 | 2000.9808
2029-01-03 15:00 | 7509.93 | 2.4264 | 79.0788 | 64.1561 | 2200.9432
2029-01-04 16:00 | 9967.42 | 3.2676 | 79.1312 | 64.1561 | 2921.1624
2029-01-05 17:00 | 8790.41 | 2.8026 | 79.9243 | 64.1561 | 2576.2149
2029-01-06 18:00 | 7265.13 | 2.3387 | 79.9745 | 64.1561 | 2129.1994
2029-01-07 19:00 | 5268.22 | 1.6943 | 79.9601 | 64.1561 | 1543.9629
2029-01-08 20:00 | 3902.7 | 1.2276 | 80.0885 | 64.1561 | 1143.7685
2029-01-09 21:00 | 3032.3 | 1 | 82.2081 | 64.1561 | 888.6794
2029-01-10 22:00 | 3083.29 | 1 | 66.5182 | 64.1561 | 903.6231
2029-01-11 23:00 | -958.479 | 3.0565 | 65.9333 | 64.1561 | -280.9025
2029-01-13 | -1611.77 | 4.5892 | 65.2709 | 64.1561 | -472.3632
2029-01-14 01:00 | -2001.6 | 5.5197 | 64.8595 | 64.1561 | -586.6111
2029-01-15 02:00 | -2299.91 | 6.2575 | 64.5988 | 64.1561 | -674.0371
2029-01-16 03:00 | -2396.18 | 6.4446 | 64.3554 | 64.1561 | -702.251
2029-01-17 04:00 | -2562.46 | 6.4446 | 64.0186 | 64.1561 | -750.9829
2029-01-18 05:00 | -2867.75 | 6.4446 | 63.6794 | 64.1561 | -840.4546
2029-01-19 06:00 | -1750.09 | 4.7533 | 63.8197 | 64.1561 | -512.9007
2029-01-20 07:00 | -557.401 | 1.6729 | 63.9609 | 64.1561 | -163.3581
2029-01-21 08:00 | 0 | 0 | 65.3796 | 64.1561 | 0
2029-01-22 09:00 | 2247.49 | 1 | 64.9233 | 64.1561 | 658.6743
2029-01-23 10:00 | 3209.82 | 1.1174 | 76.9835 | 64.1561 | 940.7054
2029-01-24 11:00 | 4797.24 | 1.6043 | 77.6966 | 64.1561 | 1405.9323
2029-01-25 12:00 | 5980.65 | 1.9751 | 78.1672 | 64.1561 | 1752.7555
2029-01-26 13:00 | 6770.97 | 2.256 | 78.3931 | 64.1561 | 1984.3754
2029-01-27 14:00 | 7528.45 | 2.4791 | 78.8375 | 64.1561 | 2206.3709
2029-01-28 15:00 | 8327.62 | 2.6438 | 79.5478 | 64.1561 | 2440.5845
2029-01-29 16:00 | 10268.1 | 3.4148 | 79.254 | 64.1561 | 3009.2831
2029-01-30 17:00 | 9245.19 | 3.0201 | 79.8837 | 64.1561 | 2709.4977
2029-01-31 18:00 | 7653.39 | 2.4614 | 80.2425 | 64.1561 | 2242.9872
2029-02-01 19:00 | 5643.58 | 1.8102 | 80.2496 | 64.1561 | 1653.97
2029-02-02 20:00 | 3576.67 | 1.1587 | 79.9751 | 64.1561 | 1048.2185
2029-02-03 21:00 | 3139.39 | 1 | 87.0248 | 64.1561 | 920.0644
2029-02-04 22:00 | 3031.26 | 1 | 66.6854 | 64.1561 | 888.3746
2029-02-05 23:00 | -691.694 | 2.3661 | 66.1522 | 64.1561 | -202.7155
2029-02-07 | -1248.18 | 3.675 | 65.4687 | 64.1561 | -365.8054
2029-02-08 01:00 | -1509.03 | 4.272 | 65.0669 | 64.1561 | -442.253
2029-02-09 02:00 | -1863.23 | 5.1787 | 64.8318 | 64.1561 | -546.0588
2029-02-10 03:00 | -1829.02 | 5.0197 | 64.5936 | 64.1561 | -536.0328
2029-02-11 04:00 | -1859.51 | 5.1287 | 64.3937 | 64.1561 | -544.9686
2029-02-12 05:00 | -1556.17 | 4.308 | 64.2779 | 64.1561 | -456.0684
2029-02-13 06:00 | -1308.77 | 3.7189 | 64.2454 | 64.1561 | -383.5626
2029-02-14 07:00 | -536.244 | 1.7031 | 64.3488 | 64.1561 | -157.1576
2029-02-15 08:00 | 158.055 | 1 | 65.5961 | 64.1561 | 46.3213
2029-02-16 09:00 | 2427.43 | 1 | 77.2091 | 64.1561 | 711.4095
2029-02-17 10:00 | 4316.53 | 1.4876 | 77.3095 | 64.1561 | 1265.0501
2029-02-18 11:00 | 5906.08 | 2.0607 | 77.5328 | 64.1561 | 1730.9012
2029-02-19 12:00 | 6114.21 | 1.971 | 78.8384 | 64.1561 | 1791.8981
2029-02-20 13:00 | 6415.06 | 2.0127 | 79.4258 | 64.1561 | 1880.0685
2029-02-21 14:00 | 6289.55 | 2.0893 | 78.9521 | 64.1561 | 1843.2851
2029-02-22 15:00 | 7536.93 | 2.4829 | 79.1812 | 64.1561 | 2208.8561
2029-02-23 16:00 | 8525.48 | 2.7494 | 79.653 | 64.1561 | 2498.5715
2029-02-24 17:00 | 8213.21 | 2.7102 | 79.6306 | 64.1561 | 2407.0542
2029-02-25 18:00 | 6673.21 | 2.1508 | 80.0611 | 64.1561 | 1955.7248
2029-02-26 19:00 | 5225.29 | 1.6636 | 80.1749 | 64.1561 | 1531.3813
2029-02-27 20:00 | 3137.05 | 1 | 82.7603 | 64.1561 | 919.3786
2029-02-28 21:00 | 3082.69 | 1 | 66.7751 | 64.1561 | 903.4473
2029-03-01 22:00 | -317.493 | 1.3814 | 66.4413 | 64.1561 | -93.048
2029-03-02 23:00 | -936.746 | 2.9289 | 65.6117 | 64.1561 | -274.5332
2029-03-04 | -1371.59 | 3.9676 | 65.1579 | 64.1561 | -401.9733
2029-03-05 01:00 | -1739.07 | 4.8711 | 64.8677 | 64.1561 | -509.6711
2029-03-06 02:00 | -1950.73 | 5.3722 | 64.6378 | 64.1561 | -571.7025
2029-03-07 03:00 | -1954.04 | 5.35 | 64.4182 | 64.1561 | -572.6726
2029-03-08 04:00 | -1962.48 | 5.3835 | 64.2859 | 64.1561 | -575.1461
2029-03-09 05:00 | -1479.84 | 4.0844 | 64.1769 | 64.1561 | -433.6983
2029-03-10 06:00 | -1183.06 | 3.4039 | 64.1901 | 64.1561 | -346.7207
2029-03-11 07:00 | -563.698 | 1.8055 | 64.3074 | 64.1561 | -165.2036
2029-03-12 08:00 | -81.4474 | 0.66239 | 65.0906 | 64.1561 | -23.8699
2029-03-13 09:00 | 2316.6 | 1 | 76.8268 | 64.1561 | 678.9284
2029-03-14 10:00 | 4532.61 | 1.5469 | 77.3582 | 64.1561 | 1328.3769
2029-03-15 11:00 | 6502.33 | 2.2174 | 77.7553 | 64.1561 | 1905.6448
2029-03-16 12:00 | 7955 | 2.6475 | 78.4724 | 64.1561 | 2331.3804
2029-03-17 13:00 | 8887.15 | 2.9702 | 78.8552 | 64.1561 | 2604.5666
2029-03-18 14:00 | 9928.72 | 3.2626 | 79.4589 | 64.1561 | 2909.8206
2029-03-19 15:00 | 11809.8 | 3.8815 | 79.8342 | 64.1561 | 3461.1107
2029-03-20 16:00 | 12117 | 3.977 | 80.3178 | 64.1561 | 3551.1422
2029-03-21 17:00 | 11822.2 | 3.7981 | 80.9232 | 64.1561 | 3464.7448
2029-03-22 18:00 | 10010.4 | 3.2115 | 81.1749 | 64.1561 | 2933.7586
2029-03-23 19:00 | 8140.95 | 2.5543 | 81.4747 | 64.1561 | 2385.8769
2029-03-24 20:00 | 5620.91 | 1.7226 | 81.6744 | 64.1561 | 1647.3261
2029-03-25 21:00 | 4321.21 | 1.3483 | 81.1442 | 64.1561 | 1266.4216
2029-03-26 22:00 | 3166.74 | 1 | 88.5248 | 64.1561 | 928.0799
2029-03-27 23:00 | 3121.25 | 1 | 67.2982 | 64.1561 | 914.7481
2029-03-29 | 0 | 0 | 67.878 | 64.1561 | 0
2029-03-30 01:00 | -249.712 | 0.91824 | 66.3489 | 64.1561 | -73.1834
2029-03-31 02:00 | -469.13 | 1.7344 | 66.0541 | 64.1561 | -137.4884
2029-04-01 03:00 | -427.621 | 1.5653 | 65.8256 | 64.1561 | -125.3233
2029-04-02 04:00 | -459.774 | 1.6665 | 65.6389 | 64.1561 | -134.7465
2029-04-03 05:00 | -223.312 | 1.0406 | 65.704 | 64.1561 | -65.4463
2029-04-04 06:00 | 1032.59 | 1 | 66.2256 | 64.1561 | 302.6223
2029-04-05 07:00 | 3331.96 | 1 | 65.7508 | 64.1561 | 976.5011
2029-04-06 08:00 | 3005.9 | 1 | 86.6404 | 64.1561 | 880.9423
2029-04-07 09:00 | 4120.21 | 1.2724 | 79.5843 | 64.1561 | 1207.5144
2029-04-08 10:00 | 5950.36 | 1.9064 | 79.3057 | 64.1561 | 1743.8784
2029-04-09 11:00 | 7385.26 | 2.5359 | 78.8005 | 64.1561 | 2164.4061
2029-04-10 12:00 | 8698.96 | 2.8704 | 79.6172 | 64.1561 | 2549.4135
2029-04-11 13:00 | 9027.83 | 2.9792 | 79.9511 | 64.1561 | 2645.7958
2029-04-12 14:00 | 10358.6 | 3.3765 | 80.3669 | 64.1561 | 3035.806
2029-04-13 15:00 | 12172.5 | 4.0699 | 80.396 | 64.1561 | 3567.4076
2029-04-14 16:00 | 12764.6 | 4.1182 | 81.2479 | 64.1561 | 3740.935
2029-04-15 17:00 | 12325.9 | 3.9908 | 81.5522 | 64.1561 | 3612.3647
2029-04-16 18:00 | 10864.9 | 3.4634 | 81.9418 | 64.1561 | 3184.1879
2029-04-17 19:00 | 8881.72 | 2.7693 | 82.2433 | 64.1561 | 2602.9752
2029-04-18 20:00 | 6352.77 | 1.9542 | 82.2962 | 64.1561 | 1861.8131
2029-04-19 21:00 | 5218.5 | 1.6121 | 81.934 | 64.1561 | 1529.3914
2029-04-20 22:00 | 3131.95 | 1 | 83.458 | 64.1561 | 917.8839
2029-04-21 23:00 | 3101.01 | 1 | 67.8764 | 64.1561 | 908.8163
2029-04-23 | 3003.41 | 1 | 67.6773 | 64.1561 | 880.2126
2029-04-24 01:00 | 326.388 | 1 | 68.1764 | 64.1561 | 95.6549
2029-04-25 02:00 | -134.236 | 0.9275 | 67.2846 | 64.1561 | -39.3407
2029-04-26 03:00 | -265.184 | 1.1992 | 66.6642 | 64.1561 | -77.7178
2029-04-27 04:00 | -177.876 | 0.95348 | 66.5969 | 64.1561 | -52.1303
2029-04-28 05:00 | 1032.19 | 1 | 66.9119 | 64.1561 | 302.505
2029-04-29 06:00 | 2391.89 | 1 | 66.5619 | 64.1561 | 700.9938
2029-04-30 07:00 | 3060.5 | 1 | 66.5274 | 64.1561 | 896.944
2029-05-01 08:00 | 3186.33 | 1 | 66.6309 | 64.1561 | 933.8211
2029-05-02 09:00 | 3634.43 | 1.1556 | 79.7899 | 64.1561 | 1065.1463
2029-05-03 10:00 | 6191.57 | 1.9927 | 79.7088 | 64.1561 | 1814.57
2029-05-04 11:00 | 8058.6 | 2.7056 | 79.5327 | 64.1561 | 2361.7425
2029-05-05 12:00 | 9842.64 | 3.2974 | 79.928 | 64.1561 | 2884.593
2029-05-06 13:00 | 10198 | 3.3559 | 80.5603 | 64.1561 | 2988.7388
2029-05-07 14:00 | 10652.8 | 3.4945 | 80.9134 | 64.1561 | 3122.0275
2029-05-08 15:00 | 12356.3 | 4.024 | 81.2732 | 64.1561 | 3621.2741
2029-05-09 16:00 | 12669.8 | 4.0659 | 81.8344 | 64.1561 | 3713.1518
2029-05-10 17:00 | 12394.2 | 3.9971 | 82.0599 | 64.1561 | 3632.3815
2029-05-11 18:00 | 10474.7 | 3.34 | 82.3615 | 64.1561 | 3069.8315
2029-05-12 19:00 | 8844.66 | 2.7569 | 82.5962 | 64.1561 | 2592.114
2029-05-13 20:00 | 6573.13 | 2.0186 | 82.6643 | 64.1561 | 1926.3942
2029-05-14 21:00 | 4991.72 | 1.5193 | 82.504 | 64.1561 | 1462.9287
2029-05-15 22:00 | 3118.89 | 1 | 85.8743 | 64.1561 | 914.0564
2029-05-16 23:00 | 3103.21 | 1 | 68.2018 | 64.1561 | 909.4611
2029-05-18 | 2949.14 | 1 | 68.004 | 64.1561 | 864.3076
2029-05-19 01:00 | 0 | 0 | 68.5461 | 64.1561 | 0
2029-05-20 02:00 | -74.3049 | 0.70408 | 67.684 | 64.1561 | -21.7766
2029-05-21 03:00 | -164.57 | 0.95472 | 67.1238 | 64.1561 | -48.2307
2029-05-22 04:00 | -119.576 | 0.82054 | 67.0402 | 64.1561 | -35.0443
2029-05-23 05:00 | 122.723 | 1 | 67.4018 | 64.1561 | 35.9666
2029-05-24 06:00 | 2312.5 | 1 | 66.7384 | 64.1561 | 677.7268
2029-05-25 07:00 | 2966.28 | 1 | 81.4297 | 64.1561 | 869.3309
2029-05-26 08:00 | 3566.54 | 1.142 | 79.7951 | 64.1561 | 1045.2497
2029-05-27 09:00 | 5385.04 | 1.7738 | 79.5779 | 64.1561 | 1578.1994
2029-05-28 10:00 | 6986.75 | 2.3342 | 79.6877 | 64.1561 | 2047.6143
2029-05-29 11:00 | 8564.27 | 2.8555 | 80.0468 | 64.1561 | 2509.9398
2029-05-30 12:00 | 9683.3 | 3.2317 | 80.3708 | 64.1561 | 2837.8951
2029-05-31 13:00 | 9875.64 | 3.2124 | 81.0318 | 64.1561 | 2894.2644
2029-06-01 14:00 | 10768.5 | 3.5655 | 81.0817 | 64.1561 | 3155.9358
2029-06-02 15:00 | 12807.4 | 4.157 | 81.5894 | 64.1561 | 3753.4784
2029-06-03 16:00 | 13305.3 | 4.2924 | 82.086 | 64.1561 | 3899.3985
2029-06-04 17:00 | 12986.8 | 4.2036 | 82.3773 | 64.1561 | 3806.0554
2029-06-05 18:00 | 10986.4 | 3.4776 | 82.8422 | 64.1561 | 3219.796
2029-06-06 19:00 | 9489.91 | 2.9577 | 83.0051 | 64.1561 | 2781.2181
2029-06-07 20:00 | 6738.18 | 2.0474 | 83.2325 | 64.1561 | 1974.7656
2029-06-08 21:00 | 5445.26 | 1.6412 | 83.0094 | 64.1561 | 1595.8482
2029-06-09 22:00 | 3270.99 | 1.0333 | 82.1097 | 64.1561 | 958.6325
2029-06-10 23:00 | 3037.92 | 1 | 68.5845 | 64.1561 | 890.3265
2029-06-12 | 3143.93 | 1 | 68.2804 | 64.1561 | 921.3949
2029-06-13 01:00 | 1928.37 | 1 | 68.4211 | 64.1561 | 565.1495
2029-06-14 02:00 | 330.996 | 1 | 68.5612 | 64.1561 | 97.0054
2029-06-15 03:00 | -217.788 | 1.1136 | 67.5107 | 64.1561 | -63.8274
2029-06-16 04:00 | -426.114 | 1.5923 | 66.9499 | 64.1561 | -124.8817
2029-06-17 05:00 | -595.756 | 1.9976 | 66.6023 | 64.1561 | -174.5988
2029-06-18 06:00 | 1632.86 | 1 | 67.1629 | 64.1561 | 478.544
2029-06-19 07:00 | 2677.73 | 1 | 81.7478 | 64.1561 | 784.7652
2029-06-20 08:00 | 2989.93 | 1 | 80.2855 | 64.1561 | 876.262
2029-06-21 09:00 | 4250.29 | 1.3667 | 80.0184 | 64.1561 | 1245.637
2029-06-22 10:00 | 6339.85 | 2.068 | 80.0268 | 64.1561 | 1858.0266
2029-06-23 11:00 | 7496.12 | 2.5464 | 79.8923 | 64.1561 | 2196.8959
2029-06-24 12:00 | 8348.17 | 2.7896 | 80.3677 | 64.1561 | 2446.6071
2029-06-25 13:00 | 8697.49 | 2.9224 | 80.5587 | 64.1561 | 2548.9827
2029-06-26 14:00 | 9800.41 | 3.1739 | 81.2172 | 64.1561 | 2872.2166
2029-06-27 15:00 | 10776.2 | 3.4311 | 81.6936 | 64.1561 | 3158.1925
2029-06-28 16:00 | 13039.1 | 4.2911 | 81.5679 | 64.1561 | 3821.383
2029-06-29 17:00 | 12265.5 | 3.915 | 82.3826 | 64.1561 | 3594.6632
2029-06-30 18:00 | 10522.6 | 3.3563 | 82.5965 | 64.1561 | 3083.8696
2029-07-01 19:00 | 8525.45 | 2.7088 | 82.6221 | 64.1561 | 2498.5628
2029-07-02 20:00 | 6977.12 | 2.2259 | 82.4261 | 64.1561 | 2044.792
2029-07-03 21:00 | 5730.45 | 1.7993 | 82.4253 | 64.1561 | 1679.4291
2029-07-04 22:00 | 4678.66 | 1.4399 | 82.4236 | 64.1561 | 1371.1799
2029-07-05 23:00 | 3101.26 | 1 | 68.7164 | 64.1561 | 908.8896
2029-07-07 | 2371.68 | 1 | 68.5628 | 64.1561 | 695.0708
2029-07-08 01:00 | -116.887 | 0.8791 | 68.3448 | 64.1561 | -34.2562
2029-07-09 02:00 | -447.399 | 1.6578 | 67.3691 | 64.1561 | -131.1197
2029-07-10 03:00 | -695.925 | 2.2438 | 66.8908 | 64.1561 | -203.9555
2029-07-11 04:00 | -816.99 | 2.5169 | 66.5717 | 64.1561 | -239.4361
2029-07-12 05:00 | -767.034 | 2.3699 | 66.3574 | 64.1561 | -224.7955
2029-07-13 06:00 | 0 | 1 | 67.4388 | 64.1561 | 0
2029-07-14 07:00 | 2338.77 | 1 | 78.93 | 64.1561 | 685.4258
2029-07-15 08:00 | 2971.28 | 1 | 80.2072 | 64.1561 | 870.7962
2029-07-16 09:00 | 4639.55 | 1.4803 | 79.9962 | 64.1561 | 1359.7179
2029-07-17 10:00 | 6420.23 | 2.1813 | 79.4793 | 64.1561 | 1881.5837
2029-07-18 11:00 | 8083.99 | 2.6931 | 80.0466 | 64.1561 | 2369.1836
2029-07-19 12:00 | 9092.88 | 3.0197 | 80.4625 | 64.1561 | 2664.8601
2029-07-20 13:00 | 9776.01 | 3.2686 | 80.7249 | 64.1561 | 2865.0657
2029-07-21 14:00 | 10689.5 | 3.4859 | 81.3255 | 64.1561 | 3132.7832
2029-07-22 15:00 | 10925.5 | 3.4516 | 82.0197 | 64.1561 | 3201.948
2029-07-23 16:00 | 12259.9 | 4.0694 | 81.6441 | 64.1561 | 3593.022
2029-07-24 17:00 | 10609.1 | 3.3385 | 82.6094 | 64.1561 | 3109.2203
2029-07-25 18:00 | 8664.84 | 2.4898 | 83.8416 | 64.1561 | 2539.4139
2029-07-26 19:00 | 6700.95 | 2.0301 | 82.9909 | 64.1561 | 1963.8546
2029-07-27 20:00 | 5429.91 | 1.6951 | 82.373 | 64.1561 | 1591.3495
2029-07-28 21:00 | 4466.69 | 1.3927 | 82.1441 | 64.1561 | 1309.0576
2029-07-29 22:00 | 3155.97 | 1.0553 | 81.0312 | 64.1561 | 924.9235
2029-07-30 23:00 | 2959.58 | 1 | 68.3227 | 64.1561 | 867.3673
2029-08-01 | 0 | 0 | 68.8212 | 64.1561 | 0
2029-08-02 01:00 | -332.61 | 1.382 | 67.4246 | 64.1561 | -97.4784
2029-08-03 02:00 | -599.236 | 2.0174 | 66.88 | 64.1561 | -175.6187
2029-08-04 03:00 | -559.189 | 1.8673 | 66.6355 | 64.1561 | -163.8821
2029-08-05 04:00 | -500.064 | 1.7301 | 66.4816 | 64.1561 | -146.5543
2029-08-06 05:00 | -129.701 | 0.78309 | 66.8012 | 64.1561 | -38.0116
2029-08-07 06:00 | 3202.82 | 1 | 66.6246 | 64.1561 | 938.6539
2029-08-08 07:00 | 2293.31 | 1 | 67.1501 | 64.1561 | 672.1028
2029-08-09 08:00 | 2975.84 | 1 | 67.0349 | 64.1561 | 872.1326
2029-08-10 09:00 | 3714.61 | 1.1733 | 80.2169 | 64.1561 | 1088.6447
2029-08-11 10:00 | 5353.65 | 1.692 | 80.3161 | 64.1561 | 1568.9999
2029-08-12 11:00 | 7026.57 | 2.3824 | 79.7235 | 64.1561 | 2059.2844
2029-08-13 12:00 | 7944.99 | 2.646 | 80.2293 | 64.1561 | 2328.4467
2029-08-14 13:00 | 8188.54 | 2.6779 | 80.7365 | 64.1561 | 2399.8242
2029-08-15 14:00 | 9253.77 | 3.044 | 80.873 | 64.1561 | 2712.0123
2029-08-16 15:00 | 10730.3 | 3.5931 | 80.9323 | 64.1561 | 3144.7405
2029-08-17 16:00 | 11471.5 | 3.6713 | 81.8088 | 64.1561 | 3361.9648
2029-08-18 17:00 | 11101.6 | 3.5859 | 81.994 | 64.1561 | 3253.5578
2029-08-19 18:00 | 9428.54 | 2.97 | 82.4531 | 64.1561 | 2763.2323
2029-08-20 19:00 | 7658.61 | 2.3651 | 82.6803 | 64.1561 | 2244.517
2029-08-21 20:00 | 5105.08 | 1.512 | 83.0773 | 64.1561 | 1496.1513
2029-08-22 21:00 | 3965.13 | 1.2094 | 82.3634 | 64.1561 | 1162.0649
2029-08-23 22:00 | 3098.73 | 1 | 68.4991 | 64.1561 | 908.1481
2029-08-24 23:00 | 3082.26 | 1 | 68.2243 | 64.1561 | 903.3212
2029-08-26 | 3060.98 | 1 | 68.058 | 64.1561 | 897.0847
2029-08-27 01:00 | 295.122 | 1 | 68.6127 | 64.1561 | 86.4917
2029-08-28 02:00 | -164.443 | 0.97656 | 67.6442 | 64.1561 | -48.1935
2029-08-29 03:00 | -148.251 | 0.88912 | 67.3592 | 64.1561 | -43.4481
2029-08-30 04:00 | -84.2561 | 0.7337 | 67.3838 | 64.1561 | -24.693
2029-08-31 05:00 | 3112.73 | 1 | 66.9338 | 64.1561 | 912.2511
2029-09-01 06:00 | 2070.53 | 1 | 67.3818 | 64.1561 | 606.8124
2029-09-02 07:00 | 2798.22 | 1 | 67.201 | 64.1561 | 820.0773
2029-09-03 08:00 | 3052.36 | 1 | 86.0201 | 64.1561 | 894.5584
2029-09-04 09:00 | 4937.68 | 1.5806 | 80.2098 | 64.1561 | 1447.0912
2029-09-05 10:00 | 6415.87 | 2.2433 | 79.4404 | 64.1561 | 1880.3059
2029-09-06 11:00 | 8006.77 | 2.7622 | 79.8408 | 64.1561 | 2346.5527
2029-09-07 12:00 | 9150.61 | 3.075 | 80.4595 | 64.1561 | 2681.7791
2029-09-08 13:00 | 9791.37 | 3.2239 | 81.039 | 64.1561 | 2869.5673
2029-09-09 14:00 | 9743.97 | 3.1995 | 81.3781 | 64.1561 | 2855.6757
2029-09-10 15:00 | 11342.7 | 3.7744 | 81.4068 | 64.1561 | 3324.2172
2029-09-11 16:00 | 11189.7 | 3.4157 | 82.7863 | 64.1561 | 3279.3774
2029-09-12 17:00 | 10124 | 3.1074 | 82.8917 | 64.1561 | 2967.0515
2029-09-13 18:00 | 7900.4 | 2.4627 | 82.722 | 64.1561 | 2315.3787
2029-09-14 19:00 | 6372.01 | 1.9659 | 82.6746 | 64.1561 | 1867.4518
2029-09-15 20:00 | 3957.22 | 1.2052 | 82.6456 | 64.1561 | 1159.7467
2029-09-16 21:00 | 3222.11 | 1 | 86.1068 | 64.1561 | 944.3072
2029-09-17 22:00 | 2071.53 | 1 | 68.635 | 64.1561 | 607.1055
2029-09-18 23:00 | -83.8749 | 0.79576 | 68.3961 | 64.1561 | -24.5813
2029-09-20 | -436.001 | 1.6363 | 67.3099 | 64.1561 | -127.7793
2029-09-21 01:00 | -706.397 | 2.2744 | 66.8167 | 64.1561 | -207.0245
2029-09-22 02:00 | -862.827 | 2.6344 | 66.5289 | 64.1561 | -252.8696
2029-09-23 03:00 | -741.707 | 2.2948 | 66.3282 | 64.1561 | -217.3729
2029-09-24 04:00 | -535.51 | 1.7899 | 66.2568 | 64.1561 | -156.9425
2029-09-25 05:00 | -108.398 | 0.72358 | 66.734 | 64.1561 | -31.7683
2029-09-26 06:00 | 1787.24 | 1 | 66.8446 | 64.1561 | 523.7883
2029-09-27 07:00 | 2856.84 | 1 | 66.7447 | 64.1561 | 837.2572
2029-09-28 08:00 | 3094.99 | 1 | 66.8854 | 64.1561 | 907.052
2029-09-29 09:00 | 3172.17 | 1 | 80.5959 | 64.1561 | 929.6713
2029-09-30 10:00 | 5038.25 | 1.6054 | 80.0648 | 64.1561 | 1476.5653
2029-10-01 11:00 | 6656.86 | 2.255 | 79.5999 | 64.1561 | 1950.9331
2029-10-02 12:00 | 7314.47 | 2.4956 | 79.8356 | 64.1561 | 2143.6595
2029-10-03 13:00 | 8333.19 | 2.6055 | 81.1205 | 64.1561 | 2442.2169
2029-10-04 14:00 | 8697.32 | 2.9097 | 80.5725 | 64.1561 | 2548.9329
2029-10-05 15:00 | 10215.1 | 3.3591 | 81.004 | 64.1561 | 2993.7503
2029-10-06 16:00 | 10989.4 | 3.6434 | 81.2204 | 64.1561 | 3220.6752
2029-10-07 17:00 | 10344.4 | 3.4456 | 81.462 | 64.1561 | 3031.6444
2029-10-08 18:00 | 8530.48 | 2.7492 | 81.9895 | 64.1561 | 2500.0369
2029-10-09 19:00 | 6944.14 | 2.1578 | 82.3597 | 64.1561 | 2035.1265
2029-10-10 20:00 | 4637.44 | 1.405 | 82.5402 | 64.1561 | 1359.0995
2029-10-11 21:00 | 3450.16 | 1.0407 | 82.2959 | 64.1561 | 1011.1421
2029-10-12 22:00 | 2992.4 | 1 | 68.3143 | 64.1561 | 876.9859
2029-10-13 23:00 | 2978.89 | 1 | 68.0947 | 64.1561 | 873.0265
2029-10-15 | -42.4812 | 0.69026 | 68.4241 | 64.1561 | -12.45
2029-10-16 01:00 | -232.035 | 1.1239 | 67.4165 | 64.1561 | -68.0027
2029-10-17 02:00 | -329.135 | 1.3426 | 66.99 | 64.1561 | -96.4599
2029-10-18 03:00 | -305.596 | 1.2671 | 66.8231 | 64.1561 | -89.5613
2029-10-19 04:00 | -238.23 | 1.1013 | 66.751 | 64.1561 | -69.8183
2029-10-20 05:00 | 1260.65 | 1 | 67.1354 | 64.1561 | 369.46
2029-10-21 06:00 | 2888.7 | 1 | 66.8168 | 64.1561 | 846.5944
2029-10-22 07:00 | 3051.82 | 1 | 66.9678 | 64.1561 | 894.4002
2029-10-23 08:00 | -91.9957 | 0.81338 | 67.3618 | 64.1561 | -26.9613
2029-10-24 09:00 | 2141.47 | 1 | 66.9943 | 64.1561 | 627.6029
2029-10-25 10:00 | 2859.51 | 1 | 66.9076 | 64.1561 | 838.0397
2029-10-26 11:00 | 3103.49 | 1 | 66.9573 | 64.1561 | 909.5431
2029-10-27 12:00 | 3146.89 | 1 | 66.9739 | 64.1561 | 922.2624
2029-10-28 13:00 | 3157.94 | 1 | 66.9623 | 64.1561 | 925.5009
2029-10-29 14:00 | 3305.33 | 1 | 66.9671 | 64.1561 | 968.6966
2029-10-30 15:00 | 3818.35 | 1.1788 | 80.4466 | 64.1561 | 1119.0479
2029-10-31 16:00 | 5309.3 | 1.7 | 79.9884 | 64.1561 | 1556.0022
2029-11-01 17:00 | 5567.77 | 1.79 | 80.1006 | 64.1561 | 1631.7523
2029-11-02 18:00 | 4648.49 | 1.4593 | 80.5033 | 64.1561 | 1362.3379
2029-11-03 19:00 | 3668.51 | 1.1558 | 80.4219 | 64.1561 | 1075.1342
2029-11-04 20:00 | 3018.79 | 1 | 67.2245 | 64.1561 | 884.72
2029-11-05 21:00 | 3038.74 | 1 | 67.1346 | 64.1561 | 890.5668
2029-11-06 22:00 | -468.951 | 1.7893 | 66.7768 | 64.1561 | -137.436
2029-11-07 23:00 | -831.556 | 2.606 | 66.1157 | 64.1561 | -243.705
2029-11-09 | -1021.94 | 3.0464 | 65.7738 | 64.1561 | -299.501
2029-11-10 01:00 | -1139.42 | 3.3243 | 65.5857 | 64.1561 | -333.931
2029-11-11 02:00 | -1132.65 | 3.2879 | 65.4376 | 64.1561 | -331.9469
2029-11-12 03:00 | -1015.67 | 2.9865 | 65.3195 | 64.1561 | -297.6635
2029-11-13 04:00 | -889.496 | 2.681 | 65.2847 | 64.1561 | -260.6855
2029-11-14 05:00 | -439.914 | 1.5227 | 65.3883 | 64.1561 | -128.9261
2029-11-15 06:00 | -140.02 | 0.83497 | 65.8372 | 64.1561 | -41.0358
2029-11-16 07:00 | 391.809 | 1 | 66.3936 | 64.1561 | 114.8279
2029-11-17 08:00 | 459.247 | 1 | 66.4219 | 64.1561 | 134.592
2029-11-18 09:00 | 2196.3 | 1 | 66.0115 | 64.1561 | 643.672
2029-11-19 10:00 | 2910.69 | 1 | 80.0214 | 64.1561 | 853.039
2029-11-20 11:00 | 3994.6 | 1.3056 | 78.8821 | 64.1561 | 1170.7017
2029-11-21 12:00 | 4842.25 | 1.5244 | 79.5559 | 64.1561 | 1419.1234
2029-11-22 13:00 | 5218.53 | 1.7013 | 79.3567 | 64.1561 | 1529.4002
2029-11-23 14:00 | 5983.81 | 1.9527 | 79.5402 | 64.1561 | 1753.6816
2029-11-24 15:00 | 7657.96 | 2.6083 | 79.2313 | 64.1561 | 2244.3265
2029-11-25 16:00 | 8097.33 | 2.6155 | 80.1732 | 64.1561 | 2373.0932
2029-11-26 17:00 | 7985.95 | 2.563 | 80.4921 | 64.1561 | 2340.4509
2029-11-27 18:00 | 6776.26 | 2.0806 | 81.2016 | 64.1561 | 1985.9258
2029-11-28 19:00 | 5530.26 | 1.6911 | 81.2663 | 64.1561 | 1620.7592
2029-11-29 20:00 | 3171.31 | 1 | 83.0121 | 64.1561 | 929.4192
2029-11-30 21:00 | 3144.04 | 1 | 67.3704 | 64.1561 | 921.4272
2029-12-01 22:00 | 0 | 0 | 67.9844 | 64.1561 | 0
2029-12-02 23:00 | -374.973 | 1.4993 | 66.5669 | 64.1561 | -109.8937
2029-12-04 | -535.918 | 1.861 | 66.1118 | 64.1561 | -157.0621
2029-12-05 01:00 | -685.015 | 2.2254 | 65.8434 | 64.1561 | -200.7581
2029-12-06 02:00 | -790.716 | 2.4764 | 65.6476 | 64.1561 | -231.736
2029-12-07 03:00 | -906.792 | 2.766 | 65.447 | 64.1561 | -265.7545
2029-12-08 04:00 | -948.291 | 2.8546 | 65.3135 | 64.1561 | -277.9167
2029-12-09 05:00 | -867.75 | 2.6376 | 65.2114 | 64.1561 | -254.3124
2029-12-10 06:00 | 85.6542 | 1 | 66.3895 | 64.1561 | 25.1028
2029-12-11 07:00 | 1795.55 | 1 | 66.0077 | 64.1561 | 526.2238
2029-12-12 08:00 | 2457.96 | 1 | 66.0536 | 64.1561 | 720.357
2029-12-13 09:00 | 3027.43 | 1 | 66.0741 | 64.1561 | 887.2521
2029-12-14 10:00 | 2961.84 | 1 | 80.1047 | 64.1561 | 868.0296
2029-12-15 11:00 | 4642.98 | 1.4738 | 79.3714 | 64.1561 | 1360.7231
2029-12-16 12:00 | 6239.49 | 2.109 | 78.8754 | 64.1561 | 1828.614
2029-12-17 13:00 | 6897.67 | 2.3342 | 79.1881 | 64.1561 | 2021.5075
2029-12-18 14:00 | 7786.11 | 2.5736 | 79.7221 | 64.1561 | 2281.8836
2029-12-19 15:00 | 8824.91 | 2.8882 | 80.0995 | 64.1561 | 2586.3258
2029-12-20 16:00 | 10104.1 | 3.3301 | 80.3284 | 64.1561 | 2961.2194
2029-12-21 17:00 | 8027.54 | 2.4455 | 81.6622 | 64.1561 | 2352.6397
2029-12-22 18:00 | 6411.75 | 1.8862 | 82.1237 | 64.1561 | 1879.0984
2029-12-23 19:00 | 4685.57 | 1.4279 | 81.5309 | 64.1561 | 1373.205
2029-12-24 20:00 | 3430.01 | 1.0686 | 81.0524 | 64.1561 | 1005.2367
2029-12-25 21:00 | 3129.18 | 1 | 83.749 | 64.1561 | 917.0721
2029-12-26 22:00 | 3012.94 | 1 | 67.3811 | 64.1561 | 883.0055
2029-12-27 23:00 | -605.377 | 2.1055 | 66.8821 | 64.1561 | -177.4185
2029-12-29 | -973.509 | 2.9462 | 66.2369 | 64.1561 | -285.3073
2029-12-30 01:00 | -1196.1 | 3.471 | 65.8657 | 64.1561 | -350.5423
2029-12-31 02:00 | -1272.42 | 3.6355 | 65.6415 | 64.1561 | -372.9095
2030-01-01 03:00 | -1280.47 | 3.6508 | 65.4443 | 64.1561 | -375.2687
2030-01-02 04:00 | -1386 | 3.938 | 65.2444 | 64.1561 | -406.1965
2030-01-03 05:00 | -1310.42 | 3.7173 | 65.1237 | 64.1561 | -384.0462
2030-01-04 06:00 | -503.185 | 1.6005 | 65.1801 | 64.1561 | -147.469
2030-01-05 07:00 | 0 | 1 | 66.4226 | 64.1561 | 0
2030-01-06 08:00 | -29.4233 | 0.66873 | 66.2858 | 64.1561 | -8.6231
2030-01-07 09:00 | 1849.78 | 1 | 65.9978 | 64.1561 | 542.117
2030-01-08 10:00 | 2749.97 | 1 | 83.4105 | 64.1561 | 805.9367
2030-01-09 11:00 | 3462.95 | 1.1667 | 78.4257 | 64.1561 | 1014.8905
2030-01-10 12:00 | 4923.31 | 1.5917 | 79.093 | 64.1561 | 1442.8797
2030-01-11 13:00 | 6176.17 | 2.1278 | 78.6099 | 64.1561 | 1810.0568
2030-01-12 14:00 | 6792.62 | 2.3156 | 79.0443 | 64.1561 | 1990.7204
2030-01-13 15:00 | 8098.82 | 2.729 | 79.4096 | 64.1561 | 2373.5298
2030-01-14 16:00 | 10758.4 | 3.4484 | 80.2906 | 64.1561 | 3152.9758
2030-01-15 17:00 | 9326.14 | 2.9836 | 80.8308 | 64.1561 | 2733.2218
2030-01-16 18:00 | 8063.01 | 2.5017 | 81.3817 | 64.1561 | 2363.035
2030-01-17 19:00 | 6474.86 | 1.945 | 81.8006 | 64.1561 | 1897.5941
2030-01-18 20:00 | 5344.94 | 1.5835 | 81.9108 | 64.1561 | 1566.4473
2030-01-19 21:00 | 4036.81 | 1.2656 | 81.0582 | 64.1561 | 1183.0722
2030-01-20 22:00 | 3115.91 | 1 | 81.4795 | 64.1561 | 913.1831
2030-01-21 23:00 | 0 | 0 | 68.1658 | 64.1561 | 0
2030-01-23 | -484.75 | 1.7191 | 66.603 | 64.1561 | -142.0662
2030-01-24 01:00 | -758.111 | 2.4191 | 66.1632 | 64.1561 | -222.1804
2030-01-25 02:00 | -1011.86 | 3.0328 | 65.865 | 64.1561 | -296.5469
2030-01-26 03:00 | -1099.03 | 3.2176 | 65.6257 | 64.1561 | -322.0939
2030-01-27 04:00 | -1142.91 | 3.3254 | 65.412 | 64.1561 | -334.9539
2030-01-28 05:00 | -1190.42 | 3.4469 | 65.277 | 64.1561 | -348.8777
2030-01-29 06:00 | -330.044 | 1.1664 | 65.4025 | 64.1561 | -96.7263
2030-01-30 07:00 | 1891.29 | 1 | 66.0583 | 64.1561 | 554.2824
2030-01-31 08:00 | 2701.21 | 1 | 66.0926 | 64.1561 | 791.6465
2030-02-01 09:00 | 3013.82 | 1 | 80.8899 | 64.1561 | 883.2635
2030-02-02 10:00 | 4867.18 | 1.5514 | 79.3095 | 64.1561 | 1426.4297
2030-02-03 11:00 | 5713.29 | 2.0077 | 78.4901 | 64.1561 | 1674.4
2030-02-04 12:00 | 6620.38 | 2.2071 | 79.3866 | 64.1561 | 1940.2419
2030-02-05 13:00 | 7100.97 | 2.3296 | 79.832 | 64.1561 | 2081.0889
2030-02-06 14:00 | 7824.36 | 2.6049 | 79.8825 | 64.1561 | 2293.0936
2030-02-07 15:00 | 8501.91 | 2.8103 | 80.2103 | 64.1561 | 2491.6639
2030-02-08 16:00 | 9607.31 | 3.0182 | 81.0451 | 64.1561 | 2815.6246
2030-02-09 17:00 | 8191.78 | 2.5577 | 81.416 | 64.1561 | 2400.7737
2030-02-10 18:00 | 7114.78 | 2.1137 | 82.1026 | 64.1561 | 2085.1362
2030-02-11 19:00 | 5523.54 | 1.7018 | 81.579 | 64.1561 | 1618.7898
2030-02-12 20:00 | 4583.83 | 1.4203 | 81.3531 | 64.1561 | 1343.388
2030-02-13 21:00 | 3699.36 | 1.1565 | 81.0777 | 64.1561 | 1084.1754
2030-02-14 22:00 | 3149.76 | 1 | 80.8647 | 64.1561 | 923.1035
2030-02-15 23:00 | 2778.38 | 1 | 67.548 | 64.1561 | 814.2628
2030-02-17 | -21.5627 | 0.64097 | 68.1028 | 64.1561 | -6.3194
2030-02-18 01:00 | -296.642 | 1.2926 | 66.7988 | 64.1561 | -86.9372
2030-02-19 02:00 | -380.254 | 1.4694 | 66.4211 | 64.1561 | -111.4414
2030-02-20 03:00 | -303.132 | 1.2571 | 66.3219 | 64.1561 | -88.8392
2030-02-21 04:00 | -289.003 | 1.2395 | 66.2059 | 64.1561 | -84.6984
2030-02-22 05:00 | 2220.31 | 1 | 66.464 | 64.1561 | 650.7086
2030-02-23 06:00 | 1909.51 | 1 | 66.7493 | 64.1561 | 559.6221
2030-02-24 07:00 | 2664.09 | 1 | 66.6334 | 64.1561 | 780.7677
2030-02-25 08:00 | 2937.85 | 1 | 85.6483 | 64.1561 | 860.9988
2030-02-26 09:00 | 4654.3 | 1.5048 | 79.5459 | 64.1561 | 1364.0407
2030-02-27 10:00 | 6559.33 | 2.2985 | 78.8691 | 64.1561 | 1922.3499
2030-02-28 11:00 | 8469.68 | 2.9364 | 79.3132 | 64.1561 | 2482.2182
2030-03-01 12:00 | 9686.57 | 3.2349 | 80.1686 | 64.1561 | 2838.8534
2030-03-02 13:00 | 10600.7 | 3.475 | 80.7894 | 64.1561 | 3106.7585
2030-03-03 14:00 | 11600.6 | 3.8384 | 81.0609 | 64.1561 | 3399.8003
2030-03-04 15:00 | 13639.9 | 4.4612 | 81.571 | 64.1561 | 3997.4601
2030-03-05 16:00 | 14104.2 | 4.5517 | 82.2178 | 64.1561 | 4133.533
2030-03-06 17:00 | 13691.6 | 4.4088 | 82.6115 | 64.1561 | 4012.6119
2030-03-07 18:00 | 11759.1 | 3.7004 | 83.1294 | 64.1561 | 3446.252
2030-03-08 19:00 | 10152.7 | 3.1566 | 83.29 | 64.1561 | 2975.4627
2030-03-09 20:00 | 7404.65 | 2.1969 | 83.8179 | 64.1561 | 2170.0887
2030-03-10 21:00 | 5948.82 | 1.8224 | 83.0947 | 64.1561 | 1743.427
2030-03-11 22:00 | 3539.04 | 1.068 | 82.9778 | 64.1561 | 1037.1902
2030-03-12 23:00 | 3181.8 | 1 | 88.5585 | 64.1561 | 932.4935
2030-03-14 | 3070.47 | 1 | 68.5557 | 64.1561 | 899.8659
2030-03-15 01:00 | 3103.92 | 1 | 68.3631 | 64.1561 | 909.6692
2030-03-16 02:00 | 3116.94 | 1 | 68.233 | 64.1561 | 913.4849
2030-03-17 03:00 | 3169.83 | 1 | 68.1049 | 64.1561 | 928.9855
2030-03-18 04:00 | 3153 | 1 | 68.0394 | 64.1561 | 924.0531
2030-03-19 05:00 | 3178.81 | 1 | 67.9557 | 64.1561 | 931.6172
2030-03-20 06:00 | 3230.62 | 1 | 85.0602 | 64.1561 | 946.8013
2030-03-21 07:00 | 4255.45 | 1.3517 | 80.9055 | 64.1561 | 1247.1493
2030-03-22 08:00 | 5339.33 | 1.6505 | 81.3354 | 64.1561 | 1564.8032
2030-03-23 09:00 | 7017.33 | 2.3217 | 80.6607 | 64.1561 | 2056.5764
2030-03-24 10:00 | 8656.93 | 2.9409 | 80.6292 | 64.1561 | 2537.0957
2030-03-25 11:00 | 10379.3 | 3.5169 | 80.999 | 64.1561 | 3041.8726
2030-03-26 12:00 | 11196.1 | 3.7457 | 81.5486 | 64.1561 | 3281.253
2030-03-27 13:00 | 12042.3 | 3.8746 | 82.3532 | 64.1561 | 3529.2497
2030-03-28 14:00 | 12659 | 4.0812 | 82.6482 | 64.1561 | 3709.9867
2030-03-29 15:00 | 14022.1 | 4.4291 | 83.178 | 64.1561 | 4109.4719
2030-03-30 16:00 | 13709.8 | 4.3796 | 83.3862 | 64.1561 | 4017.9458
2030-03-31 17:00 | 13367.7 | 4.139 | 83.9803 | 64.1561 | 3917.6861
2030-04-01 18:00 | 11152.3 | 3.5178 | 83.8949 | 64.1561 | 3268.4165
2030-04-02 19:00 | 9757.23 | 2.9957 | 84.1421 | 64.1561 | 2859.5618
2030-04-03 20:00 | 7194.3 | 2.1437 | 84.3914 | 64.1561 | 2108.4412
2030-04-04 21:00 | 5992.87 | 1.7189 | 84.5654 | 64.1561 | 1756.3368
2030-04-05 22:00 | 3686.87 | 1.1122 | 83.5919 | 64.1561 | 1080.5149
2030-04-06 23:00 | 3201.76 | 1 | 86.1539 | 64.1561 | 938.3432
2030-04-08 | 3087.79 | 1 | 69.1448 | 64.1561 | 904.9419
2030-04-09 01:00 | 3124.43 | 1 | 68.925 | 64.1561 | 915.68
2030-04-10 02:00 | 3177.24 | 1 | 68.7629 | 64.1561 | 931.1571
2030-04-11 03:00 | 3141.81 | 1 | 68.6389 | 64.1561 | 920.7736
2030-04-12 04:00 | 3110.98 | 1 | 68.5531 | 64.1561 | 911.7382
2030-04-13 05:00 | 3192.42 | 1 | 68.443 | 64.1561 | 935.6059
2030-04-14 06:00 | 3198.57 | 1 | 68.384 | 64.1561 | 937.4083
2030-04-15 07:00 | 3171.34 | 1 | 82.1464 | 64.1561 | 929.428
2030-04-16 08:00 | 3819.33 | 1.1617 | 81.8951 | 64.1561 | 1119.3351
2030-04-17 09:00 | 5749.4 | 1.887 | 80.977 | 64.1561 | 1684.9828
2030-04-18 10:00 | 7324.35 | 2.4513 | 80.9691 | 64.1561 | 2146.5551
2030-04-19 11:00 | 8807.04 | 3.0415 | 80.8867 | 64.1561 | 2581.0886
2030-04-20 12:00 | 10645.8 | 3.5897 | 81.4685 | 64.1561 | 3119.976
2030-04-21 13:00 | 11159.9 | 3.6892 | 82.0975 | 64.1561 | 3270.6438
2030-04-22 14:00 | 11434 | 3.7212 | 82.5907 | 64.1561 | 3350.9746
2030-04-23 15:00 | 12559.3 | 4.062 | 82.8741 | 64.1561 | 3680.7675
2030-04-24 16:00 | 11276.4 | 3.6659 | 83.0943 | 64.1561 | 3304.7866
2030-04-25 17:00 | 11186.3 | 3.6904 | 82.9669 | 64.1561 | 3278.3809
2030-04-26 18:00 | 9627.99 | 3.0977 | 83.3216 | 64.1561 | 2821.6853
2030-04-27 19:00 | 8211.55 | 2.5141 | 83.8602 | 64.1561 | 2406.5677
2030-04-28 20:00 | 6130.57 | 1.7688 | 84.4886 | 64.1561 | 1796.6927
2030-04-29 21:00 | 4895.2 | 1.4541 | 83.7926 | 64.1561 | 1434.6415
2030-04-30 22:00 | 3116.19 | 1 | 86.819 | 64.1561 | 913.2651
2030-05-01 23:00 | 3130.78 | 1 | 69.2331 | 64.1561 | 917.541
2030-05-03 | 3157.2 | 1 | 68.9962 | 64.1561 | 925.284
2030-05-04 01:00 | 3091.3 | 1 | 68.8517 | 64.1561 | 905.9706
2030-05-05 02:00 | 3133.63 | 1 | 68.7093 | 64.1561 | 918.3763
2030-05-06 03:00 | 3182.12 | 1 | 68.5854 | 64.1561 | 932.5873
2030-05-07 04:00 | 3186.55 | 1 | 68.5238 | 64.1561 | 933.8856
2030-05-08 05:00 | 3231.3 | 1 | 68.4486 | 64.1561 | 947.0005
2030-05-09 06:00 | 3261.5 | 1 | 87.3098 | 64.1561 | 955.8513
2030-05-10 07:00 | 4049.25 | 1.2445 | 81.8362 | 64.1561 | 1186.718
2030-05-11 08:00 | 4315.58 | 1.3614 | 81.5802 | 64.1561 | 1264.7716
2030-05-12 09:00 | 5510.63 | 1.7478 | 81.5601 | 64.1561 | 1615.0062
2030-05-13 10:00 | 6299.43 | 2.261 | 80.2773 | 64.1561 | 1846.1807
2030-05-14 11:00 | 8485.31 | 2.9499 | 80.7911 | 64.1561 | 2486.7989
2030-05-15 12:00 | 9811.21 | 3.3435 | 81.3418 | 64.1561 | 2875.3818
2030-05-16 13:00 | 10415.7 | 3.4486 | 82.0092 | 64.1561 | 3052.5403
2030-05-17 14:00 | 11000.8 | 3.6371 | 82.2917 | 64.1561 | 3224.0162
2030-05-18 15:00 | 12898.2 | 4.1721 | 82.7821 | 64.1561 | 3780.0893
2030-05-19 16:00 | 13881 | 4.4292 | 83.3394 | 64.1561 | 4068.1195
2030-05-20 17:00 | 13358 | 4.3483 | 83.4594 | 64.1561 | 3914.8434
2030-05-21 18:00 | 11696.1 | 3.7153 | 83.9527 | 64.1561 | 3427.7885
2030-05-22 19:00 | 9578.64 | 3.0675 | 83.851 | 64.1561 | 2807.2223
2030-05-23 20:00 | 7190.37 | 2.2094 | 84.2227 | 64.1561 | 2107.2894
2030-05-24 21:00 | 5902 | 1.8227 | 83.8499 | 64.1561 | 1729.7055
2030-05-25 22:00 | 3656.12 | 1.1329 | 83.521 | 64.1561 | 1071.503
2030-05-26 23:00 | 3049.57 | 1 | 89.2162 | 64.1561 | 893.7407
2030-05-28 | 3071.07 | 1 | 69.4113 | 64.1561 | 900.0418
2030-05-29 01:00 | 2994.59 | 1 | 69.2346 | 64.1561 | 877.6277
2030-05-30 02:00 | -60.8666 | 0.72581 | 69.4675 | 64.1561 | -17.8382
2030-05-31 03:00 | -398.595 | 1.5299 | 68.2825 | 64.1561 | -116.8167
2030-06-01 04:00 | -762.628 | 2.4035 | 67.7094 | 64.1561 | -223.5042
2030-06-02 05:00 | -877.429 | 2.6359 | 67.3719 | 64.1561 | -257.1491
2030-06-03 06:00 | 548.512 | 1 | 68.2971 | 64.1561 | 160.753
2030-06-04 07:00 | 3015.11 | 1 | 84.1214 | 64.1561 | 883.6415
2030-06-05 08:00 | 3026.85 | 1 | 81.5587 | 64.1561 | 887.0822
2030-06-06 09:00 | 4480.13 | 1.4154 | 81.0746 | 64.1561 | 1312.9965
2030-06-07 10:00 | 6009.5 | 1.9941 | 80.6798 | 64.1561 | 1761.2106
2030-06-08 11:00 | 7036.37 | 2.3719 | 80.7909 | 64.1561 | 2062.1565
2030-06-09 12:00 | 7859.92 | 2.5395 | 81.5506 | 64.1561 | 2303.5152
2030-06-10 13:00 | 8760.83 | 2.8664 | 81.6048 | 64.1561 | 2567.5458
2030-06-11 14:00 | 9366.34 | 3.0276 | 82.0154 | 64.1561 | 2745.0033
2030-06-12 15:00 | 9678.2 | 3.1214 | 82.27 | 64.1561 | 2836.4004
2030-06-13 16:00 | 12320 | 3.9827 | 82.416 | 64.1561 | 3610.6356
2030-06-14 17:00 | 10828.3 | 3.4789 | 82.9308 | 64.1561 | 3173.4615
2030-06-15 18:00 | 9641.59 | 3.0584 | 83.208 | 64.1561 | 2825.6711
2030-06-16 19:00 | 7642.99 | 2.4389 | 83.0944 | 64.1561 | 2239.9393
2030-06-17 20:00 | 6162.34 | 1.9082 | 83.3081 | 64.1561 | 1806.0036
2030-06-18 21:00 | 5066.79 | 1.5547 | 83.2135 | 64.1561 | 1484.9296
2030-06-19 22:00 | 4502.02 | 1.387 | 82.9095 | 64.1561 | 1319.4118
2030-06-20 23:00 | 3039.54 | 1 | 69.2975 | 64.1561 | 890.8012
2030-06-22 | 1378.33 | 1 | 69.4029 | 64.1561 | 403.9486
2030-06-23 01:00 | 251.767 | 1 | 69.3027 | 64.1561 | 73.7856
2030-06-24 02:00 | -497.241 | 1.8048 | 67.9434 | 64.1561 | -145.727
2030-06-25 03:00 | -601.325 | 1.9746 | 67.5245 | 64.1561 | -176.231
2030-06-26 04:00 | -951.125 | 2.8676 | 67.1572 | 64.1561 | -278.7472
2030-06-27 05:00 | -772.52 | 2.3387 | 66.9291 | 64.1561 | -226.4033
2030-06-28 06:00 | 1924.44 | 1 | 67.6062 | 64.1561 | 563.9977
2030-06-29 07:00 | 2935.55 | 1 | 80.9973 | 64.1561 | 860.3248
2030-06-30 08:00 | 3345.44 | 1.0927 | 80.3899 | 64.1561 | 980.4517
2030-07-01 09:00 | 5108.84 | 1.6461 | 80.6546 | 64.1561 | 1497.2532
2030-07-02 10:00 | 6652.87 | 2.216 | 80.5106 | 64.1561 | 1949.7637
2030-07-03 11:00 | 8222.59 | 2.8068 | 80.5571 | 64.1561 | 2409.8032
2030-07-04 12:00 | 9529.25 | 3.0852 | 81.5209 | 64.1561 | 2792.7475
2030-07-05 13:00 | 10060.9 | 3.2602 | 81.8666 | 64.1561 | 2948.5587
2030-07-06 14:00 | 10668.6 | 3.4724 | 82.118 | 64.1561 | 3126.658
2030-07-07 15:00 | 11120 | 3.6458 | 82.3008 | 64.1561 | 3258.9503
2030-07-08 16:00 | 13497.9 | 4.399 | 82.6034 | 64.1561 | 3955.844
2030-07-09 17:00 | 12400.5 | 3.9938 | 83.1973 | 64.1561 | 3634.2278
2030-07-10 18:00 | 10830.3 | 3.4575 | 83.4701 | 64.1561 | 3174.0476
2030-07-11 19:00 | 8809.77 | 2.7969 | 83.508 | 64.1561 | 2581.8887
2030-07-12 20:00 | 7392.48 | 2.3251 | 83.47 | 64.1561 | 2166.522
2030-07-13 21:00 | 5875.57 | 1.8331 | 83.3815 | 64.1561 | 1721.9596
2030-07-14 22:00 | 5221.32 | 1.6462 | 82.9627 | 64.1561 | 1530.2178
2030-07-15 23:00 | 3234.96 | 1 | 85.6196 | 64.1561 | 948.0732
2030-07-17 | 3135.02 | 1 | 69.2257 | 64.1561 | 918.7837
2030-07-18 01:00 | 3102.43 | 1 | 69.0186 | 64.1561 | 909.2325
2030-07-19 02:00 | 3070.08 | 1 | 68.8968 | 64.1561 | 899.7516
2030-07-20 03:00 | 3135.48 | 1 | 68.7785 | 64.1561 | 918.9185
2030-07-21 04:00 | 3143.59 | 1 | 68.6763 | 64.1561 | 921.2953
2030-07-22 05:00 | 3184.3 | 1 | 89.9615 | 64.1561 | 933.2262
2030-07-23 06:00 | 3213.67 | 1 | 83.1145 | 64.1561 | 941.8337
2030-07-24 07:00 | 4273.56 | 1.3295 | 81.8349 | 64.1561 | 1252.4568
2030-07-25 08:00 | 5256.07 | 1.618 | 82.0542 | 64.1561 | 1540.4021
2030-07-26 09:00 | 7090.04 | 2.3201 | 81.4408 | 64.1561 | 2077.8856
2030-07-27 10:00 | 9043.82 | 3.0316 | 81.4212 | 64.1561 | 2650.482
2030-07-28 11:00 | 10704.2 | 3.6122 | 81.7211 | 64.1561 | 3137.0913
2030-07-29 12:00 | 11058.3 | 3.6411 | 82.4229 | 64.1561 | 3240.8678
2030-07-30 13:00 | 11587.1 | 3.7633 | 82.8789 | 64.1561 | 3395.8438
2030-07-31 14:00 | 12637.8 | 4.1145 | 83.1129 | 64.1561 | 3703.7736
2030-08-01 15:00 | 14407.6 | 4.6798 | 83.4457 | 64.1561 | 4222.4507
2030-08-02 16:00 | 15027.3 | 4.8686 | 83.866 | 64.1561 | 4404.0669
2030-08-03 17:00 | 14857.8 | 4.7514 | 84.3506 | 64.1561 | 4354.3913
2030-08-04 18:00 | 12801.4 | 4.0897 | 84.6016 | 64.1561 | 3751.72
2030-08-05 19:00 | 11274.9 | 3.5405 | 84.8061 | 64.1561 | 3304.347
2030-08-06 20:00 | 8723.34 | 2.6556 | 85.1056 | 64.1561 | 2556.5586
2030-08-07 21:00 | 7349.22 | 2.2675 | 84.6405 | 64.1561 | 2153.8438
2030-08-08 22:00 | 5126.61 | 1.5001 | 85.024 | 64.1561 | 1502.4611
2030-08-09 23:00 | 4093.07 | 1.2705 | 83.8364 | 64.1561 | 1199.5604
2030-08-11 | 3150.08 | 1 | 83.2927 | 64.1561 | 923.1973
2030-08-12 01:00 | 3180.8 | 1 | 88.2001 | 64.1561 | 932.2005
2030-08-13 02:00 | 3127.9 | 1 | 89.4092 | 64.1561 | 916.697
2030-08-14 03:00 | 3171.04 | 1 | 90.2128 | 64.1561 | 929.3401
2030-08-15 04:00 | 3082.23 | 1 | 69.3133 | 64.1561 | 903.3124
2030-08-16 05:00 | 3108.32 | 1 | 85.649 | 64.1561 | 910.9587
2030-08-17 06:00 | 3628.3 | 1.1159 | 82.5454 | 64.1561 | 1063.3498
2030-08-18 07:00 | 5021.57 | 1.5957 | 82.1153 | 64.1561 | 1471.6769
2030-08-19 08:00 | 5920.68 | 1.8795 | 82.2545 | 64.1561 | 1735.18
2030-08-20 09:00 | 7716.84 | 2.5962 | 81.7011 | 64.1561 | 2261.5826
2030-08-21 10:00 | 9112.6 | 3.1331 | 81.725 | 64.1561 | 2670.6394
2030-08-22 11:00 | 10298.5 | 3.5037 | 82.1606 | 64.1561 | 3018.1924
2030-08-23 12:00 | 11368.7 | 3.7405 | 82.876 | 64.1561 | 3331.8371
2030-08-24 13:00 | 12012 | 3.8952 | 83.3687 | 64.1561 | 3520.3697
2030-08-25 14:00 | 12694.9 | 4.1171 | 83.6507 | 64.1561 | 3720.5079
2030-08-26 15:00 | 14979 | 4.8619 | 83.8896 | 64.1561 | 4389.9116
2030-08-27 16:00 | 15432 | 4.969 | 84.4131 | 64.1561 | 4522.6728
2030-08-28 17:00 | 15152.7 | 4.829 | 84.8745 | 64.1561 | 4440.818
2030-08-29 18:00 | 13236.2 | 4.2169 | 85.0916 | 64.1561 | 3879.1473
2030-08-30 19:00 | 11249.2 | 3.5457 | 85.2102 | 64.1561 | 3296.8151
2030-08-31 20:00 | 8419.09 | 2.56 | 85.5229 | 64.1561 | 2467.3917
2030-09-01 21:00 | 6867.66 | 2.085 | 85.177 | 64.1561 | 2012.7125
2030-09-02 22:00 | 4217.51 | 1.2591 | 85.0413 | 64.1561 | 1236.0302
2030-09-03 23:00 | 3106.38 | 1 | 86.1602 | 64.1561 | 910.3901
2030-09-05 | 3070.04 | 1 | 70.2869 | 64.1561 | 899.7399
2030-09-06 01:00 | 3063.66 | 1 | 70.0219 | 64.1561 | 897.8701
2030-09-07 02:00 | 3076.84 | 1 | 69.8317 | 64.1561 | 901.7328
2030-09-08 03:00 | 3056.08 | 1 | 69.6604 | 64.1561 | 895.6486
2030-09-09 04:00 | 3190.17 | 1 | 69.4961 | 64.1561 | 934.9465
2030-09-10 05:00 | 3183.39 | 1 | 69.4035 | 64.1561 | 932.9595
2030-09-11 06:00 | 3076.4 | 1 | 84.7287 | 64.1561 | 901.6038
2030-09-12 07:00 | 4552.24 | 1.3469 | 83.1805 | 64.1561 | 1334.1298
2030-09-13 08:00 | 5537.3 | 1.6236 | 83.3972 | 64.1561 | 1622.8224
2030-09-14 09:00 | 7569.11 | 2.4022 | 82.5178 | 64.1561 | 2218.2872
2030-09-15 10:00 | 9543.06 | 3.1663 | 82.2699 | 64.1561 | 2796.7948
2030-09-16 11:00 | 11217.8 | 3.7649 | 82.5218 | 64.1561 | 3287.6126
2030-09-17 12:00 | 12067.4 | 3.9913 | 83.1143 | 64.1561 | 3536.6058
2030-09-18 13:00 | 12863.6 | 4.1668 | 83.711 | 64.1561 | 3769.949
2030-09-19 14:00 | 13501.8 | 4.3853 | 84.0028 | 64.1561 | 3956.987
2030-09-20 15:00 | 15216.5 | 4.9522 | 84.255 | 64.1561 | 4459.5159
2030-09-21 16:00 | 15830.5 | 5.1644 | 84.602 | 64.1561 | 4639.4616
2030-09-22 17:00 | 15548.4 | 5.0475 | 84.9821 | 64.1561 | 4556.7862
2030-09-23 18:00 | 12352.4 | 4.0251 | 85.1579 | 64.1561 | 3620.1311
2030-09-24 19:00 | 9867.09 | 2.9244 | 86.1895 | 64.1561 | 2891.7586
2030-09-25 20:00 | 7157.16 | 2.0692 | 86.2377 | 64.1561 | 2097.5565
2030-09-26 21:00 | 5899.22 | 1.7081 | 85.7932 | 64.1561 | 1728.8907
2030-09-27 22:00 | 3396.38 | 1.0448 | 84.6257 | 64.1561 | 995.3807
2030-09-28 23:00 | 3090.46 | 1 | 89.0413 | 64.1561 | 905.7244
2030-09-30 | 2983.67 | 1 | 70.3264 | 64.1561 | 874.4274
2030-10-01 01:00 | 2812.87 | 1 | 70.1353 | 64.1561 | 824.3708
2030-10-02 02:00 | -16.0606 | 0.60896 | 70.6251 | 64.1561 | -4.7069
2030-10-03 03:00 | -134.412 | 0.86117 | 69.499 | 64.1561 | -39.3923
2030-10-04 04:00 | -368.123 | 1.4363 | 68.7733 | 64.1561 | -107.8862
2030-10-05 05:00 | -171.162 | 0.89738 | 68.7641 | 64.1561 | -50.1626
2030-10-06 06:00 | 494.359 | 1 | 69.1938 | 64.1561 | 144.8823
2030-10-07 07:00 | 2660.42 | 1 | 68.5637 | 64.1561 | 779.6921
2030-10-08 08:00 | 3100.72 | 1 | 68.6271 | 64.1561 | 908.7313
2030-10-09 09:00 | 3072.73 | 1 | 84.5548 | 64.1561 | 900.5283
2030-10-10 10:00 | 4185.84 | 1.3289 | 81.7829 | 64.1561 | 1226.7486
2030-10-11 11:00 | 5618.27 | 1.7944 | 81.8293 | 64.1561 | 1646.5524
2030-10-12 12:00 | 6501.4 | 2.0779 | 82.0279 | 64.1561 | 1905.3723
2030-10-13 13:00 | 7007.82 | 2.2682 | 82.0374 | 64.1561 | 2053.7893
2030-10-14 14:00 | 7952.82 | 2.5932 | 82.0975 | 64.1561 | 2330.7415
2030-10-15 15:00 | 9824.43 | 3.2377 | 82.1622 | 64.1561 | 2879.2562
2030-10-16 16:00 | 10263.6 | 3.3598 | 82.5652 | 64.1561 | 3007.9642
2030-10-17 17:00 | 10124.7 | 3.2967 | 82.8631 | 64.1561 | 2967.2567
2030-10-18 18:00 | 8521.38 | 2.7509 | 83.1158 | 64.1561 | 2497.37
2030-10-19 19:00 | 6763.75 | 2.1415 | 83.3041 | 64.1561 | 1982.2594
2030-10-20 20:00 | 4071.34 | 1.2587 | 83.4361 | 64.1561 | 1193.192
2030-10-21 21:00 | 3114.81 | 1 | 85.5002 | 64.1561 | 912.8607
2030-10-22 22:00 | 2786.89 | 1 | 69.4542 | 64.1561 | 816.7568
2030-10-23 23:00 | -171.927 | 1.0058 | 69.2338 | 64.1561 | -50.3868
2030-10-25 | -692.168 | 2.2493 | 68.2066 | 64.1561 | -202.8544
2030-10-26 01:00 | -1291.6 | 3.7016 | 67.6745 | 64.1561 | -378.5306
2030-10-27 02:00 | -1427.56 | 3.944 | 67.3487 | 64.1561 | -418.3765
2030-10-28 03:00 | -1574.54 | 4.3163 | 67.0918 | 64.1561 | -461.4521
2030-10-29 04:00 | -1576.62 | 4.3017 | 66.8484 | 64.1561 | -462.0617
2030-10-30 05:00 | -1219.66 | 3.3802 | 66.7002 | 64.1561 | -357.4471
2030-10-31 06:00 | -629.832 | 1.9303 | 66.7309 | 64.1561 | -184.5855
2030-11-01 07:00 | 1891.76 | 1 | 67.5185 | 64.1561 | 554.4201
2030-11-02 08:00 | 3169.66 | 1 | 67.4448 | 64.1561 | 928.9356
2030-11-03 09:00 | 3178.75 | 1 | 83.4314 | 64.1561 | 931.5997
2030-11-04 10:00 | 4773.61 | 1.5112 | 80.8854 | 64.1561 | 1399.007
2030-11-05 11:00 | 6412.13 | 2.1055 | 80.6949 | 64.1561 | 1879.2098
2030-11-06 12:00 | 7351.43 | 2.4218 | 81.004 | 64.1561 | 2154.4915
2030-11-07 13:00 | 7890.85 | 2.569 | 81.4292 | 64.1561 | 2312.5799
2030-11-08 14:00 | 8971.58 | 2.8689 | 81.8688 | 64.1561 | 2629.3106
2030-11-09 15:00 | 10799 | 3.5534 | 81.7994 | 64.1561 | 3164.8745
2030-11-10 16:00 | 11477.2 | 3.8008 | 82.1106 | 64.1561 | 3363.6353
2030-11-11 17:00 | 11290.9 | 3.7725 | 82.3226 | 64.1561 | 3309.0361
2030-11-12 18:00 | 9916.04 | 3.2479 | 82.7675 | 64.1561 | 2906.1045
2030-11-13 19:00 | 7788.74 | 2.531 | 82.8902 | 64.1561 | 2282.6544
2030-11-14 20:00 | 5222.1 | 1.6341 | 83.2021 | 64.1561 | 1530.4464
2030-11-15 21:00 | 3688.56 | 1.1639 | 82.7673 | 64.1561 | 1081.0102
2030-11-16 22:00 | 3052.4 | 1 | 69.3081 | 64.1561 | 894.5701
2030-11-17 23:00 | 0 | 0 | 69.7756 | 64.1561 | 0
2030-11-19 | -551.741 | 1.8431 | 68.085 | 64.1561 | -161.6993
2030-11-20 01:00 | -858.648 | 2.627 | 67.5987 | 64.1561 | -251.6449
2030-11-21 02:00 | -1080.38 | 3.1424 | 67.2783 | 64.1561 | -316.6281
2030-11-22 03:00 | -1420.87 | 3.9912 | 66.9947 | 64.1561 | -416.4159
2030-11-23 04:00 | -1687.09 | 4.6258 | 66.7113 | 64.1561 | -494.4373
2030-11-24 05:00 | -1793.26 | 4.8602 | 66.4942 | 64.1561 | -525.5526
2030-11-25 06:00 | -637.8 | 1.8277 | 66.3969 | 64.1561 | -186.9207
2030-11-26 07:00 | 2503.87 | 1 | 67.1463 | 64.1561 | 733.8119
2030-11-27 08:00 | 3136.57 | 1 | 67.3012 | 64.1561 | 919.2379
2030-11-28 09:00 | 3267.97 | 1 | 84.9817 | 64.1561 | 957.7475
2030-11-29 10:00 | 4853.99 | 1.4883 | 81.1063 | 64.1561 | 1422.564
2030-11-30 11:00 | 6516.91 | 2.0634 | 80.9849 | 64.1561 | 1909.9178
2030-12-01 12:00 | 7593.17 | 2.4313 | 81.209 | 64.1561 | 2225.3385
2030-12-02 13:00 | 8664.01 | 2.7627 | 81.5581 | 64.1561 | 2539.1707
2030-12-03 14:00 | 9260.19 | 2.961 | 81.828 | 64.1561 | 2713.8938
2030-12-04 15:00 | 10012.1 | 3.1518 | 82.2939 | 64.1561 | 2934.2569
2030-12-05 16:00 | 12504.4 | 4.0613 | 82.174 | 64.1561 | 3664.6779
2030-12-06 17:00 | 11097 | 3.6367 | 82.5426 | 64.1561 | 3252.2097
2030-12-07 18:00 | 9587.67 | 3.0916 | 82.8963 | 64.1561 | 2809.8687
2030-12-08 19:00 | 7945.88 | 2.5071 | 83.1135 | 64.1561 | 2328.7076
2030-12-09 20:00 | 6009.7 | 2.0368 | 82.1409 | 64.1561 | 1761.2692
2030-12-10 21:00 | 4813.29 | 1.6066 | 82.0984 | 64.1561 | 1410.6361
2030-12-11 22:00 | 3744.91 | 1.263 | 81.7053 | 64.1561 | 1097.5248
2030-12-12 23:00 | 2838.53 | 1 | 69.1869 | 64.1561 | 831.891
2030-12-14 | -143.155 | 0.93019 | 69.0185 | 64.1561 | -41.9546
2030-12-15 01:00 | -667.932 | 2.201 | 67.9441 | 64.1561 | -195.7515
2030-12-16 02:00 | -1305.16 | 3.7513 | 67.4239 | 64.1561 | -382.5046
2030-12-17 03:00 | -1747.38 | 4.784 | 67.0652 | 64.1561 | -512.1065
2030-12-18 04:00 | -1978.4 | 5.3167 | 66.7397 | 64.1561 | -579.8118
2030-12-19 05:00 | -2102.74 | 5.6134 | 66.4741 | 64.1561 | -616.2523
2030-12-20 06:00 | -1106.23 | 2.9832 | 66.3027 | 64.1561 | -324.204
2030-12-21 07:00 | 1293.82 | 1 | 67.3906 | 64.1561 | 379.1812
2030-12-22 08:00 | 2631.93 | 1 | 67.2684 | 64.1561 | 771.3425
2030-12-23 09:00 | 3003.05 | 1 | 81.1729 | 64.1561 | 880.1071
2030-12-24 10:00 | 4905.12 | 1.5751 | 80.4187 | 64.1561 | 1437.5488
2030-12-25 11:00 | 6081.87 | 2.0521 | 80.1169 | 64.1561 | 1782.4201
2030-12-26 12:00 | 6754.07 | 2.2695 | 80.4861 | 64.1561 | 1979.4225
2030-12-27 13:00 | 7624.07 | 2.5237 | 80.8989 | 64.1561 | 2234.3944
2030-12-28 14:00 | 8196.69 | 2.7928 | 80.8077 | 64.1561 | 2402.2127
2030-12-29 15:00 | 8826.49 | 3.0428 | 80.9112 | 64.1561 | 2586.7889
2030-12-30 16:00 | 11229.7 | 3.874 | 81.1048 | 64.1561 | 3291.1002
2030-12-31 17:00 | 10355.3 | 3.5926 | 81.4665 | 64.1561 | 3034.8389
2031-01-01 18:00 | 9187.87 | 3.0927 | 82.0007 | 64.1561 | 2692.6989
2031-01-02 19:00 | 7350.57 | 2.4513 | 82.1174 | 64.1561 | 2154.2394
2031-01-03 20:00 | 5952.65 | 1.9476 | 82.2179 | 64.1561 | 1744.5495
2031-01-04 21:00 | 4710.2 | 1.5448 | 82.0207 | 64.1561 | 1380.4234
2031-01-05 22:00 | 4046.51 | 1.2978 | 82.0454 | 64.1561 | 1185.915
2031-01-06 23:00 | 3057.32 | 1 | 68.9222 | 64.1561 | 896.012
2031-01-08 | 3050.4 | 1 | 68.7096 | 64.1561 | 893.984
2031-01-09 01:00 | 97.5902 | 1 | 69.292 | 64.1561 | 28.6009
2031-01-10 02:00 | -73.7186 | 0.76534 | 68.5356 | 64.1561 | -21.6048
2031-01-11 03:00 | -245.857 | 1.1493 | 67.8137 | 64.1561 | -72.0536
2031-01-12 04:00 | -534.726 | 1.8599 | 67.3301 | 64.1561 | -156.7127
2031-01-13 05:00 | 1628.17 | 1 | 67.8805 | 64.1561 | 477.1695
2031-01-14 06:00 | 3070.08 | 1 | 67.6147 | 64.1561 | 899.7516
2031-01-15 07:00 | 3129.42 | 1 | 83.9928 | 64.1561 | 917.1425
2031-01-16 08:00 | 3243.43 | 1.0133 | 81.1359 | 64.1561 | 950.5555
2031-01-17 09:00 | 4963.37 | 1.5621 | 81.1089 | 64.1561 | 1454.6202
2031-01-18 10:00 | 6799.46 | 2.1853 | 81.095 | 64.1561 | 1992.725
2031-01-19 11:00 | 8742.54 | 2.7899 | 81.5059 | 64.1561 | 2562.1856
2031-01-20 12:00 | 10147.7 | 3.1753 | 82.1232 | 64.1561 | 2973.9973
2031-01-21 13:00 | 10959.7 | 3.4154 | 82.5843 | 64.1561 | 3211.971
2031-01-22 14:00 | 12440.5 | 3.842 | 83.0706 | 64.1561 | 3645.9506
2031-01-23 15:00 | 14317.4 | 4.5402 | 83.1626 | 64.1561 | 4196.0157
2031-01-24 16:00 | 14699.8 | 4.7664 | 83.3873 | 64.1561 | 4308.0861
2031-01-25 17:00 | 14767.4 | 4.754 | 83.8351 | 64.1561 | 4327.8977
2031-01-26 18:00 | 13020.6 | 4.1702 | 84.1712 | 64.1561 | 3815.9612
2031-01-27 19:00 | 11288.2 | 3.557 | 84.4328 | 64.1561 | 3308.2449
2031-01-28 20:00 | 8904.84 | 2.7321 | 84.7014 | 64.1561 | 2609.751
2031-01-29 21:00 | 7682.11 | 2.3546 | 84.4637 | 64.1561 | 2251.4042
2031-01-30 22:00 | 5696.92 | 1.7018 | 84.5536 | 64.1561 | 1669.6024
2031-01-31 23:00 | 4589.95 | 1.2812 | 85.1185 | 64.1561 | 1345.1816
2031-02-02 | 3541.55 | 1.0752 | 83.6677 | 64.1561 | 1037.9258
2031-02-03 01:00 | 3173.44 | 1 | 84.3368 | 64.1561 | 930.0435
2031-02-04 02:00 | 3108.8 | 1 | 85.6944 | 64.1561 | 911.0993
2031-02-05 03:00 | 3122.24 | 1 | 84.5518 | 64.1561 | 915.0382
2031-02-06 04:00 | 3178.81 | 1 | 82.7415 | 64.1561 | 931.6172
2031-02-07 05:00 | 4068.93 | 1.2709 | 82.3967 | 64.1561 | 1192.4857
2031-02-08 06:00 | 4682.4 | 1.4879 | 82.2028 | 64.1561 | 1372.276
2031-02-09 07:00 | 5807.66 | 1.842 | 82.2835 | 64.1561 | 1702.0571
2031-02-10 08:00 | 6255.38 | 1.9733 | 82.5011 | 64.1561 | 1833.2709
2031-02-11 09:00 | 8068.59 | 2.6984 | 81.925 | 64.1561 | 2364.6703
2031-02-12 10:00 | 9494.08 | 3.1869 | 82.165 | 64.1561 | 2782.4402
2031-02-13 11:00 | 10948 | 3.6735 | 82.4935 | 64.1561 | 3208.5421
2031-02-14 12:00 | 11737 | 4.0755 | 82.4613 | 64.1561 | 3439.7751
2031-02-15 13:00 | 12322.4 | 4.1027 | 83.2605 | 64.1561 | 3611.339
2031-02-16 14:00 | 13991.9 | 4.5322 | 83.8683 | 64.1561 | 4100.6211
2031-02-17 15:00 | 15437.8 | 5.1019 | 84.0011 | 64.1561 | 4524.3726
2031-02-18 16:00 | 15577.3 | 5.0421 | 84.6584 | 64.1561 | 4565.256
2031-02-19 17:00 | 15101.1 | 4.875 | 84.9666 | 64.1561 | 4425.6955
2031-02-20 18:00 | 14067.8 | 4.4502 | 85.3846 | 64.1561 | 4122.8652
2031-02-21 19:00 | 12236.1 | 3.7881 | 85.7218 | 64.1561 | 3586.0469
2031-02-22 20:00 | 9374.03 | 2.8751 | 85.7485 | 64.1561 | 2747.257
2031-02-23 21:00 | 8124.13 | 2.4638 | 85.5548 | 64.1561 | 2380.9475
2031-02-24 22:00 | 5566.28 | 1.7049 | 85.1358 | 64.1561 | 1631.3156
2031-02-25 23:00 | 4627.16 | 1.3956 | 84.8965 | 64.1561 | 1356.0867
2031-02-27 | 4031.14 | 1.25 | 84.1715 | 64.1561 | 1181.4105
2031-02-28 01:00 | 3356.4 | 1.0607 | 83.6537 | 64.1561 | 983.6637
2031-03-01 02:00 | 3192.55 | 1 | 84.357 | 64.1561 | 935.644
2031-03-02 03:00 | 3182.42 | 1 | 83.3637 | 64.1561 | 932.6752
2031-03-03 04:00 | 3161.53 | 1 | 84.4489 | 64.1561 | 926.553
2031-03-04 05:00 | 3510.27 | 1.1239 | 82.7152 | 64.1561 | 1028.7586
2031-03-05 06:00 | 4880.98 | 1.5348 | 82.8548 | 64.1561 | 1430.474
2031-03-06 07:00 | 6098.12 | 2.0298 | 82.2419 | 64.1561 | 1787.1826
2031-03-07 08:00 | 6935.32 | 2.2786 | 82.5632 | 64.1561 | 2032.5417
2031-03-08 09:00 | 8999.07 | 3.0452 | 82.3752 | 64.1561 | 2637.3671
2031-03-09 10:00 | 10911.8 | 3.6302 | 82.9037 | 64.1561 | 3197.9329
2031-03-10 11:00 | 12343.2 | 4.0793 | 83.396 | 64.1561 | 3617.4348
2031-03-11 12:00 | 13176.1 | 4.4064 | 83.6565 | 64.1561 | 3861.5337
2031-03-12 13:00 | 13808.6 | 4.5313 | 84.2299 | 64.1561 | 4046.9012
2031-03-13 14:00 | 14145 | 4.6066 | 84.6348 | 64.1561 | 4145.4903
2031-03-14 15:00 | 16298.5 | 5.1822 | 85.167 | 64.1561 | 4776.6188
2031-03-15 16:00 | 16396.3 | 5.251 | 85.4949 | 64.1561 | 4805.2812
2031-03-16 17:00 | 16218.5 | 5.1835 | 85.8111 | 64.1561 | 4753.1731
2031-03-17 18:00 | 14413.8 | 4.4985 | 86.2981 | 64.1561 | 4224.2678
2031-03-18 19:00 | 12757.1 | 3.9523 | 86.376 | 64.1561 | 3738.7369
2031-03-19 20:00 | 10175.9 | 3.1364 | 86.3413 | 64.1561 | 2982.2619
2031-03-20 21:00 | 8808.44 | 2.7714 | 85.7665 | 64.1561 | 2581.4989
2031-03-21 22:00 | 6857.14 | 2.0834 | 85.9075 | 64.1561 | 2009.6294
2031-03-22 23:00 | 5760.14 | 1.791 | 85.2257 | 64.1561 | 1688.1304
2031-03-24 | 5144.4 | 1.5882 | 84.9698 | 64.1561 | 1507.6748
2031-03-25 01:00 | 4315.32 | 1.3272 | 84.7403 | 64.1561 | 1264.6954
2031-03-26 02:00 | 3789.91 | 1.1699 | 84.4287 | 64.1561 | 1110.713
2031-03-27 03:00 | 3607.21 | 1.1281 | 84.0029 | 64.1561 | 1057.1689
2031-03-28 04:00 | 3745.89 | 1.176 | 83.7561 | 64.1561 | 1097.812
2031-03-29 05:00 | 4644.42 | 1.4466 | 83.7103 | 64.1561 | 1361.1451
2031-03-30 06:00 | 5091.68 | 1.5981 | 83.5926 | 64.1561 | 1492.2241
2031-03-31 07:00 | 5485.39 | 1.7647 | 83.291 | 64.1561 | 1607.6091
2031-04-01 08:00 | 5632.9 | 1.7838 | 83.5117 | 64.1561 | 1650.84
2031-04-02 09:00 | 6561.23 | 2.1935 | 82.8699 | 64.1561 | 1922.9067
2031-04-03 10:00 | 8442.05 | 2.9188 | 82.5783 | 64.1561 | 2474.1206
2031-04-04 11:00 | 10672.2 | 3.5926 | 83.1239 | 64.1561 | 3127.7131
2031-04-05 12:00 | 11678.4 | 3.8648 | 83.6932 | 64.1561 | 3422.6012
2031-04-06 13:00 | 11987.5 | 3.8392 | 84.4078 | 64.1561 | 3513.1895
2031-04-07 14:00 | 11956.9 | 3.8311 | 84.6429 | 64.1561 | 3504.2215
2031-04-08 15:00 | 13050.7 | 4.2544 | 84.593 | 64.1561 | 3824.7826
2031-04-09 16:00 | 13208.8 | 4.3222 | 84.7855 | 64.1561 | 3871.1171
2031-04-10 17:00 | 12816 | 4.2129 | 84.8898 | 64.1561 | 3755.9988
2031-04-11 18:00 | 11594 | 3.7 | 85.3166 | 64.1561 | 3397.866
2031-04-12 19:00 | 10380.8 | 3.2866 | 85.3651 | 64.1561 | 3042.3122
2031-04-13 20:00 | 8728.75 | 2.5618 | 86.2435 | 64.1561 | 2558.1441
2031-04-14 21:00 | 7399.25 | 2.3036 | 85.2711 | 64.1561 | 2168.5061
2031-04-15 22:00 | 5348.9 | 1.6019 | 85.5231 | 64.1561 | 1567.6078
2031-04-16 23:00 | 4313.18 | 1.3672 | 84.4251 | 64.1561 | 1264.0683
2031-04-18 | 3691.76 | 1.1685 | 84.1018 | 64.1561 | 1081.9481
2031-04-19 01:00 | 3057.81 | 1 | 84.1206 | 64.1561 | 896.1556
2031-04-20 02:00 | 3218.33 | 1 | 85.3753 | 64.1561 | 943.1994
2031-04-21 03:00 | 3211.82 | 1 | 84.0836 | 64.1561 | 941.2915
2031-04-22 04:00 | 3257.85 | 1.041 | 83.1531 | 64.1561 | 954.7816
2031-04-23 05:00 | 4212.52 | 1.3413 | 83.0865 | 64.1561 | 1234.5677
2031-04-24 06:00 | 4720.97 | 1.478 | 83.3077 | 64.1561 | 1383.5797
2031-04-25 07:00 | 5520.87 | 1.7344 | 83.3039 | 64.1561 | 1618.0073
2031-04-26 08:00 | 5379.54 | 1.6982 | 83.3349 | 64.1561 | 1576.5875
2031-04-27 09:00 | 5974.18 | 1.9413 | 83.0024 | 64.1561 | 1750.8593
2031-04-28 10:00 | 7305.1 | 2.452 | 82.6909 | 64.1561 | 2140.9135
2031-04-29 11:00 | 8181.7 | 2.66 | 83.2433 | 64.1561 | 2397.8196
2031-04-30 12:00 | 8240.22 | 2.6813 | 83.4157 | 64.1561 | 2414.9701
2031-05-01 13:00 | 8446.35 | 2.7374 | 83.5602 | 64.1561 | 2475.3808
2031-05-02 14:00 | 9060.93 | 2.8795 | 83.888 | 64.1561 | 2655.4965
2031-05-03 15:00 | 10703.8 | 3.4661 | 83.7772 | 64.1561 | 3136.9741
2031-05-04 16:00 | 11183.5 | 3.6091 | 84.0658 | 64.1561 | 3277.5603
2031-05-05 17:00 | 11029.4 | 3.5849 | 84.164 | 64.1561 | 3232.3981
2031-05-06 18:00 | 9864.58 | 3.1473 | 84.498 | 64.1561 | 2891.023
2031-05-07 19:00 | 8435.52 | 2.6611 | 84.6091 | 64.1561 | 2472.2069
2031-05-08 20:00 | 6469.64 | 1.9299 | 85.201 | 64.1561 | 1896.0643
2031-05-09 21:00 | 5591.89 | 1.6613 | 84.9818 | 64.1561 | 1638.8212
2031-05-10 22:00 | 3417.23 | 1.0151 | 84.7466 | 64.1561 | 1001.4913
2031-05-11 23:00 | 3202.19 | 1 | 70.4377 | 64.1561 | 938.4692
2031-05-13 | 3121.56 | 1 | 70.2046 | 64.1561 | 914.8389
2031-05-14 01:00 | 3187.72 | 1 | 70.0264 | 64.1561 | 934.2285
2031-05-15 02:00 | 3123.44 | 1 | 69.9291 | 64.1561 | 915.3899
2031-05-16 03:00 | 3164.15 | 1 | 69.8001 | 64.1561 | 927.3208
2031-05-17 04:00 | 1011.32 | 1 | 70.2374 | 64.1561 | 296.3886
2031-05-18 05:00 | 1261.93 | 1 | 69.8521 | 64.1561 | 369.8352
2031-05-19 06:00 | 3181.07 | 1 | 87.8203 | 64.1561 | 932.2796
2031-05-20 07:00 | 4403.15 | 1.3539 | 82.7473 | 64.1561 | 1290.4359
2031-05-21 08:00 | 4508.16 | 1.4334 | 82.482 | 64.1561 | 1321.2113
2031-05-22 09:00 | 6059.91 | 2.0133 | 81.9939 | 64.1561 | 1775.9843
2031-05-23 10:00 | 7252.62 | 2.5017 | 81.7855 | 64.1561 | 2125.5331
2031-05-24 11:00 | 7880.98 | 2.5541 | 82.7847 | 64.1561 | 2309.6872
2031-05-25 12:00 | 9337.39 | 2.9525 | 83.2813 | 64.1561 | 2736.5189
2031-05-26 13:00 | 9242.44 | 2.9866 | 83.2919 | 64.1561 | 2708.6918
2031-05-27 14:00 | 9015.85 | 3.1341 | 82.6127 | 64.1561 | 2642.2848
2031-05-28 15:00 | 10493.2 | 3.4186 | 83.4279 | 64.1561 | 3075.2534
2031-05-29 16:00 | 12876.6 | 4.3021 | 83.3628 | 64.1561 | 3773.7589
2031-05-30 17:00 | 11889.8 | 3.9003 | 84.0201 | 64.1561 | 3484.5564
2031-05-31 18:00 | 10781.7 | 3.2371 | 85.2616 | 64.1561 | 3159.8044
2031-06-01 19:00 | 9067.91 | 2.8071 | 84.8642 | 64.1561 | 2657.5421
2031-06-02 20:00 | 8102.88 | 2.4651 | 84.9892 | 64.1561 | 2374.7197
2031-06-03 21:00 | 7111.58 | 2.1974 | 84.664 | 64.1561 | 2084.1984
2031-06-04 22:00 | 6259.12 | 1.9868 | 84.1464 | 64.1561 | 1834.367
2031-06-05 23:00 | 3208.89 | 1 | 85.2571 | 64.1561 | 940.4328
2031-06-07 | 3170.04 | 1 | 89.0181 | 64.1561 | 929.047
2031-06-08 01:00 | 3210.62 | 1 | 70.1724 | 64.1561 | 940.9398
2031-06-09 02:00 | 3155.83 | 1 | 70.0495 | 64.1561 | 924.8825
2031-06-10 03:00 | 3251.15 | 1 | 69.8827 | 64.1561 | 952.818
2031-06-11 04:00 | 3152.58 | 1 | 69.7785 | 64.1561 | 923.93
2031-06-12 05:00 | 1832.35 | 1 | 70.0157 | 64.1561 | 537.0088
2031-06-13 06:00 | 3205.15 | 1 | 91.3959 | 64.1561 | 939.3367
2031-06-14 07:00 | 4229.79 | 1.304 | 82.8801 | 64.1561 | 1239.6291
2031-06-15 08:00 | 4305.93 | 1.4047 | 82.2916 | 64.1561 | 1261.9435
2031-06-16 09:00 | 6161.79 | 2.0566 | 82.0289 | 64.1561 | 1805.8424
2031-06-17 10:00 | 7881.45 | 2.7103 | 81.867 | 64.1561 | 2309.825
2031-06-18 11:00 | 9539.88 | 3.2523 | 82.3005 | 64.1561 | 2795.8628
2031-06-19 12:00 | 10139.9 | 3.4111 | 82.8104 | 64.1561 | 2971.7113
2031-06-20 13:00 | 11081.6 | 3.5736 | 83.586 | 64.1561 | 3247.6964
2031-06-21 14:00 | 10225.8 | 3.278 | 83.9662 | 64.1561 | 2996.8861
2031-06-22 15:00 | 10466.2 | 3.2241 | 84.5561 | 64.1561 | 3067.3404
2031-06-23 16:00 | 11641.3 | 3.7418 | 84.1146 | 64.1561 | 3411.7282
2031-06-24 17:00 | 10418.4 | 3.312 | 84.4785 | 64.1561 | 3053.3316
2031-06-25 18:00 | 9066.83 | 2.8742 | 84.5277 | 64.1561 | 2657.2256
2031-06-26 19:00 | 7807.57 | 2.4266 | 84.6459 | 64.1561 | 2288.1729
2031-06-27 20:00 | 7184.74 | 2.0753 | 85.4575 | 64.1561 | 2105.6394
2031-06-28 21:00 | 6361.92 | 1.9098 | 84.8164 | 64.1561 | 1864.4947
2031-06-29 22:00 | 5663.82 | 1.6761 | 84.8226 | 64.1561 | 1659.9018
2031-06-30 23:00 | 3208.37 | 1 | 86.4721 | 64.1561 | 940.2804
2031-07-02 | 3150.54 | 1 | 91.1227 | 64.1561 | 923.3321
2031-07-03 01:00 | 3025.88 | 1 | 70.0961 | 64.1561 | 886.7979
2031-07-04 02:00 | 3126.41 | 1 | 69.9225 | 64.1561 | 916.2603
2031-07-05 03:00 | 3103.26 | 1 | 69.8049 | 64.1561 | 909.4757
2031-07-06 04:00 | 3150.61 | 1 | 69.6745 | 64.1561 | 923.3526
2031-07-07 05:00 | 3177.46 | 1 | 84.7012 | 64.1561 | 931.2216
2031-07-08 06:00 | 3242.92 | 1 | 83.4083 | 64.1561 | 950.406
2031-07-09 07:00 | 3907.77 | 1.1939 | 83.0705 | 64.1561 | 1145.2543
2031-07-10 08:00 | 3400.63 | 1.0445 | 83.0366 | 64.1561 | 996.6263
2031-07-11 09:00 | 5526.91 | 1.7121 | 82.8582 | 64.1561 | 1619.7774
2031-07-12 10:00 | 7059.59 | 2.3937 | 81.9369 | 64.1561 | 2068.9616
2031-07-13 11:00 | 8625.58 | 2.9494 | 82.1084 | 64.1561 | 2527.908
2031-07-14 12:00 | 9613.66 | 3.2332 | 82.6031 | 64.1561 | 2817.4856
2031-07-15 13:00 | 10869.2 | 3.6456 | 82.9148 | 64.1561 | 3185.4481
2031-07-16 14:00 | 12012.6 | 3.9322 | 83.5469 | 64.1561 | 3520.5455
2031-07-17 15:00 | 13957.9 | 4.5348 | 83.9746 | 64.1561 | 4090.6567
2031-07-18 16:00 | 13356.6 | 4.3698 | 84.3246 | 64.1561 | 3914.4331
2031-07-19 17:00 | 12971.7 | 4.1643 | 84.7724 | 64.1561 | 3801.63
2031-07-20 18:00 | 11431.1 | 3.6069 | 85.1285 | 64.1561 | 3350.1247
2031-07-21 19:00 | 9704.7 | 3.0587 | 85.1302 | 64.1561 | 2844.1668
2031-07-22 20:00 | 7371.6 | 2.1438 | 86.038 | 64.1561 | 2160.4027
2031-07-23 21:00 | 6182.98 | 1.8635 | 85.2431 | 64.1561 | 1812.0526
2031-07-24 22:00 | 3849.19 | 1.1418 | 85.164 | 64.1561 | 1128.0862
2031-07-25 23:00 | 3219.35 | 1 | 86.5268 | 64.1561 | 943.4983
2031-07-27 | 3162.38 | 1 | 91.2491 | 64.1561 | 926.8021
2031-07-28 01:00 | 3108.94 | 1 | 70.2758 | 64.1561 | 911.1404
2031-07-29 02:00 | 3075.11 | 1 | 70.1224 | 64.1561 | 901.2258
2031-07-30 03:00 | 3195.78 | 1 | 69.9305 | 64.1561 | 936.5907
2031-07-31 04:00 | 3214.58 | 1 | 69.8303 | 64.1561 | 942.1004
2031-08-01 05:00 | 3187.69 | 1 | 84.0466 | 64.1561 | 934.2197
2031-08-02 06:00 | 3649.89 | 1.126 | 83.0994 | 64.1561 | 1069.6772
2031-08-03 07:00 | 5256.61 | 1.6629 | 82.7655 | 64.1561 | 1540.5603
2031-08-04 08:00 | 5560.43 | 1.8283 | 82.4673 | 64.1561 | 1629.6012
2031-08-05 09:00 | 7479.83 | 2.5662 | 82.0755 | 64.1561 | 2192.1218
2031-08-06 10:00 | 8876.74 | 3.0814 | 82.2122 | 64.1561 | 2601.5157
2031-08-07 11:00 | 9562.76 | 3.3205 | 82.5318 | 64.1561 | 2802.5683
2031-08-08 12:00 | 11256.2 | 3.5036 | 84.0934 | 64.1561 | 3298.8666
2031-08-09 13:00 | 12445.6 | 3.9733 | 84.1201 | 64.1561 | 3647.4453
2031-08-10 14:00 | 12624.2 | 4.0563 | 84.4134 | 64.1561 | 3699.7878
2031-08-11 15:00 | 14536.9 | 4.7871 | 84.349 | 64.1561 | 4260.3448
2031-08-12 16:00 | 15105.6 | 4.9963 | 84.6792 | 64.1561 | 4427.0144
2031-08-13 17:00 | 14838.8 | 4.8267 | 85.2246 | 64.1561 | 4348.823
2031-08-14 18:00 | 13222.4 | 4.2167 | 85.6791 | 64.1561 | 3875.1029
2031-08-15 19:00 | 11380.9 | 3.5717 | 85.8818 | 64.1561 | 3335.4125
2031-08-16 20:00 | 9173.37 | 2.6881 | 86.6563 | 64.1561 | 2688.4494
2031-08-17 21:00 | 7280.55 | 2.2355 | 85.7739 | 64.1561 | 2133.7186
2031-08-18 22:00 | 4747.65 | 1.3838 | 86.1195 | 64.1561 | 1391.3989
2031-08-19 23:00 | 3456.68 | 1.0376 | 85.264 | 64.1561 | 1013.0529
2031-08-21 | 3250.25 | 1 | 89.2854 | 64.1561 | 952.5542
2031-08-22 01:00 | 3170.53 | 1 | 70.7688 | 64.1561 | 929.1906
2031-08-23 02:00 | 3143.75 | 1 | 70.5666 | 64.1561 | 921.3422
2031-08-24 03:00 | 3041.2 | 1 | 70.4009 | 64.1561 | 891.2877
2031-08-25 04:00 | 3121.22 | 1 | 70.2285 | 64.1561 | 914.7393
2031-08-26 05:00 | 3302.71 | 1 | 88.7182 | 64.1561 | 967.9288
2031-08-27 06:00 | 3255.13 | 1.015 | 83.3055 | 64.1561 | 953.9844
2031-08-28 07:00 | 4542.68 | 1.421 | 83.1839 | 64.1561 | 1331.3281
2031-08-29 08:00 | 5337.04 | 1.6826 | 83.1607 | 64.1561 | 1564.132
2031-08-30 09:00 | 7247.24 | 2.4007 | 82.6671 | 64.1561 | 2123.9564
2031-08-31 10:00 | 9321.08 | 3.0875 | 82.9243 | 64.1561 | 2731.7389
2031-09-01 11:00 | 10110.6 | 3.5045 | 82.7829 | 64.1561 | 2963.1244
2031-09-02 12:00 | 11362.3 | 3.7244 | 83.7397 | 64.1561 | 3329.9614
2031-09-03 13:00 | 11544.5 | 3.8778 | 83.7742 | 64.1561 | 3383.359
2031-09-04 14:00 | 12685.4 | 4.1291 | 84.3872 | 64.1561 | 3717.7238
2031-09-05 15:00 | 14295.3 | 4.77 | 84.3646 | 64.1561 | 4189.5389
2031-09-06 16:00 | 14937.2 | 4.8476 | 85.0493 | 64.1561 | 4377.6612
2031-09-07 17:00 | 14955.1 | 4.8152 | 85.452 | 64.1561 | 4382.9072
2031-09-08 18:00 | 12916.7 | 4.0839 | 85.9044 | 64.1561 | 3785.5111
2031-09-09 19:00 | 10316.3 | 3.1674 | 86.2535 | 64.1561 | 3023.4091
2031-09-10 20:00 | 7550.55 | 2.285 | 86.2101 | 64.1561 | 2212.8478
2031-09-11 21:00 | 6106.27 | 1.7924 | 86.2104 | 64.1561 | 1789.5711
2031-09-12 22:00 | 3534.07 | 1.0574 | 85.5908 | 64.1561 | 1035.7337
2031-09-13 23:00 | 3208.25 | 1 | 88.9883 | 64.1561 | 940.2453
2031-09-15 | 3138.98 | 1 | 70.9059 | 64.1561 | 919.9442
2031-09-16 01:00 | 3123.7 | 1 | 70.6848 | 64.1561 | 915.4661
2031-09-17 02:00 | 3096.63 | 1 | 70.5144 | 64.1561 | 907.5327
2031-09-18 03:00 | 3151.81 | 1 | 70.3361 | 64.1561 | 923.7043
2031-09-19 04:00 | 3202.07 | 1 | 70.2097 | 64.1561 | 938.4341
2031-09-20 05:00 | 3207.62 | 1 | 89.3995 | 64.1561 | 940.0606
2031-09-21 06:00 | 3392.68 | 1.0517 | 83.3751 | 64.1561 | 994.2964
2031-09-22 07:00 | 5043.73 | 1.5675 | 83.2897 | 64.1561 | 1478.1713
2031-09-23 08:00 | 5737.03 | 1.8423 | 83.0242 | 64.1561 | 1681.3575
2031-09-24 09:00 | 7665.19 | 2.5541 | 82.7104 | 64.1561 | 2246.4454
2031-09-25 10:00 | 9103.81 | 3.1078 | 82.7049 | 64.1561 | 2668.0633
2031-09-26 11:00 | 10595.3 | 3.6092 | 83.0508 | 64.1561 | 3105.1759
2031-09-27 12:00 | 11442.3 | 3.7817 | 83.7575 | 64.1561 | 3353.4071
2031-09-28 13:00 | 12373.8 | 4.0385 | 84.2087 | 64.1561 | 3626.4028
2031-09-29 14:00 | 13573.1 | 4.3746 | 84.6668 | 64.1561 | 3977.8829
2031-09-30 15:00 | 14950.5 | 4.8809 | 84.8345 | 64.1561 | 4381.559
2031-10-01 16:00 | 15324 | 4.9652 | 85.2909 | 64.1561 | 4491.0211
2031-10-02 17:00 | 14859.6 | 4.8115 | 85.5835 | 64.1561 | 4354.9189
2031-10-03 18:00 | 13178.5 | 4.2102 | 85.9243 | 64.1561 | 3862.2371
2031-10-04 19:00 | 11310.7 | 3.6149 | 85.9037 | 64.1561 | 3314.839
2031-10-05 20:00 | 8878.18 | 2.7076 | 86.3489 | 64.1561 | 2601.9377
2031-10-06 21:00 | 7625.04 | 2.3404 | 85.9503 | 64.1561 | 2234.6786
2031-10-07 22:00 | 5473.68 | 1.5494 | 86.737 | 64.1561 | 1604.1773
2031-10-08 23:00 | 4612.15 | 1.4349 | 85.0871 | 64.1561 | 1351.6877
2031-10-10 | 3808.81 | 1.1906 | 84.6918 | 64.1561 | 1116.252
2031-10-11 01:00 | 3194.4 | 1 | 85.309 | 64.1561 | 936.1862
2031-10-12 02:00 | 3163.71 | 1 | 86.3548 | 64.1561 | 927.1919
2031-10-13 03:00 | 3141.46 | 1 | 86.7001 | 64.1561 | 920.671
2031-10-14 04:00 | 3207.02 | 1 | 87.4493 | 64.1561 | 939.8848
2031-10-15 05:00 | 3647.97 | 1.1529 | 83.4642 | 64.1561 | 1069.1145
2031-10-16 06:00 | 4780.27 | 1.5026 | 83.4789 | 64.1561 | 1400.9588
2031-10-17 07:00 | 6115.81 | 2.0324 | 82.8703 | 64.1561 | 1792.367
2031-10-18 08:00 | 6697.51 | 2.2667 | 82.8293 | 64.1561 | 1962.8464
2031-10-19 09:00 | 8571.6 | 2.8879 | 83.0148 | 64.1561 | 2512.088
2031-10-20 10:00 | 10108.3 | 3.3214 | 83.5936 | 64.1561 | 2962.4503
2031-10-21 11:00 | 11399 | 3.6746 | 84.1644 | 64.1561 | 3340.7171
2031-10-22 12:00 | 12271.4 | 4.0247 | 84.2972 | 64.1561 | 3596.3923
2031-10-23 13:00 | 11876.5 | 3.849 | 84.7528 | 64.1561 | 3480.6586
2031-10-24 14:00 | 11447.4 | 3.757 | 84.7697 | 64.1561 | 3354.9018
2031-10-25 15:00 | 13961.6 | 4.5291 | 84.9644 | 64.1561 | 4091.7411
2031-10-26 16:00 | 15572.6 | 4.8608 | 85.7801 | 64.1561 | 4563.8785
2031-10-27 17:00 | 15270.3 | 4.8862 | 85.8722 | 64.1561 | 4475.2832
2031-10-28 18:00 | 13675.4 | 4.29 | 86.3269 | 64.1561 | 4007.8641
2031-10-29 19:00 | 12223 | 3.6789 | 86.8624 | 64.1561 | 3582.2077
2031-10-30 20:00 | 8179.27 | 2.5325 | 86.4612 | 64.1561 | 2397.1074
2031-10-31 21:00 | 6919.02 | 2.0486 | 86.5929 | 64.1561 | 2027.7646
2031-11-01 22:00 | 4301.18 | 1.2797 | 86.1518 | 64.1561 | 1260.5514
2031-11-02 23:00 | 3251.26 | 1 | 88.7779 | 64.1561 | 952.8502
2031-11-04 | 3213.11 | 1 | 71.3053 | 64.1561 | 941.6696
2031-11-05 01:00 | 3144.96 | 1 | 71.042 | 64.1561 | 921.6968
2031-11-06 02:00 | 3197.23 | 1 | 70.8508 | 64.1561 | 937.0156
2031-11-07 03:00 | 3098.15 | 1 | 70.7061 | 64.1561 | 907.9781
2031-11-08 04:00 | 3143.34 | 1 | 70.5491 | 64.1561 | 921.222
2031-11-09 05:00 | 3199.32 | 1 | 70.4175 | 64.1561 | 937.6281
2031-11-10 06:00 | 3292.78 | 1 | 88.6385 | 64.1561 | 965.0186
2031-11-11 07:00 | 4537.72 | 1.3929 | 83.7033 | 64.1561 | 1329.8745
2031-11-12 08:00 | 4343.22 | 1.3075 | 84.0367 | 64.1561 | 1272.8721
2031-11-13 09:00 | 5986.67 | 1.9106 | 83.2838 | 64.1561 | 1754.5198
2031-11-14 10:00 | 8072.34 | 2.8108 | 82.4167 | 64.1561 | 2365.7693
2031-11-15 11:00 | 9830.3 | 3.3826 | 82.8689 | 64.1561 | 2880.9765
2031-11-16 12:00 | 11012.3 | 3.8156 | 83.1532 | 64.1561 | 3227.3865
2031-11-17 13:00 | 12170.6 | 4.0462 | 83.9589 | 64.1561 | 3566.8508
2031-11-18 14:00 | 12005.4 | 3.9047 | 84.579 | 64.1561 | 3518.4354
2031-11-19 15:00 | 12323.3 | 3.9741 | 84.8835 | 64.1561 | 3611.6027
2031-11-20 16:00 | 15683 | 5.0954 | 84.948 | 64.1561 | 4596.2336
2031-11-21 17:00 | 13682.4 | 4.5068 | 85.2958 | 64.1561 | 4009.9156
2031-11-22 18:00 | 11926.3 | 3.8943 | 85.5063 | 64.1561 | 3495.2535
2031-11-23 19:00 | 10139.3 | 3.1814 | 85.8795 | 64.1561 | 2971.5355
2031-11-24 20:00 | 8769.67 | 2.7235 | 85.8647 | 64.1561 | 2570.1366
2031-11-25 21:00 | 7766.13 | 2.3923 | 85.7924 | 64.1561 | 2276.028
2031-11-26 22:00 | 6953.9 | 2.0638 | 86.039 | 64.1561 | 2037.9869
2031-11-27 23:00 | 3612.95 | 1.0381 | 86.2698 | 64.1561 | 1058.8511
2031-11-29 | 3237.85 | 1 | 90.0553 | 64.1561 | 948.9202
2031-11-30 01:00 | 3128.2 | 1 | 71.0845 | 64.1561 | 916.7849
2031-12-01 02:00 | 3153.17 | 1 | 70.8757 | 64.1561 | 924.1029
2031-12-02 03:00 | 3086.38 | 1 | 70.7188 | 64.1561 | 904.5287
2031-12-03 04:00 | 3142.27 | 1 | 70.5113 | 64.1561 | 920.9084
2031-12-04 05:00 | 3146.29 | 1 | 70.4057 | 64.1561 | 922.0866
2031-12-05 06:00 | 3203.6 | 1 | 84.936 | 64.1561 | 938.8825
2031-12-06 07:00 | 4809.15 | 1.5068 | 83.4608 | 64.1561 | 1409.4227
2031-12-07 08:00 | 4950.74 | 1.5112 | 83.9093 | 64.1561 | 1450.9187
2031-12-08 09:00 | 6487.34 | 2.2493 | 82.4231 | 64.1561 | 1901.2517
2031-12-09 10:00 | 8885.04 | 3.0108 | 82.842 | 64.1561 | 2603.9482
2031-12-10 11:00 | 10635.8 | 3.5262 | 83.4674 | 64.1561 | 3117.0453
2031-12-11 12:00 | 11817.3 | 3.907 | 83.9066 | 64.1561 | 3463.3088
2031-12-12 13:00 | 12056.8 | 4.0468 | 84.0871 | 64.1561 | 3533.4993
2031-12-13 14:00 | 12673.3 | 4.1736 | 84.5864 | 64.1561 | 3714.1776
2031-12-14 15:00 | 13313.4 | 4.3277 | 85.0021 | 64.1561 | 3901.7724
2031-12-15 16:00 | 15606.1 | 5.1299 | 85.0932 | 64.1561 | 4573.6964
2031-12-16 17:00 | 14750.8 | 4.7082 | 85.8726 | 64.1561 | 4323.0327
2031-12-17 18:00 | 13061.6 | 4.1517 | 86.1187 | 64.1561 | 3827.9771
2031-12-18 19:00 | 10980.8 | 3.4964 | 86.0732 | 64.1561 | 3218.1548
2031-12-19 20:00 | 9994.4 | 3.0777 | 86.3388 | 64.1561 | 2929.0695
2031-12-20 21:00 | 8890.92 | 2.7392 | 86.1997 | 64.1561 | 2605.6714
2031-12-21 22:00 | 7936.43 | 2.4071 | 86.195 | 64.1561 | 2325.938
2031-12-22 23:00 | 5460.13 | 1.5674 | 86.7156 | 64.1561 | 1600.2061
2031-12-24 | 4389.05 | 1.3466 | 85.4453 | 64.1561 | 1286.3036
2031-12-25 01:00 | 3440.16 | 1.0627 | 85.0274 | 64.1561 | 1008.2114
2031-12-26 02:00 | 3153.4 | 1 | 85.085 | 64.1561 | 924.1703
2031-12-27 03:00 | 3121.67 | 1 | 84.7724 | 64.1561 | 914.8712
2031-12-28 04:00 | 3179.27 | 1 | 84.1151 | 64.1561 | 931.7521
2031-12-29 05:00 | 4168.6 | 1.2914 | 84.0648 | 64.1561 | 1221.6961
2031-12-30 06:00 | 4678.5 | 1.4647 | 83.9294 | 64.1561 | 1371.133
2031-12-31 07:00 | 5760.87 | 1.873 | 83.4957 | 64.1561 | 1688.3443
2032-01-01 08:00 | 6501.45 | 2.133 | 83.5033 | 64.1561 | 1905.3869
2032-01-02 09:00 | 8499.95 | 2.8793 | 83.2543 | 64.1561 | 2491.0894
2032-01-03 10:00 | 10240.5 | 3.3469 | 83.9518 | 64.1561 | 3001.1943
2032-01-04 11:00 | 11460.2 | 3.8351 | 84.0208 | 64.1561 | 3358.6531
2032-01-05 12:00 | 12601.6 | 4.1787 | 84.4675 | 64.1561 | 3693.1644
2032-01-06 13:00 | 13182.8 | 4.2893 | 85.0387 | 64.1561 | 3863.4973
2032-01-07 14:00 | 13791.3 | 4.4814 | 85.3618 | 64.1561 | 4041.831
2032-01-08 15:00 | 15857.4 | 5.2776 | 85.3468 | 64.1561 | 4647.3452
2032-01-09 16:00 | 16334.7 | 5.3086 | 86.039 | 64.1561 | 4787.228
2032-01-10 17:00 | 15986.7 | 5.0419 | 86.7333 | 64.1561 | 4685.2393
2032-01-11 18:00 | 14198.1 | 4.4664 | 86.9647 | 64.1561 | 4161.0524
2032-01-12 19:00 | 12036.5 | 3.7557 | 87.0631 | 64.1561 | 3527.5499
2032-01-13 20:00 | 9570.14 | 2.9221 | 87.1771 | 64.1561 | 2804.7312
2032-01-14 21:00 | 8494.99 | 2.6063 | 86.7752 | 64.1561 | 2489.6358
2032-01-15 22:00 | 6629.57 | 1.9062 | 87.3317 | 64.1561 | 1942.9352
2032-01-16 23:00 | 5524.26 | 1.6559 | 86.4044 | 64.1561 | 1619.0008
2032-01-18 | 4926.89 | 1.4989 | 85.8641 | 64.1561 | 1443.9289
2032-01-19 01:00 | 4248.26 | 1.3115 | 85.4075 | 64.1561 | 1245.0421
2032-01-20 02:00 | 4105.75 | 1.2705 | 85.1309 | 64.1561 | 1203.2765
2032-01-21 03:00 | 4363 | 1.3606 | 84.8196 | 64.1561 | 1278.6691
2032-01-22 04:00 | 4648.29 | 1.4704 | 84.5149 | 64.1561 | 1362.2793
2032-01-23 05:00 | 5506.18 | 1.8069 | 83.9835 | 64.1561 | 1613.7021
2032-01-24 06:00 | 5609.77 | 1.8203 | 84.1361 | 64.1561 | 1644.0613
2032-01-25 07:00 | 6237.08 | 2.0807 | 83.8073 | 64.1561 | 1827.9077
2032-01-26 08:00 | 6249.91 | 1.9916 | 84.4222 | 64.1561 | 1831.6678
2032-01-27 09:00 | 6444.03 | 2.0719 | 84.3339 | 64.1561 | 1888.5588
2032-01-28 10:00 | 7553.14 | 2.427 | 84.3592 | 64.1561 | 2213.6068
2032-01-29 11:00 | 9331.37 | 3.1407 | 83.9218 | 64.1561 | 2734.7546
2032-01-30 12:00 | 10897.2 | 3.5654 | 84.5081 | 64.1561 | 3193.6541
2032-01-31 13:00 | 11273.3 | 3.7337 | 84.6713 | 64.1561 | 3303.8781
2032-02-01 14:00 | 12723.5 | 4.1367 | 85.1118 | 64.1561 | 3728.8898
2032-02-02 15:00 | 14154.2 | 4.6939 | 85.1758 | 64.1561 | 4148.1865
2032-02-03 16:00 | 12422 | 4.0286 | 85.8007 | 64.1561 | 3640.5288
2032-02-04 17:00 | 12694.4 | 4.1417 | 85.7376 | 64.1561 | 3720.3614
2032-02-05 18:00 | 11014.8 | 3.4299 | 86.3817 | 64.1561 | 3228.1192
2032-02-06 19:00 | 9612.61 | 2.9538 | 86.4709 | 64.1561 | 2817.1779
2032-02-07 20:00 | 7439.24 | 2.2218 | 86.6674 | 64.1561 | 2180.226
2032-02-08 21:00 | 6453.6 | 1.9147 | 86.4288 | 64.1561 | 1891.3635
2032-02-09 22:00 | 4494.98 | 1.296 | 86.5576 | 64.1561 | 1317.3486
2032-02-10 23:00 | 3994.19 | 1.1914 | 85.7242 | 64.1561 | 1170.5815
2032-02-12 | 3202.51 | 1.017 | 84.6368 | 64.1561 | 938.563
2032-02-13 01:00 | 3112.92 | 1 | 87.1477 | 64.1561 | 912.3068
2032-02-14 02:00 | 2997.21 | 1 | 90.5125 | 64.1561 | 878.3955
2032-02-15 03:00 | 3024.89 | 1 | 91.4781 | 64.1561 | 886.5077
2032-02-16 04:00 | 3061.2 | 1 | 89.9256 | 64.1561 | 897.1492
2032-02-17 05:00 | 3121.47 | 1 | 83.9648 | 64.1561 | 914.8126
2032-02-18 06:00 | 4168.29 | 1.3075 | 83.7908 | 64.1561 | 1221.6052
2032-02-19 07:00 | 5630.08 | 1.783 | 83.7042 | 64.1561 | 1650.0136
2032-02-20 08:00 | 6213.87 | 1.9889 | 83.7445 | 64.1561 | 1821.1055
2032-02-21 09:00 | 7954.14 | 2.6891 | 83.229 | 64.1561 | 2331.1283
2032-02-22 10:00 | 9773.83 | 3.301 | 83.509 | 64.1561 | 2864.4268
2032-02-23 11:00 | 11515.5 | 3.8327 | 84.0444 | 64.1561 | 3374.8599
2032-02-24 12:00 | 12610.4 | 4.2714 | 84.2432 | 64.1561 | 3695.7434
2032-02-25 13:00 | 13380.2 | 4.46 | 84.7921 | 64.1561 | 3921.3495
2032-02-26 14:00 | 14220 | 4.6011 | 85.4747 | 64.1561 | 4167.4706
2032-02-27 15:00 | 16061.9 | 5.2705 | 85.6124 | 64.1561 | 4707.2782
2032-02-28 16:00 | 16201.8 | 5.2657 | 86.1545 | 64.1561 | 4748.2789
2032-02-29 17:00 | 16112.4 | 5.2193 | 86.4954 | 64.1561 | 4722.0783
2032-03-01 18:00 | 14299.4 | 4.5489 | 86.9376 | 64.1561 | 4190.7405
2032-03-02 19:00 | 12007.1 | 3.8403 | 86.8759 | 64.1561 | 3518.9336
2032-03-03 20:00 | 9518.42 | 2.9259 | 87.2009 | 64.1561 | 2789.5735
2032-03-04 21:00 | 8232.01 | 2.5173 | 86.9295 | 64.1561 | 2412.564
2032-03-05 22:00 | 6208.36 | 1.827 | 87.128 | 64.1561 | 1819.4907
2032-03-06 23:00 | 5172.54 | 1.5465 | 86.5123 | 64.1561 | 1515.9218
2032-03-08 | 4383.76 | 1.34 | 85.8638 | 64.1561 | 1284.7532
2032-03-09 01:00 | 3587.32 | 1.1208 | 85.2809 | 64.1561 | 1051.3397
2032-03-10 02:00 | 3207.4 | 1.0191 | 84.7811 | 64.1561 | 939.9961
2032-03-11 03:00 | 3425.22 | 1.092 | 84.4706 | 64.1561 | 1003.8329
2032-03-12 04:00 | 3663 | 1.1643 | 84.3388 | 64.1561 | 1073.5193
2032-03-13 05:00 | 4476.68 | 1.3938 | 84.4713 | 64.1561 | 1311.9854
2032-03-14 06:00 | 4885.63 | 1.5822 | 83.9654 | 64.1561 | 1431.8368
2032-03-15 07:00 | 6337.93 | 1.9854 | 84.3764 | 64.1561 | 1857.4639
2032-03-16 08:00 | 6704.98 | 2.1296 | 84.3598 | 64.1561 | 1965.0357
2032-03-17 09:00 | 8645.87 | 2.8303 | 84.1014 | 64.1561 | 2533.8544
2032-03-18 10:00 | 10523.1 | 3.5466 | 84.0281 | 64.1561 | 3084.0162
2032-03-19 11:00 | 12187.1 | 4.0642 | 84.5113 | 64.1561 | 3571.6864
2032-03-20 12:00 | 12853.6 | 4.2527 | 84.9999 | 64.1561 | 3767.0183
2032-03-21 13:00 | 12669.3 | 4.1628 | 85.3979 | 64.1561 | 3713.0053
2032-03-22 14:00 | 13420.4 | 4.2283 | 86.1079 | 64.1561 | 3933.131
2032-03-23 15:00 | 12687.8 | 4.1594 | 85.8506 | 64.1561 | 3718.4271
2032-03-24 16:00 | 13745.6 | 4.4673 | 86.0247 | 64.1561 | 4028.4377
2032-03-25 17:00 | 14536.6 | 4.6598 | 86.3569 | 64.1561 | 4260.2569
2032-03-26 18:00 | 13375.3 | 4.1817 | 86.8973 | 64.1561 | 3919.9135
2032-03-27 19:00 | 11463.4 | 3.5953 | 86.9005 | 64.1561 | 3359.5909
2032-03-28 20:00 | 8711.47 | 2.7093 | 86.8691 | 64.1561 | 2553.0798
2032-03-29 21:00 | 7739.74 | 2.3773 | 86.7016 | 64.1561 | 2268.2939
2032-03-30 22:00 | 5705.57 | 1.7438 | 86.4968 | 64.1561 | 1672.1375
2032-03-31 23:00 | 5034.04 | 1.504 | 86.3916 | 64.1561 | 1475.3315
2032-04-02 | 4209.4 | 1.3105 | 85.536 | 64.1561 | 1233.6534
2032-04-03 01:00 | 3531.93 | 1.1024 | 85.216 | 64.1561 | 1035.1065
2032-04-04 02:00 | 3266.01 | 1.0276 | 84.8542 | 64.1561 | 957.173
2032-04-05 03:00 | 3400.15 | 1.0382 | 85.0202 | 64.1561 | 996.4856
2032-04-06 04:00 | 3446.41 | 1.0989 | 84.339 | 64.1561 | 1010.0431
2032-04-07 05:00 | 4590.78 | 1.3899 | 84.8576 | 64.1561 | 1345.4248
2032-04-08 06:00 | 5412.17 | 1.7058 | 84.3592 | 64.1561 | 1586.1505
2032-04-09 07:00 | 6345.76 | 2.0548 | 84.0963 | 64.1561 | 1859.7587
2032-04-10 08:00 | 6661.19 | 2.1597 | 84.2112 | 64.1561 | 1952.2021
2032-04-11 09:00 | 8379.41 | 2.807 | 83.9071 | 64.1561 | 2455.7627
2032-04-12 10:00 | 9974.76 | 3.3808 | 84.0108 | 64.1561 | 2923.3136
2032-04-13 11:00 | 11531.8 | 3.8589 | 84.4591 | 64.1561 | 3379.637
2032-04-14 12:00 | 10423.4 | 3.5292 | 84.6668 | 64.1561 | 3054.797
2032-04-15 13:00 | 10982.7 | 3.6169 | 85.0714 | 64.1561 | 3218.7116
2032-04-16 14:00 | 12422.9 | 4.0251 | 85.4041 | 64.1561 | 3640.7926
2032-04-17 15:00 | 14833.7 | 4.8059 | 85.6709 | 64.1561 | 4347.3283
2032-04-18 16:00 | 15605.7 | 4.9853 | 86.2661 | 64.1561 | 4573.5792
2032-04-19 17:00 | 14958 | 4.8812 | 86.3262 | 64.1561 | 4383.7571
2032-04-20 18:00 | 13510.7 | 4.2722 | 86.8777 | 64.1561 | 3959.5953
2032-04-21 19:00 | 11263.6 | 3.6592 | 86.5608 | 64.1561 | 3301.0353
2032-04-22 20:00 | 9214.93 | 2.7386 | 87.5194 | 64.1561 | 2700.6294
2032-04-23 21:00 | 7861.72 | 2.3817 | 86.9662 | 64.1561 | 2304.0427
2032-04-24 22:00 | 5670.62 | 1.6407 | 87.2708 | 64.1561 | 1661.8947
2032-04-25 23:00 | 4041.04 | 1.2064 | 86.4274 | 64.1561 | 1184.3119
2032-04-27 | 3135.32 | 1 | 85.7543 | 64.1561 | 918.8716
2032-04-28 01:00 | 3087.95 | 1 | 90.3226 | 64.1561 | 904.9888
2032-04-29 02:00 | 3225.15 | 1 | 71.5577 | 64.1561 | 945.1982
2032-04-30 03:00 | 3137.44 | 1 | 71.3936 | 64.1561 | 919.4929
2032-05-01 04:00 | 3114.15 | 1 | 71.2264 | 64.1561 | 912.6673
2032-05-02 05:00 | 3120.89 | 1 | 71.0774 | 64.1561 | 914.6426
2032-05-03 06:00 | 3199.69 | 1 | 84.3212 | 64.1561 | 937.7366
2032-05-04 07:00 | 5305.34 | 1.6868 | 83.8915 | 64.1561 | 1554.8417
2032-05-05 08:00 | 5701.46 | 1.8571 | 83.7517 | 64.1561 | 1670.933
2032-05-06 09:00 | 7446.98 | 2.4528 | 83.7116 | 64.1561 | 2182.4944
2032-05-07 10:00 | 9484.15 | 3.1063 | 83.9955 | 64.1561 | 2779.53
2032-05-08 11:00 | 10794 | 3.5661 | 84.2499 | 64.1561 | 3163.4091
2032-05-09 12:00 | 11308.1 | 3.7842 | 84.4697 | 64.1561 | 3314.077
2032-05-10 13:00 | 12254.6 | 4.0254 | 84.9543 | 64.1561 | 3591.4687
2032-05-11 14:00 | 12752.8 | 4.1879 | 85.2507 | 64.1561 | 3737.4767
2032-05-12 15:00 | 10232.3 | 3.2368 | 85.9577 | 64.1561 | 2998.7911
2032-05-13 16:00 | 12220.5 | 4.0124 | 85.3642 | 64.1561 | 3581.475
2032-05-14 17:00 | 10985.2 | 3.4853 | 85.9556 | 64.1561 | 3219.4443
2032-05-15 18:00 | 10032.3 | 3.1395 | 86.1408 | 64.1561 | 2940.1769
2032-05-16 19:00 | 8719.21 | 2.6078 | 86.6087 | 64.1561 | 2555.3482
2032-05-17 20:00 | 7479.6 | 2.2982 | 86.0896 | 64.1561 | 2192.0544
2032-05-18 21:00 | 6660.57 | 2.0365 | 85.9725 | 64.1561 | 1952.0204
2032-05-19 22:00 | 6059.09 | 1.8597 | 85.7081 | 64.1561 | 1775.744
2032-05-20 23:00 | 3296.64 | 1 | 89.763 | 64.1561 | 966.1498
2032-05-22 | 3218.61 | 1 | 90.3484 | 64.1561 | 943.2815
2032-05-23 01:00 | 3079.51 | 1 | 71.3516 | 64.1561 | 902.5153
2032-05-24 02:00 | 3119.76 | 1 | 71.1587 | 64.1561 | 914.3114
2032-05-25 03:00 | 3141.43 | 1 | 71.0179 | 64.1561 | 920.6623
2032-05-26 04:00 | 3214.4 | 1 | 70.8619 | 64.1561 | 942.0476
2032-05-27 05:00 | 3137.12 | 1 | 70.809 | 64.1561 | 919.3991
2032-05-28 06:00 | 3770.26 | 1.1462 | 84.3597 | 64.1561 | 1104.9541
2032-05-29 07:00 | 6000.71 | 1.9146 | 83.7142 | 64.1561 | 1758.6345
2032-05-30 08:00 | 6514.19 | 2.0564 | 84.0754 | 64.1561 | 1909.1206
2032-05-31 09:00 | 7909.3 | 2.5568 | 83.9367 | 64.1561 | 2317.987
2032-06-01 10:00 | 9203.68 | 2.9978 | 84.0568 | 64.1561 | 2697.3323
2032-06-02 11:00 | 10020.3 | 3.4014 | 83.8639 | 64.1561 | 2936.66
2032-06-03 12:00 | 11588.2 | 3.84 | 84.4142 | 64.1561 | 3396.1662
2032-06-04 13:00 | 10474.6 | 3.3907 | 85.0234 | 64.1561 | 3069.8022
2032-06-05 14:00 | 11235.7 | 3.7316 | 84.8009 | 64.1561 | 3292.8586
2032-06-06 15:00 | 11036.4 | 3.4426 | 85.7203 | 64.1561 | 3234.4496
2032-06-07 16:00 | 12090.6 | 3.9869 | 85.1301 | 64.1561 | 3543.4051
2032-06-08 17:00 | 11041.3 | 3.4165 | 86.1054 | 64.1561 | 3235.8856
2032-06-09 18:00 | 9603.54 | 3.1426 | 85.426 | 64.1561 | 2814.5197
2032-06-10 19:00 | 7830.06 | 2.3679 | 86.2898 | 64.1561 | 2294.7641
2032-06-11 20:00 | 6664.46 | 2.1522 | 85.2395 | 64.1561 | 1953.1604
2032-06-12 21:00 | 5920.9 | 1.8724 | 85.261 | 64.1561 | 1735.2445
2032-06-13 22:00 | 5381.24 | 1.6349 | 85.53 | 64.1561 | 1577.0858
2032-06-14 23:00 | 3245.48 | 1 | 88.7491 | 64.1561 | 951.1563
2032-06-16 | 3220.1 | 1 | 71.3271 | 64.1561 | 943.7182
2032-06-17 01:00 | 3125.54 | 1 | 71.1366 | 64.1561 | 916.0054
2032-06-18 02:00 | 3156.97 | 1 | 70.9773 | 64.1561 | 925.2166
2032-06-19 03:00 | 3179.89 | 1 | 70.8447 | 64.1561 | 931.9338
2032-06-20 04:00 | 3192.66 | 1 | 70.7187 | 64.1561 | 935.6763
2032-06-21 05:00 | 3170.66 | 1 | 86.1495 | 64.1561 | 929.2287
2032-06-22 06:00 | 3158.41 | 1 | 83.761 | 64.1561 | 925.6386
2032-06-23 07:00 | 5111.31 | 1.5599 | 84.069 | 64.1561 | 1497.9771
2032-06-24 08:00 | 5869.74 | 1.8926 | 83.5434 | 64.1561 | 1720.251
2032-06-25 09:00 | 7538.64 | 2.5521 | 83.1111 | 64.1561 | 2209.3573
2032-06-26 10:00 | 9323.03 | 3.1845 | 83.2402 | 64.1561 | 2732.3104
2032-06-27 11:00 | 11060.8 | 3.6938 | 83.8451 | 64.1561 | 3241.6005
2032-06-28 12:00 | 12304.6 | 3.975 | 84.6401 | 64.1561 | 3606.1223
2032-06-29 13:00 | 12780.8 | 4.1772 | 84.8771 | 64.1561 | 3745.6827
2032-06-30 14:00 | 13724.5 | 4.4858 | 85.1779 | 64.1561 | 4022.2539
2032-07-01 15:00 | 15602.9 | 5.078 | 85.5518 | 64.1561 | 4572.7586
2032-07-02 16:00 | 15984.7 | 5.2031 | 85.9853 | 64.1561 | 4684.6531
2032-07-03 17:00 | 15973.8 | 5.1639 | 86.4078 | 64.1561 | 4681.4587
2032-07-04 18:00 | 13744.2 | 4.4554 | 86.6356 | 64.1561 | 4028.0274
2032-07-05 19:00 | 11580.1 | 3.6987 | 86.8006 | 64.1561 | 3393.7923
2032-07-06 20:00 | 8570.83 | 2.6844 | 86.877 | 64.1561 | 2511.8623
2032-07-07 21:00 | 7245.5 | 2.2347 | 86.679 | 64.1561 | 2123.4464
2032-07-08 22:00 | 4975.3 | 1.5012 | 86.6091 | 64.1561 | 1458.1165
2032-07-09 23:00 | 3781.79 | 1.164 | 85.8933 | 64.1561 | 1108.3332
2032-07-11 | 3146.12 | 1 | 85.7215 | 64.1561 | 922.0368
2032-07-12 01:00 | 3135.63 | 1 | 91.6786 | 64.1561 | 918.9624
2032-07-13 02:00 | 3167.79 | 1 | 71.4628 | 64.1561 | 928.3876
2032-07-14 03:00 | 3134.66 | 1 | 71.2835 | 64.1561 | 918.6782
2032-07-15 04:00 | 3067.79 | 1 | 71.1406 | 64.1561 | 899.0805
2032-07-16 05:00 | 3184.76 | 1 | 89.7832 | 64.1561 | 933.361
2032-07-17 06:00 | 3711.81 | 1.1435 | 84.3037 | 64.1561 | 1087.8241
2032-07-18 07:00 | 5663.71 | 1.7686 | 84.1011 | 64.1561 | 1659.8695
2032-07-19 08:00 | 6443.31 | 2.0718 | 83.9181 | 64.1561 | 1888.3478
2032-07-20 09:00 | 7873.77 | 2.5936 | 83.7841 | 64.1561 | 2307.5742
2032-07-21 10:00 | 9433.8 | 3.1842 | 83.7317 | 64.1561 | 2764.7739
2032-07-22 11:00 | 11441.9 | 3.8217 | 84.1689 | 64.1561 | 3353.2899
2032-07-23 12:00 | 12712.8 | 4.1387 | 84.8898 | 64.1561 | 3725.7539
2032-07-24 13:00 | 13355.8 | 4.2928 | 85.4298 | 64.1561 | 3914.1986
2032-07-25 14:00 | 14112.1 | 4.5495 | 85.7111 | 64.1561 | 4135.8482
2032-07-26 15:00 | 15714.3 | 5.078 | 85.9777 | 64.1561 | 4605.4067
2032-07-27 16:00 | 15689.6 | 5.2041 | 86.0592 | 64.1561 | 4598.1679
2032-07-28 17:00 | 16056.1 | 5.1422 | 86.7365 | 64.1561 | 4705.5784
2032-07-29 18:00 | 14054.3 | 4.5312 | 86.9032 | 64.1561 | 4118.9087
2032-07-30 19:00 | 12082.1 | 3.8303 | 87.1016 | 64.1561 | 3540.914
2032-07-31 20:00 | 9523.41 | 2.9545 | 87.2241 | 64.1561 | 2791.036
2032-08-01 21:00 | 8094.85 | 2.5414 | 86.7513 | 64.1561 | 2372.3664
2032-08-02 22:00 | 6141.07 | 1.8121 | 87.2421 | 64.1561 | 1799.77
2032-08-03 23:00 | 4747.62 | 1.4105 | 86.7501 | 64.1561 | 1391.3901
2032-08-05 | 3787.15 | 1.1736 | 85.8109 | 64.1561 | 1109.9041
2032-08-06 01:00 | 3174.68 | 1.0013 | 85.2387 | 64.1561 | 930.4069
2032-08-07 02:00 | 3263.52 | 1 | 89.4573 | 64.1561 | 956.4433
2032-08-08 03:00 | 3208.15 | 1 | 91.8885 | 64.1561 | 940.216
2032-08-09 04:00 | 3219.22 | 1 | 71.3857 | 64.1561 | 943.4602
2032-08-10 05:00 | 3199.62 | 1 | 71.245 | 64.1561 | 937.7161
2032-08-11 06:00 | 4046.48 | 1.2237 | 84.8361 | 64.1561 | 1185.9062
2032-08-12 07:00 | 5894.09 | 1.8798 | 84.125 | 64.1561 | 1727.3873
2032-08-13 08:00 | 6052.56 | 1.9602 | 84.1187 | 64.1561 | 1773.8302
2032-08-14 09:00 | 7720.62 | 2.5889 | 83.7887 | 64.1561 | 2262.6904
2032-08-15 10:00 | 9611.03 | 3.2446 | 83.9249 | 64.1561 | 2816.7148
2032-08-16 11:00 | 10947.3 | 3.7464 | 84.1125 | 64.1561 | 3208.3369
2032-08-17 12:00 | 11877 | 4.0665 | 84.4495 | 64.1561 | 3480.8051
2032-08-18 13:00 | 12555.6 | 4.1288 | 85.2154 | 64.1561 | 3679.6831
2032-08-19 14:00 | 13455.1 | 4.3452 | 85.7107 | 64.1561 | 3943.3006
2032-08-20 15:00 | 14604.4 | 4.6301 | 86.2158 | 64.1561 | 4280.1271
2032-08-21 16:00 | 16444.3 | 5.2755 | 86.3789 | 64.1561 | 4819.3486
2032-08-22 17:00 | 15044.1 | 4.8792 | 86.6689 | 64.1561 | 4408.9905
2032-08-23 18:00 | 13688.6 | 4.3526 | 87.0443 | 64.1561 | 4011.7326
2032-08-24 19:00 | 11906.1 | 3.7126 | 87.2684 | 64.1561 | 3489.3335
2032-08-25 20:00 | 10547.4 | 3.2773 | 87.199 | 64.1561 | 3091.1378
2032-08-26 21:00 | 9463.51 | 2.9179 | 87.1251 | 64.1561 | 2773.481
2032-08-27 22:00 | 8839.82 | 2.7001 | 87.0286 | 64.1561 | 2590.6955
2032-08-28 23:00 | 5963.51 | 1.8011 | 87.0103 | 64.1561 | 1747.7323
2032-08-30 | 5337.31 | 1.5645 | 86.9895 | 64.1561 | 1564.2112
2032-08-31 01:00 | 4634.91 | 1.4206 | 86.1084 | 64.1561 | 1358.358
2032-09-01 02:00 | 4415.08 | 1.3751 | 85.655 | 64.1561 | 1293.9322
2032-09-02 03:00 | 4423.17 | 1.3679 | 85.5278 | 64.1561 | 1296.3032
2032-09-03 04:00 | 4564.09 | 1.4017 | 85.4252 | 64.1561 | 1337.6027
2032-09-04 05:00 | 5412.93 | 1.7281 | 84.8385 | 64.1561 | 1586.3732
2032-09-05 06:00 | 6439.46 | 2.1415 | 84.3532 | 64.1561 | 1887.2194
2032-09-06 07:00 | 7619.04 | 2.5429 | 84.4007 | 64.1561 | 2232.9202
2032-09-07 08:00 | 8251.5 | 2.7303 | 84.6676 | 64.1561 | 2418.2759
2032-09-08 09:00 | 10311.6 | 3.4207 | 84.7805 | 64.1561 | 3022.0316
2032-09-09 10:00 | 11588.5 | 3.9158 | 84.8688 | 64.1561 | 3396.2541
2032-09-10 11:00 | 12690.1 | 4.3521 | 85.0304 | 64.1561 | 3719.1012
2032-09-11 12:00 | 13869.2 | 4.6059 | 85.7162 | 64.1561 | 4064.6613
2032-09-12 13:00 | 14847.4 | 4.7642 | 86.4659 | 64.1561 | 4351.3434
2032-09-13 14:00 | 15537.5 | 4.9617 | 86.8704 | 64.1561 | 4553.5918
2032-09-14 15:00 | 16820.4 | 5.4893 | 86.9008 | 64.1561 | 4929.5726
2032-09-15 16:00 | 17484.5 | 5.5491 | 87.584 | 64.1561 | 5124.2011
2032-09-16 17:00 | 17157.3 | 5.5051 | 87.7705 | 64.1561 | 5028.3083
2032-09-17 18:00 | 15530.2 | 4.877 | 88.2372 | 64.1561 | 4551.4523
2032-09-18 19:00 | 13632.2 | 4.2797 | 88.2419 | 64.1561 | 3995.2034
2032-09-19 20:00 | 10597.7 | 3.3324 | 88.0942 | 64.1561 | 3105.8793
2032-09-20 21:00 | 9751.64 | 2.9974 | 88.004 | 64.1561 | 2857.9236
2032-09-21 22:00 | 8046.8 | 2.34 | 88.4412 | 64.1561 | 2358.2843
2032-09-22 23:00 | 7266.08 | 2.199 | 87.575 | 64.1561 | 2129.4778
2032-09-24 | 6388.18 | 1.9718 | 87.0257 | 64.1561 | 1872.1907
2032-09-25 01:00 | 5885.2 | 1.7521 | 87.2105 | 64.1561 | 1724.7819
2032-09-26 02:00 | 5335.72 | 1.5983 | 86.9074 | 64.1561 | 1563.7452
2032-09-27 03:00 | 5120.44 | 1.6197 | 85.9833 | 64.1561 | 1500.6528
2032-09-28 04:00 | 5123.18 | 1.6368 | 85.6689 | 64.1561 | 1501.4558
2032-09-29 05:00 | 5786.34 | 1.9122 | 85.1085 | 64.1561 | 1695.8089
2032-09-30 06:00 | 6348.73 | 2.0893 | 85.1104 | 64.1561 | 1860.6291
2032-10-01 07:00 | 7759.23 | 2.5354 | 85.1908 | 64.1561 | 2274.0058
2032-10-02 08:00 | 8551.98 | 2.7771 | 85.4128 | 64.1561 | 2506.3379
2032-10-03 09:00 | 9931.61 | 3.4008 | 84.9379 | 64.1561 | 2910.6676
2032-10-04 10:00 | 11961 | 3.9595 | 85.5572 | 64.1561 | 3505.4231
2032-10-05 11:00 | 13581.5 | 4.4733 | 85.9692 | 64.1561 | 3980.3447
2032-10-06 12:00 | 14727.2 | 4.7574 | 86.5926 | 64.1561 | 4316.1163
2032-10-07 13:00 | 15046.5 | 4.9205 | 86.8048 | 64.1561 | 4409.6939
2032-10-08 14:00 | 15773.3 | 5.2465 | 86.881 | 64.1561 | 4622.6979
2032-10-09 15:00 | 17949.4 | 5.7154 | 87.6775 | 64.1561 | 5260.4499
2032-10-10 16:00 | 18321.9 | 5.7793 | 88.2269 | 64.1561 | 5369.6188
2032-10-11 17:00 | 18186.3 | 5.6839 | 88.6634 | 64.1561 | 5329.8784
2032-10-12 18:00 | 16364.5 | 5.1443 | 88.8104 | 64.1561 | 4795.9615
2032-10-13 19:00 | 14175.2 | 4.3963 | 88.9869 | 64.1561 | 4154.341
2032-10-14 20:00 | 11363.4 | 3.5326 | 88.8099 | 64.1561 | 3330.2838
2032-10-15 21:00 | 10054 | 3.1421 | 88.3827 | 64.1561 | 2946.5365
2032-10-16 22:00 | 7975.61 | 2.4098 | 88.4886 | 64.1561 | 2337.4206
2032-10-17 23:00 | 6762.72 | 1.9846 | 88.4497 | 64.1561 | 1981.9576
2032-10-19 | 6091.61 | 1.8523 | 87.5906 | 64.1561 | 1785.2747
2032-10-20 01:00 | 5598.68 | 1.7273 | 87.0955 | 64.1561 | 1640.8111
2032-10-21 02:00 | 4903.99 | 1.5823 | 86.291 | 64.1561 | 1437.2176
2032-10-22 03:00 | 4453.9 | 1.431 | 86.0618 | 64.1561 | 1305.3092
2032-10-23 04:00 | 3719.27 | 1.1725 | 86.0449 | 64.1561 | 1090.0104
2032-10-24 05:00 | 3778.41 | 1.1721 | 85.9689 | 64.1561 | 1107.3427
2032-10-25 06:00 | 6238.36 | 2.0703 | 84.9417 | 64.1561 | 1828.2828
2032-10-26 07:00 | 8007.29 | 2.6987 | 84.8752 | 64.1561 | 2346.705
2032-10-27 08:00 | 8557.01 | 2.7952 | 85.4758 | 64.1561 | 2507.8121
2032-10-28 09:00 | 10125.2 | 3.3329 | 85.527 | 64.1561 | 2967.4032
2032-10-29 10:00 | 11537.9 | 3.9073 | 85.4585 | 64.1561 | 3381.4247
2032-10-30 11:00 | 13532.8 | 4.3322 | 86.4554 | 64.1561 | 3966.0722
2032-10-31 12:00 | 14117.9 | 4.5695 | 86.719 | 64.1561 | 4137.5481
2032-11-01 13:00 | 14014.9 | 4.6578 | 86.7018 | 64.1561 | 4107.3617
2032-11-02 14:00 | 15165.5 | 5.0064 | 86.9681 | 64.1561 | 4444.5693
2032-11-03 15:00 | 16316.8 | 5.2855 | 87.4567 | 64.1561 | 4781.982
2032-11-04 16:00 | 18359 | 5.9216 | 87.824 | 64.1561 | 5380.4918
2032-11-05 17:00 | 17520.3 | 5.5878 | 88.3934 | 64.1561 | 5134.6931
2032-11-06 18:00 | 16412.8 | 5.1445 | 88.7979 | 64.1561 | 4810.1169
2032-11-07 19:00 | 14316.9 | 4.4739 | 88.8886 | 64.1561 | 4195.8692
2032-11-08 20:00 | 12933.7 | 4.0517 | 88.7451 | 64.1561 | 3790.4933
2032-11-09 21:00 | 11689.4 | 3.6524 | 88.6128 | 64.1561 | 3425.825
2032-11-10 22:00 | 10454.1 | 3.2681 | 88.3913 | 64.1561 | 3063.7943
2032-11-11 23:00 | 7768.61 | 2.266 | 89.0428 | 64.1561 | 2276.7548
2032-11-13 | 6722.73 | 1.9988 | 88.349 | 64.1561 | 1970.2377
2032-11-14 01:00 | 5735.25 | 1.702 | 88.0237 | 64.1561 | 1680.8359
2032-11-15 02:00 | 5100.11 | 1.5513 | 87.3856 | 64.1561 | 1494.6947
2032-11-16 03:00 | 4405.08 | 1.3593 | 86.9053 | 64.1561 | 1291.0015
2032-11-17 04:00 | 3762.07 | 1.1933 | 86.2503 | 64.1561 | 1102.5539
2032-11-18 05:00 | 3617.62 | 1.1606 | 85.8339 | 64.1561 | 1060.2198
2032-11-19 06:00 | 5599.07 | 1.8468 | 85.2675 | 64.1561 | 1640.9254
2032-11-20 07:00 | 7310.98 | 2.5306 | 84.7509 | 64.1561 | 2142.6367
2032-11-21 08:00 | 8027.01 | 2.6145 | 85.6281 | 64.1561 | 2352.4844
2032-11-22 09:00 | 9853.87 | 3.2563 | 85.574 | 64.1561 | 2887.8842
2032-11-23 10:00 | 11826.3 | 3.9781 | 85.6185 | 64.1561 | 3465.9464
2032-11-24 11:00 | 13069.1 | 4.4333 | 85.9055 | 64.1561 | 3830.1751
2032-11-25 12:00 | 14560.4 | 4.7311 | 86.7563 | 64.1561 | 4267.232
2032-11-26 13:00 | 15097.7 | 4.9181 | 87.1016 | 64.1561 | 4424.6991
2032-11-27 14:00 | 15781 | 5.2003 | 87.2794 | 64.1561 | 4624.9546
2032-11-28 15:00 | 16668.7 | 5.4073 | 87.7516 | 64.1561 | 4885.1137
2032-11-29 16:00 | 18635.5 | 5.9322 | 88.2697 | 64.1561 | 5461.5259
2032-11-30 17:00 | 17591.7 | 5.5926 | 88.7299 | 64.1561 | 5155.6183
2032-12-01 18:00 | 16277.2 | 4.9315 | 89.5096 | 64.1561 | 4770.3764
2032-12-02 19:00 | 13737.6 | 4.2549 | 89.2403 | 64.1561 | 4026.0931
2032-12-03 20:00 | 11898.2 | 3.6197 | 89.2805 | 64.1561 | 3487.0182
2032-12-04 21:00 | 10116.6 | 3.227 | 88.4227 | 64.1561 | 2964.8828
2032-12-05 22:00 | 9267.37 | 2.8709 | 88.4353 | 64.1561 | 2715.998
2032-12-06 23:00 | 6608.73 | 1.9871 | 88.5389 | 64.1561 | 1936.8276
2032-12-08 | 6121.99 | 1.7301 | 88.8924 | 64.1561 | 1794.1782
2032-12-09 01:00 | 5316.31 | 1.6217 | 87.5431 | 64.1561 | 1558.0567
2032-12-10 02:00 | 4678.18 | 1.448 | 87.0689 | 64.1561 | 1371.0392
2032-12-11 03:00 | 4466.25 | 1.3962 | 86.6618 | 64.1561 | 1308.9287
2032-12-12 04:00 | 4395.96 | 1.3805 | 86.3534 | 64.1561 | 1288.3287
2032-12-13 05:00 | 5033.85 | 1.6226 | 85.8592 | 64.1561 | 1475.2758
2032-12-14 06:00 | 5652.24 | 1.8458 | 85.6161 | 64.1561 | 1656.508
2032-12-15 07:00 | 6557.78 | 2.1576 | 85.5056 | 64.1561 | 1921.8956
2032-12-16 08:00 | 6958.75 | 2.2714 | 85.6589 | 64.1561 | 2039.4083
2032-12-17 09:00 | 9013.17 | 3.004 | 85.4559 | 64.1561 | 2641.4994
2032-12-18 10:00 | 10411.1 | 3.5645 | 85.3733 | 64.1561 | 3051.1922
2032-12-19 11:00 | 12144.8 | 4.0928 | 85.8337 | 64.1561 | 3559.2895
2032-12-20 12:00 | 13217.6 | 4.3239 | 86.5166 | 64.1561 | 3873.6962
2032-12-21 13:00 | 14147.7 | 4.6018 | 86.9059 | 64.1561 | 4146.2816
2032-12-22 14:00 | 14971.8 | 4.9553 | 87.0167 | 64.1561 | 4387.8014
2032-12-23 15:00 | 17056.6 | 5.5624 | 87.481 | 64.1561 | 4998.796
2032-12-24 16:00 | 17472.9 | 5.6489 | 88.007 | 64.1561 | 5120.8015
2032-12-25 17:00 | 17326.5 | 5.5631 | 88.4088 | 64.1561 | 5077.8959
2032-12-26 18:00 | 15728.8 | 5.0303 | 88.6694 | 64.1561 | 4609.6562
2032-12-27 19:00 | 14144.5 | 4.3034 | 89.315 | 64.1561 | 4145.3437
2032-12-28 20:00 | 11483.7 | 3.4792 | 89.2891 | 64.1561 | 3365.5402
2032-12-29 21:00 | 9720.4 | 3.0371 | 88.5884 | 64.1561 | 2848.768
2032-12-30 22:00 | 7450.51 | 2.2447 | 88.7034 | 64.1561 | 2183.5289
2032-12-31 23:00 | 6421.61 | 1.9357 | 88.2534 | 64.1561 | 1881.9881
2033-01-02 | 5369.97 | 1.6182 | 87.8812 | 64.1561 | 1573.7829
2033-01-03 01:00 | 4671.4 | 1.442 | 87.2183 | 64.1561 | 1369.0522
2033-01-04 02:00 | 4068.27 | 1.2959 | 86.5209 | 64.1561 | 1192.2922
2033-01-05 03:00 | 3999.96 | 1.2584 | 86.3768 | 64.1561 | 1172.2726
2033-01-06 04:00 | 4034.68 | 1.2651 | 86.2021 | 64.1561 | 1182.448
2033-01-07 05:00 | 4641.98 | 1.4753 | 85.8587 | 64.1561 | 1360.43
2033-01-08 06:00 | 5249.71 | 1.6654 | 85.8023 | 64.1561 | 1538.5381
2033-01-09 07:00 | 6212.3 | 2.1271 | 84.8715 | 64.1561 | 1820.6454
2033-01-10 08:00 | 6813.17 | 2.2696 | 85.2622 | 64.1561 | 1996.743
2033-01-11 09:00 | 8241.61 | 2.8466 | 84.9193 | 64.1561 | 2415.3775
2033-01-12 10:00 | 10056.4 | 3.3522 | 85.5142 | 64.1561 | 2947.2399
2033-01-13 11:00 | 11664.3 | 3.8972 | 85.7773 | 64.1561 | 3418.4689
2033-01-14 12:00 | 12705.3 | 4.1689 | 86.3267 | 64.1561 | 3723.5559
2033-01-15 13:00 | 13364.9 | 4.3189 | 86.8194 | 64.1561 | 3916.8655
2033-01-16 14:00 | 14426.8 | 4.5922 | 87.278 | 64.1561 | 4228.0777
2033-01-17 15:00 | 15945.3 | 5.1807 | 87.3198 | 64.1561 | 4673.1061
2033-01-18 16:00 | 16098.3 | 5.2317 | 87.6732 | 64.1561 | 4717.946
2033-01-19 17:00 | 15582.9 | 4.9512 | 88.1878 | 64.1561 | 4566.8972
2033-01-20 18:00 | 14192.9 | 4.3908 | 88.6428 | 64.1561 | 4159.5284
2033-01-21 19:00 | 12371.9 | 3.8723 | 88.4786 | 64.1561 | 3625.846
2033-01-22 20:00 | 9638.86 | 2.9823 | 88.4792 | 64.1561 | 2824.871
2033-01-23 21:00 | 8477.81 | 2.587 | 88.294 | 64.1561 | 2484.6008
2033-01-24 22:00 | 6178.65 | 1.8663 | 88.1127 | 64.1561 | 1810.7836
2033-01-25 23:00 | 5476.16 | 1.5918 | 88.183 | 64.1561 | 1604.9041
2033-01-27 | 4577.8 | 1.4164 | 87.0199 | 64.1561 | 1341.6207
2033-01-28 01:00 | 3576.77 | 1.1121 | 86.643 | 64.1561 | 1048.2478
2033-01-29 02:00 | 3208.36 | 1 | 86.6135 | 64.1561 | 940.2775
2033-01-30 03:00 | 3130.6 | 1 | 86.1816 | 64.1561 | 917.4883
2033-01-31 04:00 | 3367.44 | 1.0607 | 85.668 | 64.1561 | 986.8992
2033-02-01 05:00 | 4146.59 | 1.3255 | 85.3365 | 64.1561 | 1215.2456
2033-02-02 06:00 | 5201.52 | 1.6373 | 85.476 | 64.1561 | 1524.415
2033-02-03 07:00 | 6392.27 | 2.1448 | 84.7587 | 64.1561 | 1873.3894
2033-02-04 08:00 | 6875.38 | 2.3314 | 84.7822 | 64.1561 | 2014.975
2033-02-05 09:00 | 8879.84 | 3.0054 | 84.9101 | 64.1561 | 2602.4242
2033-02-06 10:00 | 10555.4 | 3.5818 | 85.16 | 64.1561 | 3093.4824
2033-02-07 11:00 | 11910.8 | 4.0329 | 85.5241 | 64.1561 | 3490.7109
2033-02-08 12:00 | 13070.9 | 4.2807 | 86.2509 | 64.1561 | 3830.7026
2033-02-09 13:00 | 13761.7 | 4.4433 | 86.7595 | 64.1561 | 4033.1561
2033-02-10 14:00 | 14150.6 | 4.6151 | 86.9473 | 64.1561 | 4147.1315
2033-02-11 15:00 | 15522.1 | 4.9708 | 87.4006 | 64.1561 | 4549.0785
2033-02-12 16:00 | 15665.3 | 4.9746 | 87.8184 | 64.1561 | 4591.0462
2033-02-13 17:00 | 14490.4 | 4.5471 | 88.1954 | 64.1561 | 4246.717
2033-02-14 18:00 | 12752.5 | 3.961 | 88.3567 | 64.1561 | 3737.3888
2033-02-15 19:00 | 11255.5 | 3.4986 | 88.2264 | 64.1561 | 3298.6614
2033-02-16 20:00 | 8999.82 | 2.8208 | 87.9604 | 64.1561 | 2637.5869
2033-02-17 21:00 | 8059.41 | 2.4673 | 87.9232 | 64.1561 | 2361.9799
2033-02-18 22:00 | 5876.56 | 1.7368 | 88.0928 | 64.1561 | 1722.2497
2033-02-19 23:00 | 5065.2 | 1.4817 | 87.8185 | 64.1561 | 1484.4636
2033-02-21 | 4277.26 | 1.305 | 86.9258 | 64.1561 | 1253.5412
2033-02-22 01:00 | 3505.52 | 1.1361 | 85.8763 | 64.1561 | 1027.3665
2033-02-23 02:00 | 3262.18 | 1 | 86.7887 | 64.1561 | 956.0506
2033-02-24 03:00 | 3151.13 | 1 | 85.6234 | 64.1561 | 923.505
2033-02-25 04:00 | 3342.13 | 1.0608 | 85.407 | 64.1561 | 979.4816
2033-02-26 05:00 | 4370.26 | 1.3755 | 85.3741 | 64.1561 | 1280.7968
2033-02-27 06:00 | 5264.03 | 1.6575 | 85.3661 | 64.1561 | 1542.7349
2033-02-28 07:00 | 6097.4 | 2.0309 | 84.7499 | 64.1561 | 1786.9715
2033-03-01 08:00 | 6281.83 | 1.9689 | 85.5954 | 64.1561 | 1841.0226
2033-03-02 09:00 | 8206.9 | 2.7926 | 84.6644 | 64.1561 | 2405.205
2033-03-03 10:00 | 10022.6 | 3.4086 | 84.9137 | 64.1561 | 2937.3341
2033-03-04 11:00 | 10967 | 3.6418 | 85.5211 | 64.1561 | 3214.1104
2033-03-05 12:00 | 11812.2 | 3.9561 | 85.6964 | 64.1561 | 3461.8141
2033-03-06 13:00 | 12836.3 | 4.3012 | 85.951 | 64.1561 | 3761.9482
2033-03-07 14:00 | 14321 | 4.6541 | 86.614 | 64.1561 | 4197.0708
2033-03-08 15:00 | 16430 | 5.2905 | 87.0724 | 64.1561 | 4815.1577
2033-03-09 16:00 | 16643.1 | 5.4535 | 87.3155 | 64.1561 | 4877.6111
2033-03-10 17:00 | 16861.9 | 5.5025 | 87.6815 | 64.1561 | 4941.7351
2033-03-11 18:00 | 15315.1 | 4.8317 | 88.3591 | 64.1561 | 4488.4127
2033-03-12 19:00 | 13682.9 | 4.2252 | 88.6897 | 64.1561 | 4010.0621
2033-03-13 20:00 | 10939.3 | 3.3394 | 88.7735 | 64.1561 | 3205.9924
2033-03-14 21:00 | 9270.85 | 2.9371 | 88.0038 | 64.1561 | 2717.0179
2033-03-15 22:00 | 7404.79 | 2.1937 | 88.5407 | 64.1561 | 2170.1297
2033-03-16 23:00 | 6562.27 | 1.9438 | 88.161 | 64.1561 | 1923.2115
2033-03-18 | 5610.12 | 1.716 | 87.4334 | 64.1561 | 1644.1639
2033-03-19 01:00 | 4841.73 | 1.4606 | 87.3145 | 64.1561 | 1418.971
2033-03-20 02:00 | 4513.35 | 1.3895 | 86.7778 | 64.1561 | 1322.7323
2033-03-21 03:00 | 4482.2 | 1.4055 | 86.3084 | 64.1561 | 1313.6031
2033-03-22 04:00 | 4857.27 | 1.5102 | 86.2422 | 64.1561 | 1423.5253
2033-03-23 05:00 | 5690.98 | 1.8457 | 85.6072 | 64.1561 | 1667.8616
2033-03-24 06:00 | 5897.35 | 1.9521 | 85.3528 | 64.1561 | 1728.3427
2033-03-25 07:00 | 7290.58 | 2.4505 | 85.1531 | 64.1561 | 2136.6581
2033-03-26 08:00 | 7915.6 | 2.6153 | 85.4908 | 64.1561 | 2319.8334
2033-03-27 09:00 | 9654.9 | 3.2439 | 85.4235 | 64.1561 | 2829.5719
2033-03-28 10:00 | 11519.9 | 3.8964 | 85.5996 | 64.1561 | 3376.1494
2033-03-29 11:00 | 13230.3 | 4.5072 | 85.8631 | 64.1561 | 3877.4182
2033-03-30 12:00 | 14897.8 | 4.8165 | 86.8784 | 64.1561 | 4366.1142
2033-03-31 13:00 | 15319.5 | 4.9908 | 87.2157 | 64.1561 | 4489.7023
2033-04-01 14:00 | 16440.4 | 5.2987 | 87.6754 | 64.1561 | 4818.2056
2033-04-02 15:00 | 17989.7 | 5.7342 | 88.1486 | 64.1561 | 5272.2606
2033-04-03 16:00 | 17647.9 | 5.7795 | 88.2352 | 64.1561 | 5172.0889
2033-04-04 17:00 | 18219.3 | 5.7067 | 89.0076 | 64.1561 | 5339.5497
2033-04-05 18:00 | 15339.5 | 4.648 | 89.6844 | 64.1561 | 4495.5637
2033-04-06 19:00 | 12741.2 | 3.8553 | 89.607 | 64.1561 | 3734.0771
2033-04-07 20:00 | 10144.2 | 2.9961 | 89.6494 | 64.1561 | 2972.9715
2033-04-08 21:00 | 8416.3 | 2.6155 | 88.5945 | 64.1561 | 2466.574
2033-04-09 22:00 | 6333.22 | 1.9618 | 88.2463 | 64.1561 | 1856.0836
2033-04-10 23:00 | 5429.21 | 1.5697 | 88.6531 | 64.1561 | 1591.1444
2033-04-12 | 4610.38 | 1.4334 | 87.3044 | 64.1561 | 1351.169
2033-04-13 01:00 | 4193 | 1.3229 | 86.7824 | 64.1561 | 1228.847
2033-04-14 02:00 | 3660.66 | 1.1529 | 86.5235 | 64.1561 | 1072.8335
2033-04-15 03:00 | 3331.24 | 1.0271 | 86.5085 | 64.1561 | 976.2901
2033-04-16 04:00 | 3084.18 | 1 | 86.0031 | 64.1561 | 903.8839
2033-04-17 05:00 | 3045.5 | 1 | 86.4311 | 64.1561 | 892.5479
2033-04-18 06:00 | 4920.95 | 1.5955 | 85.2257 | 64.1561 | 1442.1881
2033-04-19 07:00 | 6712.31 | 2.3392 | 84.4471 | 64.1561 | 1967.1839
2033-04-20 08:00 | 7487.85 | 2.4091 | 85.5896 | 64.1561 | 2194.4722
2033-04-21 09:00 | 8908.44 | 2.933 | 85.4736 | 64.1561 | 2610.806
2033-04-22 10:00 | 10811.5 | 3.5868 | 85.626 | 64.1561 | 3168.5379
2033-04-23 11:00 | 12966.1 | 4.1648 | 86.3769 | 64.1561 | 3799.9888
2033-04-24 12:00 | 13663.6 | 4.4426 | 86.6717 | 64.1561 | 4004.4059
2033-04-25 13:00 | 14114.6 | 4.6583 | 86.8246 | 64.1561 | 4136.5809
2033-04-26 14:00 | 15107.9 | 4.9278 | 87.2302 | 64.1561 | 4427.6884
2033-04-27 15:00 | 15174.8 | 4.9326 | 87.5715 | 64.1561 | 4447.2949
2033-04-28 16:00 | 17785.3 | 5.6806 | 87.9912 | 64.1561 | 5212.3569
2033-04-29 17:00 | 15783.4 | 5.0852 | 88.328 | 64.1561 | 4625.6579
2033-04-30 18:00 | 13687.2 | 4.3633 | 88.5369 | 64.1561 | 4011.3223
2033-05-01 19:00 | 12077.1 | 3.892 | 88.259 | 64.1561 | 3539.4486
2033-05-02 20:00 | 10834.6 | 3.4304 | 88.301 | 64.1561 | 3175.3078
2033-05-03 21:00 | 10056.6 | 3.0993 | 88.4565 | 64.1561 | 2947.2985
2033-05-04 22:00 | 9212.47 | 2.916 | 87.9093 | 64.1561 | 2699.9084
2033-05-05 23:00 | 6612.73 | 1.9657 | 88.5038 | 64.1561 | 1937.9999
2033-05-07 | 5568 | 1.5971 | 88.5771 | 64.1561 | 1631.8197
2033-05-08 01:00 | 4616.22 | 1.4569 | 86.9918 | 64.1561 | 1352.8805
2033-05-09 02:00 | 3985.99 | 1.258 | 86.6837 | 64.1561 | 1168.1784
2033-05-10 03:00 | 3676.44 | 1.1618 | 86.3765 | 64.1561 | 1077.4582
2033-05-11 04:00 | 3340.89 | 1.0709 | 85.923 | 64.1561 | 979.1182
2033-05-12 05:00 | 3447.94 | 1.0773 | 86.0195 | 64.1561 | 1010.4915
2033-05-13 06:00 | 5284.82 | 1.693 | 85.55 | 64.1561 | 1548.8279
2033-05-14 07:00 | 6750.08 | 2.2249 | 85.2811 | 64.1561 | 1978.2532
2033-05-15 08:00 | 6843.73 | 2.121 | 86.2056 | 64.1561 | 2005.6993
2033-05-16 09:00 | 7901.83 | 2.5548 | 85.737 | 64.1561 | 2315.7978
2033-05-17 10:00 | 9587.68 | 3.0974 | 85.8721 | 64.1561 | 2809.8716
2033-05-18 11:00 | 11414.2 | 3.7584 | 85.912 | 64.1561 | 3345.1718
2033-05-19 12:00 | 12451.7 | 4.0405 | 86.4218 | 64.1561 | 3649.233
2033-05-20 13:00 | 12784.5 | 4.215 | 86.5287 | 64.1561 | 3746.7671
2033-05-21 14:00 | 13639.6 | 4.3835 | 87.0627 | 64.1561 | 3997.3722
2033-05-22 15:00 | 13950 | 4.5813 | 87.0585 | 64.1561 | 4088.3414
2033-05-23 16:00 | 16914 | 5.5537 | 87.2527 | 64.1561 | 4957.0041
2033-05-24 17:00 | 15768.1 | 5.1113 | 87.8834 | 64.1561 | 4621.1739
2033-05-25 18:00 | 14527.1 | 4.6248 | 88.2831 | 64.1561 | 4257.4727
2033-05-26 19:00 | 12968.4 | 4.0596 | 88.4984 | 64.1561 | 3800.6629
2033-05-27 20:00 | 11619.4 | 3.6364 | 88.421 | 64.1561 | 3405.31
2033-05-28 21:00 | 10392.9 | 3.3092 | 88.0773 | 64.1561 | 3045.8583
2033-05-29 22:00 | 9681.33 | 3.0495 | 87.9888 | 64.1561 | 2837.3177
2033-05-30 23:00 | 7469.24 | 2.1794 | 88.7948 | 64.1561 | 2189.0182
2033-06-01 | 6646.77 | 2.0399 | 87.7896 | 64.1561 | 1947.976
2033-06-02 01:00 | 5980.96 | 1.8388 | 87.4883 | 64.1561 | 1752.8463
2033-06-03 02:00 | 5725.92 | 1.7871 | 87.0667 | 64.1561 | 1678.1015
2033-06-04 03:00 | 5411.58 | 1.7515 | 86.4376 | 64.1561 | 1585.9775
2033-06-05 04:00 | 5561.59 | 1.7229 | 86.7776 | 64.1561 | 1629.9411
2033-06-06 05:00 | 6114.47 | 1.9405 | 86.3641 | 64.1561 | 1791.9743
2033-06-07 06:00 | 6255.62 | 2.07 | 85.8273 | 64.1561 | 1833.3412
2033-06-08 07:00 | 7348.86 | 2.36 | 86.1496 | 64.1561 | 2153.7383
2033-06-09 08:00 | 7857.64 | 2.5412 | 86.1445 | 64.1561 | 2302.847
2033-06-10 09:00 | 9820.52 | 3.2684 | 85.887 | 64.1561 | 2878.1103
2033-06-11 10:00 | 11698.2 | 3.8712 | 86.1939 | 64.1561 | 3428.404
2033-06-12 11:00 | 13063.9 | 4.2745 | 86.6692 | 64.1561 | 3828.6512
2033-06-13 12:00 | 13855.7 | 4.4415 | 87.2659 | 64.1561 | 4060.7048
2033-06-14 13:00 | 13444.8 | 4.4701 | 87.1341 | 64.1561 | 3940.2819
2033-06-15 14:00 | 14248.9 | 4.7356 | 87.3023 | 64.1561 | 4175.9404
2033-06-16 15:00 | 16269.4 | 5.3694 | 87.5942 | 64.1561 | 4768.0905
2033-06-17 16:00 | 17248.2 | 5.523 | 88.3137 | 64.1561 | 5054.9484
2033-06-18 17:00 | 17300 | 5.5002 | 88.7326 | 64.1561 | 5070.1295
2033-06-19 18:00 | 15226.9 | 4.905 | 88.8102 | 64.1561 | 4462.5639
2033-06-20 19:00 | 13605 | 4.2773 | 89.0911 | 64.1561 | 3987.2319
2033-06-21 20:00 | 11058.9 | 3.4873 | 88.9448 | 64.1561 | 3241.0437
2033-06-22 21:00 | 10170.9 | 3.1287 | 88.9431 | 64.1561 | 2980.7965
2033-06-23 22:00 | 7796.87 | 2.4343 | 88.485 | 64.1561 | 2285.037
2033-06-24 23:00 | 6808.45 | 2.1271 | 88.053 | 64.1561 | 1995.3597
2033-06-26 | 6397.74 | 1.8568 | 88.6489 | 64.1561 | 1874.9925
2033-06-27 01:00 | 5738.73 | 1.7033 | 88.0988 | 64.1561 | 1681.8557
2033-06-28 02:00 | 5031.33 | 1.5521 | 87.3682 | 64.1561 | 1474.5373
2033-06-29 03:00 | 4923.6 | 1.5433 | 86.8961 | 64.1561 | 1442.9647
2033-06-30 04:00 | 4640.22 | 1.506 | 86.2739 | 64.1561 | 1359.9142
2033-07-01 05:00 | 5272.7 | 1.7002 | 86.1611 | 64.1561 | 1545.2758
2033-07-02 06:00 | 5669.52 | 1.8429 | 85.9834 | 64.1561 | 1661.5723
2033-07-03 07:00 | 6820.29 | 2.235 | 85.8428 | 64.1561 | 1998.8297
2033-07-04 08:00 | 7392.76 | 2.4192 | 85.9456 | 64.1561 | 2166.6041
2033-07-05 09:00 | 9087.6 | 3.0539 | 85.7089 | 64.1561 | 2663.3127
2033-07-06 10:00 | 10920.4 | 3.6194 | 86.092 | 64.1561 | 3200.4533
2033-07-07 11:00 | 11976.4 | 3.8887 | 86.6543 | 64.1561 | 3509.9364
2033-07-08 12:00 | 11884.5 | 3.8363 | 87.0178 | 64.1561 | 3483.0031
2033-07-09 13:00 | 12098.1 | 3.9499 | 87.0449 | 64.1561 | 3545.6031
2033-07-10 14:00 | 13124.2 | 4.2359 | 87.3318 | 64.1561 | 3846.3233
2033-07-11 15:00 | 15287.9 | 5.0932 | 87.1633 | 64.1561 | 4480.4412
2033-07-12 16:00 | 16537.8 | 5.3301 | 87.9184 | 64.1561 | 4846.7507
2033-07-13 17:00 | 16379.9 | 5.274 | 88.2803 | 64.1561 | 4800.4748
2033-07-14 18:00 | 14754.1 | 4.5866 | 88.9455 | 64.1561 | 4323.9999
2033-07-15 19:00 | 13050.3 | 4.0994 | 88.8345 | 64.1561 | 3824.6654
2033-07-16 20:00 | 10007.9 | 3.1509 | 88.7129 | 64.1561 | 2933.026
2033-07-17 21:00 | 8487.63 | 2.7085 | 88.1833 | 64.1561 | 2487.4788
2033-07-18 22:00 | 6796.3 | 1.9891 | 88.9223 | 64.1561 | 1991.7989
2033-07-19 23:00 | 5675.37 | 1.6851 | 88.3326 | 64.1561 | 1663.2868
2033-07-21 | 4920.14 | 1.5033 | 87.597 | 64.1561 | 1441.9507
2033-07-22 01:00 | 4181.77 | 1.2911 | 87.1512 | 64.1561 | 1225.5558
2033-07-23 02:00 | 3783.02 | 1.1654 | 86.9023 | 64.1561 | 1108.6937
2033-07-24 03:00 | 3694.44 | 1.1947 | 86.0437 | 64.1561 | 1082.7335
2033-07-25 04:00 | 3933.98 | 1.2108 | 86.4498 | 64.1561 | 1152.9357
2033-07-26 05:00 | 4898.13 | 1.5324 | 86.0961 | 64.1561 | 1435.5002
2033-07-27 06:00 | 5205.44 | 1.6667 | 85.7896 | 64.1561 | 1525.5639
2033-07-28 07:00 | 6082.65 | 2.0319 | 85.2632 | 64.1561 | 1782.6487
2033-07-29 08:00 | 6641.25 | 2.2119 | 85.3681 | 64.1561 | 1946.3582
2033-07-30 09:00 | 8225.07 | 2.7713 | 85.312 | 64.1561 | 2410.5301
2033-07-31 10:00 | 10100.6 | 3.4981 | 85.1994 | 64.1561 | 2960.1936
2033-08-01 11:00 | 12129.1 | 4.0351 | 85.9661 | 64.1561 | 3554.6883
2033-08-02 12:00 | 12988.2 | 4.27 | 86.507 | 64.1561 | 3806.4657
2033-08-03 13:00 | 13230.9 | 4.2664 | 87.0796 | 64.1561 | 3877.594
2033-08-04 14:00 | 14300 | 4.5713 | 87.4365 | 64.1561 | 4190.9163
2033-08-05 15:00 | 16047.5 | 5.1829 | 87.6006 | 64.1561 | 4703.058
2033-08-06 16:00 | 16348.5 | 5.2974 | 87.9462 | 64.1561 | 4791.2724
2033-08-07 17:00 | 16233.9 | 5.118 | 88.5443 | 64.1561 | 4757.6864
2033-08-08 18:00 | 13432.8 | 3.9942 | 89.4815 | 64.1561 | 3936.7651
2033-08-09 19:00 | 11684.4 | 3.5197 | 89.1797 | 64.1561 | 3424.3596
2033-08-10 20:00 | 8870.64 | 2.7252 | 88.735 | 64.1561 | 2599.728
2033-08-11 21:00 | 7668.24 | 2.4073 | 88.0725 | 64.1561 | 2247.3393
2033-08-12 22:00 | 5992.19 | 1.7208 | 88.8819 | 64.1561 | 1756.1375
2033-08-13 23:00 | 5175.61 | 1.5175 | 88.1895 | 64.1561 | 1516.8216
2033-08-15 | 4525.78 | 1.3889 | 87.2567 | 64.1561 | 1326.3752
2033-08-16 01:00 | 4013.97 | 1.2575 | 86.7091 | 64.1561 | 1176.3785
2033-08-17 02:00 | 3635.47 | 1.1627 | 86.208 | 64.1561 | 1065.4511
2033-08-18 03:00 | 3809.12 | 1.2055 | 86.0975 | 64.1561 | 1116.3429
2033-08-19 04:00 | 3843.47 | 1.2285 | 85.8169 | 64.1561 | 1126.4099
2033-08-20 05:00 | 4572.75 | 1.4714 | 85.5906 | 64.1561 | 1340.1407
2033-08-21 06:00 | 5154.95 | 1.6337 | 85.7427 | 64.1561 | 1510.7667
2033-08-22 07:00 | 5463.88 | 1.7385 | 85.7077 | 64.1561 | 1601.3052
2033-08-23 08:00 | 4926.06 | 1.4941 | 86.3419 | 64.1561 | 1443.6857
2033-08-24 09:00 | 5700.45 | 1.8465 | 85.4498 | 64.1561 | 1670.637
2033-08-25 10:00 | 6783.17 | 2.3074 | 84.9062 | 64.1561 | 1987.9509
2033-08-26 11:00 | 8707.17 | 2.941 | 85.0971 | 64.1561 | 2551.8196
2033-08-27 12:00 | 9952.94 | 3.3755 | 85.295 | 64.1561 | 2916.9188
2033-08-28 13:00 | 10844.6 | 3.6343 | 85.6953 | 64.1561 | 3178.2385
2033-08-29 14:00 | 12387.8 | 4.1037 | 86.0834 | 64.1561 | 3630.5058
2033-08-30 15:00 | 14954.8 | 4.9837 | 86.329 | 64.1561 | 4382.8192
2033-08-31 16:00 | 15849 | 5.1573 | 87.0974 | 64.1561 | 4644.8834
2033-09-01 17:00 | 15542.5 | 5.1325 | 87.3063 | 64.1561 | 4555.0571
2033-09-02 18:00 | 14082 | 4.4897 | 87.9584 | 64.1561 | 4127.0268
2033-09-03 19:00 | 12272 | 3.8249 | 88.287 | 64.1561 | 3596.5682
2033-09-04 20:00 | 9683.59 | 2.9253 | 88.6071 | 64.1561 | 2837.9801
2033-09-05 21:00 | 8371.52 | 2.5879 | 88.0196 | 64.1561 | 2453.4503
2033-09-06 22:00 | 6001.32 | 1.7758 | 88.3084 | 64.1561 | 1758.8133
2033-09-07 23:00 | 5013.64 | 1.5146 | 87.6203 | 64.1561 | 1469.3528
2033-09-09 | 4334.55 | 1.349 | 86.8839 | 64.1561 | 1270.3312
2033-09-10 01:00 | 3962.87 | 1.218 | 86.7534 | 64.1561 | 1161.4026
2033-09-11 02:00 | 3599.39 | 1.131 | 86.2414 | 64.1561 | 1054.8771
2033-09-12 03:00 | 3648.3 | 1.1637 | 85.8174 | 64.1561 | 1069.2112
2033-09-13 04:00 | 3853.23 | 1.2004 | 85.9403 | 64.1561 | 1129.2702
2033-09-14 05:00 | 4841.68 | 1.5244 | 85.6799 | 64.1561 | 1418.9563
2033-09-15 06:00 | 5539.07 | 1.7854 | 85.3902 | 64.1561 | 1623.3412
2033-09-16 07:00 | 6570.21 | 2.2005 | 84.977 | 64.1561 | 1925.5385
2033-09-17 08:00 | 6975.1 | 2.3969 | 84.8133 | 64.1561 | 2044.2
2033-09-18 09:00 | 8756.91 | 3.078 | 84.6644 | 64.1561 | 2566.397
2033-09-19 10:00 | 10740.9 | 3.5719 | 85.5616 | 64.1561 | 3147.8471
2033-09-20 11:00 | 12498.9 | 4.0852 | 86.1334 | 64.1561 | 3663.066
2033-09-21 12:00 | 12962 | 4.204 | 86.6355 | 64.1561 | 3798.7872
2033-09-22 13:00 | 13912.3 | 4.4808 | 87.0199 | 64.1561 | 4077.2926
2033-09-23 14:00 | 14882.1 | 4.8209 | 87.2695 | 64.1561 | 4361.513
2033-09-24 15:00 | 17133.5 | 5.5213 | 87.6458 | 64.1561 | 5021.3332
2033-09-25 16:00 | 17375.4 | 5.5866 | 88.129 | 64.1561 | 5092.2271
2033-09-26 17:00 | 17225.6 | 5.5488 | 88.4159 | 64.1561 | 5048.325
2033-09-27 18:00 | 15891.3 | 5.0191 | 88.8795 | 64.1561 | 4657.2803
2033-09-28 19:00 | 13935.8 | 4.3524 | 89.0797 | 64.1561 | 4084.1798
2033-09-29 20:00 | 11119.3 | 3.4262 | 89.1597 | 64.1561 | 3258.7451
2033-09-30 21:00 | 9949.33 | 3.0434 | 88.9197 | 64.1561 | 2915.8608
2033-10-01 22:00 | 7589.13 | 2.2753 | 88.9018 | 64.1561 | 2224.1544
2033-10-02 23:00 | 5778.3 | 1.7461 | 88.3837 | 64.1561 | 1693.4526
2033-10-04 | 5016.58 | 1.5177 | 87.9158 | 64.1561 | 1470.2145
2033-10-05 01:00 | 4235.46 | 1.3172 | 87.2117 | 64.1561 | 1241.2908
2033-10-06 02:00 | 3421.51 | 1.0914 | 86.5913 | 64.1561 | 1002.7456
2033-10-07 03:00 | 3132.13 | 1 | 86.854 | 64.1561 | 917.9367
2033-10-08 04:00 | 3131.41 | 1 | 88.4461 | 64.1561 | 917.7257
2033-10-09 05:00 | 3140.09 | 1 | 88.6805 | 64.1561 | 920.2695
2033-10-10 06:00 | 5001.64 | 1.5288 | 86.1158 | 64.1561 | 1465.836
2033-10-11 07:00 | 6812.92 | 2.2184 | 85.3907 | 64.1561 | 1996.6698
2033-10-12 08:00 | 7350.11 | 2.3626 | 85.7638 | 64.1561 | 2154.1046
2033-10-13 09:00 | 8504.21 | 2.8766 | 85.2978 | 64.1561 | 2492.3379
2033-10-14 10:00 | 10279.3 | 3.4636 | 85.5411 | 64.1561 | 3012.5654
2033-10-15 11:00 | 11708.6 | 3.9602 | 85.8288 | 64.1561 | 3431.4519
2033-10-16 12:00 | 12823.8 | 4.135 | 86.7381 | 64.1561 | 3758.2848
2033-10-17 13:00 | 13071.5 | 4.3043 | 86.8055 | 64.1561 | 3830.8785
2033-10-18 14:00 | 13780.6 | 4.4911 | 87.1697 | 64.1561 | 4038.6952
2033-10-19 15:00 | 14402.7 | 4.6866 | 87.4257 | 64.1561 | 4221.0147
2033-10-20 16:00 | 17324.1 | 5.6416 | 87.6391 | 64.1561 | 5077.1925
2033-10-21 17:00 | 16677.8 | 5.3149 | 88.3916 | 64.1561 | 4887.7807
2033-10-22 18:00 | 15115 | 4.7809 | 88.7218 | 64.1561 | 4429.7692
2033-10-23 19:00 | 12973.9 | 4.0861 | 88.7799 | 64.1561 | 3802.2748
2033-10-24 20:00 | 11506.7 | 3.6431 | 88.5741 | 64.1561 | 3372.2809
2033-10-25 21:00 | 10252.5 | 3.2432 | 88.412 | 64.1561 | 3004.7111
2033-10-26 22:00 | 9205.54 | 2.917 | 88.154 | 64.1561 | 2697.8775
2033-10-27 23:00 | 6333.59 | 1.8749 | 88.7847 | 64.1561 | 1856.192
2033-10-29 | 5397.61 | 1.5947 | 88.3504 | 64.1561 | 1581.8833
2033-10-30 01:00 | 4715.63 | 1.4505 | 87.4724 | 64.1561 | 1382.0147
2033-10-31 02:00 | 3846.6 | 1.2143 | 86.8684 | 64.1561 | 1127.3272
2033-11-01 03:00 | 3209.6 | 1.0009 | 86.7201 | 64.1561 | 940.6409
2033-11-02 04:00 | 3161.91 | 1 | 89.5253 | 64.1561 | 926.6643
2033-11-03 05:00 | 3176.31 | 1 | 91.6279 | 64.1561 | 930.8846
2033-11-04 06:00 | 4745.2 | 1.4569 | 86.1905 | 64.1561 | 1390.6808
2033-11-05 07:00 | 6412.42 | 2.171 | 85.0339 | 64.1561 | 1879.2948
2033-11-06 08:00 | 6960.42 | 2.1953 | 86.0476 | 64.1561 | 2039.8977
2033-11-07 09:00 | 8682.16 | 2.7767 | 85.9848 | 64.1561 | 2544.4899
2033-11-08 10:00 | 10365.6 | 3.5457 | 85.4165 | 64.1561 | 3037.8575
2033-11-09 11:00 | 11705.9 | 3.927 | 85.9754 | 64.1561 | 3430.6606
2033-11-10 12:00 | 12545.5 | 4.1738 | 86.4016 | 64.1561 | 3676.7231
2033-11-11 13:00 | 12468.3 | 3.9141 | 87.3897 | 64.1561 | 3654.098
2033-11-12 14:00 | 11953.5 | 3.8371 | 87.3048 | 64.1561 | 3503.225
2033-11-13 15:00 | 12775.9 | 4.1105 | 87.347 | 64.1561 | 3744.2467
2033-11-14 16:00 | 14560 | 4.716 | 87.4049 | 64.1561 | 4267.1148
2033-11-15 17:00 | 11878.6 | 3.9004 | 87.5515 | 64.1561 | 3481.274
2033-11-16 18:00 | 10335.1 | 3.3448 | 87.6039 | 64.1561 | 3028.9188
2033-11-17 19:00 | 9222.18 | 2.8457 | 87.9747 | 64.1561 | 2702.7542
2033-11-18 20:00 | 8345.19 | 2.5594 | 87.8792 | 64.1561 | 2445.7338
2033-11-19 21:00 | 7392.74 | 2.3054 | 87.4735 | 64.1561 | 2166.5982
2033-11-20 22:00 | 6802.7 | 2.0782 | 87.4666 | 64.1561 | 1993.6746
2033-11-21 23:00 | 4349.23 | 1.2598 | 87.9655 | 64.1561 | 1274.6335
2033-11-23 | 3771.53 | 1.1584 | 86.7965 | 64.1561 | 1105.3263
2033-11-24 01:00 | 3473.84 | 1.0749 | 86.3983 | 64.1561 | 1018.082
2033-11-25 02:00 | 3387.62 | 1.0729 | 85.8942 | 64.1561 | 992.8134
2033-11-26 03:00 | 3681.96 | 1.166 | 85.7165 | 64.1561 | 1079.076
2033-11-27 04:00 | 4182.91 | 1.2567 | 86.2441 | 64.1561 | 1225.8899
2033-11-28 05:00 | 5077.41 | 1.5684 | 85.8629 | 64.1561 | 1488.042
2033-11-29 06:00 | 5319.9 | 1.7447 | 85.1873 | 64.1561 | 1559.1088
2033-11-30 07:00 | 6315.52 | 2.099 | 85.0603 | 64.1561 | 1850.8962
2033-12-01 08:00 | 6917.91 | 2.2513 | 85.424 | 64.1561 | 2027.4393
2033-12-02 09:00 | 8309.87 | 2.7703 | 85.253 | 64.1561 | 2435.3825
2033-12-03 10:00 | 9739.05 | 3.2277 | 85.5207 | 64.1561 | 2854.2338
2033-12-04 11:00 | 9889.17 | 3.2123 | 86.0333 | 64.1561 | 2898.2296
2033-12-05 12:00 | 10786.3 | 3.5222 | 86.1424 | 64.1561 | 3161.1525
2033-12-06 13:00 | 11282.9 | 3.7152 | 86.2537 | 64.1561 | 3306.6916
2033-12-07 14:00 | 11952.8 | 3.8654 | 86.6767 | 64.1561 | 3503.0199
2033-12-08 15:00 | 13976.5 | 4.6481 | 86.5344 | 64.1561 | 4096.1078
2033-12-09 16:00 | 15180.7 | 4.9464 | 87.1054 | 64.1561 | 4449.024
2033-12-10 17:00 | 14884.7 | 4.8706 | 87.4129 | 64.1561 | 4362.275
2033-12-11 18:00 | 12973.7 | 4.2834 | 87.5164 | 64.1561 | 3802.2161
2033-12-12 19:00 | 11466.7 | 3.6446 | 87.941 | 64.1561 | 3360.558
2033-12-13 20:00 | 8768.39 | 2.7503 | 87.9945 | 64.1561 | 2569.7614
2033-12-14 21:00 | 7623.98 | 2.3714 | 87.7625 | 64.1561 | 2234.368
2033-12-15 22:00 | 5566.54 | 1.6801 | 87.8257 | 64.1561 | 1631.3918
2033-12-16 23:00 | 4712.82 | 1.4322 | 87.3363 | 64.1561 | 1381.1912
2033-12-18 | 3808.46 | 1.1649 | 86.9194 | 64.1561 | 1116.1494
2033-12-19 01:00 | 3284.97 | 1 | 86.6999 | 64.1561 | 962.7297
2033-12-20 02:00 | 3158.39 | 1 | 87.6904 | 64.1561 | 925.6327
2033-12-21 03:00 | 3177.5 | 1 | 87.6404 | 64.1561 | 931.2333
2033-12-22 04:00 | 3173.54 | 1 | 86.3713 | 64.1561 | 930.0728
2033-12-23 05:00 | 4100.02 | 1.2644 | 85.7107 | 64.1561 | 1201.5972
2033-12-24 06:00 | 4509.56 | 1.4275 | 85.3654 | 64.1561 | 1321.6216
2033-12-25 07:00 | 5714.6 | 1.8462 | 85.1109 | 64.1561 | 1674.7839
2033-12-26 08:00 | 6250.95 | 2.0469 | 85.0594 | 64.1561 | 1831.9726
2033-12-27 09:00 | 7427.89 | 2.709 | 83.9364 | 64.1561 | 2176.8997
2033-12-28 10:00 | 8976.92 | 3.0719 | 84.8167 | 64.1561 | 2630.8755
2033-12-29 11:00 | 10500.7 | 3.5524 | 85.2089 | 64.1561 | 3077.4514
2033-12-30 12:00 | 11513.7 | 3.8227 | 85.7506 | 64.1561 | 3374.3324
2033-12-31 13:00 | 12128.5 | 3.9373 | 86.3196 | 64.1561 | 3554.5125
2034-01-01 14:00 | 12885.5 | 4.1993 | 86.5397 | 64.1561 | 3776.3673
2034-01-02 15:00 | 15088.9 | 4.8652 | 86.9207 | 64.1561 | 4422.1201
2034-01-03 16:00 | 15785.6 | 5.0639 | 87.3958 | 64.1561 | 4626.3027
2034-01-04 17:00 | 15280.9 | 4.9486 | 87.6216 | 64.1561 | 4478.3897
2034-01-05 18:00 | 13958.5 | 4.4455 | 88.0078 | 64.1561 | 4090.8325
2034-01-06 19:00 | 12119.1 | 3.854 | 88.0539 | 64.1561 | 3551.7576
2034-01-07 20:00 | 9636.81 | 2.9448 | 88.4531 | 64.1561 | 2824.2702
2034-01-08 21:00 | 8409.08 | 2.5625 | 88.1837 | 64.1561 | 2464.4581
2034-01-09 22:00 | 6082.68 | 1.8778 | 87.7351 | 64.1561 | 1782.6575
2034-01-10 23:00 | 4933.94 | 1.5532 | 87.0772 | 64.1561 | 1445.9951
2034-01-12 | 4316.73 | 1.3484 | 86.7961 | 64.1561 | 1265.1087
2034-01-13 01:00 | 3563.08 | 1.1059 | 86.5828 | 64.1561 | 1044.2357
2034-01-14 02:00 | 3184.81 | 1 | 86.7828 | 64.1561 | 933.3757
2034-01-15 03:00 | 3152.31 | 1 | 85.8044 | 64.1561 | 923.8509
2034-01-16 04:00 | 3283.92 | 1.0491 | 85.4942 | 64.1561 | 962.4219
2034-01-17 05:00 | 4147.98 | 1.2733 | 85.8443 | 64.1561 | 1215.6529
2034-01-18 06:00 | 4687.09 | 1.4597 | 85.6266 | 64.1561 | 1373.6505
2034-01-19 07:00 | 5490.96 | 1.7242 | 85.5262 | 64.1561 | 1609.2415
2034-01-20 08:00 | 5840.28 | 1.8744 | 85.3272 | 64.1561 | 1711.6171
2034-01-21 09:00 | 7665.79 | 2.4785 | 85.2905 | 64.1561 | 2246.6213
2034-01-22 10:00 | 10056.3 | 3.2439 | 85.5422 | 64.1561 | 2947.2106
2034-01-23 11:00 | 11266.1 | 3.8119 | 85.364 | 64.1561 | 3301.768
2034-01-24 12:00 | 11882.2 | 3.8136 | 86.339 | 64.1561 | 3482.3291
2034-01-25 13:00 | 12168.7 | 3.905 | 86.6195 | 64.1561 | 3566.2939
2034-01-26 14:00 | 12220 | 3.8822 | 86.9822 | 64.1561 | 3581.3285
2034-01-27 15:00 | 13625.9 | 4.376 | 87.0076 | 64.1561 | 3993.3571
2034-01-28 16:00 | 12209.3 | 3.9067 | 87.3103 | 64.1561 | 3578.1926
2034-01-29 17:00 | 11627.1 | 3.7401 | 87.2455 | 64.1561 | 3407.5666
2034-01-30 18:00 | 10390.1 | 3.236 | 87.6037 | 64.1561 | 3045.0377
2034-01-31 19:00 | 9505.93 | 2.8834 | 87.8282 | 64.1561 | 2785.9131
2034-02-01 20:00 | 7575.45 | 2.2119 | 88.213 | 64.1561 | 2220.1452
2034-02-02 21:00 | 6648.36 | 2.0367 | 87.2929 | 64.1561 | 1948.442
2034-02-03 22:00 | 4421.4 | 1.3298 | 87.2758 | 64.1561 | 1295.7844
2034-02-04 23:00 | 3683.35 | 1.1472 | 86.429 | 64.1561 | 1079.4833
2034-02-06 | 3419.6 | 1.0574 | 86.1906 | 64.1561 | 1002.1858
2034-02-07 01:00 | 3181.19 | 1 | 85.7764 | 64.1561 | 932.3148
2034-02-08 02:00 | 3161.96 | 1 | 86.5435 | 64.1561 | 926.679
2034-02-09 03:00 | 3380.26 | 1.0406 | 85.635 | 64.1561 | 990.6564
2034-02-10 04:00 | 3748.47 | 1.1925 | 85.1387 | 64.1561 | 1098.5681
2034-02-11 05:00 | 5133.71 | 1.5829 | 85.4846 | 64.1561 | 1504.5419
2034-02-12 06:00 | 5349.81 | 1.6991 | 85.2175 | 64.1561 | 1567.8745
2034-02-13 07:00 | 5863.67 | 1.9832 | 84.5219 | 64.1561 | 1718.472
2034-02-14 08:00 | 5738.63 | 1.8143 | 85.4079 | 64.1561 | 1681.8264
2034-02-15 09:00 | 7059.28 | 2.3767 | 84.6726 | 64.1561 | 2068.8707
2034-02-16 10:00 | 9017.94 | 3.1245 | 84.5001 | 64.1561 | 2642.8973
2034-02-17 11:00 | 11064.9 | 3.7831 | 84.9372 | 64.1561 | 3242.8021
2034-02-18 12:00 | 12363.1 | 4.2074 | 85.3718 | 64.1561 | 3623.2669
2034-02-19 13:00 | 13083.7 | 4.3996 | 85.8779 | 64.1561 | 3834.454
2034-02-20 14:00 | 14048 | 4.4478 | 86.9277 | 64.1561 | 4117.0624
2034-02-21 15:00 | 15033.8 | 4.9413 | 86.7995 | 64.1561 | 4405.9719
2034-02-22 16:00 | 15805.7 | 5.1319 | 87.2804 | 64.1561 | 4632.1934
2034-02-23 17:00 | 15438.6 | 4.9339 | 87.779 | 64.1561 | 4524.607
2034-02-24 18:00 | 13450.2 | 4.1781 | 88.3218 | 64.1561 | 3941.8645
2034-02-25 19:00 | 12208.2 | 3.6464 | 88.7757 | 64.1561 | 3577.8702
2034-02-26 20:00 | 9365.99 | 2.845 | 88.4771 | 64.1561 | 2744.9007
2034-02-27 21:00 | 8261.26 | 2.5316 | 88.0511 | 64.1561 | 2421.1363
2034-02-28 22:00 | 6118.81 | 1.7696 | 88.5301 | 64.1561 | 1793.2462
2034-03-01 23:00 | 5258.59 | 1.5354 | 88.003 | 64.1561 | 1541.1406
2034-03-03 | 4539.84 | 1.4464 | 86.5528 | 64.1561 | 1330.4958
2034-03-04 01:00 | 4230.39 | 1.2997 | 86.7153 | 64.1561 | 1239.8049
2034-03-05 02:00 | 4041.04 | 1.2345 | 86.5633 | 64.1561 | 1184.3119
2034-03-06 03:00 | 4282.12 | 1.3434 | 86.0262 | 64.1561 | 1254.9655
2034-03-07 04:00 | 4592.98 | 1.4507 | 85.8171 | 64.1561 | 1346.0696
2034-03-08 05:00 | 5323.99 | 1.7283 | 85.3947 | 64.1561 | 1560.3074
2034-03-09 06:00 | 5329.02 | 1.7462 | 85.2878 | 64.1561 | 1561.7816
2034-03-10 07:00 | 5279.74 | 1.7367 | 85.2162 | 64.1561 | 1547.3391
2034-03-11 08:00 | 3746.08 | 1.2055 | 85.4594 | 64.1561 | 1097.8677
2034-03-12 09:00 | 4999 | 1.5927 | 85.3739 | 64.1561 | 1465.0623
2034-03-13 10:00 | 5962.29 | 2.008 | 84.7174 | 64.1561 | 1747.3747
2034-03-14 11:00 | 6715.97 | 2.3764 | 84.2397 | 64.1561 | 1968.2565
2034-03-15 12:00 | 7478.74 | 2.5791 | 84.6105 | 64.1561 | 2191.8023
2034-03-16 13:00 | 7977.63 | 2.6726 | 85.0476 | 64.1561 | 2338.0126
2034-03-17 14:00 | 8850.07 | 2.8344 | 85.7107 | 64.1561 | 2593.6995
2034-03-18 15:00 | 9792.33 | 3.1375 | 85.8467 | 64.1561 | 2869.8486
2034-03-19 16:00 | 10020.1 | 3.2359 | 85.9226 | 64.1561 | 2936.6014
2034-03-20 17:00 | 10069 | 3.2398 | 86.0787 | 64.1561 | 2950.9326
2034-03-21 18:00 | 8946.22 | 2.7472 | 86.7442 | 64.1561 | 2621.8783
2034-03-22 19:00 | 7979.63 | 2.4372 | 86.7622 | 64.1561 | 2338.5987
2034-03-23 20:00 | 5720.76 | 1.7161 | 86.9123 | 64.1561 | 1676.5893
2034-03-24 21:00 | 4850.9 | 1.4733 | 86.4653 | 64.1561 | 1421.6585
2034-03-25 22:00 | 3291.82 | 1 | 89.748 | 64.1561 | 964.7372
2034-03-26 23:00 | 3126.03 | 1 | 72.2942 | 64.1561 | 916.149
2034-03-28 | 3090.43 | 1 | 72.0896 | 64.1561 | 905.7156
2034-03-29 01:00 | 3096.98 | 1 | 71.9354 | 64.1561 | 907.6352
2034-03-30 02:00 | 3078.93 | 1 | 71.8302 | 64.1561 | 902.3453
2034-03-31 03:00 | 817.117 | 1 | 72.2663 | 64.1561 | 239.4734
2034-04-01 04:00 | 236.894 | 1 | 72.0675 | 64.1561 | 69.4268
2034-04-02 05:00 | 419.563 | 1 | 71.7217 | 64.1561 | 122.9618
2034-04-03 06:00 | 1754.61 | 1 | 80.4415 | 64.1561 | 514.2254
2034-04-04 07:00 | 2591.87 | 1 | 82.8114 | 64.1561 | 759.6021
2034-04-05 08:00 | 2838.07 | 1 | 70.9894 | 64.1561 | 831.7562
2034-04-06 09:00 | 3036.15 | 1 | 70.9765 | 64.1561 | 889.8077
2034-04-07 10:00 | 3149.65 | 1 | 70.9801 | 64.1561 | 923.0713
2034-04-08 11:00 | 3185.63 | 1 | 70.9849 | 64.1561 | 933.616
2034-04-09 12:00 | 3157.39 | 1 | 91.2581 | 64.1561 | 925.3397
2034-04-10 13:00 | 3279.33 | 1.0188 | 84.2259 | 64.1561 | 961.0768
2034-04-11 14:00 | 3272.72 | 1.0341 | 83.9694 | 64.1561 | 959.1396
2034-04-12 15:00 | 4234.67 | 1.3879 | 83.4671 | 64.1561 | 1241.0593
2034-04-13 16:00 | 6871.49 | 2.4159 | 82.7019 | 64.1561 | 2013.8349
2034-04-14 17:00 | 6223.63 | 2.0008 | 84.05 | 64.1561 | 1823.9659
2034-04-15 18:00 | 5402.3 | 1.6777 | 84.5573 | 64.1561 | 1583.2578
2034-04-16 19:00 | 4089.56 | 1.2991 | 84.2209 | 64.1561 | 1198.5317
2034-04-17 20:00 | 3350.17 | 1.074 | 83.9816 | 64.1561 | 981.8379
2034-04-18 21:00 | 3062.63 | 1 | 87.0653 | 64.1561 | 897.5683
2034-04-19 22:00 | 3026.24 | 1 | 91.4115 | 64.1561 | 886.9034
2034-04-20 23:00 | 0 | 0 | 71.4415 | 64.1561 | 0
2034-04-22 | -549.214 | 1.7915 | 69.8413 | 64.1561 | -160.9587
2034-04-23 01:00 | -626.603 | 1.9953 | 69.5205 | 64.1561 | -183.6392
2034-04-24 02:00 | -658.737 | 2.0635 | 69.3283 | 64.1561 | -193.0568
2034-04-25 03:00 | -733.025 | 2.2482 | 69.1524 | 64.1561 | -214.8284
2034-04-26 04:00 | -737.663 | 2.2494 | 68.9682 | 64.1561 | -216.1877
2034-04-27 05:00 | -688.134 | 2.1269 | 68.8724 | 64.1561 | -201.6722
2034-04-28 06:00 | 133.288 | 1 | 70.0126 | 64.1561 | 39.0629
2034-04-29 07:00 | 1943.02 | 1 | 69.5842 | 64.1561 | 569.443
2034-04-30 08:00 | 0 | 0 | 70.2269 | 64.1561 | 0
2034-05-01 09:00 | 0 | 1 | 70.0714 | 64.1561 | 0
2034-05-02 10:00 | 3591.37 | 1 | 69.0906 | 64.1561 | 1052.5266
2034-05-03 11:00 | 3436.97 | 1.0061 | 83.6927 | 64.1561 | 1007.2765
2034-05-04 12:00 | 3544.5 | 1.0691 | 83.4312 | 64.1561 | 1038.7904
2034-05-05 13:00 | 4125.82 | 1.2261 | 83.6674 | 64.1561 | 1209.1585
2034-05-06 14:00 | 6076.48 | 1.9005 | 83.1489 | 64.1561 | 1780.8405
2034-05-07 15:00 | 6467.85 | 2.1115 | 82.951 | 64.1561 | 1895.5397
2034-05-08 16:00 | 8735.15 | 3.0596 | 82.3117 | 64.1561 | 2560.0198
2034-05-09 17:00 | 7880.07 | 2.5936 | 83.4026 | 64.1561 | 2309.4205
2034-05-10 18:00 | 7304.72 | 2.2578 | 84.3287 | 64.1561 | 2140.8021
2034-05-11 19:00 | 6236.99 | 1.9033 | 84.5419 | 64.1561 | 1827.8813
2034-05-12 20:00 | 5355.44 | 1.6703 | 84.2417 | 64.1561 | 1569.5245
2034-05-13 21:00 | 4730.54 | 1.4721 | 84.2112 | 64.1561 | 1386.3844
2034-05-14 22:00 | 4179.71 | 1.3013 | 84.0778 | 64.1561 | 1224.9521
2034-05-15 23:00 | 3081.58 | 1 | 70.69 | 64.1561 | 903.1219
2034-05-17 | 3104.83 | 1 | 70.5201 | 64.1561 | 909.9359
2034-05-18 01:00 | 3140.22 | 1 | 70.4296 | 64.1561 | 920.3076
2034-05-19 02:00 | 3295.17 | 1 | 70.3442 | 64.1561 | 965.719
2034-05-20 03:00 | 3233.98 | 1 | 70.34 | 64.1561 | 947.786
2034-05-21 04:00 | 3203.01 | 1 | 70.3031 | 64.1561 | 938.7096
2034-05-22 05:00 | 3216.82 | 1 | 84.5074 | 64.1561 | 942.7569
2034-05-23 06:00 | 3714.61 | 1.121 | 83.9677 | 64.1561 | 1088.6447
2034-05-24 07:00 | 4307.05 | 1.3103 | 83.8948 | 64.1561 | 1262.2718
2034-05-25 08:00 | 4127.64 | 1.2589 | 83.9519 | 64.1561 | 1209.6919
2034-05-26 09:00 | 5343.22 | 1.7491 | 83.102 | 64.1561 | 1565.9432
2034-05-27 10:00 | 7218.97 | 2.6253 | 82.0494 | 64.1561 | 2115.6713
2034-05-28 11:00 | 8935.02 | 3.1373 | 82.7414 | 64.1561 | 2618.5959
2034-05-29 12:00 | 10211.6 | 3.487 | 83.4223 | 64.1561 | 2992.7245
2034-05-30 13:00 | 11256.8 | 3.7644 | 84.0258 | 64.1561 | 3299.0424
2034-05-31 14:00 | 12438.7 | 4.0968 | 84.5676 | 64.1561 | 3645.4231
2034-06-01 15:00 | 14367.3 | 4.7207 | 84.9767 | 64.1561 | 4210.64
2034-06-02 16:00 | 14978.5 | 4.8351 | 85.6522 | 64.1561 | 4389.765
2034-06-03 17:00 | 15359.9 | 4.9114 | 86.1512 | 64.1561 | 4501.5423
2034-06-04 18:00 | 13503.6 | 4.1857 | 86.8662 | 64.1561 | 3957.5145
2034-06-05 19:00 | 11996.9 | 3.6888 | 87.0351 | 64.1561 | 3515.9443
2034-06-06 20:00 | 9352.5 | 2.8051 | 87.3206 | 64.1561 | 2740.9472
2034-06-07 21:00 | 7883.79 | 2.4758 | 86.4782 | 64.1561 | 2310.5108
2034-06-08 22:00 | 5888.13 | 1.6811 | 87.4453 | 64.1561 | 1725.6406
2034-06-09 23:00 | 4995.31 | 1.4406 | 86.9368 | 64.1561 | 1463.9808
2034-06-11 | 3998.83 | 1.2873 | 85.2171 | 64.1561 | 1171.9414
2034-06-12 01:00 | 3303.36 | 1.084 | 84.6846 | 64.1561 | 968.1192
2034-06-13 02:00 | 3149.05 | 1 | 85.0344 | 64.1561 | 922.8955
2034-06-14 03:00 | 3106.77 | 1.0159 | 84.2322 | 64.1561 | 910.5044
2034-06-15 04:00 | 3139.4 | 1 | 84.7158 | 64.1561 | 920.0673
2034-06-16 05:00 | 3970.18 | 1.2677 | 84.2069 | 64.1561 | 1163.5449
2034-06-17 06:00 | 4647.8 | 1.4086 | 84.8416 | 64.1561 | 1362.1357
2034-06-18 07:00 | 6020.27 | 1.8515 | 84.6867 | 64.1561 | 1764.367
2034-06-19 08:00 | 6424.63 | 2.058 | 84.3511 | 64.1561 | 1882.8732
2034-06-20 09:00 | 8230.44 | 2.8146 | 83.7146 | 64.1561 | 2412.1039
2034-06-21 10:00 | 9916.79 | 3.4275 | 83.8759 | 64.1561 | 2906.3243
2034-06-22 11:00 | 11525.4 | 3.9959 | 84.2 | 64.1561 | 3377.7613
2034-06-23 12:00 | 12770.2 | 4.2042 | 85.199 | 64.1561 | 3742.5762
2034-06-24 13:00 | 13539.3 | 4.3499 | 85.8836 | 64.1561 | 3967.9771
2034-06-25 14:00 | 13965.6 | 4.4599 | 86.3141 | 64.1561 | 4092.9133
2034-06-26 15:00 | 14985 | 5.0108 | 86.0491 | 64.1561 | 4391.67
2034-06-27 16:00 | 15922.1 | 5.1724 | 86.7096 | 64.1561 | 4666.3069
2034-06-28 17:00 | 15637.3 | 5.0741 | 87.0519 | 64.1561 | 4582.8402
2034-06-29 18:00 | 13895 | 4.3884 | 87.5927 | 64.1561 | 4072.2225
2034-06-30 19:00 | 12138.7 | 3.7961 | 87.6985 | 64.1561 | 3557.5018
2034-07-01 20:00 | 9670.86 | 2.953 | 87.8843 | 64.1561 | 2834.2493
2034-07-02 21:00 | 8512.62 | 2.5966 | 87.6038 | 64.1561 | 2494.8027
2034-07-03 22:00 | 6666.27 | 1.9579 | 87.8223 | 64.1561 | 1953.6909
2034-07-04 23:00 | 5739.08 | 1.7446 | 87.0072 | 64.1561 | 1681.9583
2034-07-06 | 5445.75 | 1.6744 | 86.5379 | 64.1561 | 1595.9918
2034-07-07 01:00 | 5033.94 | 1.5401 | 86.3714 | 64.1561 | 1475.3022
2034-07-08 02:00 | 4868.97 | 1.5148 | 85.9641 | 64.1561 | 1426.9542
2034-07-09 03:00 | 4898.56 | 1.5609 | 85.497 | 64.1561 | 1435.6262
2034-07-10 04:00 | 5048.79 | 1.5981 | 85.4586 | 64.1561 | 1479.6543
2034-07-11 05:00 | 5719.33 | 1.9034 | 84.7678 | 64.1561 | 1676.1702
2034-07-12 06:00 | 6050.42 | 2.0608 | 84.498 | 64.1561 | 1773.2031
2034-07-13 07:00 | 7319.21 | 2.4634 | 84.6476 | 64.1561 | 2145.0487
2034-07-14 08:00 | 8268.84 | 2.663 | 85.3166 | 64.1561 | 2423.3578
2034-07-15 09:00 | 10201.6 | 3.3009 | 85.438 | 64.1561 | 2989.7938
2034-07-16 10:00 | 11791.3 | 3.9691 | 85.289 | 64.1561 | 3455.6889
2034-07-17 11:00 | 12980.2 | 4.4753 | 85.38 | 64.1561 | 3804.1211
2034-07-18 12:00 | 14566.3 | 4.8752 | 86.0775 | 64.1561 | 4268.9611
2034-07-19 13:00 | 15849.6 | 5.0857 | 86.9882 | 64.1561 | 4645.0592
2034-07-20 14:00 | 16914.2 | 5.4175 | 87.4332 | 64.1561 | 4957.0627
2034-07-21 15:00 | 18332.7 | 5.8471 | 87.8738 | 64.1561 | 5372.784
2034-07-22 16:00 | 19231.9 | 5.9616 | 88.6507 | 64.1561 | 5636.3135
2034-07-23 17:00 | 18390.3 | 5.7645 | 88.9165 | 64.1561 | 5389.6649
2034-07-24 18:00 | 15706.6 | 4.9772 | 88.9958 | 64.1561 | 4603.1501
2034-07-25 19:00 | 13019.8 | 4.1409 | 88.8524 | 64.1561 | 3815.7267
2034-07-26 20:00 | 11496.8 | 3.4524 | 89.3138 | 64.1561 | 3369.3795
2034-07-27 21:00 | 10350.2 | 3.1621 | 88.8206 | 64.1561 | 3033.3442
2034-07-28 22:00 | 8218.08 | 2.4616 | 88.8111 | 64.1561 | 2408.4815
2034-07-29 23:00 | 7094.55 | 2.1864 | 88.0486 | 64.1561 | 2079.2074
2034-07-31 | 6290.37 | 1.9581 | 87.5715 | 64.1561 | 1843.5255
2034-08-01 01:00 | 5985.3 | 1.8133 | 87.6308 | 64.1561 | 1754.1183
2034-08-02 02:00 | 5555.83 | 1.736 | 87.0074 | 64.1561 | 1628.253
2034-08-03 03:00 | 5590.14 | 1.7382 | 86.8348 | 64.1561 | 1638.3083
2034-08-04 04:00 | 5652.53 | 1.7706 | 86.572 | 64.1561 | 1656.593
2034-08-05 05:00 | 6282.63 | 2.0874 | 85.7271 | 64.1561 | 1841.2571
2034-08-06 06:00 | 6419.7 | 2.1286 | 85.727 | 64.1561 | 1881.4283
2034-08-07 07:00 | 7538.23 | 2.4643 | 85.8691 | 64.1561 | 2209.2371
2034-08-08 08:00 | 8315.9 | 2.6778 | 86.1472 | 64.1561 | 2437.1497
2034-08-09 09:00 | 10480 | 3.4328 | 86.0612 | 64.1561 | 3071.3848
2034-08-10 10:00 | 12113.3 | 3.9984 | 86.2698 | 64.1561 | 3550.0578
2034-08-11 11:00 | 13641.4 | 4.4992 | 86.6289 | 64.1561 | 3997.8997
2034-08-12 12:00 | 14978.6 | 4.8736 | 87.1693 | 64.1561 | 4389.7943
2034-08-13 13:00 | 15008 | 5.0003 | 87.2763 | 64.1561 | 4398.4106
2034-08-14 14:00 | 16155.8 | 5.2385 | 87.8615 | 64.1561 | 4734.7976
2034-08-15 15:00 | 17856.4 | 5.7691 | 88.2033 | 64.1561 | 5233.1943
2034-08-16 16:00 | 18604.6 | 5.8721 | 88.8885 | 64.1561 | 5452.47
2034-08-17 17:00 | 18212.7 | 5.7376 | 89.2575 | 64.1561 | 5337.6155
2034-08-18 18:00 | 16973.5 | 5.2313 | 89.7445 | 64.1561 | 4974.4418
2034-08-19 19:00 | 15117.5 | 4.6423 | 89.8688 | 64.1561 | 4430.5019
2034-08-20 20:00 | 11072.7 | 3.4777 | 89.5161 | 64.1561 | 3245.088
2034-08-21 21:00 | 9821.79 | 3.0731 | 89.1061 | 64.1561 | 2878.4825
2034-08-22 22:00 | 7959.16 | 2.3781 | 89.3287 | 64.1561 | 2332.5995
2034-08-23 23:00 | 7185.43 | 2.1484 | 88.9154 | 64.1561 | 2105.8417
2034-08-25 | 6696.98 | 1.9892 | 88.6485 | 64.1561 | 1962.6911
2034-08-26 01:00 | 5899.53 | 1.8354 | 87.7735 | 64.1561 | 1728.9816
2034-08-27 02:00 | 5572.33 | 1.7399 | 87.4707 | 64.1561 | 1633.0887
2034-08-28 03:00 | 5683.63 | 1.7869 | 87.147 | 64.1561 | 1665.7075
2034-08-29 04:00 | 5595.31 | 1.8506 | 86.3741 | 64.1561 | 1639.8235
2034-08-30 05:00 | 6277.43 | 2.0898 | 86.1434 | 64.1561 | 1839.7331
2034-08-31 06:00 | 6694.37 | 2.1045 | 86.7797 | 64.1561 | 1961.9262
2034-09-01 07:00 | 7555.34 | 2.4865 | 86.205 | 64.1561 | 2214.2516
2034-09-02 08:00 | 8019.22 | 2.6803 | 86.105 | 64.1561 | 2350.2014
2034-09-03 09:00 | 9909.01 | 3.3217 | 86.1405 | 64.1561 | 2904.0442
2034-09-04 10:00 | 11909.7 | 3.9575 | 86.4845 | 64.1561 | 3490.3885
2034-09-05 11:00 | 13726.8 | 4.4788 | 87.0478 | 64.1561 | 4022.928
2034-09-06 12:00 | 14876.3 | 4.7128 | 87.7969 | 64.1561 | 4359.8132
2034-09-07 13:00 | 15434.4 | 5.0322 | 87.8133 | 64.1561 | 4523.3761
2034-09-08 14:00 | 16042.4 | 5.2036 | 88.183 | 64.1561 | 4701.5633
2034-09-09 15:00 | 18188.3 | 5.7312 | 88.7975 | 64.1561 | 5330.4645
2034-09-10 16:00 | 18508.8 | 5.828 | 89.2273 | 64.1561 | 5424.3938
2034-09-11 17:00 | 17423.8 | 5.6454 | 89.1837 | 64.1561 | 5106.4117
2034-09-12 18:00 | 15266.1 | 4.6847 | 89.9572 | 64.1561 | 4474.0523
2034-09-13 19:00 | 13442.3 | 4.1613 | 89.7403 | 64.1561 | 3939.5492
2034-09-14 20:00 | 10778 | 3.242 | 89.9444 | 64.1561 | 3158.72
2034-09-15 21:00 | 9592.83 | 2.9213 | 89.4142 | 64.1561 | 2811.381
2034-09-16 22:00 | 7998.37 | 2.3394 | 89.6101 | 64.1561 | 2344.0909
2034-09-17 23:00 | 6268.02 | 1.9228 | 88.6185 | 64.1561 | 1836.9753
2034-09-19 | 5700.53 | 1.7049 | 88.5217 | 64.1561 | 1670.6604
2034-09-20 01:00 | 4929.49 | 1.6177 | 87.0379 | 64.1561 | 1444.6909
2034-09-21 02:00 | 4846.42 | 1.5024 | 87.4458 | 64.1561 | 1420.3455
2034-09-22 03:00 | 4593.54 | 1.3972 | 87.4401 | 64.1561 | 1346.2337
2034-09-23 04:00 | 4121.88 | 1.3363 | 86.4245 | 64.1561 | 1208.0038
2034-09-24 05:00 | 4047.43 | 1.2389 | 86.9136 | 64.1561 | 1186.1846
2034-09-25 06:00 | 5766.13 | 1.9344 | 85.6136 | 64.1561 | 1689.8859
2034-09-26 07:00 | 7019.08 | 2.3866 | 85.5158 | 64.1561 | 2057.0893
2034-09-27 08:00 | 6839.46 | 2.1379 | 86.6714 | 64.1561 | 2004.4479
2034-09-28 09:00 | 8008.67 | 2.6521 | 85.9809 | 64.1561 | 2347.1095
2034-09-29 10:00 | 9655.65 | 3.2844 | 85.7947 | 64.1561 | 2829.7917
2034-09-30 11:00 | 11230.1 | 3.7325 | 86.3285 | 64.1561 | 3291.2174
2034-10-01 12:00 | 11908.9 | 4.0809 | 86.2705 | 64.1561 | 3490.1541
2034-10-02 13:00 | 13243.4 | 4.3705 | 86.9377 | 64.1561 | 3881.2574
2034-10-03 14:00 | 13081 | 4.0877 | 87.9062 | 64.1561 | 3833.6627
2034-10-04 15:00 | 13168 | 4.3648 | 87.356 | 64.1561 | 3859.1598
2034-10-05 16:00 | 16564 | 5.299 | 87.8875 | 64.1561 | 4854.4292
2034-10-06 17:00 | 15308.8 | 4.8447 | 88.5025 | 64.1561 | 4486.5664
2034-10-07 18:00 | 13881.7 | 4.3438 | 88.807 | 64.1561 | 4068.3247
2034-10-08 19:00 | 11994.8 | 3.7218 | 88.8577 | 64.1561 | 3515.3289
2034-10-09 20:00 | 10783 | 3.3116 | 88.8517 | 64.1561 | 3160.1853
2034-10-10 21:00 | 9653.45 | 3.0152 | 88.4931 | 64.1561 | 2829.1469
2034-10-11 22:00 | 8913.48 | 2.7716 | 88.322 | 64.1561 | 2612.2831
2034-10-12 23:00 | 6174.31 | 1.7728 | 89.1665 | 64.1561 | 1809.5116
2034-10-14 | 5510.73 | 1.5731 | 88.8215 | 64.1561 | 1615.0355
2034-10-15 01:00 | 4878.03 | 1.5037 | 87.4915 | 64.1561 | 1429.6095
2034-10-16 02:00 | 4307.99 | 1.3752 | 86.8044 | 64.1561 | 1262.5472
2034-10-17 03:00 | 4098.03 | 1.2911 | 86.7178 | 64.1561 | 1201.014
2034-10-18 04:00 | 3780.24 | 1.2134 | 86.2458 | 64.1561 | 1107.879
2034-10-19 05:00 | 3614.09 | 1.1443 | 86.2223 | 64.1561 | 1059.1852
2034-10-20 06:00 | 5342.48 | 1.7309 | 85.7628 | 64.1561 | 1565.7263
2034-10-21 07:00 | 6349.05 | 2.1526 | 85.2832 | 64.1561 | 1860.7229
2034-10-22 08:00 | 5549.18 | 1.8184 | 85.8022 | 64.1561 | 1626.3041
2034-10-23 09:00 | 6874.32 | 2.3148 | 85.4077 | 64.1561 | 2014.6643
2034-10-24 10:00 | 8931.45 | 3.0746 | 85.2365 | 64.1561 | 2617.5496
2034-10-25 11:00 | 10420.7 | 3.4893 | 85.848 | 64.1561 | 3054.0057
2034-10-26 12:00 | 11211.9 | 3.5418 | 86.8419 | 64.1561 | 3285.8835
2034-10-27 13:00 | 11286.3 | 3.664 | 86.7418 | 64.1561 | 3307.688
2034-10-28 14:00 | 11666 | 3.7657 | 86.9914 | 64.1561 | 3418.9671
2034-10-29 15:00 | 11957.7 | 3.663 | 87.8073 | 64.1561 | 3504.4559
2034-10-30 16:00 | 13973.6 | 4.5567 | 87.151 | 64.1561 | 4095.2579
2034-10-31 17:00 | 12018.7 | 4.0248 | 87.1552 | 64.1561 | 3522.3333
2034-11-01 18:00 | 11270.1 | 3.6326 | 87.5828 | 64.1561 | 3302.9403
2034-11-02 19:00 | 9957.62 | 3.1247 | 87.8422 | 64.1561 | 2918.2903
2034-11-03 20:00 | 9226.36 | 2.82 | 88.0608 | 64.1561 | 2703.9792
2034-11-04 21:00 | 8441.49 | 2.6495 | 87.6054 | 64.1561 | 2473.9565
2034-11-05 22:00 | 8015.13 | 2.4979 | 87.5089 | 64.1561 | 2349.0027
2034-11-06 23:00 | 5845.94 | 1.6912 | 88.3499 | 64.1561 | 1713.2759
2034-11-08 | 5265.76 | 1.5382 | 87.8956 | 64.1561 | 1543.2419
2034-11-09 01:00 | 4829.11 | 1.4428 | 87.353 | 64.1561 | 1415.2724
2034-11-10 02:00 | 4469.78 | 1.4082 | 86.4869 | 64.1561 | 1309.9632
2034-11-11 03:00 | 4620.04 | 1.4914 | 86.0075 | 64.1561 | 1354.0001
2034-11-12 04:00 | 4930.89 | 1.579 | 85.9614 | 64.1561 | 1445.1012
2034-11-13 05:00 | 5820.46 | 1.8953 | 85.7115 | 64.1561 | 1705.8084
2034-11-14 06:00 | 6140.7 | 2.0903 | 85.2311 | 64.1561 | 1799.6615
2034-11-15 07:00 | 7088.1 | 2.3632 | 85.5066 | 64.1561 | 2077.3171
2034-11-16 08:00 | 7747.91 | 2.4902 | 86.0641 | 64.1561 | 2270.6883
2034-11-17 09:00 | 9679.49 | 3.2456 | 85.6886 | 64.1561 | 2836.7785
2034-11-18 10:00 | 11207.4 | 3.7762 | 85.9048 | 64.1561 | 3284.5647
2034-11-19 11:00 | 13048.8 | 4.3136 | 86.4536 | 64.1561 | 3824.2258
2034-11-20 12:00 | 13571.3 | 4.5492 | 86.6926 | 64.1561 | 3977.3554
2034-11-21 13:00 | 15164.4 | 4.7869 | 87.7248 | 64.1561 | 4444.2469
2034-11-22 14:00 | 15011.3 | 4.7854 | 88.0088 | 64.1561 | 4399.3778
2034-11-23 15:00 | 16635.3 | 5.3934 | 88.0549 | 64.1561 | 4875.3252
2034-11-24 16:00 | 17189 | 5.5506 | 88.4513 | 64.1561 | 5037.5986
2034-11-25 17:00 | 16450.6 | 5.3841 | 88.6019 | 64.1561 | 4821.1949
2034-11-26 18:00 | 15212.3 | 4.7823 | 89.2459 | 64.1561 | 4458.285
2034-11-27 19:00 | 13417.6 | 4.2197 | 89.2489 | 64.1561 | 3932.3104
2034-11-28 20:00 | 11471.3 | 3.4317 | 89.779 | 64.1561 | 3361.9062
2034-11-29 21:00 | 10134.9 | 3.1294 | 89.1211 | 64.1561 | 2970.246
2034-11-30 22:00 | 8167.41 | 2.4532 | 89.201 | 64.1561 | 2393.6316
2034-12-01 23:00 | 7292.26 | 2.199 | 88.7825 | 64.1561 | 2137.1504
2034-12-03 | 6199.84 | 1.9724 | 87.7966 | 64.1561 | 1816.9937
2034-12-04 01:00 | 5921.5 | 1.8047 | 88.0201 | 64.1561 | 1735.4203
2034-12-05 02:00 | 5746.8 | 1.7408 | 87.8682 | 64.1561 | 1684.2208
2034-12-06 03:00 | 5878.14 | 1.8011 | 87.5254 | 64.1561 | 1722.7128
2034-12-07 04:00 | 5988.26 | 1.8681 | 87.1651 | 64.1561 | 1754.9858
2034-12-08 05:00 | 6399.09 | 2.1473 | 86.1811 | 64.1561 | 1875.3882
2034-12-09 06:00 | 6930.87 | 2.2412 | 86.581 | 64.1561 | 2031.2375
2034-12-10 07:00 | 7899.41 | 2.609 | 86.337 | 64.1561 | 2315.0885
2034-12-11 08:00 | 8249.38 | 2.6792 | 86.6419 | 64.1561 | 2417.6546
2034-12-12 09:00 | 9754.02 | 3.3841 | 85.9467 | 64.1561 | 2858.6211
2034-12-13 10:00 | 11592.9 | 3.9968 | 86.2191 | 64.1561 | 3397.5436
2034-12-14 11:00 | 13174.3 | 4.2983 | 87.1747 | 64.1561 | 3861.0062
2034-12-15 12:00 | 14002.8 | 4.5296 | 87.6353 | 64.1561 | 4103.8156
2034-12-16 13:00 | 14574.3 | 4.5663 | 88.3285 | 64.1561 | 4271.3057
2034-12-17 14:00 | 14998.1 | 4.6406 | 88.7605 | 64.1561 | 4395.5092
2034-12-18 15:00 | 15702.2 | 5.0088 | 88.6115 | 64.1561 | 4601.8606
2034-12-19 16:00 | 15052.5 | 4.9359 | 88.5116 | 64.1561 | 4411.4523
2034-12-20 17:00 | 12927.7 | 4.4625 | 88.0094 | 64.1561 | 3788.7349
2034-12-21 18:00 | 13077.8 | 3.8178 | 89.9222 | 64.1561 | 3832.7248
2034-12-22 19:00 | 10656.6 | 3.3947 | 88.7865 | 64.1561 | 3123.1412
2034-12-23 20:00 | 8900.35 | 2.5548 | 89.902 | 64.1561 | 2608.4351
2034-12-24 21:00 | 7486.71 | 2.3324 | 88.49 | 64.1561 | 2194.1381
2034-12-25 22:00 | 5500.44 | 1.7159 | 88.1368 | 64.1561 | 1612.0198
2034-12-26 23:00 | 5024.63 | 1.4598 | 88.6473 | 64.1561 | 1472.5737
2034-12-28 | 4119.55 | 1.2873 | 87.3671 | 64.1561 | 1207.3209
2034-12-29 01:00 | 3699.28 | 1.1773 | 86.8276 | 64.1561 | 1084.1519
2034-12-30 02:00 | 3373.55 | 1.078 | 86.5038 | 64.1561 | 988.6899
2034-12-31 03:00 | 3540.79 | 1.1466 | 86.0934 | 64.1561 | 1037.7031
2035-01-01 04:00 | 3695.51 | 1.1912 | 85.9907 | 64.1561 | 1083.0471
2035-01-02 05:00 | 4612.37 | 1.4576 | 86.1159 | 64.1561 | 1351.7522
2035-01-03 06:00 | 4985.06 | 1.6291 | 85.694 | 64.1561 | 1460.9769
2035-01-04 07:00 | 6047.31 | 1.9943 | 85.5862 | 64.1561 | 1772.2916
2035-01-05 08:00 | 6435.09 | 2.1053 | 85.7798 | 64.1561 | 1885.9387
2035-01-06 09:00 | 8308.88 | 2.6805 | 86.0207 | 64.1561 | 2435.0924
2035-01-07 10:00 | 10237.6 | 3.4431 | 85.7635 | 64.1561 | 3000.3444
2035-01-08 11:00 | 12153.4 | 4.1087 | 86.0331 | 64.1561 | 3561.8099
2035-01-09 12:00 | 13539.8 | 4.4534 | 86.7529 | 64.1561 | 3968.1237
2035-01-10 13:00 | 14051.6 | 4.6177 | 87.1506 | 64.1561 | 4118.1174
2035-01-11 14:00 | 14932.5 | 4.7799 | 87.7851 | 64.1561 | 4376.2838
2035-01-12 15:00 | 16486.2 | 5.2359 | 88.1874 | 64.1561 | 4831.6283
2035-01-13 16:00 | 14007.8 | 4.5028 | 88.4369 | 64.1561 | 4105.2809
2035-01-14 17:00 | 13959.9 | 4.5851 | 88.156 | 64.1561 | 4091.2428
2035-01-15 18:00 | 13024.7 | 4.0735 | 88.7768 | 64.1561 | 3817.1628
2035-01-16 19:00 | 12042.4 | 3.676 | 89.0734 | 64.1561 | 3529.2791
2035-01-17 20:00 | 9675.34 | 2.9825 | 88.8731 | 64.1561 | 2835.5622
2035-01-18 21:00 | 8607.05 | 2.6672 | 88.4971 | 64.1561 | 2522.4774
2035-01-19 22:00 | 7040.07 | 2.0347 | 89.1629 | 64.1561 | 2063.2408
2035-01-20 23:00 | 6331.78 | 1.9513 | 88.0063 | 64.1561 | 1855.6615
2035-01-22 | 5902.91 | 1.7971 | 87.8845 | 64.1561 | 1729.9721
2035-01-23 01:00 | 5400.91 | 1.6849 | 87.3433 | 64.1561 | 1582.8505
2035-01-24 02:00 | 5232.41 | 1.6854 | 86.7403 | 64.1561 | 1533.468
2035-01-25 03:00 | 5274.9 | 1.7163 | 86.4304 | 64.1561 | 1545.9206
2035-01-26 04:00 | 5658.73 | 1.7769 | 86.7554 | 64.1561 | 1658.4101
2035-01-27 05:00 | 6299.23 | 2.0866 | 86.0514 | 64.1561 | 1846.1221
2035-01-28 06:00 | 6402.24 | 2.0728 | 86.3358 | 64.1561 | 1876.3113
2035-01-29 07:00 | 7629.4 | 2.4051 | 86.6485 | 64.1561 | 2235.9564
2035-01-30 08:00 | 8002.62 | 2.5713 | 86.5425 | 64.1561 | 2345.3364
2035-01-31 09:00 | 9768.99 | 3.3445 | 85.8949 | 64.1561 | 2863.0084
2035-02-01 10:00 | 11387 | 3.8603 | 86.247 | 64.1561 | 3337.2003
2035-02-02 11:00 | 12949.4 | 4.2226 | 87.0106 | 64.1561 | 3795.0945
2035-02-03 12:00 | 13796.4 | 4.566 | 87.1845 | 64.1561 | 4043.3257
2035-02-04 13:00 | 14387.1 | 4.7145 | 87.6068 | 64.1561 | 4216.4428
2035-02-05 14:00 | 15397.6 | 5.1138 | 87.721 | 64.1561 | 4512.5911
2035-02-06 15:00 | 17088.7 | 5.5175 | 88.3473 | 64.1561 | 5008.2036
2035-02-07 16:00 | 18267.6 | 5.5145 | 89.5825 | 64.1561 | 5353.7051
2035-02-08 17:00 | 16619 | 5.3052 | 89.2779 | 64.1561 | 4870.5481
2035-02-09 18:00 | 14159.1 | 4.5116 | 89.4025 | 64.1561 | 4149.6226
2035-02-10 19:00 | 12637.9 | 3.9898 | 89.3705 | 64.1561 | 3703.8029
2035-02-11 20:00 | 10244.4 | 3.2028 | 89.3341 | 64.1561 | 3002.3373
2035-02-12 21:00 | 9353.56 | 2.9196 | 89.0239 | 64.1561 | 2741.2578
2035-02-13 22:00 | 7533.71 | 2.2484 | 89.3034 | 64.1561 | 2207.9125
2035-02-14 23:00 | 6867.53 | 2.026 | 89.0847 | 64.1561 | 2012.6744
2035-02-16 | 6045.61 | 1.8789 | 88.1232 | 64.1561 | 1771.7934
2035-02-17 01:00 | 5628.73 | 1.7302 | 87.9907 | 64.1561 | 1649.6179
2035-02-18 02:00 | 5414.17 | 1.7131 | 87.4038 | 64.1561 | 1586.7366
2035-02-19 03:00 | 5530.06 | 1.731 | 87.3316 | 64.1561 | 1620.7006
2035-02-20 04:00 | 5749.47 | 1.8635 | 86.7539 | 64.1561 | 1685.0033
2035-02-21 05:00 | 6439.01 | 2.1462 | 86.317 | 64.1561 | 1887.0876
2035-02-22 06:00 | 6803.74 | 2.2416 | 86.4518 | 64.1561 | 1993.9794
2035-02-23 07:00 | 8102.23 | 2.6341 | 86.6197 | 64.1561 | 2374.5292
2035-02-24 08:00 | 8919.11 | 2.8472 | 86.9852 | 64.1561 | 2613.9331
2035-02-25 09:00 | 10508.5 | 3.4596 | 86.7654 | 64.1561 | 3079.7373
2035-02-26 10:00 | 12173.2 | 4.1543 | 86.6012 | 64.1561 | 3567.6127
2035-02-27 11:00 | 13649.4 | 4.4789 | 87.3829 | 64.1561 | 4000.2443
2035-02-28 12:00 | 14400.5 | 4.7191 | 87.7589 | 64.1561 | 4220.3699
2035-03-01 13:00 | 14993 | 4.8004 | 88.3413 | 64.1561 | 4394.0146
2035-03-02 14:00 | 14486.9 | 4.6724 | 88.526 | 64.1561 | 4245.6913
2035-03-03 15:00 | 16327.1 | 5.255 | 88.6647 | 64.1561 | 4785.0007
2035-03-04 16:00 | 17795.4 | 5.6656 | 89.0943 | 64.1561 | 5215.3169
2035-03-05 17:00 | 17109 | 5.4897 | 89.3711 | 64.1561 | 5014.1529
2035-03-06 18:00 | 15748.9 | 4.9257 | 89.8596 | 64.1561 | 4615.547
2035-03-07 19:00 | 13836.2 | 4.3477 | 89.801 | 64.1561 | 4054.9899
2035-03-08 20:00 | 12232.7 | 3.5446 | 90.7405 | 64.1561 | 3585.0505
2035-03-09 21:00 | 10004.3 | 3.0618 | 89.8195 | 64.1561 | 2931.9709
2035-03-10 22:00 | 7128.63 | 2.261 | 89.0234 | 64.1561 | 2089.1952
2035-03-11 23:00 | 6019.86 | 1.8311 | 89.0253 | 64.1561 | 1764.2468
2035-03-13 | 5181.1 | 1.5675 | 88.6664 | 64.1561 | 1518.4305
2035-03-14 01:00 | 4700.65 | 1.3789 | 88.718 | 64.1561 | 1377.6245
2035-03-15 02:00 | 4116.13 | 1.2607 | 87.8551 | 64.1561 | 1206.3186
2035-03-16 03:00 | 3857.97 | 1.2275 | 87.0833 | 64.1561 | 1130.6594
2035-03-17 04:00 | 3497.94 | 1.0908 | 87.0877 | 64.1561 | 1025.145
2035-03-18 05:00 | 3402.04 | 1.0792 | 86.637 | 64.1561 | 997.0395
2035-03-19 06:00 | 5260.84 | 1.7107 | 86.1328 | 64.1561 | 1541.8
2035-03-20 07:00 | 6359.86 | 2.0942 | 86.0254 | 64.1561 | 1863.891
2035-03-21 08:00 | 5697.88 | 1.7828 | 86.7545 | 64.1561 | 1669.8838
2035-03-22 09:00 | 6526.21 | 2.1765 | 85.9144 | 64.1561 | 1912.6433
2035-03-23 10:00 | 7916.07 | 2.6536 | 85.8994 | 64.1561 | 2319.9711
2035-03-24 11:00 | 9123.26 | 3.0995 | 85.9243 | 64.1561 | 2673.7636
2035-03-25 12:00 | 10307.6 | 3.4336 | 86.3464 | 64.1561 | 3020.8594
2035-03-26 13:00 | 11283.9 | 3.803 | 86.4191 | 64.1561 | 3306.9846
2035-03-27 14:00 | 12627.5 | 4.1969 | 86.828 | 64.1561 | 3700.7549
2035-03-28 15:00 | 13829.7 | 4.434 | 87.5488 | 64.1561 | 4053.085
2035-03-29 16:00 | 14478.4 | 4.5906 | 87.9893 | 64.1561 | 4243.2002
2035-03-30 17:00 | 13176.1 | 4.2312 | 88.1109 | 64.1561 | 3861.5337
2035-03-31 18:00 | 11931.1 | 3.6313 | 88.8194 | 64.1561 | 3496.6602
2035-04-01 19:00 | 10267.7 | 3.17 | 88.5653 | 64.1561 | 3009.1658
2035-04-02 20:00 | 9372.86 | 2.8646 | 88.5269 | 64.1561 | 2746.9141
2035-04-03 21:00 | 8604.42 | 2.6616 | 88.2035 | 64.1561 | 2521.7066
2035-04-04 22:00 | 8260.64 | 2.4896 | 88.3643 | 64.1561 | 2420.9546
2035-04-05 23:00 | 5481.68 | 1.5055 | 89.5056 | 64.1561 | 1606.5218
2035-04-07 | 4355.68 | 1.3483 | 87.5166 | 64.1561 | 1276.5238
2035-04-08 01:00 | 3848.66 | 1.2133 | 86.9464 | 64.1561 | 1127.9309
2035-04-09 02:00 | 3602.93 | 1.1353 | 86.69 | 64.1561 | 1055.9146
2035-04-10 03:00 | 3493.8 | 1.1064 | 86.3976 | 64.1561 | 1023.9317
2035-04-11 04:00 | 3245.74 | 1.0446 | 85.9856 | 64.1561 | 951.2325
2035-04-12 05:00 | 3056.12 | 1 | 86.0572 | 64.1561 | 895.6604
2035-04-13 06:00 | 5016.61 | 1.6162 | 85.6446 | 64.1561 | 1470.2233
2035-04-14 07:00 | 5829.7 | 2.0089 | 84.9537 | 64.1561 | 1708.5164
2035-04-15 08:00 | 5415.4 | 1.7018 | 86.1706 | 64.1561 | 1587.0971
2035-04-16 09:00 | 6267.49 | 2.0737 | 85.5181 | 64.1561 | 1836.82
2035-04-17 10:00 | 7846.72 | 2.7216 | 85.0334 | 64.1561 | 2299.6466
2035-04-18 11:00 | 9169.09 | 3.0921 | 85.5828 | 64.1561 | 2687.195
2035-04-19 12:00 | 10063.6 | 3.3961 | 85.8179 | 64.1561 | 2949.35
2035-04-20 13:00 | 11183.4 | 3.6686 | 86.3695 | 64.1561 | 3277.531
2035-04-21 14:00 | 12459.9 | 3.9239 | 87.1343 | 64.1561 | 3651.6362
2035-04-22 15:00 | 13005.9 | 4.2791 | 86.9128 | 64.1561 | 3811.653
2035-04-23 16:00 | 15387.3 | 5.1826 | 86.8804 | 64.1561 | 4509.5725
2035-04-24 17:00 | 14700.2 | 4.7607 | 87.7898 | 64.1561 | 4308.2033
2035-04-25 18:00 | 13459.9 | 4.2408 | 88.3413 | 64.1561 | 3944.7073
2035-04-26 19:00 | 11746.9 | 3.6775 | 88.4473 | 64.1561 | 3442.6766
2035-04-27 20:00 | 10803.7 | 3.3499 | 88.4677 | 64.1561 | 3166.2519
2035-04-28 21:00 | 9705.67 | 3.0446 | 88.2248 | 64.1561 | 2844.4511
2035-04-29 22:00 | 9218.68 | 2.8123 | 88.3984 | 64.1561 | 2701.7284
2035-04-30 23:00 | 6862.36 | 1.9969 | 88.8859 | 64.1561 | 2011.1592
2035-05-02 | 5826.87 | 1.7778 | 87.9393 | 64.1561 | 1707.687
2035-05-03 01:00 | 5209.29 | 1.5664 | 87.836 | 64.1561 | 1526.6922
2035-05-04 02:00 | 4827.05 | 1.4782 | 87.3626 | 64.1561 | 1414.6687
2035-05-05 03:00 | 4726.68 | 1.5049 | 86.6709 | 64.1561 | 1385.2532
2035-05-06 04:00 | 4918.53 | 1.5546 | 86.5681 | 64.1561 | 1441.4788
2035-05-07 05:00 | 5599.8 | 1.8043 | 86.2264 | 64.1561 | 1641.1394
2035-05-08 06:00 | 6047.12 | 1.9589 | 86.1442 | 64.1561 | 1772.2359
2035-05-09 07:00 | 6891.05 | 2.2851 | 85.8784 | 64.1561 | 2019.5674
2035-05-10 08:00 | 7508.16 | 2.478 | 86.0236 | 64.1561 | 2200.4245
2035-05-11 09:00 | 9066.84 | 3.0604 | 85.8674 | 64.1561 | 2657.2285
2035-05-12 10:00 | 10344.8 | 3.4417 | 86.2546 | 64.1561 | 3031.7616
2035-05-13 11:00 | 11416.8 | 3.8612 | 86.3332 | 64.1561 | 3345.9338
2035-05-14 12:00 | 12866.6 | 4.2639 | 86.8498 | 64.1561 | 3770.8282
2035-05-15 13:00 | 13507.2 | 4.4435 | 87.2762 | 64.1561 | 3958.5696
2035-05-16 14:00 | 14316.3 | 4.6383 | 87.7531 | 64.1561 | 4195.6934
2035-05-17 15:00 | 15763 | 5.0804 | 88.0919 | 64.1561 | 4619.6793
2035-05-18 16:00 | 16675.5 | 5.3498 | 88.4907 | 64.1561 | 4887.1066
2035-05-19 17:00 | 16112.8 | 5.27 | 88.6005 | 64.1561 | 4722.1955
2035-05-20 18:00 | 14639.6 | 4.6313 | 89.1827 | 64.1561 | 4290.4432
2035-05-21 19:00 | 12984.9 | 4.0898 | 89.2426 | 64.1561 | 3805.4985
2035-05-22 20:00 | 10526 | 3.2454 | 89.4044 | 64.1561 | 3084.8661
2035-05-23 21:00 | 8841.84 | 2.9003 | 88.3435 | 64.1561 | 2591.2875
2035-05-24 22:00 | 7155.28 | 2.1112 | 89.3231 | 64.1561 | 2097.0056
2035-05-25 23:00 | 6366.54 | 1.915 | 88.6936 | 64.1561 | 1865.8487
2035-05-27 | 5750.98 | 1.7304 | 88.3765 | 64.1561 | 1685.4459
2035-05-28 01:00 | 5448.15 | 1.7206 | 87.4939 | 64.1561 | 1596.6952
2035-05-29 02:00 | 5301.74 | 1.6575 | 87.4116 | 64.1561 | 1553.7866
2035-05-30 03:00 | 5523.69 | 1.6886 | 87.5175 | 64.1561 | 1618.8337
2035-05-31 04:00 | 5451.34 | 1.7106 | 87.0749 | 64.1561 | 1597.63
2035-06-01 05:00 | 6103.12 | 1.9839 | 86.5308 | 64.1561 | 1788.6479
2035-06-02 06:00 | 6437.28 | 2.0522 | 86.7447 | 64.1561 | 1886.5805
2035-06-03 07:00 | 6947.09 | 2.2887 | 86.346 | 64.1561 | 2035.9911
2035-06-04 08:00 | 7277.32 | 2.2869 | 86.9662 | 64.1561 | 2132.772
2035-06-05 09:00 | 8858.92 | 2.9044 | 86.4945 | 64.1561 | 2596.2932
2035-06-06 10:00 | 10482.2 | 3.4459 | 86.6608 | 64.1561 | 3072.0296
2035-06-07 11:00 | 11342.9 | 3.8115 | 86.6876 | 64.1561 | 3324.2758
2035-06-08 12:00 | 12208.6 | 3.9634 | 87.3447 | 64.1561 | 3577.9875
2035-06-09 13:00 | 12617.7 | 4.0467 | 87.7386 | 64.1561 | 3697.8828
2035-06-10 14:00 | 13219.6 | 4.2892 | 87.8136 | 64.1561 | 3874.2823
2035-06-11 15:00 | 15103.2 | 4.8759 | 88.067 | 64.1561 | 4426.311
2035-06-12 16:00 | 16092 | 5.2181 | 88.3403 | 64.1561 | 4716.0997
2035-06-13 17:00 | 16308.7 | 5.1457 | 88.9927 | 64.1561 | 4779.6082
2035-06-14 18:00 | 14169.2 | 4.5576 | 88.9987 | 64.1561 | 4152.5826
2035-06-15 19:00 | 12910.1 | 3.8694 | 89.8489 | 64.1561 | 3783.5768
2035-06-16 20:00 | 10072.1 | 3.085 | 89.4883 | 64.1561 | 2951.8411
2035-06-17 21:00 | 8886.97 | 2.712 | 89.2132 | 64.1561 | 2604.5138
2035-06-18 22:00 | 6822.35 | 1.995 | 89.4663 | 64.1561 | 1999.4334
2035-06-19 23:00 | 6076.21 | 1.7617 | 89.1734 | 64.1561 | 1780.7614
2035-06-21 | 5441.55 | 1.6305 | 88.4161 | 64.1561 | 1594.7609
2035-06-22 01:00 | 5024.43 | 1.5689 | 87.6142 | 64.1561 | 1472.5151
2035-06-23 02:00 | 4729.61 | 1.4843 | 87.3316 | 64.1561 | 1386.1119
2035-06-24 03:00 | 4938.65 | 1.5683 | 86.9704 | 64.1561 | 1447.3754
2035-06-25 04:00 | 5223.26 | 1.6674 | 86.772 | 64.1561 | 1530.7864
2035-06-26 05:00 | 5882.04 | 2.0406 | 85.6976 | 64.1561 | 1723.8558
2035-06-27 06:00 | 6020.31 | 1.9437 | 86.5247 | 64.1561 | 1764.3787
2035-06-28 07:00 | 6760.57 | 2.2533 | 86.1175 | 64.1561 | 1981.3275
2035-06-29 08:00 | 7086.38 | 2.2711 | 86.6507 | 64.1561 | 2076.813
2035-06-30 09:00 | 8808.2 | 2.956 | 86.1526 | 64.1561 | 2581.4286
2035-07-01 10:00 | 10397.8 | 3.5125 | 86.288 | 64.1561 | 3047.2944
2035-07-02 11:00 | 11759.3 | 3.9282 | 86.7051 | 64.1561 | 3446.3106
2035-07-03 12:00 | 12907.7 | 4.2603 | 87.1575 | 64.1561 | 3782.8735
2035-07-04 13:00 | 13540 | 4.4828 | 87.4387 | 64.1561 | 3968.1823
2035-07-05 14:00 | 14894.2 | 4.8627 | 87.8888 | 64.1561 | 4365.0591
2035-07-06 15:00 | 16653.3 | 5.4535 | 88.1771 | 64.1561 | 4880.6005
2035-07-07 16:00 | 16834.6 | 5.4211 | 88.7857 | 64.1561 | 4933.7342
2035-07-08 17:00 | 16917.7 | 5.2475 | 89.5253 | 64.1561 | 4958.0884
2035-07-09 18:00 | 14325.7 | 4.4469 | 89.7428 | 64.1561 | 4198.4482
2035-07-10 19:00 | 12695.9 | 3.9779 | 89.5417 | 64.1561 | 3720.801
2035-07-11 20:00 | 10467.6 | 3.1821 | 89.7704 | 64.1561 | 3067.7507
2035-07-12 21:00 | 9246.83 | 2.8243 | 89.4122 | 64.1561 | 2709.9784
2035-07-13 22:00 | 7173.18 | 2.1321 | 89.4815 | 64.1561 | 2102.2515
2035-07-14 23:00 | 6150.02 | 1.8909 | 88.6373 | 64.1561 | 1802.3929
2035-07-16 | 5590.11 | 1.738 | 88.1519 | 64.1561 | 1638.2995
2035-07-17 01:00 | 5085.13 | 1.5911 | 87.7996 | 64.1561 | 1490.3045
2035-07-18 02:00 | 4998.47 | 1.5114 | 87.9895 | 64.1561 | 1464.907
2035-07-19 03:00 | 5213 | 1.6188 | 87.44 | 64.1561 | 1527.7795
2035-07-20 04:00 | 5395.93 | 1.7265 | 86.9396 | 64.1561 | 1581.391
2035-07-21 05:00 | 6040.43 | 1.9951 | 86.4534 | 64.1561 | 1770.2753
2035-07-22 06:00 | 6257.34 | 2.0566 | 86.498 | 64.1561 | 1833.8453
2035-07-23 07:00 | 7126.78 | 2.3996 | 86.2049 | 64.1561 | 2088.653
2035-07-24 08:00 | 7790.8 | 2.6047 | 86.37 | 64.1561 | 2283.2581
2035-07-25 09:00 | 9537.71 | 3.2987 | 86.0804 | 64.1561 | 2795.2269
2035-07-26 10:00 | 11746.6 | 4.0226 | 86.4356 | 64.1561 | 3442.5886
2035-07-27 11:00 | 13705.4 | 4.4868 | 87.3392 | 64.1561 | 4016.6562
2035-07-28 12:00 | 14331.3 | 4.7106 | 87.7322 | 64.1561 | 4200.0894
2035-07-29 13:00 | 15907.9 | 5.0226 | 88.5571 | 64.1561 | 4662.1453
2035-07-30 14:00 | 16239.7 | 5.1702 | 88.866 | 64.1561 | 4759.3863
2035-07-31 15:00 | 17812.5 | 5.63 | 89.2592 | 64.1561 | 5220.3284
2035-08-01 16:00 | 17784 | 5.7226 | 89.4174 | 64.1561 | 5211.9759
2035-08-02 17:00 | 17571.1 | 5.581 | 89.8248 | 64.1561 | 5149.5811
2035-08-03 18:00 | 15698.6 | 4.9948 | 89.9948 | 64.1561 | 4600.8055
2035-08-04 19:00 | 14108.5 | 4.3763 | 90.2747 | 64.1561 | 4134.7932
2035-08-05 20:00 | 12093.6 | 3.5608 | 90.835 | 64.1561 | 3544.2843
2035-08-06 21:00 | 10319.5 | 3.1873 | 89.9649 | 64.1561 | 3024.3469
2035-08-07 22:00 | 7905.68 | 2.41 | 89.8204 | 64.1561 | 2316.9261
2035-08-08 23:00 | 6872.31 | 2.0845 | 89.4312 | 64.1561 | 2014.0752
2035-08-10 | 6215.47 | 1.9053 | 88.9243 | 64.1561 | 1821.5744
2035-08-11 01:00 | 5782.94 | 1.7551 | 88.743 | 64.1561 | 1694.8124
2035-08-12 02:00 | 5298.91 | 1.6927 | 87.8395 | 64.1561 | 1552.9572
2035-08-13 03:00 | 5497.35 | 1.7048 | 87.9477 | 64.1561 | 1611.1142
2035-08-14 04:00 | 5563.26 | 1.8118 | 87.1861 | 64.1561 | 1630.4306
2035-08-15 05:00 | 6453.13 | 2.0956 | 87.0879 | 64.1561 | 1891.2257
2035-08-16 06:00 | 6524.79 | 2.1584 | 86.8568 | 64.1561 | 1912.2272
2035-08-17 07:00 | 7594.8 | 2.4374 | 87.1862 | 64.1561 | 2225.8162
2035-08-18 08:00 | 8142.84 | 2.5911 | 87.3731 | 64.1561 | 2386.4308
2035-08-19 09:00 | 9735.42 | 3.2473 | 86.8949 | 64.1561 | 2853.17
2035-08-20 10:00 | 11537.9 | 3.8742 | 87.0332 | 64.1561 | 3381.4247
2035-08-21 11:00 | 13240.5 | 4.3707 | 87.5406 | 64.1561 | 3880.4075
2035-08-22 12:00 | 14389.9 | 4.771 | 87.8565 | 64.1561 | 4217.2634
2035-08-23 13:00 | 15334.3 | 5.0177 | 88.3531 | 64.1561 | 4494.0397
2035-08-24 14:00 | 15811.5 | 5.1929 | 88.6429 | 64.1561 | 4633.8932
2035-08-25 15:00 | 17921.1 | 5.7083 | 89.2713 | 64.1561 | 5252.156
2035-08-26 16:00 | 18026.9 | 5.7388 | 89.6952 | 64.1561 | 5283.1629
2035-08-27 17:00 | 17694.4 | 5.5789 | 90.0933 | 64.1561 | 5185.7167
2035-08-28 18:00 | 15617 | 4.9057 | 90.3173 | 64.1561 | 4576.8909
2035-08-29 19:00 | 14240.3 | 4.3729 | 90.542 | 64.1561 | 4173.42
2035-08-30 20:00 | 11695.3 | 3.559 | 90.5571 | 64.1561 | 3427.5541
2035-08-31 21:00 | 10265.8 | 3.1881 | 89.9892 | 64.1561 | 3008.609
2035-09-01 22:00 | 8379.11 | 2.5226 | 90.0768 | 64.1561 | 2455.6747
2035-09-02 23:00 | 6850.28 | 2.0712 | 89.6352 | 64.1561 | 2007.6189
2035-09-04 | 6038.19 | 1.8651 | 88.9651 | 64.1561 | 1769.6188
2035-09-05 01:00 | 5391.29 | 1.6858 | 88.4693 | 64.1561 | 1580.0311
2035-09-06 02:00 | 4757.53 | 1.4864 | 88.193 | 64.1561 | 1394.2944
2035-09-07 03:00 | 4195.53 | 1.3209 | 87.7975 | 64.1561 | 1229.5885
2035-09-08 04:00 | 3963.21 | 1.2126 | 87.8741 | 64.1561 | 1161.5022
2035-09-09 05:00 | 3584.74 | 1.1529 | 87.0132 | 64.1561 | 1050.5836
2035-09-10 06:00 | 5568.03 | 1.821 | 86.5847 | 64.1561 | 1631.8285
2035-09-11 07:00 | 7143.58 | 2.4162 | 86.2292 | 64.1561 | 2093.5766
2035-09-12 08:00 | 7588.31 | 2.4476 | 86.9619 | 64.1561 | 2223.9141
2035-09-13 09:00 | 9092.53 | 3.0209 | 86.7024 | 64.1561 | 2664.7575
2035-09-14 10:00 | 10539.8 | 3.7262 | 86.1999 | 64.1561 | 3088.9105
2035-09-15 11:00 | 12858.6 | 4.4286 | 86.7839 | 64.1561 | 3768.4837
2035-09-16 12:00 | 14229.5 | 4.8251 | 87.3678 | 64.1561 | 4170.2548
2035-09-17 13:00 | 14779.7 | 4.7612 | 88.3548 | 64.1561 | 4331.5025
2035-09-18 14:00 | 15441 | 5.0472 | 88.4842 | 64.1561 | 4525.3104
2035-09-19 15:00 | 16264.2 | 5.1715 | 89.0929 | 64.1561 | 4766.5665
2035-09-20 16:00 | 18080.8 | 5.83 | 89.2115 | 64.1561 | 5298.9594
2035-09-21 17:00 | 17523.8 | 5.4554 | 90.0522 | 64.1561 | 5135.7188
2035-09-22 18:00 | 15891.9 | 4.9412 | 90.2782 | 64.1561 | 4657.4561
2035-09-23 19:00 | 13790.8 | 4.3721 | 90.0256 | 64.1561 | 4041.6845
2035-09-24 20:00 | 12723.2 | 3.961 | 90.0981 | 64.1561 | 3728.8018
2035-09-25 21:00 | 11817.7 | 3.593 | 90.2535 | 64.1561 | 3463.426
2035-09-26 22:00 | 10906.1 | 3.3793 | 89.8459 | 64.1561 | 3196.2624
2035-09-27 23:00 | 7750.66 | 2.3195 | 90.1022 | 64.1561 | 2271.4942
2035-09-29 | 7098.65 | 2.054 | 90.0867 | 64.1561 | 2080.409
2035-09-30 01:00 | 6203.82 | 1.9091 | 88.9594 | 64.1561 | 1818.1602
2035-10-01 02:00 | 5697.84 | 1.7384 | 88.7869 | 64.1561 | 1669.8721
2035-10-02 03:00 | 5215 | 1.616 | 88.3206 | 64.1561 | 1528.3656
2035-10-03 04:00 | 4605.28 | 1.4726 | 87.6587 | 64.1561 | 1349.6743
2035-10-04 05:00 | 4588.61 | 1.4131 | 87.8847 | 64.1561 | 1344.7888
2035-10-05 06:00 | 6300.72 | 2.097 | 86.7465 | 64.1561 | 1846.5588
2035-10-06 07:00 | 7682.07 | 2.6572 | 86.3537 | 64.1561 | 2251.3925
2035-10-07 08:00 | 8090.97 | 2.6704 | 87.0414 | 64.1561 | 2371.2292
2035-10-08 09:00 | 9924.88 | 3.3197 | 86.9595 | 64.1561 | 2908.6952
2035-10-09 10:00 | 11657.4 | 3.962 | 87.0064 | 64.1561 | 3416.4467
2035-10-10 11:00 | 13314.4 | 4.3845 | 87.7185 | 64.1561 | 3902.0655
2035-10-11 12:00 | 13718.1 | 4.5997 | 87.8683 | 64.1561 | 4020.3782
2035-10-12 13:00 | 14846.6 | 4.7596 | 88.6578 | 64.1561 | 4351.1089
2035-10-13 14:00 | 15144.3 | 4.8874 | 88.8848 | 64.1561 | 4438.3562
2035-10-14 15:00 | 15555.9 | 4.9351 | 89.3283 | 64.1561 | 4558.9843
2035-10-15 16:00 | 17428.6 | 5.5056 | 89.5743 | 64.1561 | 5107.8185
2035-10-16 17:00 | 15765.1 | 4.8822 | 90.1848 | 64.1561 | 4620.2947
2035-10-17 18:00 | 14337.7 | 4.3334 | 90.5606 | 64.1561 | 4201.9651
2035-10-18 19:00 | 11983.1 | 3.8067 | 89.8457 | 64.1561 | 3511.8999
2035-10-19 20:00 | 10906.5 | 3.4067 | 89.8188 | 64.1561 | 3196.3796
2035-10-20 21:00 | 9797.58 | 3.1293 | 89.3203 | 64.1561 | 2871.3873
2035-10-21 22:00 | 9172.5 | 2.8602 | 89.3462 | 64.1561 | 2688.1944
2035-10-22 23:00 | 6883.65 | 1.9948 | 90.0811 | 64.1561 | 2017.3987
2035-10-24 | 6071.33 | 1.8121 | 89.2976 | 64.1561 | 1779.3312
2035-10-25 01:00 | 5935.47 | 1.7144 | 89.4174 | 64.1561 | 1739.5145
2035-10-26 02:00 | 5761.11 | 1.7653 | 88.4336 | 64.1561 | 1688.4147
2035-10-27 03:00 | 5813.41 | 1.8557 | 87.7469 | 64.1561 | 1703.7423
2035-10-28 04:00 | 6039.48 | 1.9583 | 87.3955 | 64.1561 | 1769.9969
2035-10-29 05:00 | 6885.9 | 2.2765 | 87.0882 | 64.1561 | 2018.0581
2035-10-30 06:00 | 6980.06 | 2.2987 | 87.1589 | 64.1561 | 2045.6537
2035-10-31 07:00 | 7330.44 | 2.427 | 87.0963 | 64.1561 | 2148.3399
2035-11-01 08:00 | 6890.37 | 2.1619 | 87.7719 | 64.1561 | 2019.3681
2035-11-02 09:00 | 7790.88 | 2.5769 | 87.076 | 64.1561 | 2283.2815
2035-11-03 10:00 | 9150.21 | 3.0395 | 87.0693 | 64.1561 | 2681.6618
2035-11-04 11:00 | 10862.1 | 3.7278 | 86.8464 | 64.1561 | 3183.3673
2035-11-05 12:00 | 11045.9 | 3.6429 | 87.5723 | 64.1561 | 3237.2337
2035-11-06 13:00 | 12766.8 | 4.1869 | 87.7827 | 64.1561 | 3741.5797
2035-11-07 14:00 | 12873.2 | 4.1841 | 88.1829 | 64.1561 | 3772.7625
2035-11-08 15:00 | 15522.8 | 5.0024 | 88.473 | 64.1561 | 4549.2836
2035-11-09 16:00 | 15279.6 | 4.9889 | 88.7142 | 64.1561 | 4478.0087
2035-11-10 17:00 | 13996.6 | 4.5093 | 89.0912 | 64.1561 | 4101.9985
2035-11-11 18:00 | 11713.8 | 3.7029 | 89.3413 | 64.1561 | 3432.9759
2035-11-12 19:00 | 10475.2 | 3.2809 | 89.2624 | 64.1561 | 3069.9781
2035-11-13 20:00 | 8383.28 | 2.5088 | 89.6694 | 64.1561 | 2456.8968
2035-11-14 21:00 | 7454.72 | 2.2474 | 89.234 | 64.1561 | 2184.7628
2035-11-15 22:00 | 5584.67 | 1.6226 | 89.414 | 64.1561 | 1636.7052
2035-11-16 23:00 | 4867.43 | 1.4578 | 88.6218 | 64.1561 | 1426.5029
2035-11-18 | 4174.26 | 1.3185 | 87.6398 | 64.1561 | 1223.3548
2035-11-19 01:00 | 4071.99 | 1.2751 | 87.4592 | 64.1561 | 1193.3825
2035-11-20 02:00 | 3775.07 | 1.2247 | 86.8191 | 64.1561 | 1106.3638
2035-11-21 03:00 | 4036.83 | 1.281 | 86.8659 | 64.1561 | 1183.0781
2035-11-22 04:00 | 4471.64 | 1.4032 | 86.866 | 64.1561 | 1310.5083
2035-11-23 05:00 | 5595.39 | 1.8097 | 86.42 | 64.1561 | 1639.8469
2035-11-24 06:00 | 5714.51 | 1.8575 | 86.4178 | 64.1561 | 1674.7576
2035-11-25 07:00 | 6089.13 | 2.0438 | 86.0494 | 64.1561 | 1784.5478
2035-11-26 08:00 | 5901.17 | 1.8285 | 87.0627 | 64.1561 | 1729.4622
2035-11-27 09:00 | 6158.64 | 2.0065 | 86.4349 | 64.1561 | 1804.9192
2035-11-28 10:00 | 7581.1 | 2.5968 | 85.8604 | 64.1561 | 2221.8011
2035-11-29 11:00 | 9034.45 | 3.1015 | 85.971 | 64.1561 | 2647.7359
2035-11-30 12:00 | 10200.4 | 3.4008 | 86.5358 | 64.1561 | 2989.4421
2035-12-01 13:00 | 11299.8 | 3.7985 | 86.671 | 64.1561 | 3311.6445
2035-12-02 14:00 | 12976.3 | 4.2709 | 87.1813 | 64.1561 | 3802.9781
2035-12-03 15:00 | 15014.1 | 4.9822 | 87.4259 | 64.1561 | 4400.1984
2035-12-04 16:00 | 15920.5 | 5.1782 | 88.0952 | 64.1561 | 4665.838
2035-12-05 17:00 | 16156.3 | 5.146 | 88.7134 | 64.1561 | 4734.9441
2035-12-06 18:00 | 14300.9 | 4.4919 | 89.1766 | 64.1561 | 4191.1801
2035-12-07 19:00 | 12514.3 | 3.9106 | 89.2734 | 64.1561 | 3667.5793
2035-12-08 20:00 | 10188.3 | 3.1128 | 89.4582 | 64.1561 | 2985.896
2035-12-09 21:00 | 8979.95 | 2.7517 | 89.1582 | 64.1561 | 2631.7636
2035-12-10 22:00 | 6927.25 | 2.0566 | 89.3159 | 64.1561 | 2030.1766
2035-12-11 23:00 | 5774.95 | 1.8233 | 88.1597 | 64.1561 | 1692.4708
2035-12-13 | 5463.65 | 1.5727 | 89.0179 | 64.1561 | 1601.2378
2035-12-14 01:00 | 4923.23 | 1.5257 | 87.8123 | 64.1561 | 1442.8563
2035-12-15 02:00 | 4792.13 | 1.5204 | 87.2994 | 64.1561 | 1404.4347
2035-12-16 03:00 | 4883.41 | 1.5538 | 87.0647 | 64.1561 | 1431.1862
2035-12-17 04:00 | 5054.08 | 1.5952 | 87.024 | 64.1561 | 1481.2046
2035-12-18 05:00 | 5731.89 | 1.9076 | 86.2745 | 64.1561 | 1679.8511
2035-12-19 06:00 | 6173.36 | 1.9773 | 86.711 | 64.1561 | 1809.2332
2035-12-20 07:00 | 6748.85 | 2.2339 | 86.3266 | 64.1561 | 1977.8927
2035-12-21 08:00 | 7117.61 | 2.3187 | 86.5793 | 64.1561 | 2085.9656
2035-12-22 09:00 | 8943.66 | 2.8958 | 86.7154 | 64.1561 | 2621.128
2035-12-23 10:00 | 10361 | 3.4909 | 86.4858 | 64.1561 | 3036.5094
2035-12-24 11:00 | 11852.2 | 4.0206 | 86.6962 | 64.1561 | 3473.5369
2035-12-25 12:00 | 12847.4 | 4.2393 | 87.3457 | 64.1561 | 3765.2013
2035-12-26 13:00 | 13746.9 | 4.3857 | 88.0634 | 64.1561 | 4028.8187
2035-12-27 14:00 | 14391.2 | 4.6345 | 88.2588 | 64.1561 | 4217.6444
2035-12-28 15:00 | 15421.8 | 5.0906 | 88.2205 | 64.1561 | 4519.6834
2035-12-29 16:00 | 15762.3 | 4.9394 | 89.1371 | 64.1561 | 4619.4741
2035-12-30 17:00 | 15135.5 | 4.8751 | 89.0254 | 64.1561 | 4435.7772
2035-12-31 18:00 | 13549.4 | 4.2572 | 89.4389 | 64.1561 | 3970.9372
2036-01-01 19:00 | 11983.5 | 3.6831 | 89.6556 | 64.1561 | 3512.0172
2036-01-02 20:00 | 9877.99 | 2.9642 | 89.8239 | 64.1561 | 2894.9531
2036-01-03 21:00 | 8851.58 | 2.682 | 89.409 | 64.1561 | 2594.142
2036-01-04 22:00 | 7011.71 | 2.0612 | 89.543 | 64.1561 | 2054.9294
2036-01-05 23:00 | 6289.36 | 1.8832 | 88.9447 | 64.1561 | 1843.2295
2036-01-07 | 5796.13 | 1.748 | 88.5548 | 64.1561 | 1698.678
2036-01-08 01:00 | 5489.69 | 1.6861 | 88.0796 | 64.1561 | 1608.8693
2036-01-09 02:00 | 5408.63 | 1.6895 | 87.6705 | 64.1561 | 1585.113
2036-01-10 03:00 | 5512.31 | 1.7499 | 87.3022 | 64.1561 | 1615.4986
2036-01-11 04:00 | 4553.08 | 1.6399 | 85.7321 | 64.1561 | 1334.376
2036-01-12 05:00 | 5299.51 | 1.7596 | 86.4396 | 64.1561 | 1553.1331
2036-01-13 06:00 | 5622.49 | 1.7571 | 87.1066 | 64.1561 | 1647.7892
2036-01-14 07:00 | 5824.57 | 1.8844 | 86.6577 | 64.1561 | 1707.013
2036-01-15 08:00 | 5411.01 | 1.6574 | 87.3227 | 64.1561 | 1585.8105
2036-01-16 09:00 | 5949.27 | 1.9494 | 86.401 | 64.1561 | 1743.5589
2036-01-17 10:00 | 7220.86 | 2.4782 | 85.8683 | 64.1561 | 2116.2252
2036-01-18 11:00 | 8119.53 | 2.8 | 85.9311 | 64.1561 | 2379.5993
2036-01-19 12:00 | 9230.68 | 3.0295 | 86.638 | 64.1561 | 2705.2453
2036-01-20 13:00 | 10386.1 | 3.2875 | 87.2458 | 64.1561 | 3043.8654
2036-01-21 14:00 | 11684.1 | 3.8113 | 87.1026 | 64.1561 | 3424.2717
2036-01-22 15:00 | 13692.9 | 4.5068 | 87.256 | 64.1561 | 4012.9929
2036-01-23 16:00 | 14083.3 | 4.5896 | 87.7515 | 64.1561 | 4127.4078
2036-01-24 17:00 | 14054.4 | 4.4753 | 88.3043 | 64.1561 | 4118.938
2036-01-25 18:00 | 12086.2 | 3.7781 | 88.7222 | 64.1561 | 3542.1156
2036-01-26 19:00 | 10839.5 | 3.2971 | 89.0139 | 64.1561 | 3176.7439
2036-01-27 20:00 | 8578.42 | 2.5848 | 89.0341 | 64.1561 | 2514.0867
2036-01-28 21:00 | 7676.75 | 2.331 | 88.6548 | 64.1561 | 2249.8333
2036-01-29 22:00 | 5820.65 | 1.6878 | 89.0219 | 64.1561 | 1705.8641
2036-01-30 23:00 | 5183.67 | 1.5741 | 88.0676 | 64.1561 | 1519.1837
2036-02-01 | 4602.15 | 1.4289 | 87.5128 | 64.1561 | 1348.757
2036-02-02 01:00 | 4254.01 | 1.3674 | 86.8446 | 64.1561 | 1246.7273
2036-02-03 02:00 | 4205.4 | 1.3509 | 86.65 | 64.1561 | 1232.4811
2036-02-04 03:00 | 4573.06 | 1.4497 | 86.6317 | 64.1561 | 1340.2316
2036-02-05 04:00 | 5169.38 | 1.5644 | 87.1248 | 64.1561 | 1514.9957
2036-02-06 05:00 | 5859.16 | 2.0381 | 85.4115 | 64.1561 | 1717.1503
2036-02-07 06:00 | 6083.73 | 1.9804 | 86.218 | 64.1561 | 1782.9653
2036-02-08 07:00 | 6360.6 | 2.0381 | 86.4316 | 64.1561 | 1864.1078
2036-02-09 08:00 | 5562.7 | 1.7146 | 86.9653 | 64.1561 | 1630.2664
2036-02-10 09:00 | 6835.49 | 2.278 | 85.9388 | 64.1561 | 2003.2844
2036-02-11 10:00 | 8024.96 | 2.8052 | 85.4886 | 64.1561 | 2351.8836
2036-02-12 11:00 | 9961.41 | 3.5136 | 85.5614 | 64.1561 | 2919.4011
2036-02-13 12:00 | 11837.8 | 3.9966 | 86.3497 | 64.1561 | 3469.3167
2036-02-14 13:00 | 13134.2 | 4.2456 | 87.2326 | 64.1561 | 3849.254
2036-02-15 14:00 | 14009 | 4.6038 | 87.415 | 64.1561 | 4105.6326
2036-02-16 15:00 | 15190.4 | 5.0206 | 87.6679 | 64.1561 | 4451.8668
2036-02-17 16:00 | 15728.2 | 4.9542 | 88.5986 | 64.1561 | 4609.4804
2036-02-18 17:00 | 14969.4 | 4.8315 | 88.5909 | 64.1561 | 4387.0981
2036-02-19 18:00 | 12911.7 | 4.2281 | 88.5477 | 64.1561 | 3784.0457
2036-02-20 19:00 | 11193 | 3.5138 | 88.9627 | 64.1561 | 3280.3445
2036-02-21 20:00 | 8857.22 | 2.7101 | 89.1225 | 64.1561 | 2595.7949
2036-02-22 21:00 | 7817.98 | 2.343 | 89.0723 | 64.1561 | 2291.2238
2036-02-23 22:00 | 5927.94 | 1.6774 | 89.5651 | 64.1561 | 1737.3077
2036-02-24 23:00 | 4017.78 | 1.2248 | 88.1996 | 64.1561 | 1177.4951
2036-02-26 | 2999.7 | 1.0148 | 86.4865 | 64.1561 | 879.1253
2036-02-27 01:00 | 3153.53 | 1 | 90.873 | 64.1561 | 924.2084
2036-02-28 02:00 | 3023.21 | 1 | 73.5736 | 64.1561 | 886.0154
2036-02-29 03:00 | 3001.1 | 1 | 73.3551 | 64.1561 | 879.5356
2036-03-01 04:00 | 3046.52 | 1 | 73.1445 | 64.1561 | 892.8469
2036-03-02 05:00 | 3011.53 | 1 | 72.9994 | 64.1561 | 882.5923
2036-03-03 06:00 | 3132.95 | 1 | 72.8481 | 64.1561 | 918.177
2036-03-04 07:00 | 3462.97 | 1.1178 | 85.625 | 64.1561 | 1014.8963
2036-03-05 08:00 | 3692.24 | 1.2302 | 85.1853 | 64.1561 | 1082.0887
2036-03-06 09:00 | 5717.78 | 1.8969 | 85.2022 | 64.1561 | 1675.7159
2036-03-07 10:00 | 7369.13 | 2.5992 | 84.6843 | 64.1561 | 2159.6788
2036-03-08 11:00 | 9213.74 | 3.0835 | 85.5546 | 64.1561 | 2700.2806
2036-03-09 12:00 | 10588.8 | 3.4481 | 86.217 | 64.1561 | 3103.2709
2036-03-10 13:00 | 11378.4 | 3.713 | 86.5362 | 64.1561 | 3334.6799
2036-03-11 14:00 | 12211.1 | 3.9014 | 87.0958 | 64.1561 | 3578.7201
2036-03-12 15:00 | 12834.1 | 4.1158 | 87.3189 | 64.1561 | 3761.3034
2036-03-13 16:00 | 15027.9 | 4.8572 | 87.4604 | 64.1561 | 4404.2427
2036-03-14 17:00 | 13670.1 | 4.3778 | 87.9856 | 64.1561 | 4006.3108
2036-03-15 18:00 | 11913.8 | 3.7699 | 88.262 | 64.1561 | 3491.5901
2036-03-16 19:00 | 10164 | 3.1515 | 88.4427 | 64.1561 | 2978.7744
2036-03-17 20:00 | 9002.94 | 2.8428 | 88.0677 | 64.1561 | 2638.5013
2036-03-18 21:00 | 8106.79 | 2.5435 | 87.9792 | 64.1561 | 2375.8656
2036-03-19 22:00 | 7240.86 | 2.2862 | 87.6959 | 64.1561 | 2122.0866
2036-03-20 23:00 | 4431.07 | 1.3129 | 88.3076 | 64.1561 | 1298.6184
2036-03-22 | 3224.15 | 1 | 87.604 | 64.1561 | 944.9051
2036-03-23 01:00 | 3143.29 | 1 | 89.8873 | 64.1561 | 921.2074
2036-03-24 02:00 | 3183.07 | 1 | 94.62 | 64.1561 | 932.8657
2036-03-25 03:00 | 3077.2 | 1 | 73.1322 | 64.1561 | 901.8383
2036-03-26 04:00 | 3083.09 | 1 | 72.9288 | 64.1561 | 903.5645
2036-03-27 05:00 | 3120.21 | 1 | 72.7807 | 64.1561 | 914.4433
2036-03-28 06:00 | 3210.67 | 1.0024 | 85.968 | 64.1561 | 940.9545
2036-03-29 07:00 | 4900 | 1.5158 | 85.9799 | 64.1561 | 1436.0482
2036-03-30 08:00 | 5214.95 | 1.6244 | 86.0156 | 64.1561 | 1528.351
2036-03-31 09:00 | 6887.36 | 2.2494 | 85.5013 | 64.1561 | 2018.486
2036-04-01 10:00 | 8879.78 | 2.9745 | 85.3898 | 64.1561 | 2602.4066
2036-04-02 11:00 | 10951.6 | 3.6056 | 85.9274 | 64.1561 | 3209.5971
2036-04-03 12:00 | 12231.3 | 4.0307 | 86.3421 | 64.1561 | 3584.6402
2036-04-04 13:00 | 12647.4 | 4.3115 | 86.3264 | 64.1561 | 3706.5871
2036-04-05 14:00 | 13813.1 | 4.3736 | 87.4969 | 64.1561 | 4048.22
2036-04-06 15:00 | 13456.7 | 4.3034 | 87.7063 | 64.1561 | 3943.7695
2036-04-07 16:00 | 15543.3 | 5.0793 | 87.6124 | 64.1561 | 4555.2916
2036-04-08 17:00 | 14422.9 | 4.6315 | 88.1909 | 64.1561 | 4226.9347
2036-04-09 18:00 | 12976.9 | 4.0504 | 88.6848 | 64.1561 | 3803.154
2036-04-10 19:00 | 11369.7 | 3.4653 | 88.9509 | 64.1561 | 3332.1301
2036-04-11 20:00 | 10436 | 3.1964 | 88.7584 | 64.1561 | 3058.4897
2036-04-12 21:00 | 9164.07 | 2.855 | 88.426 | 64.1561 | 2685.7238
2036-04-13 22:00 | 8037.02 | 2.564 | 87.9143 | 64.1561 | 2355.4181
2036-04-14 23:00 | 5771.25 | 1.681 | 88.8481 | 64.1561 | 1691.3864
2036-04-16 | 4790.49 | 1.4748 | 87.743 | 64.1561 | 1403.954
2036-04-17 01:00 | 4108.97 | 1.2834 | 87.2361 | 64.1561 | 1204.2202
2036-04-18 02:00 | 3748.54 | 1.1655 | 87.0084 | 64.1561 | 1098.5886
2036-04-19 03:00 | 3650.31 | 1.1716 | 86.376 | 64.1561 | 1069.8003
2036-04-20 04:00 | 3627.62 | 1.1394 | 86.4324 | 64.1561 | 1063.1505
2036-04-21 05:00 | 4463.25 | 1.402 | 86.2818 | 64.1561 | 1308.0495
2036-04-22 06:00 | 4910.08 | 1.5341 | 86.3301 | 64.1561 | 1439.0024
2036-04-23 07:00 | 5969.47 | 1.8835 | 86.2169 | 64.1561 | 1749.479
2036-04-24 08:00 | 6521.26 | 2.2129 | 85.4491 | 64.1561 | 1911.1926
2036-04-25 09:00 | 8514.89 | 2.9309 | 85.3824 | 64.1561 | 2495.4679
2036-04-26 10:00 | 10880.2 | 3.6737 | 85.8623 | 64.1561 | 3188.6719
2036-04-27 11:00 | 12593 | 4.2502 | 86.2759 | 64.1561 | 3690.644
2036-04-28 12:00 | 14192.9 | 4.5704 | 87.257 | 64.1561 | 4159.5284
2036-04-29 13:00 | 14307.8 | 4.6306 | 87.6377 | 64.1561 | 4193.2023
2036-04-30 14:00 | 14410.5 | 4.721 | 87.8054 | 64.1561 | 4223.3007
2036-05-01 15:00 | 15955.9 | 5.1852 | 88.1325 | 64.1561 | 4676.2127
2036-05-02 16:00 | 16116.5 | 5.216 | 88.5221 | 64.1561 | 4723.2799
2036-05-03 17:00 | 15915.1 | 5.0006 | 89.1374 | 64.1561 | 4664.2554
2036-05-04 18:00 | 13756.3 | 4.3337 | 89.2685 | 64.1561 | 4031.5736
2036-05-05 19:00 | 11843.1 | 3.7379 | 89.1717 | 64.1561 | 3470.87
2036-05-06 20:00 | 9781.39 | 2.9201 | 89.7003 | 64.1561 | 2866.6424
2036-05-07 21:00 | 8705.41 | 2.5844 | 89.4693 | 64.1561 | 2551.3038
2036-05-08 22:00 | 6546.31 | 1.8931 | 89.5344 | 64.1561 | 1918.5341
2036-05-09 23:00 | 5319.98 | 1.6171 | 88.4611 | 64.1561 | 1559.1322
2036-05-11 | 4373.07 | 1.3891 | 87.5211 | 64.1561 | 1281.6203
2036-05-12 01:00 | 3926.61 | 1.2263 | 87.3954 | 64.1561 | 1150.7758
2036-05-13 02:00 | 3679.21 | 1.1293 | 87.3435 | 64.1561 | 1078.27
2036-05-14 03:00 | 3767.17 | 1.1787 | 86.8578 | 64.1561 | 1104.0485
2036-05-15 04:00 | 4101.22 | 1.3105 | 86.4269 | 64.1561 | 1201.9489
2036-05-16 05:00 | 5041.84 | 1.5523 | 86.7772 | 64.1561 | 1477.6174
2036-05-17 06:00 | 5150.28 | 1.6167 | 86.5467 | 64.1561 | 1509.3981
2036-05-18 07:00 | 5885.32 | 1.9556 | 85.8456 | 64.1561 | 1724.817
2036-05-19 08:00 | 6211.53 | 2.0717 | 85.8651 | 64.1561 | 1820.4197
2036-05-20 09:00 | 7619.02 | 2.6116 | 85.5996 | 64.1561 | 2232.9143
2036-05-21 10:00 | 8820.5 | 2.9937 | 85.8836 | 64.1561 | 2585.0334
2036-05-22 11:00 | 10424 | 3.5674 | 85.9953 | 64.1561 | 3054.9728
2036-05-23 12:00 | 11840.8 | 3.9007 | 86.7255 | 64.1561 | 3470.1959
2036-05-24 13:00 | 11576.2 | 3.7479 | 87.2606 | 64.1561 | 3392.6493
2036-05-25 14:00 | 11501.6 | 3.7245 | 87.4335 | 64.1561 | 3370.7862
2036-05-26 15:00 | 13847.9 | 4.5587 | 87.3313 | 64.1561 | 4058.4189
2036-05-27 16:00 | 15051.5 | 4.8756 | 87.8678 | 64.1561 | 4411.1592
2036-05-28 17:00 | 15152.9 | 4.8628 | 88.3215 | 64.1561 | 4440.8766
2036-05-29 18:00 | 13440.9 | 4.2463 | 88.7371 | 64.1561 | 3939.1389
2036-05-30 19:00 | 11901 | 3.7099 | 88.9066 | 64.1561 | 3487.8388
2036-05-31 20:00 | 9742.07 | 2.921 | 89.3265 | 64.1561 | 2855.1189
2036-06-01 21:00 | 8508.15 | 2.5877 | 88.8904 | 64.1561 | 2493.4926
2036-06-02 22:00 | 6551.11 | 1.9018 | 89.2423 | 64.1561 | 1919.9408
2036-06-03 23:00 | 5751.42 | 1.6844 | 88.7545 | 64.1561 | 1685.5748
2036-06-05 | 5335.64 | 1.5189 | 88.8331 | 64.1561 | 1563.7217
2036-06-06 01:00 | 4567.42 | 1.4157 | 87.4906 | 64.1561 | 1338.5787
2036-06-07 02:00 | 4305.29 | 1.3542 | 87.0841 | 64.1561 | 1261.7559
2036-06-08 03:00 | 4397.62 | 1.3862 | 86.852 | 64.1561 | 1288.8152
2036-06-09 04:00 | 4756.9 | 1.5266 | 86.494 | 64.1561 | 1394.1098
2036-06-10 05:00 | 5536.37 | 1.8002 | 86.2469 | 64.1561 | 1622.5499
2036-06-11 06:00 | 5704.8 | 1.8873 | 86.046 | 64.1561 | 1671.9118
2036-06-12 07:00 | 6532.41 | 2.2094 | 85.7851 | 64.1561 | 1914.4604
2036-06-13 08:00 | 7207.56 | 2.2899 | 86.6151 | 64.1561 | 2112.3273
2036-06-14 09:00 | 8720.22 | 2.9997 | 85.7837 | 64.1561 | 2555.6442
2036-06-15 10:00 | 10150.9 | 3.5779 | 85.7354 | 64.1561 | 2974.9351
2036-06-16 11:00 | 11883.2 | 4.071 | 86.3279 | 64.1561 | 3482.6221
2036-06-17 12:00 | 12479.1 | 4.0508 | 87.3083 | 64.1561 | 3657.2632
2036-06-18 13:00 | 13050.2 | 4.3509 | 87.275 | 64.1561 | 3824.6361
2036-06-19 14:00 | 13846.8 | 4.5956 | 87.5875 | 64.1561 | 4058.0965
2036-06-20 15:00 | 15645.1 | 5.0832 | 88.0962 | 64.1561 | 4585.1262
2036-06-21 16:00 | 16240.7 | 5.219 | 88.5982 | 64.1561 | 4759.6793
2036-06-22 17:00 | 16084.2 | 4.9148 | 89.519 | 64.1561 | 4713.8137
2036-06-23 18:00 | 14015.5 | 4.2478 | 89.8283 | 64.1561 | 4107.5376
2036-06-24 19:00 | 12242.9 | 3.7666 | 89.5927 | 64.1561 | 3588.0398
2036-06-25 20:00 | 9710.38 | 2.9247 | 89.7216 | 64.1561 | 2845.8315
2036-06-26 21:00 | 8075.49 | 2.5573 | 88.7581 | 64.1561 | 2366.6925
2036-06-27 22:00 | 5746.09 | 1.8264 | 88.3627 | 64.1561 | 1684.0127
2036-06-28 23:00 | 5234.85 | 1.4915 | 89.3106 | 64.1561 | 1534.1831
2036-06-30 | 4529.53 | 1.3765 | 88.118 | 64.1561 | 1327.4742
2036-07-01 01:00 | 3814.18 | 1.232 | 87.0695 | 64.1561 | 1117.8258
2036-07-02 02:00 | 3412.17 | 1.0793 | 87.0443 | 64.1561 | 1000.0083
2036-07-03 03:00 | 3420.6 | 1.1386 | 86.168 | 64.1561 | 1002.4789
2036-07-04 04:00 | 3457.39 | 1.1375 | 86.1225 | 64.1561 | 1013.261
2036-07-05 05:00 | 4419.35 | 1.4341 | 86.1184 | 64.1561 | 1295.1836
2036-07-06 06:00 | 4488.84 | 1.3836 | 86.728 | 64.1561 | 1315.5491
2036-07-07 07:00 | 5088.51 | 1.6185 | 86.2902 | 64.1561 | 1491.2951
2036-07-08 08:00 | 5300.98 | 1.7112 | 86.1316 | 64.1561 | 1553.5639
2036-07-09 09:00 | 7114.06 | 2.4963 | 85.1745 | 64.1561 | 2084.9252
2036-07-10 10:00 | 8626.87 | 2.8863 | 85.9186 | 64.1561 | 2528.286
2036-07-11 11:00 | 8748.56 | 2.799 | 86.7065 | 64.1561 | 2563.9498
2036-07-12 12:00 | 9374.64 | 3.0169 | 86.7743 | 64.1561 | 2747.4358
2036-07-13 13:00 | 10659.9 | 3.6083 | 86.3286 | 64.1561 | 3124.1083
2036-07-14 14:00 | 11053 | 3.6281 | 86.9519 | 64.1561 | 3239.3145
2036-07-15 15:00 | 13545.8 | 4.5457 | 86.8638 | 64.1561 | 3969.8821
2036-07-16 16:00 | 14734.6 | 4.7158 | 87.7962 | 64.1561 | 4318.285
2036-07-17 17:00 | 14603.3 | 4.6038 | 88.3483 | 64.1561 | 4279.8048
2036-07-18 18:00 | 12594.9 | 3.9414 | 88.6753 | 64.1561 | 3691.2008
2036-07-19 19:00 | 10695.2 | 3.323 | 88.7288 | 64.1561 | 3134.4537
2036-07-20 20:00 | 8342.31 | 2.5547 | 88.7707 | 64.1561 | 2444.8897
2036-07-21 21:00 | 7409.21 | 2.2012 | 88.8464 | 64.1561 | 2171.4251
2036-07-22 22:00 | 5496.04 | 1.5725 | 89.0772 | 64.1561 | 1610.7303
2036-07-23 23:00 | 4563.36 | 1.3881 | 87.8925 | 64.1561 | 1337.3888
2036-07-25 | 3877.61 | 1.2033 | 87.316 | 64.1561 | 1136.4153
2036-07-26 01:00 | 3503.67 | 1.0926 | 86.9814 | 64.1561 | 1026.8243
2036-07-27 02:00 | 3654.07 | 1.1235 | 86.9445 | 64.1561 | 1070.9022
2036-07-28 03:00 | 4008.22 | 1.2331 | 86.7701 | 64.1561 | 1174.6933
2036-07-29 04:00 | 4201.66 | 1.3232 | 86.3775 | 64.1561 | 1231.385
2036-07-30 05:00 | 5036.32 | 1.6907 | 85.5221 | 64.1561 | 1475.9997
2036-07-31 06:00 | 5095.75 | 1.6386 | 86.0552 | 64.1561 | 1493.4169
2036-08-01 07:00 | 5148.3 | 1.6381 | 86.1841 | 64.1561 | 1508.8178
2036-08-02 08:00 | 3995.43 | 1.2595 | 86.2979 | 64.1561 | 1170.9449
2036-08-03 09:00 | 5146.83 | 1.748 | 85.2514 | 64.1561 | 1508.387
2036-08-04 10:00 | 5933.71 | 1.9875 | 85.4417 | 64.1561 | 1738.9987
2036-08-05 11:00 | 6973.02 | 2.3203 | 85.5994 | 64.1561 | 2043.5904
2036-08-06 12:00 | 7406.19 | 2.4583 | 85.7567 | 64.1561 | 2170.54
2036-08-07 13:00 | 7677.23 | 2.5257 | 85.9623 | 64.1561 | 2249.974
2036-08-08 14:00 | 7810.95 | 2.5317 | 86.2375 | 64.1561 | 2289.1635
2036-08-09 15:00 | 9198.73 | 3.0732 | 85.9152 | 64.1561 | 2695.8816
2036-08-10 16:00 | 9606.75 | 3.1164 | 86.4255 | 64.1561 | 2815.4605
2036-08-11 17:00 | 9649.23 | 3.1073 | 86.6252 | 64.1561 | 2827.9102
2036-08-12 18:00 | 8572.94 | 2.6511 | 87.1983 | 64.1561 | 2512.4807
2036-08-13 19:00 | 7713.31 | 2.3987 | 87.0726 | 64.1561 | 2260.548
2036-08-14 20:00 | 5895.99 | 1.7247 | 87.7964 | 64.1561 | 1727.9441
2036-08-15 21:00 | 5203.11 | 1.5749 | 87.1125 | 64.1561 | 1524.881
2036-08-16 22:00 | 3084.61 | 1 | 86.1446 | 64.1561 | 904.01
2036-08-17 23:00 | 3028.73 | 1 | 93.6112 | 64.1561 | 887.6331
2036-08-19 | 3004.7 | 1 | 72.7088 | 64.1561 | 880.5906
2036-08-20 01:00 | 3064.27 | 1 | 72.5562 | 64.1561 | 898.0489
2036-08-21 02:00 | 3113.75 | 1 | 72.444 | 64.1561 | 912.55
2036-08-22 03:00 | 3053.26 | 1 | 72.3595 | 64.1561 | 894.8222
2036-08-23 04:00 | 3220.98 | 1 | 72.244 | 64.1561 | 943.9761
2036-08-24 05:00 | 3127.69 | 1 | 72.2042 | 64.1561 | 916.6355
2036-08-25 06:00 | 3179.01 | 1 | 91.1169 | 64.1561 | 931.6759
2036-08-26 07:00 | 3381.39 | 1.0697 | 85.1605 | 64.1561 | 990.9876
2036-08-27 08:00 | 3215.44 | 1 | 88.399 | 64.1561 | 942.3524
2036-08-28 09:00 | 3476.14 | 1.0702 | 85.4376 | 64.1561 | 1018.7561
2036-08-29 10:00 | 4770.44 | 1.5345 | 84.882 | 64.1561 | 1398.078
2036-08-30 11:00 | 6394.92 | 2.1275 | 84.5952 | 64.1561 | 1874.166
2036-08-31 12:00 | 6926.88 | 2.381 | 84.4461 | 64.1561 | 2030.0681
2036-09-01 13:00 | 7300.4 | 2.358 | 85.341 | 64.1561 | 2139.536
2036-09-02 14:00 | 8131.8 | 2.6211 | 85.4993 | 64.1561 | 2383.1953
2036-09-03 15:00 | 7927.69 | 2.598 | 85.4783 | 64.1561 | 2323.3766
2036-09-04 16:00 | 10001.2 | 3.3472 | 85.2959 | 64.1561 | 2931.0624
2036-09-05 17:00 | 8938.27 | 2.8421 | 86.1768 | 64.1561 | 2619.5484
2036-09-06 18:00 | 8037.08 | 2.5014 | 86.4987 | 64.1561 | 2355.4356
2036-09-07 19:00 | 7108.74 | 2.1861 | 86.598 | 64.1561 | 2083.366
2036-09-08 20:00 | 6533.82 | 2.031 | 86.382 | 64.1561 | 1914.8736
2036-09-09 21:00 | 5996.63 | 1.8628 | 86.3242 | 64.1561 | 1757.4388
2036-09-10 22:00 | 5168.96 | 1.6752 | 85.6976 | 64.1561 | 1514.8726
2036-09-11 23:00 | 3172.15 | 1 | 72.7384 | 64.1561 | 929.6654
2036-09-13 | 3146.3 | 1 | 72.4405 | 64.1561 | 922.0895
2036-09-14 01:00 | 3144.14 | 1 | 72.2641 | 64.1561 | 921.4565
2036-09-15 02:00 | 3131.22 | 1 | 72.1515 | 64.1561 | 917.67
2036-09-16 03:00 | 3148.22 | 1 | 72.0426 | 64.1561 | 922.6522
2036-09-17 04:00 | 3154.6 | 1 | 71.9332 | 64.1561 | 924.522
2036-09-18 05:00 | 3242.3 | 1 | 71.8498 | 64.1561 | 950.2243
2036-09-19 06:00 | 3211.23 | 1 | 93.0884 | 64.1561 | 941.1186
2036-09-20 07:00 | 3325.07 | 1.0415 | 84.9915 | 64.1561 | 974.4818
2036-09-21 08:00 | 3219.66 | 1 | 71.7321 | 64.1561 | 943.5892
2036-09-22 09:00 | 3148.6 | 1 | 71.7066 | 64.1561 | 922.7636
2036-09-23 10:00 | 3229.16 | 1 | 88.3236 | 64.1561 | 946.3734
2036-09-24 11:00 | 3572.46 | 1.1293 | 84.7161 | 64.1561 | 1046.9847
2036-09-25 12:00 | 4080.8 | 1.2823 | 84.7885 | 64.1561 | 1195.9644
2036-09-26 13:00 | 4404.63 | 1.3434 | 85.1914 | 64.1561 | 1290.8696
2036-09-27 14:00 | 5054.13 | 1.5928 | 84.8019 | 64.1561 | 1481.2193
2036-09-28 15:00 | 5450.63 | 1.7932 | 84.3462 | 64.1561 | 1597.422
2036-09-29 16:00 | 8140.41 | 2.8821 | 83.5551 | 64.1561 | 2385.7187
2036-09-30 17:00 | 7600.56 | 2.4787 | 84.8276 | 64.1561 | 2227.5043
2036-10-01 18:00 | 7037.07 | 2.2038 | 85.4497 | 64.1561 | 2062.3616
2036-10-02 19:00 | 6463.19 | 1.9797 | 85.7441 | 64.1561 | 1894.174
2036-10-03 20:00 | 6090.3 | 1.8315 | 85.9726 | 64.1561 | 1784.8907
2036-10-04 21:00 | 5555.95 | 1.7444 | 85.4187 | 64.1561 | 1628.2882
2036-10-05 22:00 | 5171.38 | 1.6394 | 85.2282 | 64.1561 | 1515.5819
2036-10-06 23:00 | 3105.53 | 1 | 72.1041 | 64.1561 | 910.141
2036-10-08 | 3098.5 | 1 | 71.8548 | 64.1561 | 908.0807
2036-10-09 01:00 | 3269.61 | 1 | 71.6757 | 64.1561 | 958.2281
2036-10-10 02:00 | 3176.1 | 1 | 71.6406 | 64.1561 | 930.823
2036-10-11 03:00 | 3193.61 | 1 | 71.5671 | 64.1561 | 935.9547
2036-10-12 04:00 | 3150.85 | 1 | 71.4909 | 64.1561 | 923.423
2036-10-13 05:00 | 3153.15 | 1 | 71.4439 | 64.1561 | 924.097
2036-10-14 06:00 | 3215.14 | 1 | 86.6082 | 64.1561 | 942.2645
2036-10-15 07:00 | 4091.46 | 1.282 | 84.5874 | 64.1561 | 1199.0886
2036-10-16 08:00 | 3067.9 | 1 | 86.4827 | 64.1561 | 899.1127
2036-10-17 09:00 | 3366.91 | 1.0891 | 84.177 | 64.1561 | 986.7439
2036-10-18 10:00 | 4645.55 | 1.4901 | 84.2444 | 64.1561 | 1361.4763
2036-10-19 11:00 | 5964.92 | 1.9464 | 84.17 | 64.1561 | 1748.1455
2036-10-20 12:00 | 7914.73 | 2.7226 | 83.7599 | 64.1561 | 2319.5784
2036-10-21 13:00 | 8144.23 | 2.6596 | 84.6782 | 64.1561 | 2386.8382
2036-10-22 14:00 | 9588.95 | 3.2609 | 84.4191 | 64.1561 | 2810.2438
2036-10-23 15:00 | 11110 | 3.656 | 85.1082 | 64.1561 | 3256.0196
2036-10-24 16:00 | 12726.8 | 4.3741 | 84.96 | 64.1561 | 3729.8569
2036-10-25 17:00 | 12266 | 3.8096 | 86.5882 | 64.1561 | 3594.8097
2036-10-26 18:00 | 10352.2 | 3.3236 | 86.394 | 64.1561 | 3033.9303
2036-10-27 19:00 | 8429.96 | 2.6581 | 86.5886 | 64.1561 | 2470.5774
2036-10-28 20:00 | 7400.39 | 2.3036 | 86.5931 | 64.1561 | 2168.8402
2036-10-29 21:00 | 6816.98 | 2.1099 | 86.511 | 64.1561 | 1997.8596
2036-10-30 22:00 | 5953.74 | 1.8657 | 86.2041 | 64.1561 | 1744.869
2036-10-31 23:00 | 3221.9 | 1 | 86.4181 | 64.1561 | 944.2457
2036-11-02 | 3196.09 | 1 | 90.1089 | 64.1561 | 936.6815
2036-11-03 01:00 | 3227.29 | 1 | 72.1459 | 64.1561 | 945.8253
2036-11-04 02:00 | 3156.42 | 1 | 72.0289 | 64.1561 | 925.0554
2036-11-05 03:00 | 3135.85 | 1 | 71.8819 | 64.1561 | 919.0269
2036-11-06 04:00 | 3163.7 | 1 | 92.5178 | 64.1561 | 927.1889
2036-11-07 05:00 | 3401.21 | 1.0544 | 84.9798 | 64.1561 | 996.7963
2036-11-08 06:00 | 3731.3 | 1.1746 | 84.7534 | 64.1561 | 1093.5361
2036-11-09 07:00 | 5029.93 | 1.5429 | 85.0673 | 64.1561 | 1474.127
2036-11-10 08:00 | 5842 | 1.8647 | 84.7015 | 64.1561 | 1712.1212
2036-11-11 09:00 | 7762.37 | 2.6385 | 84.1078 | 64.1561 | 2274.9261
2036-11-12 10:00 | 9513.05 | 3.173 | 84.6212 | 64.1561 | 2787.9997
2036-11-13 11:00 | 10490.3 | 3.5378 | 84.8836 | 64.1561 | 3074.4034
2036-11-14 12:00 | 9799.95 | 3.2579 | 85.403 | 64.1561 | 2872.0818
2036-11-15 13:00 | 10477.4 | 3.3802 | 85.9055 | 64.1561 | 3070.6228
2036-11-16 14:00 | 12272.9 | 4.0324 | 85.8857 | 64.1561 | 3596.8319
2036-11-17 15:00 | 14473.3 | 4.6125 | 86.5979 | 64.1561 | 4241.7055
2036-11-18 16:00 | 14356 | 4.701 | 86.7165 | 64.1561 | 4207.3283
2036-11-19 17:00 | 13705.2 | 4.4291 | 87.1391 | 64.1561 | 4016.5976
2036-11-20 18:00 | 11710.2 | 3.746 | 87.4221 | 64.1561 | 3431.9208
2036-11-21 19:00 | 10610 | 3.2841 | 87.7835 | 64.1561 | 3109.4841
2036-11-22 20:00 | 8604.52 | 2.5871 | 88.0664 | 64.1561 | 2521.7359
2036-11-23 21:00 | 7586.03 | 2.274 | 87.8402 | 64.1561 | 2223.2459
2036-11-24 22:00 | 5685.12 | 1.6498 | 88.0133 | 64.1561 | 1666.1442
2036-11-25 23:00 | 4929.89 | 1.5062 | 86.9894 | 64.1561 | 1444.8081
2036-11-27 | 4222.77 | 1.3215 | 86.4175 | 64.1561 | 1237.5717
2036-11-28 01:00 | 3847.15 | 1.1855 | 86.3662 | 64.1561 | 1127.4884
2036-11-29 02:00 | 3733.3 | 1.1782 | 85.8534 | 64.1561 | 1094.1222
2036-11-30 03:00 | 3542.06 | 1.1265 | 85.5697 | 64.1561 | 1038.0753
2036-12-01 04:00 | 4019.19 | 1.2577 | 85.6093 | 64.1561 | 1177.9083
2036-12-02 05:00 | 5051.89 | 1.5946 | 85.4254 | 64.1561 | 1480.5628
2036-12-03 06:00 | 5273.88 | 1.665 | 85.4795 | 64.1561 | 1545.6217
2036-12-04 07:00 | 5454.62 | 1.7612 | 85.2323 | 64.1561 | 1598.5913
2036-12-05 08:00 | 5834.33 | 1.8469 | 85.5022 | 64.1561 | 1709.8733
2036-12-06 09:00 | 6983.17 | 2.3782 | 84.6867 | 64.1561 | 2046.5651
2036-12-07 10:00 | 7218.51 | 2.3624 | 85.3146 | 64.1561 | 2115.5364
2036-12-08 11:00 | 9955.79 | 3.5025 | 84.5716 | 64.1561 | 2917.754
2036-12-09 12:00 | 10291 | 3.4472 | 85.4959 | 64.1561 | 3015.9944
2036-12-10 13:00 | 10782.5 | 3.4962 | 86.1425 | 64.1561 | 3160.0388
2036-12-11 14:00 | 11857.1 | 3.9138 | 86.1313 | 64.1561 | 3474.973
2036-12-12 15:00 | 13241.6 | 4.5269 | 85.9783 | 64.1561 | 3880.7299
2036-12-13 16:00 | 14370.4 | 4.6586 | 86.9352 | 64.1561 | 4211.5485
2036-12-14 17:00 | 13965.3 | 4.5137 | 87.2836 | 64.1561 | 4092.8254
2036-12-15 18:00 | 12232.2 | 3.8565 | 87.7747 | 64.1561 | 3584.9039
2036-12-16 19:00 | 10835.2 | 3.3644 | 87.9411 | 64.1561 | 3175.4837
2036-12-17 20:00 | 8854.98 | 2.7399 | 87.8889 | 64.1561 | 2595.1385
2036-12-18 21:00 | 7933.24 | 2.4877 | 87.4836 | 64.1561 | 2325.0031
2036-12-19 22:00 | 6242.46 | 1.9144 | 87.5477 | 64.1561 | 1829.4844
2036-12-20 23:00 | 5257.07 | 1.5813 | 87.4812 | 64.1561 | 1540.6951
2036-12-22 | 4336.26 | 1.3066 | 87.1703 | 64.1561 | 1270.8324
2036-12-23 01:00 | 3672.87 | 1.1342 | 86.5819 | 64.1561 | 1076.4119
2036-12-24 02:00 | 3388.42 | 1.0622 | 86.1433 | 64.1561 | 993.0479
2036-12-25 03:00 | 3637.87 | 1.1206 | 86.1425 | 64.1561 | 1066.1545
2036-12-26 04:00 | 3704.56 | 1.1797 | 85.5854 | 64.1561 | 1085.6994
2036-12-27 05:00 | 4846.02 | 1.5111 | 85.7228 | 64.1561 | 1420.2283
2036-12-28 06:00 | 5008.38 | 1.5928 | 85.5081 | 64.1561 | 1467.8113
2036-12-29 07:00 | 6139.82 | 1.987 | 85.3067 | 64.1561 | 1799.4036
2036-12-30 08:00 | 6752.81 | 2.1991 | 85.3525 | 64.1561 | 1979.0533
2036-12-31 09:00 | 8621.07 | 3.01 | 84.6671 | 64.1561 | 2526.5862
2037-01-01 10:00 | 10741.9 | 3.6534 | 85.2458 | 64.1561 | 3148.1401
2037-01-02 11:00 | 12817.8 | 4.1746 | 86.1402 | 64.1561 | 3756.5264
2037-01-03 12:00 | 14019.8 | 4.6247 | 86.4626 | 64.1561 | 4108.7978
2037-01-04 13:00 | 14544.4 | 4.7755 | 86.9529 | 64.1561 | 4262.5429
2037-01-05 14:00 | 14706.5 | 4.8345 | 87.298 | 64.1561 | 4310.0497
2037-01-06 15:00 | 15590.7 | 5.1104 | 87.597 | 64.1561 | 4569.1831
2037-01-07 16:00 | 16011.5 | 5.2065 | 87.9864 | 64.1561 | 4692.5074
2037-01-08 17:00 | 15788.7 | 4.9641 | 88.6485 | 64.1561 | 4627.2112
2037-01-09 18:00 | 13357.1 | 4.2282 | 88.742 | 64.1561 | 3914.5796
2037-01-10 19:00 | 11895.7 | 3.7161 | 88.7946 | 64.1561 | 3486.2855
2037-01-11 20:00 | 9574.24 | 2.9525 | 88.8106 | 64.1561 | 2805.9328
2037-01-12 21:00 | 8990.51 | 2.7026 | 88.8354 | 64.1561 | 2634.8584
2037-01-13 22:00 | 6676.05 | 2.0031 | 88.6338 | 64.1561 | 1956.5571
2037-01-14 23:00 | 5941.06 | 1.7646 | 88.3616 | 64.1561 | 1741.1528
2037-01-16 | 5265.87 | 1.6053 | 87.7028 | 64.1561 | 1543.2742
2037-01-17 01:00 | 4793.46 | 1.4645 | 87.4051 | 64.1561 | 1404.8245
2037-01-18 02:00 | 4452.57 | 1.4322 | 86.5375 | 64.1561 | 1304.9195
2037-01-19 03:00 | 4554.69 | 1.4407 | 86.521 | 64.1561 | 1334.8479
2037-01-20 04:00 | 4740.85 | 1.4829 | 86.5157 | 64.1561 | 1389.406
2037-01-21 05:00 | 5505.54 | 1.7954 | 85.8939 | 64.1561 | 1613.5145
2037-01-22 06:00 | 5497.96 | 1.8426 | 85.5714 | 64.1561 | 1611.293
2037-01-23 07:00 | 6548.14 | 2.1228 | 85.9358 | 64.1561 | 1919.0704
2037-01-24 08:00 | 7350.69 | 2.3399 | 86.251 | 64.1561 | 2154.2746
2037-01-25 09:00 | 9088.62 | 3.1257 | 85.4599 | 64.1561 | 2663.6116
2037-01-26 10:00 | 11278.9 | 3.8239 | 85.8812 | 64.1561 | 3305.5193
2037-01-27 11:00 | 13071.5 | 4.4443 | 86.2232 | 64.1561 | 3830.8785
2037-01-28 12:00 | 13915.9 | 4.661 | 86.8225 | 64.1561 | 4078.3477
2037-01-29 13:00 | 14804.4 | 4.7612 | 87.6589 | 64.1561 | 4338.7413
2037-01-30 14:00 | 15294.1 | 4.9617 | 87.8999 | 64.1561 | 4482.2583
2037-01-31 15:00 | 17217.2 | 5.4762 | 88.4275 | 64.1561 | 5045.8632
2037-02-01 16:00 | 16667.4 | 5.3946 | 88.6283 | 64.1561 | 4884.7328
2037-02-02 17:00 | 16061.4 | 5.1321 | 88.9923 | 64.1561 | 4707.1317
2037-02-03 18:00 | 13842.7 | 4.3485 | 89.3202 | 64.1561 | 4056.8949
2037-02-04 19:00 | 12305.9 | 3.8414 | 89.2944 | 64.1561 | 3606.5033
2037-02-05 20:00 | 9793.36 | 2.9953 | 89.4007 | 64.1561 | 2870.1505
2037-02-06 21:00 | 8209.5 | 2.5994 | 88.615 | 64.1561 | 2405.9669
2037-02-07 22:00 | 6097.88 | 1.8513 | 88.7867 | 64.1561 | 1787.1122
2037-02-08 23:00 | 4516.84 | 1.389 | 88.172 | 64.1561 | 1323.7551
2037-02-10 | 3769.68 | 1.1863 | 87.4367 | 64.1561 | 1104.7842
2037-02-11 01:00 | 3278.66 | 1 | 88.0919 | 64.1561 | 960.8804
2037-02-12 02:00 | 3113.84 | 1 | 89.1078 | 64.1561 | 912.5764
2037-02-13 03:00 | 3118.65 | 1 | 91.2211 | 64.1561 | 913.9861
2037-02-14 04:00 | 3143.75 | 1 | 73.1278 | 64.1561 | 921.3422
2037-02-15 05:00 | 3106.8 | 1 | 72.9774 | 64.1561 | 910.5132
2037-02-16 06:00 | 3342.85 | 1.057 | 85.9634 | 64.1561 | 979.6926
2037-02-17 07:00 | 5360.02 | 1.693 | 85.8516 | 64.1561 | 1570.8668
2037-02-18 08:00 | 5873.77 | 1.859 | 85.9735 | 64.1561 | 1721.4321
2037-02-19 09:00 | 7572.26 | 2.5293 | 85.4234 | 64.1561 | 2219.2103
2037-02-20 10:00 | 10067.7 | 3.3456 | 85.6927 | 64.1561 | 2950.5516
2037-02-21 11:00 | 11313.5 | 3.7477 | 86.1307 | 64.1561 | 3315.6596
2037-02-22 12:00 | 11683.7 | 3.8787 | 86.4791 | 64.1561 | 3424.1545
2037-02-23 13:00 | 11818.2 | 3.8654 | 86.9013 | 64.1561 | 3463.5725
2037-02-24 14:00 | 12635.8 | 4.1694 | 86.9887 | 64.1561 | 3703.1874
2037-02-25 15:00 | 13330.2 | 4.2859 | 87.5212 | 64.1561 | 3906.696
2037-02-26 16:00 | 15462.8 | 5.0542 | 87.5294 | 64.1561 | 4531.6993
2037-02-27 17:00 | 13966 | 4.4973 | 88.0952 | 64.1561 | 4093.0306
2037-02-28 18:00 | 12528 | 3.9302 | 88.521 | 64.1561 | 3671.5944
2037-03-01 19:00 | 10987.5 | 3.4438 | 88.4747 | 64.1561 | 3220.1184
2037-03-02 20:00 | 9509.37 | 3.0043 | 88.2558 | 64.1561 | 2786.9212
2037-03-03 21:00 | 8592.84 | 2.6865 | 88.1917 | 64.1561 | 2518.3128
2037-03-04 22:00 | 7796.47 | 2.4275 | 88.0141 | 64.1561 | 2284.9198
2037-03-05 23:00 | 4970.9 | 1.4342 | 88.8058 | 64.1561 | 1456.827
2037-03-07 | 4018.96 | 1.2359 | 87.5335 | 64.1561 | 1177.8409
2037-03-08 01:00 | 3340.08 | 1.0488 | 86.9182 | 64.1561 | 978.8808
2037-03-09 02:00 | 3105.45 | 1 | 87.4443 | 64.1561 | 910.1176
2037-03-10 03:00 | 3147.94 | 1 | 89.7005 | 64.1561 | 922.5701
2037-03-11 04:00 | 3139.19 | 1 | 91.3401 | 64.1561 | 920.0058
2037-03-12 05:00 | 3103.59 | 1 | 90.8461 | 64.1561 | 909.5724
2037-03-13 06:00 | 3998.9 | 1.2749 | 85.713 | 64.1561 | 1171.9619
2037-03-14 07:00 | 5823.45 | 1.904 | 85.4096 | 64.1561 | 1706.6847
2037-03-15 08:00 | 6975.6 | 2.1589 | 86.2597 | 64.1561 | 2044.3466
2037-03-16 09:00 | 8555.66 | 2.8553 | 85.5283 | 64.1561 | 2507.4164
2037-03-17 10:00 | 10688.5 | 3.563 | 85.7909 | 64.1561 | 3132.4901
2037-03-18 11:00 | 11785.3 | 3.9628 | 86.0875 | 64.1561 | 3453.9305
2037-03-19 12:00 | 12432.5 | 4.1506 | 86.5355 | 64.1561 | 3643.6061
2037-03-20 13:00 | 12210.4 | 3.809 | 87.6526 | 64.1561 | 3578.515
2037-03-21 14:00 | 11268.2 | 3.5591 | 87.6797 | 64.1561 | 3302.3834
2037-03-22 15:00 | 10935.1 | 3.5919 | 87.2303 | 64.1561 | 3204.7615
2037-03-23 16:00 | 13152.1 | 4.4707 | 86.8101 | 64.1561 | 3854.5
2037-03-24 17:00 | 12259.5 | 3.8833 | 87.9245 | 64.1561 | 3592.9048
2037-03-25 18:00 | 10674.4 | 3.3251 | 88.204 | 64.1561 | 3128.3578
2037-03-26 19:00 | 9274.99 | 2.84 | 88.2924 | 64.1561 | 2718.2312
2037-03-27 20:00 | 8325.12 | 2.6088 | 87.8357 | 64.1561 | 2439.8518
2037-03-28 21:00 | 7900.83 | 2.3495 | 88.3452 | 64.1561 | 2315.5047
2037-03-29 22:00 | 7135.07 | 2.1901 | 87.7602 | 64.1561 | 2091.0826
2037-03-30 23:00 | 4569.92 | 1.3592 | 87.9869 | 64.1561 | 1339.3113
2037-04-01 | 3747.87 | 1.1505 | 87.1781 | 64.1561 | 1098.3923
2037-04-02 01:00 | 3367.37 | 1.0727 | 86.3996 | 64.1561 | 986.8787
2037-04-03 02:00 | 3183.65 | 1 | 86.949 | 64.1561 | 933.0357
2037-04-04 03:00 | 3490.67 | 1.0866 | 86.2779 | 64.1561 | 1023.0144
2037-04-05 04:00 | 3716.14 | 1.1989 | 85.6971 | 64.1561 | 1089.0931
2037-04-06 05:00 | 4734.72 | 1.5095 | 85.7712 | 64.1561 | 1387.6095
2037-04-07 06:00 | 5080.26 | 1.6026 | 85.9549 | 64.1561 | 1488.8772
2037-04-08 07:00 | 6021.21 | 1.986 | 85.456 | 64.1561 | 1764.6425
2037-04-09 08:00 | 5511.24 | 1.7777 | 85.8359 | 64.1561 | 1615.185
2037-04-10 09:00 | 6679.52 | 2.2614 | 85.2412 | 64.1561 | 1957.5741
2037-04-11 10:00 | 8335.94 | 2.7736 | 85.5354 | 64.1561 | 2443.0229
2037-04-12 11:00 | 9408.56 | 3.2227 | 85.4325 | 64.1561 | 2757.3767
2037-04-13 12:00 | 9265.71 | 3.1089 | 85.9133 | 64.1561 | 2715.5115
2037-04-14 13:00 | 10534.7 | 3.3447 | 86.6834 | 64.1561 | 3087.4158
2037-04-15 14:00 | 11101.8 | 3.6416 | 86.5317 | 64.1561 | 3253.6164
2037-04-16 15:00 | 13235.9 | 4.3104 | 86.8407 | 64.1561 | 3879.0594
2037-04-17 16:00 | 13505.3 | 4.4183 | 87.1402 | 64.1561 | 3958.0127
2037-04-18 17:00 | 13307.5 | 4.1876 | 87.8623 | 64.1561 | 3900.0433
2037-04-19 18:00 | 11562.8 | 3.6736 | 87.9146 | 64.1561 | 3388.7222
2037-04-20 19:00 | 10328.9 | 3.1985 | 88.1869 | 64.1561 | 3027.1018
2037-04-21 20:00 | 7901 | 2.4042 | 88.3193 | 64.1561 | 2315.5545
2037-04-22 21:00 | 6905.75 | 2.0891 | 88.0862 | 64.1561 | 2023.8755
2037-04-23 22:00 | 5221.15 | 1.5277 | 88.2423 | 64.1561 | 1530.168
2037-04-24 23:00 | 4208.37 | 1.331 | 86.8997 | 64.1561 | 1233.3515
2037-04-26 | 3471.16 | 1.0723 | 86.8873 | 64.1561 | 1017.2966
2037-04-27 01:00 | 3127.06 | 1 | 86.9683 | 64.1561 | 916.4508
2037-04-28 02:00 | 3063.85 | 1 | 88.5018 | 64.1561 | 897.9258
2037-04-29 03:00 | 3108.35 | 1 | 87.5981 | 64.1561 | 910.9675
2037-04-30 04:00 | 3353.86 | 1.0564 | 85.8116 | 64.1561 | 982.9193
2037-05-01 05:00 | 3778.48 | 1.2135 | 85.4758 | 64.1561 | 1107.3632
2037-05-02 06:00 | 4035.64 | 1.2869 | 85.5252 | 64.1561 | 1182.7293
2037-05-03 07:00 | 5187.28 | 1.6005 | 85.9035 | 64.1561 | 1520.2417
2037-05-04 08:00 | 5827.15 | 1.8614 | 85.5709 | 64.1561 | 1707.7691
2037-05-05 09:00 | 8002.57 | 2.7151 | 84.9592 | 64.1561 | 2345.3218
2037-05-06 10:00 | 10345.9 | 3.4305 | 85.5088 | 64.1561 | 3032.084
2037-05-07 11:00 | 11853.2 | 4.0324 | 85.629 | 64.1561 | 3473.83
2037-05-08 12:00 | 12682.1 | 4.1342 | 86.5481 | 64.1561 | 3716.7566
2037-05-09 13:00 | 13337.6 | 4.4192 | 86.7026 | 64.1561 | 3908.8647
2037-05-10 14:00 | 14682.6 | 4.7564 | 87.2972 | 64.1561 | 4303.0453
2037-05-11 15:00 | 16050.3 | 5.2134 | 87.6334 | 64.1561 | 4703.8786
2037-05-12 16:00 | 15664.5 | 5.1051 | 87.9867 | 64.1561 | 4590.8118
2037-05-13 17:00 | 14386.6 | 4.7319 | 88.0974 | 64.1561 | 4216.2963
2037-05-14 18:00 | 12307 | 3.9305 | 88.5066 | 64.1561 | 3606.8257
2037-05-15 19:00 | 10624.6 | 3.2917 | 88.7609 | 64.1561 | 3113.7629
2037-05-16 20:00 | 8288.11 | 2.4682 | 89.078 | 64.1561 | 2429.0053
2037-05-17 21:00 | 7229.89 | 2.2007 | 88.4346 | 64.1561 | 2118.8716
2037-05-18 22:00 | 5141.72 | 1.5241 | 88.4612 | 64.1561 | 1506.8894
2037-05-19 23:00 | 4193.06 | 1.2544 | 87.9221 | 64.1561 | 1228.8646
2037-05-21 | 3396.85 | 1.0921 | 86.6561 | 64.1561 | 995.5185
2037-05-22 01:00 | 3143.15 | 1 | 89.1694 | 64.1561 | 921.1663
2037-05-23 02:00 | 3115.8 | 1 | 89.324 | 64.1561 | 913.1508
2037-05-24 03:00 | 3175.15 | 1 | 87.3462 | 64.1561 | 930.5446
2037-05-25 04:00 | 3222.74 | 1.0179 | 85.9405 | 64.1561 | 944.4919
2037-05-26 05:00 | 4195.11 | 1.3215 | 85.8473 | 64.1561 | 1229.4654
2037-05-27 06:01 | 3892.86 | 1.2913 | 85.2367 | 64.1561 | 1140.8846
2037-05-28 07:01 | 5159.35 | 1.54 | 86.4856 | 64.1561 | 1512.0562
2037-05-29 08:01 | 5263.14 | 1.7316 | 85.3601 | 64.1561 | 1542.4741
2037-05-30 09:01 | 7303.61 | 2.5548 | 84.6932 | 64.1561 | 2140.4768
2037-05-31 10:01 | 9621.83 | 3.3407 | 85.0047 | 64.1561 | 2819.88
2037-06-01 11:01 | 11556.7 | 3.8837 | 85.7482 | 64.1561 | 3386.9344
2037-06-02 12:01 | 11909.3 | 3.8615 | 86.6074 | 64.1561 | 3490.2713
2037-06-03 13:01 | 12813 | 4.1133 | 87.0155 | 64.1561 | 3755.1196
2037-06-04 14:01 | 13319.9 | 4.3285 | 87.1761 | 64.1561 | 3903.6773
2037-06-05 15:01 | 14890.4 | 4.8756 | 87.342 | 64.1561 | 4363.9455
2037-06-06 16:01 | 14703.1 | 4.7712 | 87.7946 | 64.1561 | 4309.0532
2037-06-07 17:01 | 14016.5 | 4.4285 | 88.3193 | 64.1561 | 4107.8307
2037-06-08 18:01 | 11728.6 | 3.6859 | 88.4879 | 64.1561 | 3437.3134
2037-06-09 19:01 | 10035.2 | 3.1688 | 88.2927 | 64.1561 | 2941.0268
2037-06-10 20:01 | 7681.69 | 2.3527 | 88.4875 | 64.1561 | 2251.2811
2037-06-11 21:01 | 6777.53 | 2.0509 | 88.286 | 64.1561 | 1986.298
2037-06-12 22:01 | 4709.85 | 1.4115 | 88.1148 | 64.1561 | 1380.3208
2037-06-13 23:01 | 3484.75 | 1.0983 | 87.0566 | 64.1561 | 1021.2794
2037-06-15 00:01 | 3160.88 | 1 | 88.7165 | 64.1561 | 926.3625
2037-06-16 01:01 | 3119.39 | 1 | 93.9895 | 64.1561 | 914.203
2037-06-17 02:01 | 3140.58 | 1 | 73.0403 | 64.1561 | 920.4131
2037-06-18 03:01 | 3048.95 | 1 | 72.8873 | 64.1561 | 893.559
2037-06-19 04:01 | 3057.5 | 1 | 72.7341 | 64.1561 | 896.0648
2037-06-20 05:01 | 3101.29 | 1 | 91.0334 | 64.1561 | 908.8984
2037-06-21 06:01 | 3203.06 | 1 | 90.4863 | 64.1561 | 938.7242
2037-06-22 07:01 | 3142.56 | 1 | 87.379 | 64.1561 | 920.9934
2037-06-23 08:01 | 2797.25 | 1 | 85.5403 | 64.1561 | 819.7931
2037-06-24 09:01 | 4270.35 | 1.4877 | 84.2035 | 64.1561 | 1251.516
2037-06-25 10:01 | 6253.6 | 2.1062 | 84.6555 | 64.1561 | 1832.7492
2037-06-26 11:01 | 6733.43 | 2.2171 | 85.1487 | 64.1561 | 1973.3735
2037-06-27 12:01 | 8429 | 2.7565 | 85.3689 | 64.1561 | 2470.296
2037-06-28 13:01 | 9238.1 | 2.9989 | 85.7085 | 64.1561 | 2707.4199
2037-06-29 14:01 | 10291.9 | 3.333 | 85.9868 | 64.1561 | 3016.2581
2037-06-30 15:01 | 11353.7 | 3.687 | 86.1973 | 64.1561 | 3327.441
2037-07-01 16:01 | 11172.7 | 3.6052 | 86.5296 | 64.1561 | 3274.3951
2037-07-02 17:01 | 10265.5 | 3.294 | 86.7517 | 64.1561 | 3008.5211
2037-07-03 18:01 | 8183.75 | 2.5465 | 87.1509 | 64.1561 | 2398.4204
2037-07-04 19:01 | 6577.06 | 2.0235 | 87.1226 | 64.1561 | 1927.546
2037-07-05 20:01 | 4134.14 | 1.2627 | 86.9921 | 64.1561 | 1211.5968
2037-07-06 21:01 | 3195.42 | 1 | 88.6048 | 64.1561 | 936.4852
2037-07-07 22:01 | 2959.97 | 1 | 72.7532 | 64.1561 | 867.4816
2037-07-08 23:01 | 117.582 | 1 | 73.2077 | 64.1561 | 34.4599
2037-07-10 00:01 | -308.713 | 1.2733 | 71.7992 | 64.1561 | -90.4748
2037-07-11 01:01 | -579.12 | 1.8835 | 71.1753 | 64.1561 | -169.7233
2037-07-12 02:01 | -736.313 | 2.2296 | 70.8246 | 64.1561 | -215.792
2037-07-13 03:01 | -840.637 | 2.4666 | 70.5364 | 64.1561 | -246.3664
2037-07-14 04:01 | -880.897 | 2.5542 | 70.2823 | 64.1561 | -258.1654
2037-07-15 05:01 | -560.598 | 1.7552 | 70.2059 | 64.1561 | -164.2951
2037-07-16 06:01 | -556.615 | 1.8114 | 70.1467 | 64.1561 | -163.1278
2037-07-17 07:01 | 0 | 0 | 71.2456 | 64.1561 | 0
2037-07-18 08:01 | 2493.91 | 1 | 70.6266 | 64.1561 | 730.8929
2037-07-19 09:01 | 3050.87 | 1.0365 | 82.9791 | 64.1561 | 894.1217
2037-07-20 10:01 | 5739.76 | 1.9407 | 83.1471 | 64.1561 | 1682.1576
2037-07-21 11:01 | 7642.58 | 2.6033 | 83.4196 | 64.1561 | 2239.8191
2037-07-22 12:01 | 9042.78 | 3.0232 | 84.0631 | 64.1561 | 2650.1772
2037-07-23 13:01 | 9772.88 | 3.2226 | 84.6301 | 64.1561 | 2864.1484
2037-07-24 14:01 | 10563 | 3.4232 | 85.1516 | 64.1561 | 3095.7097
2037-07-25 15:01 | 11890.3 | 3.8558 | 85.4494 | 64.1561 | 3484.7029
2037-07-26 16:01 | 11777.8 | 3.8171 | 85.8088 | 64.1561 | 3451.7324
2037-07-27 17:01 | 11073.7 | 3.5353 | 86.2146 | 64.1561 | 3245.3811
2037-07-28 18:01 | 8867.17 | 2.8009 | 86.453 | 64.1561 | 2598.711
2037-07-29 19:01 | 7541.71 | 2.3724 | 86.3899 | 64.1561 | 2210.257
2037-07-30 20:01 | 5153.73 | 1.5803 | 86.5583 | 64.1561 | 1510.4092
2037-07-31 21:01 | 3979.93 | 1.2392 | 86.0403 | 64.1561 | 1166.4023
2037-08-01 22:01 | 3088.64 | 1 | 72.4318 | 64.1561 | 905.191
2037-08-02 23:01 | 2293.77 | 1 | 72.3385 | 64.1561 | 672.2376
2037-08-04 00:01 | -84.4834 | 0.76931 | 72.1874 | 64.1561 | -24.7596
2037-08-05 01:01 | -368.794 | 1.4096 | 71.1362 | 64.1561 | -108.0829
2037-08-06 02:01 | -621.633 | 1.9888 | 70.6224 | 64.1561 | -182.1826
2037-08-07 03:01 | -770.036 | 2.3177 | 70.294 | 64.1561 | -225.6753
2037-08-08 04:01 | -908.778 | 2.6431 | 70.0183 | 64.1561 | -266.3365
2037-08-09 05:01 | -1023.21 | 2.9095 | 69.7745 | 64.1561 | -299.8732
2037-08-10 06:01 | -296.509 | 1.0755 | 69.9205 | 64.1561 | -86.8982
2037-08-11 07:01 | 2315.43 | 1 | 70.4034 | 64.1561 | 678.5855
2037-08-12 08:01 | 2876.36 | 1 | 70.5064 | 64.1561 | 842.9779
2037-08-13 09:01 | 4027.22 | 1.3062 | 83.4236 | 64.1561 | 1180.2617
2037-08-14 10:01 | 6560.15 | 2.1732 | 83.3174 | 64.1561 | 1922.5902
2037-08-15 11:01 | 8516.88 | 2.8185 | 83.7169 | 64.1561 | 2496.0511
2037-08-16 12:01 | 10147.2 | 3.3324 | 84.262 | 64.1561 | 2973.8508
2037-08-17 13:01 | 11031.9 | 3.5412 | 84.9594 | 64.1561 | 3233.1307
2037-08-18 14:01 | 11979.2 | 3.7978 | 85.4849 | 64.1561 | 3510.757
2037-08-19 15:01 | 12042.3 | 3.8672 | 85.6898 | 64.1561 | 3529.2497
2037-08-20 16:01 | 13859.7 | 4.4603 | 85.9128 | 64.1561 | 4061.8771
2037-08-21 17:01 | 12385.4 | 3.9369 | 86.4705 | 64.1561 | 3629.8024
2037-08-22 18:01 | 10609.8 | 3.3216 | 86.7924 | 64.1561 | 3109.4254
2037-08-23 19:01 | 9181.41 | 2.8576 | 86.7867 | 64.1561 | 2690.8057
2037-08-24 20:01 | 8171.12 | 2.5596 | 86.5886 | 64.1561 | 2394.7189
2037-08-25 21:01 | 7189 | 2.2562 | 86.4496 | 64.1561 | 2106.8879
2037-08-26 22:01 | 6682.33 | 2.1153 | 86.154 | 64.1561 | 1958.3976
2037-08-27 23:01 | 3848.47 | 1.1769 | 86.4457 | 64.1561 | 1127.8752
2037-08-29 00:01 | 3238.56 | 1.015 | 85.7477 | 64.1561 | 949.1282
2037-08-30 01:01 | 3183.52 | 1 | 88.1966 | 64.1561 | 932.9976
2037-08-31 02:01 | 3214.69 | 1 | 89.6373 | 64.1561 | 942.1326
2037-09-01 03:01 | 3196.51 | 1 | 91.5163 | 64.1561 | 936.8046
2037-09-02 04:01 | 3312.49 | 1 | 93.514 | 64.1561 | 970.795
2037-09-03 05:01 | 3245.31 | 1 | 90.9165 | 64.1561 | 951.1065
2037-09-04 06:01 | 4099.57 | 1.2415 | 85.3344 | 64.1561 | 1201.4654
2037-09-05 07:01 | 5007.2 | 1.5217 | 85.3434 | 64.1561 | 1467.4655
2037-09-06 08:01 | 3497.56 | 1.0803 | 85.2541 | 64.1561 | 1025.0337
2037-09-07 09:01 | 3594.94 | 1.1088 | 85.1438 | 64.1561 | 1053.5729
2037-09-08 10:01 | 4743.1 | 1.4748 | 84.9468 | 64.1561 | 1390.0654
2037-09-09 11:01 | 5976.76 | 1.9262 | 84.5895 | 64.1561 | 1751.6154
2037-09-10 12:01 | 7249.26 | 2.4315 | 84.2604 | 64.1561 | 2124.5484
2037-09-11 13:01 | 8697.88 | 2.951 | 84.3029 | 64.1561 | 2549.097
2037-09-12 14:01 | 7668.88 | 2.6778 | 84.2485 | 64.1561 | 2247.5269
2037-09-13 15:01 | 8210.47 | 2.4348 | 86.2721 | 64.1561 | 2406.2512
2037-09-14 16:01 | 10840.5 | 3.7857 | 84.3487 | 64.1561 | 3177.0369
2037-09-15 17:01 | 10179.8 | 3.2482 | 85.7766 | 64.1561 | 2983.4049
2037-09-16 18:01 | 8942.83 | 2.8588 | 85.8919 | 64.1561 | 2620.8848
2037-09-17 19:01 | 8219.68 | 2.521 | 86.34 | 64.1561 | 2408.9504
2037-09-18 20:01 | 7791.47 | 2.4321 | 86.0912 | 64.1561 | 2283.4544
2037-09-19 21:01 | 7407.14 | 2.3333 | 85.9714 | 64.1561 | 2170.8184
2037-09-20 22:01 | 7310.71 | 2.2162 | 86.3944 | 64.1561 | 2142.5576
2037-09-21 23:01 | 4986.95 | 1.4392 | 87.0259 | 64.1561 | 1461.5308
2037-09-23 00:01 | 4157.58 | 1.2758 | 85.9696 | 64.1561 | 1218.4664
2037-09-24 01:01 | 3503.88 | 1.1381 | 85.0371 | 64.1561 | 1026.8859
2037-09-25 02:01 | 3407.16 | 1.0986 | 84.9448 | 64.1561 | 998.54
2037-09-26 03:01 | 3719.51 | 1.1953 | 84.8486 | 64.1561 | 1090.0808
2037-09-27 04:01 | 4231.96 | 1.2952 | 85.3548 | 64.1561 | 1240.265
2037-09-28 05:01 | 5289.82 | 1.6768 | 84.9062 | 64.1561 | 1550.2932
2037-09-29 06:01 | 5298.4 | 1.7489 | 84.5233 | 64.1561 | 1552.8078
2037-09-30 07:01 | 5648.86 | 1.8212 | 84.8538 | 64.1561 | 1655.5174
2037-10-01 08:01 | 5224.89 | 1.591 | 85.6358 | 64.1561 | 1531.2641
2037-10-02 09:01 | 5816.3 | 1.9567 | 84.4108 | 64.1561 | 1704.5893
2037-10-03 10:01 | 6520.77 | 2.2191 | 84.3265 | 64.1561 | 1911.049
2037-10-04 11:01 | 8695.68 | 3.0579 | 84.0515 | 64.1561 | 2548.4522
2037-10-05 12:01 | 9941.06 | 3.3869 | 84.7004 | 64.1561 | 2913.4371
2037-10-06 13:01 | 10600.7 | 3.5164 | 85.3108 | 64.1561 | 3106.7585
2037-10-07 14:01 | 11317.1 | 3.7128 | 85.7062 | 64.1561 | 3316.7146
2037-10-08 15:01 | 12691.9 | 4.1537 | 85.9941 | 64.1561 | 3719.6287
2037-10-09 16:01 | 12242.5 | 4.0457 | 86.2105 | 64.1561 | 3587.9226
2037-10-10 17:01 | 11644.2 | 3.8071 | 86.4903 | 64.1561 | 3412.5782
2037-10-11 18:01 | 9369.96 | 3.0116 | 86.7577 | 64.1561 | 2746.0642
2037-10-12 19:01 | 7762.63 | 2.4705 | 86.7141 | 64.1561 | 2275.0023
2037-10-13 20:01 | 5442.61 | 1.6502 | 87.1016 | 64.1561 | 1595.0715
2037-10-14 21:01 | 4148.58 | 1.2731 | 86.5735 | 64.1561 | 1215.8288
2037-10-15 22:01 | 3093.88 | 1 | 72.7417 | 64.1561 | 906.7267
2037-10-16 23:01 | 2990.96 | 1 | 72.4285 | 64.1561 | 876.5638
2037-10-18 00:01 | 0 | 0 | 72.9151 | 64.1561 | 0
2037-10-19 01:01 | -103.963 | 0.81462 | 71.9086 | 64.1561 | -30.4685
2037-10-20 02:01 | -309.043 | 1.2615 | 71.1132 | 64.1561 | -90.5716
2037-10-21 03:01 | -251.865 | 1.0898 | 70.909 | 64.1561 | -73.8143
2037-10-22 04:01 | -212.061 | 1.0072 | 70.7719 | 64.1561 | -62.1489
2037-10-23 05:01 | 905.11 | 1 | 71.1724 | 64.1561 | 265.2616
2037-10-24 06:01 | 1776.23 | 1 | 70.956 | 64.1561 | 520.5616
2037-10-25 07:01 | 2406.98 | 1 | 70.8542 | 64.1561 | 705.4162
2037-10-26 08:01 | 2974.65 | 1 | 70.7949 | 64.1561 | 871.7839
2037-10-27 09:01 | 4291.54 | 1.4093 | 83.5185 | 64.1561 | 1257.7262
2037-10-28 10:01 | 6958.99 | 2.3763 | 83.2261 | 64.1561 | 2039.4786
2037-10-29 11:01 | 9092.49 | 3.1135 | 83.5737 | 64.1561 | 2664.7458
2037-10-30 12:01 | 10326.3 | 3.3593 | 84.6353 | 64.1561 | 3026.3398
2037-10-31 13:01 | 10445.1 | 3.3447 | 85.2337 | 64.1561 | 3061.1566
2037-11-01 14:01 | 10650.6 | 3.4991 | 85.2146 | 64.1561 | 3121.3827
2037-11-02 15:01 | 12337.1 | 4.0186 | 85.5497 | 64.1561 | 3615.6471
2037-11-03 16:01 | 11816.7 | 3.8422 | 85.9319 | 64.1561 | 3463.1329
2037-11-04 17:01 | 10860.7 | 3.4711 | 86.3126 | 64.1561 | 3182.957
2037-11-05 18:01 | 8378.85 | 2.6494 | 86.4738 | 64.1561 | 2455.5985
2037-11-06 19:01 | 6730.53 | 2.0939 | 86.4852 | 64.1561 | 1972.5236
2037-11-07 20:01 | 4332.8 | 1.3258 | 86.4703 | 64.1561 | 1269.8183
2037-11-08 21:01 | 3124.88 | 1 | 86.5855 | 64.1561 | 915.8119
2037-11-09 22:01 | 3005.23 | 1 | 72.221 | 64.1561 | 880.746
2037-11-10 23:01 | 2947.18 | 1 | 71.9829 | 64.1561 | 863.7332
2037-11-12 00:01 | 94.4339 | 1 | 72.4976 | 64.1561 | 27.6758
2037-11-13 01:01 | -277.282 | 1.2035 | 71.164 | 64.1561 | -81.2633
2037-11-14 02:01 | -437.245 | 1.5513 | 70.6484 | 64.1561 | -128.1439
2037-11-15 03:01 | -523.254 | 1.7413 | 70.3487 | 64.1561 | -153.3506
2037-11-16 04:01 | -471.637 | 1.6022 | 70.1602 | 64.1561 | -138.2232
2037-11-17 05:01 | -135.199 | 0.78099 | 70.4392 | 64.1561 | -39.6229
2037-11-18 06:01 | 671.968 | 1 | 70.8725 | 64.1561 | 196.9344
2037-11-19 07:01 | 2283.81 | 1 | 70.4916 | 64.1561 | 669.3186
2037-11-20 08:01 | 2988.73 | 1 | 70.4867 | 64.1561 | 875.9103
2037-11-21 09:01 | 3513.72 | 1.1629 | 83.178 | 64.1561 | 1029.7697
2037-11-22 10:01 | 6593.56 | 2.1665 | 83.3376 | 64.1561 | 1932.3817
2037-11-23 11:01 | 8542.68 | 2.8153 | 83.6848 | 64.1561 | 2503.6124
2037-11-24 12:01 | 9636.72 | 3.1403 | 84.265 | 64.1561 | 2824.2438
2037-11-25 13:01 | 10290 | 3.3227 | 84.7356 | 64.1561 | 3015.7013
2037-11-26 14:01 | 10434.1 | 3.3632 | 85.0692 | 64.1561 | 3057.9329
2037-11-27 15:01 | 12251.5 | 3.99 | 85.1838 | 64.1561 | 3590.5602
2037-11-28 16:01 | 12311.8 | 3.917 | 85.8353 | 64.1561 | 3608.2324
2037-11-29 17:01 | 11411.8 | 3.6712 | 85.9547 | 64.1561 | 3344.4684
2037-11-30 18:01 | 9146.49 | 2.8709 | 86.3528 | 64.1561 | 2680.5716
2037-12-01 19:01 | 7676.99 | 2.37 | 86.4239 | 64.1561 | 2249.9037
2037-12-02 20:01 | 5428.74 | 1.6252 | 86.6602 | 64.1561 | 1591.0066
2037-12-03 21:01 | 4011.26 | 1.2524 | 85.8124 | 64.1561 | 1175.5843
2037-12-04 22:01 | 3097.69 | 1 | 72.2069 | 64.1561 | 907.8433
2037-12-05 23:01 | 3028.77 | 1 | 71.9063 | 64.1561 | 887.6449
2037-12-07 00:01 | 806.242 | 1 | 72.2474 | 64.1561 | 236.2862
2037-12-08 01:01 | 236.537 | 1 | 71.9931 | 64.1561 | 69.3222
2037-12-09 02:01 | -86.0207 | 0.75106 | 71.2954 | 64.1561 | -25.2102
2037-12-10 03:01 | 158.274 | 1 | 71.4649 | 64.1561 | 46.3855
2037-12-11 04:01 | 444.421 | 1 | 71.2309 | 64.1561 | 130.2469
2037-12-12 05:01 | 2180.2 | 1 | 70.6858 | 64.1561 | 638.9535
2037-12-13 06:01 | 2774.19 | 1 | 70.6477 | 64.1561 | 813.0348
2037-12-14 07:01 | 3124.06 | 1 | 70.6583 | 64.1561 | 915.5716
2037-12-15 08:01 | 3133.8 | 1 | 70.7364 | 64.1561 | 918.4261
2037-12-16 09:01 | 4605.6 | 1.4857 | 83.6681 | 64.1561 | 1349.7681
2037-12-17 10:01 | 7064.63 | 2.3706 | 83.3516 | 64.1561 | 2070.4387
2037-12-18 11:01 | 8690.79 | 2.8799 | 83.8394 | 64.1561 | 2547.0191
2037-12-19 12:01 | 9765.47 | 3.1831 | 84.4037 | 64.1561 | 2861.9767
2037-12-20 13:01 | 9356.95 | 3.016 | 84.8788 | 64.1561 | 2742.2513
2037-12-21 14:01 | 9465.47 | 3.04 | 85.1194 | 64.1561 | 2774.0554
2037-12-22 15:01 | 11698.1 | 3.8211 | 85.0618 | 64.1561 | 3428.3747
2037-12-23 16:01 | 11839.3 | 3.8168 | 85.5818 | 64.1561 | 3469.7563
2037-12-24 17:01 | 11198.5 | 3.5823 | 85.908 | 64.1561 | 3281.9564
2037-12-25 18:01 | 9085.62 | 2.8596 | 86.195 | 64.1561 | 2662.7324
2037-12-26 19:01 | 7757.76 | 2.4063 | 86.2654 | 64.1561 | 2273.575
2037-12-27 20:01 | 5593.17 | 1.677 | 86.5748 | 64.1561 | 1639.1963
2037-12-28 21:01 | 4007.29 | 1.2257 | 86.0221 | 64.1561 | 1174.4208
2037-12-29 22:01 | 3127.37 | 1 | 72.1433 | 64.1561 | 916.5417
2037-12-30 23:01 | 3088.28 | 1 | 71.8355 | 64.1561 | 905.0855
2038-01-01 00:01 | 3105.79 | 1 | 71.6416 | 64.1561 | 910.2172
2038-01-02 01:01 | 3077.82 | 1 | 71.5215 | 64.1561 | 902.02
2038-01-03 02:01 | 3074.38 | 1 | 71.4347 | 64.1561 | 901.0118
2038-01-04 03:01 | 3200.9 | 1 | 71.325 | 64.1561 | 938.0912
2038-01-05 04:01 | 3187.64 | 1 | 71.2772 | 64.1561 | 934.2051
2038-01-06 05:01 | 3167.77 | 1 | 71.2196 | 64.1561 | 928.3817
2038-01-07 06:01 | 3243.42 | 1 | 71.1486 | 64.1561 | 950.5526
2038-01-08 07:01 | 3231.08 | 1 | 89.9249 | 64.1561 | 946.9361
2038-01-09 08:01 | 3287.51 | 1 | 84.7533 | 64.1561 | 963.4741
2038-01-10 09:01 | 5351.22 | 1.7105 | 84.0697 | 64.1561 | 1568.2878
2038-01-11 10:01 | 7368.21 | 2.5347 | 83.4058 | 64.1561 | 2159.4092
2038-01-12 11:01 | 7265.75 | 2.3142 | 84.6379 | 64.1561 | 2129.3811
2038-01-13 12:01 | 7335.91 | 2.3334 | 84.7957 | 64.1561 | 2149.943
2038-01-14 13:01 | 8061.42 | 2.5222 | 85.0953 | 64.1561 | 2362.569
2038-01-15 14:01 | 7522.85 | 2.3394 | 85.3485 | 64.1561 | 2204.7297
2038-01-16 15:01 | 8080.43 | 2.664 | 84.653 | 64.1561 | 2368.1403
2038-01-17 16:01 | 8740.35 | 2.8397 | 84.876 | 64.1561 | 2561.5437
2038-01-18 17:01 | 8489.97 | 2.6939 | 85.2862 | 64.1561 | 2488.1646
2038-01-19 18:01 | 7262.2 | 2.2645 | 85.5702 | 64.1561 | 2128.3407
2038-01-20 19:01 | 6454.74 | 1.9763 | 85.7204 | 64.1561 | 1891.6976
2038-01-21 20:01 | 4517.79 | 1.3613 | 85.8532 | 64.1561 | 1324.0335
2038-01-22 21:01 | 3476.38 | 1.0744 | 85.2877 | 64.1561 | 1018.8264
2038-01-23 22:01 | 3107.16 | 1 | 71.6335 | 64.1561 | 910.6187
2038-01-24 23:01 | 2966.04 | 1 | 71.4729 | 64.1561 | 869.2605
2038-01-26 00:01 | 0 | 0 | 72.0468 | 64.1561 | 0
2038-01-27 01:01 | -61.2523 | 0.659 | 71.2368 | 64.1561 | -17.9513
2038-01-28 02:01 | -216.206 | 1.0525 | 70.5312 | 64.1561 | -63.3637
2038-01-29 03:01 | -342.164 | 1.3363 | 70.1515 | 64.1561 | -100.2784
2038-01-30 04:01 | -561.851 | 1.8641 | 69.7874 | 64.1561 | -164.6623
2038-01-31 05:01 | -723.223 | 2.2313 | 69.4962 | 64.1561 | -211.9557
2038-02-01 06:01 | -170.681 | 0.82131 | 69.8092 | 64.1561 | -50.0217
2038-02-02 07:01 | 2258.64 | 1 | 70.0263 | 64.1561 | 661.942
2038-02-03 08:01 | 2913.98 | 1 | 70.0856 | 64.1561 | 854.0032
2038-02-04 09:01 | 3131.48 | 1 | 87.3704 | 64.1561 | 917.7462
2038-02-05 10:01 | 5395.76 | 1.8155 | 82.6051 | 64.1561 | 1581.3412
2038-02-06 11:01 | 7149.07 | 2.5291 | 82.3317 | 64.1561 | 2095.1856
2038-02-07 12:01 | 7949.35 | 2.7513 | 82.9648 | 64.1561 | 2329.7245
2038-02-08 13:01 | 8985.34 | 2.9011 | 84.0586 | 64.1561 | 2633.3432
2038-02-09 14:01 | 9447.04 | 3.0512 | 84.3567 | 64.1561 | 2768.6541
2038-02-10 15:01 | 9552.75 | 3.1296 | 84.4565 | 64.1561 | 2799.6347
2038-02-11 16:01 | 11480.7 | 3.7452 | 84.6897 | 64.1561 | 3364.661
2038-02-12 17:01 | 9648.57 | 3.0784 | 85.3251 | 64.1561 | 2827.7167
2038-02-13 18:01 | 7810.04 | 2.4465 | 85.6109 | 64.1561 | 2288.8968
2038-02-14 19:01 | 6562.7 | 2.0335 | 85.5951 | 64.1561 | 1923.3375
2038-02-15 20:01 | 5399.61 | 1.6443 | 85.6657 | 64.1561 | 1582.4695
2038-02-16 21:01 | 4368.34 | 1.3527 | 85.2886 | 64.1561 | 1280.2341
2038-02-17 22:01 | 3482.66 | 1.1218 | 84.5577 | 64.1561 | 1020.6669
2038-02-18 23:01 | 2807.35 | 1 | 71.5105 | 64.1561 | 822.7531
2038-02-20 00:01 | 0 | 0 | 71.9809 | 64.1561 | 0
2038-02-21 01:01 | -230.911 | 1.1023 | 70.7082 | 64.1561 | -67.6733
2038-02-22 02:01 | -424.226 | 1.535 | 70.1392 | 64.1561 | -124.3284
2038-02-23 03:01 | -618.893 | 1.9906 | 69.7855 | 64.1561 | -181.3796
2038-02-24 04:01 | -797.778 | 2.4078 | 69.4804 | 64.1561 | -233.8057
2038-02-25 05:01 | -909.413 | 2.6605 | 69.2388 | 64.1561 | -266.5226
2038-02-26 06:01 | 0 | 1 | 70.4441 | 64.1561 | 0
2038-02-27 07:01 | 2419.44 | 1 | 69.8481 | 64.1561 | 709.0679
2038-02-28 08:01 | 3093.08 | 1 | 88.6619 | 64.1561 | 906.4923
2038-03-01 09:01 | 4993.45 | 1.559 | 83.325 | 64.1561 | 1463.4357
2038-03-02 10:01 | 7128.6 | 2.4452 | 82.4786 | 64.1561 | 2089.1864
2038-03-03 11:01 | 8974.03 | 3.0554 | 82.9647 | 64.1561 | 2630.0286
2038-03-04 12:01 | 10378.5 | 3.4223 | 83.7961 | 64.1561 | 3041.6381
2038-03-05 13:01 | 11273.7 | 3.6347 | 84.4843 | 64.1561 | 3303.9953
2038-03-06 14:01 | 11916.1 | 3.823 | 84.9332 | 64.1561 | 3492.2642
2038-03-07 15:01 | 11871.9 | 3.8544 | 85.1318 | 64.1561 | 3479.3104
2038-03-08 16:01 | 13655.2 | 4.4245 | 85.3824 | 64.1561 | 4001.9441
2038-03-09 17:01 | 11847.5 | 3.7472 | 86.0775 | 64.1561 | 3472.1595
2038-03-10 18:01 | 9712.11 | 3.0575 | 86.2285 | 64.1561 | 2846.3385
2038-03-11 19:01 | 8172.43 | 2.5287 | 86.2994 | 64.1561 | 2395.1028
2038-03-12 20:01 | 7246.63 | 2.2043 | 86.3427 | 64.1561 | 2123.7776
2038-03-13 21:01 | 6271.98 | 1.9513 | 85.9036 | 64.1561 | 1838.1359
2038-03-14 22:01 | 5380.54 | 1.6678 | 85.7287 | 64.1561 | 1576.8806
2038-03-15 23:01 | 3237.68 | 1 | 89.1197 | 64.1561 | 948.8703
2038-03-17 00:01 | 3157.2 | 1 | 71.7884 | 64.1561 | 925.284
2038-03-18 01:01 | 3056.95 | 1 | 71.6044 | 64.1561 | 895.9036
2038-03-19 02:01 | 3106.94 | 1 | 71.4464 | 64.1561 | 910.5542
2038-03-20 03:01 | 3164.73 | 1 | 71.3192 | 64.1561 | 927.4908
2038-03-21 04:01 | 3081.9 | 1 | 71.2339 | 64.1561 | 903.2157
2038-03-22 05:01 | 3150.82 | 1 | 71.1553 | 64.1561 | 923.4142
2038-03-23 06:01 | 3101.14 | 1 | 71.13 | 64.1561 | 908.8544
2038-03-24 07:01 | 3323.29 | 1 | 87.2037 | 64.1561 | 973.9602
2038-03-25 08:01 | 4282.55 | 1.336 | 84.3236 | 64.1561 | 1255.0915
2038-03-26 09:01 | 6792.55 | 2.3506 | 83.1667 | 64.1561 | 1990.6999
2038-03-27 10:01 | 9501.27 | 3.2088 | 83.7432 | 64.1561 | 2784.5474
2038-03-28 11:01 | 11664.3 | 3.8526 | 84.4658 | 64.1561 | 3418.4689
2038-03-29 12:01 | 12980.7 | 4.2463 | 85.0817 | 64.1561 | 3804.2676
2038-03-30 13:01 | 13218.4 | 4.2551 | 85.7395 | 64.1561 | 3873.9306
2038-03-31 14:01 | 13962 | 4.454 | 86.1927 | 64.1561 | 4091.8583
2038-04-01 15:01 | 13773 | 4.468 | 86.3185 | 64.1561 | 4036.4678
2038-04-02 16:01 | 14182.2 | 4.5988 | 86.5224 | 64.1561 | 4156.3925
2038-04-03 17:01 | 13224.3 | 4.2103 | 86.9544 | 64.1561 | 3875.6598
2038-04-04 18:01 | 11199.4 | 3.4904 | 87.302 | 64.1561 | 3282.2201
2038-04-05 19:01 | 9782.68 | 3.0841 | 87.0497 | 64.1561 | 2867.0205
2038-04-06 20:01 | 7532.57 | 2.3202 | 87.1844 | 64.1561 | 2207.5783
2038-04-07 21:01 | 6568.17 | 2.0373 | 86.7929 | 64.1561 | 1924.9406
2038-04-08 22:01 | 4562.96 | 1.3659 | 86.9617 | 64.1561 | 1337.2716
2038-04-09 23:01 | 3844.35 | 1.1731 | 86.3142 | 64.1561 | 1126.6678
2038-04-11 00:01 | 3092.28 | 1.0025 | 85.2399 | 64.1561 | 906.2578
2038-04-12 01:01 | 3133.15 | 1 | 88.6462 | 64.1561 | 918.2356
2038-04-13 02:01 | 3194.12 | 1 | 92.1333 | 64.1561 | 936.1042
2038-04-14 03:01 | 3169.06 | 1 | 89.7612 | 64.1561 | 928.7598
2038-04-15 04:01 | 3108.06 | 1 | 88.6675 | 64.1561 | 910.8825
2038-04-16 05:01 | 3196.21 | 1.0407 | 84.3126 | 64.1561 | 936.7167
2038-04-17 06:01 | 3143.91 | 1.0138 | 84.3732 | 64.1561 | 921.3891
2038-04-18 07:01 | 4526.6 | 1.3915 | 84.8966 | 64.1561 | 1326.6155
2038-04-19 08:01 | 5825.97 | 1.8847 | 84.3647 | 64.1561 | 1707.4233
2038-04-20 09:01 | 8156.86 | 2.827 | 83.7334 | 64.1561 | 2390.5397
2038-04-21 10:01 | 10686.7 | 3.7235 | 84.0095 | 64.1561 | 3131.9626
2038-04-22 11:01 | 12892.2 | 4.3394 | 84.8687 | 64.1561 | 3778.3308
2038-04-23 12:01 | 12604.9 | 4.1499 | 85.6614 | 64.1561 | 3694.1315
2038-04-24 13:01 | 12426.8 | 3.9638 | 86.3355 | 64.1561 | 3641.9356
2038-04-25 14:01 | 14255.2 | 4.6424 | 86.2703 | 64.1561 | 4177.7867
2038-04-26 15:01 | 16025.8 | 5.1034 | 86.9098 | 64.1561 | 4696.6984
2038-04-27 16:01 | 15855.9 | 5.0473 | 87.3525 | 64.1561 | 4646.9056
2038-04-28 17:01 | 14659.3 | 4.6376 | 87.6817 | 64.1561 | 4296.2167
2038-04-29 18:01 | 11990.1 | 3.7933 | 87.7837 | 64.1561 | 3513.9514
2038-04-30 19:01 | 10678.9 | 3.3167 | 87.8732 | 64.1561 | 3129.6766
2038-05-01 20:01 | 8561.77 | 2.6167 | 87.9204 | 64.1561 | 2509.2071
2038-05-02 21:01 | 7546.42 | 2.2865 | 87.7221 | 64.1561 | 2211.6374
2038-05-03 22:01 | 5452.36 | 1.5654 | 88.144 | 64.1561 | 1597.929
2038-05-04 23:01 | 4871.54 | 1.5479 | 86.4177 | 64.1561 | 1427.7074
2038-05-06 00:01 | 3769.24 | 1.1764 | 86.3548 | 64.1561 | 1104.6552
2038-05-07 01:01 | 3289.07 | 1.058 | 85.6815 | 64.1561 | 963.9313
2038-05-08 02:01 | 3117.42 | 1 | 87.6851 | 64.1561 | 913.6256
2038-05-09 03:01 | 3142.21 | 1 | 87.2545 | 64.1561 | 920.8908
2038-05-10 04:01 | 3084.95 | 1 | 86.6606 | 64.1561 | 904.1096
2038-05-11 05:01 | 3639.57 | 1.1397 | 85.214 | 64.1561 | 1066.6527
2038-05-12 06:01 | 3690.99 | 1.1437 | 85.3153 | 64.1561 | 1081.7224
2038-05-13 07:01 | 4667.42 | 1.4756 | 85.0216 | 64.1561 | 1367.8858
2038-05-14 08:01 | 4539.64 | 1.4021 | 85.381 | 64.1561 | 1330.4372
2038-05-15 09:01 | 5328.08 | 1.6641 | 85.2316 | 64.1561 | 1561.5061
2038-05-16 10:01 | 6059.26 | 2.0102 | 84.5571 | 64.1561 | 1775.7938
2038-05-17 11:01 | 8897.22 | 3.1109 | 84.0322 | 64.1561 | 2607.5178
2038-05-18 12:01 | 9883.09 | 3.3567 | 84.7166 | 64.1561 | 2896.4478
2038-05-19 13:01 | 10840.3 | 3.6633 | 85.0698 | 64.1561 | 3176.9783
2038-05-20 14:01 | 11846.7 | 3.851 | 85.7964 | 64.1561 | 3471.925
2038-05-21 15:01 | 12128 | 3.9492 | 86.062 | 64.1561 | 3554.3659
2038-05-22 16:01 | 12983.5 | 4.1708 | 86.4524 | 64.1561 | 3805.0882
2038-05-23 17:01 | 12503.6 | 3.9735 | 86.8217 | 64.1561 | 3664.4434
2038-05-24 18:01 | 10446 | 3.2989 | 87.0402 | 64.1561 | 3061.4204
2038-05-25 19:01 | 9534.97 | 2.9745 | 87.0804 | 64.1561 | 2794.4239
2038-05-26 20:01 | 7730.74 | 2.3774 | 87.1593 | 64.1561 | 2265.6562
2038-05-27 21:01 | 7212.86 | 2.209 | 87.0003 | 64.1561 | 2113.8806
2038-05-28 22:01 | 5395.29 | 1.5797 | 87.4243 | 64.1561 | 1581.2034
2038-05-29 23:01 | 4742.76 | 1.4407 | 86.6337 | 64.1561 | 1389.9657
2038-05-31 00:01 | 4374.67 | 1.3666 | 86.0405 | 64.1561 | 1282.0892
2038-06-01 01:01 | 4045.3 | 1.2769 | 85.7236 | 64.1561 | 1185.5604
2038-06-02 02:01 | 4024.88 | 1.2671 | 85.5923 | 64.1561 | 1179.5759
2038-06-03 03:01 | 4251 | 1.3274 | 85.5598 | 64.1561 | 1245.8451
2038-06-04 04:01 | 4568.73 | 1.4427 | 85.3491 | 64.1561 | 1338.9626
2038-06-05 05:01 | 5413.7 | 1.7612 | 84.9533 | 64.1561 | 1586.5989
2038-06-06 06:01 | 5311.92 | 1.6479 | 85.6081 | 64.1561 | 1556.7701
2038-06-07 07:01 | 5455.67 | 1.6661 | 85.8172 | 64.1561 | 1598.899
2038-06-08 08:01 | 4263.78 | 1.317 | 85.6967 | 64.1561 | 1249.5906
2038-06-09 09:01 | 4865.04 | 1.5227 | 85.3988 | 64.1561 | 1425.8025
2038-06-10 10:01 | 5735.35 | 1.8617 | 84.9362 | 64.1561 | 1680.8652
2038-06-11 11:01 | 6241.32 | 2.1225 | 84.4463 | 64.1561 | 1829.1503
2038-06-12 12:01 | 6506.14 | 2.0967 | 85.138 | 64.1561 | 1906.7614
2038-06-13 13:01 | 6709.21 | 2.1684 | 85.1335 | 64.1561 | 1966.2754
2038-06-14 14:01 | 7263.7 | 2.435 | 84.7382 | 64.1561 | 2128.7803
2038-06-15 15:01 | 9375.91 | 3.181 | 84.66 | 64.1561 | 2747.808
2038-06-16 16:01 | 9805.7 | 3.169 | 85.4814 | 64.1561 | 2873.767
2038-06-17 17:01 | 9791.95 | 3.1214 | 85.8204 | 64.1561 | 2869.7373
2038-06-18 18:01 | 8518.49 | 2.7493 | 85.7803 | 64.1561 | 2496.523
2038-06-19 19:01 | 8034.34 | 2.481 | 86.285 | 64.1561 | 2354.6326
2038-06-20 20:01 | 6426.36 | 1.9265 | 86.6488 | 64.1561 | 1883.3802
2038-06-21 21:01 | 5729.39 | 1.7578 | 86.1698 | 64.1561 | 1679.1185
2038-06-22 22:01 | 3832.02 | 1.1771 | 85.9876 | 64.1561 | 1123.0542
2038-06-23 23:01 | 3273.7 | 1.0277 | 85.4105 | 64.1561 | 959.4268
2038-06-25 00:01 | 3158.27 | 1 | 85.8101 | 64.1561 | 925.5976
2038-06-26 01:01 | 3205.22 | 1 | 86.9192 | 64.1561 | 939.3573
2038-06-27 02:01 | 3210.23 | 1 | 86.913 | 64.1561 | 940.8255
2038-06-28 03:01 | 3144.54 | 1 | 85.2598 | 64.1561 | 921.5737
2038-06-29 04:01 | 3030.72 | 1 | 84.2663 | 64.1561 | 888.2164
2038-06-30 05:01 | 3955.29 | 1.2777 | 84.2866 | 64.1561 | 1159.1811
2038-07-01 06:01 | 3996.61 | 1.2784 | 84.4407 | 64.1561 | 1171.2908
2038-07-02 07:01 | 4446.58 | 1.3796 | 84.8161 | 64.1561 | 1303.164
2038-07-03 08:01 | 4733.25 | 1.4409 | 85.0973 | 64.1561 | 1387.1786
2038-07-04 09:01 | 5285.81 | 1.6367 | 84.9284 | 64.1561 | 1549.118
2038-07-05 10:01 | 5668.43 | 1.8601 | 84.3098 | 64.1561 | 1661.2528
2038-07-06 11:01 | 5936.02 | 1.9688 | 84.2616 | 64.1561 | 1739.6757
2038-07-07 12:01 | 5809.63 | 1.7853 | 85.2654 | 64.1561 | 1702.6345
2038-07-08 13:01 | 4596.55 | 1.5145 | 84.4287 | 64.1561 | 1347.1158
2038-07-09 14:01 | 4361.65 | 1.4578 | 84.1281 | 64.1561 | 1278.2734
2038-07-10 15:01 | 5865.08 | 2.0616 | 83.4276 | 64.1561 | 1718.8853
2038-07-11 16:01 | 5461.05 | 1.844 | 83.9698 | 64.1561 | 1600.4758
2038-07-12 17:01 | 5050.69 | 1.6809 | 84.1019 | 64.1561 | 1480.2111
2038-07-13 18:01 | 3772.28 | 1.2353 | 84.2064 | 64.1561 | 1105.5461
2038-07-14 19:01 | 3080.07 | 1 | 85.2224 | 64.1561 | 902.6794
2038-07-15 20:01 | 2935.74 | 1 | 71.2271 | 64.1561 | 860.3805
2038-07-16 21:01 | 2847.74 | 1 | 71.1125 | 64.1561 | 834.5902
2038-07-17 22:01 | -589.664 | 2.0176 | 70.5473 | 64.1561 | -172.8135
2038-07-18 23:01 | -1235.94 | 3.4895 | 69.8316 | 64.1561 | -362.2183
2038-07-20 00:01 | -1620.12 | 4.3541 | 69.4077 | 64.1561 | -474.8103
2038-07-21 01:01 | -1840.49 | 4.8535 | 69.1363 | 64.1561 | -539.3944
2038-07-22 02:01 | -2106.08 | 5.5016 | 68.8955 | 64.1561 | -617.2311
2038-07-23 03:01 | -2203.62 | 5.7124 | 68.6351 | 64.1561 | -645.8173
2038-07-24 04:01 | -2322.89 | 6.0123 | 68.4608 | 64.1561 | -680.7719
2038-07-25 05:01 | -2171.14 | 5.6073 | 68.2928 | 64.1561 | -636.2983
2038-07-26 06:01 | -1354.73 | 3.5537 | 68.195 | 64.1561 | -397.0322
2038-07-27 07:01 | -747.364 | 2.1798 | 68.3207 | 64.1561 | -219.0308
2038-07-28 08:01 | -890.778 | 2.6583 | 68.3613 | 64.1561 | -261.0613
2038-07-29 09:01 | -776.034 | 2.3292 | 68.3033 | 64.1561 | -227.4331
2038-07-30 10:01 | -122.113 | 0.69834 | 68.8859 | 64.1561 | -35.7878
2038-07-31 11:01 | 2222.59 | 1 | 69.0754 | 64.1561 | 651.3768
2038-08-01 12:01 | 2933.74 | 1 | 69.1606 | 64.1561 | 859.7943
2038-08-02 13:01 | 3117.97 | 1 | 88.4476 | 64.1561 | 913.7868
2038-08-03 14:01 | 3779.05 | 1.1887 | 82.5996 | 64.1561 | 1107.5302
2038-08-04 15:01 | 4033.03 | 1.286 | 82.5949 | 64.1561 | 1181.9644
2038-08-05 16:01 | 6404.72 | 2.1469 | 82.127 | 64.1561 | 1877.0381
2038-08-06 17:01 | 5624.32 | 1.7837 | 83.127 | 64.1561 | 1648.3255
2038-08-07 18:01 | 4801.46 | 1.4872 | 83.5403 | 64.1561 | 1407.169
2038-08-08 19:01 | 3760.89 | 1.1994 | 83.1699 | 64.1561 | 1102.2081
2038-08-09 20:01 | 3230.94 | 1.063 | 82.7277 | 64.1561 | 946.895
2038-08-10 21:01 | 3054.47 | 1 | 85.9728 | 64.1561 | 895.1768
2038-08-11 22:01 | 3088.09 | 1 | 89.2955 | 64.1561 | 905.0298
2038-08-12 23:01 | 0 | 0 | 70.7202 | 64.1561 | 0
2038-08-14 00:01 | -569.668 | 1.9431 | 69.2137 | 64.1561 | -166.9532
2038-08-15 01:01 | -721.066 | 2.2359 | 68.8406 | 64.1561 | -211.3236
2038-08-16 02:01 | -852.014 | 2.5475 | 68.6394 | 64.1561 | -249.7007
2038-08-17 03:01 | -923.494 | 2.7078 | 68.4695 | 64.1561 | -270.6494
2038-08-18 04:01 | -999.145 | 2.8923 | 68.2885 | 64.1561 | -292.8205
2038-08-19 05:01 | -1028.23 | 2.9546 | 68.1754 | 64.1561 | -301.3445
2038-08-20 06:01 | -337.014 | 1.1913 | 68.3424 | 64.1561 | -98.7691
2038-08-21 07:01 | 410.658 | 1 | 69.355 | 64.1561 | 120.352
2038-08-22 08:01 | -498.351 | 1.8092 | 68.4354 | 64.1561 | -146.0523
2038-08-23 09:01 | -606.751 | 1.9728 | 68.2117 | 64.1561 | -177.8212
2038-08-24 10:01 | -346.804 | 1.3002 | 68.2763 | 64.1561 | -101.6382
2038-08-25 11:01 | 0 | 0 | 69.3007 | 64.1561 | 0
2038-08-26 12:01 | 19.362 | 1 | 69.2923 | 64.1561 | 5.6744
2038-08-27 13:01 | 317.797 | 1 | 69.1829 | 64.1561 | 93.1371
2038-08-28 14:01 | 1860.33 | 1 | 68.8137 | 64.1561 | 545.2089
2038-08-29 15:01 | 2891.16 | 1 | 68.7247 | 64.1561 | 847.3154
2038-08-30 16:01 | 3526.38 | 1.1635 | 81.4623 | 64.1561 | 1033.48
2038-08-31 17:01 | 3117.94 | 1 | 84.1884 | 64.1561 | 913.778
2038-09-01 18:01 | 3055.9 | 1 | 69.0668 | 64.1561 | 895.5959
2038-09-02 19:01 | 3087.54 | 1 | 69.1088 | 64.1561 | 904.8687
2038-09-03 20:01 | 3103.24 | 1 | 69.1543 | 64.1561 | 909.4699
2038-09-04 21:01 | 3183.94 | 1 | 69.1706 | 64.1561 | 933.1207
2038-09-05 22:01 | 3111.86 | 1 | 69.2278 | 64.1561 | 911.9961
2038-09-06 23:01 | -604.813 | 2.0896 | 68.8874 | 64.1561 | -177.2532
2038-09-08 00:01 | -818.878 | 2.4838 | 68.3645 | 64.1561 | -239.9895
2038-09-09 01:01 | -872.744 | 2.5947 | 68.1251 | 64.1561 | -255.776
2038-09-10 02:01 | -752.295 | 2.2812 | 68.0346 | 64.1561 | -220.4759
2038-09-11 03:01 | -527.382 | 1.7358 | 68.0314 | 64.1561 | -154.5604
2038-09-12 04:01 | -306.124 | 1.2188 | 68.1502 | 64.1561 | -89.7161
2038-09-13 05:01 | 0 | 1 | 69.132 | 64.1561 | 0
2038-09-14 06:01 | 2053.94 | 1 | 68.6557 | 64.1561 | 601.9504
2038-09-15 07:01 | 3113.57 | 1 | 68.6231 | 64.1561 | 912.4973
2038-09-16 08:01 | 0 | 0 | 69.6049 | 64.1561 | 0
2038-09-17 09:01 | 2735.9 | 1 | 68.7185 | 64.1561 | 801.8131
2038-09-18 10:01 | 3464.12 | 1 | 68.7306 | 64.1561 | 1015.2334
2038-09-19 11:01 | 3412.89 | 1.023 | 82.8739 | 64.1561 | 1000.2193
2038-09-20 12:01 | 5088.68 | 1.5597 | 82.6397 | 64.1561 | 1491.3449
2038-09-21 13:01 | 5962.24 | 2.0268 | 81.6225 | 64.1561 | 1747.3601
2038-09-22 14:01 | 6654.56 | 2.1605 | 82.4718 | 64.1561 | 1950.259
2038-09-23 15:01 | 8709.43 | 2.9848 | 82.0663 | 64.1561 | 2552.482
2038-09-24 16:01 | 9517.63 | 3.155 | 82.8355 | 64.1561 | 2789.342
2038-09-25 17:01 | 9070.83 | 2.8895 | 83.678 | 64.1561 | 2658.3979
2038-09-26 18:01 | 7709.43 | 2.3519 | 84.393 | 64.1561 | 2259.4109
2038-09-27 19:01 | 6868.21 | 2.0581 | 84.6162 | 64.1561 | 2012.8737
2038-09-28 20:01 | 4856.32 | 1.4156 | 84.9795 | 64.1561 | 1423.2469
2038-09-29 21:01 | 3983.65 | 1.2274 | 84.0378 | 64.1561 | 1167.4926
2038-09-30 22:01 | 3150.24 | 1 | 70.3841 | 64.1561 | 923.2442
2038-10-01 23:01 | 3079.84 | 1 | 70.2266 | 64.1561 | 902.612
2038-10-03 00:01 | 3090.45 | 1 | 70.1148 | 64.1561 | 905.7215
2038-10-04 01:01 | 3135.74 | 1 | 70.0315 | 64.1561 | 918.9947
2038-10-05 02:01 | 3174.08 | 1 | 69.9879 | 64.1561 | 930.231
2038-10-06 03:01 | 3168.27 | 1 | 69.9529 | 64.1561 | 928.5283
2038-10-07 04:01 | 3131.68 | 1 | 69.9289 | 64.1561 | 917.8048
2038-10-08 05:01 | 3130.01 | 1 | 69.8945 | 64.1561 | 917.3154
2038-10-09 06:01 | 3095.75 | 1 | 69.8706 | 64.1561 | 907.2748
2038-10-10 07:01 | 3166.48 | 1 | 69.8181 | 64.1561 | 928.0037
2038-10-11 08:01 | 3277.01 | 1 | 85.2911 | 64.1561 | 960.3968
2038-10-12 09:01 | 5382.21 | 1.7594 | 82.54 | 64.1561 | 1577.37
2038-10-13 10:01 | 7725.72 | 2.6405 | 82.2638 | 64.1561 | 2264.185
2038-10-14 11:01 | 9321.76 | 3.2524 | 82.4358 | 64.1561 | 2731.9382
2038-10-15 12:01 | 9848.84 | 3.2214 | 83.5927 | 64.1561 | 2886.4101
2038-10-16 13:01 | 10742.7 | 3.5535 | 83.7778 | 64.1561 | 3148.3746
2038-10-17 14:01 | 11318.1 | 3.6478 | 84.4318 | 64.1561 | 3317.0077
2038-10-18 15:01 | 12721.4 | 4.1274 | 84.6451 | 64.1561 | 3728.2743
2038-10-19 16:01 | 12588.3 | 3.9906 | 85.2831 | 64.1561 | 3689.2666
2038-10-20 17:01 | 10874.8 | 3.4889 | 85.3718 | 64.1561 | 3187.0893
2038-10-21 18:01 | 9229.14 | 2.8317 | 85.9349 | 64.1561 | 2704.7939
2038-10-22 19:01 | 8135.18 | 2.3995 | 86.3378 | 64.1561 | 2384.1859
2038-10-23 20:01 | 5790.87 | 1.6728 | 86.5126 | 64.1561 | 1697.1365
2038-10-24 21:01 | 3284.66 | 1.1588 | 83.7491 | 64.1561 | 962.6388
2038-10-25 22:01 | 2852.73 | 1 | 71.5199 | 64.1561 | 836.0526
2038-10-26 23:01 | 0 | 0 | 71.8971 | 64.1561 | 0
2038-10-28 00:01 | -282.291 | 1.2683 | 70.5119 | 64.1561 | -82.7313
2038-10-29 01:01 | -748.966 | 2.3345 | 69.7426 | 64.1561 | -219.5003
2038-10-30 02:01 | -910.058 | 2.6648 | 69.3575 | 64.1561 | -266.7117
2038-10-31 03:01 | -1161.59 | 3.2807 | 69.0503 | 64.1561 | -340.4284
2038-11-01 04:01 | -1215.49 | 3.3764 | 68.77 | 64.1561 | -356.225
2038-11-02 05:01 | -1005.16 | 2.8405 | 68.6159 | 64.1561 | -294.5833
2038-11-03 06:01 | -1086.83 | 3.0969 | 68.499 | 64.1561 | -318.5184
2038-11-04 07:01 | -770.612 | 2.2755 | 68.4147 | 64.1561 | -225.8441
2038-11-05 08:01 | 0 | 1 | 69.6751 | 64.1561 | 0
2038-11-06 09:01 | 2396.55 | 1.081 | 78.3782 | 64.1561 | 702.3595
2038-11-07 10:01 | 5410.86 | 1.844 | 81.3983 | 64.1561 | 1585.7665
2038-11-08 11:01 | 6417.91 | 2.3708 | 80.9571 | 64.1561 | 1880.9038
2038-11-09 12:01 | 6817.85 | 2.293 | 82.3534 | 64.1561 | 1998.1146
2038-11-10 13:01 | 7260.65 | 2.4294 | 82.6677 | 64.1561 | 2127.8865
2038-11-11 14:01 | 7582.46 | 2.5371 | 82.9078 | 64.1561 | 2222.1997
2038-11-12 15:01 | 8822.37 | 2.879 | 83.3889 | 64.1561 | 2585.5814
2038-11-13 16:01 | 8537.1 | 2.7738 | 83.6825 | 64.1561 | 2501.977
2038-11-14 17:01 | 7385.3 | 2.3792 | 83.9197 | 64.1561 | 2164.4178
2038-11-15 18:01 | 5202.99 | 1.5901 | 84.5673 | 64.1561 | 1524.8458
2038-11-16 19:01 | 3279.69 | 1.0421 | 83.8814 | 64.1561 | 961.1823
2038-11-17 20:01 | 2991.3 | 1 | 70.5875 | 64.1561 | 876.6635
2038-11-18 21:01 | -4.6305 | 0.57369 | 71.1207 | 64.1561 | -1.3571
2038-11-19 22:01 | -1131.05 | 3.3231 | 69.3042 | 64.1561 | -331.478
2038-11-20 23:01 | -1674.79 | 4.5412 | 68.7654 | 64.1561 | -490.8325
2038-11-22 00:01 | -2069.89 | 5.4669 | 68.4182 | 64.1561 | -606.6249
2038-11-23 01:01 | -2425.78 | 6.3231 | 68.1378 | 64.1561 | -710.9259
2038-11-24 02:01 | -2598.47 | 6.4446 | 67.7969 | 64.1561 | -761.5364
2038-11-25 03:01 | -2872.32 | 6.4446 | 67.4213 | 64.1561 | -841.7939
2038-11-26 04:01 | -2643.63 | 6.4446 | 67.3619 | 64.1561 | -774.7715
2038-11-27 05:01 | -2353.39 | 6.1162 | 67.3267 | 64.1561 | -689.7105
2038-11-28 06:01 | -2364.26 | 6.1719 | 67.2569 | 64.1561 | -692.8962
2038-11-29 07:01 | -2082.49 | 5.437 | 67.1797 | 64.1561 | -610.3176
2038-11-30 08:01 | -1615.93 | 4.2895 | 67.154 | 64.1561 | -473.5823
2038-12-01 09:01 | 0 | 1 | 68.6351 | 64.1561 | 0
2038-12-02 10:01 | 2776.09 | 1 | 82.6762 | 64.1561 | 813.5917
2038-12-03 11:01 | 4363 | 1.4456 | 80.9331 | 64.1561 | 1278.6691
2038-12-04 12:01 | 6215.8 | 1.9513 | 81.9489 | 64.1561 | 1821.6712
2038-12-05 13:01 | 6879.35 | 2.1951 | 82.1574 | 64.1561 | 2016.1385
2038-12-06 14:01 | 7892.69 | 2.5038 | 82.5685 | 64.1561 | 2313.1191
2038-12-07 15:01 | 7489.85 | 2.3684 | 82.9432 | 64.1561 | 2195.0584
2038-12-08 16:01 | 6684.77 | 2.1222 | 83.0629 | 64.1561 | 1959.1127
2038-12-09 17:01 | 6080.25 | 1.9125 | 83.2215 | 64.1561 | 1781.9454
2038-12-10 18:01 | 4724.13 | 1.458 | 83.468 | 64.1561 | 1384.5058
2038-12-11 19:01 | 3332.03 | 1.0354 | 83.2854 | 64.1561 | 976.5216
2038-12-12 20:01 | 3042.96 | 1 | 69.7879 | 64.1561 | 891.8035
2038-12-13 21:01 | 3028.04 | 1 | 69.6885 | 64.1561 | 887.4309
2038-12-14 22:01 | -307.95 | 1.3312 | 69.4468 | 64.1561 | -90.2512
2038-12-15 23:01 | -629.061 | 2.0549 | 68.7351 | 64.1561 | -184.3596
2038-12-17 00:01 | -795.852 | 2.4281 | 68.3653 | 64.1561 | -233.2412
2038-12-18 01:01 | -979.521 | 2.8706 | 68.1431 | 64.1561 | -287.0693
2038-12-19 02:01 | -1088.22 | 3.1181 | 67.9362 | 64.1561 | -318.9258
2038-12-20 03:01 | -1139.39 | 3.2348 | 67.7537 | 64.1561 | -333.9222
2038-12-21 04:01 | -1123.6 | 3.1879 | 67.657 | 64.1561 | -329.2947
2038-12-22 05:01 | -1136.9 | 3.229 | 67.579 | 64.1561 | -333.1925
2038-12-23 06:01 | -1494.93 | 4.1519 | 67.4822 | 64.1561 | -438.1207
2038-12-24 07:01 | -1527.88 | 4.1637 | 67.3605 | 64.1561 | -447.7774
2038-12-25 08:01 | -1192 | 3.297 | 67.3046 | 64.1561 | -349.3407
2038-12-26 09:01 | 0 | 1 | 68.6777 | 64.1561 | 0
2038-12-27 10:01 | 3234.83 | 1 | 67.9926 | 64.1561 | 948.0351
2038-12-28 11:01 | 4168.76 | 1.2756 | 81.9467 | 64.1561 | 1221.743
2038-12-29 12:01 | 5595.1 | 1.7578 | 81.8771 | 64.1561 | 1639.7619
2038-12-30 13:01 | 6777.35 | 2.1988 | 81.7994 | 64.1561 | 1986.2452
2038-12-31 14:01 | 7264.2 | 2.3182 | 82.346 | 64.1561 | 2128.9269
2039-01-01 15:01 | 8201.92 | 2.7409 | 82.0692 | 64.1561 | 2403.7455
2039-01-02 16:01 | 8049.92 | 2.6097 | 82.7003 | 64.1561 | 2359.1987
2039-01-03 17:01 | 6834.17 | 2.1587 | 83.2034 | 64.1561 | 2002.8975
2039-01-04 18:01 | 4140.41 | 1.3125 | 83.1826 | 64.1561 | 1213.4344
2039-01-05 19:01 | 3031.57 | 1 | 86.6242 | 64.1561 | 888.4655
2039-01-06 20:01 | 0 | 0 | 70.4122 | 64.1561 | 0
2039-01-07 21:01 | -406.789 | 1.4997 | 68.9053 | 64.1561 | -119.2181
2039-01-08 22:01 | -1436.88 | 4.1025 | 68.2765 | 64.1561 | -421.108
2039-01-09 23:01 | -2188.25 | 5.8471 | 67.8694 | 64.1561 | -641.3128
2039-01-11 00:01 | -2487.57 | 6.4446 | 67.5241 | 64.1561 | -729.0348
2039-01-12 01:01 | -2932.38 | 6.4446 | 66.9971 | 64.1561 | -859.3957
2039-01-13 02:01 | -3369.2 | 6.4446 | 66.5139 | 64.1561 | -987.415
2039-01-14 03:01 | -3533.72 | 6.4446 | 66.1752 | 64.1561 | -1035.6311
2039-01-15 04:01 | -3688.99 | 6.4446 | 65.8774 | 64.1561 | -1081.1362
2039-01-16 05:01 | -3906.49 | 6.4446 | 65.5685 | 64.1561 | -1144.8792
2039-01-17 06:01 | -3188.19 | 6.4446 | 65.8471 | 64.1561 | -934.3663
2039-01-18 07:01 | -2091.2 | 5.5254 | 66.258 | 64.1561 | -612.8702
2039-01-19 08:01 | -1676.16 | 4.4797 | 66.3627 | 64.1561 | -491.234
2039-01-20 09:01 | -810.584 | 2.3073 | 66.5073 | 64.1561 | -237.5587
2039-01-21 10:01 | 2694.42 | 1 | 67.3328 | 64.1561 | 789.6566
2039-01-22 11:01 | 3066.62 | 1 | 81.2048 | 64.1561 | 898.7376
2039-01-23 12:01 | 4349.24 | 1.4024 | 80.7995 | 64.1561 | 1274.6364
2039-01-24 13:01 | 5222.9 | 1.6778 | 81.1149 | 64.1561 | 1530.6809
2039-01-25 14:01 | 6398.25 | 2.0156 | 81.6409 | 64.1561 | 1875.142
2039-01-26 15:01 | 6471.79 | 2.1512 | 81.315 | 64.1561 | 1896.6944
2039-01-27 16:01 | 8257.22 | 2.7118 | 81.6425 | 64.1561 | 2419.9523
2039-01-28 17:01 | 6019.85 | 2.0166 | 81.7752 | 64.1561 | 1764.2439
2039-01-29 18:01 | 3913.87 | 1.2955 | 81.9295 | 64.1561 | 1147.0421
2039-01-30 19:01 | 3116.81 | 1 | 86.1362 | 64.1561 | 913.4468
2039-01-31 20:01 | 3192.67 | 1 | 69.0341 | 64.1561 | 935.6792
2039-02-01 21:01 | 0 | 0 | 69.7767 | 64.1561 | 0
2039-02-02 22:01 | -281.138 | 1.1726 | 68.4154 | 64.1561 | -82.3934
2039-02-03 23:01 | -1607.77 | 4.5872 | 67.7277 | 64.1561 | -471.1909
2039-02-05 00:01 | -1971.03 | 5.2754 | 67.3647 | 64.1561 | -577.6519
2039-02-06 01:01 | -2245.66 | 5.947 | 67.1164 | 64.1561 | -658.138
2039-02-07 02:01 | -2477.04 | 6.4446 | 66.8713 | 64.1561 | -725.9488
2039-02-08 03:01 | -2831.95 | 6.4446 | 66.4952 | 64.1561 | -829.9626
2039-02-09 04:01 | -3322.24 | 6.4446 | 66.0044 | 64.1561 | -973.6524
2039-02-10 05:01 | -3430.91 | 6.4446 | 65.7595 | 64.1561 | -1005.5005
2039-02-11 06:01 | -2733.38 | 6.4446 | 66.0484 | 64.1561 | -801.0746
2039-02-12 07:01 | -1407.56 | 3.709 | 66.1915 | 64.1561 | -412.5151
2039-02-13 08:01 | -989.937 | 2.8446 | 66.4069 | 64.1561 | -290.1219
2039-02-14 09:01 | 0 | 1 | 67.8539 | 64.1561 | 0
2039-02-15 10:01 | 2645.64 | 1 | 79.0415 | 64.1561 | 775.3605
2039-02-16 11:01 | 4479.65 | 1.4407 | 80.501 | 64.1561 | 1312.8558
2039-02-17 12:01 | 5727.75 | 1.8398 | 80.9175 | 64.1561 | 1678.6378
2039-02-18 13:01 | 6349.98 | 2.1097 | 80.8676 | 64.1561 | 1860.9954
2039-02-19 14:01 | 7311.39 | 2.3948 | 81.3366 | 64.1561 | 2142.7569
2039-02-20 15:01 | 7772.28 | 2.539 | 81.6927 | 64.1561 | 2277.8304
2039-02-21 16:01 | 9580.26 | 3.1559 | 81.8478 | 64.1561 | 2807.697
2039-02-22 17:01 | 7794.38 | 2.4998 | 82.5739 | 64.1561 | 2284.3073
2039-02-23 18:01 | 5685.06 | 1.7797 | 82.9638 | 64.1561 | 1666.1266
2039-02-24 19:01 | 4123.76 | 1.3149 | 82.6044 | 64.1561 | 1208.5548
2039-02-25 20:01 | 3216.38 | 1.0193 | 82.5064 | 64.1561 | 942.6279
2039-02-26 21:01 | 3138.25 | 1 | 89.3335 | 64.1561 | 919.7303
2039-02-27 22:01 | 3060.71 | 1 | 69.1769 | 64.1561 | 897.0056
2039-02-28 23:01 | -799.345 | 2.5623 | 68.6224 | 64.1561 | -234.2649
2039-03-02 00:01 | -1318.42 | 3.7312 | 67.9893 | 64.1561 | -386.3908
2039-03-03 01:01 | -1614.66 | 4.4114 | 67.621 | 64.1561 | -473.2101
2039-03-04 02:01 | -1911.42 | 5.1338 | 67.3901 | 64.1561 | -560.1819
2039-03-05 03:01 | -2201.97 | 5.8422 | 67.1605 | 64.1561 | -645.3337
2039-03-06 04:01 | -2293.59 | 6.037 | 66.9128 | 64.1561 | -672.1849
2039-03-07 05:01 | -2431.95 | 6.393 | 66.7779 | 64.1561 | -712.7342
2039-03-08 06:01 | -1732.1 | 4.5335 | 66.6571 | 64.1561 | -507.6284
2039-03-09 07:01 | -899.7 | 2.5274 | 66.7437 | 64.1561 | -263.676
2039-03-10 08:01 | -223.086 | 0.94979 | 67.2805 | 64.1561 | -65.3801
2039-03-11 09:01 | 2592.01 | 1 | 67.6616 | 64.1561 | 759.6431
2039-03-12 10:01 | 4271.01 | 1.3509 | 80.9831 | 64.1561 | 1251.7095
2039-03-13 11:01 | 6447.07 | 2.0908 | 81.0292 | 64.1561 | 1889.4497
2039-03-14 12:01 | 7831.18 | 2.5481 | 81.4383 | 64.1561 | 2295.0923
2039-03-15 13:01 | 8930.09 | 2.8537 | 82.0943 | 64.1561 | 2617.151
2039-03-16 14:01 | 9708.27 | 3.1638 | 82.2718 | 64.1561 | 2845.2131
2039-03-17 15:01 | 10030.7 | 3.2493 | 82.7049 | 64.1561 | 2939.708
2039-03-18 16:01 | 11938.6 | 3.8967 | 82.8941 | 64.1561 | 3498.8583
2039-03-19 17:01 | 9788.37 | 3.1161 | 83.644 | 64.1561 | 2868.6881
2039-03-20 18:01 | 7937.35 | 2.4227 | 84.2578 | 64.1561 | 2326.2077
2039-03-21 19:01 | 6414.24 | 1.94 | 84.2793 | 64.1561 | 1879.8282
2039-03-22 20:01 | 5154.4 | 1.5538 | 84.1859 | 64.1561 | 1510.6055
2039-03-23 21:01 | 3885.11 | 1.2332 | 83.355 | 64.1561 | 1138.6133
2039-03-24 22:01 | 3072.69 | 1 | 83.4422 | 64.1561 | 900.5165
2039-03-25 23:01 | 2411.51 | 1 | 69.9755 | 64.1561 | 706.7438
2039-03-27 00:01 | -98.4345 | 0.82124 | 69.8888 | 64.1561 | -28.8483
2039-03-28 01:01 | -334.292 | 1.3517 | 68.9826 | 64.1561 | -97.9713
2039-03-29 02:01 | -573.758 | 1.9192 | 68.5034 | 64.1561 | -168.1519
2039-03-30 03:01 | -622.274 | 2.0019 | 68.2587 | 64.1561 | -182.3705
2039-03-31 04:01 | -631.938 | 2.0239 | 68.0665 | 64.1561 | -185.2027
2039-04-01 05:01 | -291.891 | 1.1586 | 68.1571 | 64.1561 | -85.5448
2039-04-02 06:01 | -403.361 | 1.5123 | 68.0542 | 64.1561 | -118.2134
2039-04-03 07:01 | 1405.88 | 1 | 68.7007 | 64.1561 | 412.0228
2039-04-04 08:01 | 3125.87 | 1 | 68.4417 | 64.1561 | 916.1021
2039-04-05 09:01 | 4145.08 | 1.306 | 81.8766 | 64.1561 | 1214.803
2039-04-06 10:01 | 6955.78 | 2.2955 | 81.5081 | 64.1561 | 2038.5379
2039-04-07 11:01 | 8704.76 | 2.8802 | 81.9086 | 64.1561 | 2551.1133
2039-04-08 12:01 | 10100.4 | 3.3402 | 82.3963 | 64.1561 | 2960.135
2039-04-09 13:01 | 10806.3 | 3.5093 | 83.0507 | 64.1561 | 3167.0139
2039-04-10 14:01 | 11791.1 | 3.8277 | 83.4185 | 64.1561 | 3455.6303
2039-04-11 15:01 | 13101.8 | 4.246 | 83.8164 | 64.1561 | 3839.7585
2039-04-12 16:01 | 12697 | 4.0639 | 84.3648 | 64.1561 | 3721.1234
2039-04-13 17:01 | 11257.9 | 3.5668 | 84.7339 | 64.1561 | 3299.3648
2039-04-14 18:01 | 9050.9 | 2.8068 | 85.0583 | 64.1561 | 2652.5569
2039-04-15 19:01 | 7721.33 | 2.3806 | 84.998 | 64.1561 | 2262.8984
2039-04-16 20:01 | 5563.07 | 1.6191 | 85.5918 | 64.1561 | 1630.3749
2039-04-17 21:01 | 4241.85 | 1.3177 | 84.4362 | 64.1561 | 1243.1635
2039-04-18 22:01 | 3158.46 | 1 | 70.7715 | 64.1561 | 925.6533
2039-04-19 23:01 | 3109.3 | 1 | 70.4795 | 64.1561 | 911.2459
2039-04-21 00:01 | 2984.26 | 1 | 70.3274 | 64.1561 | 874.6003
2039-04-22 01:01 | 185.496 | 1 | 70.8544 | 64.1561 | 54.3635
2039-04-23 02:01 | -152.828 | 0.92209 | 69.8294 | 64.1561 | -44.7895
2039-04-24 03:01 | -108.604 | 0.7765 | 69.6222 | 64.1561 | -31.8287
2039-04-25 04:01 | -31.3307 | 0.59629 | 70.017 | 64.1561 | -9.1821
2039-04-26 05:01 | 242.124 | 1 | 69.7784 | 64.1561 | 70.9595
2039-04-27 06:01 | 2833.19 | 1 | 69.055 | 64.1561 | 830.326
2039-04-28 07:01 | 3160.01 | 1 | 69.2062 | 64.1561 | 926.1075
2039-04-29 08:01 | 3217.31 | 1 | 88.2144 | 64.1561 | 942.9005
2039-04-30 09:01 | 5297.08 | 1.6895 | 82.4151 | 64.1561 | 1552.4209
2039-05-01 10:01 | 7866.95 | 2.6467 | 82.056 | 64.1561 | 2305.5755
2039-05-02 11:01 | 10292.7 | 3.4233 | 82.631 | 64.1561 | 3016.4926
2039-05-03 12:01 | 11515.9 | 3.852 | 83.0427 | 64.1561 | 3374.9771
2039-05-04 13:01 | 12864.6 | 4.191 | 83.797 | 64.1561 | 3770.2421
2039-05-05 14:01 | 13137.3 | 4.2826 | 84.2532 | 64.1561 | 3850.1626
2039-05-06 15:01 | 14568.9 | 4.7539 | 84.5871 | 64.1561 | 4269.7231
2039-05-07 16:01 | 13935 | 4.5078 | 85.0998 | 64.1561 | 4083.9454
2039-05-08 17:01 | 12610.6 | 3.9253 | 85.8042 | 64.1561 | 3695.802
2039-05-09 18:01 | 10166.7 | 3.1229 | 86.0138 | 64.1561 | 2979.5656
2039-05-10 19:01 | 8823.91 | 2.6724 | 86.0203 | 64.1561 | 2586.0327
2039-05-11 20:01 | 6438.95 | 1.8881 | 86.2836 | 64.1561 | 1887.07
2039-05-12 21:01 | 5247.03 | 1.6116 | 85.3448 | 64.1561 | 1537.7527
2039-05-13 22:01 | 3277.94 | 1 | 86.8532 | 64.1561 | 960.6694
2039-05-14 23:01 | 3146.89 | 1 | 71.1328 | 64.1561 | 922.2624
2039-05-16 00:01 | 3055.38 | 1 | 70.8966 | 64.1561 | 895.4435
2039-05-17 01:01 | 2899.06 | 1 | 70.7506 | 64.1561 | 849.6306
2039-05-18 02:01 | 1023.95 | 1 | 71.0512 | 64.1561 | 300.0901
2039-05-19 03:01 | 1337.32 | 1 | 70.6342 | 64.1561 | 391.9298
2039-05-20 04:01 | 2359.39 | 1 | 70.2206 | 64.1561 | 691.469
2039-05-21 05:01 | 2918.29 | 1 | 70.0861 | 64.1561 | 855.2664
2039-05-22 06:01 | 2996.44 | 1 | 70.0848 | 64.1561 | 878.1699
2039-05-23 07:01 | 3202.28 | 1 | 70.0135 | 64.1561 | 938.4956
2039-05-24 08:01 | 3234.94 | 1 | 87.5138 | 64.1561 | 948.0673
2039-05-25 09:01 | 5476.85 | 1.692 | 83.4617 | 64.1561 | 1605.1063
2039-05-26 10:01 | 7863.14 | 2.6925 | 82.4622 | 64.1561 | 2304.4589
2039-05-27 11:01 | 9933.63 | 3.3442 | 83.0271 | 64.1561 | 2911.2596
2039-05-28 12:01 | 11421 | 3.7334 | 83.7897 | 64.1561 | 3347.1647
2039-05-29 13:01 | 12102.9 | 3.9197 | 84.3108 | 64.1561 | 3547.0099
2039-05-30 14:01 | 12303.5 | 4.0503 | 84.4865 | 64.1561 | 3605.7999
2039-05-31 15:01 | 12728.6 | 4.3902 | 84.207 | 64.1561 | 3730.3844
2039-06-01 16:01 | 11612.1 | 4.0522 | 84.3082 | 64.1561 | 3403.1706
2039-06-02 17:01 | 10248.6 | 3.3761 | 85.0205 | 64.1561 | 3003.5682
2039-06-03 18:01 | 7311.74 | 2.3965 | 85.0099 | 64.1561 | 2142.8595
2039-06-04 19:01 | 5629.69 | 1.8582 | 84.6135 | 64.1561 | 1649.8993
2039-06-05 20:01 | 3000.38 | 1 | 84.5439 | 64.1561 | 879.3246
2039-06-06 21:01 | 3013.57 | 1 | 71.2723 | 64.1561 | 883.1902
2039-06-07 22:01 | 0 | 0 | 71.7116 | 64.1561 | 0
2039-06-08 23:01 | -612.045 | 1.9959 | 69.9695 | 64.1561 | -179.3727
2039-06-10 00:01 | -1095.88 | 3.1572 | 69.3869 | 64.1561 | -321.1707
2039-06-11 01:01 | -1517.55 | 4.1434 | 68.9818 | 64.1561 | -444.75
2039-06-12 02:01 | -1808.72 | 4.8173 | 68.6662 | 64.1561 | -530.0835
2039-06-13 03:01 | -1851.97 | 4.8871 | 68.3675 | 64.1561 | -542.7588
2039-06-14 04:01 | -1953.86 | 5.1546 | 68.166 | 64.1561 | -572.6198
2039-06-15 05:01 | -1801.51 | 4.7499 | 67.983 | 64.1561 | -527.9705
2039-06-16 06:01 | -2132.23 | 5.6461 | 67.8618 | 64.1561 | -624.8949
2039-06-17 07:01 | -1450.08 | 3.8162 | 67.7006 | 64.1561 | -424.9765
2039-06-18 08:01 | -640.942 | 1.8975 | 67.8322 | 64.1561 | -187.8416
2039-06-19 09:01 | 2630.2 | 1 | 68.5462 | 64.1561 | 770.8355
2039-06-20 10:01 | 3878.17 | 1.2448 | 81.7177 | 64.1561 | 1136.5794
2039-06-21 11:01 | 6053.73 | 1.9338 | 82.0316 | 64.1561 | 1774.1731
2039-06-22 12:01 | 7279.73 | 2.3807 | 82.125 | 64.1561 | 2133.4783
2039-06-23 13:01 | 8207.1 | 2.6811 | 82.5004 | 64.1561 | 2405.2636
2039-06-24 14:01 | 8864.93 | 2.9253 | 82.7123 | 64.1561 | 2598.0545
2039-06-25 15:01 | 9852.39 | 3.3085 | 82.7663 | 64.1561 | 2887.4505
2039-06-26 16:01 | 9268.44 | 3.0949 | 83.1328 | 64.1561 | 2716.3116
2039-06-27 17:01 | 7611.13 | 2.5189 | 83.379 | 64.1561 | 2230.602
2039-06-28 18:01 | 4635.78 | 1.494 | 83.6561 | 64.1561 | 1358.613
2039-06-29 19:01 | 3078.33 | 1 | 84.4846 | 64.1561 | 902.1695
2039-06-30 20:01 | 2905.12 | 1 | 70.2435 | 64.1561 | 851.4066
2039-07-01 21:01 | -286.452 | 1.2788 | 69.867 | 64.1561 | -83.9508
2039-07-02 22:01 | -1479.52 | 4.1961 | 68.8798 | 64.1561 | -433.6045
2039-07-03 23:01 | -2385.35 | 6.3148 | 68.3328 | 64.1561 | -699.0771
2039-07-05 00:01 | -2930.14 | 6.4446 | 67.6774 | 64.1561 | -858.7393
2039-07-06 01:01 | -3319.73 | 6.4446 | 67.1247 | 64.1561 | -972.9168
2039-07-07 02:01 | -3579.42 | 6.4446 | 66.6614 | 64.1561 | -1049.0244
2039-07-08 03:01 | -3721.39 | 6.4446 | 66.3247 | 64.1561 | -1090.6317
2039-07-09 04:01 | -3839.65 | 6.4446 | 66.0359 | 64.1561 | -1125.2903
2039-07-10 05:01 | -4024.7 | 6.4446 | 65.7374 | 64.1561 | -1179.5231
2039-07-11 06:01 | -3538.02 | 6.4446 | 65.8752 | 64.1561 | -1036.8913
2039-07-12 07:01 | -2069.49 | 5.4675 | 66.4668 | 64.1561 | -606.5076
2039-07-13 08:01 | -1758.67 | 4.6904 | 66.5569 | 64.1561 | -515.4153
2039-07-14 09:01 | -501.214 | 1.4827 | 66.7365 | 64.1561 | -146.8913
2039-07-15 10:01 | 2875.75 | 1 | 87.1864 | 64.1561 | 842.7991
2039-07-16 11:01 | 4234.57 | 1.3891 | 80.515 | 64.1561 | 1241.03
2039-07-17 12:01 | 5403.9 | 1.7574 | 81.0007 | 64.1561 | 1583.7268
2039-07-18 13:01 | 6496.81 | 2.1203 | 81.2686 | 64.1561 | 1904.0271
2039-07-19 14:01 | 7434.24 | 2.4289 | 81.5883 | 64.1561 | 2178.7607
2039-07-20 15:01 | 7494.16 | 2.452 | 81.8962 | 64.1561 | 2196.3215
2039-07-21 16:01 | 9196.38 | 3.015 | 82.0664 | 64.1561 | 2695.1929
2039-07-22 17:01 | 6907.88 | 2.2529 | 82.4886 | 64.1561 | 2024.4998
2039-07-23 18:01 | 4563.27 | 1.4406 | 82.901 | 64.1561 | 1337.3624
2039-07-24 19:01 | 3060.39 | 1 | 84.6717 | 64.1561 | 896.9118
2039-07-25 20:01 | 3079.08 | 1 | 69.3462 | 64.1561 | 902.3893
2039-07-26 21:01 | 2848.71 | 1 | 69.3292 | 64.1561 | 834.8745
2039-07-27 22:01 | 0 | 0 | 69.9 | 64.1561 | 0
2039-07-28 23:01 | -1421.24 | 4.0351 | 68.1355 | 64.1561 | -416.5243
2039-07-30 00:01 | -2015.35 | 5.4173 | 67.6897 | 64.1561 | -590.6408
2039-07-31 01:01 | -2301.35 | 6.0596 | 67.3964 | 64.1561 | -674.4591
2039-08-01 02:01 | -2550.32 | 6.4446 | 67.1006 | 64.1561 | -747.425
2039-08-02 03:01 | -3009.94 | 6.4446 | 66.5949 | 64.1561 | -882.1263
2039-08-03 04:01 | -3133.6 | 6.4446 | 66.2992 | 64.1561 | -918.3675
2039-08-04 05:01 | -3226.12 | 6.4446 | 66.0859 | 64.1561 | -945.4824
2039-08-05 06:01 | -2474.2 | 6.4446 | 66.4215 | 64.1561 | -725.1164
2039-08-06 07:01 | -1514.95 | 3.9735 | 66.4125 | 64.1561 | -443.988
2039-08-07 08:01 | -1061.96 | 3.0031 | 66.5801 | 64.1561 | -311.2298
2039-08-08 09:01 | 1182.06 | 1 | 67.7218 | 64.1561 | 346.4276
2039-08-09 10:01 | 3154.65 | 1 | 82.5425 | 64.1561 | 924.5367
2039-08-10 11:01 | 5002.32 | 1.5661 | 81.0871 | 64.1561 | 1466.0353
2039-08-11 12:01 | 5966.18 | 1.9554 | 80.9168 | 64.1561 | 1748.5148
2039-08-12 13:01 | 6634.53 | 2.1569 | 81.3434 | 64.1561 | 1944.3888
2039-08-13 14:01 | 7457.94 | 2.4137 | 81.689 | 64.1561 | 2185.7065
2039-08-14 15:01 | 7760.72 | 2.506 | 82.0008 | 64.1561 | 2274.4425
2039-08-15 16:01 | 9476.41 | 3.0887 | 82.1022 | 64.1561 | 2777.2616
2039-08-16 17:01 | 7212.39 | 2.334 | 82.555 | 64.1561 | 2113.7429
2039-08-17 18:01 | 5343.39 | 1.6808 | 82.9177 | 64.1561 | 1565.993
2039-08-18 19:01 | 3836.12 | 1.1979 | 82.8588 | 64.1561 | 1124.2558
2039-08-19 20:01 | 3058.88 | 1 | 85.5143 | 64.1561 | 896.4692
2039-08-20 21:01 | 3064.85 | 1 | 69.2549 | 64.1561 | 898.2189
2039-08-21 22:01 | 3023.44 | 1 | 69.1526 | 64.1561 | 886.0828
2039-08-22 23:01 | -741.681 | 2.4274 | 68.6143 | 64.1561 | -217.3652
2039-08-24 00:01 | -1262.43 | 3.5994 | 67.9777 | 64.1561 | -369.9817
2039-08-25 01:01 | -1605.25 | 4.399 | 67.6076 | 64.1561 | -470.4523
2039-08-26 02:01 | -1727.97 | 4.6597 | 67.3741 | 64.1561 | -506.418
2039-08-27 03:01 | -1691.58 | 4.5533 | 67.1773 | 64.1561 | -495.7532
2039-08-28 04:01 | -1815.69 | 4.8962 | 66.9906 | 64.1561 | -532.1262
2039-08-29 05:01 | -1419.34 | 3.8393 | 66.8853 | 64.1561 | -415.9675
2039-08-30 06:01 | -1572.24 | 4.3303 | 66.875 | 64.1561 | -460.7781
2039-08-31 07:01 | -1046.59 | 2.9232 | 66.8356 | 64.1561 | -306.7253
2039-09-01 08:01 | -473.463 | 1.5606 | 67.0532 | 64.1561 | -138.7583
2039-09-02 09:01 | 2647.56 | 1 | 85.4709 | 64.1561 | 775.9232
2039-09-03 10:01 | 5269.83 | 1.5516 | 81.86 | 64.1561 | 1544.4347
2039-09-04 11:01 | 7716.06 | 2.5373 | 80.9433 | 64.1561 | 2261.354
2039-09-05 12:01 | 8100.68 | 2.6515 | 81.5337 | 64.1561 | 2374.075
2039-09-06 13:01 | 9834.77 | 3.3423 | 81.4617 | 64.1561 | 2882.2866
2039-09-07 14:01 | 10412.9 | 3.428 | 82.2979 | 64.1561 | 3051.7197
2039-09-08 15:01 | 11420.2 | 3.7366 | 82.7436 | 64.1561 | 3346.9302
2039-09-09 16:01 | 10293 | 3.2881 | 83.3884 | 64.1561 | 3016.5805
2039-09-10 17:01 | 9244.62 | 2.9248 | 83.6381 | 64.1561 | 2709.3307
2039-09-11 18:01 | 7123.85 | 2.1967 | 84.0133 | 64.1561 | 2087.7943
2039-09-12 19:01 | 5993.12 | 1.8267 | 84.0286 | 64.1561 | 1756.4101
2039-09-13 20:01 | 3672.26 | 1.1266 | 83.8097 | 64.1561 | 1076.2332
2039-09-14 21:01 | 3100.66 | 1 | 89.7917 | 64.1561 | 908.7137
2039-09-15 22:01 | 0 | 0 | 70.4779 | 64.1561 | 0
2039-09-16 23:01 | -410.224 | 1.2798 | 68.7276 | 64.1561 | -120.2248
2039-09-18 00:01 | -602.916 | 1.9986 | 68.4664 | 64.1561 | -176.6972
2039-09-19 01:01 | -867.307 | 2.6212 | 68.1112 | 64.1561 | -254.1826
2039-09-20 02:01 | -1051.4 | 3.048 | 67.8465 | 64.1561 | -308.1349
2039-09-21 03:01 | -973.886 | 2.8205 | 67.6344 | 64.1561 | -285.4178
2039-09-22 04:01 | -976.841 | 2.8507 | 67.5301 | 64.1561 | -286.2838
2039-09-23 05:01 | -661.847 | 2.0413 | 67.5041 | 64.1561 | -193.9682
2039-09-24 06:01 | -675.142 | 2.1438 | 67.4996 | 64.1561 | -197.8646
2039-09-25 07:01 | -170.609 | 0.84369 | 67.8923 | 64.1561 | -50.0006
2039-09-26 08:01 | 2193.39 | 1 | 68.1833 | 64.1561 | 642.8192
2039-09-27 09:01 | 3159.28 | 1.0348 | 80.9122 | 64.1561 | 925.8936
2039-09-28 10:01 | 6249.23 | 2.0959 | 80.8362 | 64.1561 | 1831.4685
2039-09-29 11:01 | 7320.9 | 2.4563 | 81.2829 | 64.1561 | 2145.544
2039-09-30 12:01 | 8616.7 | 2.9325 | 81.5122 | 64.1561 | 2525.3055
2039-10-01 13:01 | 8782.72 | 2.9099 | 82.2118 | 64.1561 | 2573.9611
2039-10-02 14:01 | 8630.11 | 2.7795 | 82.8147 | 64.1561 | 2529.2356
2039-10-03 15:01 | 9913.42 | 3.2355 | 82.826 | 64.1561 | 2905.3366
2039-10-04 16:01 | 9821.54 | 3.1355 | 83.36 | 64.1561 | 2878.4092
2039-10-05 17:01 | 8876.1 | 2.826 | 83.5853 | 64.1561 | 2601.3281
2039-10-06 18:01 | 7648.86 | 2.3355 | 84.1578 | 64.1561 | 2241.6596
2039-10-07 19:01 | 6583.38 | 2.0182 | 84.0656 | 64.1561 | 1929.3982
2039-10-08 20:01 | 4542.17 | 1.3712 | 84.1846 | 64.1561 | 1331.1786
2039-10-09 21:01 | 3410.79 | 1.0842 | 83.2783 | 64.1561 | 999.6039
2039-10-10 22:01 | 3073.63 | 1 | 69.9788 | 64.1561 | 900.792
2039-10-11 23:01 | 3026.28 | 1 | 69.819 | 64.1561 | 886.9151
2039-10-13 00:01 | 3198.66 | 1 | 69.6614 | 64.1561 | 937.4347
2039-10-14 01:01 | 548.443 | 1 | 70.2313 | 64.1561 | 160.7328
2039-10-15 02:01 | -69.1892 | 0.73161 | 69.6608 | 64.1561 | -20.2774
2039-10-16 03:01 | 0 | 0 | 69.7599 | 64.1561 | 0
2039-10-17 04:01 | 236.615 | 1 | 69.5528 | 64.1561 | 69.345
2039-10-18 05:01 | 1891.39 | 1 | 69.0559 | 64.1561 | 554.3117
2039-10-19 06:01 | 2760.73 | 1 | 68.9295 | 64.1561 | 809.0901
2039-10-20 07:01 | 3065.58 | 1 | 69.0052 | 64.1561 | 898.4328
2039-10-21 08:01 | 3213.64 | 1 | 69.0824 | 64.1561 | 941.8249
2039-10-22 09:01 | 3327.82 | 1.0223 | 82.6843 | 64.1561 | 975.2878
2039-10-23 10:01 | 6218.42 | 2.0044 | 82.1018 | 64.1561 | 1822.439
2039-10-24 11:01 | 7761.28 | 2.5851 | 82.0346 | 64.1561 | 2274.6066
2039-10-25 12:01 | 8085.57 | 2.6793 | 82.4297 | 64.1561 | 2369.6467
2039-10-26 13:01 | 7934.78 | 2.5671 | 82.9444 | 64.1561 | 2325.4545
2039-10-27 14:01 | 8011.47 | 2.5528 | 83.281 | 64.1561 | 2347.9301
2039-10-28 15:01 | 9802.48 | 3.2671 | 82.882 | 64.1561 | 2872.8233
2039-10-29 16:01 | 9397.6 | 3.0413 | 83.5286 | 64.1561 | 2754.1647
2039-10-30 17:01 | 9135.54 | 2.9367 | 83.7367 | 64.1561 | 2677.3625
2039-10-31 18:01 | 8168.25 | 2.5382 | 84.2252 | 64.1561 | 2393.8778
2039-11-01 19:01 | 7589.23 | 2.3108 | 84.4752 | 64.1561 | 2224.1838
2039-11-02 20:01 | 5939.9 | 1.7495 | 84.9064 | 64.1561 | 1740.8128
2039-11-03 21:01 | 5293.88 | 1.5813 | 84.5559 | 64.1561 | 1551.4831
2039-11-04 22:01 | 3152.87 | 1 | 83.9127 | 64.1561 | 924.015
2039-11-05 23:01 | 3109.69 | 1 | 88.8849 | 64.1561 | 911.3602
2039-11-07 00:01 | 3202.32 | 1 | 70.0416 | 64.1561 | 938.5073
2039-11-08 01:01 | 3205.91 | 1 | 69.9545 | 64.1561 | 939.5595
2039-11-09 02:01 | 3228.79 | 1 | 69.8889 | 64.1561 | 946.2649
2039-11-10 03:01 | 3193.11 | 1 | 69.8324 | 64.1561 | 935.8082
2039-11-11 04:01 | 3197.7 | 1 | 69.8044 | 64.1561 | 937.1534
2039-11-12 05:01 | 3197.42 | 1 | 84.3313 | 64.1561 | 937.0713
2039-11-13 06:01 | 3140.17 | 1 | 84.5609 | 64.1561 | 920.293
2039-11-14 07:01 | 3229.13 | 1.0017 | 83.0678 | 64.1561 | 946.3646
2039-11-15 08:01 | 3199.53 | 1 | 86.4503 | 64.1561 | 937.6897
2039-11-16 09:01 | 3215.46 | 1 | 84.6692 | 64.1561 | 942.3583
2039-11-17 10:01 | 4682.25 | 1.4619 | 82.9246 | 64.1561 | 1372.232
2039-11-18 11:01 | 5910.8 | 1.86 | 82.9545 | 64.1561 | 1732.2845
2039-11-19 12:01 | 6374.01 | 2.1507 | 82.3078 | 64.1561 | 1868.0379
2039-11-20 13:01 | 7044.38 | 2.2938 | 82.868 | 64.1561 | 2064.504
2039-11-21 14:01 | 7480.32 | 2.4859 | 82.7825 | 64.1561 | 2192.2654
2039-11-22 15:01 | 9362.71 | 3.1012 | 82.9671 | 64.1561 | 2743.9394
2039-11-23 16:01 | 9572.26 | 3.15 | 83.3407 | 64.1561 | 2805.3525
2039-11-24 17:01 | 9379.2 | 3.0698 | 83.6095 | 64.1561 | 2748.7722
2039-11-25 18:01 | 8551.78 | 2.6416 | 84.4451 | 64.1561 | 2506.2793
2039-11-26 19:01 | 8031.06 | 2.4226 | 84.7745 | 64.1561 | 2353.6713
2039-11-27 20:01 | 6342.08 | 1.8471 | 85.2605 | 64.1561 | 1858.6802
2039-11-28 21:01 | 5560.9 | 1.687 | 84.5719 | 64.1561 | 1629.7389
2039-11-29 22:01 | 3559.28 | 1.0741 | 84.4936 | 64.1561 | 1043.122
2039-11-30 23:01 | 3248.22 | 1 | 85.8607 | 64.1561 | 951.9593
2039-12-02 00:01 | 3163.36 | 1 | 86.9308 | 64.1561 | 927.0893
2039-12-03 01:01 | 3125.28 | 1 | 87.6759 | 64.1561 | 915.9292
2039-12-04 02:01 | 3056.21 | 1 | 87.9232 | 64.1561 | 895.6867
2039-12-05 03:01 | 3085.35 | 1 | 85.0305 | 64.1561 | 904.2268
2039-12-06 04:01 | 3065.94 | 1 | 83.655 | 64.1561 | 898.5383
2039-12-07 05:01 | 3525.4 | 1.1824 | 82.2578 | 64.1561 | 1033.1928
2039-12-08 06:01 | 3039.7 | 1.0388 | 82.0496 | 64.1561 | 890.8481
2039-12-09 07:01 | 3103.93 | 1 | 82.9668 | 64.1561 | 909.6721
2039-12-10 08:01 | 3172.4 | 1 | 69.7477 | 64.1561 | 929.7387
2039-12-11 09:01 | 3110.88 | 1 | 85.7964 | 64.1561 | 911.7089
2039-12-12 10:01 | 4125.72 | 1.3404 | 82.4855 | 64.1561 | 1209.1292
2039-12-13 11:01 | 5386.12 | 1.8358 | 81.9923 | 64.1561 | 1578.516
2039-12-14 12:01 | 5286.6 | 1.6956 | 82.8837 | 64.1561 | 1549.3495
2039-12-15 13:01 | 6014.38 | 1.9886 | 82.5793 | 64.1561 | 1762.6408
2039-12-16 14:01 | 8472.2 | 3.0797 | 81.6158 | 64.1561 | 2482.9567
2039-12-17 15:01 | 9103.65 | 3.0903 | 82.7235 | 64.1561 | 2668.0164
2039-12-18 16:01 | 9189.26 | 3.0093 | 83.4066 | 64.1561 | 2693.1063
2039-12-19 17:01 | 8139.84 | 2.5796 | 83.9554 | 64.1561 | 2385.5516
2039-12-20 18:01 | 6535.99 | 2.0027 | 84.4074 | 64.1561 | 1915.5096
2039-12-21 19:01 | 5309.55 | 1.6195 | 84.3508 | 64.1561 | 1556.0755
2039-12-22 20:01 | 3137.1 | 1 | 85.9393 | 64.1561 | 919.3933
2039-12-23 21:01 | 3126.82 | 1 | 70.2841 | 64.1561 | 916.3805
2039-12-24 22:01 | 0 | 0 | 70.8525 | 64.1561 | 0
2039-12-25 23:01 | -772.35 | 2.4079 | 69.13 | 64.1561 | -226.3534
2039-12-27 00:01 | -1228.91 | 3.4886 | 68.6338 | 64.1561 | -360.158
2039-12-28 01:01 | -1655.28 | 4.5012 | 68.2921 | 64.1561 | -485.1147
2039-12-29 02:01 | -1984.32 | 5.2773 | 67.9923 | 64.1561 | -581.5468
2039-12-30 03:01 | -2324.24 | 6.1095 | 67.6976 | 64.1561 | -681.1675
2039-12-31 04:01 | -2752.33 | 6.4446 | 67.2851 | 64.1561 | -806.6283
2040-01-01 05:01 | -2899.55 | 6.4446 | 66.9636 | 64.1561 | -849.7742
2040-01-02 06:01 | -2544.22 | 6.4446 | 66.9864 | 64.1561 | -745.6373
2040-01-03 07:01 | -2030.58 | 5.297 | 66.9151 | 64.1561 | -595.1043
2040-01-04 08:01 | -1524.17 | 4.0757 | 66.9048 | 64.1561 | -446.6901
2040-01-05 09:01 | -416.759 | 1.3137 | 67.1047 | 64.1561 | -122.14
2040-01-06 10:01 | 2885.81 | 1 | 67.7519 | 64.1561 | 845.7474
2040-01-07 11:01 | 3160.87 | 1.0309 | 80.8512 | 64.1561 | 926.3596
2040-01-08 12:01 | 3150.2 | 1.0231 | 81.1108 | 64.1561 | 923.2325
2040-01-09 13:01 | 3816.08 | 1.2177 | 81.4384 | 64.1561 | 1118.3826
2040-01-10 14:01 | 4560.67 | 1.4606 | 81.5557 | 64.1561 | 1336.6004
2040-01-11 15:01 | 3918.9 | 1.2764 | 81.5437 | 64.1561 | 1148.5162
2040-01-12 16:01 | 5933.9 | 1.9354 | 81.525 | 64.1561 | 1739.0544
2040-01-13 17:01 | 3835.59 | 1.2432 | 81.8531 | 64.1561 | 1124.1005
2040-01-14 18:01 | 3070.64 | 1 | 69 | 64.1561 | 899.9158
2040-01-15 19:01 | 2958.51 | 1 | 68.9187 | 64.1561 | 867.0537
2040-01-16 20:01 | -82.6675 | 0.78155 | 69.1803 | 64.1561 | -24.2275
2040-01-17 21:01 | -583.435 | 1.9949 | 68.1066 | 64.1561 | -170.9879
2040-01-18 22:01 | -848.005 | 2.5856 | 67.6675 | 64.1561 | -248.5257
2040-01-19 23:01 | -2245.97 | 6.1612 | 67.3511 | 64.1561 | -658.2288
2040-01-21 00:01 | -2927.63 | 6.4446 | 66.7089 | 64.1561 | -858.0037
2040-01-22 01:01 | -3021.61 | 6.4446 | 66.3574 | 64.1561 | -885.5465
2040-01-23 02:01 | -3444.69 | 6.4446 | 65.9217 | 64.1561 | -1009.539
2040-01-24 03:01 | -3690.23 | 6.4446 | 65.5865 | 64.1561 | -1081.4997
2040-01-25 04:01 | -3746.03 | 6.4446 | 65.3489 | 64.1561 | -1097.853
2040-01-26 05:01 | -3970.18 | 6.4446 | 65.071 | 64.1561 | -1163.5449
2040-01-27 06:01 | -3009.65 | 6.4446 | 65.5137 | 64.1561 | -882.0413
2040-01-28 07:01 | -2302.77 | 6.1109 | 65.8468 | 64.1561 | -674.8753
2040-01-29 08:01 | -1743.11 | 4.6288 | 65.9025 | 64.1561 | -510.8551
2040-01-30 09:01 | -568.631 | 1.6739 | 66.1057 | 64.1561 | -166.6493
2040-01-31 10:01 | 2577.44 | 1 | 66.9505 | 64.1561 | 755.3731
2040-02-01 11:01 | 4285.48 | 1.3832 | 80.1257 | 64.1561 | 1255.9502
2040-02-02 12:01 | 5626.87 | 1.8299 | 80.4261 | 64.1561 | 1649.0728
2040-02-03 13:01 | 6176.21 | 1.9907 | 80.9189 | 64.1561 | 1810.0685
2040-02-04 14:01 | 7474.43 | 2.4554 | 81.0055 | 64.1561 | 2190.5392
2040-02-05 15:01 | 7888.57 | 2.5635 | 81.5163 | 64.1561 | 2311.9117
2040-02-06 16:01 | 9374.53 | 3.0396 | 81.821 | 64.1561 | 2747.4035
2040-02-07 17:01 | 6838.74 | 2.2051 | 82.2746 | 64.1561 | 2004.2368
2040-02-08 18:01 | 5260.86 | 1.6517 | 82.5914 | 64.1561 | 1541.8059
2040-02-09 19:01 | 3212.74 | 1.0064 | 82.4954 | 64.1561 | 941.5611
2040-02-10 20:01 | 3144.76 | 1 | 86.6453 | 64.1561 | 921.6382
2040-02-11 21:01 | 3051.04 | 1 | 68.9613 | 64.1561 | 894.1716
2040-02-12 22:01 | 3014.27 | 1 | 68.879 | 64.1561 | 883.3953
2040-02-13 23:01 | -702.068 | 2.3454 | 68.374 | 64.1561 | -205.7558
2040-02-15 00:01 | -1066.28 | 3.1126 | 67.7556 | 64.1561 | -312.4958
2040-02-16 01:01 | -1343.48 | 3.7738 | 67.4249 | 64.1561 | -393.7351
2040-02-17 02:01 | -1265.78 | 3.525 | 67.2184 | 64.1561 | -370.9635
2040-02-18 03:01 | -1397.5 | 3.8946 | 67.0582 | 64.1561 | -409.5668
2040-02-19 04:01 | -1336.28 | 3.7121 | 66.869 | 64.1561 | -391.625
2040-02-20 05:01 | -770.039 | 2.2605 | 66.8659 | 64.1561 | -225.6762
2040-02-21 06:01 | -907.008 | 2.738 | 66.907 | 64.1561 | -265.8178
2040-02-22 07:01 | -654.47 | 2.0452 | 66.9291 | 64.1561 | -191.8062
2040-02-23 08:01 | -680.936 | 2.1717 | 66.9471 | 64.1561 | -199.5626
2040-02-24 09:01 | 1957.83 | 1 | 67.6836 | 64.1561 | 573.7833
2040-02-25 10:01 | 4249.23 | 1.4201 | 80.1123 | 64.1561 | 1245.3264
2040-02-26 11:01 | 6403.35 | 2.1975 | 80.165 | 64.1561 | 1876.6366
2040-02-27 12:01 | 7891.43 | 2.6292 | 80.9539 | 64.1561 | 2312.7498
2040-02-28 13:01 | 8771.11 | 2.9068 | 81.4576 | 64.1561 | 2570.5586
2040-02-29 14:01 | 9843.29 | 3.2172 | 82.0221 | 64.1561 | 2884.7835
2040-03-01 15:01 | 10933.2 | 3.5669 | 82.4295 | 64.1561 | 3204.2046
2040-03-02 16:01 | 10191.7 | 3.291 | 82.9342 | 64.1561 | 2986.8924
2040-03-03 17:01 | 8437.07 | 2.6879 | 83.2891 | 64.1561 | 2472.6611
2040-03-04 18:01 | 6326.77 | 1.9374 | 83.765 | 64.1561 | 1854.1933
2040-03-05 19:01 | 4693.92 | 1.4789 | 83.2419 | 64.1561 | 1375.6522
2040-03-06 20:01 | 3182.97 | 1 | 88.4064 | 64.1561 | 932.8364
2040-03-07 21:01 | 3059.8 | 1 | 69.6047 | 64.1561 | 896.7389
2040-03-08 22:01 | -308.607 | 1.3215 | 69.236 | 64.1561 | -90.4438
2040-03-09 23:01 | -747.391 | 2.3613 | 68.4234 | 64.1561 | -219.0387
2040-03-11 00:01 | -1109.95 | 3.2151 | 67.9665 | 64.1561 | -325.2942
2040-03-12 01:01 | -1368.65 | 3.8189 | 67.671 | 64.1561 | -401.1117
2040-03-13 02:01 | -1445.06 | 3.9753 | 67.4262 | 64.1561 | -423.5053
2040-03-14 03:01 | -1370.59 | 3.7789 | 67.2115 | 64.1561 | -401.6803
2040-03-15 04:01 | -1225.34 | 3.4245 | 67.1033 | 64.1561 | -359.1117
2040-03-16 05:01 | -828.055 | 2.4297 | 67.0792 | 64.1561 | -242.679
2040-03-17 06:01 | -850.534 | 2.5725 | 67.0916 | 64.1561 | -249.2669
2040-03-18 07:01 | -752.887 | 2.3094 | 67.073 | 64.1561 | -220.6494
2040-03-19 08:01 | -1246.14 | 3.6086 | 66.977 | 64.1561 | -365.2076
2040-03-20 09:01 | -657.121 | 1.9766 | 66.9259 | 64.1561 | -192.5832
2040-03-21 10:01 | -424.618 | 1.5151 | 67.1249 | 64.1561 | -124.4433
2040-03-22 11:01 | -106.059 | 0.73498 | 67.6437 | 64.1561 | -31.0828
2040-03-23 12:01 | -125.599 | 0.84923 | 67.6173 | 64.1561 | -36.8094
2040-03-24 13:01 | 468.759 | 1 | 68.042 | 64.1561 | 137.3797
2040-03-25 14:01 | 2924.47 | 1 | 67.4703 | 64.1561 | 857.0776
2040-03-26 15:01 | 3029.86 | 1 | 67.6924 | 64.1561 | 887.9643
2040-03-27 16:01 | 3146.26 | 1 | 88.9166 | 64.1561 | 922.0778
2040-03-28 17:01 | 3233.17 | 1 | 67.8217 | 64.1561 | 947.5486
2040-03-29 18:01 | 3095 | 1 | 67.9461 | 64.1561 | 907.055
2040-03-30 19:01 | 400.017 | 1 | 68.6541 | 64.1561 | 117.2334
2040-03-31 20:01 | -599.755 | 2.102 | 67.3633 | 64.1561 | -175.7708
2040-04-01 21:01 | -968.205 | 2.9096 | 66.9207 | 64.1561 | -283.7529
2040-04-02 22:01 | -1846.22 | 5.1377 | 66.6618 | 64.1561 | -541.0737
2040-04-03 23:01 | -2232.8 | 5.977 | 66.4046 | 64.1561 | -654.3691
2040-04-05 00:01 | -2368.38 | 6.2752 | 66.2023 | 64.1561 | -694.1037
2040-04-06 01:01 | -2527.97 | 6.4446 | 66.0332 | 64.1561 | -740.8749
2040-04-07 02:01 | -2698.65 | 6.4446 | 65.8142 | 64.1561 | -790.8962
2040-04-08 03:01 | -2511.79 | 6.4446 | 65.8104 | 64.1561 | -736.133
2040-04-09 04:01 | -2419.95 | 6.4052 | 65.7893 | 64.1561 | -709.2173
2040-04-10 05:01 | -2157.19 | 5.7105 | 65.7308 | 64.1561 | -632.21
2040-04-11 06:01 | -2040.35 | 5.4641 | 65.7133 | 64.1561 | -597.9676
2040-04-12 07:01 | -2022.15 | 5.4382 | 65.7096 | 64.1561 | -592.6337
2040-04-13 08:01 | -2230.29 | 5.9945 | 65.7013 | 64.1561 | -653.6335
2040-04-14 09:01 | -1941.07 | 5.1795 | 65.6418 | 64.1561 | -568.8715
2040-04-15 10:01 | -1449.29 | 3.9494 | 65.6586 | 64.1561 | -424.745
2040-04-16 11:01 | -1062.62 | 3.0363 | 65.7503 | 64.1561 | -311.4232
2040-04-17 12:01 | -1323.27 | 3.8005 | 65.7908 | 64.1561 | -387.8122
2040-04-18 13:01 | -1541.41 | 4.3126 | 65.7206 | 64.1561 | -451.7427
2040-04-19 14:01 | -1364.98 | 3.8048 | 65.6467 | 64.1561 | -400.0361
2040-04-20 15:01 | -741.216 | 2.2071 | 65.6941 | 64.1561 | -217.229
2040-04-21 16:01 | -545.774 | 1.8321 | 65.8586 | 64.1561 | -159.9506
2040-04-22 17:01 | -479.995 | 1.6916 | 65.9156 | 64.1561 | -140.6726
2040-04-23 18:01 | -911.666 | 2.8338 | 65.762 | 64.1561 | -267.1829
2040-04-24 19:01 | -1202.49 | 3.5068 | 65.6379 | 64.1561 | -352.415
2040-04-25 20:01 | -1952.91 | 5.4402 | 65.5333 | 64.1561 | -572.3414
2040-04-26 21:01 | -2177.72 | 5.8781 | 65.375 | 64.1561 | -638.2267
2040-04-27 22:01 | -2945.46 | 6.4446 | 64.9466 | 64.1561 | -863.2291
2040-04-28 23:01 | -3107.22 | 6.4446 | 64.7024 | 64.1561 | -910.6363
2040-04-30 00:01 | -2906.22 | 6.4446 | 64.7167 | 64.1561 | -851.729
2040-05-01 01:01 | -3150.77 | 6.4446 | 64.5244 | 64.1561 | -923.3995
2040-05-02 02:01 | -3226.76 | 6.4446 | 64.4159 | 64.1561 | -945.67
2040-05-03 03:01 | -3037.29 | 6.4446 | 64.4632 | 64.1561 | -890.1418
2040-05-04 04:01 | -3097.82 | 6.4446 | 64.4031 | 64.1561 | -907.8814
2040-05-05 05:01 | -2571.78 | 6.4446 | 64.6844 | 64.1561 | -753.7143
2040-05-06 06:01 | -2843.69 | 6.4446 | 64.5373 | 64.1561 | -833.4033
2040-05-07 07:01 | -3416.7 | 6.4446 | 64.1582 | 64.1561 | -1001.3359
2040-05-08 08:01 | -3860.17 | 6.4446 | 63.7993 | 64.1561 | -1131.3042
2040-05-09 09:01 | -2793.44 | 6.4446 | 64.3344 | 64.1561 | -818.6764
2040-05-10 10:01 | -1364.97 | 3.6684 | 64.6177 | 64.1561 | -400.0332
2040-05-11 11:01 | 0 | 1 | 66.2313 | 64.1561 | 0
2040-05-12 12:01 | 2847.91 | 1 | 65.7681 | 64.1561 | 834.64
2040-05-13 13:01 | 2899.2 | 1 | 83.6168 | 64.1561 | 849.6716
2040-05-14 14:01 | 2859 | 1 | 80.0639 | 64.1561 | 837.8902
2040-05-15 15:01 | 3997.5 | 1.3686 | 78.7521 | 64.1561 | 1171.5516
2040-05-16 16:01 | 3089.76 | 1.0728 | 78.861 | 64.1561 | 905.5193
2040-05-17 17:01 | 2840.66 | 1 | 66.9986 | 64.1561 | 832.5153
2040-05-18 18:01 | 0 | 0 | 67.6961 | 64.1561 | 0
2040-05-19 19:01 | -909.115 | 2.7575 | 66.1505 | 64.1561 | -266.4353
2040-05-20 20:01 | -2127.13 | 5.9457 | 65.8406 | 64.1561 | -623.4003
2040-05-21 21:01 | -2878.49 | 6.4446 | 65.2474 | 64.1561 | -843.6021
2040-05-22 22:01 | -4038.24 | 6.4446 | 64.307 | 64.1561 | -1183.4913
2040-05-23 23:01 | -4486.44 | 6.4446 | 63.7343 | 64.1561 | -1314.8458
2040-05-25 00:01 | -4871.58 | 6.4446 | 63.2521 | 64.1561 | -1427.7192
2040-05-26 01:01 | -5096.25 | 6.4446 | 62.8975 | 64.1561 | -1493.5634
2040-05-27 02:01 | -5187.97 | 6.4446 | 62.6534 | 64.1561 | -1520.4439
2040-05-28 03:01 | -5285.87 | 6.4446 | 62.4191 | 64.1561 | -1549.1356
2040-05-29 04:01 | -5222.57 | 6.4446 | 62.313 | 64.1561 | -1530.5842
2040-05-30 05:01 | -4905.28 | 6.4446 | 62.3826 | 64.1561 | -1437.5957
2040-05-31 06:01 | -4904.65 | 6.4446 | 62.3309 | 64.1561 | -1437.411
2040-06-01 07:01 | -4115.6 | 6.4446 | 62.7559 | 64.1561 | -1206.1633
2040-06-02 08:01 | -2936.92 | 6.4446 | 63.5144 | 64.1561 | -860.7263
2040-06-03 09:01 | -1290.69 | 3.4995 | 63.9905 | 64.1561 | -378.2639
2040-06-04 10:01 | 1031.72 | 1 | 65.435 | 64.1561 | 302.3673
2040-06-05 11:01 | 3041.13 | 1 | 81.7573 | 64.1561 | 891.2672
2040-06-06 12:01 | 3031.66 | 1 | 79.1629 | 64.1561 | 888.4918
2040-06-07 13:01 | 4330.86 | 1.4072 | 78.8072 | 64.1561 | 1269.2498
2040-06-08 14:01 | 5122.06 | 1.6692 | 79.1052 | 64.1561 | 1501.1276
2040-06-09 15:01 | 6118.47 | 1.9727 | 79.5545 | 64.1561 | 1793.1465
2040-06-10 16:01 | 5211.09 | 1.6773 | 79.899 | 64.1561 | 1527.2197
2040-06-11 17:01 | 3428.07 | 1.0994 | 80.0596 | 64.1561 | 1004.6681
2040-06-12 18:01 | 3116.11 | 1 | 67.0641 | 64.1561 | 913.2417
2040-06-13 19:01 | 2987.5 | 1 | 67.0914 | 64.1561 | 875.5498
2040-06-14 20:01 | -665.889 | 2.2938 | 66.6955 | 64.1561 | -195.1528
2040-06-15 21:01 | -1419.53 | 4.1037 | 66.0769 | 64.1561 | -416.0232
2040-06-16 22:01 | -2158.34 | 5.9226 | 65.7035 | 64.1561 | -632.547
2040-06-17 23:01 | -2787.19 | 6.4446 | 65.2097 | 64.1561 | -816.8448
2040-06-19 00:01 | -2776.55 | 6.4446 | 64.9807 | 64.1561 | -813.7265
2040-06-20 01:01 | -2964.44 | 6.4446 | 64.6757 | 64.1561 | -868.7916
2040-06-21 02:01 | -2974.11 | 6.4446 | 64.5381 | 64.1561 | -871.6256
2040-06-22 03:01 | -3012.41 | 6.4446 | 64.3954 | 64.1561 | -882.8502
2040-06-23 04:01 | -3357.33 | 6.4446 | 64.0903 | 64.1561 | -983.9363
2040-06-24 05:01 | -3345.09 | 6.4446 | 63.9896 | 64.1561 | -980.3491
2040-06-25 06:01 | -2712.77 | 6.4446 | 64.2877 | 64.1561 | -795.0344
2040-06-26 07:01 | -2341.34 | 6.3082 | 64.4802 | 64.1561 | -686.179
2040-06-27 08:01 | -2735.55 | 6.4446 | 64.3128 | 64.1561 | -801.7106
2040-06-28 09:01 | -1670.42 | 4.4953 | 64.4731 | 64.1561 | -489.5518
2040-06-29 10:01 | -826.552 | 2.3979 | 64.6588 | 64.1561 | -242.2385
2040-06-30 11:01 | 2670.97 | 1 | 65.504 | 64.1561 | 782.784
2040-07-01 12:01 | 3150.25 | 1.0045 | 78.8718 | 64.1561 | 923.2471
2040-07-02 13:01 | 4086.14 | 1.3183 | 78.9872 | 64.1561 | 1197.5294
2040-07-03 14:01 | 4594.96 | 1.5314 | 78.8726 | 64.1561 | 1346.6498
2040-07-04 15:01 | 3252.66 | 1.0442 | 79.5698 | 64.1561 | 953.2605
2040-07-05 16:01 | 4736.97 | 1.5498 | 79.3712 | 64.1561 | 1388.2689
2040-07-06 17:01 | 3403 | 1.1086 | 79.6242 | 64.1561 | 997.3209
2040-07-07 18:01 | 3091.79 | 1 | 85.3643 | 64.1561 | 906.1142
2040-07-08 19:01 | 3163.64 | 1 | 66.8526 | 64.1561 | 927.1714
2040-07-09 20:01 | 3083.42 | 1 | 66.9375 | 64.1561 | 903.6612
2040-07-10 21:01 | 3137.26 | 1 | 67.0021 | 64.1561 | 919.4401
2040-07-11 22:01 | 3120.83 | 1 | 67.0657 | 64.1561 | 914.625
2040-07-12 23:01 | -1544.3 | 4.5766 | 66.5455 | 64.1561 | -452.5897
2040-07-14 00:01 | -2283.06 | 6.1947 | 65.9503 | 64.1561 | -669.0988
2040-07-15 01:01 | -2730.71 | 6.4446 | 65.3889 | 64.1561 | -800.2921
2040-07-16 02:01 | -2778.71 | 6.4446 | 65.1291 | 64.1561 | -814.3595
2040-07-17 03:01 | -3151.58 | 6.4446 | 64.7213 | 64.1561 | -923.6369
2040-07-18 04:01 | -2735.04 | 6.4446 | 64.7527 | 64.1561 | -801.5611
2040-07-19 05:01 | -2601.3 | 6.4446 | 64.7796 | 64.1561 | -762.3658
2040-07-20 06:01 | -2580.09 | 6.4446 | 64.7581 | 64.1561 | -756.1497
2040-07-21 07:01 | -1857.68 | 4.9734 | 64.8145 | 64.1561 | -544.4323
2040-07-22 08:01 | -1367.02 | 3.7851 | 64.893 | 64.1561 | -400.634
2040-07-23 09:01 | -1825.76 | 5.1135 | 64.9583 | 64.1561 | -535.0774
2040-07-24 10:01 | -1865.5 | 5.1071 | 64.8571 | 64.1561 | -546.7241
2040-07-25 11:01 | -1613.43 | 4.435 | 64.8148 | 64.1561 | -472.8497
2040-07-26 12:01 | -1247.38 | 3.5168 | 64.85 | 64.1561 | -365.571
2040-07-27 13:01 | -928.723 | 2.7492 | 64.9292 | 64.1561 | -272.1818
2040-07-28 14:01 | -788.816 | 2.4444 | 64.9995 | 64.1561 | -231.1791
2040-07-29 15:01 | -737.842 | 2.3351 | 65.043 | 64.1561 | -216.2401
2040-07-30 16:01 | -501.442 | 1.7192 | 65.1353 | 64.1561 | -146.9581
2040-07-31 17:01 | 1901.32 | 1 | 76.303 | 64.1561 | 557.2219
2040-08-01 18:01 | 2727.78 | 1 | 65.933 | 64.1561 | 799.4334
2040-08-02 19:01 | 2898.47 | 1 | 66.1408 | 64.1561 | 849.4577
2040-08-03 20:01 | 2118.73 | 1 | 66.4882 | 64.1561 | 620.9385
2040-08-04 21:01 | 0 | 0 | 67.0404 | 64.1561 | 0
2040-08-05 22:01 | 0 | 1 | 66.8774 | 64.1561 | 0
2040-08-06 23:01 | -55.0637 | 0.69511 | 66.5037 | 64.1561 | -16.1376
2040-08-08 00:01 | -1167.82 | 3.5818 | 65.5143 | 64.1561 | -342.2543
2040-08-09 01:01 | -1393.2 | 3.9629 | 65.2632 | 64.1561 | -408.3066
2040-08-10 02:01 | -1447.76 | 4.0792 | 65.1416 | 64.1561 | -424.2966
2040-08-11 03:01 | -1482.79 | 4.1637 | 65.1064 | 64.1561 | -434.5629
2040-08-12 04:01 | -1279.01 | 3.6153 | 65.0862 | 64.1561 | -374.8408
2040-08-13 05:01 | -1414.34 | 4.0246 | 65.0705 | 64.1561 | -414.5021
2040-08-14 06:01 | -1046.68 | 3.0126 | 65.047 | 64.1561 | -306.7516
2040-08-15 07:01 | -1198.85 | 3.5051 | 65.071 | 64.1561 | -351.3483
2040-08-16 08:01 | -1139.54 | 3.3056 | 65.039 | 64.1561 | -333.9662
2040-08-17 09:01 | -1442.73 | 4.1299 | 65.0219 | 64.1561 | -422.8224
2040-08-18 10:01 | -1099.56 | 3.1461 | 64.9767 | 64.1561 | -322.2492
2040-08-19 11:01 | -540.192 | 1.7497 | 65.1338 | 64.1561 | -158.3146
2040-08-20 12:01 | -352.116 | 1.3736 | 65.3898 | 64.1561 | -103.195
2040-08-21 13:01 | -493.121 | 1.7749 | 65.3423 | 64.1561 | -144.5195
2040-08-22 14:01 | -740.702 | 2.3951 | 65.2112 | 64.1561 | -217.0783
2040-08-23 15:01 | -939.485 | 2.8702 | 65.1125 | 64.1561 | -275.3359
2040-08-24 16:01 | -514.569 | 1.7062 | 65.1635 | 64.1561 | -150.8053
2040-08-25 17:01 | -375.498 | 1.4396 | 65.3242 | 64.1561 | -110.0476
2040-08-26 18:01 | -385.294 | 1.4876 | 65.3292 | 64.1561 | -112.9185
2040-08-27 19:01 | -733.481 | 2.4016 | 65.1319 | 64.1561 | -214.9621
2040-08-28 20:01 | -1118.43 | 3.3488 | 64.9713 | 64.1561 | -327.7795
2040-08-29 21:01 | -2031.34 | 5.7117 | 64.8302 | 64.1561 | -595.327
2040-08-30 22:01 | -2215.48 | 6.009 | 64.6362 | 64.1561 | -649.2931
2040-08-31 23:01 | -3044.18 | 6.4446 | 64.1283 | 64.1561 | -892.1611
2040-09-02 00:01 | -3352.92 | 6.4446 | 63.7844 | 64.1561 | -982.6439
2040-09-03 01:01 | -3463.07 | 6.4446 | 63.5811 | 64.1561 | -1014.9256
2040-09-04 02:01 | -3426.72 | 6.4446 | 63.5028 | 64.1561 | -1004.2725
2040-09-05 03:01 | -3386.02 | 6.4446 | 63.466 | 64.1561 | -992.3445
2040-09-06 04:01 | -3196.5 | 6.4446 | 63.5231 | 64.1561 | -936.8017
2040-09-07 05:01 | -3035.48 | 6.4446 | 63.5954 | 64.1561 | -889.6114
2040-09-08 06:01 | -2485.13 | 6.4446 | 63.9162 | 64.1561 | -728.3197
2040-09-09 07:01 | -2501.43 | 6.4446 | 63.9458 | 64.1561 | -733.0968
2040-09-10 08:01 | -2320.86 | 6.2791 | 64.0248 | 64.1561 | -680.1769
2040-09-11 09:01 | -2866.26 | 6.4446 | 63.7495 | 64.1561 | -840.0179
2040-09-12 10:01 | -2636.69 | 6.4446 | 63.8282 | 64.1561 | -772.7376
2040-09-13 11:01 | -2608.56 | 6.4446 | 63.8289 | 64.1561 | -764.4935
2040-09-14 12:01 | -2240.47 | 6.0708 | 63.9491 | 64.1561 | -656.6169
2040-09-15 13:01 | -2305.59 | 6.2709 | 63.9689 | 64.1561 | -675.7017
2040-09-16 14:01 | -1897.43 | 5.1445 | 63.9469 | 64.1561 | -556.0818
2040-09-17 15:01 | -1609.03 | 4.4634 | 64.0102 | 64.1561 | -471.5601
2040-09-18 16:01 | -1071.85 | 3.0745 | 64.0943 | 64.1561 | -314.1282
2040-09-19 17:01 | -823.063 | 2.5281 | 64.2546 | 64.1561 | -241.216
2040-09-20 18:01 | -623.118 | 2.0401 | 64.3866 | 64.1561 | -182.6179
2040-09-21 19:01 | -918.726 | 2.8698 | 64.3834 | 64.1561 | -269.252
2040-09-22 20:01 | -1192.97 | 3.5337 | 64.3189 | 64.1561 | -349.625
2040-09-23 21:01 | -1896.41 | 5.3715 | 64.2506 | 64.1561 | -555.7829
2040-09-24 22:01 | -2117.87 | 5.8131 | 64.1306 | 64.1561 | -620.6864
2040-09-25 23:01 | -2821.83 | 6.4446 | 63.7849 | 64.1561 | -826.9967
2040-09-27 00:01 | -3128.74 | 6.4446 | 63.4872 | 64.1561 | -916.9432
2040-09-28 01:01 | -3298.83 | 6.4446 | 63.2852 | 64.1561 | -966.7916
2040-09-29 02:01 | -3583.61 | 6.4446 | 63.0304 | 64.1561 | -1050.2524
2040-09-30 03:01 | -3672.04 | 6.4446 | 62.8895 | 64.1561 | -1076.1687
2040-10-01 04:01 | -3458.71 | 6.4446 | 62.9382 | 64.1561 | -1013.6478
2040-10-02 05:01 | -3283.52 | 6.4446 | 63.0107 | 64.1561 | -962.3047
2040-10-03 06:01 | -2894 | 6.4446 | 63.2252 | 64.1561 | -848.1477
2040-10-04 07:01 | -2928.96 | 6.4446 | 63.2179 | 64.1561 | -858.3934
2040-10-05 08:01 | -2776.31 | 6.4446 | 63.3044 | 64.1561 | -813.6561
2040-10-06 09:01 | -1433.91 | 3.9036 | 63.5606 | 64.1561 | -420.2375
2040-10-07 10:01 | 1382.6 | 1 | 64.8218 | 64.1561 | 405.2001
2040-10-08 11:01 | 3138.43 | 1 | 79.6938 | 64.1561 | 919.783
2040-10-09 12:01 | 4560.95 | 1.4973 | 77.8789 | 64.1561 | 1336.6825
2040-10-10 13:01 | 5535.62 | 1.8121 | 78.3343 | 64.1561 | 1622.3301
2040-10-11 14:01 | 6010.41 | 2.011 | 78.4847 | 64.1561 | 1761.4773
2040-10-12 15:01 | 5703.94 | 1.9616 | 78.5216 | 64.1561 | 1671.6598
2040-10-13 16:01 | 5910.58 | 2.033 | 78.7266 | 64.1561 | 1732.22
2040-10-14 17:01 | 3255.2 | 1.1409 | 78.7182 | 64.1561 | 954.0049
2040-10-15 18:01 | 2859.18 | 1 | 84.8748 | 64.1561 | 837.9429
2040-10-16 19:01 | 2679.15 | 1 | 66.7051 | 64.1561 | 785.1814
2040-10-17 20:01 | -288.296 | 1.3299 | 66.4904 | 64.1561 | -84.4912
2040-10-18 21:01 | -1399.2 | 4.1425 | 65.6901 | 64.1561 | -410.065
2040-10-19 22:01 | -1936.14 | 5.358 | 65.2619 | 64.1561 | -567.4266
2040-10-20 23:01 | -2909.25 | 6.4446 | 64.6961 | 64.1561 | -852.617
2040-10-22 00:01 | -3522.08 | 6.4446 | 64.053 | 64.1561 | -1032.2198
2040-10-23 01:01 | -3673.24 | 6.4446 | 63.6774 | 64.1561 | -1076.5204
2040-10-24 02:01 | -3805.14 | 6.4446 | 63.4068 | 64.1561 | -1115.1765
2040-10-25 03:01 | -3783.74 | 6.4446 | 63.2636 | 64.1561 | -1108.9047
2040-10-26 04:01 | -3606.03 | 6.4446 | 63.2346 | 64.1561 | -1056.8231
2040-10-27 05:01 | -3252.79 | 6.4446 | 63.3773 | 64.1561 | -953.2986
2040-10-28 06:01 | -2931.4 | 6.4446 | 63.544 | 64.1561 | -859.1085
2040-10-29 07:01 | -2828.34 | 6.4446 | 63.5966 | 64.1561 | -828.9046
2040-10-30 08:01 | -2256.79 | 6.1308 | 63.8778 | 64.1561 | -661.3999
2040-10-31 09:01 | -2575.04 | 6.4446 | 63.8162 | 64.1561 | -754.6697
2040-11-01 10:01 | 0 | 1 | 65.3591 | 64.1561 | 0
2040-11-02 11:01 | 3078.35 | 1.1311 | 76.294 | 64.1561 | 902.1753
2040-11-03 12:01 | 5147.41 | 1.6314 | 78.4577 | 64.1561 | 1508.557
2040-11-04 13:01 | 4971 | 1.5538 | 79.1332 | 64.1561 | 1456.8563
2040-11-05 14:01 | 5754.76 | 1.8549 | 79.0386 | 64.1561 | 1686.5537
2040-11-06 15:01 | 6021.18 | 1.9122 | 79.5505 | 64.1561 | 1764.6337
2040-11-07 16:01 | 5723.13 | 1.7795 | 80.0896 | 64.1561 | 1677.2838
2040-11-08 17:01 | 4868.72 | 1.4914 | 80.4345 | 64.1561 | 1426.881
2040-11-09 18:01 | 4418.32 | 1.3714 | 80.2909 | 64.1561 | 1294.8818
2040-11-10 19:01 | 3123.3 | 1 | 80.3154 | 64.1561 | 915.3489
2040-11-11 20:01 | 3112.81 | 1 | 85.3045 | 64.1561 | 912.2746
2040-11-12 21:01 | 1215.48 | 1 | 67.3524 | 64.1561 | 356.222
2040-11-13 22:01 | -181.592 | 1.0555 | 66.7765 | 64.1561 | -53.2194
2040-11-14 23:01 | -977.397 | 3.0463 | 65.9261 | 64.1561 | -286.4468
2040-11-16 00:01 | -1375.57 | 3.9482 | 65.574 | 64.1561 | -403.1398
2040-11-17 01:01 | -1529.52 | 4.2869 | 65.3576 | 64.1561 | -448.2581
2040-11-18 02:01 | -1712.8 | 4.754 | 65.1791 | 64.1561 | -501.9721
2040-11-19 03:01 | -1703.45 | 4.6953 | 65.0352 | 64.1561 | -499.2319
2040-11-20 04:01 | -1682.37 | 4.6493 | 64.9468 | 64.1561 | -493.054
2040-11-21 05:01 | -1588.09 | 4.4047 | 64.8872 | 64.1561 | -465.4232
2040-11-22 06:01 | -1219.54 | 3.4448 | 64.8653 | 64.1561 | -357.4119
2040-11-23 07:01 | -1023.63 | 3.0075 | 64.9241 | 64.1561 | -299.9963
2040-11-24 08:01 | -375.912 | 1.3291 | 65.157 | 64.1561 | -110.1689
2040-11-25 09:01 | 2426.56 | 1 | 65.7664 | 64.1561 | 711.1545
2040-11-26 10:01 | 3173.31 | 1.0401 | 78.6547 | 64.1561 | 930.0054
2040-11-27 11:01 | 4152.3 | 1.354 | 78.9578 | 64.1561 | 1216.919
2040-11-28 12:01 | 5140.53 | 1.6333 | 79.5188 | 64.1561 | 1506.5406
2040-11-29 13:01 | 5519.65 | 1.8212 | 79.3508 | 64.1561 | 1617.6497
2040-11-30 14:01 | 6002.02 | 1.9878 | 79.5485 | 64.1561 | 1759.0184
2040-12-01 15:01 | 5484.53 | 1.7809 | 79.982 | 64.1561 | 1607.3571
2040-12-02 16:01 | 5815.05 | 1.8965 | 80.0175 | 64.1561 | 1704.2229
2040-12-03 17:01 | 5318.84 | 1.6468 | 80.7887 | 64.1561 | 1558.7981
2040-12-04 18:01 | 4916.84 | 1.5597 | 80.5407 | 64.1561 | 1440.9836
2040-12-05 19:01 | 3610.65 | 1.1376 | 80.6516 | 64.1561 | 1058.1771
2040-12-06 20:01 | 3090.63 | 1 | 81.9266 | 64.1561 | 905.7742
2040-12-07 21:01 | 2978.6 | 1 | 67.3436 | 64.1561 | 872.9415
2040-12-08 22:01 | 0 | 0 | 68.0163 | 64.1561 | 0
2040-12-09 23:01 | -787.388 | 2.5631 | 66.4587 | 64.1561 | -230.7606
2040-12-11 00:01 | -1360.1 | 3.929 | 66.0091 | 64.1561 | -398.606
2040-12-12 01:01 | -1624.46 | 4.5198 | 65.7401 | 64.1561 | -476.0822
2040-12-13 02:01 | -1830.39 | 5.0252 | 65.53 | 64.1561 | -536.4344
2040-12-14 03:01 | -2066.72 | 5.6217 | 65.3381 | 64.1561 | -605.6958
2040-12-15 04:01 | -2119.83 | 5.72 | 65.1904 | 64.1561 | -621.2608
2040-12-16 05:01 | -2175.31 | 5.8673 | 65.0828 | 64.1561 | -637.5204
2040-12-17 06:01 | -2275.31 | 6.1293 | 64.9885 | 64.1561 | -666.8275
2040-12-18 07:01 | -1395.83 | 3.7567 | 64.9005 | 64.1561 | -409.0774
2040-12-19 08:01 | -315.234 | 1.1015 | 65.2586 | 64.1561 | -92.386
2040-12-20 09:01 | 751.856 | 1 | 66.3051 | 64.1561 | 220.3472
2040-12-21 10:01 | 2276.35 | 1 | 66.1066 | 64.1561 | 667.1323
2040-12-22 11:01 | 2963.52 | 1 | 66.1947 | 64.1561 | 868.522
2040-12-23 12:01 | 3029.15 | 1 | 66.4037 | 64.1561 | 887.7562
2040-12-24 13:01 | 3127.84 | 1 | 86.5268 | 64.1561 | 916.6794
2040-12-25 14:01 | 3159.18 | 1 | 87.4949 | 64.1561 | 925.8643
2040-12-26 15:01 | 3114.28 | 1 | 66.7023 | 64.1561 | 912.7054
2040-12-27 16:01 | 3156.84 | 1 | 66.7422 | 64.1561 | 925.1785
2040-12-28 17:01 | 4486.43 | 1.4203 | 79.9123 | 64.1561 | 1314.8428
2040-12-29 18:01 | 3611.51 | 1.1333 | 80.192 | 64.1561 | 1058.4291
2040-12-30 19:01 | 3171.79 | 1 | 82.1745 | 64.1561 | 929.5599
2040-12-31 20:01 | 3089.67 | 1 | 87.4965 | 64.1561 | 905.4929
2041-01-01 21:01 | 3122.36 | 1 | 67.0126 | 64.1561 | 915.0734
2041-01-02 22:01 | 3095.46 | 1 | 67.0648 | 64.1561 | 907.1898
2041-01-03 23:01 | 3094.71 | 1 | 67.0778 | 64.1561 | 906.97
2041-01-05 00:01 | -695.396 | 2.3593 | 66.6945 | 64.1561 | -203.8004
2041-01-06 01:01 | -1020.21 | 3.0497 | 66.15 | 64.1561 | -298.994
2041-01-07 02:01 | -1094.33 | 3.1943 | 65.8751 | 64.1561 | -320.7165
2041-01-08 03:01 | -1167.44 | 3.379 | 65.7372 | 64.1561 | -342.1429
2041-01-09 04:01 | -1255.21 | 3.5996 | 65.603 | 64.1561 | -367.8657
2041-01-10 05:01 | -1399.68 | 3.969 | 65.4486 | 64.1561 | -410.2057
2041-01-11 06:01 | -1441.91 | 4.0521 | 65.3659 | 64.1561 | -422.5821
2041-01-12 07:01 | -662.42 | 1.9854 | 65.3904 | 64.1561 | -194.1361
2041-01-13 08:01 | -251.439 | 1.0849 | 65.8196 | 64.1561 | -73.6895
2041-01-14 09:01 | -466.298 | 1.7205 | 65.6942 | 64.1561 | -136.6585
2041-01-15 10:01 | -560.483 | 1.9182 | 65.5612 | 64.1561 | -164.2614
2041-01-16 11:01 | -341.537 | 1.3281 | 65.6278 | 64.1561 | -100.0946
2041-01-17 12:01 | -170.015 | 0.92871 | 65.9158 | 64.1561 | -49.8265
2041-01-18 13:01 | 678.681 | 1 | 66.4665 | 64.1561 | 198.9018
2041-01-19 14:01 | 2803.6 | 1 | 66.0263 | 64.1561 | 821.6541
2041-01-20 15:01 | 3049.55 | 1 | 86.8522 | 64.1561 | 893.7349
2041-01-21 16:01 | 3026.7 | 1 | 81.5332 | 64.1561 | 887.0382
2041-01-22 17:01 | 4606.8 | 1.4963 | 79.265 | 64.1561 | 1350.1198
2041-01-23 18:01 | 3241.64 | 1.0378 | 79.7207 | 64.1561 | 950.0309
2041-01-24 19:01 | 3119.1 | 1 | 84.5644 | 64.1561 | 914.118
2041-01-25 20:01 | 3068.77 | 1 | 66.7915 | 64.1561 | 899.3677
2041-01-26 21:01 | 3089.76 | 1 | 66.8242 | 64.1561 | 905.5193
2041-01-27 22:01 | 3096.13 | 1 | 66.8732 | 64.1561 | 907.3861
2041-01-28 23:01 | 439.809 | 1 | 67.533 | 64.1561 | 128.8953
2041-01-30 00:01 | -815.304 | 2.6828 | 66.2146 | 64.1561 | -238.942
2041-01-31 01:01 | -1187.78 | 3.4746 | 65.813 | 64.1561 | -348.104
2041-02-01 02:01 | -1358.47 | 3.8642 | 65.5971 | 64.1561 | -398.1283
2041-02-02 03:01 | -1409.17 | 3.9713 | 65.4387 | 64.1561 | -412.987
2041-02-03 04:01 | -1264.37 | 3.5839 | 65.3141 | 64.1561 | -370.5503
2041-02-04 05:01 | -996.954 | 2.9121 | 65.2816 | 64.1561 | -292.1784
2041-02-05 06:01 | -716.803 | 2.2306 | 65.3524 | 64.1561 | -210.0742
2041-02-06 07:01 | -508.207 | 1.7396 | 65.4725 | 64.1561 | -148.9408
2041-02-07 08:01 | -113.368 | 0.74555 | 66.0281 | 64.1561 | -33.2249
2041-02-08 09:01 | -305.773 | 1.33 | 65.7563 | 64.1561 | -89.6132
2041-02-09 10:01 | 2027.63 | 1 | 75.9101 | 64.1561 | 594.2397
2041-02-10 11:01 | 5039.04 | 1.8396 | 77.5963 | 64.1561 | 1476.7968
2041-02-11 12:01 | 7105.48 | 2.5822 | 78.1307 | 64.1561 | 2082.4106
2041-02-12 13:01 | 8758.17 | 3.0631 | 79.0613 | 64.1561 | 2566.7663
2041-02-13 14:01 | 8718.94 | 2.9035 | 80.1238 | 64.1561 | 2555.2691
2041-02-14 15:01 | 8851.05 | 2.93 | 80.555 | 64.1561 | 2593.9867
2041-02-15 16:01 | 9142.85 | 2.8965 | 81.3705 | 64.1561 | 2679.5048
2041-02-16 17:01 | 7390.4 | 2.2272 | 82.2507 | 64.1561 | 2165.9124
2041-02-17 18:01 | 6613.11 | 1.9767 | 82.3525 | 64.1561 | 1938.1112
2041-02-18 19:01 | 4853.92 | 1.4457 | 82.3546 | 64.1561 | 1422.5435
2041-02-19 20:01 | 3655.95 | 1.1395 | 81.6104 | 64.1561 | 1071.4532
2041-02-20 21:01 | 2962.81 | 1 | 68.1697 | 64.1561 | 868.3139
2041-02-21 22:01 | 0 | 0 | 68.6911 | 64.1561 | 0
2041-02-22 23:01 | -970.859 | 2.8786 | 66.9287 | 64.1561 | -284.5307
2041-02-24 00:01 | -1359.94 | 3.8783 | 66.4964 | 64.1561 | -398.5591
2041-02-25 01:01 | -1687.24 | 4.6656 | 66.1807 | 64.1561 | -494.4812
2041-02-26 02:01 | -1969.93 | 5.3579 | 65.9178 | 64.1561 | -577.3295
2041-02-27 03:01 | -2235.26 | 6.0175 | 65.6705 | 64.1561 | -655.09
2041-02-28 04:01 | -2384.36 | 6.3707 | 65.4722 | 64.1561 | -698.7869
2041-03-01 05:01 | -2455.54 | 6.4446 | 65.2961 | 64.1561 | -719.6477
2041-03-02 06:01 | -2236.89 | 5.9603 | 65.1873 | 64.1561 | -655.5677
2041-03-03 07:01 | -1910.97 | 5.1353 | 65.1205 | 64.1561 | -560.05
2041-03-04 08:01 | -598.12 | 1.7234 | 65.1786 | 64.1561 | -175.2917
2041-03-05 09:01 | 1961.22 | 1 | 66.173 | 64.1561 | 574.7768
2041-03-06 10:01 | 3011.27 | 1 | 83.3767 | 64.1561 | 882.5161
2041-03-07 11:01 | 4348.08 | 1.4209 | 79.2254 | 64.1561 | 1274.2965
2041-03-08 12:01 | 5831.76 | 1.9338 | 79.3646 | 64.1561 | 1709.1201
2041-03-09 13:01 | 6148.13 | 2.1625 | 79.06 | 64.1561 | 1801.839
2041-03-10 14:01 | 6275.87 | 2.1607 | 79.5716 | 64.1561 | 1839.2759
2041-03-11 15:01 | 6077.16 | 2.08 | 79.8195 | 64.1561 | 1781.0398
2041-03-12 16:01 | 5827.6 | 2.0135 | 79.8348 | 64.1561 | 1707.901
2041-03-13 17:01 | 3803.2 | 1.3333 | 79.7586 | 64.1561 | 1114.6079
2041-03-14 18:01 | 2823.14 | 1 | 80.6647 | 64.1561 | 827.3807
2041-03-15 19:01 | 2779.35 | 1 | 67.6268 | 64.1561 | 814.5471
2041-03-16 20:01 | 0 | 0 | 68.2248 | 64.1561 | 0
2041-03-17 21:01 | -1044.19 | 3.0563 | 66.5147 | 64.1561 | -306.0219
2041-03-18 22:01 | -1586.22 | 4.4746 | 66.12 | 64.1561 | -464.8752
2041-03-19 23:01 | -2806.04 | 6.4446 | 65.5669 | 64.1561 | -822.3691
2041-03-21 00:01 | -3437.45 | 6.4446 | 64.8719 | 64.1561 | -1007.4171
2041-03-22 01:01 | -3984.09 | 6.4446 | 64.2303 | 64.1561 | -1167.6215
2041-03-23 02:01 | -4139.76 | 6.4446 | 63.882 | 64.1561 | -1213.2439
2041-03-24 03:01 | -4423.24 | 6.4446 | 63.506 | 64.1561 | -1296.3237
2041-03-25 04:01 | -4404.13 | 6.4446 | 63.3172 | 64.1561 | -1290.7231
2041-03-26 05:01 | -4282.28 | 6.4446 | 63.2529 | 64.1561 | -1255.0124
2041-03-27 06:01 | -4124.03 | 6.4446 | 63.2512 | 64.1561 | -1208.6339
2041-03-28 07:01 | -3915.28 | 6.4446 | 63.2993 | 64.1561 | -1147.4553
2041-03-29 08:01 | -2287.19 | 6.2391 | 64.1961 | 64.1561 | -670.3092
2041-03-30 09:01 | -1196.12 | 3.237 | 64.3097 | 64.1561 | -350.5482
2041-03-31 10:01 | 1376 | 1 | 65.5897 | 64.1561 | 403.2658
2041-04-01 11:01 | 2904.24 | 1 | 77.9029 | 64.1561 | 851.1487
2041-04-02 12:01 | 4449.88 | 1.5253 | 78.032 | 64.1561 | 1304.1311
2041-04-03 13:01 | 5193.14 | 1.8022 | 78.2747 | 64.1561 | 1521.9591
2041-04-04 14:01 | 5361.06 | 1.8688 | 78.5462 | 64.1561 | 1571.1716
2041-04-05 15:01 | 5084.76 | 1.7787 | 78.752 | 64.1561 | 1490.1961
2041-04-06 16:01 | 4696.43 | 1.6423 | 78.8909 | 64.1561 | 1376.3878
2041-04-07 17:01 | 2824.06 | 1 | 80.0368 | 64.1561 | 827.6503
2041-04-08 18:01 | 2822.35 | 1 | 66.99 | 64.1561 | 827.1491
2041-04-09 19:01 | 0 | 0 | 67.6281 | 64.1561 | 0
2041-04-10 20:01 | -551.553 | 1.7699 | 66.0975 | 64.1561 | -161.6442
2041-04-11 21:01 | -1642.65 | 4.7498 | 65.7307 | 64.1561 | -481.4132
2041-04-12 22:01 | -2210.68 | 6.0277 | 65.3909 | 64.1561 | -647.8864
2041-04-13 23:01 | -3671.72 | 6.4446 | 64.3717 | 64.1561 | -1076.0749
2041-04-15 00:01 | -4222.2 | 6.4446 | 63.6965 | 64.1561 | -1237.4047
2041-04-16 01:01 | -4425.1 | 6.4446 | 63.3057 | 64.1561 | -1296.8688
2041-04-17 02:01 | -4814.1 | 6.4446 | 62.8576 | 64.1561 | -1410.8734
2041-04-18 03:01 | -4920.68 | 6.4446 | 62.5873 | 64.1561 | -1442.109
2041-04-19 04:01 | -4979.19 | 6.4446 | 62.3731 | 64.1561 | -1459.2565
2041-04-20 05:01 | -4754.36 | 6.4446 | 62.3856 | 64.1561 | -1393.3654
2041-04-21 06:01 | -4443.27 | 6.4446 | 62.491 | 64.1561 | -1302.1939
2041-04-22 07:01 | -3990.19 | 6.4446 | 62.7368 | 64.1561 | -1169.4093
2041-04-23 08:01 | -1965.83 | 5.3921 | 63.734 | 64.1561 | -576.1279
2041-04-24 09:01 | -854.418 | 2.4096 | 63.9737 | 64.1561 | -250.4052
2041-04-25 10:01 | 2789.51 | 1 | 64.9102 | 64.1561 | 817.5247
2041-04-26 11:01 | 4212.17 | 1.4083 | 77.8086 | 64.1561 | 1234.4652
2041-04-27 12:01 | 6062.73 | 2.0207 | 78.2699 | 64.1561 | 1776.8108
2041-04-28 13:01 | 7130.04 | 2.3974 | 78.6475 | 64.1561 | 2089.6085
2041-04-29 14:01 | 7809.84 | 2.6103 | 79.1525 | 64.1561 | 2288.8382
2041-04-30 15:01 | 7398.33 | 2.5187 | 79.3329 | 64.1561 | 2168.2365
2041-05-01 16:01 | 7397.21 | 2.5058 | 79.6064 | 64.1561 | 2167.9082
2041-05-02 17:01 | 5467.18 | 1.8751 | 79.67 | 64.1561 | 1602.2723
2041-05-03 18:01 | 4166.85 | 1.4115 | 79.7756 | 64.1561 | 1221.1832
2041-05-04 19:01 | 2873.29 | 1 | 81.1407 | 64.1561 | 842.0782
2041-05-05 20:01 | 2861.77 | 1 | 67.2848 | 64.1561 | 838.702
2041-05-06 21:01 | 0 | 0 | 67.9164 | 64.1561 | 0
2041-05-07 22:01 | -582.766 | 1.9546 | 66.3739 | 64.1561 | -170.7919
2041-05-08 23:01 | -1682.77 | 4.8313 | 65.9129 | 64.1561 | -493.1712
2041-05-10 00:01 | -2412.34 | 6.4446 | 65.5432 | 64.1561 | -706.9871
2041-05-11 01:01 | -3005.72 | 6.4446 | 64.9166 | 64.1561 | -880.8896
2041-05-12 02:01 | -3163.45 | 6.4446 | 64.549 | 64.1561 | -927.1157
2041-05-13 03:01 | -3413.96 | 6.4446 | 64.2157 | 64.1561 | -1000.5329
2041-05-14 04:01 | -3290.58 | 6.4446 | 64.1161 | 64.1561 | -964.3738
2041-05-15 05:01 | -3499.21 | 6.4446 | 63.883 | 64.1561 | -1025.5172
2041-05-16 06:01 | -3208.5 | 6.4446 | 63.9539 | 64.1561 | -940.3185
2041-05-17 07:01 | -2756.47 | 6.4446 | 64.1827 | 64.1561 | -807.8416
2041-05-18 08:01 | -2497.34 | 6.4446 | 64.327 | 64.1561 | -731.8981
2041-05-19 09:01 | -2400.2 | 6.4446 | 64.3967 | 64.1561 | -703.4292
2041-05-20 10:01 | -768.477 | 2.0737 | 64.3707 | 64.1561 | -225.2184
2041-05-21 11:01 | 2714.67 | 1 | 83.5641 | 64.1561 | 795.5912
2041-05-22 12:01 | 3124.17 | 1 | 65.6619 | 64.1561 | 915.6038
2041-05-23 13:01 | 3153.62 | 1 | 84.9357 | 64.1561 | 924.2348
2041-05-24 14:01 | 3100.32 | 1 | 84.3818 | 64.1561 | 908.6141
2041-05-25 15:01 | 3118.2 | 1 | 79.2633 | 64.1561 | 913.8542
2041-05-26 16:01 | 4543.04 | 1.4238 | 79.5275 | 64.1561 | 1331.4336
2041-05-27 17:01 | 3817.06 | 1.227 | 79.4319 | 64.1561 | 1118.6699
2041-05-28 18:01 | 3220.3 | 1.0379 | 79.4646 | 64.1561 | 943.7768
2041-05-29 19:01 | 3158.27 | 1 | 87.2555 | 64.1561 | 925.5976
2041-05-30 20:01 | 3072.65 | 1 | 66.6373 | 64.1561 | 900.5048
2041-05-31 21:01 | -220.911 | 1.1308 | 66.6814 | 64.1561 | -64.7426
2041-06-01 22:01 | -544.773 | 1.9149 | 65.9997 | 64.1561 | -159.6572
2041-06-02 23:01 | -1372.27 | 4.0347 | 65.5637 | 64.1561 | -402.1726
2041-06-04 00:01 | -1828.94 | 5.0792 | 65.2955 | 64.1561 | -536.0094
2041-06-05 01:01 | -2092.32 | 5.7034 | 65.0797 | 64.1561 | -613.1985
2041-06-06 02:01 | -2228.2 | 6.0245 | 64.8981 | 64.1561 | -653.021
2041-06-07 03:01 | -2320.87 | 6.2522 | 64.7971 | 64.1561 | -680.1799
2041-06-08 04:01 | -2556.27 | 6.4446 | 64.5978 | 64.1561 | -749.1688
2041-06-09 05:01 | -2647.16 | 6.4446 | 64.4467 | 64.1561 | -775.806
2041-06-10 06:01 | -2903.73 | 6.4446 | 64.2105 | 64.1561 | -850.9993
2041-06-11 07:01 | -2077.42 | 5.6047 | 64.4247 | 64.1561 | -608.8317
2041-06-12 08:01 | -1414.52 | 3.8749 | 64.4521 | 64.1561 | -414.5549
2041-06-13 09:01 | -1839.13 | 5.1661 | 64.5645 | 64.1561 | -538.9958
2041-06-14 10:01 | -1614.64 | 4.45 | 64.4975 | 64.1561 | -473.2043
2041-06-15 11:01 | -1009.08 | 2.8925 | 64.5244 | 64.1561 | -295.7322
2041-06-16 12:01 | -260.971 | 1.0393 | 64.9501 | 64.1561 | -76.4831
2041-06-17 13:01 | 2215.8 | 1 | 65.4847 | 64.1561 | 649.3869
2041-06-18 14:01 | 3020.48 | 1 | 65.5864 | 64.1561 | 885.2153
2041-06-19 15:01 | 2934.48 | 1 | 65.8634 | 64.1561 | 860.0112
2041-06-20 16:01 | 3011.16 | 1 | 65.9741 | 64.1561 | 882.4839
2041-06-21 17:01 | 3151.71 | 1 | 85.0316 | 64.1561 | 923.675
2041-06-22 18:01 | 3044.45 | 1 | 66.2104 | 64.1561 | 892.2402
2041-06-23 19:01 | 818.108 | 1 | 66.8073 | 64.1561 | 239.7638
2041-06-24 20:01 | -317.163 | 1.412 | 65.9118 | 64.1561 | -92.9513
2041-06-25 21:01 | -653.284 | 2.1897 | 65.4223 | 64.1561 | -191.4586
2041-06-26 22:01 | -974.294 | 2.977 | 65.1905 | 64.1561 | -285.5374
2041-06-27 23:01 | -1237.4 | 3.6126 | 65.0246 | 64.1561 | -362.6461
2041-06-29 00:01 | -2773.13 | 6.4446 | 64.5724 | 64.1561 | -812.7242
2041-06-30 01:01 | -3396.01 | 6.4446 | 63.9519 | 64.1561 | -995.2723
2041-07-01 02:01 | -3687.71 | 6.4446 | 63.5567 | 64.1561 | -1080.7611
2041-07-02 03:01 | -3940.6 | 6.4446 | 63.2342 | 64.1561 | -1154.8759
2041-07-03 04:01 | -4205.54 | 6.4446 | 62.9134 | 64.1561 | -1232.5221
2041-07-04 05:01 | -4451.97 | 6.4446 | 62.5983 | 64.1561 | -1304.7436
2041-07-05 06:01 | -4462.36 | 6.4446 | 62.4482 | 64.1561 | -1307.7886
2041-07-06 07:01 | -3315.29 | 6.4446 | 63.0457 | 64.1561 | -971.6156
2041-07-07 08:01 | -1654.17 | 4.5153 | 63.6724 | 64.1561 | -484.7894
2041-07-08 09:01 | -735.215 | 2.1703 | 63.9703 | 64.1561 | -215.4702
2041-07-09 10:01 | 2563.84 | 1 | 64.871 | 64.1561 | 751.3873
2041-07-10 11:01 | 3346.69 | 1.0962 | 77.9092 | 64.1561 | 980.818
2041-07-11 12:01 | 5001.01 | 1.6592 | 78.0993 | 64.1561 | 1465.6514
2041-07-12 13:01 | 5701.37 | 1.8692 | 78.641 | 64.1561 | 1670.9066
2041-07-13 14:01 | 6005.62 | 1.9751 | 78.9516 | 64.1561 | 1760.0735
2041-07-14 15:01 | 6046.64 | 1.9942 | 79.2056 | 64.1561 | 1772.0953
2041-07-15 16:01 | 4741.95 | 1.5957 | 79.1682 | 64.1561 | 1389.7284
2041-07-16 17:01 | 4837.81 | 1.6231 | 79.2291 | 64.1561 | 1417.8222
2041-07-17 18:01 | 2888.15 | 1 | 81.8518 | 64.1561 | 846.4332
2041-07-18 19:01 | 2873.16 | 1 | 66.831 | 64.1561 | 842.0401
2041-07-19 20:01 | 0 | 0 | 67.4657 | 64.1561 | 0
2041-07-20 21:01 | -570.581 | 1.9167 | 65.9743 | 64.1561 | -167.2208
2041-07-21 22:01 | -1252.22 | 3.7178 | 65.5664 | 64.1561 | -366.9895
2041-07-22 23:01 | -1715.69 | 4.8078 | 65.2607 | 64.1561 | -502.8191
2041-07-24 00:01 | -3578.91 | 6.4446 | 64.2869 | 64.1561 | -1048.875
2041-07-25 01:01 | -4119.99 | 6.4446 | 63.5851 | 64.1561 | -1207.4499
2041-07-26 02:01 | -4464.98 | 6.4446 | 63.0966 | 64.1561 | -1308.5565
2041-07-27 03:01 | -4517.43 | 6.4446 | 62.8374 | 64.1561 | -1323.928
2041-07-28 04:01 | -4533.45 | 6.4446 | 62.6535 | 64.1561 | -1328.623
2041-07-29 05:01 | -4711.34 | 6.4446 | 62.391 | 64.1561 | -1380.7575
2041-07-30 06:01 | -4709.08 | 6.4446 | 62.2738 | 64.1561 | -1380.0951
2041-07-31 07:01 | -3488.47 | 6.4446 | 62.907 | 64.1561 | -1022.3696
2041-08-01 08:01 | -2266.96 | 6.2069 | 63.6541 | 64.1561 | -664.3804
2041-08-02 09:01 | -1820.96 | 4.9521 | 63.7844 | 64.1561 | -533.6707
2041-08-03 10:01 | -484.019 | 1.4578 | 64.0053 | 64.1561 | -141.852
2041-08-04 11:01 | 2895.46 | 1 | 64.7983 | 64.1561 | 848.5756
2041-08-05 12:01 | 3319.14 | 1.1141 | 77.6602 | 64.1561 | 972.7439
2041-08-06 13:01 | 4818.3 | 1.5517 | 78.4367 | 64.1561 | 1412.1043
2041-08-07 14:01 | 5396.2 | 1.7432 | 78.7395 | 64.1561 | 1581.4701
2041-08-08 15:01 | 5007.13 | 1.65 | 78.8208 | 64.1561 | 1467.4449
2041-08-09 16:01 | 3787.38 | 1.2463 | 79.0261 | 64.1561 | 1109.9715
2041-08-10 17:01 | 3847.01 | 1.2685 | 78.9877 | 64.1561 | 1127.4473
2041-08-11 18:01 | 2962.91 | 1 | 86.1535 | 64.1561 | 868.3432
2041-08-12 19:01 | 2822.29 | 1 | 66.4842 | 64.1561 | 827.1316
2041-08-13 20:01 | -282.37 | 1.3118 | 66.3023 | 64.1561 | -82.7545
2041-08-14 21:01 | -754.681 | 2.4575 | 65.6144 | 64.1561 | -221.1752
2041-08-15 22:01 | -1412.59 | 4.1118 | 65.2573 | 64.1561 | -413.9893
2041-08-16 23:01 | -1762.59 | 4.9136 | 64.9935 | 64.1561 | -516.5641
2041-08-18 00:01 | -3211.6 | 6.4446 | 64.2762 | 64.1561 | -941.227
2041-08-19 01:01 | -3789.19 | 6.4446 | 63.6161 | 64.1561 | -1110.502
2041-08-20 02:01 | -4190.59 | 6.4446 | 63.1319 | 64.1561 | -1228.1407
2041-08-21 03:01 | -4587.62 | 6.4446 | 62.6875 | 64.1561 | -1344.4987
2041-08-22 04:01 | -4714.61 | 6.4446 | 62.4216 | 64.1561 | -1381.7158
2041-08-23 05:01 | -4786.04 | 6.4446 | 62.2129 | 64.1561 | -1402.6499
2041-08-24 06:01 | -4639.07 | 6.4446 | 62.1816 | 64.1561 | -1359.5772
2041-08-25 07:01 | -4340.16 | 6.4446 | 62.2691 | 64.1561 | -1271.9753
2041-08-26 08:01 | -3837.9 | 6.4446 | 62.5359 | 64.1561 | -1124.7775
2041-08-27 09:01 | -3414.58 | 6.4446 | 62.801 | 64.1561 | -1000.7146
2041-08-28 10:01 | -1530.32 | 4.191 | 63.4576 | 64.1561 | -448.4925
2041-08-29 11:01 | -847.88 | 2.5087 | 63.7383 | 64.1561 | -248.4891
2041-08-30 12:01 | -480.832 | 1.669 | 64.0882 | 64.1561 | -140.9179
2041-08-31 13:01 | -380.481 | 1.472 | 64.3045 | 64.1561 | -111.508
2041-09-01 14:01 | -398.534 | 1.5356 | 64.3657 | 64.1561 | -116.7988
2041-09-02 15:01 | -264.855 | 1.174 | 64.5436 | 64.1561 | -77.6213
2041-09-03 16:01 | 2633.81 | 1 | 64.8319 | 64.1561 | 771.8935
2041-09-04 17:01 | 2813.57 | 1 | 65.1329 | 64.1561 | 824.576
2041-09-05 18:01 | 271.21 | 1 | 65.9642 | 64.1561 | 79.4838
2041-09-06 19:01 | -496.401 | 1.8673 | 64.8278 | 64.1561 | -145.4808
2041-09-07 20:01 | -980.008 | 3.0444 | 64.496 | 64.1561 | -287.212
2041-09-08 21:01 | -2118.97 | 6.0113 | 64.3231 | 64.1561 | -621.0088
2041-09-09 22:01 | -2692.91 | 6.4446 | 63.8612 | 64.1561 | -789.214
2041-09-10 23:01 | -4014.45 | 6.4446 | 62.8496 | 64.1561 | -1176.5192
2041-09-12 00:01 | -4194.78 | 6.4446 | 62.4963 | 64.1561 | -1229.3687
2041-09-13 01:01 | -4559.36 | 6.4446 | 62.1086 | 64.1561 | -1336.2165
2041-09-14 02:01 | -4802.41 | 6.4446 | 61.8118 | 64.1561 | -1407.4474
2041-09-15 03:01 | -4960.57 | 6.4446 | 61.584 | 64.1561 | -1453.7996
2041-09-16 04:01 | -5080.82 | 6.4446 | 61.3675 | 64.1561 | -1489.0414
2041-09-17 05:01 | -5015.61 | 6.4446 | 61.2887 | 64.1561 | -1469.9302
2041-09-18 06:01 | -4429.92 | 6.4446 | 61.5706 | 64.1561 | -1298.2814
2041-09-19 07:01 | -4719.96 | 6.4446 | 61.3967 | 64.1561 | -1383.2837
2041-09-20 08:01 | -1870.4 | 5.2194 | 62.8 | 64.1561 | -548.1601
2041-09-21 09:01 | -844.3 | 2.4225 | 63.1093 | 64.1561 | -247.4399
2041-09-22 10:01 | 2661.38 | 1 | 64.0997 | 64.1561 | 779.9735
2041-09-23 11:01 | 3388.57 | 1.1729 | 76.5836 | 64.1561 | 993.0918
2041-09-24 12:01 | 4991.32 | 1.7296 | 76.9381 | 64.1561 | 1462.8115
2041-09-25 13:01 | 5710.78 | 1.9755 | 77.4021 | 64.1561 | 1673.6644
2041-09-26 14:01 | 6277.11 | 2.1535 | 77.8718 | 64.1561 | 1839.6393
2041-09-27 15:01 | 6278.75 | 2.1169 | 78.4165 | 64.1561 | 1840.12
2041-09-28 16:01 | 6019.78 | 2.041 | 78.573 | 64.1561 | 1764.2234
2041-09-29 17:01 | 3907.3 | 1.3284 | 78.7084 | 64.1561 | 1145.1166
2041-09-30 18:01 | 2911.58 | 1 | 81.8066 | 64.1561 | 853.2999
2041-10-01 19:01 | 2823.15 | 1 | 66.3461 | 64.1561 | 827.3836
2041-10-02 20:01 | -144.985 | 0.9506 | 66.4008 | 64.1561 | -42.4909
2041-10-03 21:01 | -1488.3 | 4.4172 | 65.348 | 64.1561 | -436.1777
2041-10-04 22:01 | -2205.6 | 6.0824 | 64.8834 | 64.1561 | -646.3976
2041-10-05 23:01 | -3481.93 | 6.4446 | 63.9327 | 64.1561 | -1020.453
2041-10-07 00:01 | -3971.29 | 6.4446 | 63.3161 | 64.1561 | -1163.8702
2041-10-08 01:01 | -4125.76 | 6.4446 | 62.9272 | 64.1561 | -1209.1409
2041-10-09 02:01 | -4306.91 | 6.4446 | 62.618 | 64.1561 | -1262.2307
2041-10-10 03:01 | -4544.12 | 6.4446 | 62.3033 | 64.1561 | -1331.7501
2041-10-11 04:01 | -4412.43 | 6.4446 | 62.2156 | 64.1561 | -1293.1556
2041-10-12 05:01 | -4396.77 | 6.4446 | 62.1335 | 64.1561 | -1288.5661
2041-10-13 06:01 | -4267.01 | 6.4446 | 62.1382 | 64.1561 | -1250.5372
2041-10-14 07:01 | -3726.29 | 6.4446 | 62.4054 | 64.1561 | -1092.0678
2041-10-15 08:01 | -2256.31 | 6.2204 | 63.256 | 64.1561 | -661.2592
2041-10-16 09:01 | -916.656 | 2.5176 | 63.4027 | 64.1561 | -268.6454
2041-10-17 10:01 | 2746.85 | 1 | 64.3766 | 64.1561 | 805.0223
2041-10-18 11:01 | 3711.02 | 1.2308 | 77.367 | 64.1561 | 1087.5926
2041-10-19 12:01 | 5540.13 | 1.8153 | 77.8818 | 64.1561 | 1623.6518
2041-10-20 13:01 | 6518.65 | 2.1437 | 78.284 | 64.1561 | 1910.4277
2041-10-21 14:01 | 6989.55 | 2.2934 | 78.7261 | 64.1561 | 2048.4349
2041-10-22 15:01 | 6763.25 | 2.228 | 79.0272 | 64.1561 | 1982.1129
2041-10-23 16:01 | 5797.45 | 1.9245 | 79.1362 | 64.1561 | 1699.0649
2041-10-24 17:01 | 4270.5 | 1.3856 | 79.4892 | 64.1561 | 1251.56
2041-10-25 18:01 | 3079.45 | 1.0139 | 79.2492 | 64.1561 | 902.4977
2041-10-26 19:01 | 3003.88 | 1 | 66.5307 | 64.1561 | 880.3503
2041-10-27 20:01 | 2842.54 | 1 | 66.5385 | 64.1561 | 833.0662
2041-10-28 21:01 | -489.223 | 1.8557 | 66.1697 | 64.1561 | -143.3771
2041-10-29 22:01 | -958.281 | 2.9509 | 65.5371 | 64.1561 | -280.8444
2041-10-30 23:01 | -1818.75 | 5.1546 | 65.1756 | 64.1561 | -533.023
2041-11-01 00:01 | -2229.65 | 6.0785 | 64.8987 | 64.1561 | -653.4459
2041-11-02 01:01 | -2422.63 | 6.4446 | 64.6424 | 64.1561 | -710.0028
2041-11-03 02:01 | -2761.07 | 6.4446 | 64.2389 | 64.1561 | -809.1897
2041-11-04 03:01 | -3068.03 | 6.4446 | 63.9038 | 64.1561 | -899.1508
2041-11-05 04:01 | -3039.59 | 6.4446 | 63.7766 | 64.1561 | -890.8159
2041-11-06 05:01 | -2845.1 | 6.4446 | 63.8082 | 64.1561 | -833.8165
2041-11-07 06:01 | -2512.72 | 6.4446 | 63.97 | 64.1561 | -736.4055
2041-11-08 07:01 | -2241.92 | 6.0637 | 64.0373 | 64.1561 | -657.0419
2041-11-09 08:01 | -2117.09 | 5.7541 | 64.0337 | 64.1561 | -620.4578
2041-11-10 09:01 | -2503.01 | 6.4446 | 63.9625 | 64.1561 | -733.5598
2041-11-11 10:01 | -2170.96 | 5.877 | 63.9594 | 64.1561 | -636.2456
2041-11-12 11:01 | -1653.03 | 4.519 | 63.9403 | 64.1561 | -484.4553
2041-11-13 12:01 | -1175.53 | 3.3518 | 64.0037 | 64.1561 | -344.5138
2041-11-14 13:01 | -833.964 | 2.5371 | 64.1024 | 64.1561 | -244.4107
2041-11-15 14:01 | -551.299 | 1.8516 | 64.2338 | 64.1561 | -161.5698
2041-11-16 15:01 | -184.936 | 0.93432 | 64.6494 | 64.1561 | -54.1994
2041-11-17 16:01 | 2216.05 | 1 | 64.9419 | 64.1561 | 649.4601
2041-11-18 17:01 | 2819.08 | 1 | 65.0925 | 64.1561 | 826.1908
2041-11-19 18:01 | 2982.53 | 1 | 65.2909 | 64.1561 | 874.0933
2041-11-20 19:01 | 0 | 0 | 66.1531 | 64.1561 | 0
2041-11-21 20:01 | -471.22 | 1.6824 | 64.8474 | 64.1561 | -138.1009
2041-11-22 21:01 | -1460.45 | 4.3392 | 64.5223 | 64.1561 | -428.0156
2041-11-23 22:01 | -2008.16 | 5.5997 | 64.2832 | 64.1561 | -588.5336
2041-11-24 23:01 | -2672.01 | 6.4446 | 63.9014 | 64.1561 | -783.0888
2041-11-26 00:01 | -3256.64 | 6.4446 | 63.3593 | 64.1561 | -954.427
2041-11-27 01:01 | -3702.97 | 6.4446 | 62.9374 | 64.1561 | -1085.2334
2041-11-28 02:01 | -3923.08 | 6.4446 | 62.6576 | 64.1561 | -1149.7413
2041-11-29 03:01 | -4255.13 | 6.4446 | 62.3407 | 64.1561 | -1247.0555
2041-11-30 04:01 | -4590.17 | 6.4446 | 61.9944 | 64.1561 | -1345.246
2041-12-01 05:01 | -4487.98 | 6.4446 | 61.9033 | 64.1561 | -1315.2971
2041-12-02 06:01 | -4566.73 | 6.4446 | 61.7467 | 64.1561 | -1338.3764
2041-12-03 07:01 | -3795.63 | 6.4446 | 62.1352 | 64.1561 | -1112.3893
2041-12-04 08:01 | -2159.8 | 5.9725 | 63.0366 | 64.1561 | -632.9749
2041-12-05 09:01 | -2398.92 | 6.4446 | 63.1744 | 64.1561 | -703.0541
2041-12-06 10:01 | -1791.04 | 4.8843 | 63.2426 | 64.1561 | -524.902
2041-12-07 11:01 | -1422.12 | 4.0139 | 63.3676 | 64.1561 | -416.7822
2041-12-08 12:01 | 2165.28 | 1 | 64.3361 | 64.1561 | 634.5809
2041-12-09 13:01 | 2872.43 | 1 | 64.6234 | 64.1561 | 841.8261
2041-12-10 14:01 | 2874.69 | 1 | 81.2449 | 64.1561 | 842.4885
2041-12-11 15:01 | 2952.02 | 1.0197 | 77.1422 | 64.1561 | 865.1517
2041-12-12 16:01 | 2878.66 | 1 | 84.3718 | 64.1561 | 843.652
2041-12-13 17:01 | 2825.68 | 1 | 79.927 | 64.1561 | 828.1251
2041-12-14 18:01 | 2758.34 | 1 | 65.544 | 64.1561 | 808.3897
2041-12-15 19:01 | -333.993 | 1.4579 | 65.3757 | 64.1561 | -97.8837
2041-12-16 20:01 | -921.667 | 2.9132 | 64.7428 | 64.1561 | -270.1139
2041-12-17 21:01 | -1525.72 | 4.4169 | 64.4375 | 64.1561 | -447.1444
2041-12-18 22:01 | -2080.87 | 5.7922 | 64.2404 | 64.1561 | -609.8428
2041-12-19 23:01 | -2612.68 | 6.4446 | 63.9036 | 64.1561 | -765.7009
2041-12-21 00:01 | -4565.02 | 6.4446 | 62.5167 | 64.1561 | -1337.8753
2041-12-22 01:01 | -4981.22 | 6.4446 | 61.9348 | 64.1561 | -1459.8515
2041-12-23 02:01 | -5171.49 | 6.4446 | 61.5645 | 64.1561 | -1515.6141
2041-12-24 03:01 | -5442.19 | 6.4446 | 61.2129 | 64.1561 | -1594.9484
2041-12-25 04:01 | -5609.5 | 6.4446 | 60.9271 | 64.1561 | -1643.9822
2041-12-26 05:01 | -5823.42 | 6.4446 | 60.6216 | 64.1561 | -1706.6759
2041-12-27 06:01 | -6027.13 | 6.4446 | 60.35 | 64.1561 | -1766.3774
2041-12-28 07:01 | -5000.12 | 6.4446 | 60.8501 | 64.1561 | -1465.3905
2041-12-29 08:01 | -2971.37 | 6.4446 | 62.089 | 64.1561 | -870.8226
2041-12-30 09:01 | -1863.74 | 5.1412 | 62.6801 | 64.1561 | -546.2083
2041-12-31 10:01 | -454.103 | 1.3754 | 63.01 | 64.1561 | -133.0845
2042-01-01 11:01 | 2845.13 | 1 | 63.8894 | 64.1561 | 833.8253
2042-01-02 12:01 | 3263.96 | 1.1341 | 76.3901 | 64.1561 | 956.5722
2042-01-03 13:01 | 4433.97 | 1.5112 | 76.9489 | 64.1561 | 1299.4683
2042-01-04 14:01 | 4730.56 | 1.628 | 77.1854 | 64.1561 | 1386.3903
2042-01-05 15:01 | 4879.86 | 1.6757 | 77.5052 | 64.1561 | 1430.1458
2042-01-06 16:01 | 3901.49 | 1.3432 | 77.7124 | 64.1561 | 1143.4138
2042-01-07 17:01 | 4197.14 | 1.4334 | 77.8517 | 64.1561 | 1230.0603
2042-01-08 18:01 | 2857.63 | 1 | 82.2583 | 64.1561 | 837.4887
2042-01-09 19:01 | 2809.84 | 1 | 65.8221 | 64.1561 | 823.4828
2042-01-10 20:01 | 0 | 0 | 66.5029 | 64.1561 | 0
2042-01-11 21:01 | -564.231 | 1.9419 | 65.084 | 64.1561 | -165.3598
2042-01-12 22:01 | -843.574 | 2.6655 | 64.7846 | 64.1561 | -247.2271
2042-01-13 23:01 | -1274.68 | 3.7605 | 64.5439 | 64.1561 | -373.5718
2042-01-15 00:01 | -2156.95 | 6.05 | 64.338 | 64.1561 | -632.1396
2042-01-16 01:01 | -2728.3 | 6.4446 | 63.8589 | 64.1561 | -799.5858
2042-01-17 02:01 | -3161.67 | 6.4446 | 63.4192 | 64.1561 | -926.594
2042-01-18 03:01 | -3388.56 | 6.4446 | 63.1195 | 64.1561 | -993.0889
2042-01-19 04:01 | -3554.38 | 6.4446 | 62.8841 | 64.1561 | -1041.6859
2042-01-20 05:01 | -3258.41 | 6.4446 | 62.9395 | 64.1561 | -954.9457
2042-01-21 06:01 | -2357.17 | 6.4446 | 63.441 | 64.1561 | -690.8183
2042-01-22 07:01 | -2192.9 | 5.9653 | 63.4845 | 64.1561 | -642.6755
2042-01-23 08:01 | -1810.83 | 4.9634 | 63.5314 | 64.1561 | -530.7019
2042-01-24 09:01 | -2071.83 | 5.7633 | 63.6026 | 64.1561 | -607.1934
2042-01-25 10:01 | -1622.76 | 4.4677 | 63.5741 | 64.1561 | -475.584
2042-01-26 11:01 | -852.967 | 2.4994 | 63.678 | 64.1561 | -249.98
2042-01-27 12:01 | 0 | 1 | 65.0872 | 64.1561 | 0
2042-01-28 13:01 | 2223.09 | 1 | 64.6701 | 64.1561 | 651.5234
2042-01-29 14:01 | 5209.37 | 1.8687 | 76.4206 | 64.1561 | 1526.7156
2042-01-30 15:01 | 3919.59 | 1.2947 | 77.8522 | 64.1561 | 1148.7184
2042-01-31 16:01 | 5960.23 | 2.0307 | 77.6451 | 64.1561 | 1746.771
2042-02-01 17:01 | 5317.97 | 1.6878 | 78.8443 | 64.1561 | 1558.5432
2042-02-02 18:01 | 5317.28 | 1.6619 | 79.238 | 64.1561 | 1558.3409
2042-02-03 19:01 | 4424.38 | 1.3716 | 79.4839 | 64.1561 | 1296.6578
2042-02-04 20:01 | 3661.12 | 1.1804 | 79.0149 | 64.1561 | 1072.9684
2042-02-05 21:01 | 3148.66 | 1 | 87.7334 | 64.1561 | 922.7812
2042-02-06 22:01 | 3239.51 | 1 | 66.0855 | 64.1561 | 949.4067
2042-02-07 23:01 | 0 | 0 | 66.901 | 64.1561 | 0
2042-02-09 00:01 | -190.787 | 0.93184 | 65.778 | 64.1561 | -55.9142
2042-02-10 01:01 | -732.011 | 2.4373 | 65.2138 | 64.1561 | -214.5312
2042-02-11 02:01 | -1329.88 | 3.9112 | 64.8987 | 64.1561 | -389.7494
2042-02-12 03:01 | -1996.94 | 5.5818 | 64.657 | 64.1561 | -585.2453
2042-02-13 04:01 | -2760.58 | 6.4446 | 64.1557 | 64.1561 | -809.0461
2042-02-14 05:01 | -3209.33 | 6.4446 | 63.6853 | 64.1561 | -940.5618
2042-02-15 06:01 | -3016.07 | 6.4446 | 63.608 | 64.1561 | -883.9229
2042-02-16 07:01 | -2942.85 | 6.4446 | 63.5376 | 64.1561 | -862.4642
2042-02-17 08:01 | -3569 | 6.4446 | 63.0659 | 64.1561 | -1045.9706
2042-02-18 09:01 | -3982.39 | 6.4446 | 62.6588 | 64.1561 | -1167.1233
2042-02-19 10:01 | -3498.83 | 6.4446 | 62.7833 | 64.1561 | -1025.4059
2042-02-20 11:01 | -3200.4 | 6.4446 | 62.9132 | 64.1561 | -937.9447
2042-02-21 12:01 | -3519.94 | 6.4446 | 62.6832 | 64.1561 | -1031.5926
2042-02-22 13:01 | -3399.21 | 6.4446 | 62.6443 | 64.1561 | -996.2101
2042-02-23 14:01 | -3382.15 | 6.4446 | 62.5639 | 64.1561 | -991.2103
2042-02-24 15:01 | -3569.7 | 6.4446 | 62.3842 | 64.1561 | -1046.1758
2042-02-25 16:01 | -2888.8 | 6.4446 | 62.6942 | 64.1561 | -846.6237
2042-02-26 17:01 | -3156.52 | 6.4446 | 62.5149 | 64.1561 | -925.0847
2042-02-27 18:01 | -3189.66 | 6.4446 | 62.4288 | 64.1561 | -934.7971
2042-02-28 19:01 | -3740.88 | 6.4446 | 62.0232 | 64.1561 | -1096.3437
2042-03-01 20:01 | -4014.92 | 6.4446 | 61.7508 | 64.1561 | -1176.6569
2042-03-02 21:01 | -5040.03 | 6.4446 | 61.0312 | 64.1561 | -1477.087
2042-03-03 22:01 | -5397.37 | 6.4446 | 60.6126 | 64.1561 | -1581.813
2042-03-04 23:01 | -6130.83 | 6.4446 | 60.0022 | 64.1561 | -1796.7689
2042-03-06 00:01 | -6893.05 | 6.4446 | 59.3454 | 64.1561 | -2020.1535
2042-03-07 01:01 | -7195.97 | 6.4446 | 58.9398 | 64.1561 | -2108.9306
2042-03-08 02:01 | -7484.53 | 6.4446 | 58.5754 | 64.1561 | -2193.4992
2042-03-09 03:01 | -7935.01 | 6.4446 | 58.1415 | 64.1561 | -2325.5219
2042-03-10 04:01 | -7903.86 | 6.4446 | 57.9759 | 64.1561 | -2316.3927
2042-03-11 05:01 | -7846.7 | 6.4446 | 57.8775 | 64.1561 | -2299.6408
2042-03-12 06:01 | -7545.32 | 6.4446 | 57.9572 | 64.1561 | -2211.315
2042-03-13 07:01 | -7107.59 | 6.4446 | 58.1597 | 64.1561 | -2083.029
2042-03-14 08:01 | -5776.9 | 6.4446 | 58.9468 | 64.1561 | -1693.0423
2042-03-15 09:01 | -4777.41 | 6.4446 | 59.6761 | 64.1561 | -1400.1207
2042-03-16 10:01 | -3114.17 | 6.4446 | 60.8426 | 64.1561 | -912.6731
2042-03-17 11:01 | -1709.83 | 4.7862 | 61.595 | 64.1561 | -501.1017
2042-03-18 12:01 | -763.278 | 2.2731 | 61.986 | 64.1561 | -223.6947
2042-03-19 13:01 | 94.5076 | 1 | 63.5708 | 64.1561 | 27.6974
2042-03-20 14:01 | 1789.76 | 1 | 63.4403 | 64.1561 | 524.5269
2042-03-21 15:01 | -521.608 | 2.0004 | 63.2311 | 64.1561 | -152.8682
2042-03-22 16:01 | -1061.76 | 3.311 | 62.9738 | 64.1561 | -311.1711
2042-03-23 17:01 | -1705.84 | 4.9631 | 62.8376 | 64.1561 | -499.9324
2042-03-24 18:01 | -2174.24 | 6.1091 | 62.7433 | 64.1561 | -637.2068
2042-03-25 19:01 | -2988.3 | 6.4446 | 62.2561 | 64.1561 | -875.7843
2042-03-26 20:01 | -3640.27 | 6.4446 | 61.7023 | 64.1561 | -1066.8578
2042-03-27 21:01 | -4936.05 | 6.4446 | 60.7774 | 64.1561 | -1446.6135
2042-03-28 22:01 | -5468.04 | 6.4446 | 60.22 | 64.1561 | -1602.5243
2042-03-29 23:01 | -6720.12 | 6.4446 | 59.2568 | 64.1561 | -1969.4728
2042-03-31 00:01 | -7755.14 | 6.4446 | 58.3508 | 64.1561 | -2272.8072
2042-04-01 01:01 | -8122.1 | 6.4446 | 57.8181 | 64.1561 | -2380.3525
2042-04-02 02:01 | -8420.99 | 6.4446 | 57.3699 | 64.1561 | -2467.9485
2042-04-03 03:01 | -8690.65 | 6.4446 | 57.0035 | 64.1561 | -2546.9781
2042-04-04 04:01 | -8761.3 | 6.4446 | 56.7693 | 64.1561 | -2567.6836
2042-04-05 05:01 | -9115.53 | 6.4446 | 56.4071 | 64.1561 | -2671.4981
2042-04-06 06:01 | -9114.97 | 6.4446 | 56.2529 | 64.1561 | -2671.334
2042-04-07 07:01 | -8097.51 | 6.4446 | 56.7477 | 64.1561 | -2373.1459
2042-04-08 08:01 | -6310.1 | 6.4446 | 57.8404 | 64.1561 | -1849.3078
2042-04-09 09:01 | -5150.69 | 6.4446 | 58.7178 | 64.1561 | -1509.5182
2042-04-10 10:01 | -3968.96 | 6.4446 | 59.6188 | 64.1561 | -1163.1874
2042-04-11 11:01 | -3354.77 | 6.4446 | 60.2095 | 64.1561 | -983.186
2042-04-12 12:01 | -1806.33 | 5.1021 | 61.0617 | 64.1561 | -529.3831
2042-04-13 13:01 | -768.264 | 2.2725 | 61.4149 | 64.1561 | -225.156
2042-04-14 14:01 | -295.603 | 1.2224 | 62.0723 | 64.1561 | -86.6327
2042-04-15 15:01 | 0 | 1 | 63.2537 | 64.1561 | 0
2042-04-16 16:01 | -542.882 | 2.0263 | 62.397 | 64.1561 | -159.103
2042-04-17 17:01 | -337.127 | 1.3513 | 62.5703 | 64.1561 | -98.8022
2042-04-18 18:01 | -1312.03 | 4.0705 | 62.4054 | 64.1561 | -384.518
2042-04-19 19:01 | -2113.1 | 6.0575 | 62.2926 | 64.1561 | -619.2885
2042-04-20 20:01 | -2876.47 | 6.4446 | 61.8337 | 64.1561 | -843.0101
2042-04-21 21:01 | -3269.24 | 6.4446 | 61.4898 | 64.1561 | -958.1197
2042-04-22 22:01 | -3795.01 | 6.4446 | 61.0832 | 64.1561 | -1112.2076
2042-04-23 23:01 | -4233.52 | 6.4446 | 60.71 | 64.1561 | -1240.7222
2042-04-25 00:01 | -5183.62 | 6.4446 | 60.0246 | 64.1561 | -1519.1691
2042-04-26 01:01 | -5674.69 | 6.4446 | 59.5538 | 64.1561 | -1663.0875
2042-04-27 02:01 | -6238.7 | 6.4446 | 59.0531 | 64.1561 | -1828.3825
2042-04-28 03:01 | -6035.56 | 6.4446 | 59.0121 | 64.1561 | -1768.848
2042-04-29 04:01 | -5842.98 | 6.4446 | 59.0448 | 64.1561 | -1712.4084
2042-04-30 05:01 | -6052.67 | 6.4446 | 58.8689 | 64.1561 | -1773.8625
2042-05-01 06:01 | -5543.9 | 6.4446 | 59.1158 | 64.1561 | -1624.7567
2042-05-02 07:01 | -5047.74 | 6.4446 | 59.4284 | 64.1561 | -1479.3466
2042-05-03 08:01 | -3205.8 | 6.4446 | 60.6014 | 64.1561 | -939.5272
2042-05-04 09:01 | -1915.11 | 5.3834 | 61.372 | 64.1561 | -561.2633
2042-05-05 10:01 | -1153.7 | 3.3068 | 61.6472 | 64.1561 | -338.1161
2042-05-06 11:01 | 0 | 0 | 63.2374 | 64.1561 | 0
2042-05-07 12:01 | -172.685 | 0.99988 | 62.8272 | 64.1561 | -50.609
2042-05-08 13:01 | 92.5424 | 1 | 63.6394 | 64.1561 | 27.1215
2042-05-09 14:01 | 0 | 0 | 63.7829 | 64.1561 | 0
2042-05-10 15:01 | 0 | 1 | 63.8653 | 64.1561 | 0
2042-05-11 16:01 | 2871.46 | 1 | 63.2466 | 64.1561 | 841.5419
2042-05-12 17:01 | 2521.33 | 1 | 63.7086 | 64.1561 | 738.9289
2042-05-13 18:01 | 982.117 | 1 | 64.2832 | 64.1561 | 287.8301
2042-05-14 19:01 | -394.756 | 1.6456 | 63.5407 | 64.1561 | -115.6916
2042-05-15 20:01 | -698.483 | 2.3493 | 63.1976 | 64.1561 | -204.7052
2042-05-16 21:01 | -1690.64 | 4.9963 | 62.9913 | 64.1561 | -495.4777
2042-05-17 22:01 | -2462.2 | 6.4446 | 62.6577 | 64.1561 | -721.5996
2042-05-18 23:01 | -3439.77 | 6.4446 | 61.8736 | 64.1561 | -1008.0971
2042-05-20 00:01 | -4384.37 | 6.4446 | 61.1012 | 64.1561 | -1284.932
2042-05-21 01:01 | -4710.99 | 6.4446 | 60.6921 | 64.1561 | -1380.6549
2042-05-22 02:01 | -4454.34 | 6.4446 | 60.684 | 64.1561 | -1305.4382
2042-05-23 03:01 | -4320.76 | 6.4446 | 60.693 | 64.1561 | -1266.2898
2042-05-24 04:01 | -4322.98 | 6.4446 | 60.6194 | 64.1561 | -1266.9404
2042-05-25 05:01 | -4375.62 | 6.4446 | 60.5253 | 64.1561 | -1282.3676
2042-05-26 06:01 | -4441 | 6.4446 | 60.4433 | 64.1561 | -1301.5286
2042-05-27 07:01 | -3674.13 | 6.4446 | 60.8759 | 64.1561 | -1076.7812
2042-05-28 08:01 | -2409.65 | 6.4446 | 61.6881 | 64.1561 | -706.1987
2042-05-29 09:01 | -2062.16 | 5.7257 | 61.8935 | 64.1561 | -604.3594
2042-05-30 10:01 | -1157.67 | 3.2707 | 62.0241 | 64.1561 | -339.2796
2042-05-31 11:01 | -954.538 | 2.93 | 62.2956 | 64.1561 | -279.7475
2042-06-01 12:01 | -732.562 | 2.3475 | 62.4874 | 64.1561 | -214.6927
2042-06-02 13:01 | -559.343 | 1.9235 | 62.6827 | 64.1561 | -163.9273
2042-06-03 14:01 | -140.974 | 0.82282 | 63.2385 | 64.1561 | -41.3154
2042-06-04 15:01 | -167.837 | 0.99042 | 63.3582 | 64.1561 | -49.1882
2042-06-05 16:01 | -673.274 | 2.339 | 62.9472 | 64.1561 | -197.3171
2042-06-06 17:01 | -434.164 | 1.5793 | 62.9796 | 64.1561 | -127.2409
2042-06-07 18:01 | -1345.68 | 4.1248 | 62.8217 | 64.1561 | -394.3799
2042-06-08 19:01 | -2153.53 | 6.1356 | 62.6681 | 64.1561 | -631.1373
2042-06-09 20:01 | -2948.13 | 6.4446 | 62.1218 | 64.1561 | -864.0116
2042-06-10 21:01 | -3473.94 | 6.4446 | 61.6517 | 64.1561 | -1018.1113
2042-06-11 22:01 | -3891.32 | 6.4446 | 61.2552 | 64.1561 | -1140.4333
2042-06-12 23:01 | -4277.18 | 6.4446 | 60.8789 | 64.1561 | -1253.5177
2042-06-14 00:01 | -5981.13 | 6.4446 | 59.7167 | 64.1561 | -1752.8962
2042-06-15 01:01 | -6403.21 | 6.4446 | 59.1849 | 64.1561 | -1876.5956
2042-06-16 02:01 | -6625.08 | 6.4446 | 58.8308 | 64.1561 | -1941.6193
2042-06-17 03:01 | -6855.71 | 6.4446 | 58.5252 | 64.1561 | -2009.2103
2042-06-18 04:01 | -7099.06 | 6.4446 | 58.2204 | 64.1561 | -2080.5291
2042-06-19 05:01 | -7153.35 | 6.4446 | 58.0258 | 64.1561 | -2096.4399
2042-06-20 06:01 | -6925.1 | 6.4446 | 58.0549 | 64.1561 | -2029.5465
2042-06-21 07:01 | -6211.01 | 6.4446 | 58.4246 | 64.1561 | -1820.2673
2042-06-22 08:01 | -4192.2 | 6.4446 | 59.6584 | 64.1561 | -1228.6125
2042-06-23 09:01 | -3193.16 | 6.4446 | 60.4661 | 64.1561 | -935.8228
2042-06-24 10:01 | -1574.46 | 4.4304 | 61.2099 | 64.1561 | -461.4287
2042-06-25 11:01 | -495.711 | 1.5776 | 61.6433 | 64.1561 | -145.2786
2042-06-26 12:01 | 2754.93 | 1 | 62.5213 | 64.1561 | 807.3903
2042-06-27 13:01 | 2882.35 | 1 | 63.0514 | 64.1561 | 844.7334
2042-06-28 14:01 | 2902.35 | 1 | 75.7266 | 64.1561 | 850.5948
2042-06-29 15:01 | 2952.57 | 1 | 77.1204 | 64.1561 | 865.3128
2042-06-30 16:01 | 2939.11 | 1 | 63.8293 | 64.1561 | 861.3681
2042-07-01 17:01 | 2879.35 | 1 | 80.6244 | 64.1561 | 843.8542
2042-07-02 18:01 | 2766.71 | 1 | 64.1745 | 64.1561 | 810.8427
2042-07-03 19:01 | -467.063 | 1.84 | 63.9554 | 64.1561 | -136.8827
2042-07-04 20:01 | -1031.23 | 3.2235 | 63.4341 | 64.1561 | -302.2237
2042-07-05 21:01 | -1622.21 | 4.722 | 63.1691 | 64.1561 | -475.4228
2042-07-06 22:01 | -2150.53 | 6.047 | 62.9913 | 64.1561 | -630.2581
2042-07-07 23:01 | -2352.1 | 6.4446 | 62.8047 | 64.1561 | -689.3325
2042-07-09 00:01 | -3802.77 | 6.4446 | 61.7771 | 64.1561 | -1114.4819
2042-07-10 01:01 | -4420.89 | 6.4446 | 61.1771 | 64.1561 | -1295.635
2042-07-11 02:01 | -4545.38 | 6.4446 | 60.8925 | 64.1561 | -1332.1194
2042-07-12 03:01 | -5022.55 | 6.4446 | 60.4627 | 64.1561 | -1471.9641
2042-07-13 04:01 | -5185.56 | 6.4446 | 60.2043 | 64.1561 | -1519.7376
2042-07-14 05:01 | -5246.03 | 6.4446 | 60.0211 | 64.1561 | -1537.4596
2042-07-15 06:01 | -4973.04 | 6.4446 | 60.0829 | 64.1561 | -1457.4542
2042-07-16 07:01 | -4409.22 | 6.4446 | 60.3954 | 64.1561 | -1292.2148
2042-07-17 08:01 | -3025.32 | 6.4446 | 61.2507 | 64.1561 | -886.6338
2042-07-18 09:01 | -1947.49 | 5.4349 | 61.8297 | 64.1561 | -570.753
2042-07-19 10:01 | 0 | 0 | 63.4139 | 64.1561 | 0
2042-07-20 11:01 | 2726.35 | 1 | 63.0722 | 64.1561 | 799.0143
2042-07-21 12:01 | 3096.85 | 1.0029 | 76.3159 | 64.1561 | 907.5971
2042-07-22 13:01 | 4819.17 | 1.5172 | 76.959 | 64.1561 | 1412.3593
2042-07-23 14:01 | 4104.45 | 1.3455 | 76.8747 | 64.1561 | 1202.8956
2042-07-24 15:01 | 3357.16 | 1.0967 | 77.1345 | 64.1561 | 983.8865
2042-07-25 16:01 | 3283.75 | 1.0553 | 77.4152 | 64.1561 | 962.3721
2042-07-26 17:01 | 3155.9 | 1 | 79.2276 | 64.1561 | 924.903
2042-07-27 18:01 | 3113.21 | 1 | 81.5575 | 64.1561 | 912.3918
2042-07-28 19:01 | 3010.4 | 1 | 64.7541 | 64.1561 | 882.2611
2042-07-29 20:01 | 1940.57 | 1 | 65.0858 | 64.1561 | 568.7249
2042-07-30 21:01 | -621.951 | 2.242 | 64.4246 | 64.1561 | -182.2758
2042-07-31 22:01 | -987.832 | 3.0531 | 63.9572 | 64.1561 | -289.505
2042-08-01 23:01 | -1765.22 | 5.0961 | 63.6725 | 64.1561 | -517.3349
2042-08-03 00:01 | -2060.48 | 5.7322 | 63.4374 | 64.1561 | -603.8671
2042-08-04 01:01 | -2409.75 | 6.4446 | 63.2013 | 64.1561 | -706.228
2042-08-05 02:01 | -2256.11 | 6.1738 | 63.0797 | 64.1561 | -661.2006
2042-08-06 03:01 | -2131.55 | 5.8563 | 63.0318 | 64.1561 | -624.6956
2042-08-07 04:01 | -1817.15 | 5.0231 | 63.0122 | 64.1561 | -532.5541
2042-08-08 05:01 | -1353.81 | 3.8298 | 63.058 | 64.1561 | -396.7625
2042-08-09 06:01 | -768.628 | 2.3433 | 63.2086 | 64.1561 | -225.2626
2042-08-10 07:01 | -528.357 | 1.8237 | 63.4482 | 64.1561 | -154.8462
2042-08-11 08:01 | -421.724 | 1.5803 | 63.6068 | 64.1561 | -123.5951
2042-08-12 09:01 | -633.687 | 2.17 | 63.574 | 64.1561 | -185.7153
2042-08-13 10:01 | -292.128 | 1.2004 | 63.775 | 64.1561 | -85.6143
2042-08-14 11:01 | 2059.78 | 1 | 64.2771 | 64.1561 | 603.6619
2042-08-15 12:01 | 2994.56 | 1.0264 | 76.4829 | 64.1561 | 877.6189
2042-08-16 13:01 | 3057.05 | 1 | 78.0946 | 64.1561 | 895.9329
2042-08-17 14:01 | 3121.34 | 1 | 79.7211 | 64.1561 | 914.7745
2042-08-18 15:01 | 3208.81 | 1 | 81.4693 | 64.1561 | 940.4094
2042-08-19 16:01 | 4400.05 | 1.3815 | 78.1313 | 64.1561 | 1289.5274
2042-08-20 17:01 | 4735.92 | 1.4857 | 78.35 | 64.1561 | 1387.9611
2042-08-21 18:01 | 4987.42 | 1.5537 | 78.5978 | 64.1561 | 1461.6685
2042-08-22 19:01 | 3998.56 | 1.2838 | 78.3749 | 64.1561 | 1171.8623
2042-08-23 20:01 | 3362.01 | 1.0615 | 78.6019 | 64.1561 | 985.3079
2042-08-24 21:01 | 3128.41 | 1 | 65.4704 | 64.1561 | 916.8465
2042-08-25 22:01 | 3073.87 | 1 | 65.501 | 64.1561 | 900.8624
2042-08-26 23:01 | -156.19 | 0.98881 | 65.6288 | 64.1561 | -45.7748
2042-08-28 00:01 | -427.649 | 1.6423 | 64.8761 | 64.1561 | -125.3316
2042-08-29 01:01 | -817.422 | 2.6307 | 64.4739 | 64.1561 | -239.5627
2042-08-30 02:01 | -1311.05 | 3.8753 | 64.2337 | 64.1561 | -384.2308
2042-08-31 03:01 | -1810.73 | 5.1245 | 64.0172 | 64.1561 | -530.6726
2042-09-01 04:01 | -1937.89 | 5.3703 | 63.7958 | 64.1561 | -567.9395
2042-09-02 05:01 | -1864.43 | 5.1552 | 63.68 | 64.1561 | -546.4105
2042-09-03 06:01 | -1749.84 | 4.8678 | 63.6039 | 64.1561 | -512.8275
2042-09-04 07:01 | -1761.58 | 4.9292 | 63.5538 | 64.1561 | -516.2681
2042-09-05 08:01 | -1939.88 | 5.4138 | 63.4935 | 64.1561 | -568.5227
2042-09-06 09:01 | -1904.95 | 5.279 | 63.4127 | 64.1561 | -558.2857
2042-09-07 10:01 | -379.332 | 1.1548 | 63.4722 | 64.1561 | -111.1712
2042-09-08 11:01 | 2781.59 | 1 | 64.2226 | 64.1561 | 815.2036
2042-09-09 12:01 | 2873.25 | 1 | 80.2624 | 64.1561 | 842.0665
2042-09-10 13:01 | 3007.72 | 1.0572 | 76.6339 | 64.1561 | 881.4757
2042-09-11 14:01 | 3193.53 | 1.1218 | 76.7966 | 64.1561 | 935.9313
2042-09-12 15:01 | 2842.68 | 1 | 78.4673 | 64.1561 | 833.1073
2042-09-13 16:01 | 2848.68 | 1 | 77.4705 | 64.1561 | 834.8657
2042-09-14 17:01 | 2803.97 | 1 | 65.2736 | 64.1561 | 821.7625
2042-09-15 18:01 | 2793.64 | 1 | 65.315 | 64.1561 | 818.7351
2042-09-16 19:01 | -178.746 | 1.0577 | 65.3574 | 64.1561 | -52.3853
2042-09-17 20:01 | -740 | 2.4673 | 64.5533 | 64.1561 | -216.8726
2042-09-18 21:01 | -1912.36 | 5.513 | 64.1725 | 64.1561 | -560.4574
2042-09-19 22:01 | -2370.99 | 6.4446 | 63.8575 | 64.1561 | -694.8686
2042-09-20 23:01 | -3649.13 | 6.4446 | 62.8574 | 64.1561 | -1069.4544
2042-09-22 00:01 | -4058.95 | 6.4446 | 62.2974 | 64.1561 | -1189.5608
2042-09-23 01:01 | -4430.3 | 6.4446 | 61.8469 | 64.1561 | -1298.3928
2042-09-24 02:01 | -4650.78 | 6.4446 | 61.5131 | 64.1561 | -1363.0091
2042-09-25 03:01 | -4828.83 | 6.4446 | 61.2378 | 64.1561 | -1415.1904
2042-09-26 04:01 | -4772.66 | 6.4446 | 61.1143 | 64.1561 | -1398.7286
2042-09-27 05:01 | -4582.19 | 6.4446 | 61.1169 | 64.1561 | -1342.9073
2042-09-28 06:01 | -4164.43 | 6.4446 | 61.2871 | 64.1561 | -1220.474
2042-09-29 07:01 | -3674.39 | 6.4446 | 61.5718 | 64.1561 | -1076.8574
2042-09-30 08:01 | -3303.29 | 6.4446 | 61.8217 | 64.1561 | -968.0987
2042-10-01 09:01 | -2998.51 | 6.4446 | 62.0513 | 64.1561 | -878.7765
2042-10-02 10:01 | -2310.04 | 6.3975 | 62.4981 | 64.1561 | -677.0059
2042-10-03 11:01 | 0 | 0 | 63.9883 | 64.1561 | 0
2042-10-04 12:01 | -480.209 | 1.8453 | 63.2564 | 64.1561 | -140.7354
2042-10-05 13:01 | -371.218 | 1.447 | 63.368 | 64.1561 | -108.7933
2042-10-06 14:01 | -485.915 | 1.7893 | 63.3685 | 64.1561 | -142.4076
2042-10-07 15:01 | -370.131 | 1.4472 | 63.4835 | 64.1561 | -108.4747
2042-10-08 16:01 | 580.001 | 1 | 64.4007 | 64.1561 | 169.9815
2042-10-09 17:01 | 1067.11 | 1 | 64.3963 | 64.1561 | 312.7391
2042-10-10 18:01 | 821.337 | 1 | 64.5795 | 64.1561 | 240.7101
2042-10-11 19:01 | -211.196 | 1.1497 | 64.115 | 64.1561 | -61.8954
2042-10-12 20:01 | -555.082 | 1.9918 | 63.6878 | 64.1561 | -162.6785
2042-10-13 21:01 | -1455.98 | 4.3606 | 63.4384 | 64.1561 | -426.7056
2042-10-14 22:01 | -1753.18 | 4.9717 | 63.2527 | 64.1561 | -513.8063
2042-10-15 23:01 | -2762.19 | 6.4446 | 62.8468 | 64.1561 | -809.518
2042-10-17 00:01 | -3242.56 | 6.4446 | 62.3841 | 64.1561 | -950.3005
2042-10-18 01:01 | -3483.62 | 6.4446 | 62.0905 | 64.1561 | -1020.9482
2042-10-19 02:01 | -3683.54 | 6.4446 | 61.8564 | 64.1561 | -1079.539
2042-10-20 03:01 | -3694.9 | 6.4446 | 61.758 | 64.1561 | -1082.8683
2042-10-21 04:01 | -3680.14 | 6.4446 | 61.6874 | 64.1561 | -1078.5426
2042-10-22 05:01 | -3624.12 | 6.4446 | 61.6636 | 64.1561 | -1062.1247
2042-10-23 06:01 | -3603.42 | 6.4446 | 61.633 | 64.1561 | -1056.0582
2042-10-24 07:01 | -3655.82 | 6.4446 | 61.5683 | 64.1561 | -1071.4151
2042-10-25 08:01 | -3877.32 | 6.4446 | 61.3945 | 64.1561 | -1136.3303
2042-10-26 09:01 | -4469.21 | 6.4446 | 60.9774 | 64.1561 | -1309.7962
2042-10-27 10:01 | -4356.98 | 6.4446 | 60.9234 | 64.1561 | -1276.9048
2042-10-28 11:01 | -4257.89 | 6.4446 | 60.895 | 64.1561 | -1247.8644
2042-10-29 12:01 | -3927.32 | 6.4446 | 61.0345 | 64.1561 | -1150.9839
2042-10-30 13:01 | -3974.59 | 6.4446 | 60.974 | 64.1561 | -1164.8373
2042-10-31 14:01 | -4071.69 | 6.4446 | 60.8659 | 64.1561 | -1193.2945
2042-11-01 15:01 | -3917.28 | 6.4446 | 60.9042 | 64.1561 | -1148.0414
2042-11-02 16:01 | -3223.88 | 6.4446 | 61.2871 | 64.1561 | -944.826
2042-11-03 17:01 | -3004.59 | 6.4446 | 61.4529 | 64.1561 | -880.5584
2042-11-04 18:01 | -2806.3 | 6.4446 | 61.5892 | 64.1561 | -822.4453
2042-11-05 19:01 | -3188.13 | 6.4446 | 61.38 | 64.1561 | -934.3487
2042-11-06 20:01 | -3688.2 | 6.4446 | 61.0492 | 64.1561 | -1080.9047
2042-11-07 21:01 | -4728.11 | 6.4446 | 60.3596 | 64.1561 | -1385.6723
2042-11-08 22:01 | -5225.04 | 6.4446 | 59.9046 | 64.1561 | -1531.3081
2042-11-09 23:01 | -6259.2 | 6.4446 | 59.1348 | 64.1561 | -1834.3904
2042-11-11 00:01 | -7410.82 | 6.4446 | 58.2257 | 64.1561 | -2171.8969
2042-11-12 01:01 | -7886.46 | 6.4446 | 57.6693 | 64.1561 | -2311.2933
2042-11-13 02:01 | -8324.33 | 6.4446 | 57.1784 | 64.1561 | -2439.6203
2042-11-14 03:01 | -8666.31 | 6.4446 | 56.77 | 64.1561 | -2539.8447
2042-11-15 04:01 | -8931.86 | 6.4446 | 56.4056 | 64.1561 | -2617.6698
2042-11-16 05:01 | -9195.67 | 6.4446 | 56.0571 | 64.1561 | -2694.9848
2042-11-17 06:01 | -9377.73 | 6.4446 | 55.7684 | 64.1561 | -2748.3414
2042-11-18 07:01 | -8463.28 | 6.4446 | 56.1572 | 64.1561 | -2480.3425
2042-11-19 08:01 | -6816 | 6.4446 | 57.1251 | 64.1561 | -1997.5724
2042-11-20 09:01 | -5980.81 | 6.4446 | 57.7669 | 64.1561 | -1752.8024
2042-11-21 10:01 | -4476.99 | 6.4446 | 58.8106 | 64.1561 | -1312.0762
2042-11-22 11:01 | -2949.55 | 6.4446 | 59.9582 | 64.1561 | -864.4278
2042-11-23 12:01 | -1921.22 | 5.4394 | 60.6769 | 64.1561 | -563.054
2042-11-24 13:01 | -961.881 | 2.7916 | 61.0071 | 64.1561 | -281.8995
2042-11-25 14:01 | -748.998 | 2.435 | 61.4408 | 64.1561 | -219.5096
2042-11-26 15:01 | -744.512 | 2.4482 | 61.6791 | 64.1561 | -218.1949
2042-11-27 16:01 | -1415.12 | 4.3006 | 61.7357 | 64.1561 | -414.7307
2042-11-28 17:01 | -1244.72 | 3.6581 | 61.7326 | 64.1561 | -364.7914
2042-11-29 18:01 | -2343 | 6.4446 | 61.7196 | 64.1561 | -686.6655
2042-11-30 19:01 | -3215.34 | 6.4446 | 61.1308 | 64.1561 | -942.3231
2042-12-01 20:01 | -3931.22 | 6.4446 | 60.5688 | 64.1561 | -1152.1269
2042-12-02 21:01 | -4409.94 | 6.4446 | 60.143 | 64.1561 | -1292.4258
2042-12-03 22:01 | -4841.97 | 6.4446 | 59.7522 | 64.1561 | -1419.0413
2042-12-04 23:01 | -5210.04 | 6.4446 | 59.3887 | 64.1561 | -1526.912
2042-12-06 00:01 | -6767.57 | 6.4446 | 58.3134 | 64.1561 | -1983.379
2042-12-07 01:01 | -7227.85 | 6.4446 | 57.7668 | 64.1561 | -2118.2737
2042-12-08 02:01 | -7436.66 | 6.4446 | 57.4203 | 64.1561 | -2179.4699
2042-12-09 03:01 | -7840.62 | 6.4446 | 57.0095 | 64.1561 | -2297.8589
2042-12-10 04:01 | -8285.97 | 6.4446 | 56.5661 | 64.1561 | -2428.3781
2042-12-11 05:01 | -8619.25 | 6.4446 | 56.1714 | 64.1561 | -2526.0528
2042-12-12 06:01 | -9091.92 | 6.4446 | 55.7273 | 64.1561 | -2664.5787
2042-12-13 07:01 | -8567.99 | 6.4446 | 55.8761 | 64.1561 | -2511.03
2042-12-14 08:01 | -7065.83 | 6.4446 | 56.7158 | 64.1561 | -2070.7904
2042-12-15 09:01 | -6493.31 | 6.4446 | 57.1603 | 64.1561 | -1903.0013
2042-12-16 10:01 | -5291.62 | 6.4446 | 57.9676 | 64.1561 | -1550.8207
2042-12-17 11:01 | -3941.32 | 6.4446 | 58.9301 | 64.1561 | -1155.0869
2042-12-18 12:01 | -2956.26 | 6.4446 | 59.7684 | 64.1561 | -866.3943
2042-12-19 13:01 | -2417.95 | 6.4446 | 60.3383 | 64.1561 | -708.6312
2042-12-20 14:01 | -2065.64 | 5.8326 | 60.6108 | 64.1561 | -605.3793
2042-12-21 15:01 | -1905.59 | 5.4184 | 60.79 | 64.1561 | -558.4733
2042-12-22 16:01 | -2797.83 | 6.4446 | 60.6066 | 64.1561 | -819.963
2042-12-23 17:01 | -2939.85 | 6.4446 | 60.5153 | 64.1561 | -861.585
2042-12-24 18:01 | -4197.27 | 6.4446 | 59.7595 | 64.1561 | -1230.0984
2042-12-25 19:01 | -5088.88 | 6.4446 | 59.1087 | 64.1561 | -1491.4035
2042-12-26 20:01 | -5590.96 | 6.4446 | 58.6417 | 64.1561 | -1638.5486
2042-12-27 21:01 | -6162.76 | 6.4446 | 58.152 | 64.1561 | -1806.1267
2042-12-28 22:01 | -6447.82 | 6.4446 | 57.8304 | 64.1561 | -1889.6695
2042-12-29 23:01 | -6718.82 | 6.4446 | 57.5229 | 64.1561 | -1969.0918
2042-12-31 00:01 | -7793.39 | 6.4446 | 56.7524 | 64.1561 | -2284.0171
2043-01-01 01:01 | -8234.92 | 6.4446 | 56.2801 | 64.1561 | -2413.4168
2043-01-02 02:01 | -8615.1 | 6.4446 | 55.8626 | 64.1561 | -2524.8366
2043-01-03 03:01 | -8842.43 | 6.4446 | 55.5591 | 64.1561 | -2591.4604
2043-01-04 04:01 | -8823.75 | 6.4446 | 55.4269 | 64.1561 | -2585.9859
2043-01-05 05:01 | -8739.52 | 6.4446 | 55.3673 | 64.1561 | -2561.3005
2043-01-06 06:01 | -8467.7 | 6.4446 | 55.4715 | 64.1561 | -2481.6379
2043-01-07 07:01 | -8255.29 | 6.4446 | 55.5772 | 64.1561 | -2419.3867
2043-01-08 08:01 | -7340.73 | 6.4446 | 56.1178 | 64.1561 | -2151.3556
2043-01-09 09:01 | -6668.17 | 6.4446 | 56.6024 | 64.1561 | -1954.2477
2043-01-10 10:01 | -5026.46 | 6.4446 | 57.6938 | 64.1561 | -1473.11
2043-01-11 11:01 | -3374.25 | 6.4446 | 58.9077 | 64.1561 | -988.8951
2043-01-12 12:01 | -1976.47 | 5.6743 | 59.889 | 64.1561 | -579.2462
2043-01-13 13:01 | -1430.03 | 4.1203 | 60.217 | 64.1561 | -419.1004
2043-01-14 14:01 | -1131.15 | 3.4101 | 60.5334 | 64.1561 | -331.5073
2043-01-15 15:01 | -1137.86 | 3.4859 | 60.7675 | 64.1561 | -333.4738
2043-01-16 16:01 | -1070.96 | 3.2847 | 60.9246 | 64.1561 | -313.8674
2043-01-17 17:01 | -2036.56 | 6.0143 | 61.0009 | 64.1561 | -596.8568
2043-01-18 18:01 | -2805.3 | 6.4446 | 60.6128 | 64.1561 | -822.1523
2043-01-19 19:01 | -3552.79 | 6.4446 | 60.1028 | 64.1561 | -1041.22
2043-01-20 20:01 | -4176.85 | 6.4446 | 59.6372 | 64.1561 | -1224.1139
2043-01-21 21:01 | -5372.82 | 6.4446 | 58.8098 | 64.1561 | -1574.6181
2043-01-22 22:01 | -5731.81 | 6.4446 | 58.3914 | 64.1561 | -1679.8277
2043-01-23 23:01 | -6734.96 | 6.4446 | 57.6222 | 64.1561 | -1973.8219
2043-01-25 00:01 | -7206.62 | 6.4446 | 57.1245 | 64.1561 | -2112.0518
2043-01-26 01:01 | -7871.22 | 6.4446 | 56.5268 | 64.1561 | -2306.8269
2043-01-27 02:01 | -8217.97 | 6.4446 | 56.1091 | 64.1561 | -2408.4493
2043-01-28 03:01 | -8308.33 | 6.4446 | 55.8783 | 64.1561 | -2434.9312
2043-01-29 04:01 | -8404.9 | 6.4446 | 55.6764 | 64.1561 | -2463.233
2043-01-30 05:01 | -8315.47 | 6.4446 | 55.6196 | 64.1561 | -2437.0237
2043-01-31 06:01 | -8027.02 | 6.4446 | 55.7173 | 64.1561 | -2352.4873
2043-02-01 07:01 | -7724.9 | 6.4446 | 55.8717 | 64.1561 | -2263.9447
2043-02-02 08:01 | -6348.9 | 6.4446 | 56.7011 | 64.1561 | -1860.6789
2043-02-03 09:01 | -4619.73 | 6.4446 | 57.8878 | 64.1561 | -1353.9092
2043-02-04 10:01 | -2821.67 | 6.4446 | 59.2316 | 64.1561 | -826.9498
2043-02-05 11:01 | -1166.46 | 3.3271 | 59.8985 | 64.1561 | -341.8557
2043-02-06 12:01 | 0 | 1 | 61.6446 | 64.1561 | 0
2043-02-07 13:01 | 2805.6 | 1 | 61.3466 | 64.1561 | 822.2402
2043-02-08 14:01 | 2850.64 | 1 | 61.8976 | 64.1561 | 835.4401
2043-02-09 15:01 | 2846.02 | 1 | 62.2668 | 64.1561 | 834.0861
2043-02-10 16:01 | 2849.7 | 1 | 62.5187 | 64.1561 | 835.1646
2043-02-11 17:01 | 0 | 0 | 63.4214 | 64.1561 | 0
2043-02-12 18:01 | -705.357 | 2.4472 | 62.1729 | 64.1561 | -206.7197
2043-02-13 19:01 | -1659.83 | 4.9725 | 61.8827 | 64.1561 | -486.4482
2043-02-14 20:01 | -2508.24 | 6.4446 | 61.5527 | 64.1561 | -735.0926
2043-02-15 21:01 | -3847.19 | 6.4446 | 60.5875 | 64.1561 | -1127.5001
2043-02-16 22:01 | -4461.78 | 6.4446 | 59.9629 | 64.1561 | -1307.6186
2043-02-17 23:01 | -5423.39 | 6.4446 | 59.1911 | 64.1561 | -1589.4387
2043-02-19 00:01 | -6042.38 | 6.4446 | 58.5939 | 64.1561 | -1770.8468
2043-02-20 01:01 | -6272.32 | 6.4446 | 58.2223 | 64.1561 | -1838.2355
2043-02-21 02:01 | -6556.3 | 6.4446 | 57.8677 | 64.1561 | -1921.4619
2043-02-22 03:01 | -6698.65 | 6.4446 | 57.6224 | 64.1561 | -1963.1805
2043-02-23 04:01 | -6710.23 | 6.4446 | 57.4726 | 64.1561 | -1966.5743
2043-02-24 05:01 | -6558.13 | 6.4446 | 57.4808 | 64.1561 | -1921.9982
2043-02-25 06:01 | -6248.77 | 6.4446 | 57.6228 | 64.1561 | -1831.3337
2043-02-26 07:01 | -6108.93 | 6.4446 | 57.7004 | 64.1561 | -1790.3507
2043-02-27 08:01 | -4077.44 | 6.4446 | 58.927 | 64.1561 | -1194.9797
2043-02-28 09:01 | -2781 | 6.4446 | 59.928 | 64.1561 | -815.0306
2043-03-01 10:01 | -1048.58 | 2.9681 | 60.4825 | 64.1561 | -307.3085
2043-03-02 11:01 | 1446.96 | 1 | 61.8443 | 64.1561 | 424.0621
2043-03-03 12:01 | 2866.8 | 1 | 61.9808 | 64.1561 | 840.1761
2043-03-04 13:01 | 2860 | 1 | 76.0207 | 64.1561 | 838.1833
2043-03-05 14:01 | 2887.3 | 1 | 76.0779 | 64.1561 | 846.1841
2043-03-06 15:01 | 2814.56 | 1 | 62.9267 | 64.1561 | 824.8661
2043-03-07 16:01 | 2854.22 | 1 | 63.092 | 64.1561 | 836.4893
2043-03-08 17:01 | 941.971 | 1 | 63.6913 | 64.1561 | 276.0644
2043-03-09 18:01 | -59.0698 | 0.7657 | 63.5154 | 64.1561 | -17.3116
2043-03-10 19:01 | -622.959 | 2.2304 | 62.6082 | 64.1561 | -182.5713
2043-03-11 20:01 | -1033.77 | 3.239 | 62.3633 | 64.1561 | -302.9681
2043-03-12 21:01 | -2078.24 | 6.0442 | 62.1878 | 64.1561 | -609.072
2043-03-13 22:01 | -2649.9 | 6.4446 | 61.747 | 64.1561 | -776.609
2043-03-14 23:01 | -3471.41 | 6.4446 | 61.0896 | 64.1561 | -1017.3698
2043-03-16 00:01 | -3613.33 | 6.4446 | 60.8201 | 64.1561 | -1058.9625
2043-03-17 01:01 | -3790 | 6.4446 | 60.5834 | 64.1561 | -1110.7394
2043-03-18 02:01 | -3972.71 | 6.4446 | 60.3637 | 64.1561 | -1164.2864
2043-03-19 03:01 | -3981.78 | 6.4446 | 60.2634 | 64.1561 | -1166.9445
2043-03-20 04:01 | -3940.26 | 6.4446 | 60.2182 | 64.1561 | -1154.7762
2043-03-21 05:01 | -3862.49 | 6.4446 | 60.2388 | 64.1561 | -1131.9841
2043-03-22 06:01 | -3263.27 | 6.4446 | 60.5938 | 64.1561 | -956.37
2043-03-23 07:01 | -3101.35 | 6.4446 | 60.7534 | 64.1561 | -908.916
2043-03-24 08:01 | -2963.56 | 6.4446 | 60.8788 | 64.1561 | -868.5337
2043-03-25 09:01 | -3393.98 | 6.4446 | 60.6492 | 64.1561 | -994.6774
2043-03-26 10:01 | -3215.17 | 6.4446 | 60.7183 | 64.1561 | -942.2733
2043-03-27 11:01 | -2757.72 | 6.4446 | 60.9804 | 64.1561 | -808.208
2043-03-28 12:01 | -2366.12 | 6.4446 | 61.2379 | 64.1561 | -693.4413
2043-03-29 13:01 | -2157.7 | 6.0371 | 61.3042 | 64.1561 | -632.3594
2043-03-30 14:01 | -1970.03 | 5.543 | 61.3302 | 64.1561 | -577.3588
2043-03-31 15:01 | -1851.34 | 5.254 | 61.3693 | 64.1561 | -542.5742
2043-04-01 16:01 | -1016.55 | 2.9475 | 61.4193 | 64.1561 | -297.9214
2043-04-02 17:01 | -717.508 | 2.3271 | 61.6759 | 64.1561 | -210.2808
2043-04-03 18:01 | -444.564 | 1.6278 | 61.9137 | 64.1561 | -130.2888
2043-04-04 19:01 | -826.658 | 2.7386 | 61.8978 | 64.1561 | -242.2695
2043-04-05 20:01 | -1068.51 | 3.3097 | 61.847 | 64.1561 | -313.1494
2043-04-06 21:01 | -1867.75 | 5.4793 | 61.804 | 64.1561 | -547.3835
2043-04-07 22:01 | -2166.92 | 6.1217 | 61.6976 | 64.1561 | -635.0616
2043-04-08 23:01 | -3258.45 | 6.4446 | 61.0576 | 64.1561 | -954.9574
2043-04-10 00:01 | -3774.39 | 6.4446 | 60.6047 | 64.1561 | -1106.1645
2043-04-11 01:01 | -4116.75 | 6.4446 | 60.2662 | 64.1561 | -1206.5003
2043-04-12 02:01 | -4471 | 6.4446 | 59.9423 | 64.1561 | -1310.3208
2043-04-13 03:01 | -4803.76 | 6.4446 | 59.6371 | 64.1561 | -1407.8431
2043-04-14 04:01 | -4899 | 6.4446 | 59.4622 | 64.1561 | -1435.7552
2043-04-15 05:01 | -5232.41 | 6.4446 | 59.1746 | 64.1561 | -1533.468
2043-04-16 06:01 | -5098.95 | 6.4446 | 59.1495 | 64.1561 | -1494.3547
2043-04-17 07:01 | -5323.35 | 6.4446 | 58.9492 | 64.1561 | -1560.1199
2043-04-18 08:01 | -4148.51 | 6.4446 | 59.5782 | 64.1561 | -1215.8083
2043-04-19 09:01 | -3001.03 | 6.4446 | 60.3434 | 64.1561 | -879.5151
2043-04-20 10:01 | -1548.47 | 4.367 | 60.922 | 64.1561 | -453.8118
2043-04-21 11:01 | 0 | 0 | 62.5389 | 64.1561 | 0
2043-04-22 12:01 | 2815.77 | 1 | 62.1667 | 64.1561 | 825.2207
2043-04-23 13:01 | 2860.63 | 1 | 79.9689 | 64.1561 | 838.3679
2043-04-24 14:01 | 2840.48 | 1 | 75.8561 | 64.1561 | 832.4625
2043-04-25 15:01 | 2866.27 | 1 | 78.0452 | 64.1561 | 840.0208
2043-04-26 16:01 | 2864.69 | 1 | 77.2331 | 64.1561 | 839.5578
2043-04-27 17:01 | 2764.37 | 1 | 63.5535 | 64.1561 | 810.1569
2043-04-28 18:01 | 0 | 0 | 64.3121 | 64.1561 | 0
2043-04-29 19:01 | -799.681 | 2.7085 | 62.9472 | 64.1561 | -234.3634
2043-04-30 20:01 | -1546.3 | 4.5928 | 62.6136 | 64.1561 | -453.1758
2043-05-01 21:01 | -2730.29 | 6.4446 | 62.1322 | 64.1561 | -800.169
2043-05-02 22:01 | -3368.17 | 6.4446 | 61.5155 | 64.1561 | -987.1132
2043-05-03 23:01 | -4534.28 | 6.4446 | 60.5794 | 64.1561 | -1328.8663
2043-05-05 00:01 | -5343.61 | 6.4446 | 59.8204 | 64.1561 | -1566.0575
2043-05-06 01:01 | -5543.48 | 6.4446 | 59.4306 | 64.1561 | -1624.6336
2043-05-07 02:01 | -5685.44 | 6.4446 | 59.1426 | 64.1561 | -1666.238
2043-05-08 03:01 | -5719.05 | 6.4446 | 58.961 | 64.1561 | -1676.0881
2043-05-09 04:01 | -6057.62 | 6.4446 | 58.6156 | 64.1561 | -1775.3132
2043-05-10 05:01 | -6123 | 6.4446 | 58.4274 | 64.1561 | -1794.4742
2043-05-11 06:01 | -6235.38 | 6.4446 | 58.2597 | 64.1561 | -1827.4095
2043-05-12 07:01 | -5638.03 | 6.4446 | 58.5345 | 64.1561 | -1652.3435
2043-05-13 08:01 | -4205.7 | 6.4446 | 59.3941 | 64.1561 | -1232.569
2043-05-14 09:01 | -3846.79 | 6.4446 | 59.7451 | 64.1561 | -1127.3829
2043-05-15 10:01 | -2229.52 | 6.3535 | 60.7982 | 64.1561 | -653.4078
2043-05-16 11:01 | -1228.68 | 3.4506 | 60.9936 | 64.1561 | -360.0906
2043-05-17 12:01 | -450.146 | 1.5466 | 61.4855 | 64.1561 | -131.9248
2043-05-18 13:01 | 55.7128 | 1 | 62.8343 | 64.1561 | 16.3278
2043-05-19 14:01 | 273.405 | 1 | 62.9678 | 64.1561 | 80.1271
2043-05-20 15:01 | 277.484 | 1 | 63.1235 | 64.1561 | 81.3225
2043-05-21 16:01 | -549.693 | 2.0685 | 62.2495 | 64.1561 | -161.0991
2043-05-22 17:01 | -602.643 | 2.0795 | 62.1415 | 64.1561 | -176.6172
2043-05-23 18:01 | -1701.82 | 5.1125 | 61.9951 | 64.1561 | -498.7542
2043-05-24 19:01 | -2553.29 | 6.4446 | 61.6604 | 64.1561 | -748.2954
2043-05-25 20:01 | -3399.75 | 6.4446 | 61.0033 | 64.1561 | -996.3684
2043-05-26 21:01 | -4024.73 | 6.4446 | 60.4621 | 64.1561 | -1179.5319
2043-05-27 22:01 | -4482.37 | 6.4446 | 60.0212 | 64.1561 | -1313.653
2043-05-28 23:01 | -5012.02 | 6.4446 | 59.5401 | 64.1561 | -1468.8781
2043-05-30 00:01 | -6615.05 | 6.4446 | 58.4064 | 64.1561 | -1938.6798
2043-05-31 01:01 | -7064.71 | 6.4446 | 57.8414 | 64.1561 | -2070.4621
2043-06-01 02:01 | -7422.1 | 6.4446 | 57.3896 | 64.1561 | -2175.2028
2043-06-02 03:01 | -7562.92 | 6.4446 | 57.1092 | 64.1561 | -2216.4731
2043-06-03 04:01 | -7740.84 | 6.4446 | 56.8387 | 64.1561 | -2268.6163
2043-06-04 05:01 | -7653.53 | 6.4446 | 56.7378 | 64.1561 | -2243.0282
2043-06-05 06:01 | -7667.92 | 6.4446 | 56.6384 | 64.1561 | -2247.2455
2043-06-06 07:01 | -6787.08 | 6.4446 | 57.0961 | 64.1561 | -1989.0968
2043-06-07 08:01 | -5347.11 | 6.4446 | 57.9939 | 64.1561 | -1567.0832
2043-06-08 09:01 | -4515.04 | 6.4446 | 58.6468 | 64.1561 | -1323.2276
2043-06-09 10:01 | -3155.59 | 6.4446 | 59.6135 | 64.1561 | -924.8121
2043-06-10 11:01 | -1638.17 | 4.6605 | 60.3581 | 64.1561 | -480.1002
2043-06-11 12:01 | -515.162 | 1.6253 | 60.7835 | 64.1561 | -150.9791
2043-06-12 13:01 | 2438.8 | 1 | 61.7421 | 64.1561 | 714.7417
2043-06-13 14:01 | 2848.99 | 1 | 62.1533 | 64.1561 | 834.9565
2043-06-14 15:01 | 2846.74 | 1 | 62.523 | 64.1561 | 834.2971
2043-06-15 16:01 | 2666.91 | 1 | 62.8097 | 64.1561 | 781.5942
2043-06-16 17:01 | 2849.1 | 1 | 62.9515 | 64.1561 | 834.9888
2043-06-17 18:01 | -521.564 | 2.0084 | 62.8187 | 64.1561 | -152.8553
2043-06-18 19:01 | -1227.06 | 3.7898 | 62.332 | 64.1561 | -359.6158
2043-06-19 20:01 | -1992.52 | 5.7644 | 62.0707 | 64.1561 | -583.95
2043-06-20 21:01 | -2571.4 | 6.4446 | 61.7283 | 64.1561 | -753.6029
2043-06-21 22:01 | -3054.45 | 6.4446 | 61.2865 | 64.1561 | -895.1709
2043-06-22 23:01 | -3531.51 | 6.4446 | 60.8317 | 64.1561 | -1034.9834
2043-06-24 00:01 | -4875.8 | 6.4446 | 59.8999 | 64.1561 | -1428.9559
2043-06-25 01:01 | -5133.68 | 6.4446 | 59.4987 | 64.1561 | -1504.5331
2043-06-26 02:01 | -5478.28 | 6.4446 | 59.1064 | 64.1561 | -1605.5254
2043-06-27 03:01 | -5678.23 | 6.4446 | 58.8254 | 64.1561 | -1664.1249
2043-06-28 04:01 | -5778.59 | 6.4446 | 58.6187 | 64.1561 | -1693.5376
2043-06-29 05:01 | -5594.86 | 6.4446 | 58.5996 | 64.1561 | -1639.6916
2043-06-30 06:01 | -5462.15 | 6.4446 | 58.6388 | 64.1561 | -1600.7981
2043-07-01 07:01 | -5186.18 | 6.4446 | 58.7793 | 64.1561 | -1519.9193
2043-07-02 08:01 | -3201.02 | 6.4446 | 59.9801 | 64.1561 | -938.1264
2043-07-03 09:01 | -2213.02 | 6.2784 | 60.7535 | 64.1561 | -648.5721
2043-07-04 10:01 | -649.21 | 1.8412 | 60.9624 | 64.1561 | -190.2647
2043-07-05 11:01 | 2759.71 | 1 | 61.968 | 64.1561 | 808.7912
2043-07-06 12:01 | 3289.13 | 1.1378 | 74.5283 | 64.1561 | 963.9488
2043-07-07 13:01 | 4451.04 | 1.4923 | 75.2571 | 64.1561 | 1304.4711
2043-07-08 14:01 | 5056.49 | 1.7007 | 75.5901 | 64.1561 | 1481.9109
2043-07-09 15:01 | 5137.14 | 1.7009 | 76.1277 | 64.1561 | 1505.5471
2043-07-10 16:01 | 4817.23 | 1.6136 | 76.267 | 64.1561 | 1411.7908
2043-07-11 17:01 | 2978.3 | 1.0081 | 76.3012 | 64.1561 | 872.8536
2043-07-12 18:01 | 2924.14 | 1 | 64.0057 | 64.1561 | 856.9808
2043-07-13 19:01 | 2677.01 | 1 | 64.1031 | 64.1561 | 784.5542
2043-07-14 20:01 | -207.502 | 1.1536 | 64.0724 | 64.1561 | -60.8128
2043-07-15 21:01 | -1418.11 | 4.3309 | 63.2133 | 64.1561 | -415.607
2043-07-16 22:01 | -2097.5 | 5.9495 | 62.8344 | 64.1561 | -614.7166
2043-07-17 23:01 | -3259.5 | 6.4446 | 62.0244 | 64.1561 | -955.2652
2043-07-19 00:01 | -3690.36 | 6.4446 | 61.4937 | 64.1561 | -1081.5378
2043-07-20 01:01 | -4125.79 | 6.4446 | 60.9826 | 64.1561 | -1209.1497
2043-07-21 02:01 | -4198.32 | 6.4446 | 60.7482 | 64.1561 | -1230.4061
2043-07-22 03:01 | -4328.38 | 6.4446 | 60.528 | 64.1561 | -1268.523
2043-07-23 04:01 | -4294.56 | 6.4446 | 60.4253 | 64.1561 | -1258.6113
2043-07-24 05:01 | -4409.42 | 6.4446 | 60.2835 | 64.1561 | -1292.2734
2043-07-25 06:01 | -4045.64 | 6.4446 | 60.4289 | 64.1561 | -1185.66
2043-07-26 07:01 | -3978.55 | 6.4446 | 60.4473 | 64.1561 | -1165.9979
2043-07-27 08:01 | -3375.66 | 6.4446 | 60.7979 | 64.1561 | -989.3083
2043-07-28 09:01 | -2116.7 | 5.9519 | 61.5002 | 64.1561 | -620.3435
2043-07-29 10:01 | -509.753 | 1.4724 | 61.6824 | 64.1561 | -149.3939
2043-07-30 11:01 | 2616.62 | 1 | 77.4672 | 64.1561 | 766.8556
2043-07-31 12:01 | 3200.95 | 1 | 83.7071 | 64.1561 | 938.1058
2043-08-01 13:01 | 3836.14 | 1.1926 | 76.6669 | 64.1561 | 1124.2617
2043-08-02 14:01 | 5159.41 | 1.7573 | 75.8581 | 64.1561 | 1512.0738
2043-08-03 15:01 | 5456.24 | 1.6751 | 77.4752 | 64.1561 | 1599.0661
2043-08-04 16:01 | 5294.09 | 1.6842 | 77.3106 | 64.1561 | 1551.5446
2043-08-05 17:01 | 3881.24 | 1.2323 | 77.5029 | 64.1561 | 1137.4792
2043-08-06 18:01 | 3160.51 | 1 | 78.6295 | 64.1561 | 926.254
2043-08-07 19:01 | 3097.99 | 1 | 64.4257 | 64.1561 | 907.9312
2043-08-08 20:01 | 3085.04 | 1 | 64.4693 | 64.1561 | 904.136
2043-08-09 21:01 | -290.155 | 1.3507 | 64.4115 | 64.1561 | -85.036
2043-08-10 22:01 | -632.122 | 2.1797 | 63.778 | 64.1561 | -185.2567
2043-08-11 23:01 | -1454.73 | 4.3441 | 63.3921 | 64.1561 | -426.3393
2043-08-13 00:01 | -1940.06 | 5.4922 | 63.144 | 64.1561 | -568.5755
2043-08-14 01:01 | -2050.11 | 5.703 | 62.9345 | 64.1561 | -600.8279
2043-08-15 02:01 | -2185.88 | 6.0701 | 62.7706 | 64.1561 | -640.6182
2043-08-16 03:01 | -2301.12 | 6.3625 | 62.6692 | 64.1561 | -674.3917
2043-08-17 04:01 | -2209.87 | 6.0895 | 62.5737 | 64.1561 | -647.649
2043-08-18 05:01 | -2063.73 | 5.7129 | 62.5383 | 64.1561 | -604.8196
2043-08-19 06:01 | -1764.66 | 4.9215 | 62.5362 | 64.1561 | -517.1708
2043-08-20 07:01 | -1669.61 | 4.7312 | 62.5713 | 64.1561 | -489.3144
2043-08-21 08:01 | -1594.09 | 4.5406 | 62.5758 | 64.1561 | -467.1817
2043-08-22 09:01 | -1687.48 | 4.8145 | 62.5955 | 64.1561 | -494.5516
2043-08-23 10:01 | 422.978 | 1 | 63.8535 | 64.1561 | 123.9626
2043-08-24 11:01 | 3518.59 | 1.5268 | 73.1978 | 64.1561 | 1031.1969
2043-08-25 12:01 | 5198.93 | 1.7861 | 76.0051 | 64.1561 | 1523.656
2043-08-26 13:01 | 6056.83 | 2.0245 | 76.746 | 64.1561 | 1775.0816
2043-08-27 14:01 | 5687.47 | 1.9095 | 77.0467 | 64.1561 | 1666.8329
2043-08-28 15:01 | 3585.04 | 1.1417 | 77.9077 | 64.1561 | 1050.6715
2043-08-29 16:01 | 4708.26 | 1.4788 | 78.0129 | 64.1561 | 1379.8548
2043-08-30 17:01 | 4315.81 | 1.3696 | 78.0147 | 64.1561 | 1264.8391
2043-08-31 18:01 | 4172.85 | 1.3196 | 78.1205 | 64.1561 | 1222.9416
2043-09-01 19:01 | 3060.47 | 1 | 77.7975 | 64.1561 | 896.9352
2043-09-02 20:01 | 3060.11 | 1 | 83.3573 | 64.1561 | 896.8297
2043-09-03 21:01 | 2965.43 | 1 | 65.0318 | 64.1561 | 869.0817
2043-09-04 22:01 | 0 | 0 | 65.7722 | 64.1561 | 0
2043-09-05 23:01 | -688.514 | 2.2254 | 64.2396 | 64.1561 | -201.7835
2043-09-07 00:01 | -971.027 | 3.0101 | 63.9261 | 64.1561 | -284.5799
2043-09-08 01:01 | -1279.81 | 3.7824 | 63.7036 | 64.1561 | -375.0753
2043-09-09 02:01 | -1392.65 | 4.0275 | 63.5163 | 64.1561 | -408.1454
2043-09-10 03:01 | -1305.51 | 3.7746 | 63.39 | 64.1561 | -382.6072
2043-09-11 04:01 | -1076.63 | 3.1778 | 63.361 | 64.1561 | -315.5291
2043-09-12 05:01 | -950.282 | 2.8889 | 63.3844 | 64.1561 | -278.5002
2043-09-13 06:01 | -516.724 | 1.7424 | 63.5006 | 64.1561 | -151.4369
2043-09-14 07:01 | -411.096 | 1.5578 | 63.6702 | 64.1561 | -120.4803
2043-09-15 08:01 | -191.562 | 0.98418 | 63.9681 | 64.1561 | -56.1413
2043-09-16 09:01 | -343.266 | 1.4376 | 63.8241 | 64.1561 | -100.6013
2043-09-17 10:01 | 2072.54 | 1 | 64.2723 | 64.1561 | 607.4015
2043-09-18 11:01 | 2724.02 | 1 | 64.3755 | 64.1561 | 798.3315
2043-09-19 12:01 | 2962.66 | 1 | 64.5239 | 64.1561 | 868.2699
2043-09-20 13:01 | 3067.44 | 1 | 64.6228 | 64.1561 | 898.9779
2043-09-21 14:01 | 3104.28 | 1 | 64.7147 | 64.1561 | 909.7747
2043-09-22 15:01 | 3192.99 | 1 | 64.7979 | 64.1561 | 935.773
2043-09-23 16:01 | 3254.68 | 1 | 64.8399 | 64.1561 | 953.8526
2043-09-24 17:01 | 3137.11 | 1 | 64.919 | 64.1561 | 919.3962
2043-09-25 18:01 | 3159.64 | 1 | 86.4931 | 64.1561 | 925.9991
2043-09-26 19:01 | 3082.7 | 1 | 64.9974 | 64.1561 | 903.4502
2043-09-27 20:01 | 0 | 0 | 65.7731 | 64.1561 | 0
2043-09-28 21:01 | -875.275 | 2.7445 | 64.2186 | 64.1561 | -256.5178
2043-09-29 22:01 | -1323.22 | 3.9148 | 63.8805 | 64.1561 | -387.7975
2043-09-30 23:01 | -2245.87 | 6.3324 | 63.6356 | 64.1561 | -658.1995
2043-10-02 00:01 | -2760.47 | 6.4446 | 63.1084 | 64.1561 | -809.0139
2043-10-03 01:01 | -3597.58 | 6.4446 | 62.3619 | 64.1561 | -1054.3466
2043-10-04 02:01 | -3753.61 | 6.4446 | 62.0436 | 64.1561 | -1100.0745
2043-10-05 03:01 | -3982.69 | 6.4446 | 61.7339 | 64.1561 | -1167.2112
2043-10-06 04:01 | -3997.93 | 6.4446 | 61.566 | 64.1561 | -1171.6776
2043-10-07 05:01 | -4039.74 | 6.4446 | 61.4131 | 64.1561 | -1183.9309
2043-10-08 06:01 | -3710.67 | 6.4446 | 61.494 | 64.1561 | -1087.49
2043-10-09 07:01 | -3847.38 | 6.4446 | 61.3476 | 64.1561 | -1127.5558
2043-10-10 08:01 | -3433.29 | 6.4446 | 61.5338 | 64.1561 | -1006.198
2043-10-11 09:01 | -3095.17 | 6.4446 | 61.7309 | 64.1561 | -907.1048
2043-10-12 10:01 | -2249.16 | 6.2561 | 62.2028 | 64.1561 | -659.1637
2043-10-13 11:01 | 0 | 0 | 63.6705 | 64.1561 | 0
2043-10-14 12:01 | 2678.92 | 1 | 63.2936 | 64.1561 | 785.114
2043-10-15 13:01 | -375.031 | 1.6123 | 63.4605 | 64.1561 | -109.9107
2043-10-16 14:01 | -593.315 | 2.0695 | 63.1437 | 64.1561 | -173.8835
2043-10-17 15:01 | 2172.61 | 1 | 63.6893 | 64.1561 | 636.7291
2043-10-18 16:01 | 3081.54 | 1 | 63.8055 | 64.1561 | 903.1102
2043-10-19 17:01 | 2698.2 | 1 | 64.17 | 64.1561 | 790.7644
2043-10-20 18:01 | -159.185 | 1.0274 | 64.258 | 64.1561 | -46.6525
2043-10-21 19:01 | -931.427 | 3.0153 | 63.4391 | 64.1561 | -272.9743
2043-10-22 20:01 | -1648.88 | 4.8136 | 63.1699 | 64.1561 | -483.239
2043-10-23 21:01 | -2369.88 | 6.4446 | 62.9217 | 64.1561 | -694.5433
2043-10-24 22:01 | -2914.53 | 6.4446 | 62.3992 | 64.1561 | -854.1644
2043-10-25 23:01 | -4034.71 | 6.4446 | 61.5142 | 64.1561 | -1182.4568
2043-10-27 00:01 | -4932.44 | 6.4446 | 60.7156 | 64.1561 | -1445.5555
2043-10-28 01:01 | -5225.09 | 6.4446 | 60.2999 | 64.1561 | -1531.3227
2043-10-29 02:01 | -5761.19 | 6.4446 | 59.7951 | 64.1561 | -1688.4381
2043-10-30 03:01 | -6089.54 | 6.4446 | 59.3835 | 64.1561 | -1784.668
2043-10-31 04:01 | -6260.08 | 6.4446 | 59.0654 | 64.1561 | -1834.6483
2043-11-01 05:01 | -6549.41 | 6.4446 | 58.7119 | 64.1561 | -1919.4426
2043-11-02 06:01 | -6733.06 | 6.4446 | 58.4479 | 64.1561 | -1973.2651
2043-11-03 07:01 | -5977.43 | 6.4446 | 58.7656 | 64.1561 | -1751.8118
2043-11-04 08:01 | -5058.38 | 6.4446 | 59.2992 | 64.1561 | -1482.4648
2043-11-05 09:01 | -4723.19 | 6.4446 | 59.5617 | 64.1561 | -1384.2303
2043-11-06 10:01 | -3506.3 | 6.4446 | 60.3277 | 64.1561 | -1027.5951
2043-11-07 11:01 | -2894.55 | 6.4446 | 60.821 | 64.1561 | -848.3089
2043-11-08 12:01 | -2598.68 | 6.4446 | 61.1212 | 64.1561 | -761.5979
2043-11-09 13:01 | -1927.55 | 5.3922 | 61.3912 | 64.1561 | -564.9091
2043-11-10 14:01 | -2651.37 | 6.4446 | 61.3052 | 64.1561 | -777.0398
2043-11-11 15:01 | -2857.85 | 6.4446 | 61.1637 | 64.1561 | -837.5532
2043-11-12 16:01 | -2928.57 | 6.4446 | 61.0694 | 64.1561 | -858.2791
2043-11-13 17:01 | -1817.82 | 5.0945 | 61.4161 | 64.1561 | -532.7505
2043-11-14 18:01 | -2422.83 | 6.4446 | 61.4579 | 64.1561 | -710.0614
2043-11-15 19:01 | -3026.82 | 6.4446 | 61.0718 | 64.1561 | -887.0734
2043-11-16 20:01 | -3297.53 | 6.4446 | 60.8321 | 64.1561 | -966.4106
2043-11-17 21:01 | -3900.27 | 6.4446 | 60.4176 | 64.1561 | -1143.0563
2043-11-18 22:01 | -4124.47 | 6.4446 | 60.1886 | 64.1561 | -1208.7628
2043-11-19 23:01 | -4502.31 | 6.4446 | 59.8601 | 64.1561 | -1319.4968
2043-11-21 00:01 | -5851.65 | 6.4446 | 58.9417 | 64.1561 | -1714.9493
2043-11-22 01:01 | -6128 | 6.4446 | 58.5534 | 64.1561 | -1795.9395
2043-11-23 02:01 | -6264.67 | 6.4446 | 58.3092 | 64.1561 | -1835.9935
2043-11-24 03:01 | -6255.21 | 6.4446 | 58.2059 | 64.1561 | -1833.2211
2043-11-25 04:01 | -6359.64 | 6.4446 | 58.0548 | 64.1561 | -1863.8265
2043-11-26 05:01 | -6404.25 | 6.4446 | 57.9296 | 64.1561 | -1876.9004
2043-11-27 06:01 | -6201.77 | 6.4446 | 57.9852 | 64.1561 | -1817.5594
2043-11-28 07:01 | -5469.03 | 6.4446 | 58.3988 | 64.1561 | -1602.8145
2043-11-29 08:01 | -4922.3 | 6.4446 | 58.7734 | 64.1561 | -1442.5837
2043-11-30 09:01 | -5208.48 | 6.4446 | 58.6667 | 64.1561 | -1526.4548
2043-12-01 10:01 | -4330.39 | 6.4446 | 59.1793 | 64.1561 | -1269.112
2043-12-02 11:01 | -2363.76 | 6.4446 | 60.4432 | 64.1561 | -692.7497
2043-12-03 12:01 | -1639.49 | 4.6132 | 60.7447 | 64.1561 | -480.4871
2043-12-04 13:01 | -960.574 | 2.8657 | 61.0359 | 64.1561 | -281.5164
2043-12-05 14:01 | -1504.15 | 4.5385 | 61.248 | 64.1561 | -440.8228
2043-12-06 15:01 | -1626.05 | 4.7229 | 61.2805 | 64.1561 | -476.5482
2043-12-07 16:01 | -2114.67 | 6.0755 | 61.3234 | 64.1561 | -619.7486
2043-12-08 17:01 | -1066.8 | 3.0144 | 61.279 | 64.1561 | -312.6482
2043-12-09 18:01 | -1590.51 | 4.7529 | 61.4791 | 64.1561 | -466.1325
2043-12-10 19:01 | -2250.16 | 6.4446 | 61.4383 | 64.1561 | -659.4568
2043-12-11 20:01 | -2914.12 | 6.4446 | 60.9783 | 64.1561 | -854.0443
2043-12-12 21:01 | -3358.98 | 6.4446 | 60.6323 | 64.1561 | -984.4199
2043-12-13 22:01 | -3649.87 | 6.4446 | 60.3869 | 64.1561 | -1069.6713
2043-12-14 23:01 | -4035.37 | 6.4446 | 60.0586 | 64.1561 | -1182.6502
2043-12-16 00:01 | -5865.33 | 6.4446 | 58.8489 | 64.1561 | -1718.9585
2043-12-17 01:01 | -6229.71 | 6.4446 | 58.3549 | 64.1561 | -1825.7478
2043-12-18 02:01 | -7315.26 | 6.4446 | 57.4997 | 64.1561 | -2143.8911
2043-12-19 03:01 | -7809.38 | 6.4446 | 56.9596 | 64.1561 | -2288.7034
2043-12-20 04:01 | -7872.12 | 6.4446 | 56.6987 | 64.1561 | -2307.0906
2043-12-21 05:01 | -7598.78 | 6.4446 | 56.6882 | 64.1561 | -2226.9826
2043-12-22 06:01 | -7323.58 | 6.4446 | 56.7662 | 64.1561 | -2146.3294
2043-12-23 07:01 | -7724.44 | 6.4446 | 56.4603 | 64.1561 | -2263.8099
2043-12-24 08:01 | -6490.87 | 6.4446 | 57.1014 | 64.1561 | -1902.2862
2043-12-25 09:01 | -5890.68 | 6.4446 | 57.5238 | 64.1561 | -1726.3879
2043-12-26 10:01 | -4336.26 | 6.4446 | 58.5392 | 64.1561 | -1270.8324
2043-12-27 11:01 | -3244.23 | 6.4446 | 59.3723 | 64.1561 | -950.79
2043-12-28 12:01 | -2017.56 | 5.7648 | 60.1815 | 64.1561 | -591.2885
2043-12-29 13:01 | -1689.41 | 4.8348 | 60.4395 | 64.1561 | -495.1172
2043-12-30 14:01 | -1412.05 | 4.1275 | 60.6626 | 64.1561 | -413.831
2043-12-31 15:01 | -1469.3 | 4.346 | 60.8488 | 64.1561 | -430.6093
2044-01-01 16:01 | -1442.4 | 4.2439 | 60.9566 | 64.1561 | -422.7257
2044-01-02 17:01 | -2941.11 | 6.4446 | 60.5851 | 64.1561 | -861.9543
2044-01-03 18:01 | -3965.85 | 6.4446 | 59.8548 | 64.1561 | -1162.2759
2044-01-04 19:01 | -4905.03 | 6.4446 | 59.1324 | 64.1561 | -1437.5224
2044-01-05 20:01 | -5354.51 | 6.4446 | 58.6829 | 64.1561 | -1569.252
2044-01-06 21:01 | -6489.02 | 6.4446 | 57.841 | 64.1561 | -1901.744
2044-01-07 22:01 | -6988.71 | 6.4446 | 57.2906 | 64.1561 | -2048.1887
2044-01-08 23:01 | -8103.87 | 6.4446 | 56.3986 | 64.1561 | -2375.0099
2044-01-10 00:01 | -8511.22 | 6.4446 | 55.8869 | 64.1561 | -2494.3924
2044-01-11 01:01 | -8793.74 | 6.4446 | 55.4909 | 64.1561 | -2577.1908
2044-01-12 02:01 | -8978.91 | 6.4446 | 55.1853 | 64.1561 | -2631.4588
2044-01-13 03:01 | -8968.2 | 6.4446 | 55.028 | 64.1561 | -2628.32
2044-01-14 04:01 | -9230.55 | 6.4446 | 54.7328 | 64.1561 | -2705.2072
2044-01-15 05:01 | -8999.46 | 6.4446 | 54.7467 | 64.1561 | -2637.4814
2044-01-16 06:01 | -8831.85 | 6.4446 | 54.7764 | 64.1561 | -2588.3597
2044-01-17 07:01 | -8658.1 | 6.4446 | 54.8398 | 64.1561 | -2537.4386
2044-01-18 08:01 | -6911.06 | 6.4446 | 55.8642 | 64.1561 | -2025.4317
2044-01-19 09:01 | -5777.36 | 6.4446 | 56.7099 | 64.1561 | -1693.1771
2044-01-20 10:01 | -3845.11 | 6.4446 | 58.0793 | 64.1561 | -1126.8905
2044-01-21 11:01 | -2538.43 | 6.4446 | 59.1755 | 64.1561 | -743.9404
2044-01-22 12:01 | -1164.49 | 3.3247 | 59.6592 | 64.1561 | -341.2783
2044-01-23 13:01 | -652.798 | 2.1507 | 60.1954 | 64.1561 | -191.3162
2044-01-24 14:01 | -356.844 | 1.4226 | 60.6796 | 64.1561 | -104.5807
2044-01-25 15:01 | -168.888 | 0.96198 | 61.1982 | 64.1561 | -49.4962
2044-01-26 16:01 | 1698.74 | 1 | 61.6658 | 64.1561 | 497.8515
2044-01-27 17:01 | -828.419 | 2.8948 | 61.304 | 64.1561 | -242.7856
2044-01-28 18:01 | -1598.79 | 4.8119 | 61.0818 | 64.1561 | -468.5591
2044-01-29 19:01 | -2406.41 | 6.4446 | 60.854 | 64.1561 | -705.2492
2044-01-30 20:01 | -3284.34 | 6.4446 | 60.2541 | 64.1561 | -962.545
2044-01-31 21:01 | -4602.34 | 6.4446 | 59.3407 | 64.1561 | -1348.8127
2044-02-01 22:01 | -5207.37 | 6.4446 | 58.7247 | 64.1561 | -1526.1295
2044-02-02 23:01 | -6222.28 | 6.4446 | 57.9226 | 64.1561 | -1823.5703
2044-02-04 00:01 | -6538.26 | 6.4446 | 57.505 | 64.1561 | -1916.1749
2044-02-05 01:01 | -6925.38 | 6.4446 | 57.0877 | 64.1561 | -2029.6285
2044-02-06 02:01 | -7251.03 | 6.4446 | 56.7257 | 64.1561 | -2125.0671
2044-02-07 03:01 | -7544.33 | 6.4446 | 56.3986 | 64.1561 | -2211.0249
2044-02-08 04:01 | -7462.4 | 6.4446 | 56.2881 | 64.1561 | -2187.0136
2044-02-09 05:01 | -7349.9 | 6.4446 | 56.2712 | 64.1561 | -2154.0431
2044-02-10 06:01 | -6932.42 | 6.4446 | 56.469 | 64.1561 | -2031.6917
2044-02-11 07:01 | -6758.69 | 6.4446 | 56.5728 | 64.1561 | -1980.7765
2044-02-12 08:01 | -5136.22 | 6.4446 | 57.5552 | 64.1561 | -1505.2775
2044-02-13 09:01 | -4188.88 | 6.4446 | 58.3026 | 64.1561 | -1227.6395
2044-02-14 10:01 | -2475.42 | 6.4446 | 59.5289 | 64.1561 | -725.474
2044-02-15 11:01 | -952.162 | 2.7083 | 59.9373 | 64.1561 | -279.0511
2044-02-16 12:01 | 0 | 1 | 61.6503 | 64.1561 | 0
2044-02-17 13:01 | 2832.76 | 1 | 61.2932 | 64.1561 | 830.2
2044-02-18 14:01 | 2845.21 | 1 | 61.8113 | 64.1561 | 833.8487
2044-02-19 15:01 | 2849.69 | 1 | 62.155 | 64.1561 | 835.1617
2044-02-20 16:01 | 2851.86 | 1 | 80.2238 | 64.1561 | 835.7977
2044-02-21 17:01 | 2571.5 | 1 | 62.6435 | 64.1561 | 753.6323
2044-02-22 18:01 | -452.179 | 1.8365 | 62.4545 | 64.1561 | -132.5206
2044-02-23 19:01 | -1325.36 | 4.0945 | 61.9327 | 64.1561 | -388.4247
2044-02-24 20:01 | -2212.09 | 6.3815 | 61.6672 | 64.1561 | -648.2996
2044-02-25 21:01 | -3613.08 | 6.4446 | 60.6826 | 64.1561 | -1058.8892
2044-02-26 22:01 | -4095.39 | 6.4446 | 60.1373 | 64.1561 | -1200.2403
2044-02-27 23:01 | -5132.59 | 6.4446 | 59.2915 | 64.1561 | -1504.2136
2044-02-29 00:01 | -5493.36 | 6.4446 | 58.8542 | 64.1561 | -1609.9449
2044-03-01 01:01 | -5909.53 | 6.4446 | 58.3984 | 64.1561 | -1731.9123
2044-03-02 02:01 | -6035.68 | 6.4446 | 58.1373 | 64.1561 | -1768.8832
2044-03-03 03:01 | -6192.86 | 6.4446 | 57.9012 | 64.1561 | -1814.9481
2044-03-04 04:01 | -6205.65 | 6.4446 | 57.7624 | 64.1561 | -1818.6965
2044-03-05 05:01 | -6169.19 | 6.4446 | 57.6843 | 64.1561 | -1808.0111
2044-03-06 06:01 | -5602.3 | 6.4446 | 57.9708 | 64.1561 | -1641.8721
2044-03-07 07:01 | -5439.74 | 6.4446 | 58.0888 | 64.1561 | -1594.2304
2044-03-08 08:01 | -4916.68 | 6.4446 | 58.414 | 64.1561 | -1440.9367
2044-03-09 09:01 | -4224.86 | 6.4446 | 58.8862 | 64.1561 | -1238.1842
2044-03-10 10:01 | -3420.86 | 6.4446 | 59.4648 | 64.1561 | -1002.5551
2044-03-11 11:01 | -1744.01 | 4.9772 | 60.2971 | 64.1561 | -511.1189
2044-03-12 12:01 | -966.614 | 2.8633 | 60.5888 | 64.1561 | -283.2866
2044-03-13 13:01 | 2032.24 | 1 | 61.643 | 64.1561 | 595.5908
2044-03-14 14:01 | 3472.63 | 1 | 61.7618 | 64.1561 | 1017.7274
2044-03-15 15:01 | 711.654 | 1 | 62.8695 | 64.1561 | 208.5652
2044-03-16 16:01 | 918.532 | 1 | 62.7822 | 64.1561 | 269.1952
2044-03-17 17:01 | -457.027 | 1.841 | 62.0764 | 64.1561 | -133.9414
2044-03-18 18:01 | -799.934 | 2.6498 | 61.8261 | 64.1561 | -234.4375
2044-03-19 19:01 | -1402.52 | 4.2527 | 61.6471 | 64.1561 | -411.038
2044-03-20 20:01 | -1924.11 | 5.5727 | 61.4794 | 64.1561 | -563.901
2044-03-21 21:01 | -3149.15 | 6.4446 | 60.8469 | 64.1561 | -922.9248
2044-03-22 22:01 | -3818.73 | 6.4446 | 60.2643 | 64.1561 | -1119.1593
2044-03-23 23:01 | -4904.28 | 6.4446 | 59.4445 | 64.1561 | -1437.3026
2044-03-25 00:01 | -5398.65 | 6.4446 | 58.9304 | 64.1561 | -1582.1881
2044-03-26 01:01 | -5698.62 | 6.4446 | 58.5356 | 64.1561 | -1670.1007
2044-03-27 02:01 | -6034.3 | 6.4446 | 58.1385 | 64.1561 | -1768.4788
2044-03-28 03:01 | -6440.4 | 6.4446 | 57.7403 | 64.1561 | -1887.4949
2044-03-29 04:01 | -6625.67 | 6.4446 | 57.465 | 64.1561 | -1941.7922
2044-03-30 05:01 | -6833.88 | 6.4446 | 57.2165 | 64.1561 | -2002.8125
2044-03-31 06:01 | -6253.53 | 6.4446 | 57.4522 | 64.1561 | -1832.7287
2044-04-01 07:01 | -6433.62 | 6.4446 | 57.3182 | 64.1561 | -1885.5079
2044-04-02 08:01 | -6137.36 | 6.4446 | 57.4339 | 64.1561 | -1798.6827
2044-04-03 09:01 | -6395.29 | 6.4446 | 57.2515 | 64.1561 | -1874.2745
2044-04-04 10:01 | -5701.26 | 6.4446 | 57.607 | 64.1561 | -1670.8744
2044-04-05 11:01 | -5194.98 | 6.4446 | 57.932 | 64.1561 | -1522.4983
2044-04-06 12:01 | -4698.35 | 6.4446 | 58.2688 | 64.1561 | -1376.9505
2044-04-07 13:01 | -4321.45 | 6.4446 | 58.5299 | 64.1561 | -1266.492
2044-04-08 14:01 | -4192.88 | 6.4446 | 58.6349 | 64.1561 | -1228.8118
2044-04-09 15:01 | -4088.77 | 6.4446 | 58.7294 | 64.1561 | -1198.3002
2044-04-10 16:01 | -3459.54 | 6.4446 | 59.125 | 64.1561 | -1013.8911
2044-04-11 17:01 | -3376.08 | 6.4446 | 59.2545 | 64.1561 | -989.4314
2044-04-12 18:01 | -3259.24 | 6.4446 | 59.3763 | 64.1561 | -955.189
2044-04-13 19:01 | -3707.07 | 6.4446 | 59.1474 | 64.1561 | -1086.435
2044-04-14 20:01 | -3906.93 | 6.4446 | 59.0121 | 64.1561 | -1145.0082
2044-04-15 21:01 | -4900.41 | 6.4446 | 58.4017 | 64.1561 | -1436.1684
2044-04-16 22:01 | -5094.79 | 6.4446 | 58.1722 | 64.1561 | -1493.1356
2044-04-17 23:01 | -5895.1 | 6.4446 | 57.6093 | 64.1561 | -1727.6833
2044-04-19 00:01 | -6253.03 | 6.4446 | 57.2584 | 64.1561 | -1832.5822
2044-04-20 01:01 | -6574.02 | 6.4446 | 56.9411 | 64.1561 | -1926.6551
2044-04-21 02:01 | -6743.57 | 6.4446 | 56.7242 | 64.1561 | -1976.3453
2044-04-22 03:01 | -6764.49 | 6.4446 | 56.6243 | 64.1561 | -1982.4763
2044-04-23 04:01 | -6832.58 | 6.4446 | 56.5098 | 64.1561 | -2002.4315
2044-04-24 05:01 | -6712.18 | 6.4446 | 56.5231 | 64.1561 | -1967.1458
2044-04-25 06:01 | -6695.31 | 6.4446 | 56.4922 | 64.1561 | -1962.2017
2044-04-26 07:01 | -5931.43 | 6.4446 | 56.9241 | 64.1561 | -1738.3305
2044-04-27 08:01 | -5302.29 | 6.4446 | 57.3577 | 64.1561 | -1553.9478
2044-04-28 09:01 | -5501.82 | 6.4446 | 57.3306 | 64.1561 | -1612.4243
2044-04-29 10:01 | -5459.14 | 6.4446 | 57.3705 | 64.1561 | -1599.916
2044-04-30 11:01 | -4714.65 | 6.4446 | 57.829 | 64.1561 | -1381.7275
2044-05-01 12:01 | -4075.3 | 6.4446 | 58.3082 | 64.1561 | -1194.3525
2044-05-02 13:01 | -3855.1 | 6.4446 | 58.5496 | 64.1561 | -1129.8183
2044-05-03 14:01 | -3667.57 | 6.4446 | 58.7296 | 64.1561 | -1074.8587
2044-05-04 15:01 | -3415.09 | 6.4446 | 58.9497 | 64.1561 | -1000.8641
2044-05-05 16:01 | -3266.7 | 6.4446 | 59.1134 | 64.1561 | -957.3753
2044-05-06 17:01 | -1827.78 | 5.2463 | 59.7966 | 64.1561 | -535.6694
2044-05-07 18:01 | -2198.93 | 6.3696 | 60.0149 | 64.1561 | -644.4428
2044-05-08 19:01 | -2609.26 | 6.4446 | 59.8651 | 64.1561 | -764.6986
2044-05-09 20:01 | -2985.79 | 6.4446 | 59.6438 | 64.1561 | -875.0487
2044-05-10 21:01 | -3287.92 | 6.4446 | 59.4619 | 64.1561 | -963.5942
2044-05-11 22:01 | -3469.38 | 6.4446 | 59.3492 | 64.1561 | -1016.7749
2044-05-12 23:01 | -3644.48 | 6.4446 | 59.2191 | 64.1561 | -1068.0917
2044-05-14 00:01 | -5073.34 | 6.4446 | 58.3299 | 64.1561 | -1486.8492
2044-05-15 01:01 | -5393.46 | 6.4446 | 57.9725 | 64.1561 | -1580.6671
2044-05-16 02:01 | -5393.67 | 6.4446 | 57.8542 | 64.1561 | -1580.7286
2044-05-17 03:01 | -5378.65 | 6.4446 | 57.8067 | 64.1561 | -1576.3267
2044-05-18 04:01 | -5371.4 | 6.4446 | 57.7683 | 64.1561 | -1574.2019
2044-05-19 05:01 | -5429.2 | 6.4446 | 57.6801 | 64.1561 | -1591.1415
2044-05-20 06:01 | -5297.88 | 6.4446 | 57.7282 | 64.1561 | -1552.6554
2044-05-21 07:01 | -4567.27 | 6.4446 | 58.1642 | 64.1561 | -1338.5347
2044-05-22 08:01 | -4143.09 | 6.4446 | 58.4898 | 64.1561 | -1214.2198
2044-05-23 09:01 | -4625.9 | 6.4446 | 58.2764 | 64.1561 | -1355.7175
2044-05-24 10:01 | -4296.63 | 6.4446 | 58.4557 | 64.1561 | -1259.218
2044-05-25 11:01 | -3732.82 | 6.4446 | 58.8212 | 64.1561 | -1093.9816
2044-05-26 12:01 | -3230.91 | 6.4446 | 59.2163 | 64.1561 | -946.8863
2044-05-27 13:01 | -2473.44 | 6.4446 | 59.7709 | 64.1561 | -724.8937
2044-05-28 14:01 | -2535.61 | 6.4446 | 59.8649 | 64.1561 | -743.1139
2044-05-29 15:01 | -2591.44 | 6.4446 | 59.9132 | 64.1561 | -759.4761
2044-05-30 16:01 | -2587.01 | 6.4446 | 59.9644 | 64.1561 | -758.1778
2044-05-31 17:01 | -1234.83 | 3.503 | 60.189 | 64.1561 | -361.8929
2044-06-01 18:01 | -1652.31 | 4.9451 | 60.4501 | 64.1561 | -484.2443
2044-06-02 19:01 | -1944.14 | 5.6363 | 60.4678 | 64.1561 | -569.7712
2044-06-03 20:01 | -2375.24 | 6.4446 | 60.3842 | 64.1561 | -696.1141
2044-06-04 21:01 | -2426.88 | 6.4446 | 60.3496 | 64.1561 | -711.2483
2044-06-05 22:01 | -2558.1 | 6.4446 | 60.2888 | 64.1561 | -749.7051
2044-06-06 23:01 | -2697.65 | 6.4446 | 60.1966 | 64.1561 | -790.6032
2044-06-08 00:01 | -3732.92 | 6.4446 | 59.5648 | 64.1561 | -1094.0109
2044-06-09 01:01 | -3717.8 | 6.4446 | 59.464 | 64.1561 | -1089.5796
2044-06-10 02:01 | -3768.95 | 6.4446 | 59.3877 | 64.1561 | -1104.5702
2044-06-11 03:01 | -3829.99 | 6.4446 | 59.3304 | 64.1561 | -1122.4593
2044-06-12 04:01 | -3488 | 6.4446 | 59.5156 | 64.1561 | -1022.2319
2044-06-13 05:01 | -3249.26 | 6.4446 | 59.6714 | 64.1561 | -952.2641
2044-06-14 06:01 | -2541.5 | 6.4446 | 60.1471 | 64.1561 | -744.8401
2044-06-15 07:01 | -2380.95 | 6.4446 | 60.3463 | 64.1561 | -697.7876
2044-06-16 08:01 | -2031 | 5.7419 | 60.4865 | 64.1561 | -595.2273
2044-06-17 09:01 | -2123.56 | 6.0604 | 60.5944 | 64.1561 | -622.354
2044-06-18 10:01 | -2200.48 | 6.2449 | 60.6404 | 64.1561 | -644.897
2044-06-19 11:01 | -2200.48 | 6.2252 | 60.6636 | 64.1561 | -644.897
2044-06-20 12:01 | -2028.12 | 5.7355 | 60.6871 | 64.1561 | -594.3833
2044-06-21 13:01 | -2062.11 | 5.8759 | 60.7323 | 64.1561 | -604.3448
2044-06-22 14:01 | -2020.69 | 5.744 | 60.7435 | 64.1561 | -592.2058
2044-06-23 15:01 | -1777.51 | 5.0664 | 60.7679 | 64.1561 | -520.9368
2044-06-24 16:01 | -1049.48 | 3.0782 | 60.8509 | 64.1561 | -307.5722
2044-06-25 17:01 | -1013.54 | 3.158 | 61.0351 | 64.1561 | -297.0393
2044-06-26 18:01 | -1049.35 | 3.2484 | 61.0895 | 64.1561 | -307.5341
2044-06-27 19:01 | -1560.96 | 4.6724 | 61.0865 | 64.1561 | -457.4722
2044-06-28 20:01 | -2005.68 | 5.7961 | 61.0224 | 64.1561 | -587.8068
2044-06-29 21:01 | -2991.31 | 6.4446 | 60.5163 | 64.1561 | -876.6664
2044-06-30 22:01 | -3454.42 | 6.4446 | 60.1027 | 64.1561 | -1012.3906
2044-07-01 23:01 | -4407.78 | 6.4446 | 59.4004 | 64.1561 | -1291.7928
2044-07-03 00:01 | -5079.6 | 6.4446 | 58.8198 | 64.1561 | -1488.6838
2044-07-04 01:01 | -5168.87 | 6.4446 | 58.5864 | 64.1561 | -1514.8463
2044-07-05 02:01 | -5404.92 | 6.4446 | 58.3228 | 64.1561 | -1584.0257
2044-07-06 03:01 | -5521.59 | 6.4446 | 58.1456 | 64.1561 | -1618.2183
2044-07-07 04:01 | -5517.21 | 6.4446 | 58.0431 | 64.1561 | -1616.9346
2044-07-08 05:01 | -5947.53 | 6.4446 | 57.7061 | 64.1561 | -1743.049
2044-07-09 06:01 | -6045.77 | 6.4446 | 57.5331 | 64.1561 | -1771.8403
2044-07-10 07:01 | -5456.74 | 6.4446 | 57.7913 | 64.1561 | -1599.2126
2044-07-11 08:01 | -5108.63 | 6.4446 | 57.9919 | 64.1561 | -1497.1917
2044-07-12 09:01 | -5977.39 | 6.4446 | 57.4799 | 64.1561 | -1751.8001
2044-07-13 10:01 | -5947.46 | 6.4446 | 57.382 | 64.1561 | -1743.0285
2044-07-14 11:01 | -5768.48 | 6.4446 | 57.4238 | 64.1561 | -1690.5746
2044-07-15 12:01 | -5901.13 | 6.4446 | 57.3247 | 64.1561 | -1729.4505
2044-07-16 13:01 | -5270.27 | 6.4446 | 57.6514 | 64.1561 | -1544.5637
2044-07-17 14:01 | -5155.65 | 6.4446 | 57.733 | 64.1561 | -1510.9719
2044-07-18 15:01 | -5126.53 | 6.4446 | 57.7656 | 64.1561 | -1502.4376
2044-07-19 16:01 | -5110.75 | 6.4446 | 57.7648 | 64.1561 | -1497.813
2044-07-20 17:01 | -3779.66 | 6.4446 | 58.5586 | 64.1561 | -1107.709
2044-07-21 18:01 | -4235.31 | 6.4446 | 58.4241 | 64.1561 | -1241.2468
2044-07-22 19:01 | -4417.29 | 6.4446 | 58.3269 | 64.1561 | -1294.5799
2044-07-23 20:01 | -4754.03 | 6.4446 | 58.0968 | 64.1561 | -1393.2687
2044-07-24 21:01 | -4924.84 | 6.4446 | 57.9656 | 64.1561 | -1443.3281
2044-07-25 22:01 | -5122.79 | 6.4446 | 57.8226 | 64.1561 | -1501.3415
2044-07-26 23:01 | -5091.47 | 6.4446 | 57.7939 | 64.1561 | -1492.1626
2044-07-28 00:01 | -6297.37 | 6.4446 | 57.0481 | 64.1561 | -1845.577
2044-07-29 01:01 | -6523.04 | 6.4446 | 56.7622 | 64.1561 | -1911.7143
2044-07-30 02:01 | -6780.54 | 6.4446 | 56.4951 | 64.1561 | -1987.1801
2044-07-31 03:01 | -6597.41 | 6.4446 | 56.5155 | 64.1561 | -1933.51
2044-08-01 04:01 | -6594.15 | 6.4446 | 56.4695 | 64.1561 | -1932.5546
2044-08-02 05:01 | -6423.64 | 6.4446 | 56.5121 | 64.1561 | -1882.583
2044-08-03 06:01 | -6011.54 | 6.4446 | 56.7416 | 64.1561 | -1761.8085
2044-08-04 07:01 | -6100.32 | 6.4446 | 56.7072 | 64.1561 | -1787.8273
2044-08-05 08:01 | -6002.27 | 6.4446 | 56.7546 | 64.1561 | -1759.0917
2044-08-06 09:01 | -4902.22 | 6.4446 | 57.4165 | 64.1561 | -1436.6989
2044-08-07 10:01 | -3354.23 | 6.4446 | 58.4744 | 64.1561 | -983.0278
2044-08-08 11:01 | -1829.56 | 5.2839 | 59.3869 | 64.1561 | -536.1911
2044-08-09 12:01 | -839.08 | 2.5021 | 59.7293 | 64.1561 | -245.9101
2044-08-10 13:01 | 0.23268 | 1 | 61.3434 | 64.1561 | 0.068192
2044-08-11 14:01 | 2788.43 | 1 | 60.9829 | 64.1561 | 817.2082
2044-08-12 15:01 | 2860.1 | 1 | 61.4944 | 64.1561 | 838.2126
2044-08-13 16:01 | 926.336 | 1 | 62.3024 | 64.1561 | 271.4823
2044-08-14 17:01 | -820.151 | 2.8585 | 61.4048 | 64.1561 | -240.3625
2044-08-15 18:01 | -1485.23 | 4.495 | 61.1137 | 64.1561 | -435.2779
2044-08-16 19:01 | -2338.58 | 6.4446 | 60.9174 | 64.1561 | -685.3701
2044-08-17 20:01 | -3292.16 | 6.4446 | 60.2024 | 64.1561 | -964.8369
2044-08-18 21:01 | -4628.86 | 6.4446 | 59.1979 | 64.1561 | -1356.585
2044-08-19 22:01 | -5101.48 | 6.4446 | 58.6599 | 64.1561 | -1495.0962
2044-08-20 23:01 | -5998.16 | 6.4446 | 57.9233 | 64.1561 | -1757.8872
2044-08-22 00:01 | -6549.85 | 6.4446 | 57.3673 | 64.1561 | -1919.5715
2044-08-23 01:01 | -6858.84 | 6.4446 | 56.9623 | 64.1561 | -2010.1276
2044-08-24 02:01 | -7147.18 | 6.4446 | 56.5803 | 64.1561 | -2094.6317
2044-08-25 03:01 | -6987.76 | 6.4446 | 56.4925 | 64.1561 | -2047.9103
2044-08-26 04:01 | -6900.28 | 6.4446 | 56.4295 | 64.1561 | -2022.2724
2044-08-27 05:01 | -6718.49 | 6.4446 | 56.4684 | 64.1561 | -1968.9951
2044-08-28 06:01 | -6480.06 | 6.4446 | 56.5683 | 64.1561 | -1899.1181
2044-08-29 07:01 | -6472.4 | 6.4446 | 56.556 | 64.1561 | -1896.8732
2044-08-30 08:01 | -5226.16 | 6.4446 | 57.2924 | 64.1561 | -1531.6363
2044-08-31 09:01 | -3771 | 6.4446 | 58.2972 | 64.1561 | -1105.171
2044-09-01 10:01 | -1998.79 | 5.7902 | 59.4562 | 64.1561 | -585.7875
2044-09-02 11:01 | -673.068 | 1.9813 | 59.7862 | 64.1561 | -197.2568
2044-09-03 12:01 | 2583.89 | 1 | 60.8377 | 64.1561 | 757.2634
2044-09-04 13:01 | 2850.42 | 1 | 61.3581 | 64.1561 | 835.3756
2044-09-05 14:01 | 2850.57 | 1 | 75.8013 | 64.1561 | 835.4196
2044-09-06 15:01 | 2872.44 | 1 | 61.9866 | 64.1561 | 841.8291
2044-09-07 16:01 | 2824.14 | 1 | 62.224 | 64.1561 | 827.6737
2044-09-08 17:01 | 1981.58 | 1 | 62.6162 | 64.1561 | 580.7438
2044-09-09 18:01 | -204.032 | 1.1664 | 62.4407 | 64.1561 | -59.7959
2044-09-10 19:01 | -965.94 | 3.1625 | 61.7625 | 64.1561 | -283.0891
2044-09-11 20:01 | -1546.86 | 4.6162 | 61.5155 | 64.1561 | -453.3399
2044-09-12 21:01 | -2799.28 | 6.4446 | 61.0241 | 64.1561 | -820.388
2044-09-13 22:01 | -3202.91 | 6.4446 | 60.568 | 64.1561 | -938.6803
2044-09-14 23:01 | -4487.75 | 6.4446 | 59.6154 | 64.1561 | -1315.2297
2044-09-16 00:01 | -5156.79 | 6.4446 | 58.9625 | 64.1561 | -1511.306
2044-09-17 01:01 | -5314.78 | 6.4446 | 58.6306 | 64.1561 | -1557.6083
2044-09-18 02:01 | -5847.03 | 6.4446 | 58.1353 | 64.1561 | -1713.5953
2044-09-19 03:01 | -6028.78 | 6.4446 | 57.8414 | 64.1561 | -1766.861
2044-09-20 04:01 | -6134.43 | 6.4446 | 57.6102 | 64.1561 | -1797.824
2044-09-21 05:01 | -5884.65 | 6.4446 | 57.6378 | 64.1561 | -1724.6207
2044-09-22 06:01 | -5669.75 | 6.4446 | 57.7134 | 64.1561 | -1661.6397
2044-09-23 07:01 | -5623.9 | 6.4446 | 57.7118 | 64.1561 | -1648.2024
2044-09-24 08:01 | -4684.7 | 6.4446 | 58.2496 | 64.1561 | -1372.95
2044-09-25 09:01 | -4473.2 | 6.4446 | 58.4498 | 64.1561 | -1310.9655
2044-09-26 10:01 | -3789.58 | 6.4446 | 58.907 | 64.1561 | -1110.6163
2044-09-27 11:01 | -2949.52 | 6.4446 | 59.4954 | 64.1561 | -864.419
2044-09-28 12:01 | -2203.08 | 6.2976 | 60.036 | 64.1561 | -645.659
2044-09-29 13:01 | -1820.54 | 5.174 | 60.1664 | 64.1561 | -533.5476
2044-09-30 14:01 | -1967.13 | 5.6923 | 60.2948 | 64.1561 | -576.5089
2044-10-01 15:01 | -1565.52 | 4.4976 | 60.3302 | 64.1561 | -458.8086
2044-10-02 16:01 | -938.36 | 2.8341 | 60.475 | 64.1561 | -275.0062
2044-10-03 17:01 | -1110.93 | 3.4691 | 60.6455 | 64.1561 | -325.5814
2044-10-04 18:01 | -1295.69 | 3.9286 | 60.671 | 64.1561 | -379.7293
2044-10-05 19:01 | -1894.47 | 5.5775 | 60.665 | 64.1561 | -555.2143
2044-10-06 20:01 | -2310.6 | 6.4446 | 60.5684 | 64.1561 | -677.17
2044-10-07 21:01 | -3449.98 | 6.4446 | 59.841 | 64.1561 | -1011.0893
2044-10-08 22:01 | -3741.63 | 6.4446 | 59.5215 | 64.1561 | -1096.5635
2044-10-09 23:01 | -4659.69 | 6.4446 | 58.8601 | 64.1561 | -1365.6203
2044-10-11 00:01 | -5273.53 | 6.4446 | 58.3269 | 64.1561 | -1545.5191
2044-10-12 01:01 | -5622.41 | 6.4446 | 57.9463 | 64.1561 | -1647.7657
2044-10-13 02:01 | -5739.32 | 6.4446 | 57.7354 | 64.1561 | -1682.0287
2044-10-14 03:01 | -5851.1 | 6.4446 | 57.5673 | 64.1561 | -1714.7881
2044-10-15 04:01 | -5905.44 | 6.4446 | 57.4368 | 64.1561 | -1730.7136
2044-10-16 05:01 | -5957.47 | 6.4446 | 57.3281 | 64.1561 | -1745.9621
2044-10-17 06:01 | -6009.05 | 6.4446 | 57.231 | 64.1561 | -1761.0787
2044-10-18 07:01 | -5242.17 | 6.4446 | 57.6409 | 64.1561 | -1536.3284
2044-10-19 08:01 | -4689.69 | 6.4446 | 58.0104 | 64.1561 | -1374.4125
2044-10-20 09:01 | -4938.83 | 6.4446 | 57.9304 | 64.1561 | -1447.4282
2044-10-21 10:01 | -4506.77 | 6.4446 | 58.1822 | 64.1561 | -1320.8039
2044-10-22 11:01 | -3482.61 | 6.4446 | 58.8407 | 64.1561 | -1020.6522
2044-10-23 12:01 | -1535.37 | 4.4139 | 59.7275 | 64.1561 | -449.9725
2044-10-24 13:01 | -2015.51 | 5.9217 | 60.0397 | 64.1561 | -590.6877
2044-10-25 14:01 | -2011.07 | 5.7599 | 60.1008 | 64.1561 | -589.3864
2044-10-26 15:01 | -1760.4 | 5.055 | 60.1703 | 64.1561 | -515.9223
2044-10-27 16:01 | -1772.81 | 5.151 | 60.284 | 64.1561 | -519.5593
2044-10-28 17:01 | -608.485 | 1.8473 | 60.4053 | 64.1561 | -178.3294
2044-10-29 18:01 | -889.093 | 2.935 | 60.673 | 64.1561 | -260.5674
2044-10-30 19:01 | -1121.44 | 3.4879 | 60.6838 | 64.1561 | -328.6616
2044-10-31 20:01 | -1383.62 | 4.1741 | 60.6817 | 64.1561 | -405.499
2044-11-01 21:01 | -1709.84 | 5.0304 | 60.6822 | 64.1561 | -501.1046
2044-11-02 22:01 | -2066.64 | 5.9612 | 60.6701 | 64.1561 | -605.6724
2044-11-03 23:01 | -2186.37 | 6.2158 | 60.6233 | 64.1561 | -640.7618
2044-11-05 00:01 | -3726.73 | 6.4446 | 59.7157 | 64.1561 | -1092.1967
2044-11-06 01:01 | -4185.87 | 6.4446 | 59.2667 | 64.1561 | -1226.7574
2044-11-07 02:01 | -4707.74 | 6.4446 | 58.8111 | 64.1561 | -1379.7024
2044-11-08 03:01 | -5172.28 | 6.4446 | 58.4015 | 64.1561 | -1515.8456
2044-11-09 04:01 | -5228.34 | 6.4446 | 58.2323 | 64.1561 | -1532.2752
2044-11-10 05:01 | -5113.31 | 6.4446 | 58.1886 | 64.1561 | -1498.5632
2044-11-11 06:01 | -5011.8 | 6.4446 | 58.197 | 64.1561 | -1468.8136
2044-11-12 07:01 | -4218.02 | 6.4446 | 58.6405 | 64.1561 | -1236.1796
2044-11-13 08:01 | -3575.56 | 6.4446 | 59.0819 | 64.1561 | -1047.8932
2044-11-14 09:01 | -4035.19 | 6.4446 | 58.8977 | 64.1561 | -1182.5975
2044-11-15 10:01 | -3891.16 | 6.4446 | 58.9724 | 64.1561 | -1140.3864
2044-11-16 11:01 | -3411.63 | 6.4446 | 59.2593 | 64.1561 | -999.8501
2044-11-17 12:01 | -3036.93 | 6.4446 | 59.5431 | 64.1561 | -890.0363
2044-11-18 13:01 | -2901.45 | 6.4446 | 59.6878 | 64.1561 | -850.3311
2044-11-19 14:01 | -3077.16 | 6.4446 | 59.6169 | 64.1561 | -901.8266
2044-11-20 15:01 | -3056.4 | 6.4446 | 59.638 | 64.1561 | -895.7424
2044-11-21 16:01 | -3238.51 | 6.4446 | 59.541 | 64.1561 | -949.1136
2044-11-22 17:01 | -2006.49 | 5.7373 | 60.1212 | 64.1561 | -588.0442
2044-11-23 18:01 | -2455.37 | 6.4446 | 60.127 | 64.1561 | -719.5979
2044-11-24 19:01 | -2905.08 | 6.4446 | 59.871 | 64.1561 | -851.3949
2044-11-25 20:01 | -3082.93 | 6.4446 | 59.7157 | 64.1561 | -903.5176
2044-11-26 21:01 | -3324.73 | 6.4446 | 59.5459 | 64.1561 | -974.3822
2044-11-27 22:01 | -3576.76 | 6.4446 | 59.3691 | 64.1561 | -1048.2449
2044-11-28 23:01 | -3601.58 | 6.4446 | 59.2949 | 64.1561 | -1055.5189
2044-11-30 00:01 | -4869.71 | 6.4446 | 58.4972 | 64.1561 | -1427.1711
2044-12-01 01:01 | -5284.66 | 6.4446 | 58.0917 | 64.1561 | -1548.781
2044-12-02 02:01 | -5279.1 | 6.4446 | 57.9639 | 64.1561 | -1547.1515
2044-12-03 03:01 | -5443.31 | 6.4446 | 57.7967 | 64.1561 | -1595.2767
2044-12-04 04:01 | -5256.24 | 6.4446 | 57.8427 | 64.1561 | -1540.4519
2044-12-05 05:01 | -5163.58 | 6.4446 | 57.8486 | 64.1561 | -1513.2959
2044-12-06 06:01 | -4705.07 | 6.4446 | 58.1109 | 64.1561 | -1378.9199
2044-12-07 07:01 | -4763 | 6.4446 | 58.1078 | 64.1561 | -1395.8975
2044-12-08 08:01 | -4711.42 | 6.4446 | 58.1352 | 64.1561 | -1380.7809
2044-12-09 09:01 | -5023.77 | 6.4446 | 57.9435 | 64.1561 | -1472.3216
2044-12-10 10:01 | -4589.09 | 6.4446 | 58.1634 | 64.1561 | -1344.9295
2044-12-11 11:01 | -4483.44 | 6.4446 | 58.238 | 64.1561 | -1313.9666
2044-12-12 12:01 | -4259.63 | 6.4446 | 58.3773 | 64.1561 | -1248.3743
2044-12-13 13:01 | -3897.56 | 6.4446 | 58.6132 | 64.1561 | -1142.2621
2044-12-14 14:01 | -4134.62 | 6.4446 | 58.5128 | 64.1561 | -1211.7375
2044-12-15 15:01 | -4153.34 | 6.4446 | 58.501 | 64.1561 | -1217.2238
2044-12-16 16:01 | -3376.92 | 6.4446 | 58.9617 | 64.1561 | -989.6776
2044-12-17 17:01 | -3221.78 | 6.4446 | 59.1297 | 64.1561 | -944.2105
2044-12-18 18:01 | -3216.6 | 6.4446 | 59.1852 | 64.1561 | -942.6924
2044-12-19 19:01 | -3682.78 | 6.4446 | 58.923 | 64.1561 | -1079.3163
2044-12-20 20:01 | -3998.87 | 6.4446 | 58.7006 | 64.1561 | -1171.9531
2044-12-21 21:01 | -4846.08 | 6.4446 | 58.1487 | 64.1561 | -1420.2459
2044-12-22 22:01 | -5242.18 | 6.4446 | 57.786 | 64.1561 | -1536.3313
2044-12-23 23:01 | -6037.66 | 6.4446 | 57.183 | 64.1561 | -1769.4635
[5 empty] | 5501627.7826 | 628.0397

## Orlando
| Property | Soil |  |  |  |  | Property | Soil
| Thermal conductivity [W/m K] | 1.72 |  | W/M-K | 0.57779 | BTU/HR-FT-R | Thermal conductivity [Btu/Hr-ft-R] | 0.99379
| Specific heat [J/kg K] | 1900
| Density [kg/m3] | 1300
| Volumeric specific heat [MJ/K-M3] | 2.47
| Thermal diffusivity [m2/hr] | 0.0025069 |  | m2/hr | 10.7639 | ft2/hr | Thermal diffusivity [ft2/hr] | 0.026984
VBGHE design and performance
| Borehole number | 2
| Borehole depth | 360 | ft | 110 | m
| Annual Max. LFT | 95.2 | F
| Annual Min. LFT | 70.9 | F
Time | Thermal load | Fluid flow | Outlet temperature | Far field ground temperature | Load
| Btu/hr | GPM | F | F | W
2020-01-01 | 0 | 0 | 74.6386 | 74.6386 | 0
2020-01-02 01:00 | -843.511 | 2.3751 | 73.7963 | 74.6386 | -247.2087
2020-01-03 02:00 | -973.223 | 2.6932 | 73.7174 | 74.6386 | -285.2235
2020-01-04 03:00 | -1242.13 | 3.3131 | 73.6379 | 74.6386 | -364.0324
2020-01-05 04:00 | -1350.26 | 3.5251 | 73.5711 | 74.6386 | -395.7221
2020-01-06 05:00 | -1386.05 | 3.5959 | 73.5205 | 74.6386 | -406.2112
2020-01-07 06:00 | -1470.97 | 3.7959 | 73.4766 | 74.6386 | -431.0988
2020-01-08 07:00 | -676.372 | 1.8762 | 73.5088 | 74.6386 | -198.2251
2020-01-09 08:00 | -158.955 | 0.79548 | 73.9238 | 74.6386 | -46.5851
2020-01-10 09:00 | -665.201 | 2.081 | 73.6928 | 74.6386 | -194.9512
2020-01-11 10:00 | -660.621 | 1.9734 | 73.6414 | 74.6386 | -193.6089
2020-01-12 11:00 | 4219.71 | 2.1629 | 79.0522 | 74.6386 | 1236.6749
2020-01-13 12:00 | 6634.13 | 2.5392 | 80.9859 | 74.6386 | 1944.2716
2020-01-14 13:00 | 7457.97 | 2.7258 | 81.6734 | 74.6386 | 2185.7152
2020-01-15 14:00 | 6151.52 | 1.9751 | 82.854 | 74.6386 | 1802.8325
2020-01-16 15:00 | 5885.68 | 1.8293 | 83.2178 | 74.6386 | 1724.9225
2020-01-17 16:00 | 5937.1 | 1.9051 | 83.1062 | 74.6386 | 1739.9922
2020-01-18 17:00 | 7664.1 | 2.5593 | 82.921 | 74.6386 | 2246.126
2020-01-19 18:00 | 6392.92 | 2.0202 | 83.5314 | 74.6386 | 1873.5799
2020-01-20 19:00 | 5395.62 | 1.6175 | 83.9769 | 74.6386 | 1581.3001
2020-01-21 20:00 | 4178.52 | 1.307 | 83.6334 | 74.6386 | 1224.6033
2020-01-22 21:00 | 3217.54 | 1 | 84.5242 | 74.6386 | 942.9679
2020-01-23 22:00 | 3100.04 | 1 | 87.016 | 74.6386 | 908.532
2020-01-24 23:00 | 3052.49 | 1 | 74.4171 | 74.6386 | 894.5965
2020-01-26 | 0 | 0 | 75.8426 | 74.6386 | 0
2020-01-27 01:00 | -405.889 | 1.3281 | 74.8491 | 74.6386 | -118.9543
2020-01-28 02:00 | -705.519 | 2.1163 | 74.6052 | 74.6386 | -206.7672
2020-01-29 03:00 | -733.405 | 2.1253 | 74.4624 | 74.6386 | -214.9398
2020-01-30 04:00 | -715.494 | 2.0844 | 74.3683 | 74.6386 | -209.6906
2020-01-31 05:00 | -392.092 | 1.3245 | 74.3796 | 74.6386 | -114.9108
2020-02-01 06:00 | 359.004 | 1 | 74.8794 | 74.6386 | 105.2137
2020-02-02 07:00 | 1976.63 | 1 | 74.1252 | 74.6386 | 579.2931
2020-02-03 08:00 | 2815.25 | 1 | 73.8499 | 74.6386 | 825.0683
2020-02-04 09:00 | 2899.41 | 1 | 73.9451 | 74.6386 | 849.7332
2020-02-05 10:00 | 3065.08 | 1 | 86.5173 | 74.6386 | 898.2863
2020-02-06 11:00 | 3048.2 | 1 | 87.3823 | 74.6386 | 893.3392
2020-02-07 12:00 | 3130.68 | 1 | 86.8566 | 74.6386 | 917.5117
2020-02-08 13:00 | 2980.44 | 1 | 74.1399 | 74.6386 | 873.4807
2020-02-09 14:00 | 3056.39 | 1 | 74.1245 | 74.6386 | 895.7395
2020-02-10 15:00 | 3139.43 | 1 | 74.1122 | 74.6386 | 920.0761
2020-02-11 16:00 | 3185.01 | 1 | 83.7742 | 74.6386 | 933.4343
2020-02-12 17:00 | 3234.56 | 1.0335 | 83.089 | 74.6386 | 947.956
2020-02-13 18:00 | 3177.44 | 1 | 83.2775 | 74.6386 | 931.2157
2020-02-14 19:00 | 3014.22 | 1 | 74.2615 | 74.6386 | 883.3807
2020-02-15 20:00 | 2929.03 | 1 | 74.3017 | 74.6386 | 858.414
2020-02-16 21:00 | -167.593 | 0.93396 | 75.2882 | 74.6386 | -49.1167
2020-02-17 22:00 | -417.263 | 1.4656 | 74.8061 | 74.6386 | -122.2877
2020-02-18 23:00 | -1284.3 | 3.4768 | 74.4529 | 74.6386 | -376.3912
2020-02-20 | -1601.26 | 4.0832 | 74.2576 | 74.6386 | -469.283
2020-02-21 01:00 | -1783.87 | 4.4772 | 74.115 | 74.6386 | -522.8007
2020-02-22 02:00 | -1833.9 | 4.5712 | 73.9952 | 74.6386 | -537.463
2020-02-23 03:00 | -1903.75 | 4.7346 | 73.927 | 74.6386 | -557.934
2020-02-24 04:00 | -1780.88 | 4.4299 | 73.8639 | 74.6386 | -521.9244
2020-02-25 05:00 | -1674.81 | 4.2019 | 73.8309 | 74.6386 | -490.8384
2020-02-26 06:00 | -1154.36 | 2.9759 | 73.8227 | 74.6386 | -338.3095
2020-02-27 07:00 | -1048.81 | 2.8215 | 73.8585 | 74.6386 | -307.3759
2020-02-28 08:00 | -835.878 | 2.3264 | 73.8727 | 74.6386 | -244.9717
2020-02-29 09:00 | -934.277 | 2.5995 | 73.8811 | 74.6386 | -273.8096
2020-03-01 10:00 | -364.254 | 1.2226 | 74.0188 | 74.6386 | -106.7523
2020-03-02 11:00 | 1802.31 | 1 | 73.8865 | 74.6386 | 528.2049
2020-03-03 12:00 | 2943.53 | 1 | 73.5065 | 74.6386 | 862.6635
2020-03-04 13:00 | 3092.87 | 1 | 73.6117 | 74.6386 | 906.4307
2020-03-05 14:00 | 3110.27 | 1 | 73.7139 | 74.6386 | 911.5302
2020-03-06 15:00 | 3152.99 | 1 | 73.7805 | 74.6386 | 924.0502
2020-03-07 16:00 | 3259.85 | 1.0298 | 82.8849 | 74.6386 | 955.3677
2020-03-08 17:00 | 3450.23 | 1.0722 | 83.0502 | 74.6386 | 1011.1626
2020-03-09 18:00 | 3217.22 | 1.0431 | 82.7834 | 74.6386 | 942.8741
2020-03-10 19:00 | 3045.34 | 1 | 86.3693 | 74.6386 | 892.5011
2020-03-11 20:00 | 3096.98 | 1 | 74.0238 | 74.6386 | 907.6352
2020-03-12 21:00 | 0 | 0 | 75.5603 | 74.6386 | 0
2020-03-13 22:00 | -258.426 | 1.065 | 74.7861 | 74.6386 | -75.7372
2020-03-14 23:00 | -1162.12 | 3.2178 | 74.3705 | 74.6386 | -340.5838
2020-03-16 | -1533 | 3.945 | 74.1708 | 74.6386 | -449.278
2020-03-17 01:00 | -1913.64 | 4.8039 | 74.0209 | 74.6386 | -560.8325
2020-03-18 02:00 | -1971.94 | 4.8819 | 73.8807 | 74.6386 | -577.9186
2020-03-19 03:00 | -2091.62 | 5.1674 | 73.8057 | 74.6386 | -612.9933
2020-03-20 04:00 | -1958.54 | 4.8281 | 73.7327 | 74.6386 | -573.9914
2020-03-21 05:00 | -1876.55 | 4.6607 | 73.6934 | 74.6386 | -549.9625
2020-03-22 06:00 | -1570.09 | 3.9396 | 73.6643 | 74.6386 | -460.148
2020-03-23 07:00 | -1452.83 | 3.7168 | 73.6649 | 74.6386 | -425.7824
2020-03-24 08:00 | -1332.09 | 3.4459 | 73.6536 | 74.6386 | -390.397
2020-03-25 09:00 | -1781.26 | 4.546 | 73.6408 | 74.6386 | -522.0358
2020-03-26 10:00 | -1492.66 | 3.7664 | 73.5872 | 74.6386 | -437.4555
2020-03-27 11:00 | -818.69 | 2.2153 | 73.6392 | 74.6386 | -239.9344
2020-03-28 12:00 | -690.012 | 2.0305 | 73.744 | 74.6386 | -202.2226
2020-03-29 13:00 | -520.276 | 1.6405 | 73.8157 | 74.6386 | -152.4778
2020-03-30 14:00 | -411.772 | 1.4126 | 73.8891 | 74.6386 | -120.6785
2020-03-31 15:00 | -365.167 | 1.3193 | 73.9432 | 74.6386 | -107.0199
2020-04-01 16:00 | 185.864 | 1 | 74.5212 | 74.6386 | 54.4714
2020-04-02 17:00 | 451.035 | 1 | 74.433 | 74.6386 | 132.1853
2020-04-03 18:00 | -15.2229 | 0.57939 | 74.7079 | 74.6386 | -4.4614
2020-04-04 19:00 | -529.003 | 1.7609 | 73.9595 | 74.6386 | -155.0355
2020-04-05 20:00 | -872.838 | 2.4998 | 73.7947 | 74.6386 | -255.8036
2020-04-06 21:00 | -1532.57 | 4.022 | 73.686 | 74.6386 | -449.1519
2020-04-07 22:00 | -1891.5 | 4.7682 | 73.5787 | 74.6386 | -554.3439
2020-04-08 23:00 | -2682.77 | 6.5195 | 73.4702 | 74.6386 | -786.2423
2020-04-10 | -3043.49 | 6.5195 | 73.236 | 74.6386 | -891.9589
2020-04-11 01:00 | -3378.05 | 6.5195 | 73.0232 | 74.6386 | -990.0087
2020-04-12 02:00 | -3622.52 | 6.5195 | 72.8483 | 74.6386 | -1061.6558
2020-04-13 03:00 | -3731.88 | 6.5195 | 72.7302 | 74.6386 | -1093.7061
2020-04-14 04:00 | -3972.79 | 6.5195 | 72.5706 | 74.6386 | -1164.3098
2020-04-15 05:00 | -3783.42 | 6.5195 | 72.5653 | 74.6386 | -1108.8109
2020-04-16 06:00 | -3468.64 | 6.5195 | 72.6355 | 74.6386 | -1016.558
2020-04-17 07:00 | -3514.74 | 6.5195 | 72.6034 | 74.6386 | -1030.0686
2020-04-18 08:00 | -3034.33 | 6.5195 | 72.7498 | 74.6386 | -889.2743
2020-04-19 09:00 | -2502.98 | 6.0959 | 72.891 | 74.6386 | -733.551
2020-04-20 10:00 | -1809.92 | 4.4344 | 72.9375 | 74.6386 | -530.4352
2020-04-21 11:00 | -289.888 | 0.90636 | 73.2074 | 74.6386 | -84.9578
2020-04-22 12:00 | 2884.26 | 1 | 72.7128 | 74.6386 | 845.2932
2020-04-23 13:00 | 3247.81 | 1 | 83.3283 | 74.6386 | 951.8392
2020-04-24 14:00 | 3310.61 | 1.056 | 82.0576 | 74.6386 | 970.244
2020-04-25 15:00 | 3067.51 | 1 | 86.148 | 74.6386 | 898.9984
2020-04-26 16:00 | 3023.06 | 1 | 83.2611 | 74.6386 | 885.9714
2020-04-27 17:00 | 3114.18 | 1 | 73.4638 | 74.6386 | 912.6761
2020-04-28 18:00 | 3036.43 | 1 | 73.5615 | 74.6386 | 889.8898
2020-04-29 19:00 | 0 | 0 | 75.0753 | 74.6386 | 0
2020-04-30 20:00 | -478.227 | 1.6088 | 74.1867 | 74.6386 | -140.1545
2020-05-01 21:00 | -1581.98 | 4.1987 | 73.8831 | 74.6386 | -463.6326
2020-05-02 22:00 | -1971.57 | 4.9399 | 73.7021 | 74.6386 | -577.8101
2020-05-03 23:00 | -2852.11 | 6.5195 | 73.4908 | 74.6386 | -835.8709
2020-05-05 | -3447.78 | 6.5195 | 73.105 | 74.6386 | -1010.4446
2020-05-06 01:00 | -3682.79 | 6.5195 | 72.8784 | 74.6386 | -1079.3192
2020-05-07 02:00 | -3727.67 | 6.5195 | 72.7456 | 74.6386 | -1092.4722
2020-05-08 03:00 | -3888.34 | 6.5195 | 72.6021 | 74.6386 | -1139.56
2020-05-09 04:00 | -3856.67 | 6.5195 | 72.5281 | 74.6386 | -1130.2784
2020-05-10 05:00 | -3803.34 | 6.5195 | 72.48 | 74.6386 | -1114.6489
2020-05-11 06:00 | -3522.8 | 6.5195 | 72.5265 | 74.6386 | -1032.4308
2020-05-12 07:00 | -2570.87 | 6.2789 | 72.8214 | 74.6386 | -753.4476
2020-05-13 08:00 | -1674.04 | 4.0931 | 72.8705 | 74.6386 | -490.6127
2020-05-14 09:00 | -1074.87 | 2.8194 | 73.0252 | 74.6386 | -315.0133
2020-05-15 10:00 | -266.179 | 0.97913 | 73.3719 | 74.6386 | -78.0094
2020-05-16 11:00 | 2200.57 | 1 | 83.2342 | 74.6386 | 644.9234
2020-05-17 12:00 | 2946.78 | 1 | 72.9569 | 74.6386 | 863.616
2020-05-18 13:00 | 3150.42 | 1 | 73.0646 | 74.6386 | 923.297
2020-05-19 14:00 | 3181.76 | 1 | 73.1865 | 74.6386 | 932.4818
2020-05-20 15:00 | 3203.56 | 1 | 73.2887 | 74.6386 | 938.8708
2020-05-21 16:00 | 3240.49 | 1 | 87.008 | 74.6386 | 949.6939
2020-05-22 17:00 | 5823.15 | 1.785 | 82.7147 | 74.6386 | 1706.5968
2020-05-23 18:00 | 4846.14 | 1.5411 | 82.694 | 74.6386 | 1420.2634
2020-05-24 19:00 | 4315.19 | 1.3522 | 82.9021 | 74.6386 | 1264.6574
2020-05-25 20:00 | 3623.27 | 1.1137 | 83.0835 | 74.6386 | 1061.8756
2020-05-26 21:00 | 3349.54 | 1.0578 | 82.8984 | 74.6386 | 981.6533
2020-05-27 22:00 | 3204.11 | 1 | 83.9648 | 74.6386 | 939.0319
2020-05-28 23:00 | 3203.03 | 1 | 84.9029 | 74.6386 | 938.7154
2020-05-30 | 0 | 0 | 75.4437 | 74.6386 | 0
2020-05-31 01:00 | -110.272 | 0.69614 | 74.8494 | 74.6386 | -32.3175
2020-06-01 02:00 | -162.024 | 0.88868 | 74.6759 | 74.6386 | -47.4845
2020-06-02 03:00 | -70.7816 | 0.65993 | 74.802 | 74.6386 | -20.744
2020-06-03 04:00 | -29.1208 | 0.57966 | 75.0522 | 74.6386 | -8.5345
2020-06-04 05:00 | 49.9012 | 1 | 74.938 | 74.6386 | 14.6246
2020-06-05 06:00 | 291.337 | 1 | 74.8144 | 74.6386 | 85.3824
2020-06-06 07:00 | 1870.29 | 1 | 80.5689 | 74.6386 | 548.1279
2020-06-07 08:00 | 2621.59 | 1 | 82.3075 | 74.6386 | 768.3122
2020-06-08 09:00 | 2523.69 | 1 | 73.9898 | 74.6386 | 739.6205
2020-06-09 10:00 | 2927.11 | 1 | 73.854 | 74.6386 | 857.8513
2020-06-10 11:00 | 3183.04 | 1 | 73.7943 | 74.6386 | 932.8569
2020-06-11 12:00 | 3144.2 | 1 | 73.8946 | 74.6386 | 921.4741
2020-06-12 13:00 | 3329.16 | 1.0672 | 82.849 | 74.6386 | 975.6805
2020-06-13 14:00 | 5518.57 | 1.8966 | 82.3826 | 74.6386 | 1617.3332
2020-06-14 15:00 | 5843.69 | 2.0653 | 82.3983 | 74.6386 | 1712.6165
2020-06-15 16:00 | 5005.94 | 1.7353 | 82.6812 | 74.6386 | 1467.0962
2020-06-16 17:00 | 5453.72 | 1.9284 | 82.5708 | 74.6386 | 1598.3276
2020-06-17 18:00 | 3230.56 | 1.0908 | 82.9678 | 74.6386 | 946.7837
2020-06-18 19:00 | 3037.89 | 1 | 88.4239 | 74.6386 | 890.3177
2020-06-19 20:00 | 3053.14 | 1 | 74.3151 | 74.6386 | 894.787
2020-06-20 21:00 | 0 | 0 | 75.7678 | 74.6386 | 0
2020-06-21 22:00 | -219.144 | 1.0189 | 75.0144 | 74.6386 | -64.2248
2020-06-22 23:00 | -504.021 | 1.6648 | 74.6374 | 74.6386 | -147.714
2020-06-24 | -1600.23 | 4.2156 | 74.3698 | 74.6386 | -468.9811
2020-06-25 01:00 | -1955.63 | 4.875 | 74.1651 | 74.6386 | -573.1386
2020-06-26 02:00 | -2217.55 | 5.4592 | 73.999 | 74.6386 | -649.8998
2020-06-27 03:00 | -2321.14 | 5.6679 | 73.8858 | 74.6386 | -680.259
2020-06-28 04:00 | -2512.24 | 6.1177 | 73.7929 | 74.6386 | -736.2649
2020-06-29 05:00 | -2585.77 | 6.2655 | 73.6918 | 74.6386 | -757.8144
2020-06-30 06:00 | -2329.05 | 5.6376 | 73.6235 | 74.6386 | -682.5772
2020-07-01 07:00 | -2407.41 | 5.8807 | 73.5898 | 74.6386 | -705.5422
2020-07-02 08:00 | -1565.39 | 3.8344 | 73.5362 | 74.6386 | -458.7705
2020-07-03 09:00 | -825.619 | 2.226 | 73.6507 | 74.6386 | -241.965
2020-07-04 10:00 | 1135.43 | 1 | 74.0408 | 74.6386 | 332.7617
2020-07-05 11:00 | 3106.87 | 1 | 85.4816 | 74.6386 | 910.5337
2020-07-06 12:00 | 4546.38 | 1.4649 | 82.3369 | 74.6386 | 1332.4125
2020-07-07 13:00 | 5395.52 | 1.7273 | 82.6414 | 74.6386 | 1581.2708
2020-07-08 14:00 | 6002.83 | 1.9501 | 82.7525 | 74.6386 | 1759.2558
2020-07-09 15:00 | 6460.28 | 2.0724 | 83.0459 | 74.6386 | 1893.3212
2020-07-10 16:00 | 6996.4 | 2.2676 | 83.1489 | 74.6386 | 2050.4424
2020-07-11 17:00 | 5124.68 | 1.5982 | 83.5992 | 74.6386 | 1501.8955
2020-07-12 18:00 | 3104.18 | 1.0254 | 83.16 | 74.6386 | 909.7454
2020-07-13 19:00 | 3003.32 | 1 | 74.4167 | 74.6386 | 880.1862
2020-07-14 20:00 | 0 | 0 | 75.8195 | 74.6386 | 0
2020-07-15 21:00 | -1237.51 | 3.3863 | 74.7182 | 74.6386 | -362.6784
2020-07-16 22:00 | -1815.02 | 4.5933 | 74.3974 | 74.6386 | -531.9299
2020-07-17 23:00 | -2838.96 | 6.5195 | 74.1171 | 74.6386 | -832.017
2020-07-19 | -3337.82 | 6.5195 | 73.74 | 74.6386 | -978.2185
2020-07-20 01:00 | -3688.26 | 6.5195 | 73.4201 | 74.6386 | -1080.9223
2020-07-21 02:00 | -3884.13 | 6.5195 | 73.2004 | 74.6386 | -1138.3261
2020-07-22 03:00 | -4200.32 | 6.5195 | 72.9559 | 74.6386 | -1230.9923
2020-07-23 04:00 | -3832.73 | 6.5195 | 72.9536 | 74.6386 | -1123.2623
2020-07-24 05:00 | -3661.94 | 6.5195 | 72.9464 | 74.6386 | -1073.2087
2020-07-25 06:00 | -3366.84 | 6.5195 | 73.0094 | 74.6386 | -986.7234
2020-07-26 07:00 | -2991.01 | 6.5195 | 73.1144 | 74.6386 | -876.5785
2020-07-27 08:00 | -1516.82 | 3.6822 | 73.2265 | 74.6386 | -444.5361
2020-07-28 09:00 | -266.3 | 0.90754 | 73.6128 | 74.6386 | -78.0448
2020-07-29 10:00 | 2620.87 | 1 | 81.9673 | 74.6386 | 768.1012
2020-07-30 11:00 | 4579.02 | 1.4931 | 81.9901 | 74.6386 | 1341.9783
2020-07-31 12:00 | 6018.6 | 2.0183 | 82.0995 | 74.6386 | 1763.8775
2020-08-01 13:00 | 7197.26 | 2.3426 | 82.609 | 74.6386 | 2109.3087
2020-08-02 14:00 | 7887.81 | 2.5406 | 82.9653 | 74.6386 | 2311.6889
2020-08-03 15:00 | 7978.09 | 2.5619 | 83.2403 | 74.6386 | 2338.1474
2020-08-04 16:00 | 8364.47 | 2.7141 | 83.3399 | 74.6386 | 2451.3842
2020-08-05 17:00 | 5813.55 | 1.8815 | 83.5275 | 74.6386 | 1703.7833
2020-08-06 18:00 | 4380.43 | 1.3813 | 83.6715 | 74.6386 | 1283.7773
2020-08-07 19:00 | 3027.27 | 1 | 86.0776 | 74.6386 | 887.2053
2020-08-08 20:00 | 3024.39 | 1 | 74.4907 | 74.6386 | 886.3612
2020-08-09 21:00 | -544.143 | 1.8285 | 75.2021 | 74.6386 | -159.4726
2020-08-10 22:00 | -1134.41 | 3.0858 | 74.7253 | 74.6386 | -332.4628
2020-08-11 23:00 | -2096.48 | 5.2862 | 74.4379 | 74.6386 | -614.4176
2020-08-13 | -2613.27 | 6.3627 | 74.2135 | 74.6386 | -765.8738
2020-08-14 01:00 | -3126.68 | 6.5195 | 73.8732 | 74.6386 | -916.3395
2020-08-15 02:00 | -3240.6 | 6.5195 | 73.6472 | 74.6386 | -949.7261
2020-08-16 03:00 | -3409.28 | 6.5195 | 73.4648 | 74.6386 | -999.1613
2020-08-17 04:00 | -3232.44 | 6.5195 | 73.4127 | 74.6386 | -947.3346
2020-08-18 05:00 | -2776.56 | 6.5195 | 73.5109 | 74.6386 | -813.7294
2020-08-19 06:00 | -2499.75 | 6.0382 | 73.5175 | 74.6386 | -732.6044
2020-08-20 07:00 | -2420.38 | 5.8839 | 73.5181 | 74.6386 | -709.3434
2020-08-21 08:00 | -1150.92 | 2.841 | 73.5099 | 74.6386 | -337.3014
2020-08-22 09:00 | 1938.91 | 1 | 73.6203 | 74.6386 | 568.2384
2020-08-23 10:00 | 3820.4 | 1.186 | 82.4594 | 74.6386 | 1119.6487
2020-08-24 11:00 | 6212.72 | 2.0244 | 82.3624 | 74.6386 | 1820.7685
2020-08-25 12:00 | 7746.81 | 2.5736 | 82.556 | 74.6386 | 2270.3659
2020-08-26 13:00 | 9018.94 | 2.9258 | 83.0623 | 74.6386 | 2643.1904
2020-08-27 14:00 | 8844.98 | 2.8362 | 83.4663 | 74.6386 | 2592.2078
2020-08-28 15:00 | 8676.26 | 2.787 | 83.6505 | 74.6386 | 2542.7608
2020-08-29 16:00 | 8615.78 | 2.799 | 83.7063 | 74.6386 | 2525.0359
2020-08-30 17:00 | 6173.4 | 1.9446 | 84.054 | 74.6386 | 1809.2449
2020-08-31 18:00 | 4842.94 | 1.5358 | 83.929 | 74.6386 | 1419.3256
2020-09-01 19:00 | 3020.39 | 1 | 83.8392 | 74.6386 | 885.1889
2020-09-02 20:00 | 3117.26 | 1 | 74.693 | 74.6386 | 913.5787
2020-09-03 21:00 | 0 | 0 | 76.1275 | 74.6386 | 0
2020-09-04 22:00 | -684.287 | 1.8996 | 74.9877 | 74.6386 | -200.5447
2020-09-05 23:00 | -1518.49 | 3.9886 | 74.7192 | 74.6386 | -445.0255
2020-09-07 | -1937.87 | 4.8336 | 74.4811 | 74.6386 | -567.9336
2020-09-08 01:00 | -2039.03 | 5.0168 | 74.3028 | 74.6386 | -597.5807
2020-09-09 02:00 | -2155.55 | 5.2893 | 74.1571 | 74.6386 | -631.7293
2020-09-10 03:00 | -2177.49 | 5.3259 | 74.0547 | 74.6386 | -638.1593
2020-09-11 04:00 | -2023.55 | 4.9584 | 73.9689 | 74.6386 | -593.044
2020-09-12 05:00 | -1725.47 | 4.2757 | 73.9311 | 74.6386 | -505.6853
2020-09-13 06:00 | -1338.72 | 3.4059 | 73.9375 | 74.6386 | -392.3401
2020-09-14 07:00 | -1301.55 | 3.3861 | 73.9675 | 74.6386 | -381.4467
2020-09-15 08:00 | 0 | 1 | 74.8672 | 74.6386 | 0
2020-09-16 09:00 | 3019.76 | 1 | 83.4912 | 74.6386 | 885.0043
2020-09-17 10:00 | 5596.94 | 1.7978 | 82.5861 | 74.6386 | 1640.3012
2020-09-18 11:00 | 7739.61 | 2.5567 | 82.7143 | 74.6386 | 2268.2558
2020-09-19 12:00 | 8722.96 | 2.8682 | 83.0927 | 74.6386 | 2556.4472
2020-09-20 13:00 | 7759.52 | 2.5063 | 83.5197 | 74.6386 | 2274.0908
2020-09-21 14:00 | 9470.55 | 3.124 | 83.5006 | 74.6386 | 2775.5442
2020-09-22 15:00 | 7963.47 | 2.528 | 84.0193 | 74.6386 | 2333.8627
2020-09-23 16:00 | 8357.24 | 2.7485 | 83.8141 | 74.6386 | 2449.2653
2020-09-24 17:00 | 7276.55 | 2.2634 | 84.3083 | 74.6386 | 2132.5463
2020-09-25 18:00 | 6131.74 | 1.8783 | 84.4346 | 74.6386 | 1797.0356
2020-09-26 19:00 | 4442.1 | 1.3723 | 84.3383 | 74.6386 | 1301.851
2020-09-27 20:00 | 3126.19 | 1 | 83.9911 | 74.6386 | 916.1958
2020-09-28 21:00 | 3047.41 | 1 | 74.9355 | 74.6386 | 893.1077
2020-09-29 22:00 | 0 | 0 | 76.3192 | 74.6386 | 0
2020-09-30 23:00 | -729.924 | 2.1176 | 75.2136 | 74.6386 | -213.9196
2020-10-02 | -1060.99 | 2.8847 | 74.9241 | 74.6386 | -310.9455
2020-10-03 01:00 | -1335.92 | 3.4801 | 74.7366 | 74.6386 | -391.5195
2020-10-04 02:00 | -1543.68 | 3.9318 | 74.5766 | 74.6386 | -452.4079
2020-10-05 03:00 | -1634.77 | 4.1184 | 74.4373 | 74.6386 | -479.1038
2020-10-06 04:00 | -1618.4 | 4.0686 | 74.3466 | 74.6386 | -474.3062
2020-10-07 05:00 | -1522.32 | 3.8465 | 74.2852 | 74.6386 | -446.148
2020-10-08 06:00 | -1249.54 | 3.2166 | 74.2542 | 74.6386 | -366.204
2020-10-09 07:00 | -772.402 | 2.1341 | 74.3002 | 74.6386 | -226.3687
2020-10-10 08:00 | 2460.93 | 1 | 83.8593 | 74.6386 | 721.2274
2020-10-11 09:00 | 3985.42 | 1.2792 | 82.7687 | 74.6386 | 1168.0113
2020-10-12 10:00 | 6946.34 | 2.3962 | 82.493 | 74.6386 | 2035.7713
2020-10-13 11:00 | 8834.03 | 3.024 | 82.8885 | 74.6386 | 2588.9986
2020-10-14 12:00 | 10111.2 | 3.3427 | 83.4881 | 74.6386 | 2963.3002
2020-10-15 13:00 | 11023.4 | 3.6105 | 83.8865 | 74.6386 | 3230.6396
2020-10-16 14:00 | 9971.92 | 3.164 | 84.3997 | 74.6386 | 2922.4813
2020-10-17 15:00 | 9626.22 | 3.0478 | 84.548 | 74.6386 | 2821.1666
2020-10-18 16:00 | 9329.31 | 3.0009 | 84.5137 | 74.6386 | 2734.1509
2020-10-19 17:00 | 8237.53 | 2.5915 | 84.7546 | 74.6386 | 2414.1817
2020-10-20 18:00 | 7153.96 | 2.2255 | 84.8378 | 74.6386 | 2096.6187
2020-10-21 19:00 | 5503.38 | 1.7054 | 84.8175 | 74.6386 | 1612.8815
2020-10-22 20:00 | 4292.39 | 1.3353 | 84.6671 | 74.6386 | 1257.9753
2020-10-23 21:00 | 3065.08 | 1 | 75.4415 | 74.6386 | 898.2863
2020-10-24 22:00 | 3061.34 | 1 | 75.2785 | 74.6386 | 897.1902
2020-10-25 23:00 | 0 | 0 | 76.6578 | 74.6386 | 0
2020-10-27 | -541.666 | 1.6543 | 75.5817 | 74.6386 | -158.7466
2020-10-28 01:00 | -698.662 | 2.06 | 75.3262 | 74.6386 | -204.7576
2020-10-29 02:00 | -737.809 | 2.1241 | 75.1659 | 74.6386 | -216.2305
2020-10-30 03:00 | -683.183 | 1.9934 | 75.0667 | 74.6386 | -200.2212
2020-10-31 04:00 | -680.801 | 1.9999 | 74.9719 | 74.6386 | -199.5231
2020-11-01 05:00 | -696.44 | 2.0374 | 74.9122 | 74.6386 | -204.1064
2020-11-02 06:00 | -758.372 | 2.1812 | 74.8515 | 74.6386 | -222.2569
2020-11-03 07:00 | 5.9973 | 1 | 75.6327 | 74.6386 | 1.7576
2020-11-04 08:00 | 2215.22 | 1.0828 | 80.4991 | 74.6386 | 649.2169
2020-11-05 09:00 | 3050.11 | 1.083 | 82.4741 | 74.6386 | 893.899
2020-11-06 10:00 | 4811.26 | 1.6648 | 82.7638 | 74.6386 | 1410.0411
2020-11-07 11:00 | 5886.85 | 2.018 | 83.02 | 74.6386 | 1725.2654
2020-11-08 12:00 | 7269.21 | 2.4369 | 83.3736 | 74.6386 | 2130.3952
2020-11-09 13:00 | 6978.35 | 2.2137 | 83.9988 | 74.6386 | 2045.1525
2020-11-10 14:00 | 6075.63 | 1.817 | 84.5621 | 74.6386 | 1780.5914
2020-11-11 15:00 | 5656.79 | 1.788 | 84.1539 | 74.6386 | 1657.8415
2020-11-12 16:00 | 5877.4 | 1.8597 | 84.1438 | 74.6386 | 1722.4959
2020-11-13 17:00 | 7589.78 | 2.4675 | 83.982 | 74.6386 | 2224.3449
2020-11-14 18:00 | 6579.88 | 1.9772 | 84.7374 | 74.6386 | 1928.3725
2020-11-15 19:00 | 5382.18 | 1.6974 | 84.3984 | 74.6386 | 1577.3613
2020-11-16 20:00 | 4491.63 | 1.3931 | 84.4703 | 74.6386 | 1316.3668
2020-11-17 21:00 | 3896.88 | 1.2354 | 84.2463 | 74.6386 | 1142.0628
2020-11-18 22:00 | 3329.04 | 1.0495 | 84.2272 | 74.6386 | 975.6453
2020-11-19 23:00 | 3194.89 | 1 | 84.6136 | 74.6386 | 936.3298
2020-11-21 | 0 | 0 | 76.5777 | 74.6386 | 0
2020-11-22 01:00 | 417.896 | 1 | 76.1072 | 74.6386 | 122.4732
2020-11-23 02:00 | 92.6568 | 1 | 76.1482 | 74.6386 | 27.155
2020-11-24 03:00 | 182.329 | 1 | 76.0225 | 74.6386 | 53.4354
2020-11-25 04:00 | 511.312 | 1 | 75.7961 | 74.6386 | 149.8508
2020-11-26 05:00 | 626.555 | 1 | 75.6915 | 74.6386 | 183.6251
2020-11-27 06:00 | 52.4736 | 1 | 75.9627 | 74.6386 | 15.3785
2020-11-28 07:00 | 2620.91 | 1 | 74.6619 | 74.6386 | 768.1129
2020-11-29 08:00 | 2891.65 | 1 | 74.6781 | 74.6386 | 847.459
2020-11-30 09:00 | 2844.92 | 1 | 74.7927 | 74.6386 | 833.7637
2020-12-01 10:00 | 3271.21 | 1 | 74.6051 | 74.6386 | 958.697
2020-12-02 11:00 | 3186.68 | 1 | 74.6829 | 74.6386 | 933.9237
2020-12-03 12:00 | 3227.96 | 1 | 74.7006 | 74.6386 | 946.0217
2020-12-04 13:00 | 3053.12 | 1 | 74.7835 | 74.6386 | 894.7811
2020-12-05 14:00 | 3085.23 | 1 | 74.7568 | 74.6386 | 904.1917
2020-12-06 15:00 | 3112.13 | 1 | 74.7417 | 74.6386 | 912.0753
2020-12-07 16:00 | 3104.51 | 1 | 74.7401 | 74.6386 | 909.8421
2020-12-08 17:00 | 3888.54 | 1.2135 | 83.8232 | 74.6386 | 1139.6186
2020-12-09 18:00 | 3107.04 | 1 | 84.3595 | 74.6386 | 910.5835
2020-12-10 19:00 | 3135.1 | 1 | 88.6821 | 74.6386 | 918.8071
2020-12-11 20:00 | 3122.3 | 1 | 74.7304 | 74.6386 | 915.0558
2020-12-12 21:00 | 3108.33 | 1 | 74.743 | 74.6386 | 910.9616
2020-12-13 22:00 | 3120.2 | 1 | 74.7389 | 74.6386 | 914.4404
2020-12-14 23:00 | 3104.88 | 1 | 74.746 | 74.6386 | 909.9505
2020-12-16 | -732.846 | 2.2665 | 75.4987 | 74.6386 | -214.776
2020-12-17 01:00 | -1195.26 | 3.1831 | 75.1041 | 74.6386 | -350.2961
2020-12-18 02:00 | -1393.5 | 3.5869 | 74.8896 | 74.6386 | -408.3945
2020-12-19 03:00 | -1469.15 | 3.7387 | 74.7679 | 74.6386 | -430.5654
2020-12-20 04:00 | -1704.62 | 4.2899 | 74.6545 | 74.6386 | -499.5748
2020-12-21 05:00 | -2021.61 | 5.007 | 74.5193 | 74.6386 | -592.4754
2020-12-22 06:00 | -1950.92 | 4.7855 | 74.4297 | 74.6386 | -571.7582
2020-12-23 07:00 | -1294.06 | 3.2423 | 74.3851 | 74.6386 | -379.2515
2020-12-24 08:00 | -708.777 | 1.9781 | 74.4677 | 74.6386 | -207.722
2020-12-25 09:00 | -808.624 | 2.3127 | 74.4943 | 74.6386 | -236.9843
2020-12-26 10:00 | -948.764 | 2.6196 | 74.4285 | 74.6386 | -278.0553
2020-12-27 11:00 | -177.401 | 0.77428 | 74.6899 | 74.6386 | -51.9911
2020-12-28 12:00 | 2023.07 | 1 | 74.2884 | 74.6386 | 592.9033
2020-12-29 13:00 | 2747.03 | 1 | 74.1124 | 74.6386 | 805.075
2020-12-30 14:00 | 2983.78 | 1 | 74.1353 | 74.6386 | 874.4596
2020-12-31 15:00 | 3032.16 | 1 | 88.2911 | 74.6386 | 888.6384
2021-01-01 16:00 | 3130.04 | 1 | 74.2344 | 74.6386 | 917.3242
2021-01-02 17:00 | 3306.51 | 1.0442 | 83.3217 | 74.6386 | 969.0424
2021-01-03 18:00 | 3087.93 | 1 | 74.3786 | 74.6386 | 904.9829
2021-01-04 19:00 | 2933.84 | 1 | 74.4757 | 74.6386 | 859.8236
2021-01-05 20:00 | 0 | 0 | 75.9001 | 74.6386 | 0
2021-01-06 21:00 | -221.649 | 1.0593 | 75.2004 | 74.6386 | -64.9589
2021-01-07 22:00 | -433.964 | 1.494 | 74.886 | 74.6386 | -127.1823
2021-01-08 23:00 | -770.766 | 2.2558 | 74.6837 | 74.6386 | -225.8892
2021-01-10 | -1940.31 | 4.9755 | 74.4807 | 74.6386 | -568.6487
2021-01-11 01:00 | -2323.03 | 5.6871 | 74.2723 | 74.6386 | -680.8129
2021-01-12 02:00 | -2593.32 | 6.2866 | 74.1495 | 74.6386 | -760.0271
2021-01-13 03:00 | -2757.32 | 6.5195 | 74.0282 | 74.6386 | -808.0907
2021-01-14 04:00 | -2707.28 | 6.5084 | 73.9538 | 74.6386 | -793.4254
2021-01-15 05:00 | -2631.01 | 6.3292 | 73.8817 | 74.6386 | -771.0729
2021-01-16 06:00 | -2323.83 | 5.6063 | 73.8356 | 74.6386 | -681.0473
2021-01-17 07:00 | -2132.61 | 5.2063 | 73.8175 | 74.6386 | -625.0063
2021-01-18 08:00 | -1586.65 | 3.9281 | 73.8216 | 74.6386 | -465.0012
2021-01-19 09:00 | -1531.65 | 3.8978 | 73.8703 | 74.6386 | -448.8823
2021-01-20 10:00 | -1553.64 | 3.9527 | 73.8734 | 74.6386 | -455.3269
2021-01-21 11:00 | -1233.21 | 3.1825 | 73.8726 | 74.6386 | -361.4182
2021-01-22 12:00 | -1064.6 | 2.8411 | 73.9078 | 74.6386 | -312.0035
2021-01-23 13:00 | -344.749 | 1.1563 | 74.0943 | 74.6386 | -101.036
2021-01-24 14:00 | 2711.39 | 1 | 83.2354 | 74.6386 | 794.63
2021-01-25 15:00 | 3128.71 | 1 | 85.2219 | 74.6386 | 916.9344
2021-01-26 16:00 | 3096.42 | 1 | 85.1837 | 74.6386 | 907.4711
2021-01-27 17:00 | 3096.85 | 1 | 73.8599 | 74.6386 | 907.5971
2021-01-28 18:00 | 2960.55 | 1 | 74.0126 | 74.6386 | 867.6516
2021-01-29 19:00 | -104.936 | 0.80171 | 75.1972 | 74.6386 | -30.7537
2021-01-30 20:00 | -665.175 | 2.0616 | 74.5492 | 74.6386 | -194.9435
2021-01-31 21:00 | -1618.83 | 4.2353 | 74.268 | 74.6386 | -474.4322
2021-02-01 22:00 | -2016.6 | 5.0236 | 74.0878 | 74.6386 | -591.0071
2021-02-02 23:00 | -2829.42 | 6.5195 | 73.8884 | 74.6386 | -829.2211
2021-02-04 | -3163.14 | 6.5195 | 73.6247 | 74.6386 | -927.0248
2021-02-05 01:00 | -3136.78 | 6.5195 | 73.5365 | 74.6386 | -919.2995
2021-02-06 02:00 | -3188.99 | 6.5195 | 73.4369 | 74.6386 | -934.6007
2021-02-07 03:00 | -3280.79 | 6.5195 | 73.3347 | 74.6386 | -961.5046
2021-02-08 04:00 | -3086.18 | 6.5195 | 73.3362 | 74.6386 | -904.4701
2021-02-09 05:00 | -2920.04 | 6.5195 | 73.3566 | 74.6386 | -855.7792
2021-02-10 06:00 | -2550.84 | 6.173 | 73.4108 | 74.6386 | -747.5774
2021-02-11 07:00 | -2466.72 | 5.9915 | 73.4222 | 74.6386 | -722.9243
2021-02-12 08:00 | -2421.73 | 5.8974 | 73.4232 | 74.6386 | -709.739
2021-02-13 09:00 | -3053.05 | 6.5195 | 73.2849 | 74.6386 | -894.7606
2021-02-14 10:00 | -2806.71 | 6.5195 | 73.3195 | 74.6386 | -822.5655
2021-02-15 11:00 | -2353.03 | 5.6952 | 73.3416 | 74.6386 | -689.605
2021-02-16 12:00 | 1638.41 | 1 | 73.5417 | 74.6386 | 480.1706
2021-02-17 13:00 | 3174.49 | 1 | 82.5489 | 74.6386 | 930.3512
2021-02-18 14:00 | 5215.38 | 1.6236 | 82.4874 | 74.6386 | 1528.477
2021-02-19 15:00 | 6186.51 | 2.0119 | 82.4633 | 74.6386 | 1813.0871
2021-02-20 16:00 | 6535.55 | 2.1303 | 82.723 | 74.6386 | 1915.3806
2021-02-21 17:00 | 5058.65 | 1.5921 | 83.2076 | 74.6386 | 1482.544
2021-02-22 18:00 | 3148.07 | 1.0207 | 83.0203 | 74.6386 | 922.6082
2021-02-23 19:00 | 3061.24 | 1 | 74.1619 | 74.6386 | 897.1609
2021-02-24 20:00 | 2964.18 | 1 | 74.193 | 74.6386 | 868.7154
2021-02-25 21:00 | -619.143 | 2.0218 | 74.9089 | 74.6386 | -181.4529
2021-02-26 22:00 | -1269.14 | 3.3981 | 74.4896 | 74.6386 | -371.9482
2021-02-27 23:00 | -2309.63 | 5.783 | 74.2534 | 74.6386 | -676.8857
2021-03-01 | -2696.25 | 6.5195 | 74.0599 | 74.6386 | -790.1929
2021-03-02 01:00 | -2938.96 | 6.5195 | 73.8195 | 74.6386 | -861.3242
2021-03-03 02:00 | -2993.88 | 6.5195 | 73.6501 | 74.6386 | -877.4196
2021-03-04 03:00 | -3265.99 | 6.5195 | 73.4526 | 74.6386 | -957.1672
2021-03-05 04:00 | -3179.78 | 6.5195 | 73.376 | 74.6386 | -931.9015
2021-03-06 05:00 | -3298.19 | 6.5195 | 73.2628 | 74.6386 | -966.6041
2021-03-07 06:00 | -2785.73 | 6.5195 | 73.388 | 74.6386 | -816.4169
2021-03-08 07:00 | -2397.14 | 5.7978 | 73.4014 | 74.6386 | -702.5324
2021-03-09 08:00 | -957.406 | 2.3872 | 73.426 | 74.6386 | -280.588
2021-03-10 09:00 | 1826.05 | 1 | 73.6061 | 74.6386 | 535.1624
2021-03-11 10:00 | 3197.48 | 1.0293 | 82.1216 | 74.6386 | 937.0889
2021-03-12 11:00 | 6435.73 | 2.0692 | 82.3817 | 74.6386 | 1886.1263
2021-03-13 12:00 | 7732.88 | 2.5163 | 82.689 | 74.6386 | 2266.2834
2021-03-14 13:00 | 6726.72 | 2.1276 | 83.2551 | 74.6386 | 1971.407
2021-03-15 14:00 | 7701.23 | 2.5472 | 83.0753 | 74.6386 | 2257.0077
2021-03-16 15:00 | 7219.22 | 2.3027 | 83.5319 | 74.6386 | 2115.7445
2021-03-17 16:00 | 7094.02 | 2.2637 | 83.6532 | 74.6386 | 2079.052
2021-03-18 17:00 | 6999.85 | 2.1993 | 83.8453 | 74.6386 | 2051.4535
2021-03-19 18:00 | 5850.8 | 1.7894 | 84.1212 | 74.6386 | 1714.7002
2021-03-20 19:00 | 4183.7 | 1.2998 | 84.0053 | 74.6386 | 1226.1214
2021-03-21 20:00 | 3144.19 | 1 | 85.1301 | 74.6386 | 921.4711
2021-03-22 21:00 | 2987.85 | 1 | 74.7355 | 74.6386 | 875.6524
2021-03-23 22:00 | 0 | 0 | 76.1226 | 74.6386 | 0
2021-03-24 23:00 | -852.984 | 2.4712 | 75.0304 | 74.6386 | -249.9849
2021-03-26 | -1160.67 | 3.0987 | 74.7307 | 74.6386 | -340.1588
2021-03-27 01:00 | -1347.96 | 3.4984 | 74.5646 | 74.6386 | -395.0481
2021-03-28 02:00 | -1468.33 | 3.7576 | 74.4303 | 74.6386 | -430.325
2021-03-29 03:00 | -1516.2 | 3.8557 | 74.3118 | 74.6386 | -444.3544
2021-03-30 04:00 | -1455.87 | 3.7071 | 74.2423 | 74.6386 | -426.6734
2021-03-31 05:00 | -1461.52 | 3.7344 | 74.1949 | 74.6386 | -428.3292
2021-04-01 06:00 | -990.526 | 2.6127 | 74.1804 | 74.6386 | -290.2945
2021-04-02 07:00 | -800.82 | 2.2508 | 74.2382 | 74.6386 | -234.6972
2021-04-03 08:00 | -506.281 | 1.5814 | 74.3273 | 74.6386 | -148.3763
2021-04-04 09:00 | -527.386 | 1.683 | 74.3481 | 74.6386 | -154.5616
2021-04-05 10:00 | 1497.8 | 1 | 74.3711 | 74.6386 | 438.9618
2021-04-06 11:00 | 2777.22 | 1 | 73.8977 | 74.6386 | 813.9228
2021-04-07 12:00 | 2932.16 | 1 | 83.8503 | 74.6386 | 859.3313
2021-04-08 13:00 | 3054.85 | 1 | 85.2057 | 74.6386 | 895.2882
2021-04-09 14:00 | 3791.78 | 1.2051 | 82.9986 | 74.6386 | 1111.261
2021-04-10 15:00 | 6571.64 | 2.1426 | 82.9257 | 74.6386 | 1925.9576
2021-04-11 16:00 | 7663.22 | 2.4913 | 83.2189 | 74.6386 | 2245.8681
2021-04-12 17:00 | 6128.88 | 1.9345 | 83.6776 | 74.6386 | 1796.1974
2021-04-13 18:00 | 6239.73 | 1.9354 | 83.8478 | 74.6386 | 1828.6843
2021-04-14 19:00 | 5391.81 | 1.5437 | 84.5614 | 74.6386 | 1580.1835
2021-04-15 20:00 | 3029.5 | 1.0292 | 83.2971 | 74.6386 | 887.8588
2021-04-16 21:00 | 2624.8 | 1 | 74.9158 | 74.6386 | 769.2529
2021-04-17 22:00 | -84.3191 | 0.75249 | 75.8151 | 74.6386 | -24.7115
2021-04-18 23:00 | -1219.26 | 3.3532 | 74.9838 | 74.6386 | -357.3298
2021-04-20 | -1956.88 | 4.9192 | 74.675 | 74.6386 | -573.5049
2021-04-21 01:00 | -2395.83 | 5.8537 | 74.4632 | 74.6386 | -702.1485
2021-04-22 02:00 | -2727.8 | 6.5195 | 74.2945 | 74.6386 | -799.4393
2021-04-23 03:00 | -3081.65 | 6.5195 | 74.0097 | 74.6386 | -903.1425
2021-04-24 04:00 | -3400.14 | 6.5195 | 73.7567 | 74.6386 | -996.4827
2021-04-25 05:00 | -3413.17 | 6.5195 | 73.6323 | 74.6386 | -1000.3014
2021-04-26 06:00 | -3573.93 | 6.5195 | 73.476 | 74.6386 | -1047.4155
2021-04-27 07:00 | -2751 | 6.5195 | 73.681 | 74.6386 | -806.2385
2021-04-28 08:00 | -1985.96 | 4.7869 | 73.6856 | 74.6386 | -582.0274
2021-04-29 09:00 | -2361.14 | 5.8289 | 73.7344 | 74.6386 | -691.9818
2021-04-30 10:00 | -1329.3 | 3.2662 | 73.6979 | 74.6386 | -389.5794
2021-05-01 11:00 | 0 | 0 | 74.7041 | 74.6386 | 0
2021-05-02 12:00 | -198.393 | 0.99207 | 74.3501 | 74.6386 | -58.1432
2021-05-03 13:00 | -190.326 | 0.93468 | 74.3775 | 74.6386 | -55.779
2021-05-04 14:00 | -118.837 | 0.77067 | 74.4987 | 74.6386 | -34.8277
2021-05-05 15:00 | 2859.54 | 1 | 73.4961 | 74.6386 | 838.0484
2021-05-06 16:00 | 0 | 0 | 75.0978 | 74.6386 | 0
2021-05-07 17:00 | 2787.88 | 1 | 73.6496 | 74.6386 | 817.047
2021-05-08 18:00 | 0 | 0 | 75.1434 | 74.6386 | 0
2021-05-09 19:00 | -336.602 | 1.3297 | 74.4491 | 74.6386 | -98.6483
2021-05-10 20:00 | -880.619 | 2.5406 | 74.1471 | 74.6386 | -258.084
2021-05-11 21:00 | -1473.44 | 3.8648 | 73.9748 | 74.6386 | -431.8226
2021-05-12 22:00 | -1959 | 4.9275 | 73.8679 | 74.6386 | -574.1262
2021-05-13 23:00 | -2350.73 | 5.7923 | 73.7354 | 74.6386 | -688.931
2021-05-15 | -3903.35 | 6.5195 | 73.202 | 74.6386 | -1143.959
2021-05-16 01:00 | -4031.92 | 6.5195 | 72.9885 | 74.6386 | -1181.6391
2021-05-17 02:00 | -4089.82 | 6.5195 | 72.8554 | 74.6386 | -1198.6079
2021-05-18 03:00 | -4109.58 | 6.5195 | 72.7554 | 74.6386 | -1204.399
2021-05-19 04:00 | -4113.91 | 6.5195 | 72.6889 | 74.6386 | -1205.668
2021-05-20 05:00 | -4165.89 | 6.5195 | 72.5937 | 74.6386 | -1220.9018
2021-05-21 06:00 | -4202.72 | 6.5195 | 72.5373 | 74.6386 | -1231.6956
2021-05-22 07:00 | -3479.64 | 6.5195 | 72.7568 | 74.6386 | -1019.7818
2021-05-23 08:00 | -2805.89 | 6.5195 | 73.0158 | 74.6386 | -822.3252
2021-05-24 09:00 | -3134.12 | 6.5195 | 72.9448 | 74.6386 | -918.5199
2021-05-25 10:00 | -2269.76 | 5.5161 | 73.0927 | 74.6386 | -665.201
2021-05-26 11:00 | -1617.33 | 4.006 | 73.1538 | 74.6386 | -473.9926
2021-05-27 12:00 | -902.871 | 2.4057 | 73.2989 | 74.6386 | -264.6054
2021-05-28 13:00 | -664.006 | 1.9593 | 73.4706 | 74.6386 | -194.6009
2021-05-29 14:00 | -147.038 | 0.76108 | 73.8738 | 74.6386 | -43.0926
2021-05-30 15:00 | 2852.72 | 1 | 73.021 | 74.6386 | 836.0497
2021-05-31 16:00 | 2950.07 | 1 | 73.243 | 74.6386 | 864.5802
2021-06-01 17:00 | 2946.27 | 1 | 73.4027 | 74.6386 | 863.4665
2021-06-02 18:00 | 0 | 0 | 74.9234 | 74.6386 | 0
2021-06-03 19:00 | -555.002 | 1.773 | 74.05 | 74.6386 | -162.655
2021-06-04 20:00 | -1066.38 | 2.9577 | 73.8524 | 74.6386 | -312.5251
2021-06-05 21:00 | -1326.77 | 3.4913 | 73.7261 | 74.6386 | -388.8379
2021-06-06 22:00 | -1619.43 | 4.1542 | 73.6297 | 74.6386 | -474.6081
2021-06-07 23:00 | -1785.14 | 4.5036 | 73.5367 | 74.6386 | -523.1729
2021-06-09 | -3010.42 | 6.5195 | 73.3467 | 74.6386 | -882.267
2021-06-10 01:00 | -3344.5 | 6.5195 | 73.1143 | 74.6386 | -980.1762
2021-06-11 02:00 | -3327.75 | 6.5195 | 73.0299 | 74.6386 | -975.2673
2021-06-12 03:00 | -3206.2 | 6.5195 | 73.0041 | 74.6386 | -939.6445
2021-06-13 04:00 | -3037.67 | 6.5195 | 73.0139 | 74.6386 | -890.2532
2021-06-14 05:00 | -2827.7 | 6.5195 | 73.0499 | 74.6386 | -828.7171
2021-06-15 06:00 | -2327.58 | 5.6494 | 73.1035 | 74.6386 | -682.1464
2021-06-16 07:00 | -2246.98 | 5.5195 | 73.1481 | 74.6386 | -658.5248
2021-06-17 08:00 | -1917.31 | 4.73 | 73.1698 | 74.6386 | -561.9081
2021-06-18 09:00 | -2086.09 | 5.2012 | 73.21 | 74.6386 | -611.3726
2021-06-19 10:00 | -1714.01 | 4.2629 | 73.2067 | 74.6386 | -502.3267
2021-06-20 11:00 | -424.839 | 1.2407 | 73.3655 | 74.6386 | -124.508
2021-06-21 12:00 | 2815.84 | 1 | 81.6133 | 74.6386 | 825.2412
2021-06-22 13:00 | 3446.3 | 1.0683 | 82.2243 | 74.6386 | 1010.0108
2021-06-23 14:00 | 6227.66 | 1.9501 | 82.3652 | 74.6386 | 1825.147
2021-06-24 15:00 | 5676.86 | 1.8079 | 82.575 | 74.6386 | 1663.7234
2021-06-25 16:00 | 7278.46 | 2.3796 | 82.5753 | 74.6386 | 2133.1061
2021-06-26 17:00 | 5517.24 | 1.798 | 82.8557 | 74.6386 | 1616.9434
2021-06-27 18:00 | 3199.17 | 1.0713 | 82.7152 | 74.6386 | 937.5842
2021-06-28 19:00 | 2932.32 | 1 | 74.1284 | 74.6386 | 859.3782
2021-06-29 20:00 | 0 | 0 | 75.4954 | 74.6386 | 0
2021-06-30 21:00 | -1043.42 | 2.8857 | 74.4277 | 74.6386 | -305.7962
2021-07-01 22:00 | -1578.24 | 4.0797 | 74.1574 | 74.6386 | -462.5365
2021-07-02 23:00 | -2567.62 | 6.3679 | 73.9727 | 74.6386 | -752.4951
2021-07-04 | -3093.57 | 6.5195 | 73.6367 | 74.6386 | -906.6359
2021-07-05 01:00 | -3574.51 | 6.5195 | 73.2972 | 74.6386 | -1047.5855
2021-07-06 02:00 | -3860.54 | 6.5195 | 73.0473 | 74.6386 | -1131.4126
2021-07-07 03:00 | -3996.24 | 6.5195 | 72.8721 | 74.6386 | -1171.1823
2021-07-08 04:00 | -3755.64 | 6.5195 | 72.8377 | 74.6386 | -1100.6694
2021-07-09 05:00 | -3415.99 | 6.5195 | 72.8907 | 74.6386 | -1001.1278
2021-07-10 06:00 | -3089.04 | 6.5195 | 72.9794 | 74.6386 | -905.3083
2021-07-11 07:00 | -2745.16 | 6.5195 | 73.0893 | 74.6386 | -804.527
2021-07-12 08:00 | -1927.09 | 4.6749 | 73.1238 | 74.6386 | -564.7743
2021-07-13 09:00 | -1160.78 | 2.9718 | 73.2432 | 74.6386 | -340.191
2021-07-14 10:00 | -223.424 | 0.86277 | 73.6456 | 74.6386 | -65.4791
2021-07-15 11:00 | 2489.55 | 1 | 81.2141 | 74.6386 | 729.6151
2021-07-16 12:00 | 4476.46 | 1.3992 | 82.216 | 74.6386 | 1311.9209
2021-07-17 13:00 | 3114.23 | 1 | 83.9217 | 74.6386 | 912.6907
2021-07-18 14:00 | 3967 | 1.1486 | 83.1958 | 74.6386 | 1162.6129
2021-07-19 15:00 | 5218.8 | 1.6197 | 82.7763 | 74.6386 | 1529.4793
2021-07-20 16:00 | 4875.12 | 1.6538 | 82.3311 | 74.6386 | 1428.7566
2021-07-21 17:00 | 4893.82 | 1.7075 | 82.2291 | 74.6386 | 1434.2371
2021-07-22 18:00 | 3227.01 | 1.1242 | 82.3042 | 74.6386 | 945.7433
2021-07-23 19:00 | 2925.85 | 1 | 74.0579 | 74.6386 | 857.482
2021-07-24 20:00 | 0 | 0 | 75.4593 | 74.6386 | 0
2021-07-25 21:00 | -1091.96 | 2.9169 | 74.3621 | 74.6386 | -320.0219
2021-07-26 22:00 | -1643.44 | 4.2337 | 74.1379 | 74.6386 | -481.6447
2021-07-27 23:00 | -2736.22 | 6.5195 | 73.9074 | 74.6386 | -801.9069
2021-07-29 | -3294.6 | 6.5195 | 73.5169 | 74.6386 | -965.5519
2021-07-30 01:00 | -3742.23 | 6.5195 | 73.1843 | 74.6386 | -1096.7394
2021-07-31 02:00 | -4072.46 | 6.5195 | 72.9318 | 74.6386 | -1193.5202
2021-08-01 03:00 | -4354.97 | 6.5195 | 72.7029 | 74.6386 | -1276.3157
2021-08-02 04:00 | -4582.23 | 6.5195 | 72.5 | 74.6386 | -1342.919
2021-08-03 05:00 | -4688.65 | 6.5195 | 72.3514 | 74.6386 | -1374.1077
2021-08-04 06:00 | -4268.85 | 6.5195 | 72.4144 | 74.6386 | -1251.0764
2021-08-05 07:00 | -4256.27 | 6.5195 | 72.3747 | 74.6386 | -1247.3896
2021-08-06 08:00 | -3121.97 | 6.5195 | 72.7514 | 74.6386 | -914.9591
2021-08-07 09:00 | -2414.15 | 5.8761 | 72.9631 | 74.6386 | -707.5175
2021-08-08 10:00 | -1151.02 | 2.8561 | 73.051 | 74.6386 | -337.3307
2021-08-09 11:00 | 0 | 1 | 74.1248 | 74.6386 | 0
2021-08-10 12:00 | 2907.93 | 1 | 72.8599 | 74.6386 | 852.2302
2021-08-11 13:00 | 2916.62 | 1 | 85.8388 | 74.6386 | 854.7769
2021-08-12 14:00 | 3136.44 | 1.0562 | 81.7629 | 74.6386 | 919.1998
2021-08-13 15:00 | 3182.45 | 1.064 | 81.9374 | 74.6386 | 932.684
2021-08-14 16:00 | 3821.99 | 1.2675 | 82.0956 | 74.6386 | 1120.1147
2021-08-15 17:00 | 2971.42 | 1 | 86.2886 | 74.6386 | 870.8372
2021-08-16 18:00 | 2735.47 | 1 | 73.7853 | 74.6386 | 801.6871
2021-08-17 19:00 | -641.641 | 2.0839 | 74.3943 | 74.6386 | -188.0464
2021-08-18 20:00 | -1150.45 | 3.1275 | 74.0413 | 74.6386 | -337.1636
2021-08-19 21:00 | -2269.59 | 5.7351 | 73.838 | 74.6386 | -665.1512
2021-08-20 22:00 | -2956.32 | 6.5195 | 73.5465 | 74.6386 | -866.4119
2021-08-21 23:00 | -4077.22 | 6.5195 | 72.9862 | 74.6386 | -1194.9152
2021-08-23 | -4426.18 | 6.5195 | 72.653 | 74.6386 | -1297.1853
2021-08-24 01:00 | -4727.94 | 6.5195 | 72.4041 | 74.6386 | -1385.6224
2021-08-25 02:00 | -4992.72 | 6.5195 | 72.1848 | 74.6386 | -1463.2218
2021-08-26 03:00 | -5282.25 | 6.5195 | 71.9677 | 74.6386 | -1548.0747
2021-08-27 04:00 | -5113.32 | 6.5195 | 71.9144 | 74.6386 | -1498.5662
2021-08-28 05:00 | -4984.31 | 6.5195 | 71.893 | 74.6386 | -1460.7571
2021-08-29 06:00 | -4660 | 6.5195 | 71.9566 | 74.6386 | -1365.7112
2021-08-30 07:00 | -4211.1 | 6.5195 | 72.1069 | 74.6386 | -1234.1516
2021-08-31 08:00 | -2504.56 | 6.143 | 72.6811 | 74.6386 | -734.0141
2021-09-01 09:00 | -1693.84 | 4.1551 | 72.8073 | 74.6386 | -496.4155
2021-09-02 10:00 | -236.815 | 0.80241 | 73.1946 | 74.6386 | -69.4036
2021-09-03 11:00 | 2914.95 | 1 | 72.6579 | 74.6386 | 854.2875
2021-09-04 12:00 | 3293.78 | 1.0484 | 81.845 | 74.6386 | 965.3116
2021-09-05 13:00 | 4368.78 | 1.3821 | 82.1072 | 74.6386 | 1280.363
2021-09-06 14:00 | 5031.3 | 1.5752 | 82.4012 | 74.6386 | 1474.5285
2021-09-07 15:00 | 3802.99 | 1.2408 | 82.3075 | 74.6386 | 1114.5463
2021-09-08 16:00 | 4749.86 | 1.5445 | 82.3879 | 74.6386 | 1392.0466
2021-09-09 17:00 | 3607.47 | 1.1885 | 82.4104 | 74.6386 | 1057.2451
2021-09-10 18:00 | 2965.39 | 1 | 73.8176 | 74.6386 | 869.07
2021-09-11 19:00 | 2689.25 | 1 | 73.9407 | 74.6386 | 788.1414
2021-09-12 20:00 | -482.803 | 1.7088 | 74.5651 | 74.6386 | -141.4956
2021-09-13 21:00 | -1491.55 | 3.9639 | 74.1376 | 74.6386 | -437.1302
2021-09-14 22:00 | -2155.44 | 5.3905 | 73.8875 | 74.6386 | -631.6971
2021-09-15 23:00 | -3277.77 | 6.5195 | 73.4918 | 74.6386 | -960.6196
2021-09-17 | -3536.99 | 6.5195 | 73.2095 | 74.6386 | -1036.5894
2021-09-18 01:00 | -4025.33 | 6.5195 | 72.871 | 74.6386 | -1179.7078
2021-09-19 02:00 | -4319.39 | 6.5195 | 72.6332 | 74.6386 | -1265.8882
2021-09-20 03:00 | -4498.7 | 6.5195 | 72.4571 | 74.6386 | -1318.4388
2021-09-21 04:00 | -4807.86 | 6.5195 | 72.2407 | 74.6386 | -1409.0447
2021-09-22 05:00 | -4385.5 | 6.5195 | 72.2993 | 74.6386 | -1285.2632
2021-09-23 06:00 | -3811.9 | 6.5195 | 72.4633 | 74.6386 | -1117.1576
2021-09-24 07:00 | -3132.46 | 6.5195 | 72.7083 | 74.6386 | -918.0334
2021-09-25 08:00 | -1799.28 | 4.3825 | 72.9127 | 74.6386 | -527.3169
2021-09-26 09:00 | -829.099 | 2.2029 | 73.1048 | 74.6386 | -242.9849
2021-09-27 10:00 | 2523.14 | 1 | 72.9103 | 74.6386 | 739.4593
2021-09-28 11:00 | 3700.59 | 1.1613 | 81.9986 | 74.6386 | 1084.5359
2021-09-29 12:00 | 5315.68 | 1.6962 | 82.1272 | 74.6386 | 1557.872
2021-09-30 13:00 | 6287.76 | 2.0195 | 82.3572 | 74.6386 | 1842.7606
2021-10-01 14:00 | 7119.38 | 2.2858 | 82.6184 | 74.6386 | 2086.4843
2021-10-02 15:00 | 7412.77 | 2.3505 | 82.9645 | 74.6386 | 2172.4684
2021-10-03 16:00 | 7808.81 | 2.5557 | 82.9174 | 74.6386 | 2288.5363
2021-10-04 17:00 | 5920.97 | 2.0211 | 82.8003 | 74.6386 | 1735.265
2021-10-05 18:00 | 4481.88 | 1.4614 | 83.125 | 74.6386 | 1313.5094
2021-10-06 19:00 | 2961.32 | 1 | 83.6241 | 74.6386 | 867.8772
2021-10-07 20:00 | 2977.18 | 1 | 74.2547 | 74.6386 | 872.5253
2021-10-08 21:00 | 0 | 0 | 75.6599 | 74.6386 | 0
2021-10-09 22:00 | -1092.26 | 2.9098 | 74.5171 | 74.6386 | -320.1098
2021-10-10 23:00 | -2096.84 | 5.3118 | 74.2524 | 74.6386 | -614.5231
2021-10-12 | -2816.4 | 6.5195 | 73.9702 | 74.6386 | -825.4054
2021-10-13 01:00 | -3490.37 | 6.5195 | 73.5446 | 74.6386 | -1022.9265
2021-10-14 02:00 | -3641.96 | 6.5195 | 73.2957 | 74.6386 | -1067.3531
2021-10-15 03:00 | -4148.85 | 6.5195 | 72.9782 | 74.6386 | -1215.9079
2021-10-16 04:00 | -4436.58 | 6.5195 | 72.7313 | 74.6386 | -1300.2332
2021-10-17 05:00 | -4335.87 | 6.5195 | 72.6456 | 74.6386 | -1270.7181
2021-10-18 06:00 | -4297.59 | 6.5195 | 72.579 | 74.6386 | -1259.4993
2021-10-19 07:00 | -2912.85 | 6.5195 | 73.0224 | 74.6386 | -853.6721
2021-10-20 08:00 | -1253.65 | 3.0501 | 73.1427 | 74.6386 | -367.4085
2021-10-21 09:00 | -460.314 | 1.4217 | 73.4867 | 74.6386 | -134.9047
2021-10-22 10:00 | 2800.44 | 1 | 84.7991 | 74.6386 | 820.7279
2021-10-23 11:00 | 4297.73 | 1.4373 | 81.7411 | 74.6386 | 1259.5403
2021-10-24 12:00 | 6149.08 | 2.0278 | 82.1356 | 74.6386 | 1802.1175
2021-10-25 13:00 | 6969.44 | 2.3376 | 82.3196 | 74.6386 | 2042.5412
2021-10-26 14:00 | 7246.27 | 2.4327 | 82.5686 | 74.6386 | 2123.6721
2021-10-27 15:00 | 7751.23 | 2.5239 | 82.9944 | 74.6386 | 2271.6613
2021-10-28 16:00 | 6008.33 | 1.9381 | 83.2423 | 74.6386 | 1760.8677
2021-10-29 17:00 | 7399.52 | 2.463 | 83.0294 | 74.6386 | 2168.5852
2021-10-30 18:00 | 4901.78 | 1.5858 | 83.3848 | 74.6386 | 1436.5699
2021-10-31 19:00 | 3722.75 | 1.2512 | 83.0464 | 74.6386 | 1091.0303
2021-11-01 20:00 | 3080.88 | 1 | 87.4414 | 74.6386 | 902.9168
2021-11-02 21:00 | 3161.06 | 1 | 74.2992 | 74.6386 | 926.4152
2021-11-03 22:00 | 3281.36 | 1 | 74.23 | 74.6386 | 961.6717
2021-11-04 23:00 | -74.6102 | 0.73394 | 75.5571 | 74.6386 | -21.8661
2021-11-06 | -1571.88 | 4.1975 | 74.6578 | 74.6386 | -460.6726
2021-11-07 01:00 | -1932.31 | 4.8112 | 74.3436 | 74.6386 | -566.3042
2021-11-08 02:00 | -2046.9 | 5.0447 | 74.1759 | 74.6386 | -599.8872
2021-11-09 03:00 | -2010.72 | 4.9463 | 74.0456 | 74.6386 | -589.2839
2021-11-10 04:00 | -2159.15 | 5.3165 | 73.9425 | 74.6386 | -632.7844
2021-11-11 05:00 | -2116.38 | 5.1886 | 73.8568 | 74.6386 | -620.2498
2021-11-12 06:00 | -2115.26 | 5.1986 | 73.8184 | 74.6386 | -619.9215
2021-11-13 07:00 | -1300.61 | 3.2452 | 73.7996 | 74.6386 | -381.1712
2021-11-14 08:00 | 0 | 0 | 74.7744 | 74.6386 | 0
2021-11-15 09:00 | -195.266 | 0.98241 | 74.3947 | 74.6386 | -57.2268
2021-11-16 10:00 | 2546.6 | 1 | 85.1022 | 74.6386 | 746.3348
2021-11-17 11:00 | 3234.82 | 1 | 87.1566 | 74.6386 | 948.0322
2021-11-18 12:00 | 3253.14 | 1 | 73.677 | 74.6386 | 953.4012
2021-11-19 13:00 | 3949.16 | 1.2501 | 82.8272 | 74.6386 | 1157.3845
2021-11-20 14:00 | 4440.1 | 1.4342 | 82.775 | 74.6386 | 1301.2649
2021-11-21 15:00 | 5684.41 | 1.9407 | 82.5039 | 74.6386 | 1665.9361
2021-11-22 16:00 | 4941.83 | 1.6013 | 83.0379 | 74.6386 | 1448.3074
2021-11-23 17:00 | 6651.23 | 2.2421 | 82.7996 | 74.6386 | 1949.2831
2021-11-24 18:00 | 5548.2 | 1.7367 | 83.5271 | 74.6386 | 1626.0169
2021-11-25 19:00 | 4476.83 | 1.4225 | 83.4729 | 74.6386 | 1312.0294
2021-11-26 20:00 | 3519.72 | 1.0747 | 83.7438 | 74.6386 | 1031.5281
2021-11-27 21:00 | 3190.04 | 1 | 84.0515 | 74.6386 | 934.9084
2021-11-28 22:00 | 3155.16 | 1 | 86.002 | 74.6386 | 924.6861
2021-11-29 23:00 | 3167.8 | 1 | 89.0144 | 74.6386 | 928.3905
2021-12-01 | 0 | 0 | 75.875 | 74.6386 | 0
2021-12-02 01:00 | -244.714 | 0.9072 | 75.0102 | 74.6386 | -71.7186
2021-12-03 02:00 | -381.034 | 1.3824 | 74.8623 | 74.6386 | -111.67
2021-12-04 03:00 | -483.589 | 1.589 | 74.7153 | 74.6386 | -141.7259
2021-12-05 04:00 | -311.073 | 1.1685 | 74.734 | 74.6386 | -91.1665
2021-12-06 05:00 | -116.577 | 0.74422 | 74.9298 | 74.6386 | -34.1653
2021-12-07 06:00 | 1859.51 | 1 | 74.3979 | 74.6386 | 544.9686
2021-12-08 07:00 | 2704.8 | 1 | 74.1291 | 74.6386 | 792.6986
2021-12-09 08:00 | 3089.73 | 1 | 74.0797 | 74.6386 | 905.5105
2021-12-10 09:00 | 3306.98 | 1 | 74.0781 | 74.6386 | 969.1802
2021-12-11 10:00 | 3267.85 | 1 | 74.1708 | 74.6386 | 957.7123
2021-12-12 11:00 | 3105.67 | 1 | 87.281 | 74.6386 | 910.182
2021-12-13 12:00 | 3487.86 | 1.0905 | 83.3803 | 74.6386 | 1022.1909
2021-12-14 13:00 | 3828.85 | 1.2129 | 83.3303 | 74.6386 | 1122.1252
2021-12-15 14:00 | 4404.89 | 1.4043 | 83.3371 | 74.6386 | 1290.9458
2021-12-16 15:00 | 4780.47 | 1.5382 | 83.3419 | 74.6386 | 1401.0175
2021-12-17 16:00 | 6201.82 | 2.0925 | 83.0812 | 74.6386 | 1817.574
2021-12-18 17:00 | 6293.85 | 2.0369 | 83.539 | 74.6386 | 1844.5454
2021-12-19 18:00 | 6150.07 | 1.9581 | 83.7654 | 74.6386 | 1802.4076
2021-12-20 19:00 | 4908.39 | 1.5984 | 83.6615 | 74.6386 | 1438.5071
2021-12-21 20:00 | 4145.57 | 1.3975 | 83.3823 | 74.6386 | 1214.9466
2021-12-22 21:00 | 2961.53 | 1 | 86.6634 | 74.6386 | 867.9388
2021-12-23 22:00 | 2994.85 | 1 | 74.7502 | 74.6386 | 877.7039
2021-12-24 23:00 | 0 | 0 | 76.1463 | 74.6386 | 0
2021-12-26 | -174.75 | 0.89598 | 75.439 | 74.6386 | -51.2142
2021-12-27 01:00 | -426.319 | 1.486 | 75.0723 | 74.6386 | -124.9418
2021-12-28 02:00 | -531.834 | 1.691 | 74.9086 | 74.6386 | -155.8652
2021-12-29 03:00 | -670.9 | 2.004 | 74.7786 | 74.6386 | -196.6214
2021-12-30 04:00 | -585.245 | 1.7803 | 74.6988 | 74.6386 | -171.5184
2021-12-31 05:00 | -640.543 | 1.9286 | 74.6459 | 74.6386 | -187.7246
2022-01-01 06:00 | -470.895 | 1.5183 | 74.6453 | 74.6386 | -138.0057
2022-01-02 07:00 | -597.71 | 1.8491 | 74.5805 | 74.6386 | -175.1715
2022-01-03 08:00 | -777.747 | 2.2501 | 74.4813 | 74.6386 | -227.9351
2022-01-04 09:00 | -1269.16 | 3.3856 | 74.3614 | 74.6386 | -371.9541
2022-01-05 10:00 | -1258.71 | 3.2754 | 74.2505 | 74.6386 | -368.8915
2022-01-06 11:00 | -963.12 | 2.5831 | 74.2265 | 74.6386 | -282.2626
2022-01-07 12:00 | -717.752 | 2.0561 | 74.2585 | 74.6386 | -210.3523
2022-01-08 13:00 | -629.642 | 1.8888 | 74.2807 | 74.6386 | -184.5299
2022-01-09 14:00 | -534.646 | 1.6774 | 74.292 | 74.6386 | -156.6893
2022-01-10 15:00 | -505.004 | 1.6239 | 74.2908 | 74.6386 | -148.0021
2022-01-11 16:00 | 2498.37 | 1 | 73.7956 | 74.6386 | 732.2
2022-01-12 17:00 | 3168.62 | 1 | 73.6665 | 74.6386 | 928.6309
2022-01-13 18:00 | 2962.92 | 1 | 73.9159 | 74.6386 | 868.3461
2022-01-14 19:00 | -315.898 | 1.3104 | 74.8366 | 74.6386 | -92.5806
2022-01-15 20:00 | -752.813 | 2.2331 | 74.4208 | 74.6386 | -220.6277
2022-01-16 21:00 | -1807.02 | 4.6745 | 74.1996 | 74.6386 | -529.5853
2022-01-17 22:00 | -2336.85 | 5.7617 | 74.0097 | 74.6386 | -684.8631
2022-01-18 23:00 | -3260.08 | 6.5195 | 73.6425 | 74.6386 | -955.4351
2022-01-20 | -3568.56 | 6.5195 | 73.3618 | 74.6386 | -1045.8417
2022-01-21 01:00 | -3896.23 | 6.5195 | 73.1329 | 74.6386 | -1141.8723
2022-01-22 02:00 | -4321.41 | 6.5195 | 72.8768 | 74.6386 | -1266.4803
2022-01-23 03:00 | -4398.78 | 6.5195 | 72.7454 | 74.6386 | -1289.1552
2022-01-24 04:00 | -4413.88 | 6.5195 | 72.6377 | 74.6386 | -1293.5805
2022-01-25 05:00 | -4265.11 | 6.5195 | 72.6063 | 74.6386 | -1249.9804
2022-01-26 06:00 | -3814.49 | 6.5195 | 72.6993 | 74.6386 | -1117.9167
2022-01-27 07:00 | -3680.84 | 6.5195 | 72.7296 | 74.6386 | -1078.7477
2022-01-28 08:00 | -2590.31 | 6.3118 | 73.0763 | 74.6386 | -759.1449
2022-01-29 09:00 | -2121.35 | 5.1608 | 73.1339 | 74.6386 | -621.7063
2022-01-30 10:00 | -1153.44 | 2.915 | 73.2285 | 74.6386 | -338.0399
2022-01-31 11:00 | 1765.39 | 1 | 73.4124 | 74.6386 | 517.3847
2022-02-01 12:00 | 2913.22 | 1 | 84.888 | 74.6386 | 853.7805
2022-02-02 13:00 | 2833.67 | 1 | 81.5639 | 74.6386 | 830.4667
2022-02-03 14:00 | 2836.97 | 1 | 83.8866 | 74.6386 | 831.4338
2022-02-04 15:00 | 2841.41 | 1 | 82.0489 | 74.6386 | 832.7351
2022-02-05 16:00 | 3288.14 | 1.148 | 81.9008 | 74.6386 | 963.6587
2022-02-06 17:00 | 2821.63 | 1 | 73.8404 | 74.6386 | 826.9381
2022-02-07 18:00 | 2785.63 | 1 | 73.8782 | 74.6386 | 816.3876
2022-02-08 19:00 | -469.016 | 1.6722 | 74.5931 | 74.6386 | -137.455
2022-02-09 20:00 | -1207.39 | 3.2891 | 74.1841 | 74.6386 | -353.8511
2022-02-10 21:00 | -2125.22 | 5.3674 | 73.962 | 74.6386 | -622.8405
2022-02-11 22:00 | -2378.63 | 5.8206 | 73.7838 | 74.6386 | -697.1076
2022-02-12 23:00 | -3047.66 | 6.5195 | 73.5184 | 74.6386 | -893.181
2022-02-14 | -3196.13 | 6.5195 | 73.309 | 74.6386 | -936.6932
2022-02-15 01:00 | -3042.3 | 6.5195 | 73.268 | 74.6386 | -891.6101
2022-02-16 02:00 | -2808.15 | 6.5195 | 73.2966 | 74.6386 | -822.9875
2022-02-17 03:00 | -2495.29 | 6.0425 | 73.3101 | 74.6386 | -731.2973
2022-02-18 04:00 | -2143.17 | 5.2262 | 73.3022 | 74.6386 | -628.1011
2022-02-19 05:00 | -1677.58 | 4.1671 | 73.3287 | 74.6386 | -491.6502
2022-02-20 06:00 | -1125.23 | 2.9227 | 73.3976 | 74.6386 | -329.7724
2022-02-21 07:00 | -879.837 | 2.4322 | 73.5183 | 74.6386 | -257.8548
2022-02-22 08:00 | -573.954 | 1.7391 | 73.6484 | 74.6386 | -168.2093
2022-02-23 09:00 | -762.658 | 2.2418 | 73.6853 | 74.6386 | -223.513
2022-02-24 10:00 | -465.482 | 1.4943 | 73.7769 | 74.6386 | -136.4193
2022-02-25 11:00 | -295.161 | 1.1474 | 73.9394 | 74.6386 | -86.5032
2022-02-26 12:00 | 57.3232 | 1 | 74.5518 | 74.6386 | 16.7998
2022-02-27 13:00 | 107.721 | 1 | 74.5683 | 74.6386 | 31.5699
2022-02-28 14:00 | 40.1003 | 1 | 74.6245 | 74.6386 | 11.7522
2022-03-01 15:00 | 155.771 | 1 | 74.5782 | 74.6386 | 45.652
2022-03-02 16:00 | 2101.61 | 1 | 73.6467 | 74.6386 | 615.9211
2022-03-03 17:00 | 2829.9 | 1 | 86.4507 | 74.6386 | 829.3618
2022-03-04 18:00 | 2993.07 | 1 | 85.9931 | 74.6386 | 877.1822
2022-03-05 19:00 | 2901.67 | 1 | 73.6395 | 74.6386 | 850.3955
2022-03-06 20:00 | 2968.71 | 1 | 73.6875 | 74.6386 | 870.043
2022-03-07 21:00 | -354.651 | 1.3972 | 74.6061 | 74.6386 | -103.9379
2022-03-08 22:00 | -442.646 | 1.4977 | 74.3177 | 74.6386 | -129.7267
2022-03-09 23:00 | -1137.89 | 3.1413 | 74.0609 | 74.6386 | -333.4826
2022-03-11 | -1198.36 | 3.1623 | 73.9352 | 74.6386 | -351.2046
2022-03-12 01:00 | -1138.52 | 3.02 | 73.8742 | 74.6386 | -333.6673
2022-03-13 02:00 | -1069.58 | 2.8681 | 73.8377 | 74.6386 | -313.463
2022-03-14 03:00 | -993.171 | 2.6978 | 73.8482 | 74.6386 | -291.0697
2022-03-15 04:00 | -764.013 | 2.1653 | 73.8735 | 74.6386 | -223.9101
2022-03-16 05:00 | -491.162 | 1.5582 | 73.9678 | 74.6386 | -143.9454
2022-03-17 06:00 | 0 | 1 | 74.7281 | 74.6386 | 0
2022-03-18 07:00 | 1446.42 | 1 | 74.0649 | 74.6386 | 423.9039
2022-03-19 08:00 | 1956.51 | 1 | 73.9379 | 74.6386 | 573.3965
2022-03-20 09:00 | 2748.36 | 1 | 73.6781 | 74.6386 | 805.4648
2022-03-21 10:00 | 3002.37 | 1 | 73.689 | 74.6386 | 879.9078
2022-03-22 11:00 | 3166.44 | 1 | 73.722 | 74.6386 | 927.992
2022-03-23 12:00 | 3159.13 | 1 | 87.9598 | 74.6386 | 925.8496
2022-03-24 13:00 | 3188.22 | 1 | 87.4725 | 74.6386 | 934.375
2022-03-25 14:00 | 3209.09 | 1 | 73.903 | 74.6386 | 940.4914
2022-03-26 15:00 | 3268.84 | 1 | 73.9193 | 74.6386 | 958.0024
2022-03-27 16:00 | 3641.39 | 1.1537 | 83.0111 | 74.6386 | 1067.1861
2022-03-28 17:00 | 4130.92 | 1.2905 | 83.1583 | 74.6386 | 1210.6531
2022-03-29 18:00 | 4426.24 | 1.3868 | 83.211 | 74.6386 | 1297.2029
2022-03-30 19:00 | 3267.27 | 1.0407 | 83.1602 | 74.6386 | 957.5423
2022-03-31 20:00 | 3127.39 | 1 | 84.5411 | 74.6386 | 916.5475
2022-04-01 21:00 | 3063.3 | 1 | 74.2094 | 74.6386 | 897.7646
2022-04-02 22:00 | 3074.7 | 1 | 74.2161 | 74.6386 | 901.1056
2022-04-03 23:00 | -357.236 | 1.4001 | 75.1097 | 74.6386 | -104.6955
2022-04-05 | -741.157 | 2.1932 | 74.6655 | 74.6386 | -217.2117
2022-04-06 01:00 | -853.552 | 2.4027 | 74.4698 | 74.6386 | -250.1514
2022-04-07 02:00 | -962.362 | 2.6464 | 74.3659 | 74.6386 | -282.0405
2022-04-08 03:00 | -1003.53 | 2.7275 | 74.2742 | 74.6386 | -294.1056
2022-04-09 04:00 | -997.405 | 2.709 | 74.1908 | 74.6386 | -292.3106
2022-04-10 05:00 | -1020.27 | 2.7659 | 74.1489 | 74.6386 | -299.0116
2022-04-11 06:00 | -1050.98 | 2.8358 | 74.1034 | 74.6386 | -308.0118
2022-04-12 07:00 | -181.616 | 0.76908 | 74.3824 | 74.6386 | -53.2264
2022-04-13 08:00 | 2011.05 | 1 | 73.9993 | 74.6386 | 589.3806
2022-04-14 09:00 | 2743.97 | 1 | 73.8108 | 74.6386 | 804.1782
2022-04-15 10:00 | 2850.48 | 1 | 73.8915 | 74.6386 | 835.3932
2022-04-16 11:00 | 3122.71 | 1 | 88.1761 | 74.6386 | 915.176
2022-04-17 12:00 | 4379.16 | 1.4118 | 82.7959 | 74.6386 | 1283.4051
2022-04-18 13:00 | 3190.94 | 1 | 83.2211 | 74.6386 | 935.1722
2022-04-19 14:00 | 3177.05 | 1 | 84.4898 | 74.6386 | 931.1014
2022-04-20 15:00 | 2908.63 | 1 | 83.3248 | 74.6386 | 852.4353
2022-04-21 16:00 | 3145.77 | 1 | 84.5388 | 74.6386 | 921.9342
2022-04-22 17:00 | 5349.83 | 1.7419 | 82.9636 | 74.6386 | 1567.8804
2022-04-23 18:00 | 4207.82 | 1.3561 | 83.2191 | 74.6386 | 1233.1903
2022-04-24 19:00 | 3320.88 | 1.0867 | 83.1431 | 74.6386 | 973.2539
2022-04-25 20:00 | 3012.77 | 1 | 84.508 | 74.6386 | 882.9557
2022-04-26 21:00 | 2991.47 | 1 | 86.5579 | 74.6386 | 876.7133
2022-04-27 22:00 | 3147.08 | 1 | 74.3237 | 74.6386 | 922.3181
2022-04-28 23:00 | 3096.84 | 1 | 74.3568 | 74.6386 | 907.5942
2022-04-30 | -425.323 | 1.5294 | 75.1984 | 74.6386 | -124.6499
2022-05-01 01:00 | -710.313 | 2.1077 | 74.8156 | 74.6386 | -208.1722
2022-05-02 02:00 | -1022.92 | 2.8056 | 74.6021 | 74.6386 | -299.7883
2022-05-03 03:00 | -1171.56 | 3.1066 | 74.4791 | 74.6386 | -343.3503
2022-05-04 04:00 | -1319.38 | 3.4373 | 74.3702 | 74.6386 | -386.6721
2022-05-05 05:00 | -1504.8 | 3.8569 | 74.2479 | 74.6386 | -441.0133
2022-05-06 06:00 | -1552.61 | 3.9403 | 74.1754 | 74.6386 | -455.0251
2022-05-07 07:00 | -627.873 | 1.7363 | 74.1972 | 74.6386 | -184.0114
2022-05-08 08:00 | 2318.29 | 1 | 73.9533 | 74.6386 | 679.4237
2022-05-09 09:00 | 2935.34 | 1 | 86.7448 | 74.6386 | 860.2632
2022-05-10 10:00 | 3716.31 | 1.2355 | 82.541 | 74.6386 | 1089.1429
2022-05-11 11:00 | 5444.4 | 1.7827 | 82.781 | 74.6386 | 1595.5961
2022-05-12 12:00 | 5572.31 | 1.8148 | 83.0579 | 74.6386 | 1633.0829
2022-05-13 13:00 | 5611.77 | 1.8088 | 83.3053 | 74.6386 | 1644.6474
2022-05-14 14:00 | 5595.93 | 1.8085 | 83.388 | 74.6386 | 1640.0052
2022-05-15 15:00 | 6125.64 | 1.9715 | 83.5091 | 74.6386 | 1795.2479
2022-05-16 16:00 | 6546.67 | 2.1508 | 83.4797 | 74.6386 | 1918.6396
2022-05-17 17:00 | 7673.29 | 2.5122 | 83.6122 | 74.6386 | 2248.8193
2022-05-18 18:00 | 5511.05 | 1.7265 | 84.1108 | 74.6386 | 1615.1293
2022-05-19 19:00 | 3981.78 | 1.2677 | 83.9568 | 74.6386 | 1166.9445
2022-05-20 20:00 | 3146.19 | 1 | 85.776 | 74.6386 | 922.0573
2022-05-21 21:00 | 3067.78 | 1 | 74.8206 | 74.6386 | 899.0776
2022-05-22 22:00 | 3072.22 | 1 | 74.7577 | 74.6386 | 900.3788
2022-05-23 23:00 | 3047.78 | 1 | 74.7079 | 74.6386 | 893.2161
2022-05-25 | -818.385 | 2.4817 | 75.3742 | 74.6386 | -239.845
2022-05-26 01:00 | -1179.83 | 3.1347 | 74.9679 | 74.6386 | -345.774
2022-05-27 02:00 | -1424.27 | 3.6689 | 74.7509 | 74.6386 | -417.4123
2022-05-28 03:00 | -1435.14 | 3.6576 | 74.6167 | 74.6386 | -420.598
2022-05-29 04:00 | -1394.54 | 3.5666 | 74.507 | 74.6386 | -408.6993
2022-05-30 05:00 | -1245.03 | 3.2229 | 74.4067 | 74.6386 | -364.8823
2022-05-31 06:00 | -854.623 | 2.3254 | 74.4126 | 74.6386 | -250.4653
2022-06-01 07:00 | -591.646 | 1.774 | 74.488 | 74.6386 | -173.3943
2022-06-02 08:00 | 2282.99 | 1 | 74.1715 | 74.6386 | 669.0783
2022-06-03 09:00 | 3017.47 | 1 | 83.602 | 74.6386 | 884.3332
2022-06-04 10:00 | 5198.99 | 1.7471 | 82.6594 | 74.6386 | 1523.6736
2022-06-05 11:00 | 6181.95 | 2.0241 | 83.0754 | 74.6386 | 1811.7507
2022-06-06 12:00 | 6886.39 | 2.2994 | 83.173 | 74.6386 | 2018.2017
2022-06-07 13:00 | 8211.25 | 2.7075 | 83.4817 | 74.6386 | 2406.4798
2022-06-08 14:00 | 7921.95 | 2.5866 | 83.7966 | 74.6386 | 2321.6944
2022-06-09 15:00 | 8477.64 | 2.745 | 84.0124 | 74.6386 | 2484.551
2022-06-10 16:00 | 8608.14 | 2.7704 | 84.2075 | 74.6386 | 2522.7968
2022-06-11 17:00 | 7231.01 | 2.2993 | 84.4237 | 74.6386 | 2119.1998
2022-06-12 18:00 | 6550.17 | 2.0856 | 84.4194 | 74.6386 | 1919.6653
2022-06-13 19:00 | 5185.92 | 1.6046 | 84.6187 | 74.6386 | 1519.8431
2022-06-14 20:00 | 4065.23 | 1.2811 | 84.3963 | 74.6386 | 1191.4013
2022-06-15 21:00 | 3110.34 | 1 | 75.2645 | 74.6386 | 911.5507
2022-06-16 22:00 | 3086.98 | 1 | 75.1295 | 74.6386 | 904.7045
2022-06-17 23:00 | -243.298 | 1.1063 | 76.0119 | 74.6386 | -71.3036
2022-06-19 | -621.717 | 1.9178 | 75.4679 | 74.6386 | -182.2073
2022-06-20 01:00 | -904.782 | 2.5258 | 75.1777 | 74.6386 | -265.1654
2022-06-21 02:00 | -917.56 | 2.513 | 75.0233 | 74.6386 | -268.9103
2022-06-22 03:00 | -1105.17 | 2.9592 | 74.8896 | 74.6386 | -323.8934
2022-06-23 04:00 | -1035.36 | 2.7635 | 74.7637 | 74.6386 | -303.4341
2022-06-24 05:00 | -832.194 | 2.3009 | 74.7333 | 74.6386 | -243.892
2022-06-25 06:00 | -340.976 | 1.1812 | 74.8688 | 74.6386 | -99.9302
2022-06-26 07:00 | -256.164 | 1.0684 | 74.9853 | 74.6386 | -75.0743
2022-06-27 08:00 | 2027.98 | 1 | 74.5553 | 74.6386 | 594.3423
2022-06-28 09:00 | 2914.39 | 1 | 74.2738 | 74.6386 | 854.1234
2022-06-29 10:00 | 2943.86 | 1 | 85.091 | 74.6386 | 862.7602
2022-06-30 11:00 | 5402.12 | 1.7669 | 83.1169 | 74.6386 | 1583.2051
2022-07-01 12:00 | 7555.16 | 2.5375 | 83.1648 | 74.6386 | 2214.1988
2022-07-02 13:00 | 7931.62 | 2.7811 | 83.1851 | 74.6386 | 2324.5284
2022-07-03 14:00 | 6557.81 | 2.0344 | 84.2676 | 74.6386 | 1921.9044
2022-07-04 15:00 | 8028.56 | 2.6063 | 83.9596 | 74.6386 | 2352.9387
2022-07-05 16:00 | 8301.45 | 2.6564 | 84.2424 | 74.6386 | 2432.9148
2022-07-06 17:00 | 7786.65 | 2.4613 | 84.481 | 74.6386 | 2282.0418
2022-07-07 18:00 | 7011.2 | 2.2489 | 84.4196 | 74.6386 | 2054.7799
2022-07-08 19:00 | 5701.28 | 1.7834 | 84.6099 | 74.6386 | 1670.8802
2022-07-09 20:00 | 4785.07 | 1.4846 | 84.6178 | 74.6386 | 1402.3656
2022-07-10 21:00 | 3141.26 | 1 | 86.6192 | 74.6386 | 920.6124
2022-07-11 22:00 | 3105.18 | 1 | 75.2405 | 74.6386 | 910.0384
2022-07-12 23:00 | 0 | 0 | 76.6511 | 74.6386 | 0
2022-07-14 | -150.109 | 0.83583 | 75.9352 | 74.6386 | -43.9926
2022-07-15 01:00 | -334.422 | 1.2704 | 75.55 | 74.6386 | -98.0094
2022-07-16 02:00 | -484.284 | 1.5888 | 75.3357 | 74.6386 | -141.9296
2022-07-17 03:00 | -557.431 | 1.7379 | 75.1916 | 74.6386 | -163.3669
2022-07-18 04:00 | -465.599 | 1.5133 | 75.1174 | 74.6386 | -136.4536
2022-07-19 05:00 | -245.632 | 1.0161 | 75.2224 | 74.6386 | -71.9876
2022-07-20 06:00 | 601.449 | 1 | 75.4738 | 74.6386 | 176.2673
2022-07-21 07:00 | 2798.71 | 1 | 74.4465 | 74.6386 | 820.2209
2022-07-22 08:00 | 2966.74 | 1 | 74.5291 | 74.6386 | 869.4657
2022-07-23 09:00 | 3111.6 | 1 | 74.5569 | 74.6386 | 911.9199
2022-07-24 10:00 | 3149 | 1 | 74.5955 | 74.6386 | 922.8808
2022-07-25 11:00 | 5097.37 | 1.6096 | 83.6793 | 74.6386 | 1493.8917
2022-07-26 12:00 | 7170.47 | 2.3838 | 83.4733 | 74.6386 | 2101.4573
2022-07-27 13:00 | 7184.18 | 2.3201 | 83.9321 | 74.6386 | 2105.4753
2022-07-28 14:00 | 5890.33 | 1.8237 | 84.3985 | 74.6386 | 1726.2853
2022-07-29 15:00 | 6826.46 | 2.2598 | 83.9088 | 74.6386 | 2000.6379
2022-07-30 16:00 | 7770.31 | 2.4706 | 84.3166 | 74.6386 | 2277.2531
2022-07-31 17:00 | 7225.92 | 2.2519 | 84.6232 | 74.6386 | 2117.7081
2022-08-01 18:00 | 6469.3 | 2.0134 | 84.6742 | 74.6386 | 1895.9647
2022-08-02 19:00 | 4995.8 | 1.5782 | 84.5388 | 74.6386 | 1464.1245
2022-08-03 20:00 | 3858.23 | 1.2017 | 84.5664 | 74.6386 | 1130.7356
2022-08-04 21:00 | 3242.65 | 1 | 75.2922 | 74.6386 | 950.3269
2022-08-05 22:00 | 3011.69 | 1 | 75.3002 | 74.6386 | 882.6392
2022-08-06 23:00 | -418.905 | 1.5235 | 76.0303 | 74.6386 | -122.7689
2022-08-08 | -828.929 | 2.3685 | 75.54 | 74.6386 | -242.9351
2022-08-09 01:00 | -1107.12 | 2.9628 | 75.2728 | 74.6386 | -324.4648
2022-08-10 02:00 | -1311.61 | 3.4025 | 75.1148 | 74.6386 | -384.3949
2022-08-11 03:00 | -1548.97 | 3.9335 | 74.9689 | 74.6386 | -453.9583
2022-08-12 04:00 | -1593.3 | 4.0027 | 74.8227 | 74.6386 | -466.9501
2022-08-13 05:00 | -1560.25 | 3.9224 | 74.7413 | 74.6386 | -457.2641
2022-08-14 06:00 | -1282.8 | 3.2741 | 74.6881 | 74.6386 | -375.9516
2022-08-15 07:00 | -1064.99 | 2.8112 | 74.6772 | 74.6386 | -312.1178
2022-08-16 08:00 | -934.406 | 2.5398 | 74.6713 | 74.6386 | -273.8474
2022-08-17 09:00 | -1360.95 | 3.5712 | 74.6104 | 74.6386 | -398.8551
2022-08-18 10:00 | -1116.17 | 2.9129 | 74.5354 | 74.6386 | -327.1171
2022-08-19 11:00 | -849.219 | 2.3339 | 74.549 | 74.6386 | -248.8815
2022-08-20 12:00 | -577.325 | 1.7376 | 74.6007 | 74.6386 | -169.1973
2022-08-21 13:00 | -537.991 | 1.6913 | 74.6172 | 74.6386 | -157.6696
2022-08-22 14:00 | -481.434 | 1.5619 | 74.6184 | 74.6386 | -141.0944
2022-08-23 15:00 | -380.459 | 1.3343 | 74.6497 | 74.6386 | -111.5015
2022-08-24 16:00 | 2030.36 | 1 | 74.3211 | 74.6386 | 595.0398
2022-08-25 17:00 | 3002.23 | 1 | 74.0044 | 74.6386 | 879.8668
2022-08-26 18:00 | 3098.15 | 1 | 74.1071 | 74.6386 | 907.9781
2022-08-27 19:00 | 223.921 | 1 | 75.5813 | 74.6386 | 65.6248
2022-08-28 20:00 | -134.343 | 0.84391 | 75.1635 | 74.6386 | -39.372
2022-08-29 21:00 | -922.725 | 2.662 | 74.6393 | 74.6386 | -270.424
2022-08-30 22:00 | -1234.71 | 3.2683 | 74.4609 | 74.6386 | -361.8578
2022-08-31 23:00 | -2091.36 | 5.2664 | 74.3212 | 74.6386 | -612.9171
2022-09-02 | -2398.1 | 5.851 | 74.1585 | 74.6386 | -702.8137
2022-09-03 01:00 | -2594.4 | 6.2817 | 74.066 | 74.6386 | -760.3436
2022-09-04 02:00 | -2738.18 | 6.5195 | 73.9808 | 74.6386 | -802.4813
2022-09-05 03:00 | -2653.6 | 6.3799 | 73.9331 | 74.6386 | -777.6934
2022-09-06 04:00 | -2568.63 | 6.1893 | 73.8811 | 74.6386 | -752.7911
2022-09-07 05:00 | -2353.72 | 5.6895 | 73.8406 | 74.6386 | -689.8072
2022-09-08 06:00 | -2022 | 4.9334 | 73.8185 | 74.6386 | -592.5897
2022-09-09 07:00 | -1773.57 | 4.3976 | 73.8359 | 74.6386 | -519.7821
2022-09-10 08:00 | -1980.29 | 4.9367 | 73.8481 | 74.6386 | -580.3657
2022-09-11 09:00 | -1325.4 | 3.3245 | 73.8351 | 74.6386 | -388.4364
2022-09-12 10:00 | 616.245 | 1 | 74.514 | 74.6386 | 180.6036
2022-09-13 11:00 | 3317.28 | 1.033 | 82.5832 | 74.6386 | 972.1988
2022-09-14 12:00 | 4679.18 | 1.5378 | 82.454 | 74.6386 | 1371.3323
2022-09-15 13:00 | 5881.14 | 1.9008 | 82.836 | 74.6386 | 1723.592
2022-09-16 14:00 | 6615.64 | 2.1605 | 83.0229 | 74.6386 | 1938.8527
2022-09-17 15:00 | 7130.86 | 2.3221 | 83.2874 | 74.6386 | 2089.8488
2022-09-18 16:00 | 7780.38 | 2.5258 | 83.5109 | 74.6386 | 2280.2043
2022-09-19 17:00 | 6370.64 | 2.0606 | 83.7219 | 74.6386 | 1867.0503
2022-09-20 18:00 | 4530.43 | 1.4309 | 83.9273 | 74.6386 | 1327.738
2022-09-21 19:00 | 3083.63 | 1 | 85.6761 | 74.6386 | 903.7227
2022-09-22 20:00 | 3132.91 | 1 | 74.7273 | 74.6386 | 918.1653
2022-09-23 21:00 | 0 | 0 | 76.2101 | 74.6386 | 0
2022-09-24 22:00 | -898.941 | 2.593 | 75.1253 | 74.6386 | -263.4536
2022-09-25 23:00 | -1922.92 | 4.8914 | 74.7943 | 74.6386 | -563.5522
2022-09-27 | -2633.74 | 6.4189 | 74.5598 | 74.6386 | -771.873
2022-09-28 01:00 | -2987.05 | 6.5195 | 74.26 | 74.6386 | -875.4179
2022-09-29 02:00 | -3286.67 | 6.5195 | 73.9754 | 74.6386 | -963.2279
2022-09-30 03:00 | -3530.39 | 6.5195 | 73.7498 | 74.6386 | -1034.6552
2022-10-01 04:00 | -3738.91 | 6.5195 | 73.5415 | 74.6386 | -1095.7664
2022-10-02 05:00 | -4162.41 | 6.5195 | 73.2736 | 74.6386 | -1219.882
2022-10-03 06:00 | -4212.17 | 6.5195 | 73.139 | 74.6386 | -1234.4652
2022-10-04 07:00 | -2961.21 | 6.5195 | 73.5029 | 74.6386 | -867.845
2022-10-05 08:00 | -1276.31 | 3.089 | 73.615 | 74.6386 | -374.0495
2022-10-06 09:00 | -457.311 | 1.4047 | 73.9478 | 74.6386 | -134.0246
2022-10-07 10:00 | 2754.43 | 1 | 73.502 | 74.6386 | 807.2437
2022-10-08 11:00 | 3875.66 | 1.2482 | 82.4892 | 74.6386 | 1135.8438
2022-10-09 12:00 | 5602.3 | 1.8727 | 82.4723 | 74.6386 | 1641.8721
2022-10-10 13:00 | 6322.21 | 2.1744 | 82.5538 | 74.6386 | 1852.8568
2022-10-11 14:00 | 7012.56 | 2.3802 | 82.8836 | 74.6386 | 2055.1785
2022-10-12 15:00 | 7399.55 | 2.4981 | 83.1442 | 74.6386 | 2168.594
2022-10-13 16:00 | 6014.87 | 2.0857 | 83.131 | 74.6386 | 1762.7844
2022-10-14 17:00 | 6629.26 | 2.3129 | 83.1222 | 74.6386 | 1942.8443
2022-10-15 18:00 | 4203.44 | 1.4902 | 83.1162 | 74.6386 | 1231.9067
2022-10-16 19:00 | 2816.49 | 1 | 84.076 | 74.6386 | 825.4317
2022-10-17 20:00 | 2805.46 | 1 | 74.8615 | 74.6386 | 822.1992
2022-10-18 21:00 | 399.347 | 1 | 75.9759 | 74.6386 | 117.0371
2022-10-19 22:00 | -288.011 | 1.2226 | 75.4059 | 74.6386 | -84.4077
2022-10-20 23:00 | -888.251 | 2.5446 | 74.9504 | 74.6386 | -260.3207
2022-10-22 | -2361.85 | 5.9455 | 74.6951 | 74.6386 | -692.1899
2022-10-23 01:00 | -2798.4 | 6.5195 | 74.4128 | 74.6386 | -820.1301
2022-10-24 02:00 | -3054.49 | 6.5195 | 74.135 | 74.6386 | -895.1827
2022-10-25 03:00 | -3282.76 | 6.5195 | 73.9186 | 74.6386 | -962.082
2022-10-26 04:00 | -3362.27 | 6.5195 | 73.7734 | 74.6386 | -985.3841
2022-10-27 05:00 | -3434.35 | 6.5195 | 73.6414 | 74.6386 | -1006.5086
2022-10-28 06:00 | -3626.2 | 6.5195 | 73.5002 | 74.6386 | -1062.7343
2022-10-29 07:00 | -2694.84 | 6.5143 | 73.7635 | 74.6386 | -789.7796
2022-10-30 08:00 | -910.921 | 2.2094 | 73.7669 | 74.6386 | -266.9646
2022-10-31 09:00 | 768.064 | 1 | 74.4985 | 74.6386 | 225.0973
2022-11-01 10:00 | 2639.91 | 1 | 81.617 | 74.6386 | 773.6812
2022-11-02 11:00 | 5134.78 | 1.704 | 82.389 | 74.6386 | 1504.8555
2022-11-03 12:00 | 6304.17 | 2.1769 | 82.4287 | 74.6386 | 1847.5698
2022-11-04 13:00 | 6940.7 | 2.3955 | 82.7124 | 74.6386 | 2034.1184
2022-11-05 14:00 | 7242.54 | 2.4649 | 83.0292 | 74.6386 | 2122.5789
2022-11-06 15:00 | 6777.1 | 2.3264 | 83.1481 | 74.6386 | 1986.1719
2022-11-07 16:00 | 6226.57 | 2.1567 | 83.1876 | 74.6386 | 1824.8275
2022-11-08 17:00 | 7186.88 | 2.4357 | 83.3744 | 74.6386 | 2106.2666
2022-11-09 18:00 | 4879.36 | 1.6219 | 83.6467 | 74.6386 | 1429.9993
2022-11-10 19:00 | 3498.85 | 1.1504 | 83.6592 | 74.6386 | 1025.4117
2022-11-11 20:00 | 3055.16 | 1 | 74.8555 | 74.6386 | 895.379
2022-11-12 21:00 | 3105.15 | 1 | 74.7659 | 74.6386 | 910.0296
2022-11-13 22:00 | 1264.91 | 1 | 75.6304 | 74.6386 | 370.7085
2022-11-14 23:00 | -109.819 | 0.81064 | 75.7412 | 74.6386 | -32.1848
2022-11-16 | -1496.84 | 4.0023 | 74.9796 | 74.6386 | -438.6805
2022-11-17 01:00 | -2113.54 | 5.2388 | 74.7026 | 74.6386 | -619.4174
2022-11-18 02:00 | -2454.53 | 5.9655 | 74.5048 | 74.6386 | -719.3517
2022-11-19 03:00 | -2761.83 | 6.5195 | 74.3211 | 74.6386 | -809.4125
2022-11-20 04:00 | -2829.6 | 6.5195 | 74.1682 | 74.6386 | -829.2739
2022-11-21 05:00 | -2761.26 | 6.5195 | 74.0882 | 74.6386 | -809.2454
2022-11-22 06:00 | -2319.8 | 5.5687 | 74.0455 | 74.6386 | -679.8663
2022-11-23 07:00 | -2056.52 | 5.0134 | 74.0451 | 74.6386 | -602.7065
2022-11-24 08:00 | -1002.65 | 2.5416 | 74.0684 | 74.6386 | -293.8477
2022-11-25 09:00 | 0 | 1 | 75.0504 | 74.6386 | 0
2022-11-26 10:00 | 2983.53 | 1 | 73.6946 | 74.6386 | 874.3863
2022-11-27 11:00 | 3811.6 | 1.2675 | 82.5192 | 74.6386 | 1117.0697
2022-11-28 12:00 | 5518.54 | 1.8258 | 82.7455 | 74.6386 | 1617.3244
2022-11-29 13:00 | 6022.04 | 2.0161 | 82.9068 | 74.6386 | 1764.8857
2022-11-30 14:00 | 5468.52 | 1.7945 | 83.2506 | 74.6386 | 1602.665
2022-12-01 15:00 | 5561.91 | 1.8112 | 83.4058 | 74.6386 | 1630.0349
2022-12-02 16:00 | 5995.89 | 1.9405 | 83.5303 | 74.6386 | 1757.2219
2022-12-03 17:00 | 4869.38 | 1.5773 | 83.6282 | 74.6386 | 1427.0744
2022-12-04 18:00 | 4034.56 | 1.295 | 83.6869 | 74.6386 | 1182.4128
2022-12-05 19:00 | 3080.8 | 1 | 85.9964 | 74.6386 | 902.8934
2022-12-06 20:00 | 3096.67 | 1 | 74.7093 | 74.6386 | 907.5444
2022-12-07 21:00 | 0 | 0 | 76.185 | 74.6386 | 0
2022-12-08 22:00 | -589.234 | 1.7365 | 75.1242 | 74.6386 | -172.6874
2022-12-09 23:00 | -1453.47 | 3.8415 | 74.8442 | 74.6386 | -425.97
2022-12-11 | -1755.08 | 4.4028 | 74.6292 | 74.6386 | -514.3632
2022-12-12 01:00 | -1954.85 | 4.841 | 74.4776 | 74.6386 | -572.91
2022-12-13 02:00 | -2073.32 | 5.0957 | 74.3469 | 74.6386 | -607.6301
2022-12-14 03:00 | -2128.28 | 5.2114 | 74.2628 | 74.6386 | -623.7373
2022-12-15 04:00 | -1901.75 | 4.664 | 74.1922 | 74.6386 | -557.3479
2022-12-16 05:00 | -1678.42 | 4.1757 | 74.1727 | 74.6386 | -491.8963
2022-12-17 06:00 | -1248.89 | 3.1911 | 74.1831 | 74.6386 | -366.0135
2022-12-18 07:00 | -942.954 | 2.5415 | 74.2436 | 74.6386 | -276.3525
2022-12-19 08:00 | 2138.19 | 1 | 74.1031 | 74.6386 | 626.6416
2022-12-20 09:00 | 2856.45 | 1 | 86.379 | 74.6386 | 837.1429
2022-12-21 10:00 | 4807.2 | 1.4906 | 83.1821 | 74.6386 | 1408.8512
2022-12-22 11:00 | 6189.18 | 2.0404 | 82.97 | 74.6386 | 1813.8696
2022-12-23 12:00 | 7925.93 | 2.5435 | 83.4212 | 74.6386 | 2322.8608
2022-12-24 13:00 | 8436.96 | 2.7397 | 83.6339 | 74.6386 | 2472.6289
2022-12-25 14:00 | 9319.09 | 3.0505 | 83.7952 | 74.6386 | 2731.1557
2022-12-26 15:00 | 9222.53 | 2.9319 | 84.2382 | 74.6386 | 2702.8567
2022-12-27 16:00 | 9787.01 | 3.1901 | 84.2103 | 74.6386 | 2868.2895
2022-12-28 17:00 | 8416.4 | 2.659 | 84.6114 | 74.6386 | 2466.6034
2022-12-29 18:00 | 7304.53 | 2.2526 | 84.8282 | 74.6386 | 2140.7464
2022-12-30 19:00 | 5883.12 | 1.7756 | 84.9758 | 74.6386 | 1724.1723
2022-12-31 20:00 | 4887.23 | 1.498 | 84.7601 | 74.6386 | 1432.3057
2023-01-01 21:00 | 3254.88 | 1 | 87.0403 | 74.6386 | 953.9112
2023-01-02 22:00 | 3179.27 | 1 | 75.2344 | 74.6386 | 931.7521
2023-01-03 23:00 | 0 | 0 | 76.6769 | 74.6386 | 0
2023-01-05 | -292.587 | 1.103 | 75.7527 | 74.6386 | -85.7488
2023-01-06 01:00 | -407.348 | 1.4196 | 75.5026 | 74.6386 | -119.3819
2023-01-07 02:00 | -446.049 | 1.4886 | 75.3432 | 74.6386 | -130.7241
2023-01-08 03:00 | -473.037 | 1.548 | 75.2285 | 74.6386 | -138.6335
2023-01-09 04:00 | -300.782 | 1.142 | 75.2261 | 74.6386 | -88.1505
2023-01-10 05:00 | -184.145 | 0.90053 | 75.3264 | 74.6386 | -53.9676
2023-01-11 06:00 | 1960.52 | 1 | 74.8379 | 74.6386 | 574.5717
2023-01-12 07:00 | 2899.02 | 1 | 74.5215 | 74.6386 | 849.6189
2023-01-13 08:00 | 3194.25 | 1 | 88.4592 | 74.6386 | 936.1423
2023-01-14 09:00 | 3520.48 | 1.0671 | 83.9405 | 74.6386 | 1031.7508
2023-01-15 10:00 | 4023.76 | 1.3129 | 83.4623 | 74.6386 | 1179.2476
2023-01-16 11:00 | 6276.23 | 2.1772 | 83.1354 | 74.6386 | 1839.3814
2023-01-17 12:00 | 7338.66 | 2.5112 | 83.4465 | 74.6386 | 2150.7489
2023-01-18 13:00 | 5684.68 | 1.8432 | 84.0323 | 74.6386 | 1666.0153
2023-01-19 14:00 | 4242.84 | 1.2208 | 84.9529 | 74.6386 | 1243.4537
2023-01-20 15:00 | 3465.98 | 1.0715 | 84.2955 | 74.6386 | 1015.7785
2023-01-21 16:00 | 4579.44 | 1.479 | 83.8901 | 74.6386 | 1342.1014
2023-01-22 17:00 | 4562.27 | 1.5004 | 83.7937 | 74.6386 | 1337.0694
2023-01-23 18:00 | 4492.54 | 1.4794 | 83.7776 | 74.6386 | 1316.6335
2023-01-24 19:00 | 2978.09 | 1 | 84.1978 | 74.6386 | 872.792
2023-01-25 20:00 | 2831.52 | 1 | 75.1116 | 74.6386 | 829.8366
2023-01-26 21:00 | 0 | 0 | 76.4364 | 74.6386 | 0
2023-01-27 22:00 | -336.142 | 1.254 | 75.5598 | 74.6386 | -98.5135
2023-01-28 23:00 | -1262.56 | 3.4143 | 75.1441 | 74.6386 | -370.0198
2023-01-30 | -1684.7 | 4.2569 | 74.8994 | 74.6386 | -493.7368
2023-01-31 01:00 | -2053.12 | 5.0729 | 74.7293 | 74.6386 | -601.7101
2023-02-01 02:00 | -2341.64 | 5.7041 | 74.5814 | 74.6386 | -686.2669
2023-02-02 03:00 | -2444.71 | 5.906 | 74.4781 | 74.6386 | -716.4738
2023-02-03 04:00 | -2476.37 | 5.9716 | 74.3857 | 74.6386 | -725.7524
2023-02-04 05:00 | -2457 | 5.9247 | 74.3125 | 74.6386 | -720.0756
2023-02-05 06:00 | -2164.64 | 5.2322 | 74.2442 | 74.6386 | -634.3934
2023-02-06 07:00 | -1609.78 | 3.9638 | 74.2227 | 74.6386 | -471.7799
2023-02-07 08:00 | -274.088 | 0.89614 | 74.4507 | 74.6386 | -80.3273
2023-02-08 09:00 | 2611.67 | 1 | 74.0005 | 74.6386 | 765.4049
2023-02-09 10:00 | 2916.28 | 1 | 84.4889 | 74.6386 | 854.6773
2023-02-10 11:00 | 3713.02 | 1.3069 | 82.3786 | 74.6386 | 1088.1787
2023-02-11 12:00 | 3790.37 | 1.326 | 82.5565 | 74.6386 | 1110.8478
2023-02-12 13:00 | 3849.45 | 1.3568 | 82.6148 | 74.6386 | 1128.1624
2023-02-13 14:00 | 3765.51 | 1.3223 | 82.7234 | 74.6386 | 1103.562
2023-02-14 15:00 | 3485.72 | 1.2484 | 82.6329 | 74.6386 | 1021.5637
2023-02-15 16:00 | 3266.48 | 1.1688 | 82.6516 | 74.6386 | 957.3108
2023-02-16 17:00 | 2732.6 | 1 | 74.7146 | 74.6386 | 800.846
2023-02-17 18:00 | 2540.45 | 1 | 74.7794 | 74.6386 | 744.5324
2023-02-18 19:00 | -631.356 | 2.0445 | 75.2553 | 74.6386 | -185.0322
2023-02-19 20:00 | -1225.36 | 3.2796 | 74.8545 | 74.6386 | -359.1176
2023-02-20 21:00 | -2586.12 | 6.4312 | 74.5959 | 74.6386 | -757.917
2023-02-21 22:00 | -3559.07 | 6.5195 | 74.0432 | 74.6386 | -1043.0605
2023-02-22 23:00 | -4764.33 | 6.5195 | 73.3856 | 74.6386 | -1396.2873
2023-02-24 | -5236.61 | 6.5195 | 72.9648 | 74.6386 | -1534.6989
2023-02-25 01:00 | -5661.16 | 6.5195 | 72.6242 | 74.6386 | -1659.1222
2023-02-26 02:00 | -6121.06 | 6.5195 | 72.2859 | 74.6386 | -1793.9056
2023-02-27 03:00 | -6402.42 | 6.5195 | 72.0198 | 74.6386 | -1876.3641
2023-02-28 04:00 | -6499.8 | 6.5195 | 71.8354 | 74.6386 | -1904.9033
2023-03-01 05:00 | -6575.07 | 6.5195 | 71.6878 | 74.6386 | -1926.9628
2023-03-02 06:00 | -6338.49 | 6.5195 | 71.6588 | 74.6386 | -1857.628
2023-03-03 07:00 | -6244.36 | 6.5195 | 71.6221 | 74.6386 | -1830.0413
2023-03-04 08:00 | -5090.54 | 6.5195 | 71.9758 | 74.6386 | -1491.89
2023-03-05 09:00 | -4397.05 | 6.5195 | 72.2443 | 74.6386 | -1288.6481
2023-03-06 10:00 | -2654.38 | 6.4995 | 72.9088 | 74.6386 | -777.922
2023-03-07 11:00 | -1525.98 | 3.7099 | 73.0248 | 74.6386 | -447.2206
2023-03-08 12:00 | -376.915 | 1.1711 | 73.3736 | 74.6386 | -110.4629
2023-03-09 13:00 | 2655.61 | 1 | 73.0144 | 74.6386 | 778.2825
2023-03-10 14:00 | 2828.18 | 1 | 73.254 | 74.6386 | 828.8577
2023-03-11 15:00 | 2821.18 | 1 | 73.4705 | 74.6386 | 826.8062
2023-03-12 16:00 | 2804.03 | 1 | 73.6039 | 74.6386 | 821.7801
2023-03-13 17:00 | 2691.11 | 1 | 73.7677 | 74.6386 | 788.6865
2023-03-14 18:00 | -470.223 | 1.6702 | 74.4853 | 74.6386 | -137.8088
2023-03-15 19:00 | -1359.3 | 3.6536 | 74.097 | 74.6386 | -398.3715
2023-03-16 20:00 | -2163.36 | 5.4344 | 73.8891 | 74.6386 | -634.0182
2023-03-17 21:00 | -3446.87 | 6.5195 | 73.468 | 74.6386 | -1010.1779
2023-03-18 22:00 | -3993.91 | 6.5195 | 73.0956 | 74.6386 | -1170.4995
2023-03-19 23:00 | -5018.22 | 6.5195 | 72.5647 | 74.6386 | -1470.6951
2023-03-21 | -5777.8 | 6.5195 | 72.1293 | 74.6386 | -1693.306
2023-03-22 01:00 | -6278.63 | 6.5195 | 71.7672 | 74.6386 | -1840.0848
2023-03-23 02:00 | -6610.15 | 6.5195 | 71.4834 | 74.6386 | -1937.2437
2023-03-24 03:00 | -6792.67 | 6.5195 | 71.2763 | 74.6386 | -1990.7351
2023-03-25 04:00 | -6967.27 | 6.5195 | 71.0855 | 74.6386 | -2041.9053
2023-03-26 05:00 | -6854.17 | 6.5195 | 71.0117 | 74.6386 | -2008.7589
2023-03-27 06:00 | -6887.24 | 6.5195 | 70.9302 | 74.6386 | -2018.4508
2023-03-28 07:00 | -5235.83 | 6.5195 | 71.4694 | 74.6386 | -1534.4703
2023-03-29 08:00 | -3112.59 | 6.5195 | 72.306 | 74.6386 | -912.2101
2023-03-30 09:00 | -2144.09 | 5.237 | 72.644 | 74.6386 | -628.3708
2023-03-31 10:00 | -600.194 | 1.5883 | 72.8674 | 74.6386 | -175.8995
2023-04-01 11:00 | 2844.06 | 1 | 72.5847 | 74.6386 | 833.5117
2023-04-02 12:00 | 3130.15 | 1.0721 | 81.2669 | 74.6386 | 917.3564
2023-04-03 13:00 | 4034.19 | 1.4027 | 81.3945 | 74.6386 | 1182.3044
2023-04-04 14:00 | 4572.66 | 1.6007 | 81.5584 | 74.6386 | 1340.1144
2023-04-05 15:00 | 4190.36 | 1.4692 | 81.7534 | 74.6386 | 1228.0733
2023-04-06 16:00 | 3816.72 | 1.3426 | 81.8545 | 74.6386 | 1118.5702
2023-04-07 17:00 | 4985.94 | 1.7363 | 81.9773 | 74.6386 | 1461.2348
2023-04-08 18:00 | 2800.39 | 1 | 82.3951 | 74.6386 | 820.7133
2023-04-09 19:00 | 2784.77 | 1 | 73.9703 | 74.6386 | 816.1355
2023-04-10 20:00 | 2351.1 | 1 | 74.1741 | 74.6386 | 689.0394
2023-04-11 21:00 | -77.9669 | 0.74539 | 75.0711 | 74.6386 | -22.8498
2023-04-12 22:00 | -429.824 | 1.5143 | 74.4845 | 74.6386 | -125.969
2023-04-13 23:00 | -827.193 | 2.3991 | 74.2082 | 74.6386 | -242.4263
2023-04-15 | -2340.79 | 5.9512 | 74.0188 | 74.6386 | -686.0178
2023-04-16 01:00 | -2958.73 | 6.5195 | 73.7017 | 74.6386 | -867.1182
2023-04-17 02:00 | -3377.77 | 6.5195 | 73.388 | 74.6386 | -989.9267
2023-04-18 03:00 | -3550.63 | 6.5195 | 73.2147 | 74.6386 | -1040.5869
2023-04-19 04:00 | -3859.95 | 6.5195 | 73.0112 | 74.6386 | -1131.2397
2023-04-20 05:00 | -4024.73 | 6.5195 | 72.8475 | 74.6386 | -1179.5319
2023-04-21 06:00 | -3896.74 | 6.5195 | 72.8219 | 74.6386 | -1142.0218
2023-04-22 07:00 | -2718.43 | 6.5195 | 73.2001 | 74.6386 | -796.6932
2023-04-23 08:00 | -926.776 | 2.2595 | 73.2527 | 74.6386 | -271.6112
2023-04-24 09:00 | -217.932 | 0.90552 | 73.801 | 74.6386 | -63.8696
2023-04-25 10:00 | 2544.55 | 1 | 73.2619 | 74.6386 | 745.734
2023-04-26 11:00 | 2998 | 1 | 82.4466 | 74.6386 | 878.6271
2023-04-27 12:00 | 3559.54 | 1.1334 | 82.3814 | 74.6386 | 1043.1982
2023-04-28 13:00 | 3716.02 | 1.1639 | 82.6604 | 74.6386 | 1089.058
2023-04-29 14:00 | 3640.79 | 1.1947 | 82.4363 | 74.6386 | 1067.0102
2023-04-30 15:00 | 4130.4 | 1.3336 | 82.6458 | 74.6386 | 1210.5007
2023-05-01 16:00 | 4000.83 | 1.2611 | 82.9205 | 74.6386 | 1172.5275
2023-05-02 17:00 | 6046.95 | 1.9377 | 82.8608 | 74.6386 | 1772.1861
2023-05-03 18:00 | 4874.81 | 1.5143 | 83.3138 | 74.6386 | 1428.6658
2023-05-04 19:00 | 3469.14 | 1.1273 | 83.0408 | 74.6386 | 1016.7046
2023-05-05 20:00 | 3122.93 | 1 | 85.8563 | 74.6386 | 915.2404
2023-05-06 21:00 | 3130.48 | 1 | 74.1799 | 74.6386 | 917.4531
2023-05-07 22:00 | 3058.67 | 1 | 74.2309 | 74.6386 | 896.4077
2023-05-08 23:00 | 3066.42 | 1 | 74.2177 | 74.6386 | 898.679
2023-05-10 | -854.391 | 2.5707 | 74.9212 | 74.6386 | -250.3973
2023-05-11 01:00 | -1171.58 | 3.1223 | 74.5544 | 74.6386 | -343.3562
2023-05-12 02:00 | -1253.11 | 3.2784 | 74.379 | 74.6386 | -367.2503
2023-05-13 03:00 | -1415.1 | 3.6545 | 74.2851 | 74.6386 | -414.7249
2023-05-14 04:00 | -1528.74 | 3.899 | 74.1909 | 74.6386 | -448.0295
2023-05-15 05:00 | -1576.52 | 3.9979 | 74.0881 | 74.6386 | -462.0324
2023-05-16 06:00 | -1501.39 | 3.8121 | 74.0515 | 74.6386 | -440.014
2023-05-17 07:00 | -576.472 | 1.6262 | 74.1218 | 74.6386 | -168.9473
2023-05-18 08:00 | 2300.97 | 1 | 73.8901 | 74.6386 | 674.3477
2023-05-19 09:00 | 2882.28 | 1 | 73.8305 | 74.6386 | 844.7129
2023-05-20 10:00 | 3123.17 | 1 | 88.2172 | 74.6386 | 915.3108
2023-05-21 11:00 | 4003.45 | 1.2771 | 82.8627 | 74.6386 | 1173.2954
2023-05-22 12:00 | 5317.95 | 1.7756 | 82.6898 | 74.6386 | 1558.5373
2023-05-23 13:00 | 6416.74 | 2.0571 | 83.1913 | 74.6386 | 1880.5609
2023-05-24 14:00 | 8034.91 | 2.6351 | 83.2203 | 74.6386 | 2354.7997
2023-05-25 15:00 | 8809.6 | 2.9457 | 83.3346 | 74.6386 | 2581.8389
2023-05-26 16:00 | 8092.96 | 2.5805 | 83.9175 | 74.6386 | 2371.8124
2023-05-27 17:00 | 9877.41 | 3.204 | 83.8991 | 74.6386 | 2894.7831
2023-05-28 18:00 | 7850.16 | 2.3924 | 84.613 | 74.6386 | 2300.6548
2023-05-29 19:00 | 6221.79 | 1.9049 | 84.6128 | 74.6386 | 1823.4267
2023-05-30 20:00 | 4929.37 | 1.5228 | 84.4497 | 74.6386 | 1444.6557
2023-05-31 21:00 | 3769.56 | 1.1975 | 84.1279 | 74.6386 | 1104.749
2023-06-01 22:00 | 3075.79 | 1 | 84.7158 | 74.6386 | 901.4251
2023-06-02 23:00 | 3105.49 | 1 | 88.1496 | 74.6386 | 910.1293
2023-06-04 | 0 | 0 | 76.3727 | 74.6386 | 0
2023-06-05 01:00 | -405.208 | 1.4048 | 75.4262 | 74.6386 | -118.7547
2023-06-06 02:00 | -657.468 | 1.9865 | 75.1372 | 74.6386 | -192.6849
2023-06-07 03:00 | -881.535 | 2.472 | 74.9523 | 74.6386 | -258.3524
2023-06-08 04:00 | -666.817 | 1.932 | 74.8682 | 74.6386 | -195.4248
2023-06-09 05:00 | -563.377 | 1.7322 | 74.8212 | 74.6386 | -165.1095
2023-06-10 06:00 | -157.882 | 0.79569 | 75.0845 | 74.6386 | -46.2706
2023-06-11 07:00 | 2850.96 | 1 | 74.1752 | 74.6386 | 835.5339
2023-06-12 08:00 | 2717.25 | 1.2472 | 80.9242 | 74.6386 | 796.3474
2023-06-13 09:00 | 2871.08 | 1.0642 | 82.2473 | 74.6386 | 841.4305
2023-06-14 10:00 | 5518.34 | 1.9152 | 82.7324 | 74.6386 | 1617.2658
2023-06-15 11:00 | 7159.84 | 2.5186 | 82.8852 | 74.6386 | 2098.342
2023-06-16 12:00 | 8536.17 | 3.0173 | 83.1439 | 74.6386 | 2501.7045
2023-06-17 13:00 | 9410.33 | 3.1427 | 83.7861 | 74.6386 | 2757.8955
2023-06-18 14:00 | 10924.5 | 3.6355 | 84.0518 | 74.6386 | 3201.6549
2023-06-19 15:00 | 11426.4 | 3.7572 | 84.4359 | 74.6386 | 3348.7473
2023-06-20 16:00 | 11293.8 | 3.6788 | 84.7433 | 74.6386 | 3309.8861
2023-06-21 17:00 | 10697.7 | 3.315 | 85.2697 | 74.6386 | 3135.1864
2023-06-22 18:00 | 9369.13 | 2.9137 | 85.3381 | 74.6386 | 2745.821
2023-06-23 19:00 | 7657.21 | 2.3525 | 85.4265 | 74.6386 | 2244.1067
2023-06-24 20:00 | 6620.96 | 1.9995 | 85.4656 | 74.6386 | 1940.4118
2023-06-25 21:00 | 4264.27 | 1.2645 | 85.5153 | 74.6386 | 1249.7342
2023-06-26 22:00 | 3223.91 | 1 | 85.0741 | 74.6386 | 944.8348
2023-06-27 23:00 | 3004.68 | 1 | 75.6571 | 74.6386 | 880.5848
2023-06-29 | 0 | 0 | 76.9887 | 74.6386 | 0
2023-06-30 01:00 | -149.965 | 0.79448 | 76.2372 | 74.6386 | -43.9504
2023-07-01 02:00 | -377.227 | 1.3689 | 75.82 | 74.6386 | -110.5543
2023-07-02 03:00 | -619.479 | 1.892 | 75.5585 | 74.6386 | -181.5514
2023-07-03 04:00 | -657.878 | 1.9452 | 75.3995 | 74.6386 | -192.805
2023-07-04 05:00 | -436.777 | 1.4264 | 75.3571 | 74.6386 | -128.0067
2023-07-05 06:00 | -75.7623 | 0.62435 | 76.1147 | 74.6386 | -22.2037
2023-07-06 07:00 | 2206.2 | 1 | 74.9383 | 74.6386 | 646.5734
2023-07-07 08:00 | 3732.34 | 1.2596 | 83.1561 | 74.6386 | 1093.8409
2023-07-08 09:00 | 5790.39 | 1.9742 | 83.2569 | 74.6386 | 1696.9958
2023-07-09 10:00 | 8100.89 | 2.8049 | 83.3929 | 74.6386 | 2374.1365
2023-07-10 11:00 | 9715.23 | 3.3449 | 83.7443 | 74.6386 | 2847.2529
2023-07-11 12:00 | 11187.7 | 3.7794 | 84.206 | 74.6386 | 3278.7912
2023-07-12 13:00 | 11552 | 3.8178 | 84.6746 | 74.6386 | 3385.557
2023-07-13 14:00 | 12443.4 | 4.0067 | 85.1011 | 74.6386 | 3646.8006
2023-07-14 15:00 | 13057 | 4.2415 | 85.275 | 74.6386 | 3826.629
2023-07-15 16:00 | 13089.7 | 4.1199 | 85.7318 | 74.6386 | 3836.2124
2023-07-16 17:00 | 12177.5 | 3.7948 | 85.9731 | 74.6386 | 3568.873
2023-07-17 18:00 | 10406.6 | 3.2437 | 86.0451 | 74.6386 | 3049.8734
2023-07-18 19:00 | 8691.97 | 2.6066 | 86.301 | 74.6386 | 2547.3649
2023-07-19 20:00 | 7428.11 | 2.2382 | 86.1488 | 74.6386 | 2176.9641
2023-07-20 21:00 | 5192.6 | 1.5025 | 86.3421 | 74.6386 | 1521.8008
2023-07-21 22:00 | 4008.76 | 1.2155 | 85.7294 | 74.6386 | 1174.8516
2023-07-22 23:00 | 3149.84 | 1 | 76.1758 | 74.6386 | 923.127
2023-07-24 | 3014.16 | 1 | 76.0566 | 74.6386 | 883.3631
2023-07-25 01:00 | 2962.5 | 1 | 75.9554 | 74.6386 | 868.223
2023-07-26 02:00 | 0 | 0 | 77.2882 | 74.6386 | 0
2023-07-27 03:00 | 428.609 | 1 | 76.7885 | 74.6386 | 125.6129
2023-07-28 04:00 | 3471.21 | 1 | 75.1683 | 74.6386 | 1017.3112
2023-07-29 05:00 | 1846.55 | 1 | 76.0927 | 74.6386 | 541.1704
2023-07-30 06:00 | 2796.75 | 1 | 75.5555 | 74.6386 | 819.6465
2023-07-31 07:00 | 3021.14 | 1 | 75.4324 | 74.6386 | 885.4087
2023-08-01 08:00 | 3223.98 | 1 | 89.489 | 74.6386 | 944.8553
2023-08-02 09:00 | 3158.61 | 1 | 75.4391 | 74.6386 | 925.6972
2023-08-03 10:00 | 3271.76 | 1 | 86.6588 | 74.6386 | 958.8582
2023-08-04 11:00 | 7456.32 | 2.6525 | 83.5829 | 74.6386 | 2185.2317
2023-08-05 12:00 | 7811.25 | 2.577 | 84.399 | 74.6386 | 2289.2514
2023-08-06 13:00 | 8207.91 | 2.6637 | 84.6976 | 74.6386 | 2405.501
2023-08-07 14:00 | 10808.1 | 3.6613 | 84.522 | 74.6386 | 3167.5414
2023-08-08 15:00 | 11668 | 3.9622 | 84.8095 | 74.6386 | 3419.5532
2023-08-09 16:00 | 11254.6 | 3.7051 | 85.2881 | 74.6386 | 3298.3977
2023-08-10 17:00 | 10863.6 | 3.4657 | 85.628 | 74.6386 | 3183.8069
2023-08-11 18:00 | 9870.42 | 3.1273 | 85.7551 | 74.6386 | 2892.7346
2023-08-12 19:00 | 8752.02 | 2.6259 | 86.1977 | 74.6386 | 2564.9639
2023-08-13 20:00 | 7683.88 | 2.3166 | 86.1099 | 74.6386 | 2251.9229
2023-08-14 21:00 | 5514.85 | 1.6321 | 86.1826 | 74.6386 | 1616.243
2023-08-15 22:00 | 4484.58 | 1.3637 | 85.7946 | 74.6386 | 1314.3007
2023-08-16 23:00 | 3178.82 | 1 | 88.8978 | 74.6386 | 931.6202
2023-08-18 | 3248.24 | 1 | 76.0769 | 74.6386 | 951.9652
2023-08-19 01:00 | 3120 | 1 | 76.0323 | 74.6386 | 914.3817
2023-08-20 02:00 | 3202.9 | 1 | 75.9032 | 74.6386 | 938.6773
2023-08-21 03:00 | 3259.86 | 1 | 75.817 | 74.6386 | 955.3707
2023-08-22 04:00 | 3208.67 | 1 | 75.7933 | 74.6386 | 940.3684
2023-08-23 05:00 | 3215.85 | 1 | 75.7579 | 74.6386 | 942.4726
2023-08-24 06:00 | 3185.04 | 1 | 86.8652 | 74.6386 | 933.4431
2023-08-25 07:00 | 3229.85 | 1 | 85.3477 | 74.6386 | 946.5756
2023-08-26 08:00 | 4324.65 | 1.351 | 84.8008 | 74.6386 | 1267.4298
2023-08-27 09:00 | 4647.54 | 1.4793 | 84.7277 | 74.6386 | 1362.0595
2023-08-28 10:00 | 4723.2 | 1.5422 | 84.5994 | 74.6386 | 1384.2333
2023-08-29 11:00 | 7559.7 | 2.6019 | 84.2514 | 74.6386 | 2215.5294
2023-08-30 12:00 | 9489.95 | 3.3536 | 84.2979 | 74.6386 | 2781.2298
2023-08-31 13:00 | 9529.92 | 3.1815 | 84.9688 | 74.6386 | 2792.9439
2023-09-01 14:00 | 9350.76 | 3.0916 | 85.1792 | 74.6386 | 2740.4372
2023-09-02 15:00 | 8747.77 | 2.8214 | 85.4401 | 74.6386 | 2563.7183
2023-09-03 16:00 | 8547.23 | 2.8158 | 85.3272 | 74.6386 | 2504.9458
2023-09-04 17:00 | 8972.78 | 2.9937 | 85.2509 | 74.6386 | 2629.6622
2023-09-05 18:00 | 7896.07 | 2.5033 | 85.6708 | 74.6386 | 2314.1097
2023-09-06 19:00 | 6493.9 | 2.0443 | 85.6888 | 74.6386 | 1903.1742
2023-09-07 20:00 | 5488.02 | 1.6572 | 85.8952 | 74.6386 | 1608.3799
2023-09-08 21:00 | 3213.93 | 1 | 85.9052 | 74.6386 | 941.9099
2023-09-09 22:00 | 3111.62 | 1 | 76.2378 | 74.6386 | 911.9258
2023-09-10 23:00 | 0 | 0 | 77.5953 | 74.6386 | 0
2023-09-12 | -356.776 | 1.3497 | 76.6361 | 74.6386 | -104.5607
2023-09-13 01:00 | -580.05 | 1.789 | 76.2532 | 74.6386 | -169.9959
2023-09-14 02:00 | -834.875 | 2.351 | 76.0117 | 74.6386 | -244.6777
2023-09-15 03:00 | -1053.32 | 2.8211 | 75.8269 | 74.6386 | -308.6976
2023-09-16 04:00 | -1233.13 | 3.2101 | 75.6532 | 74.6386 | -361.3947
2023-09-17 05:00 | -1340.93 | 3.4366 | 75.528 | 74.6386 | -392.9878
2023-09-18 06:00 | -1363.9 | 3.4766 | 75.4231 | 74.6386 | -399.7196
2023-09-19 07:00 | -669.213 | 1.8477 | 75.4084 | 74.6386 | -196.127
2023-09-20 08:00 | -104.95 | 0.65849 | 75.8643 | 74.6386 | -30.7578
2023-09-21 09:00 | 2329.03 | 1 | 75.1303 | 74.6386 | 682.5713
2023-09-22 10:00 | 2809.65 | 1 | 84.6123 | 74.6386 | 823.4271
2023-09-23 11:00 | 4725.65 | 1.5827 | 83.6022 | 74.6386 | 1384.9513
2023-09-24 12:00 | 4887.29 | 1.603 | 83.9487 | 74.6386 | 1432.3233
2023-09-25 13:00 | 6025.1 | 1.983 | 84.0522 | 74.6386 | 1765.7825
2023-09-26 14:00 | 6657.36 | 2.1711 | 84.2812 | 74.6386 | 1951.0796
2023-09-27 15:00 | 7030.01 | 2.2677 | 84.5037 | 74.6386 | 2060.2926
2023-09-28 16:00 | 6558.7 | 2.0991 | 84.6871 | 74.6386 | 1922.1652
2023-09-29 17:00 | 8339.32 | 2.7227 | 84.5822 | 74.6386 | 2444.0134
2023-09-30 18:00 | 6103.13 | 1.8873 | 85.1777 | 74.6386 | 1788.6508
2023-10-01 19:00 | 4430.46 | 1.3704 | 85.1387 | 74.6386 | 1298.4397
2023-10-02 20:00 | 3168.65 | 1 | 85.2936 | 74.6386 | 928.6396
2023-10-03 21:00 | 3103.5 | 1 | 75.7181 | 74.6386 | 909.5461
2023-10-04 22:00 | 3092.87 | 1 | 75.6579 | 74.6386 | 906.4307
2023-10-05 23:00 | 3014.76 | 1 | 75.6319 | 74.6386 | 883.5389
2023-10-07 | -772.547 | 2.3477 | 76.27 | 74.6386 | -226.4112
2023-10-08 01:00 | -1189.83 | 3.1388 | 75.8445 | 74.6386 | -348.7048
2023-10-09 02:00 | -1373.55 | 3.5155 | 75.6122 | 74.6386 | -402.5478
2023-10-10 03:00 | -1526.57 | 3.8507 | 75.4649 | 74.6386 | -447.3935
2023-10-11 04:00 | -1592.47 | 3.985 | 75.3297 | 74.6386 | -466.7069
2023-10-12 05:00 | -1571.18 | 3.9301 | 75.1946 | 74.6386 | -460.4674
2023-10-13 06:00 | -1485.41 | 3.7348 | 75.1334 | 74.6386 | -435.3307
2023-10-14 07:00 | -488.675 | 1.4089 | 75.206 | 74.6386 | -143.2165
2023-10-15 08:00 | 2098.79 | 1 | 75.045 | 74.6386 | 615.0946
2023-10-16 09:00 | 2613.28 | 1 | 74.9818 | 74.6386 | 765.8768
2023-10-17 10:00 | 3047.3 | 1 | 74.8921 | 74.6386 | 893.0755
2023-10-18 11:00 | 5276.87 | 1.7254 | 83.6841 | 74.6386 | 1546.4979
2023-10-19 12:00 | 4786.54 | 1.5099 | 84.1739 | 74.6386 | 1402.7964
2023-10-20 13:00 | 5735.99 | 1.9066 | 83.8971 | 74.6386 | 1681.0527
2023-10-21 14:00 | 5338.74 | 1.7673 | 84.0439 | 74.6386 | 1564.6302
2023-10-22 15:00 | 6111.93 | 2.0179 | 84.1229 | 74.6386 | 1791.2299
2023-10-23 16:00 | 5513.19 | 1.7903 | 84.3524 | 74.6386 | 1615.7565
2023-10-24 17:00 | 7554.52 | 2.4434 | 84.3943 | 74.6386 | 2214.0113
2023-10-25 18:00 | 6343.97 | 2.0198 | 84.7005 | 74.6386 | 1859.2341
2023-10-26 19:00 | 5275.36 | 1.5856 | 85.1767 | 74.6386 | 1546.0554
2023-10-27 20:00 | 4305.46 | 1.3467 | 84.8186 | 74.6386 | 1261.8058
2023-10-28 21:00 | 3499.28 | 1.1635 | 84.2981 | 74.6386 | 1025.5377
2023-10-29 22:00 | 3222.28 | 1 | 87.5417 | 74.6386 | 944.357
2023-10-30 23:00 | 3139.16 | 1 | 75.4997 | 74.6386 | 919.997
2023-11-01 | 0 | 0 | 76.9794 | 74.6386 | 0
2023-11-02 01:00 | -525.437 | 1.6682 | 75.9732 | 74.6386 | -153.9904
2023-11-03 02:00 | -629.502 | 1.8893 | 75.7496 | 74.6386 | -184.4888
2023-11-04 03:00 | -669.586 | 1.9681 | 75.6274 | 74.6386 | -196.2363
2023-11-05 04:00 | -610.503 | 1.826 | 75.5515 | 74.6386 | -178.9208
2023-11-06 05:00 | -503.918 | 1.5898 | 75.5002 | 74.6386 | -147.6838
2023-11-07 06:00 | -74.6663 | 0.60822 | 76.297 | 74.6386 | -21.8825
2023-11-08 07:00 | 106.015 | 1 | 76.1591 | 74.6386 | 31.0699
2023-11-09 08:00 | 1959.16 | 1 | 75.2571 | 74.6386 | 574.1731
2023-11-10 09:00 | 2789.62 | 1 | 74.9755 | 74.6386 | 817.5569
2023-11-11 10:00 | 3974.2 | 1.3418 | 83.4589 | 74.6386 | 1164.723
2023-11-12 11:00 | 6671 | 2.2301 | 83.6475 | 74.6386 | 1955.0771
2023-11-13 12:00 | 7251.61 | 2.4016 | 84.011 | 74.6386 | 2125.2371
2023-11-14 13:00 | 8197.41 | 2.6978 | 84.285 | 74.6386 | 2402.4237
2023-11-15 14:00 | 8541.39 | 2.7906 | 84.5437 | 74.6386 | 2503.2343
2023-11-16 15:00 | 9007.4 | 2.9889 | 84.6095 | 74.6386 | 2639.8084
2023-11-17 16:00 | 8826.82 | 2.926 | 84.7888 | 74.6386 | 2586.8856
2023-11-18 17:00 | 7693.17 | 2.5611 | 84.8512 | 74.6386 | 2254.6456
2023-11-19 18:00 | 6234.96 | 2.0405 | 84.9762 | 74.6386 | 1827.2864
2023-11-20 19:00 | 4598.52 | 1.4605 | 85.1217 | 74.6386 | 1347.6932
2023-11-21 20:00 | 3314.71 | 1.0568 | 84.9521 | 74.6386 | 971.4456
2023-11-22 21:00 | 2983.42 | 1 | 75.924 | 74.6386 | 874.3541
2023-11-23 22:00 | 0 | 0 | 77.2437 | 74.6386 | 0
2023-11-24 23:00 | -951.696 | 2.6299 | 76.0705 | 74.6386 | -278.9146
2023-11-26 | -1456.35 | 3.7433 | 75.7514 | 74.6386 | -426.8141
2023-11-27 01:00 | -1862.69 | 4.6201 | 75.5295 | 74.6386 | -545.9006
2023-11-28 02:00 | -2357.63 | 5.73 | 75.3395 | 74.6386 | -690.9531
2023-11-29 03:00 | -2516.77 | 6.0314 | 75.1418 | 74.6386 | -737.5925
2023-11-30 04:00 | -2531.95 | 6.0523 | 75.0056 | 74.6386 | -742.0413
2023-12-01 05:00 | -2489.41 | 5.956 | 74.905 | 74.6386 | -729.5741
2023-12-02 06:00 | -2096.6 | 5.0339 | 74.8278 | 74.6386 | -614.4528
2023-12-03 07:00 | -1957.76 | 4.7796 | 74.805 | 74.6386 | -573.7628
2023-12-04 08:00 | -1682.7 | 4.1488 | 74.7747 | 74.6386 | -493.1507
2023-12-05 09:00 | -1896.45 | 4.7078 | 74.7504 | 74.6386 | -555.7946
2023-12-06 10:00 | -1407.14 | 3.5046 | 74.7086 | 74.6386 | -412.392
2023-12-07 11:00 | -734.536 | 2.0113 | 74.7787 | 74.6386 | -215.2713
2023-12-08 12:00 | 69.984 | 1 | 75.6298 | 74.6386 | 20.5103
2023-12-09 13:00 | 2848.32 | 1 | 87.0951 | 74.6386 | 834.7602
2023-12-10 14:00 | 3018.61 | 1 | 74.4655 | 74.6386 | 884.6673
2023-12-11 15:00 | 3042.38 | 1 | 74.5841 | 74.6386 | 891.6336
2023-12-12 16:00 | 3097.32 | 1 | 85.6315 | 74.6386 | 907.7349
2023-12-13 17:00 | 3124.88 | 1 | 86.3445 | 74.6386 | 915.8119
2023-12-14 18:00 | 3104.51 | 1 | 74.7296 | 74.6386 | 909.8421
2023-12-15 19:00 | 2887.02 | 1 | 74.86 | 74.6386 | 846.102
2023-12-16 20:00 | 0 | 0 | 76.2631 | 74.6386 | 0
2023-12-17 21:00 | -762.801 | 2.1385 | 75.2206 | 74.6386 | -223.5549
2023-12-18 22:00 | -1074.86 | 2.9121 | 75.0387 | 74.6386 | -315.0104
2023-12-19 23:00 | -1868.48 | 4.7325 | 74.8824 | 74.6386 | -547.5974
2023-12-21 | -2146.84 | 5.2582 | 74.7226 | 74.6386 | -629.1767
2023-12-22 01:00 | -2405.31 | 5.8409 | 74.584 | 74.6386 | -704.9268
2023-12-23 02:00 | -2429.67 | 5.8581 | 74.4887 | 74.6386 | -712.066
2023-12-24 03:00 | -2336.48 | 5.638 | 74.4232 | 74.6386 | -684.7547
2023-12-25 04:00 | -2137.34 | 5.1823 | 74.3781 | 74.6386 | -626.3925
2023-12-26 05:00 | -1831.3 | 4.4895 | 74.3612 | 74.6386 | -536.7011
2023-12-27 06:00 | -1331.04 | 3.3542 | 74.3765 | 74.6386 | -390.0893
2023-12-28 07:00 | -1010.3 | 2.6825 | 74.4402 | 74.6386 | -296.0897
2023-12-29 08:00 | -576.873 | 1.7096 | 74.5656 | 74.6386 | -169.0648
2023-12-30 09:00 | -681.97 | 2.032 | 74.6165 | 74.6386 | -199.8657
2023-12-31 10:00 | 0 | 0 | 75.4249 | 74.6386 | 0
2024-01-01 11:00 | 1986.22 | 1 | 74.5179 | 74.6386 | 582.1036
2024-01-02 12:00 | 2878.32 | 1 | 74.2612 | 74.6386 | 843.5523
2024-01-03 13:00 | 2949.04 | 1 | 74.3791 | 74.6386 | 864.2783
2024-01-04 14:00 | 3048.55 | 1 | 87.5502 | 74.6386 | 893.4418
2024-01-05 15:00 | 5282.18 | 1.6846 | 83.3714 | 74.6386 | 1548.0541
2024-01-06 16:00 | 5599.71 | 1.8091 | 83.5081 | 74.6386 | 1641.113
2024-01-07 17:00 | 5667.24 | 1.8065 | 83.7599 | 74.6386 | 1660.9041
2024-01-08 18:00 | 5450.16 | 1.6696 | 84.1561 | 74.6386 | 1597.2842
2024-01-09 19:00 | 4431.93 | 1.3838 | 84.0836 | 74.6386 | 1298.8705
2024-01-10 20:00 | 3580.71 | 1.123 | 84.0608 | 74.6386 | 1049.4025
2024-01-11 21:00 | 3107.23 | 1 | 74.9739 | 74.6386 | 910.6392
2024-01-12 22:00 | 3116.02 | 1 | 74.9385 | 74.6386 | 913.2153
2024-01-13 23:00 | -200.053 | 1.0085 | 75.9623 | 74.6386 | -58.6297
2024-01-15 | -464.626 | 1.5596 | 75.4762 | 74.6386 | -136.1684
2024-01-16 01:00 | -601.652 | 1.8422 | 75.2568 | 74.6386 | -176.3268
2024-01-17 02:00 | -702.965 | 2.0598 | 75.1433 | 74.6386 | -206.0187
2024-01-18 03:00 | -687.657 | 2.0091 | 75.0559 | 74.6386 | -201.5324
2024-01-19 04:00 | -555.164 | 1.7035 | 75.014 | 74.6386 | -162.7025
2024-01-20 05:00 | -303.351 | 1.137 | 75.1253 | 74.6386 | -88.9034
2024-01-21 06:00 | 1226.61 | 1 | 75.1542 | 74.6386 | 359.4839
2024-01-22 07:00 | 2731.15 | 1 | 74.5271 | 74.6386 | 800.4211
2024-01-23 08:00 | 3039.94 | 1 | 88.022 | 74.6386 | 890.9185
2024-01-24 09:00 | 4415.92 | 1.4223 | 83.4592 | 74.6386 | 1294.1784
2024-01-25 10:00 | 6976.54 | 2.4915 | 82.9132 | 74.6386 | 2044.622
2024-01-26 11:00 | 8781.64 | 3.0172 | 83.4977 | 74.6386 | 2573.6446
2024-01-27 12:00 | 9476.05 | 3.1608 | 84.0349 | 74.6386 | 2777.1561
2024-01-28 13:00 | 10934.4 | 3.5696 | 84.442 | 74.6386 | 3204.5563
2024-01-29 14:00 | 11537.1 | 3.7866 | 84.7071 | 74.6386 | 3381.1902
2024-01-30 15:00 | 12116.9 | 3.9484 | 85.0241 | 74.6386 | 3551.1128
2024-01-31 16:00 | 12515.9 | 4.0489 | 85.3052 | 74.6386 | 3668.0482
2024-02-01 17:00 | 11831.5 | 3.8064 | 85.5488 | 74.6386 | 3467.4704
2024-02-02 18:00 | 10164.2 | 3.2252 | 85.7629 | 74.6386 | 2978.833
2024-02-03 19:00 | 8766.73 | 2.712 | 85.9314 | 74.6386 | 2569.2749
2024-02-04 20:00 | 7665.68 | 2.3476 | 85.9442 | 74.6386 | 2246.589
2024-02-05 21:00 | 5657.96 | 1.6195 | 86.4003 | 74.6386 | 1658.1844
2024-02-06 22:00 | 4547.58 | 1.3686 | 85.8008 | 74.6386 | 1332.7641
2024-02-07 23:00 | 3131.07 | 1 | 76.2433 | 74.6386 | 917.626
2024-02-09 | 3141.47 | 1 | 76.0413 | 74.6386 | 920.674
2024-02-10 01:00 | 3121.97 | 1 | 75.9285 | 74.6386 | 914.9591
2024-02-11 02:00 | 3124.12 | 1 | 75.8422 | 74.6386 | 915.5892
2024-02-12 03:00 | 3172.07 | 1 | 75.7559 | 74.6386 | 929.6419
2024-02-13 04:00 | 3185.07 | 1 | 75.6999 | 74.6386 | 933.4519
2024-02-14 05:00 | 3145.04 | 1 | 75.6904 | 74.6386 | 921.7202
2024-02-15 06:00 | 3290.91 | 1 | 75.5903 | 74.6386 | 964.4705
2024-02-16 07:00 | 3255.18 | 1 | 85.7123 | 74.6386 | 953.9991
2024-02-17 08:00 | 4933.09 | 1.5342 | 84.7528 | 74.6386 | 1445.746
2024-02-18 09:00 | 5310.21 | 1.6965 | 84.6681 | 74.6386 | 1556.2689
2024-02-19 10:00 | 6914.65 | 2.3456 | 84.3257 | 74.6386 | 2026.4839
2024-02-20 11:00 | 7042.46 | 2.3852 | 84.5002 | 74.6386 | 2063.9413
2024-02-21 12:00 | 9298.56 | 3.2355 | 84.4223 | 74.6386 | 2725.1389
2024-02-22 13:00 | 10184.8 | 3.3945 | 84.9621 | 74.6386 | 2984.8702
2024-02-23 14:00 | 10911.4 | 3.6144 | 85.215 | 74.6386 | 3197.8157
2024-02-24 15:00 | 11524.1 | 3.8436 | 85.3493 | 74.6386 | 3377.3803
2024-02-25 16:00 | 12288.3 | 4.1178 | 85.4836 | 74.6386 | 3601.3452
2024-02-26 17:00 | 11693.7 | 3.74 | 86.0148 | 74.6386 | 3427.0852
2024-02-27 18:00 | 9931.41 | 3.1877 | 86.0797 | 74.6386 | 2910.609
2024-02-28 19:00 | 8178.73 | 2.6106 | 86.0796 | 74.6386 | 2396.9492
2024-02-29 20:00 | 7127.41 | 2.2328 | 86.0989 | 74.6386 | 2088.8377
2024-03-01 21:00 | 4957.11 | 1.4809 | 86.353 | 74.6386 | 1452.7855
2024-03-02 22:00 | 3714.92 | 1.1498 | 85.8522 | 74.6386 | 1088.7356
2024-03-03 23:00 | 3096.4 | 1 | 76.501 | 74.6386 | 907.4653
2024-03-05 | 0 | 0 | 77.8274 | 74.6386 | 0
2024-03-06 01:00 | -463.188 | 1.4531 | 76.7264 | 74.6386 | -135.747
2024-03-07 02:00 | -307.484 | 1.1492 | 76.586 | 74.6386 | -90.1147
2024-03-08 03:00 | -237.395 | 1.0119 | 76.5118 | 74.6386 | -69.5736
2024-03-09 04:00 | -178.401 | 0.88729 | 76.4589 | 74.6386 | -52.2842
2024-03-10 05:00 | -265.125 | 1.0983 | 76.2415 | 74.6386 | -77.7005
2024-03-11 06:00 | -252.244 | 1.0533 | 76.1616 | 74.6386 | -73.9254
2024-03-12 07:00 | 1937.05 | 1 | 83.4407 | 74.6386 | 567.6933
2024-03-13 08:00 | 4623.52 | 1.7157 | 83.1367 | 74.6386 | 1355.02
2024-03-14 09:00 | 4737.39 | 1.6234 | 83.908 | 74.6386 | 1388.392
2024-03-15 10:00 | 6917.8 | 2.4259 | 83.8706 | 74.6386 | 2027.407
2024-03-16 11:00 | 8777.51 | 3.0589 | 84.1449 | 74.6386 | 2572.4342
2024-03-17 12:00 | 9703.22 | 3.3466 | 84.5276 | 74.6386 | 2843.7331
2024-03-18 13:00 | 10321.4 | 3.427 | 85.0434 | 74.6386 | 3024.9037
2024-03-19 14:00 | 9958.71 | 3.3017 | 85.2479 | 74.6386 | 2918.6098
2024-03-20 15:00 | 9639.33 | 3.0602 | 85.6891 | 74.6386 | 2825.0088
2024-03-21 16:00 | 9970.81 | 3.3309 | 85.3877 | 74.6386 | 2922.156
2024-03-22 17:00 | 11341.2 | 3.7618 | 85.5293 | 74.6386 | 3323.7776
2024-03-23 18:00 | 9175.88 | 2.9318 | 85.9896 | 74.6386 | 2689.185
2024-03-24 19:00 | 8373.23 | 2.528 | 86.3822 | 74.6386 | 2453.9515
2024-03-25 20:00 | 7145.33 | 2.1607 | 86.308 | 74.6386 | 2094.0895
2024-03-26 21:00 | 6309.55 | 1.8912 | 86.3046 | 74.6386 | 1849.1466
2024-03-27 22:00 | 5361.38 | 1.6356 | 86.0724 | 74.6386 | 1571.2654
2024-03-28 23:00 | 4869.66 | 1.4842 | 85.9402 | 74.6386 | 1427.1565
2024-03-30 | 3120.53 | 1 | 76.5728 | 74.6386 | 914.5371
2024-03-31 01:00 | 3235.95 | 1 | 76.3285 | 74.6386 | 948.3633
2024-04-01 02:00 | 3062.16 | 1 | 76.3131 | 74.6386 | 897.4305
2024-04-02 03:00 | 942.532 | 1 | 77.2663 | 74.6386 | 276.2289
2024-04-03 04:00 | 262.951 | 1 | 77.3756 | 74.6386 | 77.0633
2024-04-04 05:00 | 439.468 | 1 | 77.088 | 74.6386 | 128.7954
2024-04-05 06:00 | 85.1194 | 1 | 77.1672 | 74.6386 | 24.946
2024-04-06 07:00 | 2227.7 | 1.1447 | 81.7042 | 74.6386 | 652.8744
2024-04-07 08:00 | 5214.14 | 1.9708 | 83.4087 | 74.6386 | 1528.1136
2024-04-08 09:00 | 5879.09 | 2.1168 | 83.9678 | 74.6386 | 1722.9912
2024-04-09 10:00 | 3091.23 | 1.0679 | 84.4146 | 74.6386 | 905.9501
2024-04-10 11:00 | 3080.5 | 1 | 87.0237 | 74.6386 | 902.8054
2024-04-11 12:00 | 3106.92 | 1 | 89.1519 | 74.6386 | 910.5484
2024-04-12 13:00 | 3153.53 | 1 | 75.8419 | 74.6386 | 924.2084
2024-04-13 14:00 | 3049.93 | 1 | 75.8372 | 74.6386 | 893.8462
2024-04-14 15:00 | 3133.65 | 1 | 75.7327 | 74.6386 | 918.3822
2024-04-15 16:00 | 3148.23 | 1 | 75.7075 | 74.6386 | 922.6551
2024-04-16 17:00 | 3637.3 | 1.169 | 84.5777 | 74.6386 | 1065.9874
2024-04-17 18:00 | 3191 | 1 | 85.2269 | 74.6386 | 935.1898
2024-04-18 19:00 | 3080.83 | 1 | 87.9841 | 74.6386 | 902.9021
2024-04-19 20:00 | 3174.27 | 1 | 75.6192 | 74.6386 | 930.2867
2024-04-20 21:00 | 3129.79 | 1 | 75.6187 | 74.6386 | 917.2509
2024-04-21 22:00 | 3012.87 | 1 | 75.669 | 74.6386 | 882.985
2024-04-22 23:00 | 2834.62 | 1 | 75.7389 | 74.6386 | 830.7451
2024-04-24 | -817.467 | 2.4487 | 76.3085 | 74.6386 | -239.5759
2024-04-25 01:00 | -1181.63 | 3.1093 | 75.9238 | 74.6386 | -346.3016
2024-04-26 02:00 | -1536.25 | 3.8951 | 75.7053 | 74.6386 | -450.2304
2024-04-27 03:00 | -1832.18 | 4.5349 | 75.5592 | 74.6386 | -536.959
2024-04-28 04:00 | -1817.88 | 4.457 | 75.4258 | 74.6386 | -532.768
2024-04-29 05:00 | -1834.64 | 4.508 | 75.3193 | 74.6386 | -537.6799
2024-04-30 06:00 | -1635.95 | 4.0379 | 75.2678 | 74.6386 | -479.4496
2024-05-01 07:00 | -1260.52 | 3.1927 | 75.2449 | 74.6386 | -369.4219
2024-05-02 08:00 | -294.353 | 0.99576 | 75.4437 | 74.6386 | -86.2663
2024-05-03 09:00 | 999.649 | 1 | 75.6842 | 74.6386 | 292.9682
2024-05-04 10:00 | 3046.05 | 1 | 74.7823 | 74.6386 | 892.7091
2024-05-05 11:00 | 3413.48 | 1.1367 | 83.5474 | 74.6386 | 1000.3922
2024-05-06 12:00 | 4952.82 | 1.7261 | 83.3548 | 74.6386 | 1451.5283
2024-05-07 13:00 | 5321.1 | 1.8693 | 83.4969 | 74.6386 | 1559.4605
2024-05-08 14:00 | 5085.46 | 1.7993 | 83.6079 | 74.6386 | 1490.4012
2024-05-09 15:00 | 5102.27 | 1.8052 | 83.6929 | 74.6386 | 1495.3277
2024-05-10 16:00 | 5583.04 | 1.9365 | 83.8862 | 74.6386 | 1636.2275
2024-05-11 17:00 | 4678.61 | 1.5851 | 84.1402 | 74.6386 | 1371.1652
2024-05-12 18:00 | 3007.85 | 1 | 84.4628 | 74.6386 | 881.5138
2024-05-13 19:00 | 3079.61 | 1 | 75.5436 | 74.6386 | 902.5446
2024-05-14 20:00 | 2987.06 | 1 | 75.5473 | 74.6386 | 875.4209
2024-05-15 21:00 | -481.92 | 1.6642 | 76.2783 | 74.6386 | -141.2368
2024-05-16 22:00 | -945.293 | 2.6219 | 75.8075 | 74.6386 | -277.038
2024-05-17 23:00 | -1907.82 | 4.815 | 75.5082 | 74.6386 | -559.1268
2024-05-19 | -2310.09 | 5.6049 | 75.2907 | 74.6386 | -677.0205
2024-05-20 01:00 | -2741.29 | 6.5195 | 75.098 | 74.6386 | -803.3928
2024-05-21 02:00 | -2899.56 | 6.5195 | 74.8698 | 74.6386 | -849.7772
2024-05-22 03:00 | -3111.53 | 6.5195 | 74.6796 | 74.6386 | -911.8994
2024-05-23 04:00 | -3069.34 | 6.5195 | 74.5828 | 74.6386 | -899.5348
2024-05-24 05:00 | -3143.28 | 6.5195 | 74.4744 | 74.6386 | -921.2044
2024-05-25 06:00 | -2875.93 | 6.5195 | 74.5024 | 74.6386 | -842.8519
2024-05-26 07:00 | -2455.97 | 5.8678 | 74.5086 | 74.6386 | -719.7738
2024-05-27 08:00 | -1716.4 | 4.1541 | 74.4911 | 74.6386 | -503.0272
2024-05-28 09:00 | -1056.8 | 2.7246 | 74.5774 | 74.6386 | -309.7175
2024-05-29 10:00 | 2243.4 | 1 | 74.4576 | 74.6386 | 657.4756
2024-05-30 11:00 | 2886.79 | 1 | 74.4111 | 74.6386 | 846.0346
2024-05-31 12:00 | 2992.8 | 1.0511 | 82.7411 | 74.6386 | 877.1031
2024-06-01 13:00 | 4150.1 | 1.4945 | 82.6713 | 74.6386 | 1216.2742
2024-06-02 14:00 | 4498.79 | 1.6137 | 82.8693 | 74.6386 | 1318.4652
2024-06-03 15:00 | 4776.86 | 1.7151 | 83.0142 | 74.6386 | 1399.9595
2024-06-04 16:00 | 5380.03 | 1.9033 | 83.208 | 74.6386 | 1576.7311
2024-06-05 17:00 | 3919.83 | 1.4002 | 83.2645 | 74.6386 | 1148.7888
2024-06-06 18:00 | 2787.93 | 1 | 86.0989 | 74.6386 | 817.0616
2024-06-07 19:00 | 2695.58 | 1 | 75.2518 | 74.6386 | 789.9965
2024-06-08 20:00 | -82.8323 | 0.73842 | 76.2621 | 74.6386 | -24.2758
2024-06-09 21:00 | -1132.66 | 3.1346 | 75.4634 | 74.6386 | -331.9499
2024-06-10 22:00 | -1611.79 | 4.0946 | 75.1636 | 74.6386 | -472.369
2024-06-11 23:00 | -2616.45 | 6.4116 | 74.9752 | 74.6386 | -766.8058
2024-06-13 | -3143.06 | 6.5195 | 74.6284 | 74.6386 | -921.14
2024-06-14 01:00 | -3345.03 | 6.5195 | 74.3808 | 74.6386 | -980.3315
2024-06-15 02:00 | -3510.45 | 6.5195 | 74.2012 | 74.6386 | -1028.8113
2024-06-16 03:00 | -3668.16 | 6.5195 | 74.041 | 74.6386 | -1075.0316
2024-06-17 04:00 | -3699.38 | 6.5195 | 73.926 | 74.6386 | -1084.1813
2024-06-18 05:00 | -3727.65 | 6.5195 | 73.8401 | 74.6386 | -1092.4664
2024-06-19 06:00 | -3373.04 | 6.5195 | 73.9078 | 74.6386 | -988.5404
2024-06-20 07:00 | -2844.87 | 6.5195 | 74.0661 | 74.6386 | -833.7491
2024-06-21 08:00 | -1878.91 | 4.5088 | 74.1211 | 74.6386 | -550.6542
2024-06-22 09:00 | -1034.7 | 2.6534 | 74.2473 | 74.6386 | -303.2406
2024-06-23 10:00 | 1617.51 | 1 | 74.4657 | 74.6386 | 474.0454
2024-06-24 11:00 | 2875.09 | 1 | 86.7754 | 74.6386 | 842.6057
2024-06-25 12:00 | 3706.17 | 1.346 | 82.2148 | 74.6386 | 1086.1712
2024-06-26 13:00 | 4538.18 | 1.6375 | 82.4467 | 74.6386 | 1330.0093
2024-06-27 14:00 | 5197.01 | 1.8693 | 82.6528 | 74.6386 | 1523.0933
2024-06-28 15:00 | 5370.37 | 1.9266 | 82.8529 | 74.6386 | 1573.9001
2024-06-29 16:00 | 6127.25 | 2.2006 | 82.9687 | 74.6386 | 1795.7197
2024-06-30 17:00 | 5033.46 | 1.8022 | 83.141 | 74.6386 | 1475.1615
2024-07-01 18:00 | 3170.27 | 1.1365 | 83.1699 | 74.6386 | 929.1144
2024-07-02 19:00 | 2767.07 | 1 | 75.1342 | 74.6386 | 810.9482
2024-07-03 20:00 | 2740.15 | 1 | 75.0973 | 74.6386 | 803.0587
2024-07-04 21:00 | -794.454 | 2.4176 | 75.6383 | 74.6386 | -232.8315
2024-07-05 22:00 | -1362.94 | 3.5613 | 75.2243 | 74.6386 | -399.4383
2024-07-06 23:00 | -2467.66 | 6.1001 | 74.9671 | 74.6386 | -723.1998
2024-07-08 | -3149.84 | 6.5195 | 74.5998 | 74.6386 | -923.127
2024-07-09 01:00 | -3375.42 | 6.5195 | 74.3318 | 74.6386 | -989.238
2024-07-10 02:00 | -3840.17 | 6.5195 | 73.9996 | 74.6386 | -1125.4427
2024-07-11 03:00 | -3738.49 | 6.5195 | 73.9043 | 74.6386 | -1095.6433
2024-07-12 04:00 | -3859.55 | 6.5195 | 73.7578 | 74.6386 | -1131.1224
2024-07-13 05:00 | -4009.15 | 6.5195 | 73.6181 | 74.6386 | -1174.9659
2024-07-14 06:00 | -3589.81 | 6.5195 | 73.6948 | 74.6386 | -1052.0695
2024-07-15 07:00 | -2643.18 | 6.3721 | 73.9805 | 74.6386 | -774.6396
2024-07-16 08:00 | -1246.43 | 3.0134 | 74.0073 | 74.6386 | -365.2926
2024-07-17 09:00 | 0 | 0 | 75.0977 | 74.6386 | 0
2024-07-18 10:00 | 2873.51 | 1 | 86.4345 | 74.6386 | 842.1427
2024-07-19 11:00 | 4331.31 | 1.5262 | 82.2344 | 74.6386 | 1269.3817
2024-07-20 12:00 | 5891.24 | 2.0548 | 82.589 | 74.6386 | 1726.552
2024-07-21 13:00 | 6387.32 | 2.2439 | 82.8241 | 74.6386 | 1871.9387
2024-07-22 14:00 | 6989.46 | 2.4581 | 83.0433 | 74.6386 | 2048.4085
2024-07-23 15:00 | 7245.56 | 2.5227 | 83.3198 | 74.6386 | 2123.464
2024-07-24 16:00 | 8310.4 | 2.8452 | 83.5949 | 74.6386 | 2435.5378
2024-07-25 17:00 | 7767.47 | 2.6271 | 83.8892 | 74.6386 | 2276.4207
2024-07-26 18:00 | 5782.6 | 1.9491 | 84.0299 | 74.6386 | 1694.7128
2024-07-27 19:00 | 3685.49 | 1.2124 | 84.1557 | 74.6386 | 1080.1105
2024-07-28 20:00 | 2984.59 | 1 | 86.9798 | 74.6386 | 874.697
2024-07-29 21:00 | 771.579 | 1 | 76.3521 | 74.6386 | 226.1275
2024-07-30 22:00 | -464.908 | 1.6297 | 75.8213 | 74.6386 | -136.2511
2024-07-31 23:00 | -1423.37 | 3.7569 | 75.3658 | 74.6386 | -417.1486
2024-08-02 | -2190.34 | 5.417 | 75.1025 | 74.6386 | -641.9253
2024-08-03 01:00 | -2537.07 | 6.1217 | 74.8961 | 74.6386 | -743.5418
2024-08-04 02:00 | -2832.55 | 6.5195 | 74.6894 | 74.6386 | -830.1385
2024-08-05 03:00 | -3003.47 | 6.5195 | 74.4978 | 74.6386 | -880.2302
2024-08-06 04:00 | -3173.06 | 6.5195 | 74.319 | 74.6386 | -929.9321
2024-08-07 05:00 | -3083.6 | 6.5195 | 74.2484 | 74.6386 | -903.714
2024-08-08 06:00 | -2601.84 | 6.2361 | 74.3125 | 74.6386 | -762.524
2024-08-09 07:00 | -1689.87 | 4.0698 | 74.2984 | 74.6386 | -495.252
2024-08-10 08:00 | 0 | 0 | 75.3175 | 74.6386 | 0
2024-08-11 09:00 | 2558.6 | 1 | 74.2165 | 74.6386 | 749.8516
2024-08-12 10:00 | 3629.94 | 1.1915 | 82.9237 | 74.6386 | 1063.8304
2024-08-13 11:00 | 5749.24 | 1.8936 | 83.1035 | 74.6386 | 1684.9359
2024-08-14 12:00 | 7248.5 | 2.4036 | 83.3396 | 74.6386 | 2124.3257
2024-08-15 13:00 | 7322.15 | 2.5048 | 83.4195 | 74.6386 | 2145.9103
2024-08-16 14:00 | 7193.92 | 2.4154 | 83.7437 | 74.6386 | 2108.3298
2024-08-17 15:00 | 7031.36 | 2.3179 | 83.994 | 74.6386 | 2060.6882
2024-08-18 16:00 | 8523.72 | 2.6666 | 84.4717 | 74.6386 | 2498.0557
2024-08-19 17:00 | 8091.58 | 2.5392 | 84.639 | 74.6386 | 2371.408
2024-08-20 18:00 | 6107.92 | 1.8398 | 85.0588 | 74.6386 | 1790.0546
2024-08-21 19:00 | 4949.85 | 1.5115 | 84.892 | 74.6386 | 1450.6578
2024-08-22 20:00 | 3527.36 | 1.0794 | 84.7927 | 74.6386 | 1033.7672
2024-08-23 21:00 | 3129.16 | 1 | 75.4351 | 74.6386 | 917.0663
2024-08-24 22:00 | 3061.6 | 1 | 75.3721 | 74.6386 | 897.2664
2024-08-25 23:00 | -428.48 | 1.5519 | 76.1311 | 74.6386 | -125.5751
2024-08-27 | -964.84 | 2.6807 | 75.6321 | 74.6386 | -282.7667
2024-08-28 01:00 | -1142.59 | 3.0185 | 75.3743 | 74.6386 | -334.8601
2024-08-29 02:00 | -1430.24 | 3.6731 | 75.2264 | 74.6386 | -419.162
2024-08-30 03:00 | -1308.65 | 3.3401 | 75.099 | 74.6386 | -383.5275
2024-08-31 04:00 | -1526.4 | 3.8844 | 74.9878 | 74.6386 | -447.3437
2024-09-01 05:00 | -1722.78 | 4.3098 | 74.8958 | 74.6386 | -504.897
2024-09-02 06:00 | -1754.08 | 4.3537 | 74.8185 | 74.6386 | -514.0701
2024-09-03 07:00 | -646.936 | 1.7366 | 74.8332 | 74.6386 | -189.5982
2024-09-04 08:00 | 2209.09 | 1 | 74.686 | 74.6386 | 647.4204
2024-09-05 09:00 | 2796.57 | 1 | 86.4626 | 74.6386 | 819.5938
2024-09-06 10:00 | 4459.6 | 1.4741 | 83.2494 | 74.6386 | 1306.9797
2024-09-07 11:00 | 5813.2 | 1.9266 | 83.4347 | 74.6386 | 1703.6807
2024-09-08 12:00 | 5059.98 | 1.6394 | 83.8341 | 74.6386 | 1482.9338
2024-09-09 13:00 | 6647.79 | 2.196 | 83.781 | 74.6386 | 1948.2749
2024-09-10 14:00 | 7014.24 | 2.3279 | 83.9187 | 74.6386 | 2055.6708
2024-09-11 15:00 | 7060.99 | 2.2359 | 84.4157 | 74.6386 | 2069.3719
2024-09-12 16:00 | 6655.88 | 2.1491 | 84.3602 | 74.6386 | 1950.6459
2024-09-13 17:00 | 8062.46 | 2.6755 | 84.1995 | 74.6386 | 2362.8738
2024-09-14 18:00 | 5701.35 | 1.8062 | 84.7163 | 74.6386 | 1670.9007
2024-09-15 19:00 | 3836.48 | 1.1745 | 84.9194 | 74.6386 | 1124.3613
2024-09-16 20:00 | 3047.19 | 1 | 88.0429 | 74.6386 | 893.0432
2024-09-17 21:00 | 2965.31 | 1 | 75.4726 | 74.6386 | 869.0466
2024-09-18 22:00 | 2101.37 | 1 | 75.8252 | 74.6386 | 615.8508
2024-09-19 23:00 | 602.753 | 1 | 76.4214 | 74.6386 | 176.6495
2024-09-21 | -1266.15 | 3.4708 | 75.6746 | 74.6386 | -371.0719
2024-09-22 01:00 | -1732.03 | 4.3427 | 75.3575 | 74.6386 | -507.6079
2024-09-23 02:00 | -2029.88 | 4.9867 | 75.1632 | 74.6386 | -594.8991
2024-09-24 03:00 | -2307.44 | 5.6026 | 75.0055 | 74.6386 | -676.2439
2024-09-25 04:00 | -2465.27 | 5.9378 | 74.863 | 74.6386 | -722.4993
2024-09-26 05:00 | -2438.8 | 5.8557 | 74.7382 | 74.6386 | -714.7417
2024-09-27 06:00 | -2449.36 | 5.8922 | 74.6684 | 74.6386 | -717.8366
2024-09-28 07:00 | -1119.98 | 2.733 | 74.6228 | 74.6386 | -328.2337
2024-09-29 08:00 | 2352.59 | 1 | 74.4959 | 74.6386 | 689.4761
2024-09-30 09:00 | 3122.12 | 1 | 87.3844 | 74.6386 | 915.003
2024-10-01 10:00 | 3103.47 | 1 | 84.4923 | 74.6386 | 909.5373
2024-10-02 11:00 | 3858.97 | 1.2155 | 83.6602 | 74.6386 | 1130.9525
2024-10-03 12:00 | 6135.88 | 2.117 | 83.1445 | 74.6386 | 1798.2489
2024-10-04 13:00 | 7190.34 | 2.5772 | 83.1559 | 74.6386 | 2107.2806
2024-10-05 14:00 | 8314.65 | 2.7664 | 83.8837 | 74.6386 | 2436.7834
2024-10-06 15:00 | 8637.65 | 2.9013 | 84.0344 | 74.6386 | 2531.4453
2024-10-07 16:00 | 8525.15 | 2.7844 | 84.4217 | 74.6386 | 2498.4748
2024-10-08 17:00 | 9746.84 | 3.1585 | 84.6116 | 74.6386 | 2856.5168
2024-10-09 18:00 | 7440.39 | 2.3533 | 84.9995 | 74.6386 | 2180.5631
2024-10-10 19:00 | 5869.83 | 1.8507 | 85.0074 | 74.6386 | 1720.2774
2024-10-11 20:00 | 4599.73 | 1.4246 | 85.0255 | 74.6386 | 1348.0478
2024-10-12 21:00 | 3359.43 | 1.0777 | 84.6382 | 74.6386 | 984.5517
2024-10-13 22:00 | 3114.44 | 1 | 87.1466 | 74.6386 | 912.7523
2024-10-14 23:00 | 3143.38 | 1 | 75.4939 | 74.6386 | 921.2337
2024-10-16 | 0 | 0 | 76.9639 | 74.6386 | 0
2024-10-17 01:00 | -727.118 | 2.1292 | 75.8844 | 74.6386 | -213.0973
2024-10-18 02:00 | -1141.78 | 3.052 | 75.5915 | 74.6386 | -334.6227
2024-10-19 03:00 | -1070.41 | 2.8187 | 75.4292 | 74.6386 | -313.7062
2024-10-20 04:00 | -1198.74 | 3.1414 | 75.3134 | 74.6386 | -351.316
2024-10-21 05:00 | -867.37 | 2.3419 | 75.2166 | 74.6386 | -254.2011
2024-10-22 06:00 | -543.575 | 1.646 | 75.2707 | 74.6386 | -159.3061
2024-10-23 07:00 | 1299.98 | 1 | 75.4133 | 74.6386 | 380.9865
2024-10-24 08:00 | 3455.38 | 1.1237 | 83.434 | 74.6386 | 1012.6719
2024-10-25 09:00 | 5612.89 | 1.7164 | 84.0909 | 74.6386 | 1644.9757
2024-10-26 10:00 | 8037.79 | 2.6488 | 83.7992 | 74.6386 | 2355.6437
2024-10-27 11:00 | 10354.6 | 3.4128 | 84.1296 | 74.6386 | 3034.6337
2024-10-28 12:00 | 11539.7 | 3.854 | 84.4335 | 74.6386 | 3381.9522
2024-10-29 13:00 | 12241 | 4.0728 | 84.804 | 74.6386 | 3587.483
2024-10-30 14:00 | 12096.3 | 3.9749 | 85.179 | 74.6386 | 3545.0756
2024-10-31 15:00 | 12887.8 | 4.1508 | 85.5257 | 74.6386 | 3777.0413
2024-11-01 16:00 | 13510.7 | 4.3139 | 85.8116 | 74.6386 | 3959.5953
2024-11-02 17:00 | 12745.6 | 4.1191 | 85.9326 | 74.6386 | 3735.3666
2024-11-03 18:00 | 11266 | 3.5726 | 86.1865 | 74.6386 | 3301.7387
2024-11-04 19:00 | 9847.05 | 3.076 | 86.3026 | 74.6386 | 2885.8855
2024-11-05 20:00 | 8952.95 | 2.7574 | 86.3611 | 74.6386 | 2623.8506
2024-11-06 21:00 | 7107.29 | 2.0895 | 86.6649 | 74.6386 | 2082.9411
2024-11-07 22:00 | 6346.63 | 1.8458 | 86.5852 | 74.6386 | 1860.0136
2024-11-08 23:00 | 4014.53 | 1.1727 | 86.3988 | 74.6386 | 1176.5426
2024-11-10 | 3260.91 | 1 | 86.2737 | 74.6386 | 955.6784
2024-11-11 01:00 | 3242.23 | 1 | 88.6591 | 74.6386 | 950.2038
2024-11-12 02:00 | 3236.11 | 1 | 90.7085 | 74.6386 | 948.4102
2024-11-13 03:00 | 3151.22 | 1 | 89.8897 | 74.6386 | 923.5314
2024-11-14 04:00 | 3242.07 | 1 | 87.4085 | 74.6386 | 950.1569
2024-11-15 05:00 | 3231.39 | 1 | 85.5578 | 74.6386 | 947.0269
2024-11-16 06:00 | 4383.24 | 1.383 | 85.034 | 74.6386 | 1284.6008
2024-11-17 07:00 | 5424.45 | 1.7656 | 84.8702 | 74.6386 | 1589.7494
2024-11-18 08:00 | 6147.66 | 1.9457 | 85.1764 | 74.6386 | 1801.7013
2024-11-19 09:00 | 6414.65 | 2.0495 | 85.2076 | 74.6386 | 1879.9483
2024-11-20 10:00 | 6805.1 | 2.2214 | 85.1239 | 74.6386 | 1994.3779
2024-11-21 11:00 | 7535.1 | 2.411 | 85.3547 | 74.6386 | 2208.3198
2024-11-22 12:00 | 7503.04 | 2.3856 | 85.505 | 74.6386 | 2198.924
2024-11-23 13:00 | 6852.71 | 2.0882 | 85.8811 | 74.6386 | 2008.3311
2024-11-24 14:00 | 6259.47 | 1.9575 | 85.6631 | 74.6386 | 1834.4696
2024-11-25 15:00 | 5947.7 | 1.9172 | 85.3887 | 74.6386 | 1743.0988
2024-11-26 16:00 | 7286.27 | 2.4484 | 85.0392 | 74.6386 | 2135.3949
2024-11-27 17:00 | 7761.37 | 2.5554 | 85.2486 | 74.6386 | 2274.633
2024-11-28 18:00 | 7793.43 | 2.5235 | 85.4374 | 74.6386 | 2284.0289
2024-11-29 19:00 | 6874.6 | 2.1545 | 85.7195 | 74.6386 | 2014.7464
2024-11-30 20:00 | 6374.86 | 1.914 | 86.0195 | 74.6386 | 1868.287
2024-12-01 21:00 | 4412.75 | 1.3338 | 85.9388 | 74.6386 | 1293.2494
2024-12-02 22:00 | 3514.75 | 1.1118 | 85.4313 | 74.6386 | 1030.0715
2024-12-03 23:00 | 3029.83 | 1 | 76.3324 | 74.6386 | 887.9555
2024-12-05 | 3125.94 | 1 | 76.1681 | 74.6386 | 916.1226
2024-12-06 01:00 | 2825.64 | 1 | 76.2508 | 74.6386 | 828.1133
2024-12-07 02:00 | 531.52 | 1 | 77.2907 | 74.6386 | 155.7731
2024-12-08 03:00 | -3.2352 | 0.54002 | 77.3439 | 74.6386 | -0.94815
2024-12-09 04:00 | 2157.39 | 1 | 76.1308 | 74.6386 | 632.2686
2024-12-10 05:00 | 1682.5 | 1 | 76.4211 | 74.6386 | 493.0921
2024-12-11 06:00 | 2431.51 | 1 | 76.0203 | 74.6386 | 712.6052
2024-12-12 07:00 | 2893.35 | 1 | 75.791 | 74.6386 | 847.9572
2024-12-13 08:00 | 2951.26 | 1 | 85.0674 | 74.6386 | 864.9289
2024-12-14 09:00 | 4014.54 | 1.3041 | 84.5349 | 74.6386 | 1176.5455
2024-12-15 10:00 | 4883.99 | 1.6143 | 84.4772 | 74.6386 | 1431.3562
2024-12-16 11:00 | 4892.92 | 1.5401 | 84.9358 | 74.6386 | 1433.9733
2024-12-17 12:00 | 5072.66 | 1.5876 | 85.019 | 74.6386 | 1486.6499
2024-12-18 13:00 | 4797.56 | 1.5422 | 84.8522 | 74.6386 | 1406.026
2024-12-19 14:00 | 4791.73 | 1.5315 | 84.9166 | 74.6386 | 1404.3174
2024-12-20 15:00 | 4398.61 | 1.2923 | 85.582 | 74.6386 | 1289.1053
2024-12-21 16:00 | 5881.36 | 1.9538 | 84.6119 | 74.6386 | 1723.6565
2024-12-22 17:00 | 6096.06 | 1.9669 | 84.9125 | 74.6386 | 1786.5788
2024-12-23 18:00 | 5797.49 | 1.7903 | 85.3048 | 74.6386 | 1699.0766
2024-12-24 19:00 | 4538.21 | 1.4265 | 85.1844 | 74.6386 | 1330.0181
2024-12-25 20:00 | 3579.97 | 1.1327 | 85.0642 | 74.6386 | 1049.1856
2024-12-26 21:00 | 3175.16 | 1 | 75.9617 | 74.6386 | 930.5475
2024-12-27 22:00 | 3101.92 | 1 | 75.913 | 74.6386 | 909.083
2024-12-28 23:00 | 0 | 0 | 77.3543 | 74.6386 | 0
2024-12-30 | -355.324 | 1.2105 | 76.3818 | 74.6386 | -104.1352
2024-12-31 01:00 | -507.117 | 1.6325 | 76.1563 | 74.6386 | -148.6213
2025-01-01 02:00 | -599.218 | 1.8168 | 76.0048 | 74.6386 | -175.6135
2025-01-02 03:00 | -584.235 | 1.7699 | 75.9125 | 74.6386 | -171.2224
2025-01-03 04:00 | -374.822 | 1.2886 | 75.9054 | 74.6386 | -109.8495
2025-01-04 05:00 | 0 | 1 | 76.5517 | 74.6386 | 0
2025-01-05 06:00 | 1841.8 | 1 | 75.6429 | 74.6386 | 539.7783
2025-01-06 07:00 | 2786.7 | 1 | 84.9565 | 74.6386 | 816.7012
2025-01-07 08:00 | 5179.07 | 1.684 | 84.0358 | 74.6386 | 1517.8356
2025-01-08 09:00 | 4556.89 | 1.4568 | 84.3946 | 74.6386 | 1335.4926
2025-01-09 10:00 | 5786.39 | 1.9068 | 84.2583 | 74.6386 | 1695.8235
2025-01-10 11:00 | 8309.24 | 2.9174 | 83.9814 | 74.6386 | 2435.1979
2025-01-11 12:00 | 9799 | 3.4621 | 84.2447 | 74.6386 | 2871.8034
2025-01-12 13:00 | 10947 | 3.7762 | 84.7112 | 74.6386 | 3208.249
2025-01-13 14:00 | 11801.5 | 3.9226 | 85.2369 | 74.6386 | 3458.6782
2025-01-14 15:00 | 12002.9 | 3.9368 | 85.6079 | 74.6386 | 3517.7027
2025-01-15 16:00 | 12220 | 3.9849 | 85.8683 | 74.6386 | 3581.3285
2025-01-16 17:00 | 11738.7 | 3.7736 | 86.149 | 74.6386 | 3440.2734
2025-01-17 18:00 | 10209.5 | 3.2567 | 86.309 | 74.6386 | 2992.1091
2025-01-18 19:00 | 8788.69 | 2.7242 | 86.5087 | 74.6386 | 2575.7108
2025-01-19 20:00 | 7579.29 | 2.3426 | 86.4433 | 74.6386 | 2221.2706
2025-01-20 21:00 | 5517.24 | 1.5883 | 86.9104 | 74.6386 | 1616.9434
2025-01-21 22:00 | 4581.54 | 1.3576 | 86.48 | 74.6386 | 1342.7168
2025-01-22 23:00 | 3161.86 | 1 | 90.7109 | 74.6386 | 926.6497
2025-01-24 | 3234.19 | 1 | 76.5535 | 74.6386 | 947.8475
2025-01-25 01:00 | 3149.29 | 1 | 76.4749 | 74.6386 | 922.9658
2025-01-26 02:00 | 3158.72 | 1 | 76.3806 | 74.6386 | 925.7295
2025-01-27 03:00 | 3136.15 | 1 | 76.3295 | 74.6386 | 919.1148
2025-01-28 04:00 | 3227.33 | 1 | 76.2295 | 74.6386 | 945.8371
2025-01-29 05:00 | 3301.47 | 1 | 76.1655 | 74.6386 | 967.5653
2025-01-30 06:00 | 3216.12 | 1 | 87.1238 | 74.6386 | 942.5517
2025-01-31 07:00 | 3295.93 | 1 | 85.515 | 74.6386 | 965.9417
2025-02-01 08:00 | 4013.54 | 1.2282 | 85.4101 | 74.6386 | 1176.2525
2025-02-02 09:00 | 4505.47 | 1.3704 | 85.4966 | 74.6386 | 1320.4229
2025-02-03 10:00 | 6128.67 | 1.9631 | 85.1527 | 74.6386 | 1796.1359
2025-02-04 11:00 | 6028.76 | 1.9969 | 85.0503 | 74.6386 | 1766.8551
2025-02-05 12:00 | 7385.25 | 2.6212 | 84.6388 | 74.6386 | 2164.4031
2025-02-06 13:00 | 9897.25 | 3.427 | 84.9415 | 74.6386 | 2900.5976
2025-02-07 14:00 | 10413.1 | 3.5985 | 85.2289 | 74.6386 | 3051.7784
2025-02-08 15:00 | 10551.9 | 3.549 | 85.6179 | 74.6386 | 3092.4566
2025-02-09 16:00 | 12108.5 | 4.0038 | 85.8598 | 74.6386 | 3548.6511
2025-02-10 17:00 | 11547.1 | 3.6852 | 86.347 | 74.6386 | 3384.121
2025-02-11 18:00 | 9963.71 | 3.195 | 86.4376 | 74.6386 | 2920.0752
2025-02-12 19:00 | 9129.7 | 2.7623 | 86.8487 | 74.6386 | 2675.6509
2025-02-13 20:00 | 8133.42 | 2.4841 | 86.7377 | 74.6386 | 2383.6701
2025-02-14 21:00 | 6295.1 | 1.7927 | 87.248 | 74.6386 | 1844.9117
2025-02-15 22:00 | 4973.13 | 1.5236 | 86.4929 | 74.6386 | 1457.4805
2025-02-16 23:00 | 3115.77 | 1 | 89.2257 | 74.6386 | 913.142
2025-02-18 | 3113.42 | 1 | 76.8711 | 74.6386 | 912.4533
2025-02-19 01:00 | 2999.16 | 1 | 76.7831 | 74.6386 | 878.967
2025-02-20 02:00 | 2971.98 | 1 | 76.6873 | 74.6386 | 871.0014
2025-02-21 03:00 | 0 | 0 | 78.0374 | 74.6386 | 0
2025-02-22 04:00 | 234.58 | 1 | 77.6226 | 74.6386 | 68.7486
2025-02-23 05:00 | -191.64 | 0.96383 | 77.1012 | 74.6386 | -56.1641
2025-02-24 06:00 | -422.797 | 1.4476 | 76.74 | 74.6386 | -123.9096
2025-02-25 07:00 | 2396.8 | 1 | 76.1298 | 74.6386 | 702.4327
2025-02-26 08:00 | 3368.07 | 1.162 | 84.2381 | 74.6386 | 987.0839
2025-02-27 09:00 | 4484.65 | 1.4689 | 84.7131 | 74.6386 | 1314.3212
2025-02-28 10:00 | 5422.23 | 1.8486 | 84.5455 | 74.6386 | 1589.0987
2025-03-01 11:00 | 7007.48 | 2.2804 | 85.0216 | 74.6386 | 2053.6897
2025-03-02 12:00 | 8527.39 | 2.7829 | 85.2107 | 74.6386 | 2499.1313
2025-03-03 13:00 | 9155.25 | 3.0149 | 85.359 | 74.6386 | 2683.1389
2025-03-04 14:00 | 7754.19 | 2.6046 | 85.387 | 74.6386 | 2272.5288
2025-03-05 15:00 | 7213.18 | 2.4177 | 85.4196 | 74.6386 | 2113.9744
2025-03-06 16:00 | 6137.89 | 2.044 | 85.4536 | 74.6386 | 1798.838
2025-03-07 17:00 | 8542.46 | 2.8664 | 85.3341 | 74.6386 | 2503.5479
2025-03-08 18:00 | 6383.14 | 2.157 | 85.4386 | 74.6386 | 1870.7137
2025-03-09 19:00 | 5737.41 | 1.6887 | 86.3896 | 74.6386 | 1681.4689
2025-03-10 20:00 | 4665.23 | 1.3614 | 86.3634 | 74.6386 | 1367.2439
2025-03-11 21:00 | 3357.6 | 1.0372 | 85.8124 | 74.6386 | 984.0154
2025-03-12 22:00 | 3130.34 | 1 | 87.278 | 74.6386 | 917.4121
2025-03-13 23:00 | 3038.07 | 1 | 90.1308 | 74.6386 | 890.3704
2025-03-15 | 0 | 0 | 77.8014 | 74.6386 | 0
2025-03-16 01:00 | -620.284 | 1.9436 | 76.7416 | 74.6386 | -181.7873
2025-03-17 02:00 | -1017.98 | 2.7534 | 76.3932 | 74.6386 | -298.3405
2025-03-18 03:00 | -1288.4 | 3.3249 | 76.2 | 74.6386 | -377.5928
2025-03-19 04:00 | -1557.2 | 3.9133 | 76.0352 | 74.6386 | -456.3703
2025-03-20 05:00 | -1709.33 | 4.2305 | 75.8639 | 74.6386 | -500.9552
2025-03-21 06:00 | -1738.6 | 4.279 | 75.7561 | 74.6386 | -509.5334
2025-03-22 07:00 | -947.315 | 2.4266 | 75.7008 | 74.6386 | -277.6306
2025-03-23 08:00 | -307.11 | 1.0806 | 75.9297 | 74.6386 | -90.0051
2025-03-24 09:00 | -623.17 | 1.9156 | 75.8401 | 74.6386 | -182.6331
2025-03-25 10:00 | -497.995 | 1.5642 | 75.8024 | 74.6386 | -145.9479
2025-03-26 11:00 | -190.073 | 0.87629 | 75.9929 | 74.6386 | -55.7049
2025-03-27 12:00 | -242.134 | 1.0492 | 75.9477 | 74.6386 | -70.9625
2025-03-28 13:00 | -88.0359 | 0.67924 | 76.1467 | 74.6386 | -25.8008
2025-03-29 14:00 | 86.7891 | 1 | 76.3766 | 74.6386 | 25.4354
2025-03-30 15:00 | 353.424 | 1 | 76.2294 | 74.6386 | 103.5783
2025-03-31 16:00 | 1354.28 | 1 | 75.7393 | 74.6386 | 396.9003
2025-04-01 17:00 | 3079.21 | 1.0194 | 83.5976 | 74.6386 | 902.4274
2025-04-02 18:00 | 3090.26 | 1 | 88.2684 | 74.6386 | 905.6658
2025-04-03 19:00 | 3236.38 | 1 | 75.1074 | 74.6386 | 948.4893
2025-04-04 20:00 | 3132.13 | 1 | 75.2174 | 74.6386 | 917.9367
2025-04-05 21:00 | 3103.27 | 1 | 75.2823 | 74.6386 | 909.4787
2025-04-06 22:00 | 1416.37 | 1 | 76.1361 | 74.6386 | 415.0971
2025-04-07 23:00 | 0 | 0 | 76.7163 | 74.6386 | 0
2025-04-09 | -844.289 | 2.3696 | 75.7258 | 74.6386 | -247.4367
2025-04-10 01:00 | -1015.62 | 2.7397 | 75.5585 | 74.6386 | -297.6488
2025-04-11 02:00 | -1025.25 | 2.7365 | 75.4583 | 74.6386 | -300.4711
2025-04-12 03:00 | -994.684 | 2.667 | 75.3967 | 74.6386 | -291.5131
2025-04-13 04:00 | -737.258 | 2.0706 | 75.3924 | 74.6386 | -216.069
2025-04-14 05:00 | -450.224 | 1.4462 | 75.4808 | 74.6386 | -131.9476
2025-04-15 06:00 | 55.8665 | 1 | 76.1972 | 74.6386 | 16.3729
2025-04-16 07:00 | 1941.46 | 1 | 75.309 | 74.6386 | 568.9858
2025-04-17 08:00 | 2894.24 | 1 | 74.9863 | 74.6386 | 848.218
2025-04-18 09:00 | 3085.29 | 1 | 75.0336 | 74.6386 | 904.2092
2025-04-19 10:00 | 3110.29 | 1 | 75.1134 | 74.6386 | 911.536
2025-04-20 11:00 | 3227.99 | 1 | 75.1253 | 74.6386 | 946.0305
2025-04-21 12:00 | 3112.79 | 1 | 86.6507 | 74.6386 | 912.2687
2025-04-22 13:00 | 3246.71 | 1 | 75.2103 | 74.6386 | 951.5168
2025-04-23 14:00 | 3138.99 | 1 | 75.2938 | 74.6386 | 919.9472
2025-04-24 15:00 | 3135.06 | 1 | 87.9779 | 74.6386 | 918.7954
2025-04-25 16:00 | 4315.8 | 1.3521 | 84.3853 | 74.6386 | 1264.8361
2025-04-26 17:00 | 4989.03 | 1.538 | 84.604 | 74.6386 | 1462.1404
2025-04-27 18:00 | 5405.69 | 1.7176 | 84.4852 | 74.6386 | 1584.2514
2025-04-28 19:00 | 4486.22 | 1.425 | 84.5756 | 74.6386 | 1314.7813
2025-04-29 20:00 | 3965.2 | 1.2563 | 84.5852 | 74.6386 | 1162.0854
2025-04-30 21:00 | 3119.8 | 1 | 75.5855 | 74.6386 | 914.3231
2025-05-01 22:00 | 3115.11 | 1 | 75.5263 | 74.6386 | 912.9486
2025-05-02 23:00 | 0 | 0 | 76.9998 | 74.6386 | 0
2025-05-04 | 44.1214 | 1 | 76.7323 | 74.6386 | 12.9307
2025-05-05 01:00 | -108.248 | 0.77733 | 76.2916 | 74.6386 | -31.7244
2025-05-06 02:00 | -138.981 | 0.81762 | 76.1418 | 74.6386 | -40.7313
2025-05-07 03:00 | -196.177 | 0.94749 | 75.9901 | 74.6386 | -57.4938
2025-05-08 04:00 | 58.6195 | 1 | 76.3808 | 74.6386 | 17.1797
2025-05-09 05:00 | 465.659 | 1 | 76.1685 | 74.6386 | 136.4712
2025-05-10 06:00 | 1962.6 | 1 | 75.4493 | 74.6386 | 575.1813
2025-05-11 07:00 | 2700.45 | 1 | 86.3358 | 74.6386 | 791.4238
2025-05-12 08:00 | 3565.09 | 1.2901 | 83.1289 | 74.6386 | 1044.8247
2025-05-13 09:00 | 4038.9 | 1.4445 | 83.3252 | 74.6386 | 1183.6847
2025-05-14 10:00 | 6263.75 | 2.2004 | 83.5489 | 74.6386 | 1835.7239
2025-05-15 11:00 | 6741.11 | 2.3027 | 83.995 | 74.6386 | 1975.6243
2025-05-16 12:00 | 7270.26 | 2.4253 | 84.3523 | 74.6386 | 2130.7029
2025-05-17 13:00 | 8037.3 | 2.6578 | 84.5771 | 74.6386 | 2355.5001
2025-05-18 14:00 | 4620.41 | 1.3901 | 85.471 | 74.6386 | 1354.1085
2025-05-19 15:00 | 6365.51 | 2.1604 | 84.4611 | 74.6386 | 1865.5468
2025-05-20 16:00 | 6553.27 | 2.2063 | 84.5913 | 74.6386 | 1920.5739
2025-05-21 17:00 | 5612.49 | 1.865 | 84.7687 | 74.6386 | 1644.8584
2025-05-22 18:00 | 4632.86 | 1.4604 | 85.113 | 74.6386 | 1357.7572
2025-05-23 19:00 | 3053.17 | 1 | 85.0848 | 74.6386 | 894.7958
2025-05-24 20:00 | 3106.88 | 1 | 75.8758 | 74.6386 | 910.5366
2025-05-25 21:00 | 0 | 0 | 77.2996 | 74.6386 | 0
2025-05-26 22:00 | -494.935 | 1.6619 | 76.2956 | 74.6386 | -145.0511
2025-05-27 23:00 | -1458.81 | 3.8165 | 75.8805 | 74.6386 | -427.535
2025-05-29 | -2035.63 | 5.0166 | 75.6229 | 74.6386 | -596.5843
2025-05-30 01:00 | -2244.79 | 5.4267 | 75.4145 | 74.6386 | -657.883
2025-05-31 02:00 | -2337.38 | 5.6223 | 75.2619 | 74.6386 | -685.0185
2025-06-01 03:00 | -2355.13 | 5.6554 | 75.1539 | 74.6386 | -690.2205
2025-06-02 04:00 | -2235.4 | 5.3745 | 75.0581 | 74.6386 | -655.1311
2025-06-03 05:00 | -2092.25 | 5.0611 | 74.9952 | 74.6386 | -613.1779
2025-06-04 06:00 | -1767.36 | 4.3186 | 74.9513 | 74.6386 | -517.9621
2025-06-05 07:00 | -1266.26 | 3.1941 | 74.9501 | 74.6386 | -371.1042
2025-06-06 08:00 | -494.472 | 1.4672 | 75.0797 | 74.6386 | -144.9154
2025-06-07 09:00 | -616.492 | 1.8859 | 75.1461 | 74.6386 | -180.676
2025-06-08 10:00 | -398.784 | 1.3445 | 75.2101 | 74.6386 | -116.8721
2025-06-09 11:00 | 2756.84 | 1 | 74.581 | 74.6386 | 807.95
2025-06-10 12:00 | 2915.57 | 1 | 86.8123 | 74.6386 | 854.4692
2025-06-11 13:00 | 3154.64 | 1 | 85.6318 | 74.6386 | 924.5337
2025-06-12 14:00 | 3012.32 | 1 | 74.9032 | 74.6386 | 882.8238
2025-06-13 15:00 | 3040.95 | 1 | 74.9533 | 74.6386 | 891.2145
2025-06-14 16:00 | 3133.72 | 1 | 74.9666 | 74.6386 | 918.4027
2025-06-15 17:00 | 3066.83 | 1 | 75.0249 | 74.6386 | 898.7991
2025-06-16 18:00 | 3113.7 | 1 | 75.0202 | 74.6386 | 912.5354
2025-06-17 19:00 | 0 | 0 | 76.5464 | 74.6386 | 0
2025-06-18 20:00 | -278.007 | 1.0756 | 75.7184 | 74.6386 | -81.4758
2025-06-19 21:00 | -1248.73 | 3.3863 | 75.3326 | 74.6386 | -365.9666
2025-06-20 22:00 | -1673.39 | 4.2213 | 75.1367 | 74.6386 | -490.4222
2025-06-21 23:00 | -2530.55 | 6.197 | 74.9713 | 74.6386 | -741.631
2025-06-23 | -3037.4 | 6.5195 | 74.6672 | 74.6386 | -890.1741
2025-06-24 01:00 | -3289.88 | 6.5195 | 74.4438 | 74.6386 | -964.1687
2025-06-25 02:00 | -3458.98 | 6.5195 | 74.2701 | 74.6386 | -1013.727
2025-06-26 03:00 | -3473.47 | 6.5195 | 74.1701 | 74.6386 | -1017.9736
2025-06-27 04:00 | -3343.94 | 6.5195 | 74.1349 | 74.6386 | -980.0121
2025-06-28 05:00 | -3318.88 | 6.5195 | 74.0859 | 74.6386 | -972.6677
2025-06-29 06:00 | -2881.04 | 6.5195 | 74.1874 | 74.6386 | -844.3495
2025-06-30 07:00 | -2185.22 | 5.2366 | 74.2371 | 74.6386 | -640.4248
2025-07-01 08:00 | -1339.55 | 3.317 | 74.2981 | 74.6386 | -392.5834
2025-07-02 09:00 | -442.882 | 1.3441 | 74.5432 | 74.6386 | -129.7959
2025-07-03 10:00 | 2720.26 | 1 | 74.1043 | 74.6386 | 797.2295
2025-07-04 11:00 | 3105.61 | 1 | 83.2665 | 74.6386 | 910.1644
2025-07-05 12:00 | 4713.43 | 1.5027 | 83.3128 | 74.6386 | 1381.37
2025-07-06 13:00 | 5454.65 | 1.752 | 83.4886 | 74.6386 | 1598.6001
2025-07-07 14:00 | 6211.81 | 1.996 | 83.7101 | 74.6386 | 1820.5018
2025-07-08 15:00 | 6673.82 | 2.1599 | 83.8717 | 74.6386 | 1955.9036
2025-07-09 16:00 | 7571.51 | 2.4596 | 84.0122 | 74.6386 | 2218.9905
2025-07-10 17:00 | 7127.44 | 2.3051 | 84.2475 | 74.6386 | 2088.8465
2025-07-11 18:00 | 5420.38 | 1.737 | 84.4261 | 74.6386 | 1588.5566
2025-07-12 19:00 | 3503.51 | 1.1271 | 84.3751 | 74.6386 | 1026.7774
2025-07-13 20:00 | 3131.36 | 1 | 88.8405 | 74.6386 | 917.711
2025-07-14 21:00 | 0 | 0 | 76.8435 | 74.6386 | 0
2025-07-15 22:00 | -430.418 | 1.4698 | 75.8739 | 74.6386 | -126.1431
2025-07-16 23:00 | -1460.3 | 3.8501 | 75.4771 | 74.6386 | -427.9717
2025-07-18 | -1923.21 | 4.7696 | 75.2388 | 74.6386 | -563.6372
2025-07-19 01:00 | -2254.28 | 5.4901 | 75.0663 | 74.6386 | -660.6643
2025-07-20 02:00 | -2386.26 | 5.7555 | 74.9116 | 74.6386 | -699.3438
2025-07-21 03:00 | -2505.3 | 6.0244 | 74.8096 | 74.6386 | -734.231
2025-07-22 04:00 | -2687.75 | 6.4455 | 74.7082 | 74.6386 | -787.7018
2025-07-23 05:00 | -2426.1 | 5.7923 | 74.6125 | 74.6386 | -711.0197
2025-07-24 06:00 | -1887.05 | 4.5622 | 74.5751 | 74.6386 | -553.0398
2025-07-25 07:00 | -1197.79 | 3.0242 | 74.6144 | 74.6386 | -351.0376
2025-07-26 08:00 | 52.5316 | 1 | 75.5543 | 74.6386 | 15.3955
2025-07-27 09:00 | 2832.71 | 1 | 74.32 | 74.6386 | 830.1854
2025-07-28 10:00 | 4177.3 | 1.3928 | 83.0557 | 74.6386 | 1224.2458
2025-07-29 11:00 | 6055.73 | 2.0451 | 83.1995 | 74.6386 | 1774.7593
2025-07-30 12:00 | 8033.32 | 2.6157 | 83.7425 | 74.6386 | 2354.3337
2025-07-31 13:00 | 8817.15 | 2.8876 | 84.0379 | 74.6386 | 2584.0516
2025-08-01 14:00 | 9398.78 | 3.0511 | 84.3831 | 74.6386 | 2754.5105
2025-08-02 15:00 | 9592.63 | 3.1273 | 84.579 | 74.6386 | 2811.3223
2025-08-03 16:00 | 10353.9 | 3.3905 | 84.7353 | 74.6386 | 3034.4286
2025-08-04 17:00 | 9866.89 | 3.2164 | 84.9732 | 74.6386 | 2891.7
2025-08-05 18:00 | 7926.3 | 2.4645 | 85.443 | 74.6386 | 2322.9692
2025-08-06 19:00 | 5742.01 | 1.8139 | 85.2934 | 74.6386 | 1682.817
2025-08-07 20:00 | 4106.09 | 1.3 | 85.1387 | 74.6386 | 1203.3762
2025-08-08 21:00 | 3102.06 | 1 | 76.0049 | 74.6386 | 909.124
2025-08-09 22:00 | 149.166 | 1 | 77.2708 | 74.6386 | 43.7162
2025-08-10 23:00 | -828.088 | 2.4506 | 76.2208 | 74.6386 | -242.6886
2025-08-12 | -1766.56 | 4.4806 | 75.8191 | 74.6386 | -517.7276
2025-08-13 01:00 | -2022.39 | 4.9365 | 75.5548 | 74.6386 | -592.704
2025-08-14 02:00 | -2287.78 | 5.5377 | 75.3656 | 74.6386 | -670.4821
2025-08-15 03:00 | -2338.91 | 5.6212 | 75.1953 | 74.6386 | -685.4669
2025-08-16 04:00 | -2482.53 | 5.9633 | 75.0738 | 74.6386 | -727.5577
2025-08-17 05:00 | -2519.48 | 6.0312 | 74.9593 | 74.6386 | -738.3867
2025-08-18 06:00 | -2524.46 | 6.0435 | 74.8715 | 74.6386 | -739.8462
2025-08-19 07:00 | -1001.71 | 2.4364 | 74.8149 | 74.6386 | -293.5722
2025-08-20 08:00 | 2230.41 | 1 | 74.7655 | 74.6386 | 653.6686
2025-08-21 09:00 | 2919.6 | 1 | 84.5506 | 74.6386 | 855.6503
2025-08-22 10:00 | 4700.08 | 1.6502 | 83.0011 | 74.6386 | 1377.4575
2025-08-23 11:00 | 6786.88 | 2.3087 | 83.4451 | 74.6386 | 1989.0382
2025-08-24 12:00 | 8267.32 | 2.759 | 83.8897 | 74.6386 | 2422.9123
2025-08-25 13:00 | 9002.14 | 2.9261 | 84.3791 | 74.6386 | 2638.2668
2025-08-26 14:00 | 9132.35 | 3.0545 | 84.4036 | 74.6386 | 2676.4276
2025-08-27 15:00 | 9595.5 | 3.1275 | 84.7657 | 74.6386 | 2812.1635
2025-08-28 16:00 | 9431.72 | 3.0486 | 84.9937 | 74.6386 | 2764.1643
2025-08-29 17:00 | 11006.9 | 3.5607 | 85.1021 | 74.6386 | 3225.804
2025-08-30 18:00 | 8906.11 | 2.7992 | 85.5398 | 74.6386 | 2610.1232
2025-08-31 19:00 | 7329.87 | 2.19 | 85.9411 | 74.6386 | 2148.1728
2025-09-01 20:00 | 5661.61 | 1.7514 | 85.5816 | 74.6386 | 1659.2541
2025-09-02 21:00 | 4348.45 | 1.3427 | 85.4724 | 74.6386 | 1274.4049
2025-09-03 22:00 | 3109.37 | 1 | 85.9024 | 74.6386 | 911.2664
2025-09-04 23:00 | 3061.69 | 1 | 88.3122 | 74.6386 | 897.2928
2025-09-06 | 0 | 0 | 77.382 | 74.6386 | 0
2025-09-07 01:00 | -1080.11 | 2.9369 | 76.2153 | 74.6386 | -316.549
2025-09-08 02:00 | -1356.98 | 3.4814 | 75.9051 | 74.6386 | -397.6916
2025-09-09 03:00 | -1363.77 | 3.4615 | 75.7241 | 74.6386 | -399.6815
2025-09-10 04:00 | -1663.56 | 4.1713 | 75.5879 | 74.6386 | -487.5413
2025-09-11 05:00 | -1901.24 | 4.6827 | 75.4191 | 74.6386 | -557.1984
2025-09-12 06:00 | -2231.44 | 5.4288 | 75.2981 | 74.6386 | -653.9705
2025-09-13 07:00 | -748.484 | 1.8816 | 75.2237 | 74.6386 | -219.359
2025-09-14 08:00 | 2371.03 | 1 | 75.0453 | 74.6386 | 694.8803
2025-09-15 09:00 | 2926.35 | 1 | 86.1262 | 74.6386 | 857.6285
2025-09-16 10:00 | 4401 | 1.4701 | 83.6294 | 74.6386 | 1289.8058
2025-09-17 11:00 | 6571.4 | 2.147 | 83.9536 | 74.6386 | 1925.8872
2025-09-18 12:00 | 7603.89 | 2.4871 | 84.2307 | 74.6386 | 2228.4802
2025-09-19 13:00 | 7634.92 | 2.5255 | 84.4011 | 74.6386 | 2237.5742
2025-09-20 14:00 | 8117.86 | 2.6264 | 84.7027 | 74.6386 | 2379.1099
2025-09-21 15:00 | 7933.29 | 2.5258 | 84.9695 | 74.6386 | 2325.0178
2025-09-22 16:00 | 7520.26 | 2.43 | 84.9618 | 74.6386 | 2203.9706
2025-09-23 17:00 | 8975.38 | 2.9503 | 84.8729 | 74.6386 | 2630.4242
2025-09-24 18:00 | 7134.48 | 2.2889 | 85.2137 | 74.6386 | 2090.9097
2025-09-25 19:00 | 5758.33 | 1.821 | 85.3075 | 74.6386 | 1687.5999
2025-09-26 20:00 | 4598.4 | 1.4437 | 85.258 | 74.6386 | 1347.658
2025-09-27 21:00 | 3138.93 | 1 | 85.0986 | 74.6386 | 919.9296
2025-09-28 22:00 | 3199.45 | 1 | 88.3379 | 74.6386 | 937.6662
2025-09-29 23:00 | 3216.29 | 1 | 75.8031 | 74.6386 | 942.6016
2025-10-01 | 0 | 0 | 77.3085 | 74.6386 | 0
2025-10-02 01:00 | -771.477 | 2.1132 | 76.1684 | 74.6386 | -226.0976
2025-10-03 02:00 | -1024.21 | 2.7682 | 75.9384 | 74.6386 | -300.1663
2025-10-04 03:00 | -1077.24 | 2.8459 | 75.7862 | 74.6386 | -315.7079
2025-10-05 04:00 | -1014.96 | 2.6977 | 75.6811 | 74.6386 | -297.4554
2025-10-06 05:00 | -1046.43 | 2.7858 | 75.5749 | 74.6386 | -306.6784
2025-10-07 06:00 | -517.321 | 1.5445 | 75.6133 | 74.6386 | -151.6118
2025-10-08 07:00 | -156.496 | 0.8007 | 75.9365 | 74.6386 | -45.8645
2025-10-09 08:00 | 2129.93 | 1 | 75.3696 | 74.6386 | 624.2209
2025-10-10 09:00 | -86.6921 | 0.7476 | 76.2793 | 74.6386 | -25.4069
2025-10-11 10:00 | 2496.41 | 1.0932 | 81.8637 | 74.6386 | 731.6255
2025-10-12 11:00 | 5414.95 | 1.8763 | 83.3908 | 74.6386 | 1586.9652
2025-10-13 12:00 | 7143.92 | 2.4517 | 83.7528 | 74.6386 | 2093.6763
2025-10-14 13:00 | 7699.99 | 2.6199 | 84.0984 | 74.6386 | 2256.6443
2025-10-15 14:00 | 8159.33 | 2.7086 | 84.4599 | 74.6386 | 2391.2636
2025-10-16 15:00 | 8264.44 | 2.7374 | 84.6757 | 74.6386 | 2422.0683
2025-10-17 16:00 | 9394.73 | 3.0804 | 84.8985 | 74.6386 | 2753.3236
2025-10-18 17:00 | 8496.05 | 2.8675 | 84.8728 | 74.6386 | 2489.9465
2025-10-19 18:00 | 7248.22 | 2.3763 | 85.1398 | 74.6386 | 2124.2436
2025-10-20 19:00 | 5420.93 | 1.5956 | 85.9322 | 74.6386 | 1588.7178
2025-10-21 20:00 | 3609.93 | 1.1476 | 85.2124 | 74.6386 | 1057.966
2025-10-22 21:00 | 3001.44 | 1 | 76.1624 | 74.6386 | 879.6352
2025-10-23 22:00 | 0 | 0 | 77.4728 | 74.6386 | 0
2025-10-24 23:00 | -903.044 | 2.4781 | 76.2889 | 74.6386 | -264.6561
2025-10-26 | -1390.46 | 3.5922 | 75.9739 | 74.6386 | -407.5036
2025-10-27 01:00 | -1728.81 | 4.3066 | 75.7516 | 74.6386 | -506.6642
2025-10-28 02:00 | -2189.92 | 5.3442 | 75.5721 | 74.6386 | -641.8022
2025-10-29 03:00 | -2456.76 | 5.9035 | 75.3894 | 74.6386 | -720.0053
2025-10-30 04:00 | -2552.55 | 6.0952 | 75.2476 | 74.6386 | -748.0786
2025-10-31 05:00 | -2484.28 | 5.9249 | 75.1379 | 74.6386 | -728.0706
2025-11-01 06:00 | -2129.93 | 5.1025 | 75.0595 | 74.6386 | -624.2209
2025-11-02 07:00 | -1354.77 | 3.3368 | 75.041 | 74.6386 | -397.0439
2025-11-03 08:00 | 0 | 0 | 76.0077 | 74.6386 | 0
2025-11-04 09:00 | 2921.42 | 1 | 74.6842 | 74.6386 | 856.1837
2025-11-05 10:00 | 3180.55 | 1 | 85.0101 | 74.6386 | 932.1272
2025-11-06 11:00 | 5212.15 | 1.6565 | 83.9492 | 74.6386 | 1527.5304
2025-11-07 12:00 | 6804.54 | 2.2122 | 84.0143 | 74.6386 | 1994.2138
2025-11-08 13:00 | 7540.62 | 2.475 | 84.2177 | 74.6386 | 2209.9376
2025-11-09 14:00 | 7885.93 | 2.6029 | 84.3998 | 74.6386 | 2311.1379
2025-11-10 15:00 | 8214.54 | 2.6765 | 84.6526 | 74.6386 | 2407.444
2025-11-11 16:00 | 9326.11 | 3.0507 | 84.7764 | 74.6386 | 2733.213
2025-11-12 17:00 | 7994.6 | 2.613 | 84.9776 | 74.6386 | 2342.986
2025-11-13 18:00 | 5719.17 | 1.8935 | 84.9241 | 74.6386 | 1676.1233
2025-11-14 19:00 | 3475.76 | 1.1605 | 84.7479 | 74.6386 | 1018.6447
2025-11-15 20:00 | 2939.9 | 1 | 89.7005 | 74.6386 | 861.5996
2025-11-16 21:00 | 0 | 0 | 77.3309 | 74.6386 | 0
2025-11-17 22:00 | -674.9 | 1.9244 | 76.1945 | 74.6386 | -197.7937
2025-11-18 23:00 | -1746.68 | 4.4711 | 75.856 | 74.6386 | -511.9014
2025-11-20 | -2230.67 | 5.4265 | 75.5865 | 74.6386 | -653.7448
2025-11-21 01:00 | -2517.95 | 6.042 | 75.3883 | 74.6386 | -737.9383
2025-11-22 02:00 | -2691.32 | 6.4158 | 75.2178 | 74.6386 | -788.748
2025-11-23 03:00 | -2739.52 | 6.5093 | 75.0918 | 74.6386 | -802.8741
2025-11-24 04:00 | -2845.94 | 6.5195 | 74.941 | 74.6386 | -834.0627
2025-11-25 05:00 | -2658.59 | 6.3254 | 74.8842 | 74.6386 | -779.1558
2025-11-26 06:00 | -2078.88 | 4.9618 | 74.8284 | 74.6386 | -609.2596
2025-11-27 07:00 | -1118.65 | 2.7973 | 74.8676 | 74.6386 | -327.844
2025-11-28 08:00 | 1343.7 | 1 | 75.207 | 74.6386 | 393.7996
2025-11-29 09:00 | 3128.95 | 1 | 74.543 | 74.6386 | 917.0047
2025-11-30 10:00 | 4365.71 | 1.3536 | 83.9321 | 74.6386 | 1279.4633
2025-12-01 11:00 | 5963.33 | 1.8886 | 83.9749 | 74.6386 | 1747.6795
2025-12-02 12:00 | 6364.92 | 2.0831 | 83.9846 | 74.6386 | 1865.3739
2025-12-03 13:00 | 7930.65 | 2.635 | 84.0687 | 74.6386 | 2324.2441
2025-12-04 14:00 | 8373.9 | 2.7628 | 84.3566 | 74.6386 | 2454.1478
2025-12-05 15:00 | 8178.44 | 2.5985 | 84.8215 | 74.6386 | 2396.8642
2025-12-06 16:00 | 9369.63 | 2.9914 | 84.8952 | 74.6386 | 2745.9675
2025-12-07 17:00 | 8704.97 | 2.7803 | 85.0747 | 74.6386 | 2551.1749
2025-12-08 18:00 | 7543.18 | 2.3363 | 85.4071 | 74.6386 | 2210.6878
2025-12-09 19:00 | 5934.46 | 1.824 | 85.4631 | 74.6386 | 1739.2185
2025-12-10 20:00 | 5002.06 | 1.5123 | 85.5004 | 74.6386 | 1465.9591
2025-12-11 21:00 | 3157.56 | 1 | 86.3395 | 74.6386 | 925.3895
2025-12-12 22:00 | 3143.7 | 1 | 75.8932 | 74.6386 | 921.3275
2025-12-13 23:00 | 2719.92 | 1 | 75.9996 | 74.6386 | 797.1299
2025-12-15 | 593.673 | 1 | 76.9471 | 74.6386 | 173.9884
2025-12-16 01:00 | -4.8039 | 0.54642 | 77.0256 | 74.6386 | -1.4079
2025-12-17 02:00 | -60.5627 | 0.64933 | 76.9072 | 74.6386 | -17.7492
2025-12-18 03:00 | -35.7891 | 0.5849 | 76.7945 | 74.6386 | -10.4887
2025-12-19 04:00 | 1293.54 | 1 | 76.0425 | 74.6386 | 379.0992
2025-12-20 05:00 | 2015.92 | 1 | 75.7192 | 74.6386 | 590.8078
2025-12-21 06:00 | 2826.22 | 1 | 75.3976 | 74.6386 | 828.2833
2025-12-22 07:00 | 3143.49 | 1 | 87.22 | 74.6386 | 921.266
2025-12-23 08:00 | 3679.71 | 1.0919 | 84.8989 | 74.6386 | 1078.4165
2025-12-24 09:00 | 3653.79 | 1.1291 | 84.6744 | 74.6386 | 1070.8201
2025-12-25 10:00 | 5450 | 1.7773 | 84.3142 | 74.6386 | 1597.2373
2025-12-26 11:00 | 5255.55 | 1.6776 | 84.6221 | 74.6386 | 1540.2497
2025-12-27 12:00 | 2845.74 | 1 | 84.5839 | 74.6386 | 834.0041
2025-12-28 13:00 | 2985.6 | 1 | 88.7904 | 74.6386 | 874.993
2025-12-29 14:00 | 3116.15 | 1 | 75.584 | 74.6386 | 913.2534
2025-12-30 15:00 | 3189.57 | 1 | 75.545 | 74.6386 | 934.7707
2025-12-31 16:00 | 3393.86 | 1.0574 | 84.6465 | 74.6386 | 994.6422
2026-01-01 17:00 | 3785.21 | 1.2057 | 84.4353 | 74.6386 | 1109.3355
2026-01-02 18:00 | 3971.92 | 1.2584 | 84.499 | 74.6386 | 1164.0548
2026-01-03 19:00 | 3124.7 | 1 | 84.6606 | 74.6386 | 915.7592
2026-01-04 20:00 | 3073.03 | 1 | 88.7836 | 74.6386 | 900.6162
2026-01-05 21:00 | 3001.72 | 1 | 75.5432 | 74.6386 | 879.7173
2026-01-06 22:00 | 0 | 0 | 76.9771 | 74.6386 | 0
2026-01-07 23:00 | -508.109 | 1.585 | 75.974 | 74.6386 | -148.912
2026-01-09 | -824.046 | 2.3478 | 75.7399 | 74.6386 | -241.504
2026-01-10 01:00 | -1055.82 | 2.8345 | 75.5894 | 74.6386 | -309.4303
2026-01-11 02:00 | -751.773 | 2.0886 | 75.5225 | 74.6386 | -220.3229
2026-01-12 03:00 | -945.599 | 2.6007 | 75.4545 | 74.6386 | -277.1277
2026-01-13 04:00 | -731.44 | 2.0615 | 75.4281 | 74.6386 | -214.3639
2026-01-14 05:00 | -530.301 | 1.6335 | 75.4705 | 74.6386 | -155.4159
2026-01-15 06:00 | 201.049 | 1 | 76.125 | 74.6386 | 58.9216
2026-01-16 07:00 | 2019.45 | 1 | 75.2792 | 74.6386 | 591.8424
2026-01-17 08:00 | 3107.63 | 1.1047 | 83.0526 | 74.6386 | 910.7564
2026-01-18 09:00 | 3121.79 | 1 | 88.1759 | 74.6386 | 914.9063
2026-01-19 10:00 | 5497.39 | 1.7353 | 84.1013 | 74.6386 | 1611.126
2026-01-20 11:00 | 6290.99 | 2.0795 | 84.0049 | 74.6386 | 1843.7072
2026-01-21 12:00 | 7595.99 | 2.5406 | 84.1404 | 74.6386 | 2226.1649
2026-01-22 13:00 | 8130.19 | 2.6265 | 84.6125 | 74.6386 | 2382.7235
2026-01-23 14:00 | 9409.25 | 3.1599 | 84.5227 | 74.6386 | 2757.579
2026-01-24 15:00 | 9264.66 | 3.0441 | 84.9243 | 74.6386 | 2715.2038
2026-01-25 16:00 | 10947.5 | 3.669 | 84.9309 | 74.6386 | 3208.3955
2026-01-26 17:00 | 10817 | 3.5199 | 85.3883 | 74.6386 | 3170.1498
2026-01-27 18:00 | 9728.57 | 3.1095 | 85.6876 | 74.6386 | 2851.1624
2026-01-28 19:00 | 8188.81 | 2.5516 | 85.9251 | 74.6386 | 2399.9033
2026-01-29 20:00 | 7019.89 | 2.1895 | 85.8649 | 74.6386 | 2057.3267
2026-01-30 21:00 | 4778.62 | 1.4063 | 86.2536 | 74.6386 | 1400.4753
2026-01-31 22:00 | 3700.39 | 1.1493 | 85.6387 | 74.6386 | 1084.4773
2026-02-01 23:00 | 3191.8 | 1 | 76.2984 | 74.6386 | 935.4242
2026-02-03 | 3118.39 | 1 | 76.2027 | 74.6386 | 913.9099
2026-02-04 01:00 | 3073.64 | 1 | 76.1406 | 74.6386 | 900.795
2026-02-05 02:00 | 0 | 0 | 77.5558 | 74.6386 | 0
2026-02-06 03:00 | -129.45 | 0.72933 | 76.8655 | 74.6386 | -37.9381
2026-02-07 04:00 | -312.539 | 1.216 | 76.4959 | 74.6386 | -91.5961
2026-02-08 05:00 | -319.853 | 1.1982 | 76.3454 | 74.6386 | -93.7397
2026-02-09 06:00 | -334.43 | 1.2345 | 76.2201 | 74.6386 | -98.0118
2026-02-10 07:00 | 1706 | 1 | 82.7761 | 74.6386 | 499.9792
2026-02-11 08:00 | 2899.44 | 1.1329 | 82.8945 | 74.6386 | 849.742
2026-02-12 09:00 | 2823.96 | 1 | 84.3636 | 74.6386 | 827.621
2026-02-13 10:00 | 3577.53 | 1.2002 | 84.0543 | 74.6386 | 1048.4705
2026-02-14 11:00 | 6430.57 | 2.1704 | 84.086 | 74.6386 | 1884.614
2026-02-15 12:00 | 8292.37 | 2.7502 | 84.4763 | 74.6386 | 2430.2537
2026-02-16 13:00 | 9449.25 | 3.0181 | 85.0243 | 74.6386 | 2769.3018
2026-02-17 14:00 | 7682.93 | 2.4277 | 85.3539 | 74.6386 | 2251.6445
2026-02-18 15:00 | 6155.3 | 1.9007 | 85.5734 | 74.6386 | 1803.9404
2026-02-19 16:00 | 5605.77 | 1.7104 | 85.6124 | 74.6386 | 1642.889
2026-02-20 17:00 | 7773.68 | 2.5638 | 84.9836 | 74.6386 | 2278.2407
2026-02-21 18:00 | 6623.52 | 2.067 | 85.5383 | 74.6386 | 1941.1621
2026-02-22 19:00 | 5771.86 | 1.7882 | 85.5759 | 74.6386 | 1691.5652
2026-02-23 20:00 | 4783.92 | 1.4943 | 85.4467 | 74.6386 | 1402.0286
2026-02-24 21:00 | 4299.95 | 1.3573 | 85.305 | 74.6386 | 1260.1909
2026-02-25 22:00 | 3837.15 | 1.2222 | 85.1978 | 74.6386 | 1124.5577
2026-02-26 23:00 | 3498.9 | 1.1164 | 85.1024 | 74.6386 | 1025.4264
2026-02-28 | 2798.38 | 1 | 76.2553 | 74.6386 | 820.1242
2026-03-01 01:00 | 391.825 | 1 | 77.3093 | 74.6386 | 114.8326
2026-03-02 02:00 | 0 | 0 | 77.2675 | 74.6386 | 0
2026-03-03 03:00 | -39.632 | 0.60157 | 77.1582 | 74.6386 | -11.615
2026-03-04 04:00 | -107.901 | 0.75214 | 76.6832 | 74.6386 | -31.6227
2026-03-05 05:00 | -31.8005 | 0.56972 | 76.9667 | 74.6386 | -9.3198
2026-03-06 06:00 | 1739.32 | 1 | 83.8852 | 74.6386 | 509.7444
2026-03-07 07:00 | 3634.38 | 1.3567 | 83.2793 | 74.6386 | 1065.1316
2026-03-08 08:00 | 3918.43 | 1.3213 | 84.1331 | 74.6386 | 1148.3785
2026-03-09 09:00 | 5153.84 | 1.7872 | 84.0429 | 74.6386 | 1510.4414
2026-03-10 10:00 | 5982.88 | 2.0003 | 84.4456 | 74.6386 | 1753.409
2026-03-11 11:00 | 7893.33 | 2.6894 | 84.4683 | 74.6386 | 2313.3067
2026-03-12 12:00 | 9515.42 | 3.1502 | 84.8945 | 74.6386 | 2788.6943
2026-03-13 13:00 | 10059 | 3.3916 | 85.0208 | 74.6386 | 2948.0019
2026-03-14 14:00 | 10816.1 | 3.5059 | 85.5143 | 74.6386 | 3169.886
2026-03-15 15:00 | 11268.1 | 3.7603 | 85.5147 | 74.6386 | 3302.3541
2026-03-16 16:00 | 13133.3 | 4.327 | 85.804 | 74.6386 | 3848.9903
2026-03-17 17:00 | 11987.2 | 3.8727 | 86.2263 | 74.6386 | 3513.1015
2026-03-18 18:00 | 9991.79 | 3.1106 | 86.6042 | 74.6386 | 2928.3046
2026-03-19 19:00 | 8678.39 | 2.7087 | 86.5234 | 74.6386 | 2543.385
2026-03-20 20:00 | 8075.22 | 2.4977 | 86.5112 | 74.6386 | 2366.6134
2026-03-21 21:00 | 7241.85 | 2.2405 | 86.4563 | 74.6386 | 2122.3767
2026-03-22 22:00 | 6650.29 | 2.0123 | 86.5303 | 74.6386 | 1949.0076
2026-03-23 23:00 | 3989.76 | 1.1739 | 86.6538 | 74.6386 | 1169.2832
2026-03-25 | 3267.2 | 1.0011 | 86.0878 | 74.6386 | 957.5218
2026-03-26 01:00 | 3237.14 | 1 | 88.1158 | 74.6386 | 948.7121
2026-03-27 02:00 | 3103.45 | 1 | 88.6106 | 74.6386 | 909.5314
2026-03-28 03:00 | 3132.45 | 1 | 90.9458 | 74.6386 | 918.0305
2026-03-29 04:00 | 3140.69 | 1 | 89.5602 | 74.6386 | 920.4454
2026-03-30 05:00 | 3668.86 | 1.1551 | 85.3633 | 74.6386 | 1075.2367
2026-03-31 06:00 | 3743.48 | 1.1577 | 85.5125 | 74.6386 | 1097.1057
2026-04-01 07:00 | 5325.55 | 1.6508 | 85.4899 | 74.6386 | 1560.7646
2026-04-02 08:00 | 5962.91 | 2.0308 | 84.9086 | 74.6386 | 1747.5564
2026-04-03 09:00 | 7859.03 | 2.5934 | 85.2333 | 74.6386 | 2303.2543
2026-04-04 10:00 | 9321.1 | 3.1429 | 85.2725 | 74.6386 | 2731.7448
2026-04-05 11:00 | 11080.1 | 3.7308 | 85.5122 | 74.6386 | 3247.2568
2026-04-06 12:00 | 12388.4 | 4.0318 | 86.0329 | 74.6386 | 3630.6816
2026-04-07 13:00 | 12766.9 | 4.2352 | 86.1651 | 74.6386 | 3741.609
2026-04-08 14:00 | 13347.9 | 4.3742 | 86.4699 | 74.6386 | 3911.8833
2026-04-09 15:00 | 14813.3 | 4.7711 | 86.7967 | 74.6386 | 4341.3497
2026-04-10 16:00 | 15127.8 | 4.8569 | 87.0835 | 74.6386 | 4433.5205
2026-04-11 17:00 | 14164.1 | 4.5729 | 87.2464 | 74.6386 | 4151.0879
2026-04-12 18:00 | 12443 | 3.7062 | 87.9463 | 74.6386 | 3646.6833
2026-04-13 19:00 | 10498.3 | 3.2744 | 87.5593 | 74.6386 | 3076.748
2026-04-14 20:00 | 8414.84 | 2.4406 | 88.0202 | 74.6386 | 2466.1462
2026-04-15 21:00 | 7102.87 | 2.2062 | 87.2786 | 74.6386 | 2081.6457
2026-04-16 22:00 | 5347.72 | 1.5181 | 87.7897 | 74.6386 | 1567.262
2026-04-17 23:00 | 4352.79 | 1.3569 | 86.7973 | 74.6386 | 1275.6768
2026-04-19 | 3617.42 | 1.1246 | 86.5949 | 74.6386 | 1060.1612
2026-04-20 01:00 | 3030.4 | 1 | 86.6502 | 74.6386 | 888.1226
2026-04-21 02:00 | 3153.77 | 1 | 88.5424 | 74.6386 | 924.2787
2026-04-22 03:00 | 3122.39 | 1 | 86.7437 | 74.6386 | 915.0822
2026-04-23 04:00 | 3144.33 | 1 | 86.0129 | 74.6386 | 921.5122
2026-04-24 05:00 | 3534.85 | 1.1162 | 85.8365 | 74.6386 | 1035.9623
2026-04-25 06:00 | 3759.88 | 1.1771 | 85.8721 | 74.6386 | 1101.9121
2026-04-26 07:00 | 5226.71 | 1.5722 | 86.1639 | 74.6386 | 1531.7975
2026-04-27 08:00 | 5929.35 | 1.8225 | 86.0842 | 74.6386 | 1737.7209
2026-04-28 09:00 | 7553.99 | 2.6426 | 85.2437 | 74.6386 | 2213.8559
2026-04-29 10:00 | 9322.57 | 3.1724 | 85.6017 | 74.6386 | 2732.1756
2026-04-30 11:00 | 11051.1 | 3.6317 | 86.0763 | 74.6386 | 3238.7577
2026-05-01 12:00 | 11945.6 | 3.9519 | 86.2944 | 74.6386 | 3500.9098
2026-05-02 13:00 | 12216.4 | 4.1127 | 86.3993 | 74.6386 | 3580.2734
2026-05-03 14:00 | 13008.9 | 4.2726 | 86.7487 | 74.6386 | 3812.5322
2026-05-04 15:00 | 14472.6 | 4.7347 | 86.9588 | 74.6386 | 4241.5004
2026-05-05 16:00 | 14706.1 | 4.6953 | 87.3718 | 74.6386 | 4309.9325
2026-05-06 17:00 | 13644.9 | 4.3768 | 87.5098 | 74.6386 | 3998.9254
2026-05-07 18:00 | 11187.8 | 3.5526 | 87.639 | 74.6386 | 3278.8205
2026-05-08 19:00 | 9833.42 | 3.0254 | 87.772 | 74.6386 | 2881.8909
2026-05-09 20:00 | 7828.35 | 2.3466 | 87.8582 | 74.6386 | 2294.2629
2026-05-10 21:00 | 6828.21 | 2.0009 | 87.839 | 74.6386 | 2001.1508
2026-05-11 22:00 | 4961.23 | 1.376 | 88.1032 | 74.6386 | 1453.993
2026-05-12 23:00 | 4015.36 | 1.1801 | 87.3702 | 74.6386 | 1176.7859
2026-05-14 | 3426.24 | 1.0513 | 86.8143 | 74.6386 | 1004.1318
2026-05-15 01:00 | 3078.8 | 1 | 86.4223 | 74.6386 | 902.3072
2026-05-16 02:00 | 3148.13 | 1 | 87.0845 | 74.6386 | 922.6258
2026-05-17 03:00 | 3197.83 | 1.0107 | 86.1487 | 74.6386 | 937.1915
2026-05-18 04:00 | 3579.76 | 1.1349 | 86.0419 | 74.6386 | 1049.1241
2026-05-19 05:00 | 4728.31 | 1.4814 | 86.0884 | 74.6386 | 1385.7309
2026-05-20 06:00 | 4841.36 | 1.5353 | 86.052 | 74.6386 | 1418.8626
2026-05-21 07:00 | 5640.87 | 1.8636 | 85.7754 | 74.6386 | 1653.1758
2026-05-22 08:00 | 5391.8 | 1.7207 | 86.0927 | 74.6386 | 1580.1806
2026-05-23 09:00 | 6901.42 | 2.2633 | 85.9072 | 74.6386 | 2022.6065
2026-05-24 10:00 | 6702.97 | 2.071 | 86.4708 | 74.6386 | 1964.4466
2026-05-25 11:00 | 8131.33 | 2.8951 | 85.5001 | 74.6386 | 2383.0576
2026-05-26 12:00 | 9303.5 | 3.1056 | 86.0664 | 74.6386 | 2726.5867
2026-05-27 13:00 | 9794.5 | 3.2749 | 86.2142 | 74.6386 | 2870.4846
2026-05-28 14:00 | 10665.6 | 3.4823 | 86.5184 | 74.6386 | 3125.7788
2026-05-29 15:00 | 11805.1 | 4.0373 | 86.3265 | 74.6386 | 3459.7333
2026-05-30 16:00 | 11649.1 | 4.0212 | 86.4481 | 74.6386 | 3414.0142
2026-05-31 17:00 | 10842.5 | 3.7014 | 86.6237 | 74.6386 | 3177.6231
2026-06-01 18:00 | 8612.79 | 2.8209 | 86.9351 | 74.6386 | 2524.1596
2026-06-02 19:00 | 6706.78 | 2.2566 | 86.6182 | 74.6386 | 1965.5632
2026-06-03 20:00 | 4336.22 | 1.3933 | 86.7673 | 74.6386 | 1270.8206
2026-06-04 21:00 | 3176.8 | 1 | 87.4774 | 74.6386 | 931.0282
2026-06-05 22:00 | 3029.71 | 1 | 77.4228 | 74.6386 | 887.9204
2026-06-06 23:00 | 0 | 0 | 78.7238 | 74.6386 | 0
2026-06-08 | -212.158 | 0.97319 | 77.8645 | 74.6386 | -62.1774
2026-06-09 01:00 | -459.106 | 1.5193 | 77.4298 | 74.6386 | -134.5507
2026-06-10 02:00 | -619.727 | 1.85 | 77.1873 | 74.6386 | -181.6241
2026-06-11 03:00 | -681.084 | 1.9694 | 77.004 | 74.6386 | -199.606
2026-06-12 04:00 | -714.027 | 2.0393 | 76.8432 | 74.6386 | -209.2607
2026-06-13 05:00 | -469.812 | 1.4742 | 76.8085 | 74.6386 | -137.6883
2026-06-14 06:00 | -559.745 | 1.7245 | 76.7205 | 74.6386 | -164.0451
2026-06-15 07:00 | 0 | 1 | 77.41 | 74.6386 | 0
2026-06-16 08:00 | 2618.21 | 1 | 76.1216 | 74.6386 | 767.3216
2026-06-17 09:00 | 3110.05 | 1 | 85.4024 | 74.6386 | 911.4657
2026-06-18 10:00 | 5498.69 | 1.7658 | 85.0088 | 74.6386 | 1611.507
2026-06-19 11:00 | 7396.73 | 2.4769 | 84.9291 | 74.6386 | 2167.7676
2026-06-20 12:00 | 8643.2 | 2.855 | 85.3033 | 74.6386 | 2533.0719
2026-06-21 13:00 | 9372.32 | 3.0772 | 85.6041 | 74.6386 | 2746.7559
2026-06-22 14:00 | 9931 | 3.2314 | 85.8703 | 74.6386 | 2910.4888
2026-06-23 15:00 | 11417.9 | 3.641 | 86.2025 | 74.6386 | 3346.2562
2026-06-24 16:00 | 11019.9 | 3.5898 | 86.2801 | 74.6386 | 3229.6139
2026-06-25 17:00 | 10338.6 | 3.2494 | 86.6713 | 74.6386 | 3029.9446
2026-06-26 18:00 | 7777.29 | 2.3933 | 86.8891 | 74.6386 | 2279.2987
2026-06-27 19:00 | 5658.91 | 1.7626 | 86.686 | 74.6386 | 1658.4628
2026-06-28 20:00 | 3062.69 | 1 | 88.191 | 74.6386 | 897.5858
2026-06-29 21:00 | 3047.08 | 1 | 77.1427 | 74.6386 | 893.011
2026-06-30 22:00 | -221.974 | 1.0278 | 77.9323 | 74.6386 | -65.0542
2026-07-01 23:00 | -651.73 | 1.9555 | 77.2944 | 74.6386 | -191.0032
2026-07-03 | -840.857 | 2.3288 | 76.9673 | 74.6386 | -246.4309
2026-07-04 01:00 | -999.026 | 2.6697 | 76.7607 | 74.6386 | -292.7856
2026-07-05 02:00 | -1077.72 | 2.8299 | 76.6016 | 74.6386 | -315.8486
2026-07-06 03:00 | -983.291 | 2.6034 | 76.4591 | 74.6386 | -288.1741
2026-07-07 04:00 | -897.01 | 2.4234 | 76.3826 | 74.6386 | -262.8877
2026-07-08 05:00 | -558.967 | 1.6566 | 76.3773 | 74.6386 | -163.8171
2026-07-09 06:00 | -431.975 | 1.4221 | 76.4138 | 74.6386 | -126.5994
2026-07-10 07:00 | 1926.11 | 1 | 76.1689 | 74.6386 | 564.4871
2026-07-11 08:00 | 3092.8 | 1 | 75.7479 | 74.6386 | 906.4102
2026-07-12 09:00 | 3853.69 | 1.2057 | 84.9616 | 74.6386 | 1129.4051
2026-07-13 10:00 | 5726.92 | 1.867 | 84.7781 | 74.6386 | 1678.3946
2026-07-14 11:00 | 6896.11 | 2.2904 | 84.8618 | 74.6386 | 2021.0503
2026-07-15 12:00 | 7958.19 | 2.6398 | 85.0969 | 74.6386 | 2332.3153
2026-07-16 13:00 | 8487.12 | 2.7625 | 85.4347 | 74.6386 | 2487.3293
2026-07-17 14:00 | 9424.9 | 3.0875 | 85.556 | 74.6386 | 2762.1655
2026-07-18 15:00 | 10654.2 | 3.4566 | 85.8106 | 74.6386 | 3122.4378
2026-07-19 16:00 | 10889.9 | 3.5218 | 86.049 | 74.6386 | 3191.5146
2026-07-20 17:00 | 10212.9 | 3.2647 | 86.2982 | 74.6386 | 2993.1055
2026-07-21 18:00 | 7984.7 | 2.484 | 86.5826 | 74.6386 | 2340.0846
2026-07-22 19:00 | 6357.12 | 1.9681 | 86.5381 | 74.6386 | 1863.088
2026-07-23 20:00 | 3857.88 | 1.1813 | 86.4955 | 74.6386 | 1130.633
2026-07-24 21:00 | 3124.42 | 1 | 88.7951 | 74.6386 | 915.6771
2026-07-25 22:00 | 2784.47 | 1 | 76.9969 | 74.6386 | 816.0476
2026-07-26 23:00 | -251.286 | 1.1255 | 77.6799 | 74.6386 | -73.6447
2026-07-28 | -630.433 | 1.904 | 77.1074 | 74.6386 | -184.7617
2026-07-29 01:00 | -810.943 | 2.2675 | 76.8197 | 74.6386 | -237.6639
2026-07-30 02:00 | -868.087 | 2.3754 | 76.6588 | 74.6386 | -254.4112
2026-07-31 03:00 | -896.391 | 2.4359 | 76.5205 | 74.6386 | -262.7063
2026-08-01 04:00 | -956.896 | 2.5747 | 76.3851 | 74.6386 | -280.4385
2026-08-02 05:00 | -876.053 | 2.3791 | 76.3048 | 74.6386 | -256.7458
2026-08-03 06:00 | 0 | 1 | 77.1159 | 74.6386 | 0
2026-08-04 07:00 | 1935.8 | 1 | 83.7572 | 74.6386 | 567.327
2026-08-05 08:00 | 2705.55 | 1 | 85.2102 | 74.6386 | 792.9184
2026-08-06 09:00 | 4634.31 | 1.5679 | 84.3563 | 74.6386 | 1358.1822
2026-08-07 10:00 | 6572.26 | 2.2943 | 84.3281 | 74.6386 | 1926.1393
2026-08-08 11:00 | 7990.83 | 2.7844 | 84.6085 | 74.6386 | 2341.8811
2026-08-09 12:00 | 9121.87 | 3.0379 | 85.1849 | 74.6386 | 2673.3562
2026-08-10 13:00 | 9719.74 | 3.1797 | 85.552 | 74.6386 | 2848.5746
2026-08-11 14:00 | 10628.1 | 3.4245 | 85.8699 | 74.6386 | 3114.7886
2026-08-12 15:00 | 10478.9 | 3.4678 | 85.8811 | 74.6386 | 3071.0624
2026-08-13 16:00 | 12533.3 | 4.1988 | 85.9215 | 74.6386 | 3673.1476
2026-08-14 17:00 | 11249.5 | 3.5473 | 86.6198 | 74.6386 | 3296.903
2026-08-15 18:00 | 9191.51 | 2.8772 | 86.7668 | 74.6386 | 2693.7657
2026-08-16 19:00 | 7925.59 | 2.3913 | 86.9777 | 74.6386 | 2322.7611
2026-08-17 20:00 | 6795.1 | 2.057 | 86.8705 | 74.6386 | 1991.4472
2026-08-18 21:00 | 5622.73 | 1.7007 | 86.7838 | 74.6386 | 1647.8595
2026-08-19 22:00 | 5096.43 | 1.5817 | 86.4328 | 74.6386 | 1493.6162
2026-08-20 23:00 | 3094.4 | 1 | 77.2018 | 74.6386 | 906.8791
2026-08-22 | 3048.17 | 1 | 77.0186 | 74.6386 | 893.3304
2026-08-23 01:00 | 3176.62 | 1 | 76.8324 | 74.6386 | 930.9754
2026-08-24 02:00 | 0 | 0 | 78.3017 | 74.6386 | 0
2026-08-25 03:00 | -75.9603 | 0.64836 | 78.086 | 74.6386 | -22.2618
2026-08-26 04:00 | -170.093 | 0.88407 | 77.3442 | 74.6386 | -49.8493
2026-08-27 05:00 | -151.631 | 0.82986 | 77.2469 | 74.6386 | -44.4387
2026-08-28 06:00 | 1715.28 | 1 | 76.7481 | 74.6386 | 502.6989
2026-08-29 07:00 | 2974.29 | 1.1082 | 83.9695 | 74.6386 | 871.6784
2026-08-30 08:00 | 3237.28 | 1.0721 | 84.8679 | 74.6386 | 948.7531
2026-08-31 09:00 | 5300.88 | 1.6867 | 85.2141 | 74.6386 | 1553.5346
2026-09-01 10:00 | 6997.31 | 2.3874 | 84.8884 | 74.6386 | 2050.7091
2026-09-02 11:00 | 8585.63 | 2.9318 | 85.1205 | 74.6386 | 2516.1998
2026-09-03 12:00 | 9489.86 | 3.0726 | 85.7339 | 74.6386 | 2781.2034
2026-09-04 13:00 | 9276.84 | 3.0264 | 85.8792 | 74.6386 | 2718.7734
2026-09-05 14:00 | 8739.05 | 2.7761 | 86.2126 | 74.6386 | 2561.1627
2026-09-06 15:00 | 8706.47 | 2.7415 | 86.3372 | 74.6386 | 2551.6145
2026-09-07 16:00 | 10709.8 | 3.6044 | 85.9026 | 74.6386 | 3138.7325
2026-09-08 17:00 | 9841.07 | 3.161 | 86.4372 | 74.6386 | 2884.1329
2026-09-09 18:00 | 8811.25 | 2.7164 | 86.8048 | 74.6386 | 2582.3225
2026-09-10 19:00 | 7455.6 | 2.3677 | 86.5544 | 74.6386 | 2185.0207
2026-09-11 20:00 | 6581.52 | 2.0441 | 86.6577 | 74.6386 | 1928.8531
2026-09-12 21:00 | 5687.59 | 1.7187 | 86.7944 | 74.6386 | 1666.8681
2026-09-13 22:00 | 4786.62 | 1.4756 | 86.5176 | 74.6386 | 1402.8198
2026-09-14 23:00 | 3341.22 | 1 | 92.5505 | 74.6386 | 979.2149
2026-09-16 | 3200.19 | 1 | 76.9806 | 74.6386 | 937.8831
2026-09-17 01:00 | 3200.88 | 1 | 76.8686 | 74.6386 | 938.0853
2026-09-18 02:00 | 3313.39 | 1 | 76.7567 | 74.6386 | 971.0588
2026-09-19 03:00 | 3282.98 | 1 | 76.737 | 74.6386 | 962.1465
2026-09-20 04:00 | 3244.45 | 1 | 90.7437 | 74.6386 | 950.8544
2026-09-21 05:00 | 3534.62 | 1.1035 | 85.8299 | 74.6386 | 1035.8949
2026-09-22 06:00 | 3922.23 | 1.2207 | 85.8616 | 74.6386 | 1149.4921
2026-09-23 07:00 | 4991 | 1.5269 | 86.0163 | 74.6386 | 1462.7177
2026-09-24 08:00 | 5554.67 | 1.733 | 85.9514 | 74.6386 | 1627.9131
2026-09-25 09:00 | 6109.16 | 1.9746 | 85.7709 | 74.6386 | 1790.4181
2026-09-26 10:00 | 7236.98 | 2.4085 | 85.6415 | 74.6386 | 2120.9495
2026-09-27 11:00 | 7202.26 | 2.3643 | 85.8743 | 74.6386 | 2110.774
2026-09-28 12:00 | 8047.38 | 2.4922 | 86.3807 | 74.6386 | 2358.4543
2026-09-29 13:00 | 9265.22 | 3.0502 | 86.0307 | 74.6386 | 2715.3679
2026-09-30 14:00 | 10573.7 | 3.5064 | 86.1404 | 74.6386 | 3098.8456
2026-10-01 15:00 | 11798.5 | 4.0459 | 86.1036 | 74.6386 | 3457.799
2026-10-02 16:00 | 11725.6 | 3.8215 | 86.6665 | 74.6386 | 3436.4341
2026-10-03 17:00 | 10810.6 | 3.5849 | 86.6798 | 74.6386 | 3168.2741
2026-10-04 18:00 | 7680.35 | 2.9169 | 85.8207 | 74.6386 | 2250.8884
2026-10-05 19:00 | 6465.16 | 2.181 | 86.4286 | 74.6386 | 1894.7514
2026-10-06 20:00 | 4201.8 | 1.3577 | 86.572 | 74.6386 | 1231.426
2026-10-07 21:00 | 3199.67 | 1 | 86.8855 | 74.6386 | 937.7307
2026-10-08 22:00 | 3152.24 | 1 | 77.2415 | 74.6386 | 923.8303
2026-10-09 23:00 | 1702.75 | 1 | 77.802 | 74.6386 | 499.0268
2026-10-11 | -17.7362 | 0.585 | 78.4503 | 74.6386 | -5.198
2026-10-12 01:00 | -298.294 | 1.1759 | 77.5568 | 74.6386 | -87.4213
2026-10-13 02:00 | -457.324 | 1.5034 | 77.2518 | 74.6386 | -134.0284
2026-10-14 03:00 | -432.041 | 1.4239 | 77.1032 | 74.6386 | -126.6187
2026-10-15 04:00 | -383.455 | 1.3203 | 76.9972 | 74.6386 | -112.3796
2026-10-16 05:00 | 377.011 | 1 | 77.3957 | 74.6386 | 110.491
2026-10-17 06:00 | 586.367 | 1 | 77.2797 | 74.6386 | 171.8472
2026-10-18 07:00 | 2187.71 | 1 | 76.4856 | 74.6386 | 641.1545
2026-10-19 08:00 | 2661.87 | 1 | 76.3485 | 74.6386 | 780.1171
2026-10-20 09:00 | 2985.8 | 1 | 85.9119 | 74.6386 | 875.0516
2026-10-21 10:00 | 4228.51 | 1.4338 | 84.7243 | 74.6386 | 1239.254
2026-10-22 11:00 | 5572.81 | 1.885 | 84.8544 | 74.6386 | 1633.2294
2026-10-23 12:00 | 6363.83 | 2.1229 | 85.123 | 74.6386 | 1865.0545
2026-10-24 13:00 | 6866.17 | 2.2085 | 85.5286 | 74.6386 | 2012.2758
2026-10-25 14:00 | 7488.27 | 2.4463 | 85.5354 | 74.6386 | 2194.5953
2026-10-26 15:00 | 8727.3 | 2.8645 | 85.6287 | 74.6386 | 2557.7191
2026-10-27 16:00 | 8987.06 | 2.9233 | 85.867 | 74.6386 | 2633.8473
2026-10-28 17:00 | 8341.29 | 2.6857 | 86.0667 | 74.6386 | 2444.5908
2026-10-29 18:00 | 5958.81 | 1.8764 | 86.2802 | 74.6386 | 1746.3548
2026-10-30 19:00 | 4194.81 | 1.3436 | 86.0276 | 74.6386 | 1229.3775
2026-10-31 20:00 | 3154.51 | 1 | 76.9464 | 74.6386 | 924.4956
2026-11-01 21:00 | 3097.76 | 1 | 76.8141 | 74.6386 | 907.8638
2026-11-02 22:00 | -385.991 | 1.4204 | 77.5577 | 74.6386 | -113.1228
2026-11-03 23:00 | -759.215 | 2.1792 | 77.0349 | 74.6386 | -222.504
2026-11-05 | -1071.95 | 2.8497 | 76.7426 | 74.6386 | -314.1575
2026-11-06 01:00 | -1371.84 | 3.4982 | 76.5536 | 74.6386 | -402.0466
2026-11-07 02:00 | -1593.86 | 3.9702 | 76.3842 | 74.6386 | -467.1143
2026-11-08 03:00 | -1606.5 | 3.9698 | 76.2207 | 74.6386 | -470.8187
2026-11-09 04:00 | -1543.32 | 3.8267 | 76.1223 | 74.6386 | -452.3024
2026-11-10 05:00 | -1164.61 | 2.9581 | 76.0585 | 74.6386 | -341.3135
2026-11-11 06:00 | -1202.46 | 3.1149 | 76.0341 | 74.6386 | -352.4062
2026-11-12 07:00 | -834.47 | 2.2478 | 76.0165 | 74.6386 | -244.559
2026-11-13 08:00 | -666.088 | 1.9238 | 76.0503 | 74.6386 | -195.2111
2026-11-14 09:00 | 0 | 1 | 76.8444 | 74.6386 | 0
2026-11-15 10:00 | 3227.64 | 1 | 75.3101 | 74.6386 | 945.9279
2026-11-16 11:00 | 3615.78 | 1.155 | 84.523 | 74.6386 | 1059.6805
2026-11-17 12:00 | 4573.94 | 1.4859 | 84.5345 | 74.6386 | 1340.4895
2026-11-18 13:00 | 5139.23 | 1.6359 | 84.8235 | 74.6386 | 1506.1596
2026-11-19 14:00 | 5392.37 | 1.7815 | 84.6911 | 74.6386 | 1580.3476
2026-11-20 15:00 | 6791.35 | 2.2468 | 84.7883 | 74.6386 | 1990.3482
2026-11-21 16:00 | 6805.49 | 2.2779 | 84.8562 | 74.6386 | 1994.4922
2026-11-22 17:00 | 6294.05 | 2.1184 | 84.9182 | 74.6386 | 1844.604
2026-11-23 18:00 | 4214.65 | 1.396 | 85.0709 | 74.6386 | 1235.192
2026-11-24 19:00 | 3049.13 | 1 | 86.8809 | 74.6386 | 893.6118
2026-11-25 20:00 | 2917.94 | 1 | 76.3022 | 74.6386 | 855.1638
2026-11-26 21:00 | -89.9654 | 0.75582 | 77.3666 | 74.6386 | -26.3663
2026-11-27 22:00 | -1180.36 | 3.2089 | 76.503 | 74.6386 | -345.9294
2026-11-28 23:00 | -1823.4 | 4.5377 | 76.1728 | 74.6386 | -534.3858
2026-11-30 | -2206.33 | 5.3414 | 75.9643 | 74.6386 | -646.6115
2026-12-01 01:00 | -2463.5 | 5.8931 | 75.7953 | 74.6386 | -721.9806
2026-12-02 02:00 | -2313.52 | 5.505 | 75.6412 | 74.6386 | -678.0258
2026-12-03 03:00 | -2403.27 | 5.7534 | 75.5547 | 74.6386 | -704.3289
2026-12-04 04:00 | -2326.85 | 5.5583 | 75.4668 | 74.6386 | -681.9324
2026-12-05 05:00 | -1815.11 | 4.3698 | 75.4028 | 74.6386 | -531.9562
2026-12-06 06:00 | -1738.39 | 4.2837 | 75.4084 | 74.6386 | -509.4718
2026-12-07 07:00 | -852.381 | 2.2111 | 75.4327 | 74.6386 | -249.8082
2026-12-08 08:00 | -186.138 | 0.81821 | 75.8357 | 74.6386 | -54.5517
2026-12-09 09:00 | 2478.65 | 1 | 75.243 | 74.6386 | 726.4206
2026-12-10 10:00 | 3411.92 | 1.145 | 83.7224 | 74.6386 | 999.935
2026-12-11 11:00 | 5791.99 | 1.8998 | 84.061 | 74.6386 | 1697.4647
2026-12-12 12:00 | 7032.24 | 2.3333 | 84.2608 | 74.6386 | 2060.9461
2026-12-13 13:00 | 7672.3 | 2.5082 | 84.6388 | 74.6386 | 2248.5292
2026-12-14 14:00 | 8524.57 | 2.7733 | 84.8983 | 74.6386 | 2498.3049
2026-12-15 15:00 | 9754.01 | 3.1863 | 85.0735 | 74.6386 | 2858.6181
2026-12-16 16:00 | 9991.21 | 3.2086 | 85.443 | 74.6386 | 2928.1346
2026-12-17 17:00 | 9324.06 | 3.0265 | 85.5434 | 74.6386 | 2732.6122
2026-12-18 18:00 | 6910.04 | 2.1867 | 85.8252 | 74.6386 | 2025.1328
2026-12-19 19:00 | 5225.99 | 1.6014 | 85.9916 | 74.6386 | 1531.5865
2026-12-20 20:00 | 3085.12 | 1 | 88.6789 | 74.6386 | 904.1594
2026-12-21 21:00 | 2927.66 | 1 | 76.5164 | 74.6386 | 858.0124
2026-12-22 22:00 | -375.047 | 1.392 | 77.1694 | 74.6386 | -109.9154
2026-12-23 23:00 | -714.716 | 2.0873 | 76.6661 | 74.6386 | -209.4626
2026-12-25 | -1079.11 | 2.8846 | 76.367 | 74.6386 | -316.2559
2026-12-26 01:00 | -1287.72 | 3.3141 | 76.1738 | 74.6386 | -377.3935
2026-12-27 02:00 | -1646.68 | 4.124 | 76.0133 | 74.6386 | -482.5943
2026-12-28 03:00 | -1631.34 | 4.032 | 75.8464 | 74.6386 | -478.0986
2026-12-29 04:00 | -1629.32 | 4.0386 | 75.7514 | 74.6386 | -477.5066
2026-12-30 05:00 | -1197.14 | 3.0293 | 75.6855 | 74.6386 | -350.8471
2026-12-31 06:00 | -989.156 | 2.6227 | 75.6948 | 74.6386 | -289.893
2027-01-01 07:00 | 0 | 0 | 76.5661 | 74.6386 | 0
2027-01-02 08:00 | 2030 | 1 | 75.6372 | 74.6386 | 594.9343
2027-01-03 09:00 | 2914.29 | 1 | 85.7529 | 74.6386 | 854.0941
2027-01-04 10:00 | 4695.53 | 1.492 | 84.376 | 74.6386 | 1376.124
2027-01-05 11:00 | 6276.29 | 2.0715 | 84.3106 | 74.6386 | 1839.399
2027-01-06 12:00 | 7097.06 | 2.3247 | 84.6157 | 74.6386 | 2079.943
2027-01-07 13:00 | 7713.89 | 2.4806 | 84.9629 | 74.6386 | 2260.718
2027-01-08 14:00 | 8103.14 | 2.6385 | 85.0474 | 74.6386 | 2374.7959
2027-01-09 15:00 | 9303.18 | 3.0747 | 85.0913 | 74.6386 | 2726.4929
2027-01-10 16:00 | 9508.98 | 3.0681 | 85.4607 | 74.6386 | 2786.8069
2027-01-11 17:00 | 8886.28 | 2.9142 | 85.4894 | 74.6386 | 2604.3116
2027-01-12 18:00 | 6733.12 | 2.1311 | 85.8238 | 74.6386 | 1973.2827
2027-01-13 19:00 | 5201.74 | 1.6249 | 85.8437 | 74.6386 | 1524.4795
2027-01-14 20:00 | 3158.54 | 1 | 87.5735 | 74.6386 | 925.6767
2027-01-15 21:00 | 3100.91 | 1 | 76.4462 | 74.6386 | 908.787
2027-01-16 22:00 | 0 | 0 | 77.8312 | 74.6386 | 0
2027-01-17 23:00 | -835.343 | 2.4032 | 76.6999 | 74.6386 | -244.8149
2027-01-19 | -1291 | 3.3522 | 76.3646 | 74.6386 | -378.3548
2027-01-20 01:00 | -1491.98 | 3.7539 | 76.1572 | 74.6386 | -437.2562
2027-01-21 02:00 | -1772.98 | 4.3854 | 76.0024 | 74.6386 | -519.6091
2027-01-22 03:00 | -2122.09 | 5.163 | 75.8347 | 74.6386 | -621.9232
2027-01-23 04:00 | -2152.36 | 5.1803 | 75.696 | 74.6386 | -630.7944
2027-01-24 05:00 | -2375.11 | 5.7104 | 75.5925 | 74.6386 | -696.076
2027-01-25 06:00 | -1497.32 | 3.6061 | 75.5002 | 74.6386 | -438.8212
2027-01-26 07:00 | 0 | 1 | 76.4705 | 74.6386 | 0
2027-01-27 08:00 | 2175.47 | 1 | 75.5047 | 74.6386 | 637.5673
2027-01-28 09:00 | 2935.41 | 1 | 87.4821 | 74.6386 | 860.2837
2027-01-29 10:00 | 4235.24 | 1.373 | 84.1861 | 74.6386 | 1241.2263
2027-01-30 11:00 | 5835.6 | 1.9024 | 84.3337 | 74.6386 | 1710.2455
2027-01-31 12:00 | 6247.43 | 2.0621 | 84.4811 | 74.6386 | 1830.941
2027-02-01 13:00 | 6932.7 | 2.2739 | 84.6987 | 74.6386 | 2031.7738
2027-02-02 14:00 | 7612.13 | 2.4887 | 84.8731 | 74.6386 | 2230.8951
2027-02-03 15:00 | 7942.5 | 2.5701 | 85.1068 | 74.6386 | 2327.717
2027-02-04 16:00 | 10313.6 | 3.4007 | 85.1013 | 74.6386 | 3022.6178
2027-02-05 17:00 | 9168.14 | 2.9737 | 85.4942 | 74.6386 | 2686.9166
2027-02-06 18:00 | 7407.21 | 2.3253 | 85.8447 | 74.6386 | 2170.839
2027-02-07 19:00 | 5683.16 | 1.7866 | 85.7908 | 74.6386 | 1665.5698
2027-02-08 20:00 | 4725.24 | 1.455 | 85.8412 | 74.6386 | 1384.8311
2027-02-09 21:00 | 3101.96 | 1 | 86.2106 | 74.6386 | 909.0947
2027-02-10 22:00 | 3060.68 | 1 | 88.7435 | 74.6386 | 896.9968
2027-02-11 23:00 | 0 | 0 | 77.775 | 74.6386 | 0
2027-02-13 | -770.287 | 2.1408 | 76.6395 | 74.6386 | -225.7488
2027-02-14 01:00 | -1205.39 | 3.1731 | 76.3671 | 74.6386 | -353.2649
2027-02-15 02:00 | -1370.62 | 3.4848 | 76.1698 | 74.6386 | -401.6891
2027-02-16 03:00 | -1523.28 | 3.8219 | 76.0275 | 74.6386 | -446.4293
2027-02-17 04:00 | -1743.19 | 4.3165 | 75.8724 | 74.6386 | -510.8786
2027-02-18 05:00 | -1757.46 | 4.3163 | 75.7589 | 74.6386 | -515.0607
2027-02-19 06:00 | -1051.41 | 2.6663 | 75.7095 | 74.6386 | -308.1379
2027-02-20 07:00 | 1400.64 | 1 | 75.9557 | 74.6386 | 410.4871
2027-02-21 08:00 | 3083.29 | 1 | 75.2925 | 74.6386 | 903.6231
2027-02-22 09:00 | 2979.87 | 1 | 85.7451 | 74.6386 | 873.3137
2027-02-23 10:00 | 4735.33 | 1.5582 | 84.2397 | 74.6386 | 1387.7882
2027-02-24 11:00 | 6480.07 | 2.177 | 84.2859 | 74.6386 | 1899.121
2027-02-25 12:00 | 7524.6 | 2.5069 | 84.6085 | 74.6386 | 2205.2426
2027-02-26 13:00 | 8510.59 | 2.7743 | 84.9867 | 74.6386 | 2494.2077
2027-02-27 14:00 | 9184.46 | 2.9733 | 85.2438 | 74.6386 | 2691.6995
2027-02-28 15:00 | 9595.76 | 3.1396 | 85.3719 | 74.6386 | 2812.2397
2027-03-01 16:00 | 12099.6 | 3.9773 | 85.5043 | 74.6386 | 3546.0427
2027-03-02 17:00 | 10858.4 | 3.4784 | 86.0073 | 74.6386 | 3182.2829
2027-03-03 18:00 | 9151.79 | 2.9069 | 86.1981 | 74.6386 | 2682.1249
2027-03-04 19:00 | 7414.18 | 2.2427 | 86.5424 | 74.6386 | 2172.8817
2027-03-05 20:00 | 6517.24 | 1.9263 | 86.6297 | 74.6386 | 1910.0145
2027-03-06 21:00 | 5487.9 | 1.646 | 86.441 | 74.6386 | 1608.3447
2027-03-07 22:00 | 4429.6 | 1.3999 | 85.9151 | 74.6386 | 1298.1876
2027-03-08 23:00 | 3075.35 | 1 | 76.8058 | 74.6386 | 901.2961
2027-03-10 | 3053.77 | 1 | 76.6479 | 74.6386 | 894.9716
2027-03-11 01:00 | 0 | 0 | 78.0313 | 74.6386 | 0
2027-03-12 02:00 | 435.068 | 1 | 77.5344 | 74.6386 | 127.5058
2027-03-13 03:00 | 864.494 | 1 | 77.1817 | 74.6386 | 253.3582
2027-03-14 04:00 | 2581.66 | 1 | 76.2828 | 74.6386 | 756.6099
2027-03-15 05:00 | 2054.59 | 1 | 76.6015 | 74.6386 | 602.1409
2027-03-16 06:00 | 2912.89 | 1 | 76.1549 | 74.6386 | 853.6838
2027-03-17 07:00 | 2981.97 | 1 | 85.3662 | 74.6386 | 873.9291
2027-03-18 08:00 | 3651.75 | 1.1818 | 84.9592 | 74.6386 | 1070.2223
2027-03-19 09:00 | 5939.99 | 1.937 | 84.9662 | 74.6386 | 1740.8392
2027-03-20 10:00 | 7838.79 | 2.6837 | 84.811 | 74.6386 | 2297.3226
2027-03-21 11:00 | 9361.24 | 3.1882 | 85.1 | 74.6386 | 2743.5086
2027-03-22 12:00 | 10193.6 | 3.3794 | 85.5376 | 74.6386 | 2987.4493
2027-03-23 13:00 | 10710 | 3.5075 | 85.8657 | 74.6386 | 3138.7912
2027-03-24 14:00 | 11748.2 | 3.7914 | 86.182 | 74.6386 | 3443.0575
2027-03-25 15:00 | 13225.5 | 4.3025 | 86.3453 | 74.6386 | 3876.0114
2027-03-26 16:00 | 13661.8 | 4.4359 | 86.6039 | 74.6386 | 4003.8783
2027-03-27 17:00 | 13296.4 | 4.2455 | 86.9286 | 74.6386 | 3896.7902
2027-03-28 18:00 | 11041.3 | 3.4835 | 87.1453 | 74.6386 | 3235.8856
2027-03-29 19:00 | 9444.53 | 2.9644 | 87.1468 | 74.6386 | 2767.9185
2027-03-30 20:00 | 7478.49 | 2.1612 | 87.7044 | 74.6386 | 2191.7291
2027-03-31 21:00 | 5878.27 | 1.7674 | 87.2123 | 74.6386 | 1722.7509
2027-04-01 22:00 | 3675.15 | 1.0809 | 87.1743 | 74.6386 | 1077.0801
2027-04-02 23:00 | 3178.71 | 1 | 86.7487 | 74.6386 | 931.5879
2027-04-04 | 3130.63 | 1 | 90.8396 | 74.6386 | 917.4971
2027-04-05 01:00 | 3073.5 | 1 | 77.0393 | 74.6386 | 900.7539
2027-04-06 02:00 | 3129.36 | 1 | 76.9204 | 74.6386 | 917.1249
2027-04-07 03:00 | 3116.76 | 1 | 76.8488 | 74.6386 | 913.4322
2027-04-08 04:00 | 3187.44 | 1 | 76.7554 | 74.6386 | 934.1465
2027-04-09 05:00 | 3128.67 | 1 | 76.7391 | 74.6386 | 916.9227
2027-04-10 06:00 | 3298.86 | 1 | 90.2315 | 74.6386 | 966.8004
2027-04-11 07:00 | 3951.34 | 1.1665 | 86.1932 | 74.6386 | 1158.0234
2027-04-12 08:00 | 4513.96 | 1.4145 | 85.7623 | 74.6386 | 1322.9111
2027-04-13 09:00 | 6324.74 | 2.0848 | 85.4388 | 74.6386 | 1853.5983
2027-04-14 10:00 | 7796.51 | 2.7179 | 85.2063 | 74.6386 | 2284.9315
2027-04-15 11:00 | 9808.04 | 3.3333 | 85.5776 | 74.6386 | 2874.4528
2027-04-16 12:00 | 11001.4 | 3.6207 | 86.0651 | 74.6386 | 3224.1921
2027-04-17 13:00 | 11546.4 | 3.8069 | 86.2996 | 74.6386 | 3383.9158
2027-04-18 14:00 | 12513.1 | 4.0978 | 86.5481 | 74.6386 | 3667.2276
2027-04-19 15:00 | 14008.7 | 4.6609 | 86.6377 | 74.6386 | 4105.5447
2027-04-20 16:00 | 14521.5 | 4.7618 | 86.9934 | 74.6386 | 4255.8315
2027-04-21 17:00 | 14238.6 | 4.5739 | 87.3472 | 74.6386 | 4172.9217
2027-04-22 18:00 | 11952.5 | 3.7872 | 87.5844 | 74.6386 | 3502.932
2027-04-23 19:00 | 10572.3 | 3.2195 | 87.8462 | 74.6386 | 3098.4353
2027-04-24 20:00 | 8374.4 | 2.4328 | 88.1477 | 74.6386 | 2454.2944
2027-04-25 21:00 | 6995.98 | 2.0816 | 87.779 | 74.6386 | 2050.3193
2027-04-26 22:00 | 4420.44 | 1.3422 | 87.4316 | 74.6386 | 1295.5031
2027-04-27 23:00 | 3343.99 | 1.0295 | 87.0219 | 74.6386 | 980.0267
2027-04-29 | 3100.98 | 1 | 88.8638 | 74.6386 | 908.8075
2027-04-30 01:00 | 3136.36 | 1 | 77.3983 | 74.6386 | 919.1764
2027-05-01 02:00 | 3095.24 | 1 | 77.3018 | 74.6386 | 907.1253
2027-05-02 03:00 | 3149.92 | 1 | 77.1652 | 74.6386 | 923.1504
2027-05-03 04:00 | 3167.44 | 1 | 77.0777 | 74.6386 | 928.285
2027-05-04 05:00 | 3082.81 | 1 | 88.9734 | 74.6386 | 903.4824
2027-05-05 06:00 | 3327.47 | 1 | 87.9982 | 74.6386 | 975.1852
2027-05-06 07:00 | 4349.48 | 1.2964 | 86.3906 | 74.6386 | 1274.7068
2027-05-07 08:00 | 5235.18 | 1.6242 | 86.1307 | 74.6386 | 1534.2798
2027-05-08 09:00 | 6952.97 | 2.3728 | 85.5159 | 74.6386 | 2037.7144
2027-05-09 10:00 | 8632.27 | 2.9806 | 85.6026 | 74.6386 | 2529.8686
2027-05-10 11:00 | 9963.16 | 3.4424 | 85.8184 | 74.6386 | 2919.914
2027-05-11 12:00 | 11006.2 | 3.6045 | 86.4225 | 74.6386 | 3225.5988
2027-05-12 13:00 | 11493.9 | 3.7866 | 86.5959 | 74.6386 | 3368.5296
2027-05-13 14:00 | 12735 | 4.0889 | 86.9614 | 74.6386 | 3732.2601
2027-05-14 15:00 | 14419.6 | 4.6992 | 87.0594 | 74.6386 | 4225.9676
2027-05-15 16:00 | 14592.2 | 4.6322 | 87.5139 | 74.6386 | 4276.5517
2027-05-16 17:00 | 13773.4 | 4.3606 | 87.7179 | 74.6386 | 4036.5851
2027-05-17 18:00 | 11577.5 | 3.6672 | 87.7983 | 74.6386 | 3393.0303
2027-05-18 19:00 | 9606.75 | 3.0419 | 87.7374 | 74.6386 | 2815.4605
2027-05-19 20:00 | 7268.45 | 2.1739 | 88.0377 | 74.6386 | 2130.1724
2027-05-20 21:00 | 6070.85 | 1.7802 | 87.9597 | 74.6386 | 1779.1905
2027-05-21 22:00 | 3675.32 | 1.1057 | 87.5418 | 74.6386 | 1077.13
2027-05-22 23:00 | 3186.19 | 1 | 88.5147 | 74.6386 | 933.7801
2027-05-24 | 3184.23 | 1 | 91.7552 | 74.6386 | 933.2057
2027-05-25 01:00 | 3120.86 | 1 | 77.5094 | 74.6386 | 914.6338
2027-05-26 02:00 | 3231.84 | 1 | 77.348 | 74.6386 | 947.1588
2027-05-27 03:00 | 3267.88 | 1 | 77.2352 | 74.6386 | 957.7211
2027-05-28 04:00 | 3155.69 | 1 | 77.2236 | 74.6386 | 924.8414
2027-05-29 05:00 | 3191.03 | 1 | 86.8649 | 74.6386 | 935.1986
2027-05-30 06:00 | 3913.1 | 1.1428 | 86.7306 | 74.6386 | 1146.8164
2027-05-31 07:00 | 5341.48 | 1.647 | 86.3168 | 74.6386 | 1565.4333
2027-06-01 08:00 | 5677.15 | 1.8741 | 85.9189 | 74.6386 | 1663.8084
2027-06-02 09:00 | 7172.48 | 2.4619 | 85.7171 | 74.6386 | 2102.0464
2027-06-03 10:00 | 9018.06 | 3.0663 | 85.9359 | 74.6386 | 2642.9325
2027-06-04 11:00 | 10165.5 | 3.509 | 86.0649 | 74.6386 | 2979.214
2027-06-05 12:00 | 10697.7 | 3.5818 | 86.4953 | 74.6386 | 3135.1864
2027-06-06 13:00 | 11326.7 | 3.6575 | 86.9215 | 74.6386 | 3319.5281
2027-06-07 14:00 | 11822.7 | 3.9149 | 86.9033 | 74.6386 | 3464.8913
2027-06-08 15:00 | 13272.8 | 4.3833 | 87.066 | 74.6386 | 3889.8737
2027-06-09 16:00 | 13360.7 | 4.3341 | 87.3952 | 74.6386 | 3915.6346
2027-06-10 17:00 | 12866.9 | 4.1342 | 87.6062 | 74.6386 | 3770.9162
2027-06-11 18:00 | 11229.1 | 3.4937 | 87.9223 | 74.6386 | 3290.9244
2027-06-12 19:00 | 10036.3 | 2.9967 | 88.1998 | 74.6386 | 2941.3492
2027-06-13 20:00 | 7522.92 | 2.25 | 88.1193 | 74.6386 | 2204.7502
2027-06-14 21:00 | 6592.1 | 1.9586 | 87.9626 | 74.6386 | 1931.9538
2027-06-15 22:00 | 4424.57 | 1.3224 | 87.7392 | 74.6386 | 1296.7135
2027-06-16 23:00 | 3644.56 | 1.1234 | 87.2383 | 74.6386 | 1068.1151
2027-06-18 | 3077.9 | 1 | 86.8524 | 74.6386 | 902.0434
2027-06-19 01:00 | 3085.45 | 1 | 88.7567 | 74.6386 | 904.2561
2027-06-20 02:00 | 3053.23 | 1 | 90.7035 | 74.6386 | 894.8134
2027-06-21 03:00 | 3262.77 | 1 | 91.5848 | 74.6386 | 956.2235
2027-06-22 04:00 | 3127.93 | 1 | 87.8977 | 74.6386 | 916.7058
2027-06-23 05:00 | 3508.89 | 1.1162 | 86.2484 | 74.6386 | 1028.3541
2027-06-24 06:00 | 3858.71 | 1.2142 | 86.3066 | 74.6386 | 1130.8763
2027-06-25 07:00 | 4378.27 | 1.396 | 86.2009 | 74.6386 | 1283.1443
2027-06-26 08:00 | 3588.39 | 1.1544 | 86.1627 | 74.6386 | 1051.6533
2027-06-27 09:00 | 4392.17 | 1.3979 | 86.1785 | 74.6386 | 1287.218
2027-06-28 10:00 | 5458.42 | 1.7344 | 86.2079 | 74.6386 | 1599.705
2027-06-29 11:00 | 6484.62 | 2.2026 | 85.8076 | 74.6386 | 1900.4545
2027-06-30 12:00 | 8238.74 | 2.753 | 86.0261 | 74.6386 | 2414.5363
2027-07-01 13:00 | 8952.21 | 2.9649 | 86.2632 | 74.6386 | 2623.6338
2027-07-02 14:00 | 8846.35 | 2.7999 | 86.7532 | 74.6386 | 2592.6093
2027-07-03 15:00 | 9747.29 | 3.2343 | 86.4817 | 74.6386 | 2856.6487
2027-07-04 16:00 | 9847.19 | 3.1665 | 86.8277 | 74.6386 | 2885.9265
2027-07-05 17:00 | 9491.51 | 2.895 | 87.3142 | 74.6386 | 2781.687
2027-07-06 18:00 | 8210.76 | 2.5019 | 87.3494 | 74.6386 | 2406.3362
2027-07-07 19:00 | 7250.39 | 2.1922 | 87.347 | 74.6386 | 2124.8796
2027-07-08 20:00 | 5111.41 | 1.4993 | 87.5206 | 74.6386 | 1498.0064
2027-07-09 21:00 | 3885.43 | 1.2275 | 86.7584 | 74.6386 | 1138.7071
2027-07-10 22:00 | 3033.96 | 1 | 77.6192 | 74.6386 | 889.1659
2027-07-11 23:00 | 305.415 | 1 | 78.7688 | 74.6386 | 89.5083
2027-07-13 | 133.859 | 1 | 78.5319 | 74.6386 | 39.2302
2027-07-14 01:00 | -26.2183 | 0.57337 | 78.4062 | 74.6386 | -7.6838
2027-07-15 02:00 | -121.37 | 0.77641 | 77.8544 | 74.6386 | -35.57
2027-07-16 03:00 | -99.3256 | 0.71586 | 77.7571 | 74.6386 | -29.1095
2027-07-17 04:00 | -175.332 | 0.89407 | 77.5007 | 74.6386 | -51.3847
2027-07-18 05:00 | -170.466 | 0.87048 | 77.4117 | 74.6386 | -49.9587
2027-07-19 06:00 | 1743.07 | 1 | 76.9547 | 74.6386 | 510.8434
2027-07-20 07:00 | 2683.83 | 1 | 84.7059 | 74.6386 | 786.5529
2027-07-21 08:00 | 2879.72 | 1 | 87.7497 | 74.6386 | 843.9626
2027-07-22 09:00 | 3621.53 | 1.2067 | 85.1047 | 74.6386 | 1061.3657
2027-07-23 10:00 | 5464.99 | 1.902 | 84.8797 | 74.6386 | 1601.6305
2027-07-24 11:00 | 7150.96 | 2.4767 | 85.1097 | 74.6386 | 2095.7395
2027-07-25 12:00 | 8405.54 | 2.7846 | 85.6414 | 74.6386 | 2463.4206
2027-07-26 13:00 | 9285.2 | 3.0741 | 85.8589 | 74.6386 | 2721.2235
2027-07-27 14:00 | 10286.4 | 3.4695 | 85.9325 | 74.6386 | 3014.6463
2027-07-28 15:00 | 10709.2 | 3.5826 | 86.2034 | 74.6386 | 3138.5567
2027-07-29 16:00 | 13263.4 | 4.1272 | 86.9064 | 74.6386 | 3887.1188
2027-07-30 17:00 | 11525 | 3.626 | 87.139 | 74.6386 | 3377.6441
2027-07-31 18:00 | 9529.38 | 2.9957 | 87.2232 | 74.6386 | 2792.7856
2027-08-01 19:00 | 7992.41 | 2.4195 | 87.4348 | 74.6386 | 2342.3442
2027-08-02 20:00 | 6777.76 | 2.1275 | 87.0582 | 74.6386 | 1986.3654
2027-08-03 21:00 | 5719.2 | 1.754 | 87.1283 | 74.6386 | 1676.1321
2027-08-04 22:00 | 5016.67 | 1.573 | 86.8051 | 74.6386 | 1470.2408
2027-08-05 23:00 | 3068.73 | 1 | 77.651 | 74.6386 | 899.356
2027-08-07 | 3065.51 | 1 | 77.4393 | 74.6386 | 898.4123
2027-08-08 01:00 | 0 | 0 | 78.7938 | 74.6386 | 0
2027-08-09 02:00 | -88.6672 | 0.73251 | 78.1948 | 74.6386 | -25.9858
2027-08-10 03:00 | -396.538 | 1.393 | 77.5955 | 74.6386 | -116.2138
2027-08-11 04:00 | -669.686 | 1.9713 | 77.2847 | 74.6386 | -196.2656
2027-08-12 05:00 | -881.943 | 2.4192 | 77.0713 | 74.6386 | -258.472
2027-08-13 06:00 | 76.8057 | 1 | 77.7476 | 74.6386 | 22.5095
2027-08-14 07:00 | 2343.68 | 1 | 86.1226 | 74.6386 | 686.8648
2027-08-15 08:00 | 2809.89 | 1 | 88.3438 | 74.6386 | 823.4975
2027-08-16 09:00 | 3541.29 | 1.2527 | 84.6579 | 74.6386 | 1037.8496
2027-08-17 10:00 | 5396.1 | 1.8073 | 85.1135 | 74.6386 | 1581.4408
2027-08-18 11:00 | 6591.47 | 2.2636 | 85.13 | 74.6386 | 1931.7692
2027-08-19 12:00 | 6961.89 | 2.4731 | 85.0906 | 74.6386 | 2040.3286
2027-08-20 13:00 | 7610.29 | 2.5607 | 85.5924 | 74.6386 | 2230.3558
2027-08-21 14:00 | 8208.89 | 2.6971 | 85.8968 | 74.6386 | 2405.7882
2027-08-22 15:00 | 8322.37 | 2.6639 | 86.2288 | 74.6386 | 2439.0459
2027-08-23 16:00 | 10183.3 | 3.3378 | 86.1427 | 74.6386 | 2984.4306
2027-08-24 17:00 | 8611.91 | 2.7938 | 86.4261 | 74.6386 | 2523.9017
2027-08-25 18:00 | 6486.58 | 2.1176 | 86.4094 | 74.6386 | 1901.0289
2027-08-26 19:00 | 4351.76 | 1.4512 | 86.1252 | 74.6386 | 1275.375
2027-08-27 20:00 | 3335.69 | 1.0476 | 86.3656 | 74.6386 | 977.5942
2027-08-28 21:00 | 3155.84 | 1 | 91.0649 | 74.6386 | 924.8854
2027-08-29 22:00 | 3145.47 | 1 | 77.0094 | 74.6386 | 921.8463
2027-08-30 23:00 | -382.769 | 1.3989 | 77.7947 | 74.6386 | -112.1785
2027-09-01 | -866.237 | 2.4199 | 77.2683 | 74.6386 | -253.869
2027-09-02 01:00 | -1080.16 | 2.8427 | 76.9974 | 74.6386 | -316.5636
2027-09-03 02:00 | -1327.67 | 3.3865 | 76.8262 | 74.6386 | -389.1017
2027-09-04 03:00 | -1277.93 | 3.2349 | 76.6761 | 74.6386 | -374.5243
2027-09-05 04:00 | -1034.34 | 2.6871 | 76.5623 | 74.6386 | -303.1351
2027-09-06 05:00 | -649.207 | 1.8406 | 76.5778 | 74.6386 | -190.2638
2027-09-07 06:00 | -392.771 | 1.3144 | 76.6779 | 74.6386 | -115.1098
2027-09-08 07:00 | 1948.13 | 1 | 76.4258 | 74.6386 | 570.9405
2027-09-09 08:00 | 3058.15 | 1 | 76.0391 | 74.6386 | 896.2553
2027-09-10 09:00 | 3099.46 | 1 | 90.037 | 74.6386 | 908.3621
2027-09-11 10:00 | 3935.31 | 1.2565 | 85.1276 | 74.6386 | 1153.3255
2027-09-12 11:00 | 5301.67 | 1.7938 | 84.8245 | 74.6386 | 1553.7661
2027-09-13 12:00 | 6383.73 | 2.0542 | 85.3647 | 74.6386 | 1870.8866
2027-09-14 13:00 | 6332.76 | 2.087 | 85.3622 | 74.6386 | 1855.9487
2027-09-15 14:00 | 6904.7 | 2.2584 | 85.5064 | 74.6386 | 2023.5678
2027-09-16 15:00 | 8602.87 | 2.7139 | 85.8829 | 74.6386 | 2521.2523
2027-09-17 16:00 | 8331.05 | 2.7101 | 85.8554 | 74.6386 | 2441.5897
2027-09-18 17:00 | 7877.39 | 2.5726 | 85.9309 | 74.6386 | 2308.6351
2027-09-19 18:00 | 5635.13 | 1.8405 | 85.9732 | 74.6386 | 1651.4936
2027-09-20 19:00 | 3991.32 | 1.2818 | 85.9852 | 74.6386 | 1169.7404
2027-09-21 20:00 | 3092.51 | 1 | 76.9619 | 74.6386 | 906.3252
2027-09-22 21:00 | 2439.83 | 1 | 77.124 | 74.6386 | 715.0436
2027-09-23 22:00 | -763.381 | 2.301 | 77.3724 | 74.6386 | -223.7249
2027-09-24 23:00 | -1327.4 | 3.424 | 76.904 | 74.6386 | -389.0225
2027-09-26 | -1652.99 | 4.1028 | 76.6265 | 74.6386 | -484.4435
2027-09-27 01:00 | -1900.48 | 4.6337 | 76.4501 | 74.6386 | -556.9757
2027-09-28 02:00 | -2035.72 | 4.9156 | 76.2929 | 74.6386 | -596.6106
2027-09-29 03:00 | -2021.19 | 4.8674 | 76.1437 | 74.6386 | -592.3523
2027-09-30 04:00 | -1865.14 | 4.5107 | 76.0528 | 74.6386 | -546.6186
2027-10-01 05:00 | -1339.86 | 3.3143 | 76.0026 | 74.6386 | -392.6742
2027-10-02 06:00 | -862.377 | 2.2962 | 76.0483 | 74.6386 | -252.7378
2027-10-03 07:00 | 718.777 | 1 | 76.588 | 74.6386 | 210.6527
2027-10-04 08:00 | 2347.14 | 1 | 75.8964 | 74.6386 | 687.8788
2027-10-05 09:00 | 2873.78 | 1.0011 | 83.9917 | 74.6386 | 842.2218
2027-10-06 10:00 | 4710.46 | 1.5911 | 84.3224 | 74.6386 | 1380.4996
2027-10-07 11:00 | 6279.92 | 2.0898 | 84.6363 | 74.6386 | 1840.4629
2027-10-08 12:00 | 6940.25 | 2.3068 | 84.8948 | 74.6386 | 2033.9865
2027-10-09 13:00 | 7487.4 | 2.4591 | 85.1756 | 74.6386 | 2194.3403
2027-10-10 14:00 | 8381.99 | 2.7068 | 85.4616 | 74.6386 | 2456.5188
2027-10-11 15:00 | 9736.21 | 3.18 | 85.5663 | 74.6386 | 2853.4015
2027-10-12 16:00 | 9949.3 | 3.2401 | 85.8128 | 74.6386 | 2915.852
2027-10-13 17:00 | 9429.52 | 3.1144 | 85.8742 | 74.6386 | 2763.5195
2027-10-14 18:00 | 7559.8 | 2.4191 | 86.1973 | 74.6386 | 2215.5587
2027-10-15 19:00 | 6113.16 | 1.9174 | 86.3032 | 74.6386 | 1791.5903
2027-10-16 20:00 | 3746.15 | 1.1222 | 86.559 | 74.6386 | 1097.8882
2027-10-17 21:00 | 3151.01 | 1 | 89.935 | 74.6386 | 923.4699
2027-10-18 22:00 | 0 | 0 | 78.2911 | 74.6386 | 0
2027-10-19 23:00 | -199.063 | 0.94716 | 77.4651 | 74.6386 | -58.3396
2027-10-21 | -667.373 | 2.0043 | 76.9637 | 74.6386 | -195.5877
2027-10-22 01:00 | -1002.39 | 2.7034 | 76.7109 | 74.6386 | -293.7715
2027-10-23 02:00 | -1178.05 | 3.0614 | 76.5328 | 74.6386 | -345.2524
2027-10-24 03:00 | -1197.05 | 3.0827 | 76.3846 | 74.6386 | -350.8207
2027-10-25 04:00 | -1202.19 | 3.096 | 76.293 | 74.6386 | -352.3271
2027-10-26 05:00 | -791.692 | 2.1446 | 76.2538 | 74.6386 | -232.022
2027-10-27 06:00 | -362.984 | 1.2262 | 76.3885 | 74.6386 | -106.3801
2027-10-28 07:00 | 2083.85 | 1 | 76.0688 | 74.6386 | 610.7161
2027-10-29 08:00 | 2854.29 | 1 | 89.0483 | 74.6386 | 836.5098
2027-10-30 09:00 | 4448.57 | 1.5181 | 84.2935 | 74.6386 | 1303.7472
2027-10-31 10:00 | 6422.17 | 2.2331 | 84.362 | 74.6386 | 1882.1522
2027-11-01 11:00 | 8040.8 | 2.7367 | 84.7732 | 74.6386 | 2356.5259
2027-11-02 12:00 | 8788.09 | 2.9841 | 85.0751 | 74.6386 | 2575.5349
2027-11-03 13:00 | 9278.67 | 3.0407 | 85.5494 | 74.6386 | 2719.3097
2027-11-04 14:00 | 10139.3 | 3.2786 | 85.8375 | 74.6386 | 2971.5355
2027-11-05 15:00 | 11684.5 | 3.7988 | 85.9958 | 74.6386 | 3424.3889
2027-11-06 16:00 | 11925.2 | 3.919 | 86.1702 | 74.6386 | 3494.9311
2027-11-07 17:00 | 11453.8 | 3.7259 | 86.4305 | 74.6386 | 3356.7774
2027-11-08 18:00 | 9408.81 | 2.9421 | 86.838 | 74.6386 | 2757.45
2027-11-09 19:00 | 7578.13 | 2.3245 | 86.9417 | 74.6386 | 2220.9307
2027-11-10 20:00 | 4900.12 | 1.4924 | 86.8843 | 74.6386 | 1436.0834
2027-11-11 21:00 | 3157.64 | 1.005 | 86.305 | 74.6386 | 925.4129
2027-11-12 22:00 | 3096.51 | 1 | 77.1206 | 74.6386 | 907.4975
2027-11-13 23:00 | 119.785 | 1 | 78.4041 | 74.6386 | 35.1055
2027-11-15 | -154.273 | 0.89145 | 77.7289 | 74.6386 | -45.213
2027-11-16 01:00 | -431.51 | 1.4662 | 77.217 | 74.6386 | -126.4631
2027-11-17 02:00 | -612.433 | 1.8412 | 76.9757 | 74.6386 | -179.4864
2027-11-18 03:00 | -567.378 | 1.7124 | 76.8411 | 74.6386 | -166.2821
2027-11-19 04:00 | -516.524 | 1.6072 | 76.7407 | 74.6386 | -151.3782
2027-11-20 05:00 | -174.278 | 0.8292 | 76.9249 | 74.6386 | -51.0758
2027-11-21 06:00 | 2130.85 | 1 | 76.352 | 74.6386 | 624.4905
2027-11-22 07:00 | 2927.55 | 1 | 86.8277 | 74.6386 | 857.9802
2027-11-23 08:00 | 3366.69 | 1.114 | 84.7686 | 74.6386 | 986.6794
2027-11-24 09:00 | 5278.44 | 1.8207 | 84.5643 | 74.6386 | 1546.9581
2027-11-25 10:00 | 6838.45 | 2.4082 | 84.6122 | 74.6386 | 2004.1519
2027-11-26 11:00 | 8239.21 | 2.7747 | 85.1624 | 74.6386 | 2414.6741
2027-11-27 12:00 | 8994.21 | 2.9555 | 85.5686 | 74.6386 | 2635.9427
2027-11-28 13:00 | 9303.44 | 3.0069 | 85.8923 | 74.6386 | 2726.5691
2027-11-29 14:00 | 10101.5 | 3.2559 | 86.0792 | 74.6386 | 2960.4574
2027-11-30 15:00 | 11559.8 | 3.778 | 86.1487 | 74.6386 | 3387.843
2027-12-01 16:00 | 11778 | 3.8121 | 86.4475 | 74.6386 | 3451.7911
2027-12-02 17:00 | 11374.8 | 3.5874 | 86.8069 | 74.6386 | 3333.6248
2027-12-03 18:00 | 9211.64 | 2.9212 | 86.8569 | 74.6386 | 2699.6652
2027-12-04 19:00 | 7570.79 | 2.3676 | 86.8993 | 74.6386 | 2218.7795
2027-12-05 20:00 | 5179.84 | 1.5487 | 87.1374 | 74.6386 | 1518.0613
2027-12-06 21:00 | 4099.02 | 1.2561 | 86.7228 | 74.6386 | 1201.3042
2027-12-07 22:00 | 3183.79 | 1 | 77.2633 | 74.6386 | 933.0767
2027-12-08 23:00 | 3087.89 | 1 | 77.1275 | 74.6386 | 904.9712
2027-12-10 | 3106.69 | 1 | 77.0017 | 74.6386 | 910.481
2027-12-11 01:00 | 0 | 0 | 78.4277 | 74.6386 | 0
2027-12-12 02:00 | 1552.19 | 1 | 77.3955 | 74.6386 | 454.902
2027-12-13 03:00 | 1817.77 | 1 | 77.2047 | 74.6386 | 532.7358
2027-12-14 04:00 | 2613.43 | 1 | 76.7981 | 74.6386 | 765.9207
2027-12-15 05:00 | 2953.87 | 1 | 76.6357 | 74.6386 | 865.6938
2027-12-16 06:00 | 3089.11 | 1 | 90.4181 | 74.6386 | 905.3288
2027-12-17 07:00 | 3860.04 | 1.238 | 85.4615 | 74.6386 | 1131.2661
2027-12-18 08:00 | 4802.74 | 1.5209 | 85.6285 | 74.6386 | 1407.5442
2027-12-19 09:00 | 6197.81 | 2.113 | 85.2026 | 74.6386 | 1816.3988
2027-12-20 10:00 | 7973.93 | 2.7668 | 85.2343 | 74.6386 | 2336.9282
2027-12-21 11:00 | 9636.49 | 3.2424 | 85.6597 | 74.6386 | 2824.1764
2027-12-22 12:00 | 10653 | 3.4794 | 86.1209 | 74.6386 | 3122.0861
2027-12-23 13:00 | 11259.5 | 3.6352 | 86.453 | 74.6386 | 3299.8337
2027-12-24 14:00 | 12219 | 3.939 | 86.6676 | 74.6386 | 3581.0354
2027-12-25 15:00 | 13524.7 | 4.4856 | 86.6715 | 74.6386 | 3963.6983
2027-12-26 16:00 | 14264.4 | 4.4557 | 87.3504 | 74.6386 | 4180.483
2027-12-27 17:00 | 13092.5 | 4.1299 | 87.4913 | 74.6386 | 3837.033
2027-12-28 18:00 | 10972.9 | 3.4237 | 87.6515 | 74.6386 | 3215.8395
2027-12-29 19:00 | 9117.68 | 2.8318 | 87.6233 | 74.6386 | 2672.1282
2027-12-30 20:00 | 6967.16 | 2.0448 | 87.948 | 74.6386 | 2041.873
2027-12-31 21:00 | 5717.28 | 1.7372 | 87.4718 | 74.6386 | 1675.5694
2028-01-01 22:00 | 3680.14 | 1.1199 | 87.2546 | 74.6386 | 1078.5426
2028-01-02 23:00 | 3165.97 | 1 | 92.1084 | 74.6386 | 927.8542
2028-01-04 | 3145.83 | 1 | 77.4903 | 74.6386 | 921.9518
2028-01-05 01:00 | 3061.36 | 1 | 77.4174 | 74.6386 | 897.1961
2028-01-06 02:00 | 3014.6 | 1 | 77.3443 | 74.6386 | 883.492
2028-01-07 03:00 | 1476.61 | 1 | 77.9975 | 74.6386 | 432.7517
2028-01-08 04:00 | 577.862 | 1 | 78.2464 | 74.6386 | 169.3546
2028-01-09 05:00 | 620.142 | 1 | 78.0337 | 74.6386 | 181.7457
2028-01-10 06:00 | 1839.89 | 1 | 82.8227 | 74.6386 | 539.2185
2028-01-11 07:00 | 3930.17 | 1.438 | 84.6727 | 74.6386 | 1151.8191
2028-01-12 08:00 | 4508.82 | 1.524 | 85.326 | 74.6386 | 1321.4047
2028-01-13 09:00 | 6082.7 | 2.1165 | 85.2207 | 74.6386 | 1782.6634
2028-01-14 10:00 | 7383.39 | 2.5597 | 85.4164 | 74.6386 | 2163.858
2028-01-15 11:00 | 7278.98 | 2.3621 | 86.0844 | 74.6386 | 2133.2585
2028-01-16 12:00 | 7761.76 | 2.5932 | 85.9759 | 74.6386 | 2274.7473
2028-01-17 13:00 | 7904.53 | 2.5673 | 86.2662 | 74.6386 | 2316.5891
2028-01-18 14:00 | 8237.7 | 2.6694 | 86.3554 | 74.6386 | 2414.2316
2028-01-19 15:00 | 9014.79 | 2.9545 | 86.3389 | 74.6386 | 2641.9742
2028-01-20 16:00 | 11755.6 | 3.9024 | 86.3442 | 74.6386 | 3445.2263
2028-01-21 17:00 | 10863.1 | 3.4687 | 86.9083 | 74.6386 | 3183.6603
2028-01-22 18:00 | 9462.9 | 2.9048 | 87.3175 | 74.6386 | 2773.3022
2028-01-23 19:00 | 7761.39 | 2.3731 | 87.3247 | 74.6386 | 2274.6389
2028-01-24 20:00 | 6606.08 | 2.0368 | 87.1753 | 74.6386 | 1936.0509
2028-01-25 21:00 | 5846.53 | 1.7449 | 87.3233 | 74.6386 | 1713.4488
2028-01-26 22:00 | 5071.59 | 1.5409 | 87.0571 | 74.6386 | 1486.3363
2028-01-27 23:00 | 3123.16 | 1 | 77.6407 | 74.6386 | 915.3078
2028-01-29 | 3129.27 | 1 | 77.4221 | 74.6386 | 917.0985
2028-01-30 01:00 | 1995.84 | 1 | 77.8551 | 74.6386 | 584.923
2028-01-31 02:00 | 282.259 | 1 | 78.5294 | 74.6386 | 82.7219
2028-02-01 03:00 | -11.5543 | 0.54676 | 78.4422 | 74.6386 | -3.3862
2028-02-02 04:00 | -126.809 | 0.79067 | 77.8559 | 74.6386 | -37.164
2028-02-03 05:00 | -188.809 | 0.91818 | 77.6201 | 74.6386 | -55.3345
2028-02-04 06:00 | 1944.54 | 1 | 84.716 | 74.6386 | 569.8884
2028-02-05 07:00 | 4249.32 | 1.5539 | 84.5172 | 74.6386 | 1245.3528
2028-02-06 08:00 | 4823.57 | 1.6532 | 85.1441 | 74.6386 | 1413.6488
2028-02-07 09:00 | 5838.19 | 2.0193 | 85.2042 | 74.6386 | 1711.0046
2028-02-08 10:00 | 7225.31 | 2.5945 | 85.0872 | 74.6386 | 2117.5293
2028-02-09 11:00 | 8671.55 | 2.9905 | 85.5642 | 74.6386 | 2541.3804
2028-02-10 12:00 | 9650.33 | 3.14 | 86.1953 | 74.6386 | 2828.2325
2028-02-11 13:00 | 9686.02 | 3.1472 | 86.4037 | 74.6386 | 2838.6922
2028-02-12 14:00 | 10087.5 | 3.2893 | 86.5204 | 74.6386 | 2956.3544
2028-02-13 15:00 | 10221.6 | 3.1818 | 87.0012 | 74.6386 | 2995.6552
2028-02-14 16:00 | 12329.9 | 3.9954 | 86.8061 | 74.6386 | 3613.537
2028-02-15 17:00 | 10926.7 | 3.428 | 87.2879 | 74.6386 | 3202.2997
2028-02-16 18:00 | 9246.51 | 2.8525 | 87.4665 | 74.6386 | 2709.8846
2028-02-17 19:00 | 7537.73 | 2.3075 | 87.4489 | 74.6386 | 2209.0906
2028-02-18 20:00 | 6541.7 | 1.9963 | 87.3475 | 74.6386 | 1917.183
2028-02-19 21:00 | 5668.72 | 1.785 | 86.9914 | 74.6386 | 1661.3378
2028-02-20 22:00 | 5159.1 | 1.5944 | 86.9856 | 74.6386 | 1511.983
2028-02-21 23:00 | 3319.71 | 1 | 91.9334 | 74.6386 | 972.911
2028-02-23 | 3220.42 | 1 | 77.4411 | 74.6386 | 943.8119
2028-02-24 01:00 | 3231.95 | 1 | 77.3124 | 74.6386 | 947.191
2028-02-25 02:00 | 3139.29 | 1 | 77.2862 | 74.6386 | 920.0351
2028-02-26 03:00 | 3221.88 | 1 | 77.1836 | 74.6386 | 944.2398
2028-02-27 04:00 | 3233.86 | 1 | 77.1189 | 74.6386 | 947.7508
2028-02-28 05:00 | 3200.03 | 1 | 87.3088 | 74.6386 | 937.8362
2028-02-29 06:00 | 3254.58 | 1 | 86.5942 | 74.6386 | 953.8232
2028-03-01 07:00 | 3673.68 | 1.098 | 86.5084 | 74.6386 | 1076.6493
2028-03-02 08:00 | 4331.2 | 1.3233 | 86.3435 | 74.6386 | 1269.3494
2028-03-03 09:00 | 6352.48 | 2.1484 | 85.6347 | 74.6386 | 1861.7281
2028-03-04 10:00 | 7566.74 | 2.6663 | 85.5126 | 74.6386 | 2217.5926
2028-03-05 11:00 | 9237.39 | 3.0521 | 86.1386 | 74.6386 | 2707.2118
2028-03-06 12:00 | 9855.36 | 3.2327 | 86.4157 | 74.6386 | 2888.3209
2028-03-07 13:00 | 9509.96 | 3.0724 | 86.7163 | 74.6386 | 2787.0942
2028-03-08 14:00 | 9655.59 | 3.0946 | 86.877 | 74.6386 | 2829.7741
2028-03-09 15:00 | 10189 | 3.2852 | 86.9158 | 74.6386 | 2986.1011
2028-03-10 16:00 | 9598.61 | 3.0377 | 87.1518 | 74.6386 | 2813.0749
2028-03-11 17:00 | 9515.14 | 2.9962 | 87.2088 | 74.6386 | 2788.6123
2028-03-12 18:00 | 8338.55 | 2.6445 | 87.1794 | 74.6386 | 2443.7878
2028-03-13 19:00 | 7493.49 | 2.3022 | 87.381 | 74.6386 | 2196.1251
2028-03-14 20:00 | 5671.43 | 1.6239 | 87.8796 | 74.6386 | 1662.1321
2028-03-15 21:00 | 4804.83 | 1.4533 | 87.2721 | 74.6386 | 1408.1567
2028-03-16 22:00 | 3131.78 | 1 | 89.6743 | 74.6386 | 917.8341
2028-03-17 23:00 | 3132.01 | 1 | 77.5656 | 74.6386 | 917.9015
2028-03-19 | 3074.74 | 1 | 77.4577 | 74.6386 | 901.1173
2028-03-20 01:00 | 3128.99 | 1 | 77.3387 | 74.6386 | 917.0164
2028-03-21 02:00 | 3120.34 | 1 | 77.2801 | 74.6386 | 914.4814
2028-03-22 03:00 | 3166.96 | 1 | 77.2011 | 74.6386 | 928.1444
2028-03-23 04:00 | 3182.7 | 1 | 77.1642 | 74.6386 | 932.7573
2028-03-24 05:00 | 3232.54 | 1 | 88.0615 | 74.6386 | 947.364
2028-03-25 06:00 | 3605.99 | 1.1196 | 86.265 | 74.6386 | 1056.8113
2028-03-26 07:00 | 5358.19 | 1.6777 | 86.2041 | 74.6386 | 1570.3305
2028-03-27 08:00 | 5930.03 | 1.8796 | 86.241 | 74.6386 | 1737.9202
2028-03-28 09:00 | 6866.01 | 2.4046 | 85.6381 | 74.6386 | 2012.2289
2028-03-29 10:00 | 8514.61 | 3.0645 | 85.5837 | 74.6386 | 2495.3859
2028-03-30 11:00 | 10374.6 | 3.4788 | 86.2666 | 74.6386 | 3040.4951
2028-03-31 12:00 | 11319 | 3.7684 | 86.5797 | 74.6386 | 3317.2714
2028-04-01 13:00 | 12001.3 | 3.8926 | 86.99 | 74.6386 | 3517.2338
2028-04-02 14:00 | 12875.4 | 3.9748 | 87.5584 | 74.6386 | 3773.4073
2028-04-03 15:00 | 13798.3 | 4.4545 | 87.4336 | 74.6386 | 4043.8825
2028-04-04 16:00 | 14255.9 | 4.59 | 87.67 | 74.6386 | 4177.9919
2028-04-05 17:00 | 14269.7 | 4.4742 | 88.0528 | 74.6386 | 4182.0362
2028-04-06 18:00 | 11989.9 | 3.7654 | 88.1909 | 74.6386 | 3513.8928
2028-04-07 19:00 | 10384.3 | 3.2285 | 88.2233 | 74.6386 | 3043.3379
2028-04-08 20:00 | 8140.55 | 2.4113 | 88.5016 | 74.6386 | 2385.7597
2028-04-09 21:00 | 6923.19 | 2.0906 | 88.1616 | 74.6386 | 2028.9867
2028-04-10 22:00 | 4900.42 | 1.4335 | 88.2299 | 74.6386 | 1436.1713
2028-04-11 23:00 | 4060.35 | 1.2102 | 87.8141 | 74.6386 | 1189.9711
2028-04-13 | 3494.62 | 1.0904 | 87.2402 | 74.6386 | 1024.172
2028-04-14 01:00 | 3164.4 | 1 | 88.0482 | 74.6386 | 927.3941
2028-04-15 02:00 | 3080.61 | 1 | 88.3474 | 74.6386 | 902.8377
2028-04-16 03:00 | 3208.13 | 1 | 87.7919 | 74.6386 | 940.2101
2028-04-17 04:00 | 3138.75 | 1 | 86.8182 | 74.6386 | 919.8768
2028-04-18 05:00 | 3836.06 | 1.2226 | 86.4692 | 74.6386 | 1124.2382
2028-04-19 06:00 | 5135.23 | 1.5876 | 86.6912 | 74.6386 | 1504.9874
2028-04-20 07:00 | 6531.45 | 2.1481 | 86.3084 | 74.6386 | 1914.179
2028-04-21 08:00 | 6946.78 | 2.3007 | 86.3984 | 74.6386 | 2035.9002
2028-04-22 09:00 | 8337.29 | 2.922 | 86.1051 | 74.6386 | 2443.4185
2028-04-23 10:00 | 10294 | 3.4694 | 86.5443 | 74.6386 | 3016.8736
2028-04-24 11:00 | 11475.3 | 3.8893 | 86.7582 | 74.6386 | 3363.0784
2028-04-25 12:00 | 13203.9 | 4.3058 | 87.2696 | 74.6386 | 3869.6811
2028-04-26 13:00 | 13064 | 4.2621 | 87.5423 | 74.6386 | 3828.6805
2028-04-27 14:00 | 12892.8 | 4.077 | 87.9522 | 74.6386 | 3778.5067
2028-04-28 15:00 | 14018 | 4.3887 | 88.1419 | 74.6386 | 4108.2703
2028-04-29 16:00 | 13027.5 | 4.3033 | 87.9296 | 74.6386 | 3817.9834
2028-04-30 17:00 | 12113.8 | 3.8337 | 88.2991 | 74.6386 | 3550.2043
2028-05-01 18:00 | 10745.7 | 3.3017 | 88.5004 | 74.6386 | 3149.2538
2028-05-02 19:00 | 9417.72 | 2.9221 | 88.3485 | 74.6386 | 2760.0613
2028-05-03 20:00 | 7272.87 | 2.1411 | 88.6547 | 74.6386 | 2131.4678
2028-05-04 21:00 | 6435.17 | 1.8564 | 88.6024 | 74.6386 | 1885.9622
2028-05-05 22:00 | 4312.22 | 1.2667 | 88.2799 | 74.6386 | 1263.7869
2028-05-06 23:00 | 3566.04 | 1.0886 | 87.7153 | 74.6386 | 1045.1032
2028-05-08 | 3115.91 | 1 | 87.9397 | 74.6386 | 913.1831
2028-05-09 01:00 | 3090 | 1 | 89.975 | 74.6386 | 905.5896
2028-05-10 02:00 | 3151.26 | 1 | 91.5854 | 74.6386 | 923.5431
2028-05-11 03:00 | 3163.53 | 1 | 89.8179 | 74.6386 | 927.1391
2028-05-12 04:00 | 3148.1 | 1 | 88.0616 | 74.6386 | 922.617
2028-05-13 05:00 | 3827.11 | 1.1963 | 86.7763 | 74.6386 | 1121.6152
2028-05-14 06:00 | 4568.31 | 1.3956 | 86.9528 | 74.6386 | 1338.8395
2028-05-15 07:00 | 6025.5 | 1.9332 | 86.615 | 74.6386 | 1765.8997
2028-05-16 08:00 | 6985.34 | 2.3109 | 86.5098 | 74.6386 | 2047.2011
2028-05-17 09:00 | 8732.08 | 2.987 | 86.4016 | 74.6386 | 2559.12
2028-05-18 10:00 | 10125.1 | 3.3973 | 86.7405 | 74.6386 | 2967.3739
2028-05-19 11:00 | 10914.6 | 3.6647 | 86.9589 | 74.6386 | 3198.7535
2028-05-20 12:00 | 12114.4 | 3.9505 | 87.3585 | 74.6386 | 3550.3802
2028-05-21 13:00 | 12687.8 | 4.1814 | 87.4937 | 74.6386 | 3718.4271
2028-05-22 14:00 | 12789.1 | 4.1071 | 87.8699 | 74.6386 | 3748.1152
2028-05-23 15:00 | 13476.1 | 4.157 | 88.2983 | 74.6386 | 3949.455
2028-05-24 16:00 | 12846.2 | 3.8974 | 88.5737 | 74.6386 | 3764.8496
2028-05-25 17:00 | 11510.2 | 3.8553 | 87.9057 | 74.6386 | 3373.3066
2028-05-26 18:00 | 9913.27 | 3.1477 | 88.2564 | 74.6386 | 2905.2926
2028-05-27 19:00 | 8634.12 | 2.7207 | 88.2008 | 74.6386 | 2530.4108
2028-05-28 20:00 | 6971.37 | 1.974 | 88.9193 | 74.6386 | 2043.1069
2028-05-29 21:00 | 6083.77 | 1.8075 | 88.3293 | 74.6386 | 1782.977
2028-05-30 22:00 | 3718.21 | 1.1273 | 87.9938 | 74.6386 | 1089.6998
2028-05-31 23:00 | 3159.11 | 1 | 87.951 | 74.6386 | 925.8437
2028-06-02 | 3167.13 | 1 | 89.6393 | 74.6386 | 928.1942
2028-06-03 01:00 | 3059.05 | 1 | 91.0132 | 74.6386 | 896.5191
2028-06-04 02:00 | 3143.96 | 1 | 91.9474 | 74.6386 | 921.4037
2028-06-05 03:00 | 3174.86 | 1 | 90.0887 | 74.6386 | 930.4596
2028-06-06 04:00 | 3252.08 | 1 | 88.2963 | 74.6386 | 953.0906
2028-06-07 05:00 | 4019.18 | 1.2434 | 86.8806 | 74.6386 | 1177.9054
2028-06-08 06:00 | 4992.77 | 1.5403 | 86.9156 | 74.6386 | 1463.2364
2028-06-09 07:00 | 6411.68 | 2.0352 | 86.7619 | 74.6386 | 1879.0779
2028-06-10 08:00 | 7303.28 | 2.3018 | 86.9443 | 74.6386 | 2140.3801
2028-06-11 09:00 | 8805.93 | 2.9388 | 86.6546 | 74.6386 | 2580.7633
2028-06-12 10:00 | 9917.21 | 3.4475 | 86.563 | 74.6386 | 2906.4473
2028-06-13 11:00 | 11432.5 | 3.8431 | 86.9936 | 74.6386 | 3350.535
2028-06-14 12:00 | 11656 | 3.8829 | 87.2871 | 74.6386 | 3416.0364
2028-06-15 13:00 | 12495.9 | 3.9977 | 87.7386 | 74.6386 | 3662.1868
2028-06-16 14:00 | 12652.7 | 4.1683 | 87.6987 | 74.6386 | 3708.1403
2028-06-17 15:00 | 14557.2 | 4.8425 | 87.7595 | 74.6386 | 4266.2942
2028-06-18 16:00 | 14446.7 | 4.8709 | 87.9081 | 74.6386 | 4233.9098
2028-06-19 17:00 | 13615.8 | 4.516 | 88.1787 | 74.6386 | 3990.3971
2028-06-20 18:00 | 11760.5 | 3.7052 | 88.614 | 74.6386 | 3446.6623
2028-06-21 19:00 | 10311.9 | 3.2122 | 88.6343 | 74.6386 | 3022.1196
2028-06-22 20:00 | 8144.33 | 2.445 | 88.8235 | 74.6386 | 2386.8675
2028-06-23 21:00 | 6860.72 | 2.1022 | 88.456 | 74.6386 | 2010.6786
2028-06-24 22:00 | 4771.8 | 1.4097 | 88.5418 | 74.6386 | 1398.4765
2028-06-25 23:00 | 3373.63 | 1.0458 | 87.8908 | 74.6386 | 988.7134
2028-06-27 | 3174.17 | 1 | 88.6308 | 74.6386 | 930.2574
2028-06-28 01:00 | 3319.76 | 1 | 91.9436 | 74.6386 | 972.9256
2028-06-29 02:00 | 3162.66 | 1 | 78.1666 | 74.6386 | 926.8842
2028-06-30 03:00 | 3125.09 | 1 | 78.0638 | 74.6386 | 915.8735
2028-07-01 04:00 | 2892.2 | 1 | 78.0788 | 74.6386 | 847.6201
2028-07-02 05:00 | 3089.56 | 1 | 77.8916 | 74.6386 | 905.4607
2028-07-03 06:00 | 3276.86 | 1 | 88.6159 | 74.6386 | 960.3529
2028-07-04 07:00 | 4551.83 | 1.4639 | 86.627 | 74.6386 | 1334.0097
2028-07-05 08:00 | 4164.5 | 1.3761 | 86.4824 | 74.6386 | 1220.4945
2028-07-06 09:00 | 5679.62 | 1.8102 | 86.7202 | 74.6386 | 1664.5323
2028-07-07 10:00 | 7019.88 | 2.3561 | 86.4317 | 74.6386 | 2057.3237
2028-07-08 11:00 | 7836.06 | 2.7371 | 86.3016 | 74.6386 | 2296.5225
2028-07-09 12:00 | 8262.62 | 2.8597 | 86.495 | 74.6386 | 2421.5349
2028-07-10 13:00 | 9141.83 | 3.014 | 86.925 | 74.6386 | 2679.2059
2028-07-11 14:00 | 10317.2 | 3.3352 | 87.1989 | 74.6386 | 3023.6728
2028-07-12 15:00 | 10685.6 | 3.5137 | 87.2326 | 74.6386 | 3131.6402
2028-07-13 16:00 | 13033.6 | 4.3293 | 87.2766 | 74.6386 | 3819.7711
2028-07-14 17:00 | 11809.7 | 3.8616 | 87.645 | 74.6386 | 3461.0814
2028-07-15 18:00 | 10006.7 | 3.1541 | 88.0018 | 74.6386 | 2932.6743
2028-07-16 19:00 | 8453.21 | 2.5146 | 88.3816 | 74.6386 | 2477.3913
2028-07-17 20:00 | 6961.64 | 2.1152 | 88.1105 | 74.6386 | 2040.2553
2028-07-18 21:00 | 5676.13 | 1.7455 | 87.8766 | 74.6386 | 1663.5095
2028-07-19 22:00 | 4731.32 | 1.4546 | 87.6917 | 74.6386 | 1386.613
2028-07-20 23:00 | 3008.84 | 1 | 78.3728 | 74.6386 | 881.804
2028-07-22 | 1933.63 | 1 | 78.6655 | 74.6386 | 566.691
2028-07-23 01:00 | 0 | 0 | 79.3757 | 74.6386 | 0
2028-07-24 02:00 | -112.017 | 0.76448 | 78.7367 | 74.6386 | -32.8289
2028-07-25 03:00 | -266.952 | 1.0898 | 78.2992 | 74.6386 | -78.2359
2028-07-26 04:00 | -346.831 | 1.2481 | 78.0439 | 74.6386 | -101.6461
2028-07-27 05:00 | -451.344 | 1.4759 | 77.8283 | 74.6386 | -132.2759
2028-07-28 06:00 | 1949.75 | 1 | 77.4813 | 74.6386 | 571.4153
2028-07-29 07:00 | 3166.22 | 1.1031 | 85.3048 | 74.6386 | 927.9275
2028-07-30 08:00 | 3782.84 | 1.2638 | 85.6975 | 74.6386 | 1108.641
2028-07-31 09:00 | 5235.99 | 1.7907 | 85.608 | 74.6386 | 1534.5172
2028-08-01 10:00 | 6948.26 | 2.3447 | 85.8424 | 74.6386 | 2036.334
2028-08-02 11:00 | 8447.87 | 2.8777 | 85.9957 | 74.6386 | 2475.8263
2028-08-03 12:00 | 9613.3 | 3.1421 | 86.513 | 74.6386 | 2817.3801
2028-08-04 13:00 | 10292.2 | 3.4289 | 86.601 | 74.6386 | 3016.3461
2028-08-05 14:00 | 10650 | 3.5038 | 86.8914 | 74.6386 | 3121.2069
2028-08-06 15:00 | 11121.7 | 3.6431 | 87.0838 | 74.6386 | 3259.4485
2028-08-07 16:00 | 13678.5 | 4.4526 | 87.272 | 74.6386 | 4008.7726
2028-08-08 17:00 | 12028.3 | 3.924 | 87.5612 | 74.6386 | 3525.1468
2028-08-09 18:00 | 10575.3 | 3.1894 | 88.2243 | 74.6386 | 3099.3145
2028-08-10 19:00 | 8638.82 | 2.649 | 88.0513 | 74.6386 | 2531.7882
2028-08-11 20:00 | 7251.4 | 2.2368 | 87.8954 | 74.6386 | 2125.1756
2028-08-12 21:00 | 6047.5 | 1.8589 | 87.7877 | 74.6386 | 1772.3473
2028-08-13 22:00 | 5267.97 | 1.6365 | 87.5262 | 74.6386 | 1543.8896
2028-08-14 23:00 | 3310.87 | 1 | 92.7574 | 74.6386 | 970.3202
2028-08-16 | 3116.24 | 1 | 78.013 | 74.6386 | 913.2798
2028-08-17 01:00 | 3110.94 | 1 | 77.8667 | 74.6386 | 911.7265
2028-08-18 02:00 | 3210.93 | 1 | 77.7266 | 74.6386 | 941.0307
2028-08-19 03:00 | 3180.88 | 1 | 77.6739 | 74.6386 | 932.2239
2028-08-20 04:00 | 3217.16 | 1 | 77.5781 | 74.6386 | 942.8565
2028-08-21 05:00 | 3136.91 | 1 | 90.3058 | 74.6386 | 919.3376
2028-08-22 06:00 | 3465.03 | 1.0637 | 86.7432 | 74.6386 | 1015.5
2028-08-23 07:00 | 5263.7 | 1.5763 | 86.9245 | 74.6386 | 1542.6382
2028-08-24 08:00 | 5860.5 | 1.8644 | 86.5782 | 74.6386 | 1717.543
2028-08-25 09:00 | 6826.9 | 2.3548 | 86.0993 | 74.6386 | 2000.7669
2028-08-26 10:00 | 8992.68 | 3.0685 | 86.2869 | 74.6386 | 2635.4943
2028-08-27 11:00 | 10160.6 | 3.4185 | 86.6263 | 74.6386 | 2977.7779
2028-08-28 12:00 | 10975.5 | 3.6437 | 86.9549 | 74.6386 | 3216.6015
2028-08-29 13:00 | 11588.1 | 3.7278 | 87.3738 | 74.6386 | 3396.1369
2028-08-30 14:00 | 12296.8 | 4.0043 | 87.4622 | 74.6386 | 3603.8363
2028-08-31 15:00 | 13886.5 | 4.569 | 87.5691 | 74.6386 | 4069.7314
2028-09-01 16:00 | 14104.2 | 4.5597 | 87.9253 | 74.6386 | 4133.533
2028-09-02 17:00 | 13285.5 | 4.2074 | 88.2539 | 74.6386 | 3893.5957
2028-09-03 18:00 | 11292.7 | 3.5498 | 88.3848 | 74.6386 | 3309.5637
2028-09-04 19:00 | 9953.29 | 3.0894 | 88.4173 | 74.6386 | 2917.0214
2028-09-05 20:00 | 7647.55 | 2.3606 | 88.3698 | 74.6386 | 2241.2757
2028-09-06 21:00 | 6671.88 | 2.0634 | 88.1507 | 74.6386 | 1955.335
2028-09-07 22:00 | 4738.87 | 1.4139 | 88.2406 | 74.6386 | 1388.8257
2028-09-08 23:00 | 3704.42 | 1.158 | 87.631 | 74.6386 | 1085.6583
2028-09-10 | 3193.16 | 1 | 88.4811 | 74.6386 | 935.8228
2028-09-11 01:00 | 3183.8 | 1 | 91.6439 | 74.6386 | 933.0797
2028-09-12 02:00 | 3161.48 | 1 | 78.0166 | 74.6386 | 926.5383
2028-09-13 03:00 | 3080.08 | 1 | 77.9516 | 74.6386 | 902.6823
2028-09-14 04:00 | 3210.76 | 1 | 91.9931 | 74.6386 | 940.9809
2028-09-15 05:00 | 3272.89 | 1.0139 | 86.9201 | 74.6386 | 959.1894
2028-09-16 06:00 | 4058.2 | 1.2682 | 86.8164 | 74.6386 | 1189.341
2028-09-17 07:00 | 5652.11 | 1.7669 | 86.8254 | 74.6386 | 1656.4699
2028-09-18 08:00 | 6312.12 | 1.9775 | 86.9262 | 74.6386 | 1849.8998
2028-09-19 09:00 | 7603.11 | 2.5069 | 86.6516 | 74.6386 | 2228.2516
2028-09-20 10:00 | 8972.68 | 3.0253 | 86.6409 | 74.6386 | 2629.6329
2028-09-21 11:00 | 9853.09 | 3.3057 | 86.8716 | 74.6386 | 2887.6556
2028-09-22 12:00 | 10638.8 | 3.5343 | 87.1242 | 74.6386 | 3117.9245
2028-09-23 13:00 | 11483.9 | 3.8395 | 87.2435 | 74.6386 | 3365.5989
2028-09-24 14:00 | 11860.3 | 3.9866 | 87.3818 | 74.6386 | 3475.9108
2028-09-25 15:00 | 13728.8 | 4.5212 | 87.6662 | 74.6386 | 4023.5141
2028-09-26 16:00 | 14338.1 | 4.657 | 87.9964 | 74.6386 | 4202.0823
2028-09-27 17:00 | 13701.6 | 4.4707 | 88.1689 | 74.6386 | 4015.5426
2028-09-28 18:00 | 12063.2 | 3.7502 | 88.6271 | 74.6386 | 3535.3749
2028-09-29 19:00 | 10889 | 3.2558 | 88.9003 | 74.6386 | 3191.2509
2028-09-30 20:00 | 8488.11 | 2.5262 | 88.8867 | 74.6386 | 2487.6195
2028-10-01 21:00 | 7256.12 | 2.1825 | 88.6135 | 74.6386 | 2126.5589
2028-10-02 22:00 | 5022.27 | 1.4917 | 88.5218 | 74.6386 | 1471.882
2028-10-03 23:00 | 4081.47 | 1.2168 | 88.2263 | 74.6386 | 1196.1608
2028-10-05 | 3386.96 | 1.0344 | 87.8123 | 74.6386 | 992.62
2028-10-06 01:00 | 3222.99 | 1 | 88.4037 | 74.6386 | 944.5651
2028-10-07 02:00 | 3229.02 | 1 | 88.0161 | 74.6386 | 946.3323
2028-10-08 03:00 | 3363.98 | 1.0398 | 87.2638 | 74.6386 | 985.8852
2028-10-09 04:00 | 3835.84 | 1.2095 | 87.0331 | 74.6386 | 1124.1737
2028-10-10 05:00 | 4975.46 | 1.5789 | 86.9519 | 74.6386 | 1458.1634
2028-10-11 06:00 | 5485.08 | 1.7526 | 86.9522 | 74.6386 | 1607.5183
2028-10-12 07:00 | 6805.52 | 2.2389 | 86.7829 | 74.6386 | 1994.501
2028-10-13 08:00 | 7319.76 | 2.4054 | 86.9096 | 74.6386 | 2145.2099
2028-10-14 09:00 | 8623.07 | 2.925 | 86.7896 | 74.6386 | 2527.1724
2028-10-15 10:00 | 10310.1 | 3.4944 | 86.9557 | 74.6386 | 3021.592
2028-10-16 11:00 | 12033.5 | 4.0376 | 87.2487 | 74.6386 | 3526.6707
2028-10-17 12:00 | 12950.7 | 4.2786 | 87.6272 | 74.6386 | 3795.4755
2028-10-18 13:00 | 13361.6 | 4.3685 | 87.9336 | 74.6386 | 3915.8984
2028-10-19 14:00 | 13717.8 | 4.3745 | 88.3065 | 74.6386 | 4020.2903
2028-10-20 15:00 | 13755.4 | 4.419 | 88.4122 | 74.6386 | 4031.3098
2028-10-21 16:00 | 14495.5 | 4.5564 | 88.6894 | 74.6386 | 4248.2117
2028-10-22 17:00 | 14153.1 | 4.4765 | 88.7819 | 74.6386 | 4147.8642
2028-10-23 18:00 | 11881.1 | 3.7196 | 88.9452 | 74.6386 | 3482.0067
2028-10-24 19:00 | 10480.3 | 3.249 | 88.9241 | 74.6386 | 3071.4727
2028-10-25 20:00 | 8657.58 | 2.528 | 89.2768 | 74.6386 | 2537.2862
2028-10-26 21:00 | 7536.04 | 2.2528 | 88.9185 | 74.6386 | 2208.5953
2028-10-27 22:00 | 5609.39 | 1.5897 | 89.1741 | 74.6386 | 1643.9499
2028-10-28 23:00 | 4541.94 | 1.3833 | 88.3393 | 74.6386 | 1331.1112
2028-10-30 | 3703.54 | 1.1878 | 87.7227 | 74.6386 | 1085.4004
2028-10-31 01:00 | 3201.55 | 1.0108 | 87.6372 | 74.6386 | 938.2817
2028-11-01 02:00 | 3123.66 | 1 | 87.5137 | 74.6386 | 915.4544
2028-11-02 03:00 | 3357.61 | 1.0578 | 87.347 | 74.6386 | 984.0184
2028-11-03 04:00 | 3514.64 | 1.1265 | 87.1341 | 74.6386 | 1030.0393
2028-11-04 05:00 | 4587.2 | 1.4428 | 87.2072 | 74.6386 | 1344.3756
2028-11-05 06:00 | 5679.85 | 1.8003 | 87.1728 | 74.6386 | 1664.5997
2028-11-06 07:00 | 6608.13 | 2.2241 | 86.8151 | 74.6386 | 1936.6517
2028-11-07 08:00 | 7208.68 | 2.3977 | 87.0003 | 74.6386 | 2112.6556
2028-11-08 09:00 | 8999.6 | 3.0176 | 87.0353 | 74.6386 | 2637.5224
2028-11-09 10:00 | 10303.6 | 3.4731 | 87.1898 | 74.6386 | 3019.6871
2028-11-10 11:00 | 11669.3 | 3.9575 | 87.3541 | 74.6386 | 3419.9342
2028-11-11 12:00 | 12401.9 | 4.054 | 87.8363 | 74.6386 | 3634.6381
2028-11-12 13:00 | 12621.2 | 4.1518 | 87.9875 | 74.6386 | 3698.9086
2028-11-13 14:00 | 13268.7 | 4.2648 | 88.3111 | 74.6386 | 3888.6721
2028-11-14 15:00 | 14730.9 | 4.8493 | 88.2921 | 74.6386 | 4317.2006
2028-11-15 16:00 | 15029 | 4.8751 | 88.6176 | 74.6386 | 4404.5651
2028-11-16 17:00 | 14329 | 4.5526 | 88.9335 | 74.6386 | 4199.4154
2028-11-17 18:00 | 12346.3 | 3.9173 | 89.0123 | 74.6386 | 3618.3434
2028-11-18 19:00 | 11612.3 | 3.5166 | 89.3023 | 74.6386 | 3403.2292
2028-11-19 20:00 | 9165.28 | 2.7817 | 89.2401 | 74.6386 | 2686.0784
2028-11-20 21:00 | 7828.65 | 2.413 | 88.928 | 74.6386 | 2294.3508
2028-11-21 22:00 | 5767.59 | 1.6584 | 89.2769 | 74.6386 | 1690.3138
2028-11-22 23:00 | 4765.78 | 1.4203 | 88.7234 | 74.6386 | 1396.7122
2028-11-24 | 4058.31 | 1.2835 | 88.0413 | 74.6386 | 1189.3733
2028-11-25 01:00 | 3887.05 | 1.1704 | 88.2206 | 74.6386 | 1139.1819
2028-11-26 02:00 | 3605.2 | 1.1198 | 87.8374 | 74.6386 | 1056.5798
2028-11-27 03:00 | 3620.56 | 1.1515 | 87.5211 | 74.6386 | 1061.0814
2028-11-28 04:00 | 3893.52 | 1.2313 | 87.4616 | 74.6386 | 1141.0781
2028-11-29 05:00 | 4704.85 | 1.5072 | 87.301 | 74.6386 | 1378.8554
2028-11-30 06:00 | 5527.26 | 1.7594 | 87.3526 | 74.6386 | 1619.88
2028-12-01 07:00 | 6570.08 | 2.2252 | 86.9408 | 74.6386 | 1925.5004
2028-12-02 08:00 | 7411.99 | 2.4929 | 87.0784 | 74.6386 | 2172.2398
2028-12-03 09:00 | 8799.64 | 2.9738 | 87.1469 | 74.6386 | 2578.9199
2028-12-04 10:00 | 10194.4 | 3.3998 | 87.4009 | 74.6386 | 2987.6837
2028-12-05 11:00 | 11153.1 | 3.7892 | 87.4649 | 74.6386 | 3268.651
2028-12-06 12:00 | 12468.1 | 4.0596 | 87.9528 | 74.6386 | 3654.0394
2028-12-07 13:00 | 12771.1 | 4.1411 | 88.1968 | 74.6386 | 3742.8399
2028-12-08 14:00 | 13023.4 | 4.1718 | 88.4514 | 74.6386 | 3816.7818
2028-12-09 15:00 | 14218.8 | 4.6472 | 88.4296 | 74.6386 | 4167.1189
2028-12-10 16:00 | 14800.7 | 4.8015 | 88.6644 | 74.6386 | 4337.657
2028-12-11 17:00 | 14572.4 | 4.5949 | 89.0442 | 74.6386 | 4270.7489
2028-12-12 18:00 | 12569.5 | 3.9104 | 89.2483 | 74.6386 | 3683.7568
2028-12-13 19:00 | 10605.1 | 3.2894 | 89.2138 | 74.6386 | 3108.048
2028-12-14 20:00 | 8206.41 | 2.4514 | 89.3726 | 74.6386 | 2405.0614
2028-12-15 21:00 | 7059.46 | 2.1089 | 89.1399 | 74.6386 | 2068.9235
2028-12-16 22:00 | 4896.48 | 1.4156 | 89.1937 | 74.6386 | 1435.0166
2028-12-17 23:00 | 3244.5 | 1 | 88.4391 | 74.6386 | 950.8691
2028-12-19 | 3121.26 | 1 | 90.9126 | 74.6386 | 914.751
2028-12-20 01:00 | 3146.58 | 1 | 78.7072 | 74.6386 | 922.1716
2028-12-21 02:00 | 3054.28 | 1 | 78.6264 | 74.6386 | 895.1211
2028-12-22 03:00 | 3114.61 | 1 | 78.4708 | 74.6386 | 912.8021
2028-12-23 04:00 | 3125.72 | 1 | 78.3684 | 74.6386 | 916.0581
2028-12-24 05:00 | 3166.9 | 1 | 78.2699 | 74.6386 | 928.1268
2028-12-25 06:00 | 3834.27 | 1.1582 | 87.5713 | 74.6386 | 1123.7136
2028-12-26 07:00 | 6191.56 | 2.0468 | 86.8689 | 74.6386 | 1814.5671
2028-12-27 08:00 | 6424.25 | 2.0913 | 87.135 | 74.6386 | 1882.7618
2028-12-28 09:00 | 7556.93 | 2.5728 | 86.8986 | 74.6386 | 2214.7176
2028-12-29 10:00 | 8766.1 | 3.0408 | 86.8909 | 74.6386 | 2569.0903
2028-12-30 11:00 | 10252.6 | 3.4594 | 87.2573 | 74.6386 | 3004.7405
2028-12-31 12:00 | 10883 | 3.6179 | 87.5768 | 74.6386 | 3189.4925
2029-01-01 13:00 | 11441.9 | 3.6873 | 87.9612 | 74.6386 | 3353.2899
2029-01-02 14:00 | 11993.3 | 3.8462 | 88.1462 | 74.6386 | 3514.8893
2029-01-03 15:00 | 12808.6 | 4.1245 | 88.2543 | 74.6386 | 3753.8301
2029-01-04 16:00 | 14667.7 | 4.838 | 88.2335 | 74.6386 | 4298.6785
2029-01-05 17:00 | 13282.5 | 4.2578 | 88.6845 | 74.6386 | 3892.7165
2029-01-06 18:00 | 11295.4 | 3.6003 | 88.7904 | 74.6386 | 3310.355
2029-01-07 19:00 | 9574.88 | 3.0343 | 88.742 | 74.6386 | 2806.1203
2029-01-08 20:00 | 8457.22 | 2.6412 | 88.7252 | 74.6386 | 2478.5665
2029-01-09 21:00 | 7546.37 | 2.3153 | 88.7311 | 74.6386 | 2211.6227
2029-01-10 22:00 | 6913.47 | 2.0911 | 88.6929 | 74.6386 | 2026.1381
2029-01-11 23:00 | 3569.4 | 1.0747 | 88.5991 | 74.6386 | 1046.0879
2029-01-13 | 3133.44 | 1 | 89.7462 | 74.6386 | 918.3206
2029-01-14 01:00 | 3232.95 | 1 | 78.6391 | 74.6386 | 947.4841
2029-01-15 02:00 | 3099.96 | 1 | 78.5818 | 74.6386 | 908.5086
2029-01-16 03:00 | 3084.22 | 1 | 78.4667 | 74.6386 | 903.8957
2029-01-17 04:00 | 3193.93 | 1 | 78.2875 | 74.6386 | 936.0485
2029-01-18 05:00 | 3139.48 | 1 | 78.2477 | 74.6386 | 920.0908
2029-01-19 06:00 | 3498.37 | 1.0546 | 87.5614 | 74.6386 | 1025.271
2029-01-20 07:00 | 6143.24 | 1.8454 | 87.5417 | 74.6386 | 1800.4059
2029-01-21 08:00 | 5890.14 | 1.7921 | 87.6053 | 74.6386 | 1726.2296
2029-01-22 09:00 | 7326.72 | 2.4437 | 86.9745 | 74.6386 | 2147.2497
2029-01-23 10:00 | 8972.11 | 3.0717 | 86.9045 | 74.6386 | 2629.4659
2029-01-24 11:00 | 10269.9 | 3.4828 | 87.1802 | 74.6386 | 3009.8106
2029-01-25 12:00 | 11265 | 3.6994 | 87.6301 | 74.6386 | 3301.4456
2029-01-26 13:00 | 11602.1 | 3.7227 | 87.9873 | 74.6386 | 3400.2399
2029-01-27 14:00 | 11689.5 | 3.7194 | 88.2079 | 74.6386 | 3425.8543
2029-01-28 15:00 | 12321.1 | 3.8459 | 88.4641 | 74.6386 | 3610.958
2029-01-29 16:00 | 13887.9 | 4.6851 | 88.0191 | 74.6386 | 4070.1417
2029-01-30 17:00 | 12850.4 | 4.1157 | 88.6022 | 74.6386 | 3766.0805
2029-01-31 18:00 | 11528.2 | 3.5751 | 88.9101 | 74.6386 | 3378.5819
2029-02-01 19:00 | 10056.2 | 3.1609 | 88.7666 | 74.6386 | 2947.1813
2029-02-02 20:00 | 8727.32 | 2.8399 | 88.4296 | 74.6386 | 2557.725
2029-02-03 21:00 | 8213.37 | 2.5367 | 88.6981 | 74.6386 | 2407.1011
2029-02-04 22:00 | 7436.27 | 2.3042 | 88.56 | 74.6386 | 2179.3556
2029-02-05 23:00 | 5169.17 | 1.4455 | 89.2748 | 74.6386 | 1514.9342
2029-02-07 | 4517.74 | 1.3127 | 88.7214 | 74.6386 | 1324.0189
2029-02-08 01:00 | 3975.79 | 1.2258 | 88.0732 | 74.6386 | 1165.189
2029-02-09 02:00 | 3621.34 | 1.1323 | 87.8261 | 74.6386 | 1061.31
2029-02-10 03:00 | 3950.27 | 1.2154 | 87.8126 | 74.6386 | 1157.7099
2029-02-11 04:00 | 4085.06 | 1.2883 | 87.5359 | 74.6386 | 1197.2129
2029-02-12 05:00 | 5091.78 | 1.6217 | 87.4135 | 74.6386 | 1492.2534
2029-02-13 06:00 | 5781.27 | 1.8648 | 87.3496 | 74.6386 | 1694.323
2029-02-14 07:00 | 7070.51 | 2.3623 | 87.1464 | 74.6386 | 2072.1619
2029-02-15 08:00 | 7593.3 | 2.5246 | 87.3007 | 74.6386 | 2225.3766
2029-02-16 09:00 | 9110.21 | 3.1205 | 87.187 | 74.6386 | 2669.939
2029-02-17 10:00 | 10555.6 | 3.6072 | 87.3664 | 74.6386 | 3093.541
2029-02-18 11:00 | 12135.7 | 4.0603 | 87.7225 | 74.6386 | 3556.6226
2029-02-19 12:00 | 13026.2 | 4.2106 | 88.2139 | 74.6386 | 3817.6024
2029-02-20 13:00 | 13689.6 | 4.4286 | 88.4264 | 74.6386 | 4012.0257
2029-02-21 14:00 | 14350 | 4.5934 | 88.7085 | 74.6386 | 4205.5699
2029-02-22 15:00 | 16425.2 | 5.2135 | 88.9608 | 74.6386 | 4813.7509
2029-02-23 16:00 | 16396.3 | 5.2429 | 89.192 | 74.6386 | 4805.2812
2029-02-24 17:00 | 15399.3 | 4.9016 | 89.4126 | 74.6386 | 4513.0893
2029-02-25 18:00 | 13100.6 | 4.1638 | 89.4904 | 74.6386 | 3839.4069
2029-02-26 19:00 | 11085.4 | 3.5394 | 89.3735 | 74.6386 | 3248.81
2029-02-27 20:00 | 8776.97 | 2.7318 | 89.4176 | 74.6386 | 2572.276
2029-02-28 21:00 | 7790.9 | 2.387 | 89.2914 | 74.6386 | 2283.2874
2029-03-01 22:00 | 5808.84 | 1.6905 | 89.4856 | 74.6386 | 1702.403
2029-03-02 23:00 | 5038.45 | 1.4617 | 89.2393 | 74.6386 | 1476.6239
2029-03-04 | 4438.7 | 1.3397 | 88.7016 | 74.6386 | 1300.8546
2029-03-05 01:00 | 3750.95 | 1.1983 | 88.0877 | 74.6386 | 1099.2949
2029-03-06 02:00 | 3543.23 | 1.1337 | 87.9031 | 74.6386 | 1038.4182
2029-03-07 03:00 | 3764.66 | 1.1887 | 87.8439 | 74.6386 | 1103.3129
2029-03-08 04:00 | 3689.26 | 1.1768 | 87.6712 | 74.6386 | 1081.2154
2029-03-09 05:00 | 4642.55 | 1.4598 | 87.6846 | 74.6386 | 1360.5971
2029-03-10 06:00 | 5461.92 | 1.7663 | 87.472 | 74.6386 | 1600.7307
2029-03-11 07:00 | 7011.07 | 2.2719 | 87.4968 | 74.6386 | 2054.7418
2029-03-12 08:00 | 7732.1 | 2.5328 | 87.5463 | 74.6386 | 2266.0548
2029-03-13 09:00 | 9011.06 | 3.0429 | 87.4431 | 74.6386 | 2640.881
2029-03-14 10:00 | 10549.6 | 3.6468 | 87.4425 | 74.6386 | 3091.7826
2029-03-15 11:00 | 12067.2 | 3.9639 | 88.0087 | 74.6386 | 3536.5472
2029-03-16 12:00 | 12770.1 | 4.1827 | 88.267 | 74.6386 | 3742.5469
2029-03-17 13:00 | 13926.5 | 4.3995 | 88.7279 | 74.6386 | 4081.4543
2029-03-18 14:00 | 14073.9 | 4.6619 | 88.603 | 74.6386 | 4124.6529
2029-03-19 15:00 | 16052.9 | 5.1406 | 89.0043 | 74.6386 | 4704.6406
2029-03-20 16:00 | 16004.6 | 5.0504 | 89.3707 | 74.6386 | 4690.4852
2029-03-21 17:00 | 15476.3 | 4.9421 | 89.4512 | 74.6386 | 4535.6558
2029-03-22 18:00 | 13354.2 | 4.1776 | 89.6967 | 74.6386 | 3913.7297
2029-03-23 19:00 | 11644.3 | 3.6086 | 89.7024 | 74.6386 | 3412.6075
2029-03-24 20:00 | 9157.78 | 2.7828 | 89.742 | 74.6386 | 2683.8804
2029-03-25 21:00 | 8346.19 | 2.4488 | 89.7848 | 74.6386 | 2446.0268
2029-03-26 22:00 | 6206.48 | 1.8365 | 89.5336 | 74.6386 | 1818.9397
2029-03-27 23:00 | 5445.24 | 1.6023 | 89.3104 | 74.6386 | 1595.8423
2029-03-29 | 4368.2 | 1.3468 | 88.7275 | 74.6386 | 1280.193
2029-03-30 01:00 | 3823.76 | 1.2037 | 88.3538 | 74.6386 | 1120.6334
2029-03-31 02:00 | 3637.11 | 1.1439 | 88.1833 | 74.6386 | 1065.9317
2029-04-01 03:00 | 3657.7 | 1.1652 | 87.9303 | 74.6386 | 1071.9661
2029-04-02 04:00 | 3862.93 | 1.2473 | 87.7188 | 74.6386 | 1132.113
2029-04-03 05:00 | 4942.12 | 1.5611 | 87.7956 | 74.6386 | 1448.3924
2029-04-04 06:00 | 5725.71 | 1.7994 | 87.8456 | 74.6386 | 1678.04
2029-04-05 07:00 | 7052.29 | 2.2919 | 87.6385 | 74.6386 | 2066.8222
2029-04-06 08:00 | 7744.47 | 2.5515 | 87.6512 | 74.6386 | 2269.6801
2029-04-07 09:00 | 9460.21 | 3.1569 | 87.663 | 74.6386 | 2772.5139
2029-04-08 10:00 | 10867.3 | 3.6839 | 87.7409 | 74.6386 | 3184.8912
2029-04-09 11:00 | 12389.2 | 4.2111 | 87.9318 | 74.6386 | 3630.9161
2029-04-10 12:00 | 13572.2 | 4.4841 | 88.3723 | 74.6386 | 3977.6192
2029-04-11 13:00 | 14369.9 | 4.7014 | 88.6791 | 74.6386 | 4211.402
2029-04-12 14:00 | 15364.7 | 4.9176 | 89.0606 | 74.6386 | 4502.9491
2029-04-13 15:00 | 15156.4 | 4.9851 | 89.0781 | 74.6386 | 4441.9024
2029-04-14 16:00 | 16073.6 | 4.9688 | 89.671 | 74.6386 | 4710.7072
2029-04-15 17:00 | 15063.5 | 4.7688 | 89.6597 | 74.6386 | 4414.6761
2029-04-16 18:00 | 13529.9 | 4.2177 | 89.8368 | 74.6386 | 3965.2223
2029-04-17 19:00 | 11697.8 | 3.6525 | 89.7755 | 74.6386 | 3428.2868
2029-04-18 20:00 | 8846.54 | 2.7445 | 89.7012 | 74.6386 | 2592.6649
2029-04-19 21:00 | 7848.88 | 2.437 | 89.4389 | 74.6386 | 2300.2797
2029-04-20 22:00 | 5769.69 | 1.6748 | 89.7538 | 74.6386 | 1690.9292
2029-04-21 23:00 | 5126.76 | 1.5173 | 89.3191 | 74.6386 | 1502.505
2029-04-23 | 4915.49 | 1.4891 | 88.9105 | 74.6386 | 1440.5879
2029-04-24 01:00 | 4425.43 | 1.3639 | 88.6181 | 74.6386 | 1296.9655
2029-04-25 02:00 | 4382.24 | 1.3357 | 88.5562 | 74.6386 | 1284.3078
2029-04-26 03:00 | 4657.04 | 1.4526 | 88.2613 | 74.6386 | 1364.8437
2029-04-27 04:00 | 4608.73 | 1.4906 | 87.9255 | 74.6386 | 1350.6854
2029-04-28 05:00 | 5621.66 | 1.8036 | 87.916 | 74.6386 | 1647.5459
2029-04-29 06:00 | 6211.43 | 1.9824 | 87.9671 | 74.6386 | 1820.3904
2029-04-30 07:00 | 7082.07 | 2.2957 | 87.8864 | 74.6386 | 2075.5498
2029-05-01 08:00 | 7427.25 | 2.4699 | 87.7799 | 74.6386 | 2176.7121
2029-05-02 09:00 | 9507.02 | 3.2307 | 87.6854 | 74.6386 | 2786.2325
2029-05-03 10:00 | 10865.8 | 3.675 | 87.9113 | 74.6386 | 3184.4516
2029-05-04 11:00 | 12134.1 | 4.0312 | 88.243 | 74.6386 | 3556.1537
2029-05-05 12:00 | 13219 | 4.3634 | 88.4958 | 74.6386 | 3874.1065
2029-05-06 13:00 | 13788.9 | 4.4094 | 88.9372 | 74.6386 | 4041.1277
2029-05-07 14:00 | 14868 | 4.8463 | 88.9842 | 74.6386 | 4357.3807
2029-05-08 15:00 | 15673 | 5.2325 | 89.0123 | 74.6386 | 4593.3029
2029-05-09 16:00 | 13624 | 4.2026 | 89.7901 | 74.6386 | 3992.8003
2029-05-10 17:00 | 11845.2 | 3.8589 | 89.3583 | 74.6386 | 3471.4854
2029-05-11 18:00 | 10639.2 | 3.3053 | 89.5946 | 74.6386 | 3118.0417
2029-05-12 19:00 | 9216.79 | 2.861 | 89.4856 | 74.6386 | 2701.1745
2029-05-13 20:00 | 7105.55 | 2.1092 | 89.6823 | 74.6386 | 2082.4311
2029-05-14 21:00 | 6410.74 | 1.8807 | 89.5139 | 74.6386 | 1878.8024
2029-05-15 22:00 | 4571.18 | 1.3508 | 89.2645 | 74.6386 | 1339.6806
2029-05-16 23:00 | 4075.5 | 1.2641 | 88.6369 | 74.6386 | 1194.4111
2029-05-18 | 3734.8 | 1.193 | 88.2129 | 74.6386 | 1094.5618
2029-05-19 01:00 | 3584.2 | 1.0802 | 88.4957 | 74.6386 | 1050.4253
2029-05-20 02:00 | 3471.22 | 1.107 | 87.9323 | 74.6386 | 1017.3142
2029-05-21 03:00 | 3861.38 | 1.2227 | 87.8589 | 74.6386 | 1131.6588
2029-05-22 04:00 | 4231.5 | 1.3502 | 87.747 | 74.6386 | 1240.1302
2029-05-23 05:00 | 5142.87 | 1.6708 | 87.589 | 74.6386 | 1507.2264
2029-05-24 06:00 | 5631.66 | 1.7955 | 87.7595 | 74.6386 | 1650.4766
2029-05-25 07:00 | 6729.8 | 2.2615 | 87.4167 | 74.6386 | 1972.3097
2029-05-26 08:00 | 6747.1 | 2.096 | 88.092 | 74.6386 | 1977.3798
2029-05-27 09:00 | 7000.14 | 2.2791 | 87.7876 | 74.6386 | 2051.5385
2029-05-28 10:00 | 8355.04 | 2.8478 | 87.5033 | 74.6386 | 2448.6205
2029-05-29 11:00 | 9495.42 | 3.1142 | 87.894 | 74.6386 | 2782.8329
2029-05-30 12:00 | 10531 | 3.5306 | 87.8834 | 74.6386 | 3086.3314
2029-05-31 13:00 | 11171.8 | 3.658 | 88.1987 | 74.6386 | 3274.1314
2029-06-01 14:00 | 12413.1 | 3.9337 | 88.5735 | 74.6386 | 3637.9205
2029-06-02 15:00 | 12793.8 | 4.3098 | 88.3105 | 74.6386 | 3749.4927
2029-06-03 16:00 | 12470 | 4.1035 | 88.6199 | 74.6386 | 3654.5962
2029-06-04 17:00 | 11754.7 | 3.7395 | 88.9375 | 74.6386 | 3444.9625
2029-06-05 18:00 | 10037 | 3.2056 | 88.9211 | 74.6386 | 2941.5543
2029-06-06 19:00 | 8930.18 | 2.7881 | 88.9967 | 74.6386 | 2617.1774
2029-06-07 20:00 | 7014.02 | 2.1207 | 89.1322 | 74.6386 | 2055.6063
2029-06-08 21:00 | 6297.4 | 1.8793 | 89.0442 | 74.6386 | 1845.5858
2029-06-09 22:00 | 4141.13 | 1.2657 | 88.7015 | 74.6386 | 1213.6454
2029-06-10 23:00 | 3147.08 | 1 | 89.9965 | 74.6386 | 922.3181
2029-06-12 | 3195.36 | 1 | 78.9348 | 74.6386 | 936.4676
2029-06-13 01:00 | 3075.3 | 1 | 78.8517 | 74.6386 | 901.2815
2029-06-14 02:00 | 3121.43 | 1 | 78.7116 | 74.6386 | 914.8008
2029-06-15 03:00 | 3113.79 | 1 | 78.6087 | 74.6386 | 912.5618
2029-06-16 04:00 | 3195.81 | 1 | 78.4909 | 74.6386 | 936.5995
2029-06-17 05:00 | 3088.96 | 1 | 78.4815 | 74.6386 | 905.2848
2029-06-18 06:00 | 3224.03 | 1 | 88.7236 | 74.6386 | 944.8699
2029-06-19 07:00 | 4414.9 | 1.4056 | 87.283 | 74.6386 | 1293.8795
2029-06-20 08:00 | 3531.94 | 1.1149 | 87.3949 | 74.6386 | 1035.1094
2029-06-21 09:00 | 5002.63 | 1.5606 | 87.4214 | 74.6386 | 1466.1261
2029-06-22 10:00 | 6414.01 | 2.0784 | 87.1969 | 74.6386 | 1879.7608
2029-06-23 11:00 | 7912.57 | 2.6609 | 87.0675 | 74.6386 | 2318.9454
2029-06-24 12:00 | 8963.72 | 3.0319 | 87.1959 | 74.6386 | 2627.007
2029-06-25 13:00 | 9648.62 | 3.2355 | 87.4126 | 74.6386 | 2827.7314
2029-06-26 14:00 | 10078.2 | 3.1728 | 88.023 | 74.6386 | 2953.6289
2029-06-27 15:00 | 8560.25 | 2.5867 | 88.4561 | 74.6386 | 2508.7616
2029-06-28 16:00 | 9897.5 | 3.2363 | 87.8244 | 74.6386 | 2900.6709
2029-06-29 17:00 | 8722.63 | 2.6815 | 88.3771 | 74.6386 | 2556.3505
2029-06-30 18:00 | 7464.15 | 2.3154 | 88.2932 | 74.6386 | 2187.5264
2029-07-01 19:00 | 6038.14 | 1.8684 | 88.2059 | 74.6386 | 1769.6042
2029-07-02 20:00 | 5210.33 | 1.6638 | 87.83 | 74.6386 | 1526.997
2029-07-03 21:00 | 4563.05 | 1.4523 | 87.7362 | 74.6386 | 1337.2979
2029-07-04 22:00 | 4019.57 | 1.2386 | 87.8526 | 74.6386 | 1178.0197
2029-07-05 23:00 | 3034.64 | 1 | 78.5901 | 74.6386 | 889.3652
2029-07-07 | 62.3198 | 1 | 79.8708 | 74.6386 | 18.2641
2029-07-08 01:00 | 73.2842 | 1 | 79.5392 | 74.6386 | 21.4775
2029-07-09 02:00 | -205.452 | 0.96468 | 78.8651 | 74.6386 | -60.212
2029-07-10 03:00 | -263.368 | 1.0632 | 78.6305 | 74.6386 | -77.1855
2029-07-11 04:00 | -400.417 | 1.3664 | 78.3725 | 74.6386 | -117.3506
2029-07-12 05:00 | -424.806 | 1.4019 | 78.2128 | 74.6386 | -124.4983
2029-07-13 06:00 | 2184.05 | 1 | 77.7872 | 74.6386 | 640.0819
2029-07-14 07:00 | 2984.54 | 1 | 89.9645 | 74.6386 | 874.6823
2029-07-15 08:00 | 3044.63 | 1 | 77.586 | 74.6386 | 892.293
2029-07-16 09:00 | 3082.02 | 1 | 87.8205 | 74.6386 | 903.2509
2029-07-17 10:00 | 4682.19 | 1.5252 | 86.3591 | 74.6386 | 1372.2144
2029-07-18 11:00 | 5696.15 | 1.83 | 86.5908 | 74.6386 | 1669.3768
2029-07-19 12:00 | 6214.98 | 2.0471 | 86.5437 | 74.6386 | 1821.4308
2029-07-20 13:00 | 6282.34 | 2.0879 | 86.5765 | 74.6386 | 1841.1721
2029-07-21 14:00 | 7111.58 | 2.3911 | 86.5567 | 74.6386 | 2084.1984
2029-07-22 15:00 | 7246.43 | 2.3548 | 86.9176 | 74.6386 | 2123.719
2029-07-23 16:00 | 9411.38 | 3.1808 | 86.7117 | 74.6386 | 2758.2032
2029-07-24 17:00 | 8338.84 | 2.6862 | 87.2698 | 74.6386 | 2443.8728
2029-07-25 18:00 | 6532.19 | 2.0711 | 87.4346 | 74.6386 | 1914.3959
2029-07-26 19:00 | 4809.06 | 1.5082 | 87.4223 | 74.6386 | 1409.3964
2029-07-27 20:00 | 3546.27 | 1.1562 | 86.9857 | 74.6386 | 1039.3091
2029-07-28 21:00 | 3019.37 | 1 | 88.5046 | 74.6386 | 884.89
2029-07-29 22:00 | 3011.91 | 1 | 77.9704 | 74.6386 | 882.7037
2029-07-30 23:00 | 0 | 0 | 79.3297 | 74.6386 | 0
2029-08-01 | -371.047 | 1.3774 | 78.4049 | 74.6386 | -108.7431
2029-08-02 01:00 | -658.504 | 1.9318 | 78.0381 | 74.6386 | -192.9885
2029-08-03 02:00 | -754.512 | 2.1127 | 77.8613 | 74.6386 | -221.1256
2029-08-04 03:00 | -650.063 | 1.8639 | 77.7576 | 74.6386 | -190.5147
2029-08-05 04:00 | -499.714 | 1.5421 | 77.6958 | 74.6386 | -146.4517
2029-08-06 05:00 | -104.819 | 0.66879 | 78.0263 | 74.6386 | -30.7194
2029-08-07 06:00 | 2096.63 | 1 | 77.3497 | 74.6386 | 614.4616
2029-08-08 07:00 | 3105.55 | 1 | 76.9869 | 74.6386 | 910.1469
2029-08-09 08:00 | 3083.23 | 1 | 90.8784 | 74.6386 | 903.6055
2029-08-10 09:00 | 4403.9 | 1.3791 | 86.2234 | 74.6386 | 1290.6557
2029-08-11 10:00 | 5864.35 | 1.9268 | 85.9997 | 74.6386 | 1718.6713
2029-08-12 11:00 | 7071.97 | 2.4004 | 85.9718 | 74.6386 | 2072.5898
2029-08-13 12:00 | 7963.38 | 2.6553 | 86.289 | 74.6386 | 2333.8363
2029-08-14 13:00 | 8282.38 | 2.6922 | 86.6528 | 74.6386 | 2427.326
2029-08-15 14:00 | 8515.87 | 2.7532 | 86.8425 | 74.6386 | 2495.7551
2029-08-16 15:00 | 9936.35 | 3.2769 | 86.8225 | 74.6386 | 2912.0567
2029-08-17 16:00 | 9976.54 | 3.2767 | 87.0434 | 74.6386 | 2923.8353
2029-08-18 17:00 | 9152.84 | 3.0077 | 87.1744 | 74.6386 | 2682.4326
2029-08-19 18:00 | 6994.59 | 2.2325 | 87.4155 | 74.6386 | 2049.912
2029-08-20 19:00 | 5388.81 | 1.6791 | 87.4848 | 74.6386 | 1579.3043
2029-08-21 20:00 | 3141.71 | 1 | 88.229 | 74.6386 | 920.7443
2029-08-22 21:00 | 3192.58 | 1 | 77.9619 | 74.6386 | 935.6528
2029-08-23 22:00 | 0 | 0 | 79.3586 | 74.6386 | 0
2029-08-24 23:00 | -391.749 | 1.3254 | 78.3252 | 74.6386 | -114.8103
2029-08-26 | -668.885 | 1.9601 | 77.9827 | 74.6386 | -196.0308
2029-08-27 01:00 | -844.186 | 2.3166 | 77.7658 | 74.6386 | -247.4065
2029-08-28 02:00 | -928.033 | 2.4847 | 77.6132 | 74.6386 | -271.9796
2029-08-29 03:00 | -874.617 | 2.3534 | 77.4806 | 74.6386 | -256.3249
2029-08-30 04:00 | -722.219 | 2.0167 | 77.4253 | 74.6386 | -211.6615
2029-08-31 05:00 | -197.198 | 0.8444 | 77.6526 | 74.6386 | -57.793
2029-09-01 06:00 | 2066.64 | 1 | 77.1795 | 74.6386 | 605.6724
2029-09-02 07:00 | 2924.41 | 1 | 76.8951 | 74.6386 | 857.06
2029-09-03 08:00 | 2887.25 | 1 | 87.643 | 74.6386 | 846.1694
2029-09-04 09:00 | 4355.29 | 1.4062 | 85.8082 | 74.6386 | 1276.4095
2029-09-05 10:00 | 5718.17 | 1.9376 | 85.6189 | 74.6386 | 1675.8302
2029-09-06 11:00 | 7116.08 | 2.3668 | 85.9505 | 74.6386 | 2085.5172
2029-09-07 12:00 | 7985.82 | 2.6012 | 86.3035 | 74.6386 | 2340.4128
2029-09-08 13:00 | 8676.94 | 2.8234 | 86.4982 | 74.6386 | 2542.9601
2029-09-09 14:00 | 9697.79 | 3.1324 | 86.7353 | 74.6386 | 2842.1417
2029-09-10 15:00 | 11606.3 | 3.8039 | 86.8266 | 74.6386 | 3401.4708
2029-09-11 16:00 | 12023.8 | 3.936 | 87.1106 | 74.6386 | 3523.8279
2029-09-12 17:00 | 11875.3 | 3.8279 | 87.4348 | 74.6386 | 3480.3069
2029-09-13 18:00 | 9842.43 | 3.1364 | 87.6581 | 74.6386 | 2884.5315
2029-09-14 19:00 | 7727.54 | 2.4587 | 87.6464 | 74.6386 | 2264.7184
2029-09-15 20:00 | 5160.78 | 1.6016 | 87.7167 | 74.6386 | 1512.4753
2029-09-16 21:00 | 3708.03 | 1.1597 | 87.4193 | 74.6386 | 1086.7163
2029-09-17 22:00 | 3101.37 | 1 | 78.1295 | 74.6386 | 908.9218
2029-09-18 23:00 | 298.483 | 1 | 79.3053 | 74.6386 | 87.4767
2029-09-20 | 127.668 | 1 | 79.064 | 74.6386 | 37.4158
2029-09-21 01:00 | -207.007 | 0.97579 | 78.4101 | 74.6386 | -60.6678
2029-09-22 02:00 | -376.448 | 1.3227 | 78.0856 | 74.6386 | -110.326
2029-09-23 03:00 | -416.815 | 1.3913 | 77.9042 | 74.6386 | -122.1564
2029-09-24 04:00 | -315.26 | 1.1573 | 77.8357 | 74.6386 | -92.3936
2029-09-25 05:00 | 0 | 1 | 78.3946 | 74.6386 | 0
2029-09-26 06:00 | 3013.73 | 1 | 76.8777 | 74.6386 | 883.2371
2029-09-27 07:00 | 3413.97 | 1.0646 | 86.0968 | 74.6386 | 1000.5358
2029-09-28 08:00 | 4410.77 | 1.4245 | 85.9382 | 74.6386 | 1292.6691
2029-09-29 09:00 | 6021.51 | 2.0558 | 85.6637 | 74.6386 | 1764.7304
2029-09-30 10:00 | 7519.32 | 2.6705 | 85.5939 | 74.6386 | 2203.6952
2029-10-01 11:00 | 9115.44 | 3.0793 | 86.1826 | 74.6386 | 2671.4718
2029-10-02 12:00 | 10328.4 | 3.393 | 86.6277 | 74.6386 | 3026.9552
2029-10-03 13:00 | 10988.9 | 3.5878 | 86.9259 | 74.6386 | 3220.5287
2029-10-04 14:00 | 11746.5 | 3.8765 | 87.0682 | 74.6386 | 3442.5593
2029-10-05 15:00 | 13692.8 | 4.5148 | 87.2788 | 74.6386 | 4012.9635
2029-10-06 16:00 | 14332.1 | 4.6893 | 87.6281 | 74.6386 | 4200.3239
2029-10-07 17:00 | 14245.3 | 4.5834 | 87.9979 | 74.6386 | 4174.8853
2029-10-08 18:00 | 12158.5 | 3.8918 | 88.1983 | 74.6386 | 3563.3046
2029-10-09 19:00 | 9856.9 | 3.1469 | 88.2128 | 74.6386 | 2888.7722
2029-10-10 20:00 | 7523.49 | 2.2876 | 88.4686 | 74.6386 | 2204.9173
2029-10-11 21:00 | 6084.13 | 1.8852 | 88.1146 | 74.6386 | 1783.0825
2029-10-12 22:00 | 3714.88 | 1.1404 | 87.9772 | 74.6386 | 1088.7239
2029-10-13 23:00 | 3179.54 | 1 | 89.5555 | 74.6386 | 931.8312
2029-10-15 | 3224.23 | 1 | 78.2044 | 74.6386 | 944.9285
2029-10-16 01:00 | 3035.02 | 1 | 78.177 | 74.6386 | 889.4766
2029-10-17 02:00 | 3055.27 | 1 | 78.0665 | 74.6386 | 895.4112
2029-10-18 03:00 | 3215 | 1 | 77.9013 | 74.6386 | 942.2235
2029-10-19 04:00 | 3118.84 | 1 | 77.9002 | 74.6386 | 914.0418
2029-10-20 05:00 | 3182.5 | 1 | 77.8143 | 74.6386 | 932.6987
2029-10-21 06:00 | 3408.06 | 1.0544 | 86.9537 | 74.6386 | 998.8038
2029-10-22 07:00 | 5358.87 | 1.6834 | 86.8013 | 74.6386 | 1570.5298
2029-10-23 08:00 | 6273.14 | 2.1168 | 86.4084 | 74.6386 | 1838.4759
2029-10-24 09:00 | 7546.14 | 2.5496 | 86.529 | 74.6386 | 2211.5553
2029-10-25 10:00 | 9653.76 | 3.1868 | 86.8595 | 74.6386 | 2829.2378
2029-10-26 11:00 | 11591.1 | 3.7447 | 87.2774 | 74.6386 | 3397.0161
2029-10-27 12:00 | 11979.6 | 3.923 | 87.4884 | 74.6386 | 3510.8742
2029-10-28 13:00 | 12427.7 | 3.9691 | 87.8819 | 74.6386 | 3642.1993
2029-10-29 14:00 | 12677.1 | 4.1186 | 87.9343 | 74.6386 | 3715.2913
2029-10-30 15:00 | 14107.2 | 4.6602 | 87.9628 | 74.6386 | 4134.4122
2029-10-31 16:00 | 14394.7 | 4.6787 | 88.2899 | 74.6386 | 4218.6701
2029-11-01 17:00 | 13786.8 | 4.4548 | 88.4921 | 74.6386 | 4040.5122
2029-11-02 18:00 | 11591.4 | 3.7091 | 88.647 | 74.6386 | 3397.104
2029-11-03 19:00 | 9848.29 | 3.1016 | 88.6908 | 74.6386 | 2886.2489
2029-11-04 20:00 | 7838.97 | 2.3227 | 89.0419 | 74.6386 | 2297.3753
2029-11-05 21:00 | 6817.58 | 2.0205 | 88.8447 | 74.6386 | 1998.0355
2029-11-06 22:00 | 4325.69 | 1.292 | 88.5999 | 74.6386 | 1267.7346
2029-11-07 23:00 | 3390.43 | 1.0607 | 87.9448 | 74.6386 | 993.6369
2029-11-09 | 3163.34 | 1 | 89.1881 | 74.6386 | 927.0834
2029-11-10 01:00 | 3086.06 | 1 | 90.6915 | 74.6386 | 904.4349
2029-11-11 02:00 | 3151.63 | 1 | 92.8232 | 74.6386 | 923.6516
2029-11-12 03:00 | 3234.89 | 1 | 78.1877 | 74.6386 | 948.0527
2029-11-13 04:00 | 3170.91 | 1 | 78.1514 | 74.6386 | 929.302
2029-11-14 05:00 | 3152.92 | 1 | 88.0627 | 74.6386 | 924.0296
2029-11-15 06:00 | 3891.64 | 1.1898 | 87.2953 | 74.6386 | 1140.5271
2029-11-16 07:00 | 5515.85 | 1.7095 | 87.1959 | 74.6386 | 1616.5361
2029-11-17 08:00 | 5960.77 | 1.9952 | 86.7433 | 74.6386 | 1746.9292
2029-11-18 09:00 | 7842.2 | 2.6344 | 86.7956 | 74.6386 | 2298.3219
2029-11-19 10:00 | 9481.5 | 3.2928 | 86.7458 | 74.6386 | 2778.7534
2029-11-20 11:00 | 11154.3 | 3.7787 | 87.1496 | 74.6386 | 3269.0026
2029-11-21 12:00 | 11769.7 | 3.9964 | 87.393 | 74.6386 | 3449.3586
2029-11-22 13:00 | 13370.3 | 4.2816 | 88.0119 | 74.6386 | 3918.4481
2029-11-23 14:00 | 13772.5 | 4.4727 | 88.1692 | 74.6386 | 4036.3213
2029-11-24 15:00 | 15559.4 | 5.0378 | 88.3863 | 74.6386 | 4560.01
2029-11-25 16:00 | 15146.5 | 4.9302 | 88.6142 | 74.6386 | 4439.001
2029-11-26 17:00 | 14501.2 | 4.7039 | 88.7931 | 74.6386 | 4249.8822
2029-11-27 18:00 | 12773.3 | 3.9347 | 89.2641 | 74.6386 | 3743.4847
2029-11-28 19:00 | 11057.7 | 3.419 | 89.1975 | 74.6386 | 3240.692
2029-11-29 20:00 | 8794.81 | 2.6593 | 89.2746 | 74.6386 | 2577.5044
2029-11-30 21:00 | 7591.98 | 2.351 | 88.8813 | 74.6386 | 2224.9897
2029-12-01 22:00 | 5413.58 | 1.6434 | 88.8494 | 74.6386 | 1586.5637
2029-12-02 23:00 | 3765.77 | 1.1718 | 88.3917 | 74.6386 | 1103.6382
2029-12-04 | 3195.52 | 1 | 89.2352 | 74.6386 | 936.5145
2029-12-05 01:00 | 3059.77 | 1 | 89.3041 | 74.6386 | 896.7301
2029-12-06 02:00 | 3121.27 | 1 | 78.6264 | 74.6386 | 914.7539
2029-12-07 03:00 | 3036.05 | 1 | 78.5378 | 74.6386 | 889.7784
2029-12-08 04:00 | 3255.73 | 1 | 78.3244 | 74.6386 | 954.1603
2029-12-09 05:00 | 3111.82 | 1 | 78.3288 | 74.6386 | 911.9844
2029-12-10 06:00 | 3441.24 | 1.0713 | 87.3714 | 74.6386 | 1008.5279
2029-12-11 07:00 | 5624.7 | 1.8 | 87.1125 | 74.6386 | 1648.4368
2029-12-12 08:00 | 5964.52 | 1.9092 | 87.2396 | 74.6386 | 1748.0283
2029-12-13 09:00 | 7159.4 | 2.4421 | 86.8622 | 74.6386 | 2098.213
2029-12-14 10:00 | 8967.34 | 3.0525 | 86.9935 | 74.6386 | 2628.0679
2029-12-15 11:00 | 10654.9 | 3.4135 | 87.6391 | 74.6386 | 3122.6429
2029-12-16 12:00 | 11206.7 | 3.6382 | 87.7971 | 74.6386 | 3284.3596
2029-12-17 13:00 | 12183.6 | 3.8805 | 88.1137 | 74.6386 | 3570.6607
2029-12-18 14:00 | 12996.9 | 4.1288 | 88.3258 | 74.6386 | 3809.0154
2029-12-19 15:00 | 13251.1 | 4.3332 | 88.3022 | 74.6386 | 3883.5141
2029-12-20 16:00 | 15385 | 5.0299 | 88.4435 | 74.6386 | 4508.8984
2029-12-21 17:00 | 14068 | 4.5873 | 88.7249 | 74.6386 | 4122.9238
2029-12-22 18:00 | 12351.1 | 4.0061 | 88.8566 | 74.6386 | 3619.7501
2029-12-23 19:00 | 10805.1 | 3.3756 | 89.0829 | 74.6386 | 3166.6622
2029-12-24 20:00 | 9231.71 | 2.9408 | 88.8479 | 74.6386 | 2705.5471
2029-12-25 21:00 | 8230.8 | 2.6111 | 88.7486 | 74.6386 | 2412.2094
2029-12-26 22:00 | 7078.04 | 2.2513 | 88.576 | 74.6386 | 2074.3688
2029-12-27 23:00 | 3944.04 | 1.169 | 88.9568 | 74.6386 | 1155.884
2029-12-29 | 3167.4 | 1 | 90.8542 | 74.6386 | 928.2733
2029-12-30 01:00 | 3193.82 | 1 | 78.8603 | 74.6386 | 936.0162
2029-12-31 02:00 | 3204.06 | 1 | 78.7094 | 74.6386 | 939.0173
2030-01-01 03:00 | 3079.47 | 1 | 78.6475 | 74.6386 | 902.5036
2030-01-02 04:00 | 3063.55 | 1 | 78.523 | 74.6386 | 897.8379
2030-01-03 05:00 | 1752.65 | 1 | 79.0748 | 74.6386 | 513.651
2030-01-04 06:00 | 3289.19 | 1 | 89.776 | 74.6386 | 963.9664
2030-01-05 07:00 | 5648.4 | 1.662 | 87.7865 | 74.6386 | 1655.3826
2030-01-06 08:00 | 5719.45 | 1.917 | 86.9655 | 74.6386 | 1676.2053
2030-01-07 09:00 | 7209.15 | 2.4322 | 86.9781 | 74.6386 | 2112.7933
2030-01-08 10:00 | 9130.78 | 3.0833 | 87.0922 | 74.6386 | 2675.9675
2030-01-09 11:00 | 10955.3 | 3.562 | 87.6065 | 74.6386 | 3210.6815
2030-01-10 12:00 | 11760.5 | 3.8175 | 87.8933 | 74.6386 | 3446.6623
2030-01-11 13:00 | 12115.3 | 3.8478 | 88.2594 | 74.6386 | 3550.6439
2030-01-12 14:00 | 12685.6 | 4.0832 | 88.3274 | 74.6386 | 3717.7824
2030-01-13 15:00 | 12983.7 | 4.1544 | 88.532 | 74.6386 | 3805.1469
2030-01-14 16:00 | 14854.5 | 4.9443 | 88.3728 | 74.6386 | 4353.4242
2030-01-15 17:00 | 13784 | 4.4294 | 88.8677 | 74.6386 | 4039.6916
2030-01-16 18:00 | 12516.7 | 3.9111 | 89.162 | 74.6386 | 3668.2827
2030-01-17 19:00 | 11052.9 | 3.4355 | 89.1804 | 74.6386 | 3239.2852
2030-01-18 20:00 | 10121 | 3.0847 | 89.2624 | 74.6386 | 2966.1723
2030-01-19 21:00 | 8561.14 | 2.7556 | 88.7757 | 74.6386 | 2509.0225
2030-01-20 22:00 | 8030.57 | 2.4618 | 88.9802 | 74.6386 | 2353.5277
2030-01-21 23:00 | 5175.89 | 1.4481 | 89.5982 | 74.6386 | 1516.9036
2030-01-23 | 4087.32 | 1.1941 | 88.9655 | 74.6386 | 1197.8752
2030-01-24 01:00 | 3449.67 | 1.0693 | 88.2603 | 74.6386 | 1010.9985
2030-01-25 02:00 | 3109.12 | 1 | 89.0449 | 74.6386 | 911.1931
2030-01-26 03:00 | 3097.71 | 1 | 91.5508 | 74.6386 | 907.8492
2030-01-27 04:00 | 3198.42 | 1 | 93.0591 | 74.6386 | 937.3644
2030-01-28 05:00 | 3116.72 | 1 | 91.5042 | 74.6386 | 913.4205
2030-01-29 06:00 | 4629.92 | 1.4246 | 87.6644 | 74.6386 | 1356.8956
2030-01-30 07:00 | 5941.17 | 1.9374 | 87.2799 | 74.6386 | 1741.185
2030-01-31 08:00 | 6025.72 | 1.8447 | 87.8601 | 74.6386 | 1765.9642
2030-02-01 09:00 | 7016.33 | 2.3798 | 87.1519 | 74.6386 | 2056.2833
2030-02-02 10:00 | 8598.35 | 2.8713 | 87.3445 | 74.6386 | 2519.9276
2030-02-03 11:00 | 9560.73 | 3.1759 | 87.56 | 74.6386 | 2801.9734
2030-02-04 12:00 | 9592.79 | 3.1734 | 87.7557 | 74.6386 | 2811.3692
2030-02-05 13:00 | 10108.5 | 3.2966 | 87.9504 | 74.6386 | 2962.5089
2030-02-06 14:00 | 11516.6 | 3.7856 | 88.0021 | 74.6386 | 3375.1823
2030-02-07 15:00 | 11968 | 4.0301 | 88.0146 | 74.6386 | 3507.4746
2030-02-08 16:00 | 14544.5 | 4.6331 | 88.5475 | 74.6386 | 4262.5722
2030-02-09 17:00 | 12226.2 | 3.8855 | 88.8477 | 74.6386 | 3583.1455
2030-02-10 18:00 | 10894.8 | 3.3725 | 89.0624 | 74.6386 | 3192.9507
2030-02-11 19:00 | 9140.25 | 2.8408 | 88.966 | 74.6386 | 2678.7428
2030-02-12 20:00 | 8371.69 | 2.562 | 88.9613 | 74.6386 | 2453.5001
2030-02-13 21:00 | 7716.22 | 2.3708 | 88.8256 | 74.6386 | 2261.4009
2030-02-14 22:00 | 6956.77 | 2.2304 | 88.3714 | 74.6386 | 2038.828
2030-02-15 23:00 | 4700.49 | 1.3134 | 89.3429 | 74.6386 | 1377.5776
2030-02-17 | 4185.53 | 1.2329 | 88.6767 | 74.6386 | 1226.6578
2030-02-18 01:00 | 3599.58 | 1.1257 | 88.0497 | 74.6386 | 1054.9328
2030-02-19 02:00 | 3486.06 | 1.0923 | 87.8907 | 74.6386 | 1021.6633
2030-02-20 03:00 | 3558.62 | 1.1409 | 87.6002 | 74.6386 | 1042.9286
2030-02-21 04:00 | 3871.9 | 1.2074 | 87.7008 | 74.6386 | 1134.7419
2030-02-22 05:00 | 4977.44 | 1.5446 | 87.6997 | 74.6386 | 1458.7437
2030-02-23 06:00 | 5702.53 | 1.7637 | 87.7665 | 74.6386 | 1671.2466
2030-02-24 07:00 | 6885.88 | 2.2624 | 87.3817 | 74.6386 | 2018.0522
2030-02-25 08:00 | 7210.56 | 2.2591 | 87.8475 | 74.6386 | 2113.2065
2030-02-26 09:00 | 8338.09 | 2.8403 | 87.3254 | 74.6386 | 2443.653
2030-02-27 10:00 | 9705.19 | 3.4051 | 87.2509 | 74.6386 | 2844.3104
2030-02-28 11:00 | 10360.3 | 3.4346 | 87.8255 | 74.6386 | 3036.3042
2030-03-01 12:00 | 9159.23 | 2.9809 | 88.1163 | 74.6386 | 2684.3053
2030-03-02 13:00 | 8488.18 | 2.6676 | 88.3796 | 74.6386 | 2487.64
2030-03-03 14:00 | 8085.03 | 2.5244 | 88.3987 | 74.6386 | 2369.4884
2030-03-04 15:00 | 9130.71 | 3.0016 | 87.9827 | 74.6386 | 2675.9469
2030-03-05 16:00 | 9925.69 | 3.1803 | 88.209 | 74.6386 | 2908.9326
2030-03-06 17:00 | 10002.6 | 3.1663 | 88.3678 | 74.6386 | 2931.4727
2030-03-07 18:00 | 9101.7 | 2.8631 | 88.4646 | 74.6386 | 2667.445
2030-03-08 19:00 | 8546.98 | 2.6075 | 88.6732 | 74.6386 | 2504.8726
2030-03-09 20:00 | 6650.51 | 1.9508 | 88.9536 | 74.6386 | 1949.0721
2030-03-10 21:00 | 5665.32 | 1.802 | 88.1728 | 74.6386 | 1660.3414
2030-03-11 22:00 | 3692.88 | 1.1056 | 88.4674 | 74.6386 | 1082.2763
2030-03-12 23:00 | 3178.48 | 1 | 88.7968 | 74.6386 | 931.5205
2030-03-14 | 3182.98 | 1 | 91.0537 | 74.6386 | 932.8394
2030-03-15 01:00 | 3085.89 | 1 | 91.9984 | 74.6386 | 904.3851
2030-03-16 02:00 | 3232.33 | 1 | 93.1424 | 74.6386 | 947.3024
2030-03-17 03:00 | 3110.24 | 1 | 90.4883 | 74.6386 | 911.5214
2030-03-18 04:00 | 3135.39 | 1 | 88.8876 | 74.6386 | 918.8921
2030-03-19 05:00 | 3787.58 | 1.1864 | 87.3358 | 74.6386 | 1110.0301
2030-03-20 06:00 | 4877.64 | 1.4908 | 87.5262 | 74.6386 | 1429.4952
2030-03-21 07:00 | 6256.3 | 2.0136 | 87.1951 | 74.6386 | 1833.5405
2030-03-22 08:00 | 7062.01 | 2.2857 | 87.2801 | 74.6386 | 2069.6708
2030-03-23 09:00 | 8546.89 | 2.9571 | 86.9317 | 74.6386 | 2504.8462
2030-03-24 10:00 | 10037.3 | 3.3963 | 87.273 | 74.6386 | 2941.6423
2030-03-25 11:00 | 11226.2 | 3.7401 | 87.6092 | 74.6386 | 3290.0744
2030-03-26 12:00 | 12370.6 | 4.0261 | 88.0079 | 74.6386 | 3625.465
2030-03-27 13:00 | 13094 | 4.3144 | 88.1538 | 74.6386 | 3837.4726
2030-03-28 14:00 | 14211.5 | 4.6773 | 88.38 | 74.6386 | 4164.9795
2030-03-29 15:00 | 16353.2 | 5.0997 | 89.012 | 74.6386 | 4792.6498
2030-03-30 16:00 | 15749.7 | 5.0067 | 89.1885 | 74.6386 | 4615.7814
2030-03-31 17:00 | 14256.4 | 4.5863 | 89.2728 | 74.6386 | 4178.1384
2030-04-01 18:00 | 12769.1 | 3.9128 | 89.6624 | 74.6386 | 3742.2538
2030-04-02 19:00 | 11292.3 | 3.4574 | 89.6268 | 74.6386 | 3309.4464
2030-04-03 20:00 | 8775.54 | 2.6221 | 89.7299 | 74.6386 | 2571.8569
2030-04-04 21:00 | 7882.02 | 2.3762 | 89.4249 | 74.6386 | 2309.992
2030-04-05 22:00 | 5419.88 | 1.581 | 89.5006 | 74.6386 | 1588.41
2030-04-06 23:00 | 4306.76 | 1.3219 | 88.8207 | 74.6386 | 1262.1868
2030-04-08 | 3660 | 1.1515 | 88.3784 | 74.6386 | 1072.6401
2030-04-09 01:00 | 3230.18 | 1 | 88.5293 | 74.6386 | 946.6723
2030-04-10 02:00 | 3101.56 | 1 | 88.4342 | 74.6386 | 908.9775
2030-04-11 03:00 | 3165.67 | 1 | 88.1591 | 74.6386 | 927.7663
2030-04-12 04:00 | 3368.41 | 1.0564 | 87.7602 | 74.6386 | 987.1835
2030-04-13 05:00 | 4455.88 | 1.4019 | 87.6663 | 74.6386 | 1305.8895
2030-04-14 06:00 | 5377.08 | 1.7077 | 87.6108 | 74.6386 | 1575.8666
2030-04-15 07:00 | 6729.39 | 2.2999 | 87.1364 | 74.6386 | 1972.1895
2030-04-16 08:00 | 7525.32 | 2.46 | 87.5711 | 74.6386 | 2205.4536
2030-04-17 09:00 | 9144.36 | 3.0501 | 87.5416 | 74.6386 | 2679.9474
2030-04-18 10:00 | 11143.8 | 3.7369 | 87.6948 | 74.6386 | 3265.9254
2030-04-19 11:00 | 13018.7 | 4.3094 | 88.049 | 74.6386 | 3815.4043
2030-04-20 12:00 | 13694.8 | 4.4444 | 88.4922 | 74.6386 | 4013.5497
2030-04-21 13:00 | 14164 | 4.5696 | 88.7732 | 74.6386 | 4151.0586
2030-04-22 14:00 | 14849.1 | 4.8811 | 88.8407 | 74.6386 | 4351.8416
2030-04-23 15:00 | 16660 | 5.4471 | 89.076 | 74.6386 | 4882.564
2030-04-24 16:00 | 16919.8 | 5.5371 | 89.3456 | 74.6386 | 4958.7039
2030-04-25 17:00 | 16287.1 | 5.2434 | 89.6662 | 74.6386 | 4773.2778
2030-04-26 18:00 | 14615.8 | 4.3722 | 90.3304 | 74.6386 | 4283.4681
2030-04-27 19:00 | 12939.8 | 3.9178 | 90.2217 | 74.6386 | 3792.281
2030-04-28 20:00 | 9527.11 | 2.9497 | 89.9736 | 74.6386 | 2792.1203
2030-04-29 21:00 | 8224.99 | 2.53 | 89.7463 | 74.6386 | 2410.5066
2030-04-30 22:00 | 6118.74 | 1.8202 | 89.7676 | 74.6386 | 1793.2257
2030-05-01 23:00 | 5163.03 | 1.5584 | 89.3623 | 74.6386 | 1513.1347
2030-05-03 | 4432.64 | 1.3933 | 88.7997 | 74.6386 | 1299.0785
2030-05-04 01:00 | 3803.24 | 1.2308 | 88.3677 | 74.6386 | 1114.6196
2030-05-05 02:00 | 3321.38 | 1.0804 | 88.1464 | 74.6386 | 973.4004
2030-05-06 03:00 | 3195.99 | 1.0365 | 87.9868 | 74.6386 | 936.6522
2030-05-07 04:00 | 3310.34 | 1.0617 | 87.9285 | 74.6386 | 970.1649
2030-05-08 05:00 | 4030.93 | 1.2992 | 87.7855 | 74.6386 | 1181.349
2030-05-09 06:00 | 5164.47 | 1.6447 | 87.8344 | 74.6386 | 1513.5567
2030-05-10 07:00 | 6527.69 | 2.1258 | 87.7017 | 74.6386 | 1913.0771
2030-05-11 08:00 | 6924.07 | 2.2712 | 87.7589 | 74.6386 | 2029.2446
2030-05-12 09:00 | 7956.68 | 2.6252 | 87.7917 | 74.6386 | 2331.8727
2030-05-13 10:00 | 9351.57 | 3.0593 | 87.9681 | 74.6386 | 2740.6746
2030-05-14 11:00 | 10461 | 3.4536 | 88.0708 | 74.6386 | 3065.8165
2030-05-15 12:00 | 10674.1 | 3.511 | 88.2722 | 74.6386 | 3128.2699
2030-05-16 13:00 | 11476.6 | 3.6918 | 88.5469 | 74.6386 | 3363.4594
2030-05-17 14:00 | 11941.5 | 3.7336 | 88.8973 | 74.6386 | 3499.7082
2030-05-18 15:00 | 13021.9 | 4.2535 | 88.6952 | 74.6386 | 3816.3422
2030-05-19 16:00 | 12884.2 | 4.2281 | 88.816 | 74.6386 | 3775.9863
2030-05-20 17:00 | 12462.8 | 4.0262 | 89.0184 | 74.6386 | 3652.4861
2030-05-21 18:00 | 10810.3 | 3.4888 | 89.0666 | 74.6386 | 3168.1862
2030-05-22 19:00 | 9312.84 | 2.9108 | 89.2275 | 74.6386 | 2729.324
2030-05-23 20:00 | 7040.96 | 2.1317 | 89.3496 | 74.6386 | 2063.5017
2030-05-24 21:00 | 6006.06 | 1.8273 | 89.0814 | 74.6386 | 1760.2024
2030-05-25 22:00 | 3905.65 | 1.1947 | 88.8378 | 74.6386 | 1144.633
2030-05-26 23:00 | 3142.99 | 1 | 90.6241 | 74.6386 | 921.1194
2030-05-28 | 3137.9 | 1 | 79.0806 | 74.6386 | 919.6277
2030-05-29 01:00 | 3150.37 | 1 | 78.9283 | 74.6386 | 923.2823
2030-05-30 02:00 | 3210.68 | 1 | 78.7941 | 74.6386 | 940.9574
2030-05-31 03:00 | 3159.23 | 1 | 78.7246 | 74.6386 | 925.8789
2030-06-01 04:00 | 3169.26 | 1 | 78.6459 | 74.6386 | 928.8184
2030-06-02 05:00 | 3191.96 | 1 | 78.5696 | 74.6386 | 935.4711
2030-06-03 06:00 | 3326.16 | 1.0393 | 87.6319 | 74.6386 | 974.8013
2030-06-04 07:00 | 5653.35 | 1.7963 | 87.4455 | 74.6386 | 1656.8333
2030-06-05 08:00 | 5869.27 | 1.887 | 87.4929 | 74.6386 | 1720.1132
2030-06-06 09:00 | 6628.49 | 2.1248 | 87.5882 | 74.6386 | 1942.6187
2030-06-07 10:00 | 7217.43 | 2.4581 | 87.2382 | 74.6386 | 2115.2199
2030-06-08 11:00 | 8709.8 | 2.9383 | 87.4011 | 74.6386 | 2552.5904
2030-06-09 12:00 | 9252.56 | 2.9469 | 87.9896 | 74.6386 | 2711.6577
2030-06-10 13:00 | 10212.6 | 3.2942 | 88.0187 | 74.6386 | 2993.0176
2030-06-11 14:00 | 10741.5 | 3.4836 | 88.1242 | 74.6386 | 3148.0229
2030-06-12 15:00 | 10904.4 | 3.5712 | 88.1806 | 74.6386 | 3195.7642
2030-06-13 16:00 | 13071.2 | 4.3709 | 88.1281 | 74.6386 | 3830.7906
2030-06-14 17:00 | 11944.6 | 3.9047 | 88.5208 | 74.6386 | 3500.6167
2030-06-15 18:00 | 10316.5 | 3.3437 | 88.6586 | 74.6386 | 3023.4677
2030-06-16 19:00 | 8752.62 | 2.7436 | 88.8346 | 74.6386 | 2565.1397
2030-06-17 20:00 | 7537.81 | 2.3427 | 88.7888 | 74.6386 | 2209.114
2030-06-18 21:00 | 6631.26 | 2.0431 | 88.7331 | 74.6386 | 1943.4305
2030-06-19 22:00 | 5877.9 | 1.8095 | 88.5984 | 74.6386 | 1722.6424
2030-06-20 23:00 | 3178.69 | 1 | 92.0324 | 74.6386 | 931.5821
2030-06-22 | 3125.06 | 1 | 78.9888 | 74.6386 | 915.8647
2030-06-23 01:00 | 3150.16 | 1 | 78.8074 | 74.6386 | 923.2208
2030-06-24 02:00 | 3129.63 | 1 | 78.7136 | 74.6386 | 917.204
2030-06-25 03:00 | 474.319 | 1 | 79.9019 | 74.6386 | 139.0092
2030-06-26 04:00 | 1327.42 | 1 | 79.1893 | 74.6386 | 389.0284
2030-06-27 05:00 | 158.968 | 1 | 79.6416 | 74.6386 | 46.5889
2030-06-28 06:00 | 2923.22 | 1 | 87.2899 | 74.6386 | 856.7112
2030-06-29 07:00 | 5229.96 | 1.7642 | 86.6179 | 74.6386 | 1532.75
2030-06-30 08:00 | 5798.43 | 1.8798 | 87.0774 | 74.6386 | 1699.3521
2030-07-01 09:00 | 7265.43 | 2.4562 | 86.9032 | 74.6386 | 2129.2873
2030-07-02 10:00 | 9025.59 | 3.0804 | 87.0001 | 74.6386 | 2645.1393
2030-07-03 11:00 | 10135.1 | 3.3669 | 87.4526 | 74.6386 | 2970.3046
2030-07-04 12:00 | 10911.4 | 3.5691 | 87.7886 | 74.6386 | 3197.8157
2030-07-05 13:00 | 11241.4 | 3.6628 | 87.9977 | 74.6386 | 3294.5291
2030-07-06 14:00 | 12045.4 | 3.9027 | 88.188 | 74.6386 | 3530.1583
2030-07-07 15:00 | 12252.3 | 3.8789 | 88.5383 | 74.6386 | 3590.7947
2030-07-08 16:00 | 14668.4 | 4.6709 | 88.6231 | 74.6386 | 4298.8837
2030-07-09 17:00 | 12915.9 | 4.1955 | 88.7678 | 74.6386 | 3785.2766
2030-07-10 18:00 | 11326.1 | 3.5929 | 89.0027 | 74.6386 | 3319.3522
2030-07-11 19:00 | 9455.58 | 2.975 | 89.0033 | 74.6386 | 2771.1569
2030-07-12 20:00 | 8392.15 | 2.5782 | 89.062 | 74.6386 | 2459.4964
2030-07-13 21:00 | 7414.59 | 2.2461 | 89.0509 | 74.6386 | 2173.0018
2030-07-14 22:00 | 6632.86 | 2.0542 | 88.7221 | 74.6386 | 1943.8994
2030-07-15 23:00 | 3944.31 | 1.1543 | 89.0288 | 74.6386 | 1155.9632
2030-07-17 | 3357.95 | 1 | 88.835 | 74.6386 | 984.118
2030-07-18 01:00 | 3114.8 | 1 | 89.123 | 74.6386 | 912.8578
2030-07-19 02:00 | 3144.14 | 1 | 89.758 | 74.6386 | 921.4565
2030-07-20 03:00 | 3199.43 | 1 | 88.9713 | 74.6386 | 937.6604
2030-07-21 04:00 | 3098.99 | 1 | 87.6016 | 74.6386 | 908.2243
2030-07-22 05:00 | 3998.37 | 1.2577 | 87.5488 | 74.6386 | 1171.8066
2030-07-23 06:00 | 5434.38 | 1.755 | 87.3627 | 74.6386 | 1592.6596
2030-07-24 07:00 | 6927.53 | 2.2738 | 87.3381 | 74.6386 | 2030.2586
2030-07-25 08:00 | 7300.79 | 2.4395 | 87.3588 | 74.6386 | 2139.6503
2030-07-26 09:00 | 9123.93 | 3.0563 | 87.4401 | 74.6386 | 2673.9599
2030-07-27 10:00 | 10607.7 | 3.5558 | 87.629 | 74.6386 | 3108.81
2030-07-28 11:00 | 11898.9 | 3.9876 | 87.8699 | 74.6386 | 3487.2234
2030-07-29 12:00 | 12806.1 | 4.204 | 88.2535 | 74.6386 | 3753.0974
2030-07-30 13:00 | 13135.2 | 4.3221 | 88.4528 | 74.6386 | 3849.5471
2030-07-31 14:00 | 14009.6 | 4.5482 | 88.7285 | 74.6386 | 4105.8085
2030-08-01 15:00 | 16291.2 | 5.2394 | 88.988 | 74.6386 | 4774.4794
2030-08-02 16:00 | 16535.1 | 5.2515 | 89.3815 | 74.6386 | 4845.9594
2030-08-03 17:00 | 15916.7 | 5.0804 | 89.5616 | 74.6386 | 4664.7243
2030-08-04 18:00 | 13653.4 | 4.3829 | 89.6287 | 74.6386 | 4001.4165
2030-08-05 19:00 | 11519.4 | 3.6686 | 89.6366 | 74.6386 | 3376.0029
2030-08-06 20:00 | 9032.99 | 2.7662 | 89.7986 | 74.6386 | 2647.308
2030-08-07 21:00 | 7803.24 | 2.3598 | 89.6484 | 74.6386 | 2286.9039
2030-08-08 22:00 | 5830.87 | 1.6989 | 89.7168 | 74.6386 | 1708.8593
2030-08-09 23:00 | 4577.64 | 1.3991 | 89.0611 | 74.6386 | 1341.5739
2030-08-11 | 3841.8 | 1.1665 | 88.8524 | 74.6386 | 1125.9204
2030-08-12 01:00 | 3492.28 | 1.0872 | 88.4479 | 74.6386 | 1023.4862
2030-08-13 02:00 | 3203.19 | 1 | 88.4962 | 74.6386 | 938.7623
2030-08-14 03:00 | 3161.16 | 1 | 88.2587 | 74.6386 | 926.4445
2030-08-15 04:00 | 3283.36 | 1.0449 | 87.8386 | 74.6386 | 962.2578
2030-08-16 05:00 | 4866.39 | 1.4617 | 88.1925 | 74.6386 | 1426.1981
2030-08-17 06:00 | 5902.54 | 1.9384 | 87.5617 | 74.6386 | 1729.8637
2030-08-18 07:00 | 7161.51 | 2.3997 | 87.4945 | 74.6386 | 2098.8314
2030-08-19 08:00 | 7866.65 | 2.6059 | 87.7013 | 74.6386 | 2305.4875
2030-08-20 09:00 | 9545.92 | 3.1883 | 87.7606 | 74.6386 | 2797.633
2030-08-21 10:00 | 11138.1 | 3.7434 | 87.9169 | 74.6386 | 3264.2549
2030-08-22 11:00 | 12709.5 | 4.1735 | 88.3173 | 74.6386 | 3724.7868
2030-08-23 12:00 | 14325.2 | 4.5724 | 88.7837 | 74.6386 | 4198.3017
2030-08-24 13:00 | 14874.3 | 4.8393 | 88.9294 | 74.6386 | 4359.227
2030-08-25 14:00 | 15085.1 | 4.9513 | 89.1006 | 74.6386 | 4421.0064
2030-08-26 15:00 | 16999 | 5.5223 | 89.3475 | 74.6386 | 4981.9151
2030-08-27 16:00 | 17184.9 | 5.4678 | 89.7744 | 74.6386 | 5036.397
2030-08-28 17:00 | 16620.5 | 5.2674 | 90.0041 | 74.6386 | 4870.9877
2030-08-29 18:00 | 14270.1 | 4.5551 | 90.0517 | 74.6386 | 4182.1535
2030-08-30 19:00 | 12234.9 | 3.8587 | 90.0753 | 74.6386 | 3585.6952
2030-08-31 20:00 | 9396.9 | 2.9833 | 89.8952 | 74.6386 | 2753.9595
2030-09-01 21:00 | 8201.97 | 2.5409 | 89.8143 | 74.6386 | 2403.7601
2030-09-02 22:00 | 6204.54 | 1.8358 | 89.9424 | 74.6386 | 1818.3712
2030-09-03 23:00 | 5460.09 | 1.5896 | 89.7892 | 74.6386 | 1600.1944
2030-09-05 | 4508.51 | 1.3904 | 89.1042 | 74.6386 | 1321.3138
2030-09-06 01:00 | 3935.02 | 1.2237 | 88.8234 | 74.6386 | 1153.2405
2030-09-07 02:00 | 3850.76 | 1.1978 | 88.6406 | 74.6386 | 1128.5464
2030-09-08 03:00 | 4165.91 | 1.3146 | 88.3837 | 74.6386 | 1220.9077
2030-09-09 04:00 | 4437.32 | 1.3573 | 88.5337 | 74.6386 | 1300.4501
2030-09-10 05:00 | 5332.52 | 1.7252 | 88.0429 | 74.6386 | 1562.8073
2030-09-11 06:00 | 6415.77 | 2.0311 | 88.2086 | 74.6386 | 1880.2766
2030-09-12 07:00 | 8127.53 | 2.6192 | 88.1413 | 74.6386 | 2381.9439
2030-09-13 08:00 | 8672.75 | 2.8075 | 88.2682 | 74.6386 | 2541.7321
2030-09-14 09:00 | 10184.1 | 3.4954 | 87.9732 | 74.6386 | 2984.6651
2030-09-15 10:00 | 11994 | 4.0511 | 88.27 | 74.6386 | 3515.0944
2030-09-16 11:00 | 13210.7 | 4.4273 | 88.5738 | 74.6386 | 3871.674
2030-09-17 12:00 | 14924.3 | 4.8818 | 88.9878 | 74.6386 | 4373.8806
2030-09-18 13:00 | 15696.4 | 5.0427 | 89.3965 | 74.6386 | 4600.1607
2030-09-19 14:00 | 16376.7 | 5.2856 | 89.6125 | 74.6386 | 4799.537
2030-09-20 15:00 | 18134.3 | 5.6694 | 90.0619 | 74.6386 | 5314.6387
2030-09-21 16:00 | 17751.5 | 5.6489 | 90.2117 | 74.6386 | 5202.4511
2030-09-22 17:00 | 16794.6 | 5.4273 | 90.2666 | 74.6386 | 4922.0114
2030-09-23 18:00 | 14241.1 | 4.5636 | 90.388 | 74.6386 | 4173.6544
2030-09-24 19:00 | 12653.5 | 3.8955 | 90.5833 | 74.6386 | 3708.3748
2030-09-25 20:00 | 10070.1 | 3.0604 | 90.5583 | 74.6386 | 2951.255
2030-09-26 21:00 | 9133.06 | 2.7447 | 90.3986 | 74.6386 | 2676.6357
2030-09-27 22:00 | 6910.54 | 2.0503 | 90.299 | 74.6386 | 2025.2794
2030-09-28 23:00 | 6292.31 | 1.8359 | 90.1533 | 74.6386 | 1844.094
2030-09-30 | 5464.2 | 1.7167 | 89.3623 | 74.6386 | 1601.3989
2030-10-01 01:00 | 5172.49 | 1.5997 | 89.2861 | 74.6386 | 1515.9072
2030-10-02 02:00 | 4950.74 | 1.5214 | 89.1828 | 74.6386 | 1450.9187
2030-10-03 03:00 | 5335.31 | 1.6202 | 89.1332 | 74.6386 | 1563.625
2030-10-04 04:00 | 5516.02 | 1.7602 | 88.6857 | 74.6386 | 1616.5859
2030-10-05 05:00 | 6298.48 | 2.0887 | 88.3504 | 74.6386 | 1845.9023
2030-10-06 06:00 | 6714.66 | 2.1756 | 88.5267 | 74.6386 | 1967.8726
2030-10-07 07:00 | 8173.2 | 2.7031 | 88.3936 | 74.6386 | 2395.3285
2030-10-08 08:00 | 8351.74 | 2.7784 | 88.4659 | 74.6386 | 2447.6534
2030-10-09 09:00 | 10157.8 | 3.3488 | 88.5948 | 74.6386 | 2976.9573
2030-10-10 10:00 | 11292.8 | 3.8639 | 88.5026 | 74.6386 | 3309.593
2030-10-11 11:00 | 13112.1 | 4.4114 | 88.8011 | 74.6386 | 3842.7772
2030-10-12 12:00 | 14779.5 | 4.8876 | 89.1622 | 74.6386 | 4331.4439
2030-10-13 13:00 | 15494.7 | 4.9879 | 89.6237 | 74.6386 | 4541.0483
2030-10-14 14:00 | 16402.2 | 5.2488 | 89.8959 | 74.6386 | 4807.0103
2030-10-15 15:00 | 17902 | 5.7122 | 90.1249 | 74.6386 | 5246.5583
2030-10-16 16:00 | 18025.3 | 5.7167 | 90.4332 | 74.6386 | 5282.694
2030-10-17 17:00 | 17827.3 | 5.5003 | 90.8274 | 74.6386 | 5224.6659
2030-10-18 18:00 | 15227.4 | 4.7638 | 90.8515 | 74.6386 | 4462.7104
2030-10-19 19:00 | 13274.2 | 4.177 | 90.7365 | 74.6386 | 3890.284
2030-10-20 20:00 | 10653.4 | 3.2529 | 90.8352 | 74.6386 | 3122.2033
2030-10-21 21:00 | 9677.79 | 2.9364 | 90.6408 | 74.6386 | 2836.2803
2030-10-22 22:00 | 7521.56 | 2.2859 | 90.4344 | 74.6386 | 2204.3516
2030-10-23 23:00 | 6793.27 | 2.054 | 90.1948 | 74.6386 | 1990.9109
2030-10-25 | 6529.23 | 1.9431 | 90.0984 | 74.6386 | 1913.5284
2030-10-26 01:00 | 6060.28 | 1.8445 | 89.7675 | 74.6386 | 1776.0927
2030-10-27 02:00 | 5910.33 | 1.7824 | 89.6997 | 74.6386 | 1732.1467
2030-10-28 03:00 | 6010.78 | 1.8432 | 89.4397 | 74.6386 | 1761.5857
2030-10-29 04:00 | 6090.88 | 1.9515 | 89.0259 | 74.6386 | 1785.0607
2030-10-30 05:00 | 6716.02 | 2.2864 | 88.5197 | 74.6386 | 1968.2712
2030-10-31 06:00 | 7859.93 | 2.5231 | 88.9256 | 74.6386 | 2303.5181
2030-11-01 07:00 | 9194.33 | 3.0112 | 88.8386 | 74.6386 | 2694.5921
2030-11-02 08:00 | 9636.69 | 3.0266 | 89.277 | 74.6386 | 2824.235
2030-11-03 09:00 | 10777 | 3.5621 | 88.995 | 74.6386 | 3158.4269
2030-11-04 10:00 | 12056.3 | 4.0031 | 89.1067 | 74.6386 | 3533.3527
2030-11-05 11:00 | 13460.1 | 4.4063 | 89.3916 | 74.6386 | 3944.7659
2030-11-06 12:00 | 13994.9 | 4.6565 | 89.481 | 74.6386 | 4101.5003
2030-11-07 13:00 | 14619.2 | 4.7834 | 89.7607 | 74.6386 | 4284.4646
2030-11-08 14:00 | 13078.3 | 4.2005 | 90.0503 | 74.6386 | 3832.8714
2030-11-09 15:00 | 13312.8 | 4.2626 | 90.0539 | 74.6386 | 3901.5965
2030-11-10 16:00 | 12501.8 | 4.0538 | 89.9801 | 74.6386 | 3663.9159
2030-11-11 17:00 | 12059.7 | 3.8067 | 90.1394 | 74.6386 | 3534.3492
2030-11-12 18:00 | 10958.6 | 3.3912 | 90.2388 | 74.6386 | 3211.6486
2030-11-13 19:00 | 9821.65 | 3.0574 | 90.0845 | 74.6386 | 2878.4415
2030-11-14 20:00 | 7994.64 | 2.3273 | 90.4921 | 74.6386 | 2342.9977
2030-11-15 21:00 | 7244.44 | 2.1428 | 90.1581 | 74.6386 | 2123.1358
2030-11-16 22:00 | 5396.55 | 1.5817 | 90.0649 | 74.6386 | 1581.5727
2030-11-17 23:00 | 4362.44 | 1.3197 | 89.5671 | 74.6386 | 1278.505
2030-11-19 | 3921.54 | 1.2492 | 88.9349 | 74.6386 | 1149.2899
2030-11-20 01:00 | 3531.75 | 1.0977 | 88.9278 | 74.6386 | 1035.0538
2030-11-21 02:00 | 3124.4 | 1 | 88.8526 | 74.6386 | 915.6713
2030-11-22 03:00 | 3125.36 | 1 | 89.0455 | 74.6386 | 915.9526
2030-11-23 04:00 | 3115.86 | 1 | 89.116 | 74.6386 | 913.1684
2030-11-24 05:00 | 3087.36 | 1 | 88.1775 | 74.6386 | 904.8159
2030-11-25 06:00 | 5564.34 | 1.7577 | 88.2088 | 74.6386 | 1630.7471
2030-11-26 07:00 | 7480.7 | 2.4207 | 88.1368 | 74.6386 | 2192.3768
2030-11-27 08:00 | 7862 | 2.3864 | 88.8086 | 74.6386 | 2304.1248
2030-11-28 09:00 | 9116.41 | 2.9628 | 88.3997 | 74.6386 | 2671.756
2030-11-29 10:00 | 10380.4 | 3.3666 | 88.5713 | 74.6386 | 3042.1949
2030-11-30 11:00 | 11447.5 | 3.7932 | 88.6192 | 74.6386 | 3354.9311
2030-12-01 12:00 | 12658.4 | 4.1936 | 88.8063 | 74.6386 | 3709.8108
2030-12-02 13:00 | 10907.2 | 3.7881 | 88.672 | 74.6386 | 3196.5848
2030-12-03 14:00 | 11620.9 | 3.7824 | 89.1316 | 74.6386 | 3405.7496
2030-12-04 15:00 | 11761.4 | 3.6872 | 89.4766 | 74.6386 | 3446.9261
2030-12-05 16:00 | 14534.9 | 4.8491 | 89.0966 | 74.6386 | 4259.7587
2030-12-06 17:00 | 13991.1 | 4.4814 | 89.6494 | 74.6386 | 4100.3866
2030-12-07 18:00 | 12170.4 | 3.8839 | 89.7829 | 74.6386 | 3566.7922
2030-12-08 19:00 | 11191.9 | 3.335 | 90.26 | 74.6386 | 3280.0221
2030-12-09 20:00 | 10026.2 | 3.0674 | 90.0007 | 74.6386 | 2938.3892
2030-12-10 21:00 | 8967.76 | 2.8042 | 89.7545 | 74.6386 | 2628.191
2030-12-11 22:00 | 8258.84 | 2.5701 | 89.6561 | 74.6386 | 2420.4271
2030-12-12 23:00 | 5348.44 | 1.5081 | 90.3163 | 74.6386 | 1567.473
2030-12-14 | 4245.02 | 1.3376 | 89.1464 | 74.6386 | 1244.0926
2030-12-15 01:00 | 3500.61 | 1.1073 | 88.8784 | 74.6386 | 1025.9275
2030-12-16 02:00 | 3585.18 | 1.094 | 88.9565 | 74.6386 | 1050.7125
2030-12-17 03:00 | 3308.27 | 1.0258 | 88.7013 | 74.6386 | 969.5582
2030-12-18 04:00 | 3124.68 | 1 | 88.7243 | 74.6386 | 915.7533
2030-12-19 05:00 | 3148.82 | 1 | 88.7017 | 74.6386 | 922.828
2030-12-20 06:00 | 5795.57 | 1.9154 | 87.8691 | 74.6386 | 1698.5139
2030-12-21 07:00 | 7917.85 | 2.6231 | 87.9696 | 74.6386 | 2320.4928
2030-12-22 08:00 | 8298.55 | 2.6347 | 88.4779 | 74.6386 | 2432.0649
2030-12-23 09:00 | 9797.87 | 3.1915 | 88.4009 | 74.6386 | 2871.4722
2030-12-24 10:00 | 11312.1 | 3.5948 | 88.7541 | 74.6386 | 3315.2493
2030-12-25 11:00 | 11887.7 | 4.007 | 88.571 | 74.6386 | 3483.941
2030-12-26 12:00 | 12944.6 | 4.1765 | 89.0618 | 74.6386 | 3793.6878
2030-12-27 13:00 | 13126.2 | 4.298 | 89.1456 | 74.6386 | 3846.9095
2030-12-28 14:00 | 13364.5 | 4.338 | 89.3634 | 74.6386 | 3916.7483
2030-12-29 15:00 | 13085.3 | 4.2195 | 89.5388 | 74.6386 | 3834.9229
2030-12-30 16:00 | 14612.6 | 4.7248 | 89.587 | 74.6386 | 4282.5303
2030-12-31 17:00 | 12342.9 | 3.9655 | 89.8199 | 74.6386 | 3617.3469
2031-01-01 18:00 | 10559.1 | 3.2855 | 90.0107 | 74.6386 | 3094.5667
2031-01-02 19:00 | 9160.86 | 2.8176 | 89.9487 | 74.6386 | 2684.783
2031-01-03 20:00 | 8139.28 | 2.5181 | 89.7511 | 74.6386 | 2385.3875
2031-01-04 21:00 | 7611 | 2.3216 | 89.7077 | 74.6386 | 2230.5639
2031-01-05 22:00 | 7318.21 | 2.2269 | 89.5722 | 74.6386 | 2144.7556
2031-01-06 23:00 | 4969.23 | 1.4555 | 89.7726 | 74.6386 | 1456.3376
2031-01-08 | 4248.53 | 1.2923 | 89.2328 | 74.6386 | 1245.1212
2031-01-09 01:00 | 3935.61 | 1.2306 | 88.8259 | 74.6386 | 1153.4134
2031-01-10 02:00 | 3924.94 | 1.222 | 88.7186 | 74.6386 | 1150.2864
2031-01-11 03:00 | 4482.68 | 1.3988 | 88.5943 | 74.6386 | 1313.7438
2031-01-12 04:00 | 4987.64 | 1.54 | 88.6106 | 74.6386 | 1461.733
2031-01-13 05:00 | 6012.9 | 1.9809 | 88.13 | 74.6386 | 1762.207
2031-01-14 06:00 | 6559.83 | 2.1912 | 88.09 | 74.6386 | 1922.4964
2031-01-15 07:00 | 7660.67 | 2.4643 | 88.4197 | 74.6386 | 2245.1208
2031-01-16 08:00 | 7702.83 | 2.3423 | 88.9538 | 74.6386 | 2257.4766
2031-01-17 09:00 | 8880.77 | 2.9874 | 88.261 | 74.6386 | 2602.6968
2031-01-18 10:00 | 10319 | 3.3588 | 88.6043 | 74.6386 | 3024.2004
2031-01-19 11:00 | 11761 | 3.8398 | 88.7567 | 74.6386 | 3446.8089
2031-01-20 12:00 | 11496.5 | 3.7785 | 88.916 | 74.6386 | 3369.2916
2031-01-21 13:00 | 12337.5 | 3.9879 | 89.1404 | 74.6386 | 3615.7643
2031-01-22 14:00 | 13686.2 | 4.5117 | 89.1421 | 74.6386 | 4011.0293
2031-01-23 15:00 | 15168.5 | 4.9792 | 89.3786 | 74.6386 | 4445.4485
2031-01-24 16:00 | 15436.5 | 4.9316 | 89.8047 | 74.6386 | 4523.9916
2031-01-25 17:00 | 15237.6 | 4.8376 | 90.0117 | 74.6386 | 4465.6997
2031-01-26 18:00 | 12725.5 | 4.09 | 90.0419 | 74.6386 | 3729.4759
2031-01-27 19:00 | 10897 | 3.3958 | 90.1951 | 74.6386 | 3193.5954
2031-01-28 20:00 | 8614.49 | 2.5363 | 90.4955 | 74.6386 | 2524.6578
2031-01-29 21:00 | 7666.75 | 2.2976 | 90.1222 | 74.6386 | 2246.9026
2031-01-30 22:00 | 5972.86 | 1.694 | 90.364 | 74.6386 | 1750.4725
2031-01-31 23:00 | 5197.84 | 1.5902 | 89.5035 | 74.6386 | 1523.3365
2031-02-02 | 4616.6 | 1.461 | 89.0456 | 74.6386 | 1352.9919
2031-02-03 01:00 | 4107.34 | 1.3185 | 88.7716 | 74.6386 | 1203.7425
2031-02-04 02:00 | 4052.64 | 1.2693 | 88.8014 | 74.6386 | 1187.7115
2031-02-05 03:00 | 4393.51 | 1.3697 | 88.7066 | 74.6386 | 1287.6107
2031-02-06 04:00 | 4867.94 | 1.5173 | 88.6342 | 74.6386 | 1426.6524
2031-02-07 05:00 | 5869.63 | 1.907 | 88.2852 | 74.6386 | 1720.2187
2031-02-08 06:00 | 6947.11 | 2.3048 | 88.1644 | 74.6386 | 2035.997
2031-02-09 07:00 | 8299.7 | 2.7017 | 88.3806 | 74.6386 | 2432.402
2031-02-10 08:00 | 8520.72 | 2.7152 | 88.6799 | 74.6386 | 2497.1765
2031-02-11 09:00 | 10059.3 | 3.3726 | 88.4018 | 74.6386 | 2948.0898
2031-02-12 10:00 | 10861.9 | 3.5687 | 88.7162 | 74.6386 | 3183.3087
2031-02-13 11:00 | 11242.6 | 3.7246 | 88.8191 | 74.6386 | 3294.8808
2031-02-14 12:00 | 11672.6 | 3.7939 | 89.0818 | 74.6386 | 3420.9014
2031-02-15 13:00 | 11764.2 | 3.6406 | 89.56 | 74.6386 | 3447.7467
2031-02-16 14:00 | 11881.2 | 3.8036 | 89.3975 | 74.6386 | 3482.036
2031-02-17 15:00 | 13622.5 | 4.449 | 89.3146 | 74.6386 | 3992.3607
2031-02-18 16:00 | 14200.1 | 4.5951 | 89.5552 | 74.6386 | 4161.6385
2031-02-19 17:00 | 14030.6 | 4.4179 | 89.9116 | 74.6386 | 4111.963
2031-02-20 18:00 | 12799.7 | 4.0742 | 89.9218 | 74.6386 | 3751.2218
2031-02-21 19:00 | 11176.4 | 3.5816 | 89.8646 | 74.6386 | 3275.4795
2031-02-22 20:00 | 9248.35 | 2.8037 | 90.206 | 74.6386 | 2710.4238
2031-02-23 21:00 | 8209.03 | 2.5249 | 89.9155 | 74.6386 | 2405.8292
2031-02-24 22:00 | 6334.63 | 1.8268 | 90.258 | 74.6386 | 1856.4968
2031-02-25 23:00 | 5480.66 | 1.6321 | 89.7646 | 74.6386 | 1606.2229
2031-02-27 | 5137.62 | 1.5281 | 89.5716 | 74.6386 | 1505.6878
2031-02-28 01:00 | 4295.24 | 1.4168 | 88.647 | 74.6386 | 1258.8106
2031-03-01 02:00 | 4217.33 | 1.3295 | 88.823 | 74.6386 | 1235.9774
2031-03-02 03:00 | 4511.76 | 1.4108 | 88.7547 | 74.6386 | 1322.2663
2031-03-03 04:00 | 4629.71 | 1.474 | 88.5494 | 74.6386 | 1356.8341
2031-03-04 05:00 | 5583.79 | 1.8685 | 88.126 | 74.6386 | 1636.4473
2031-03-05 06:00 | 6789.31 | 2.2282 | 88.2699 | 74.6386 | 1989.7503
2031-03-06 07:00 | 8250.24 | 2.7491 | 88.2376 | 74.6386 | 2417.9067
2031-03-07 08:00 | 8991.85 | 2.9423 | 88.511 | 74.6386 | 2635.2511
2031-03-08 09:00 | 10972.3 | 3.618 | 88.5799 | 74.6386 | 3215.6637
2031-03-09 10:00 | 12701.3 | 4.2252 | 88.7439 | 74.6386 | 3722.3836
2031-03-10 11:00 | 14160.5 | 4.6665 | 89.0808 | 74.6386 | 4150.0329
2031-03-11 12:00 | 15240.7 | 4.8758 | 89.5691 | 74.6386 | 4466.6083
2031-03-12 13:00 | 15728 | 4.9825 | 89.9036 | 74.6386 | 4609.4218
2031-03-13 14:00 | 16271 | 5.3392 | 89.8702 | 74.6386 | 4768.5594
2031-03-14 15:00 | 18561 | 5.6985 | 90.5595 | 74.6386 | 5439.6921
2031-03-15 16:00 | 18341.1 | 5.6889 | 90.7946 | 74.6386 | 5375.2458
2031-03-16 17:00 | 17635.4 | 5.5995 | 90.8108 | 74.6386 | 5168.4255
2031-03-17 18:00 | 15626.3 | 4.8765 | 91.0329 | 74.6386 | 4579.6165
2031-03-18 19:00 | 13348.7 | 4.2698 | 90.8087 | 74.6386 | 3912.1178
2031-03-19 20:00 | 11133.1 | 3.3778 | 91.0745 | 74.6386 | 3262.7895
2031-03-20 21:00 | 10012.8 | 3.0475 | 90.8207 | 74.6386 | 2934.462
2031-03-21 22:00 | 7937.12 | 2.3512 | 90.836 | 74.6386 | 2326.1403
2031-03-22 23:00 | 7053.54 | 2.118 | 90.4569 | 74.6386 | 2067.1885
2031-03-24 | 6592.47 | 1.9856 | 90.2031 | 74.6386 | 1932.0622
2031-03-25 01:00 | 6028.15 | 1.8579 | 89.8576 | 74.6386 | 1766.6764
2031-03-26 02:00 | 5570.88 | 1.7842 | 89.4154 | 74.6386 | 1632.6638
2031-03-27 03:00 | 5695.84 | 1.8098 | 89.3109 | 74.6386 | 1669.2859
2031-03-28 04:00 | 5806.33 | 1.9103 | 88.9536 | 74.6386 | 1701.6673
2031-03-29 05:00 | 6621.39 | 2.2194 | 88.7424 | 74.6386 | 1940.5379
2031-03-30 06:00 | 8027.31 | 2.5731 | 89.0521 | 74.6386 | 2352.5723
2031-03-31 07:00 | 9558.75 | 3.0301 | 89.2121 | 74.6386 | 2801.3931
2031-04-01 08:00 | 9855.53 | 3.1688 | 89.2583 | 74.6386 | 2888.3707
2031-04-02 09:00 | 11064.8 | 3.7232 | 89.0245 | 74.6386 | 3242.7728
2031-04-03 10:00 | 12782.9 | 4.2075 | 89.3302 | 74.6386 | 3746.2982
2031-04-04 11:00 | 13586.1 | 4.5708 | 89.3991 | 74.6386 | 3981.6929
2031-04-05 12:00 | 14874.9 | 4.7783 | 89.9192 | 74.6386 | 4359.4029
2031-04-06 13:00 | 15842.7 | 5.0816 | 90.1393 | 74.6386 | 4643.037
2031-04-07 14:00 | 16824.4 | 5.3435 | 90.4363 | 74.6386 | 4930.7449
2031-04-08 15:00 | 17819.8 | 5.6567 | 90.6565 | 74.6386 | 5222.4679
2031-04-09 16:00 | 17818.8 | 5.7503 | 90.7538 | 74.6386 | 5222.1748
2031-04-10 17:00 | 17287.6 | 5.3965 | 91.1597 | 74.6386 | 5066.4954
2031-04-11 18:00 | 15095.3 | 4.7535 | 91.179 | 74.6386 | 4423.9957
2031-04-12 19:00 | 13237.6 | 4.1352 | 91.1649 | 74.6386 | 3879.5576
2031-04-13 20:00 | 10825.7 | 3.293 | 91.2308 | 74.6386 | 3172.6995
2031-04-14 21:00 | 9787.17 | 2.9575 | 91.0467 | 74.6386 | 2868.3364
2031-04-15 22:00 | 7570.98 | 2.2635 | 90.9289 | 74.6386 | 2218.8352
2031-04-16 23:00 | 6773.49 | 2.0523 | 90.5402 | 74.6386 | 1985.114
2031-04-18 | 6243.29 | 1.8852 | 90.3354 | 74.6386 | 1829.7277
2031-04-19 01:00 | 5979.7 | 1.8147 | 90.1122 | 74.6386 | 1752.4771
2031-04-20 02:00 | 5640.86 | 1.7708 | 89.7074 | 74.6386 | 1653.1729
2031-04-21 03:00 | 5720.11 | 1.8481 | 89.3459 | 74.6386 | 1676.3988
2031-04-22 04:00 | 6019.31 | 1.8872 | 89.4704 | 74.6386 | 1764.0856
2031-04-23 05:00 | 6766.84 | 2.2432 | 88.9967 | 74.6386 | 1983.165
2031-04-24 06:00 | 8001.24 | 2.6406 | 89.0234 | 74.6386 | 2344.932
2031-04-25 07:00 | 9506.36 | 3.1006 | 89.1729 | 74.6386 | 2786.0391
2031-04-26 08:00 | 9991.24 | 3.2337 | 89.3724 | 74.6386 | 2928.1434
2031-04-27 09:00 | 11540.5 | 3.8099 | 89.3342 | 74.6386 | 3382.1867
2031-04-28 10:00 | 12510.6 | 4.1284 | 89.5165 | 74.6386 | 3666.4949
2031-04-29 11:00 | 14062.6 | 4.5955 | 89.7695 | 74.6386 | 4121.3412
2031-04-30 12:00 | 14681.6 | 4.7693 | 90.0345 | 74.6386 | 4302.7522
2031-05-01 13:00 | 15115.9 | 4.9203 | 90.1989 | 74.6386 | 4430.033
2031-05-02 14:00 | 15561.3 | 4.9288 | 90.5532 | 74.6386 | 4560.5668
2031-05-03 15:00 | 15138.5 | 4.7758 | 90.7152 | 74.6386 | 4436.6564
2031-05-04 16:00 | 13319.9 | 4.2975 | 90.6133 | 74.6386 | 3903.6773
2031-05-05 17:00 | 12666.5 | 4.0771 | 90.5405 | 74.6386 | 3712.1847
2031-05-06 18:00 | 11153.3 | 3.5825 | 90.4801 | 74.6386 | 3268.7096
2031-05-07 19:00 | 10126.8 | 3.0936 | 90.72 | 74.6386 | 2967.8721
2031-05-08 20:00 | 7891.57 | 2.3718 | 90.6969 | 74.6386 | 2312.7909
2031-05-09 21:00 | 7099.8 | 2.1239 | 90.4769 | 74.6386 | 2080.746
2031-05-10 22:00 | 5022.15 | 1.494 | 90.3247 | 74.6386 | 1471.8469
2031-05-11 23:00 | 3615.36 | 1.117 | 89.7471 | 74.6386 | 1059.5574
2031-05-13 | 3276.06 | 1.0325 | 89.3058 | 74.6386 | 960.1184
2031-05-14 01:00 | 3090.38 | 1 | 89.3376 | 74.6386 | 905.701
2031-05-15 02:00 | 3155.68 | 1 | 89.6934 | 74.6386 | 924.8385
2031-05-16 03:00 | 3233.53 | 1 | 90.7658 | 74.6386 | 947.6541
2031-05-17 04:00 | 3146.36 | 1 | 90.2648 | 74.6386 | 922.1071
2031-05-18 05:00 | 3279.46 | 1 | 90.3238 | 74.6386 | 961.1149
2031-05-19 06:00 | 5591.52 | 1.8723 | 88.0747 | 74.6386 | 1638.7127
2031-05-20 07:00 | 7961.87 | 2.6354 | 88.2589 | 74.6386 | 2333.3938
2031-05-21 08:00 | 8477.58 | 2.6971 | 88.7628 | 74.6386 | 2484.5334
2031-05-22 09:00 | 9272.06 | 3.1397 | 88.4442 | 74.6386 | 2717.3725
2031-05-23 10:00 | 11200.4 | 3.6384 | 88.8765 | 74.6386 | 3282.5132
2031-05-24 11:00 | 13012.8 | 4.0755 | 89.394 | 74.6386 | 3813.6752
2031-05-25 12:00 | 11005.5 | 3.6927 | 89.1695 | 74.6386 | 3225.3937
2031-05-26 13:00 | 11585.3 | 3.669 | 89.5873 | 74.6386 | 3395.3163
2031-05-27 14:00 | 12389.3 | 3.9869 | 89.5301 | 74.6386 | 3630.9454
2031-05-28 15:00 | 12757.8 | 3.9565 | 89.9367 | 74.6386 | 3738.9421
2031-05-29 16:00 | 14936.2 | 4.9709 | 89.5198 | 74.6386 | 4377.3681
2031-05-30 17:00 | 13794.3 | 4.3658 | 90.1084 | 74.6386 | 4042.7103
2031-05-31 18:00 | 11875.4 | 3.7704 | 90.1652 | 74.6386 | 3480.3362
2031-06-01 19:00 | 10482.8 | 3.2819 | 90.1857 | 74.6386 | 3072.2054
2031-06-02 20:00 | 9646.68 | 3.0052 | 90.1155 | 74.6386 | 2827.1628
2031-06-03 21:00 | 8429.41 | 2.6932 | 89.8317 | 74.6386 | 2470.4162
2031-06-04 22:00 | 8073.67 | 2.4964 | 89.9174 | 74.6386 | 2366.1591
2031-06-05 23:00 | 5136.29 | 1.4419 | 90.5694 | 74.6386 | 1505.298
2031-06-07 | 4466.24 | 1.3315 | 89.805 | 74.6386 | 1308.9257
2031-06-08 01:00 | 3808.38 | 1.191 | 89.2276 | 74.6386 | 1116.126
2031-06-09 02:00 | 3477.33 | 1.0957 | 88.9963 | 74.6386 | 1019.1048
2031-06-10 03:00 | 3348.96 | 1.0496 | 88.8831 | 74.6386 | 981.4833
2031-06-11 04:00 | 3381.81 | 1.0481 | 88.8178 | 74.6386 | 991.1107
2031-06-12 05:00 | 3467.69 | 1.0841 | 88.6565 | 74.6386 | 1016.2796
2031-06-13 06:00 | 5597.06 | 1.857 | 88.141 | 74.6386 | 1640.3364
2031-06-14 07:00 | 7573.8 | 2.5509 | 88.1197 | 74.6386 | 2219.6617
2031-06-15 08:00 | 7777.65 | 2.4349 | 88.8244 | 74.6386 | 2279.4042
2031-06-16 09:00 | 8609.8 | 2.8339 | 88.5414 | 74.6386 | 2523.2833
2031-06-17 10:00 | 10346.1 | 3.4204 | 88.6074 | 74.6386 | 3032.1426
2031-06-18 11:00 | 9386.01 | 3.084 | 88.8585 | 74.6386 | 2750.768
2031-06-19 12:00 | 10175.2 | 3.1669 | 89.3034 | 74.6386 | 2982.0568
2031-06-20 13:00 | 11215.1 | 3.5903 | 89.1695 | 74.6386 | 3286.8214
2031-06-21 14:00 | 12153 | 3.9171 | 89.2653 | 74.6386 | 3561.6927
2031-06-22 15:00 | 12870.2 | 4.1345 | 89.4464 | 74.6386 | 3771.8833
2031-06-23 16:00 | 15035.9 | 5.0603 | 89.2459 | 74.6386 | 4406.5873
2031-06-24 17:00 | 13746.3 | 4.4189 | 89.852 | 74.6386 | 4028.6428
2031-06-25 18:00 | 12232.1 | 3.897 | 90.0023 | 74.6386 | 3584.8746
2031-06-26 19:00 | 10574.7 | 3.3327 | 90.0345 | 74.6386 | 3099.1386
2031-06-27 20:00 | 9555.94 | 2.9791 | 90.0103 | 74.6386 | 2800.5696
2031-06-28 21:00 | 8732.32 | 2.7444 | 89.8392 | 74.6386 | 2559.1904
2031-06-29 22:00 | 8139.79 | 2.5419 | 89.7472 | 74.6386 | 2385.537
2031-06-30 23:00 | 6111.15 | 1.7182 | 90.4818 | 74.6386 | 1791.0013
2031-07-02 | 5460.32 | 1.5929 | 89.9706 | 74.6386 | 1600.2618
2031-07-03 01:00 | 5162.51 | 1.5786 | 89.4361 | 74.6386 | 1512.9823
2031-07-04 02:00 | 4980.39 | 1.5417 | 89.225 | 74.6386 | 1459.6082
2031-07-05 03:00 | 5298.79 | 1.6589 | 89.0358 | 74.6386 | 1552.9221
2031-07-06 04:00 | 5308.64 | 1.7459 | 88.5993 | 74.6386 | 1555.8088
2031-07-07 05:00 | 6350.2 | 2.0903 | 88.5455 | 74.6386 | 1861.0599
2031-07-08 06:00 | 7136.89 | 2.3853 | 88.4678 | 74.6386 | 2091.616
2031-07-09 07:00 | 8672.45 | 2.8416 | 88.668 | 74.6386 | 2541.6442
2031-07-10 08:00 | 8681.27 | 2.8609 | 88.7642 | 74.6386 | 2544.2291
2031-07-11 09:00 | 10793.7 | 3.583 | 88.7818 | 74.6386 | 3163.3212
2031-07-12 10:00 | 11399.6 | 3.706 | 89.1257 | 74.6386 | 3340.893
2031-07-13 11:00 | 13157 | 4.3158 | 89.2318 | 74.6386 | 3855.9361
2031-07-14 12:00 | 13438.9 | 4.4841 | 89.3489 | 74.6386 | 3938.5528
2031-07-15 13:00 | 14348.4 | 4.6316 | 89.7577 | 74.6386 | 4205.1009
2031-07-16 14:00 | 15066.4 | 4.8084 | 90.0335 | 74.6386 | 4415.526
2031-07-17 15:00 | 15786.9 | 5.2021 | 89.9809 | 74.6386 | 4626.6837
2031-07-18 16:00 | 16709.7 | 5.2636 | 90.4879 | 74.6386 | 4897.1297
2031-07-19 17:00 | 16334.9 | 5.2282 | 90.558 | 74.6386 | 4787.2866
2031-07-20 18:00 | 14960 | 4.607 | 90.9687 | 74.6386 | 4384.3432
2031-07-21 19:00 | 12894.9 | 4.0792 | 90.7639 | 74.6386 | 3779.1221
2031-07-22 20:00 | 10511.8 | 3.2625 | 90.799 | 74.6386 | 3080.7045
2031-07-23 21:00 | 9192.65 | 2.8801 | 90.5116 | 74.6386 | 2694.0998
2031-07-24 22:00 | 7691.22 | 2.2588 | 90.8036 | 74.6386 | 2254.0741
2031-07-25 23:00 | 6580.54 | 1.9962 | 90.3147 | 74.6386 | 1928.5659
2031-07-27 | 6039.07 | 1.7861 | 90.29 | 74.6386 | 1769.8767
2031-07-28 01:00 | 5413.04 | 1.7313 | 89.5089 | 74.6386 | 1586.4054
2031-07-29 02:00 | 5705.77 | 1.6837 | 89.9678 | 74.6386 | 1672.1961
2031-07-30 03:00 | 5590.41 | 1.7697 | 89.3259 | 74.6386 | 1638.3874
2031-07-31 04:00 | 5677.51 | 1.8389 | 89.0661 | 74.6386 | 1663.9139
2031-08-01 05:00 | 6671.23 | 2.172 | 88.9534 | 74.6386 | 1955.1445
2031-08-02 06:00 | 6994.42 | 2.328 | 88.8032 | 74.6386 | 2049.8622
2031-08-03 07:00 | 8094.75 | 2.6417 | 88.9547 | 74.6386 | 2372.337
2031-08-04 08:00 | 8592.46 | 2.7199 | 89.2539 | 74.6386 | 2518.2014
2031-08-05 09:00 | 10493.3 | 3.3995 | 89.154 | 74.6386 | 3075.2827
2031-08-06 10:00 | 11849.3 | 4.0172 | 89.0112 | 74.6386 | 3472.687
2031-08-07 11:00 | 13404.2 | 4.413 | 89.4218 | 74.6386 | 3928.3832
2031-08-08 12:00 | 14343.8 | 4.6764 | 89.7306 | 74.6386 | 4203.7528
2031-08-09 13:00 | 13923 | 4.349 | 90.2676 | 74.6386 | 4080.4285
2031-08-10 14:00 | 11608.6 | 3.7728 | 90.0892 | 74.6386 | 3402.1448
2031-08-11 15:00 | 13230.5 | 4.3618 | 89.8937 | 74.6386 | 3877.4768
2031-08-12 16:00 | 13980.7 | 4.5495 | 90.0765 | 74.6386 | 4097.3387
2031-08-13 17:00 | 14517.4 | 4.6951 | 90.2384 | 74.6386 | 4254.63
2031-08-14 18:00 | 13223.2 | 4.0402 | 90.7653 | 74.6386 | 3875.3374
2031-08-15 19:00 | 11459.1 | 3.5793 | 90.5757 | 74.6386 | 3358.3307
2031-08-16 20:00 | 9355 | 2.7881 | 90.854 | 74.6386 | 2741.6799
2031-08-17 21:00 | 8340.52 | 2.4961 | 90.6299 | 74.6386 | 2444.3651
2031-08-18 22:00 | 6283.36 | 1.8173 | 90.7271 | 74.6386 | 1841.471
2031-08-19 23:00 | 5430.93 | 1.6155 | 90.2312 | 74.6386 | 1591.6485
2031-08-21 | 4870.45 | 1.5037 | 89.7051 | 74.6386 | 1427.388
2031-08-22 01:00 | 4530.89 | 1.4184 | 89.4153 | 74.6386 | 1327.8728
2031-08-23 02:00 | 4474.9 | 1.4037 | 89.2642 | 74.6386 | 1311.4637
2031-08-24 03:00 | 4742.61 | 1.4861 | 89.1551 | 74.6386 | 1389.9218
2031-08-25 04:00 | 5140.28 | 1.6466 | 88.9233 | 74.6386 | 1506.4674
2031-08-26 05:00 | 5973.32 | 1.9608 | 88.7028 | 74.6386 | 1750.6073
2031-08-27 06:00 | 6789.96 | 2.3651 | 88.3014 | 74.6386 | 1989.9408
2031-08-28 07:00 | 8239.85 | 2.6257 | 88.9818 | 74.6386 | 2414.8617
2031-08-29 08:00 | 9098.43 | 2.8395 | 89.2658 | 74.6386 | 2666.4866
2031-08-30 09:00 | 10626.9 | 3.5918 | 88.8092 | 74.6386 | 3114.437
2031-08-31 10:00 | 12005.8 | 4.1052 | 88.9151 | 74.6386 | 3518.5527
2031-09-01 11:00 | 13281.1 | 4.4637 | 89.2465 | 74.6386 | 3892.3062
2031-09-02 12:00 | 11747.7 | 3.6721 | 90.0024 | 74.6386 | 3442.911
2031-09-03 13:00 | 10794.3 | 3.3696 | 90.0387 | 74.6386 | 3163.4971
2031-09-04 14:00 | 11047.4 | 3.484 | 89.9346 | 74.6386 | 3237.6733
2031-09-05 15:00 | 12286.9 | 4.0263 | 89.6755 | 74.6386 | 3600.9349
2031-09-06 16:00 | 13052 | 4.1436 | 90.0089 | 74.6386 | 3825.1636
2031-09-07 17:00 | 13052.9 | 4.1439 | 90.1028 | 74.6386 | 3825.4274
2031-09-08 18:00 | 12212.8 | 3.7082 | 90.5118 | 74.6386 | 3579.2184
2031-09-09 19:00 | 10821.8 | 3.3665 | 90.3307 | 74.6386 | 3171.5565
2031-09-10 20:00 | 8492.39 | 2.6355 | 90.2799 | 74.6386 | 2488.8738
2031-09-11 21:00 | 7611.42 | 2.3033 | 90.2694 | 74.6386 | 2230.687
2031-09-12 22:00 | 5605.13 | 1.6338 | 90.3875 | 74.6386 | 1642.7014
2031-09-13 23:00 | 4953.02 | 1.4815 | 89.9196 | 74.6386 | 1451.5869
2031-09-15 | 4494.04 | 1.3882 | 89.4636 | 74.6386 | 1317.0731
2031-09-16 01:00 | 3958.59 | 1.2692 | 89.029 | 74.6386 | 1160.1482
2031-09-17 02:00 | 3886.25 | 1.2404 | 88.9212 | 74.6386 | 1138.9474
2031-09-18 03:00 | 4204.26 | 1.3319 | 88.8583 | 74.6386 | 1232.147
2031-09-19 04:00 | 4609.22 | 1.4464 | 88.8662 | 74.6386 | 1350.829
2031-09-20 05:00 | 5623.9 | 1.8453 | 88.4998 | 74.6386 | 1648.2024
2031-09-21 06:00 | 6495.23 | 2.1584 | 88.4354 | 74.6386 | 1903.564
2031-09-22 07:00 | 8478.8 | 2.701 | 88.801 | 74.6386 | 2484.891
2031-09-23 08:00 | 9321.5 | 2.9588 | 89.0018 | 74.6386 | 2731.862
2031-09-24 09:00 | 10517.2 | 3.4684 | 88.8737 | 74.6386 | 3082.2871
2031-09-25 10:00 | 12178.2 | 4.0658 | 88.9622 | 74.6386 | 3569.0781
2031-09-26 11:00 | 11646.7 | 3.8732 | 89.2231 | 74.6386 | 3413.3108
2031-09-27 12:00 | 12259.8 | 3.896 | 89.6644 | 74.6386 | 3592.9927
2031-09-28 13:00 | 11083.2 | 3.4885 | 89.8596 | 74.6386 | 3248.1653
2031-09-29 14:00 | 10927.2 | 3.5495 | 89.6431 | 74.6386 | 3202.4462
2031-09-30 15:00 | 12487.4 | 4.0778 | 89.6091 | 74.6386 | 3659.6957
2031-10-01 16:00 | 13094.8 | 4.1757 | 89.9042 | 74.6386 | 3837.707
2031-10-02 17:00 | 13138.2 | 4.1504 | 90.0962 | 74.6386 | 3850.4263
2031-10-03 18:00 | 11810.7 | 3.7264 | 90.1766 | 74.6386 | 3461.3745
2031-10-04 19:00 | 10557.1 | 3.3434 | 90.1182 | 74.6386 | 3093.9806
2031-10-05 20:00 | 8801.22 | 2.6349 | 90.4753 | 74.6386 | 2579.383
2031-10-06 21:00 | 8041.24 | 2.4127 | 90.2928 | 74.6386 | 2356.6548
2031-10-07 22:00 | 6289.88 | 1.8569 | 90.2719 | 74.6386 | 1843.3819
2031-10-08 23:00 | 5828.75 | 1.7316 | 90.0045 | 74.6386 | 1708.238
2031-10-10 | 5429.07 | 1.6803 | 89.5197 | 74.6386 | 1591.1034
2031-10-11 01:00 | 5252.88 | 1.6113 | 89.4661 | 74.6386 | 1539.4672
2031-10-12 02:00 | 5364.43 | 1.6446 | 89.3801 | 74.6386 | 1572.1592
2031-10-13 03:00 | 5579.43 | 1.7998 | 88.9265 | 74.6386 | 1635.1695
2031-10-14 04:00 | 5942.91 | 1.9135 | 88.9022 | 74.6386 | 1741.695
2031-10-15 05:00 | 6723.97 | 2.2657 | 88.5555 | 74.6386 | 1970.6011
2031-10-16 06:00 | 7435.43 | 2.4393 | 88.7776 | 74.6386 | 2179.1094
2031-10-17 07:00 | 8983.48 | 2.8964 | 88.9564 | 74.6386 | 2632.7981
2031-10-18 08:00 | 9724.76 | 3.0719 | 89.2464 | 74.6386 | 2850.0458
2031-10-19 09:00 | 10713.3 | 3.6181 | 88.8882 | 74.6386 | 3139.7583
2031-10-20 10:00 | 12702.6 | 4.1015 | 89.355 | 74.6386 | 3722.7646
2031-10-21 11:00 | 11586.7 | 3.8512 | 89.3878 | 74.6386 | 3395.7266
2031-10-22 12:00 | 11434.4 | 3.6915 | 89.6665 | 74.6386 | 3351.0918
2031-10-23 13:00 | 11307.4 | 3.6819 | 89.6431 | 74.6386 | 3313.8718
2031-10-24 14:00 | 13015 | 4.0181 | 90.0841 | 74.6386 | 3814.32
2031-10-25 15:00 | 15213.2 | 4.875 | 89.9619 | 74.6386 | 4458.5488
2031-10-26 16:00 | 14451.4 | 4.8268 | 89.9065 | 74.6386 | 4235.2873
2031-10-27 17:00 | 13573.1 | 4.464 | 90.1103 | 74.6386 | 3977.8829
2031-10-28 18:00 | 12377.7 | 3.9495 | 90.3457 | 74.6386 | 3627.5458
2031-10-29 19:00 | 11317.5 | 3.5159 | 90.513 | 74.6386 | 3316.8318
2031-10-30 20:00 | 9328.92 | 2.8278 | 90.6298 | 74.6386 | 2734.0366
2031-10-31 21:00 | 8576.4 | 2.5936 | 90.452 | 74.6386 | 2513.4947
2031-11-01 22:00 | 6742.63 | 1.9672 | 90.576 | 74.6386 | 1976.0698
2031-11-02 23:00 | 5645.76 | 1.6607 | 90.293 | 74.6386 | 1654.6089
2031-11-04 | 5267.62 | 1.5887 | 89.8857 | 74.6386 | 1543.787
2031-11-05 01:00 | 4870.71 | 1.5219 | 89.4616 | 74.6386 | 1427.4642
2031-11-06 02:00 | 4403.16 | 1.4082 | 89.1529 | 74.6386 | 1290.4388
2031-11-07 03:00 | 4265.35 | 1.3694 | 88.9679 | 74.6386 | 1250.0507
2031-11-08 04:00 | 4089.02 | 1.291 | 88.9731 | 74.6386 | 1198.3735
2031-11-09 05:00 | 4273.72 | 1.3196 | 89.0369 | 74.6386 | 1252.5037
2031-11-10 06:00 | 6619.86 | 2.1742 | 88.5027 | 74.6386 | 1940.0895
2031-11-11 07:00 | 8739.24 | 2.9448 | 88.4229 | 74.6386 | 2561.2184
2031-11-12 08:00 | 9475.82 | 3.0254 | 89.0116 | 74.6386 | 2777.0887
2031-11-13 09:00 | 11135.4 | 3.555 | 89.1545 | 74.6386 | 3263.4636
2031-11-14 10:00 | 12536.1 | 4.0905 | 89.203 | 74.6386 | 3673.9682
2031-11-15 11:00 | 13416 | 4.5078 | 89.249 | 74.6386 | 3931.8415
2031-11-16 12:00 | 14415.5 | 4.6935 | 89.6909 | 74.6386 | 4224.766
2031-11-17 13:00 | 14634.4 | 4.8006 | 89.8526 | 74.6386 | 4288.9193
2031-11-18 14:00 | 16704 | 5.2224 | 90.381 | 74.6386 | 4895.4592
2031-11-19 15:00 | 16376.1 | 5.2871 | 90.4161 | 74.6386 | 4799.3611
2031-11-20 16:00 | 19258.9 | 5.9733 | 90.88 | 74.6386 | 5644.2264
2031-11-21 17:00 | 14944.6 | 5.1522 | 90.4617 | 74.6386 | 4379.8299
2031-11-22 18:00 | 13769.9 | 4.3716 | 90.9651 | 74.6386 | 4035.5593
2031-11-23 19:00 | 12332.1 | 3.8081 | 91.0708 | 74.6386 | 3614.1817
2031-11-24 20:00 | 11312.1 | 3.5113 | 90.9201 | 74.6386 | 3315.2493
2031-11-25 21:00 | 10122.6 | 3.2322 | 90.586 | 74.6386 | 2966.6412
2031-11-26 22:00 | 9404.75 | 2.9977 | 90.4127 | 74.6386 | 2756.2601
2031-11-27 23:00 | 6773.45 | 1.9653 | 91.0147 | 74.6386 | 1985.1022
2031-11-29 | 6151.31 | 1.8008 | 90.6691 | 74.6386 | 1802.771
2031-11-30 01:00 | 5711.83 | 1.7179 | 90.2497 | 74.6386 | 1673.9721
2031-12-01 02:00 | 5350.76 | 1.6259 | 90.0032 | 74.6386 | 1568.153
2031-12-02 03:00 | 5056.78 | 1.6115 | 89.4902 | 74.6386 | 1481.9959
2031-12-03 04:00 | 4866.24 | 1.5383 | 89.3876 | 74.6386 | 1426.1542
2031-12-04 05:00 | 4883.89 | 1.5419 | 89.2931 | 74.6386 | 1431.3269
2031-12-05 06:00 | 7608.48 | 2.492 | 88.9358 | 74.6386 | 2229.8254
2031-12-06 07:00 | 9755.39 | 3.2281 | 88.9884 | 74.6386 | 2859.0226
2031-12-07 08:00 | 10327.5 | 3.258 | 89.548 | 74.6386 | 3026.6915
2031-12-08 09:00 | 11750.8 | 3.8704 | 89.367 | 74.6386 | 3443.8195
2031-12-09 10:00 | 13350.8 | 4.388 | 89.5646 | 74.6386 | 3912.7332
2031-12-10 11:00 | 14311.9 | 4.6059 | 89.9783 | 74.6386 | 4194.4038
2031-12-11 12:00 | 12263.7 | 4.2866 | 89.6214 | 74.6386 | 3594.1357
2031-12-12 13:00 | 14492 | 4.5525 | 90.3669 | 74.6386 | 4247.1859
2031-12-13 14:00 | 16190.3 | 5.1794 | 90.4144 | 74.6386 | 4744.9085
2031-12-14 15:00 | 15805.9 | 4.97 | 90.8058 | 74.6386 | 4632.252
2031-12-15 16:00 | 16908.9 | 5.6408 | 90.4825 | 74.6386 | 4955.5094
2031-12-16 17:00 | 14834.1 | 4.9795 | 90.6154 | 74.6386 | 4347.4456
2031-12-17 18:00 | 13648.4 | 4.3547 | 90.9893 | 74.6386 | 3999.9512
2031-12-18 19:00 | 12355 | 3.8707 | 91.0535 | 74.6386 | 3620.8931
2031-12-19 20:00 | 11688.5 | 3.5357 | 91.2134 | 74.6386 | 3425.5612
2031-12-20 21:00 | 10476.7 | 3.3085 | 90.7902 | 74.6386 | 3070.4177
2031-12-21 22:00 | 10051.4 | 3.115 | 90.7757 | 74.6386 | 2945.7746
2031-12-22 23:00 | 8032.61 | 2.2991 | 91.3008 | 74.6386 | 2354.1256
2031-12-24 | 7187.79 | 2.1726 | 90.6706 | 74.6386 | 2106.5333
2031-12-25 01:00 | 6657.52 | 2.0444 | 90.3697 | 74.6386 | 1951.1265
2031-12-26 02:00 | 6444.97 | 2.0124 | 90.0886 | 74.6386 | 1888.8343
2031-12-27 03:00 | 6618.32 | 2.1048 | 89.8323 | 74.6386 | 1939.6381
2031-12-28 04:00 | 6918.89 | 2.2019 | 89.7377 | 74.6386 | 2027.7265
2031-12-29 05:00 | 7829.88 | 2.5245 | 89.6105 | 74.6386 | 2294.7113
2031-12-30 06:00 | 8603.66 | 2.8301 | 89.4944 | 74.6386 | 2521.4838
2031-12-31 07:00 | 10556.4 | 3.3382 | 89.8381 | 74.6386 | 3093.7754
2032-01-01 08:00 | 11552.6 | 3.6337 | 90.0426 | 74.6386 | 3385.7328
2032-01-02 09:00 | 13465.5 | 4.405 | 89.9137 | 74.6386 | 3946.3485
2032-01-03 10:00 | 15521.5 | 5.0466 | 90.1842 | 74.6386 | 4548.9026
2032-01-04 11:00 | 17015.6 | 5.539 | 90.4756 | 74.6386 | 4986.7801
2032-01-05 12:00 | 18274.6 | 5.7577 | 91.028 | 74.6386 | 5355.7566
2032-01-06 13:00 | 15776.9 | 5.2248 | 90.9573 | 74.6386 | 4623.753
2032-01-07 14:00 | 14823.3 | 4.8894 | 91.0016 | 74.6386 | 4344.2804
2032-01-08 15:00 | 16103.6 | 5.2915 | 91.0002 | 74.6386 | 4719.4993
2032-01-09 16:00 | 15624.2 | 5.0484 | 91.2312 | 74.6386 | 4579.001
2032-01-10 17:00 | 15450.1 | 4.907 | 91.3979 | 74.6386 | 4527.9773
2032-01-11 18:00 | 13949.1 | 4.3884 | 91.4735 | 74.6386 | 4088.0777
2032-01-12 19:00 | 12243.4 | 3.9205 | 91.275 | 74.6386 | 3588.1863
2032-01-13 20:00 | 10264.2 | 3.1607 | 91.4356 | 74.6386 | 3008.1401
2032-01-14 21:00 | 10001.2 | 2.9027 | 91.6796 | 74.6386 | 2931.0624
2032-01-15 22:00 | 8132.85 | 2.365 | 91.513 | 74.6386 | 2383.5031
2032-01-16 23:00 | 7359.15 | 2.2168 | 90.9904 | 74.6386 | 2156.754
2032-01-18 | 7024.8 | 2.1448 | 90.665 | 74.6386 | 2058.7657
2032-01-19 01:00 | 6779.84 | 2.0899 | 90.4456 | 74.6386 | 1986.975
2032-01-20 02:00 | 6753.63 | 2.1063 | 90.2496 | 74.6386 | 1979.2936
2032-01-21 03:00 | 7190.25 | 2.233 | 90.1817 | 74.6386 | 2107.2543
2032-01-22 04:00 | 7433.95 | 2.3664 | 89.9608 | 74.6386 | 2178.6757
2032-01-23 05:00 | 8290.51 | 2.7278 | 89.6959 | 74.6386 | 2429.7086
2032-01-24 06:00 | 9562.18 | 3.0351 | 89.99 | 74.6386 | 2802.3983
2032-01-25 07:00 | 11318.8 | 3.5833 | 90.1065 | 74.6386 | 3317.2128
2032-01-26 08:00 | 12094.2 | 3.7369 | 90.4729 | 74.6386 | 3544.4601
2032-01-27 09:00 | 12962.3 | 4.2996 | 90.0965 | 74.6386 | 3798.8751
2032-01-28 10:00 | 14096.7 | 4.7213 | 90.1814 | 74.6386 | 4131.335
2032-01-29 11:00 | 15740.3 | 5.1478 | 90.5357 | 74.6386 | 4613.0266
2032-01-30 12:00 | 13963.4 | 4.746 | 90.5055 | 74.6386 | 4092.2686
2032-01-31 13:00 | 12366.1 | 4.0437 | 90.7973 | 74.6386 | 3624.1462
2032-02-01 14:00 | 12443.5 | 4.0236 | 90.7878 | 74.6386 | 3646.8299
2032-02-02 15:00 | 14225.5 | 4.689 | 90.6281 | 74.6386 | 4169.0825
2032-02-03 16:00 | 14923.7 | 4.7814 | 90.9618 | 74.6386 | 4373.7047
2032-02-04 17:00 | 15852.9 | 4.833 | 91.4384 | 74.6386 | 4646.0264
2032-02-05 18:00 | 14504 | 4.4057 | 91.6061 | 74.6386 | 4250.7028
2032-02-06 19:00 | 12315.7 | 3.9958 | 91.124 | 74.6386 | 3609.3754
2032-02-07 20:00 | 10207.5 | 3.154 | 91.3656 | 74.6386 | 2991.5229
2032-02-08 21:00 | 9201.62 | 2.9001 | 91.0021 | 74.6386 | 2696.7286
2032-02-09 22:00 | 7735.94 | 2.2659 | 91.3842 | 74.6386 | 2267.1802
2032-02-10 23:00 | 6734.19 | 2.0732 | 90.7497 | 74.6386 | 1973.5963
2032-02-12 | 6317.27 | 1.9602 | 90.4689 | 74.6386 | 1851.4091
2032-02-13 01:00 | 5921.59 | 1.8289 | 90.3512 | 74.6386 | 1735.4467
2032-02-14 02:00 | 5594.94 | 1.7424 | 90.1636 | 74.6386 | 1639.7151
2032-02-15 03:00 | 5585.1 | 1.7673 | 89.9151 | 74.6386 | 1636.8312
2032-02-16 04:00 | 5953.35 | 1.8958 | 89.7692 | 74.6386 | 1744.7547
2032-02-17 05:00 | 6968.59 | 2.2778 | 89.5149 | 74.6386 | 2042.2921
2032-02-18 06:00 | 7756.83 | 2.558 | 89.4609 | 74.6386 | 2273.3025
2032-02-19 07:00 | 8322.64 | 2.6062 | 89.8795 | 74.6386 | 2439.125
2032-02-20 08:00 | 7371.03 | 2.339 | 89.8293 | 74.6386 | 2160.2356
2032-02-21 09:00 | 7949.93 | 2.5629 | 89.6549 | 74.6386 | 2329.8945
2032-02-22 10:00 | 8883.48 | 2.8783 | 89.6189 | 74.6386 | 2603.491
2032-02-23 11:00 | 9591.94 | 3.1094 | 89.6713 | 74.6386 | 2811.1201
2032-02-24 12:00 | 10305.1 | 3.3851 | 89.6395 | 74.6386 | 3020.1267
2032-02-25 13:00 | 11926.2 | 3.8788 | 89.7936 | 74.6386 | 3495.2242
2032-02-26 14:00 | 11804.4 | 3.7855 | 90.0804 | 74.6386 | 3459.5281
2032-02-27 15:00 | 12506.9 | 4.1385 | 89.9468 | 74.6386 | 3665.4106
2032-02-28 16:00 | 12317.6 | 4.0793 | 90.0432 | 74.6386 | 3609.9322
2032-02-29 17:00 | 12272.9 | 3.9309 | 90.3387 | 74.6386 | 3596.8319
2032-03-01 18:00 | 11200 | 3.5027 | 90.5541 | 74.6386 | 3282.396
2032-03-02 19:00 | 10339.1 | 3.1871 | 90.6127 | 74.6386 | 3030.0911
2032-03-03 20:00 | 8415.62 | 2.5335 | 90.7341 | 74.6386 | 2466.3748
2032-03-04 21:00 | 7648.49 | 2.3274 | 90.4821 | 74.6386 | 2241.5511
2032-03-05 22:00 | 6077.41 | 1.7544 | 90.7599 | 74.6386 | 1781.1131
2032-03-06 23:00 | 5605.41 | 1.6784 | 90.2674 | 74.6386 | 1642.7835
2032-03-08 | 5295.62 | 1.6341 | 89.8753 | 74.6386 | 1551.993
2032-03-09 01:00 | 5198.1 | 1.6 | 89.7612 | 74.6386 | 1523.4127
2032-03-10 02:00 | 5234.68 | 1.6398 | 89.5314 | 74.6386 | 1534.1333
2032-03-11 03:00 | 5529.72 | 1.7817 | 89.2423 | 74.6386 | 1620.601
2032-03-12 04:00 | 5686.87 | 1.8621 | 89.0883 | 74.6386 | 1666.6571
2032-03-13 05:00 | 6630.41 | 2.2232 | 88.885 | 74.6386 | 1943.1814
2032-03-14 06:00 | 6895.97 | 2.2263 | 89.1881 | 74.6386 | 2021.0093
2032-03-15 07:00 | 7852.48 | 2.5249 | 89.234 | 74.6386 | 2301.3347
2032-03-16 08:00 | 7795.05 | 2.4215 | 89.5682 | 74.6386 | 2284.5036
2032-03-17 09:00 | 9761.38 | 3.2437 | 89.1037 | 74.6386 | 2860.7781
2032-03-18 10:00 | 11387.1 | 3.9086 | 89.0429 | 74.6386 | 3337.2296
2032-03-19 11:00 | 12799.1 | 4.2162 | 89.545 | 74.6386 | 3751.0459
2032-03-20 12:00 | 11328.7 | 3.5994 | 90.0421 | 74.6386 | 3320.1142
2032-03-21 13:00 | 10659.5 | 3.4438 | 89.9491 | 74.6386 | 3123.9911
2032-03-22 14:00 | 11078.7 | 3.4879 | 90.1386 | 74.6386 | 3246.8465
2032-03-23 15:00 | 12573.7 | 3.982 | 90.1402 | 74.6386 | 3684.9877
2032-03-24 16:00 | 13288.7 | 4.3146 | 90.0924 | 74.6386 | 3894.5335
2032-03-25 17:00 | 13494.5 | 4.2601 | 90.4115 | 74.6386 | 3954.8476
2032-03-26 18:00 | 12218.5 | 3.769 | 90.6876 | 74.6386 | 3580.8889
2032-03-27 19:00 | 11003.5 | 3.4536 | 90.5504 | 74.6386 | 3224.8075
2032-03-28 20:00 | 8724.31 | 2.702 | 90.5969 | 74.6386 | 2556.8429
2032-03-29 21:00 | 7833.92 | 2.4321 | 90.3874 | 74.6386 | 2295.8953
2032-03-30 22:00 | 6101.65 | 1.8086 | 90.5741 | 74.6386 | 1788.2171
2032-03-31 23:00 | 5425.53 | 1.6593 | 90.0878 | 74.6386 | 1590.0659
2032-04-02 | 5302.82 | 1.5725 | 90.1384 | 74.6386 | 1554.1031
2032-04-03 01:00 | 5090.94 | 1.5594 | 89.7587 | 74.6386 | 1492.0072
2032-04-04 02:00 | 5294.53 | 1.6058 | 89.7375 | 74.6386 | 1551.6736
2032-04-05 03:00 | 5431.44 | 1.7526 | 89.1966 | 74.6386 | 1591.7979
2032-04-06 04:00 | 5870.69 | 1.8827 | 89.1934 | 74.6386 | 1720.5294
2032-04-07 05:00 | 6736.79 | 2.2522 | 88.8704 | 74.6386 | 1974.3583
2032-04-08 06:00 | 7622.01 | 2.466 | 89.1391 | 74.6386 | 2233.7906
2032-04-09 07:00 | 9572.85 | 3.0015 | 89.4389 | 74.6386 | 2805.5254
2032-04-10 08:00 | 9909.75 | 3.1868 | 89.4344 | 74.6386 | 2904.261
2032-04-11 09:00 | 11631.7 | 3.824 | 89.3991 | 74.6386 | 3408.9148
2032-04-12 10:00 | 12069.1 | 4.0704 | 89.4224 | 74.6386 | 3537.1041
2032-04-13 11:00 | 12672.6 | 4.2029 | 89.7039 | 74.6386 | 3713.9724
2032-04-14 12:00 | 14036.1 | 4.3994 | 90.2712 | 74.6386 | 4113.5748
2032-04-15 13:00 | 14467.1 | 4.6048 | 90.3641 | 74.6386 | 4239.8885
2032-04-16 14:00 | 14750.2 | 4.7499 | 90.4588 | 74.6386 | 4322.8569
2032-04-17 15:00 | 15268.3 | 5.0057 | 90.46 | 74.6386 | 4474.697
2032-04-18 16:00 | 15723.1 | 5.1195 | 90.6532 | 74.6386 | 4607.9857
2032-04-19 17:00 | 15615.8 | 5.0162 | 90.8952 | 74.6386 | 4576.5392
2032-04-20 18:00 | 13548.3 | 4.347 | 91.0003 | 74.6386 | 3970.6148
2032-04-21 19:00 | 11897.3 | 3.746 | 91.0644 | 74.6386 | 3486.7544
2032-04-22 20:00 | 9605.59 | 2.9556 | 91.1126 | 74.6386 | 2815.1205
2032-04-23 21:00 | 8270.34 | 2.5903 | 90.7556 | 74.6386 | 2423.7974
2032-04-24 22:00 | 6287.79 | 1.8733 | 90.9254 | 74.6386 | 1842.7693
2032-04-25 23:00 | 4626.16 | 1.4154 | 90.4368 | 74.6386 | 1355.7937
2032-04-27 | 3816.07 | 1.1843 | 90.0278 | 74.6386 | 1118.3797
2032-04-28 01:00 | 3252.06 | 1.0052 | 89.8069 | 74.6386 | 953.0847
2032-04-29 02:00 | 3148.02 | 1 | 90.3941 | 74.6386 | 922.5936
2032-04-30 03:00 | 3188.79 | 1 | 91.3791 | 74.6386 | 934.5421
2032-05-01 04:00 | 3202.83 | 1 | 91.4209 | 74.6386 | 938.6568
2032-05-02 05:00 | 3157.47 | 1 | 90.7806 | 74.6386 | 925.3631
2032-05-03 06:00 | 5399.3 | 1.6681 | 89.0668 | 74.6386 | 1582.3786
2032-05-04 07:00 | 7004.23 | 2.3491 | 88.5402 | 74.6386 | 2052.7372
2032-05-05 08:00 | 6939.11 | 2.2442 | 88.9426 | 74.6386 | 2033.6524
2032-05-06 09:00 | 8003.78 | 2.6378 | 88.8459 | 74.6386 | 2345.6764
2032-05-07 10:00 | 9731.08 | 3.2755 | 88.7944 | 74.6386 | 2851.898
2032-05-08 11:00 | 11109.1 | 3.6153 | 89.2383 | 74.6386 | 3255.7558
2032-05-09 12:00 | 11474.9 | 3.779 | 89.3614 | 74.6386 | 3362.9612
2032-05-10 13:00 | 12369.4 | 3.9876 | 89.6606 | 74.6386 | 3625.1133
2032-05-11 14:00 | 12948.4 | 4.1894 | 89.8075 | 74.6386 | 3794.8014
2032-05-12 15:00 | 13041.2 | 4.2668 | 89.8886 | 74.6386 | 3821.9984
2032-05-13 16:00 | 15412.7 | 5.095 | 89.923 | 74.6386 | 4517.0165
2032-05-14 17:00 | 14096.9 | 4.5786 | 90.3085 | 74.6386 | 4131.3936
2032-05-15 18:00 | 12206.9 | 3.9218 | 90.4619 | 74.6386 | 3577.4892
2032-05-16 19:00 | 10649.2 | 3.3308 | 90.5764 | 74.6386 | 3120.9724
2032-05-17 20:00 | 9375.08 | 2.9409 | 90.4419 | 74.6386 | 2747.5647
2032-05-18 21:00 | 8562.65 | 2.6667 | 90.3721 | 74.6386 | 2509.465
2032-05-19 22:00 | 8045.24 | 2.4967 | 90.2535 | 74.6386 | 2357.8271
2032-05-20 23:00 | 5411.52 | 1.4972 | 91.061 | 74.6386 | 1585.96
2032-05-22 | 4887.07 | 1.4523 | 90.2087 | 74.6386 | 1432.2588
2032-05-23 01:00 | 4593.62 | 1.3822 | 89.9178 | 74.6386 | 1346.2571
2032-05-24 02:00 | 4368.11 | 1.3414 | 89.6247 | 74.6386 | 1280.1667
2032-05-25 03:00 | 4294.08 | 1.3396 | 89.3807 | 74.6386 | 1258.4706
2032-05-26 04:00 | 4130.2 | 1.2853 | 89.2738 | 74.6386 | 1210.4421
2032-05-27 05:00 | 4161.13 | 1.3049 | 89.1235 | 74.6386 | 1219.5068
2032-05-28 06:00 | 6006.53 | 2.0004 | 88.6071 | 74.6386 | 1760.3402
2032-05-29 07:00 | 7171.09 | 2.4804 | 88.4142 | 74.6386 | 2101.639
2032-05-30 08:00 | 6510.78 | 1.9911 | 89.4211 | 74.6386 | 1908.1213
2032-05-31 09:00 | 7873.73 | 2.7146 | 88.5337 | 74.6386 | 2307.5625
2032-06-01 10:00 | 8931.65 | 3.0551 | 88.6757 | 74.6386 | 2617.6082
2032-06-02 11:00 | 10493.9 | 3.4576 | 89.0849 | 74.6386 | 3075.4585
2032-06-03 12:00 | 11915.1 | 3.8915 | 89.3287 | 74.6386 | 3491.9711
2032-06-04 13:00 | 12840.3 | 3.9609 | 89.955 | 74.6386 | 3763.1205
2032-06-05 14:00 | 12722 | 4.0638 | 89.8957 | 74.6386 | 3728.4502
2032-06-06 15:00 | 11491.3 | 3.5985 | 90.1647 | 74.6386 | 3367.7676
2032-06-07 16:00 | 13141.4 | 4.4278 | 89.6226 | 74.6386 | 3851.3642
2032-06-08 17:00 | 12314.8 | 3.9145 | 90.1883 | 74.6386 | 3609.1116
2032-06-09 18:00 | 11153.8 | 3.5281 | 90.259 | 74.6386 | 3268.8561
2032-06-10 19:00 | 10159 | 3.153 | 90.3331 | 74.6386 | 2977.309
2032-06-11 20:00 | 9514.49 | 2.9238 | 90.3328 | 74.6386 | 2788.4218
2032-06-12 21:00 | 8958.03 | 2.7691 | 90.2287 | 74.6386 | 2625.3394
2032-06-13 22:00 | 8786.85 | 2.6625 | 90.3007 | 74.6386 | 2575.1715
2032-06-14 23:00 | 6732.07 | 1.882 | 90.9033 | 74.6386 | 1972.975
2032-06-16 | 6241.22 | 1.8321 | 90.3171 | 74.6386 | 1829.121
2032-06-17 01:00 | 5766.01 | 1.757 | 89.8797 | 74.6386 | 1689.8507
2032-06-18 02:00 | 5464.68 | 1.7716 | 89.2994 | 74.6386 | 1601.5396
2032-06-19 03:00 | 5890.9 | 1.854 | 89.4213 | 74.6386 | 1726.4524
2032-06-20 04:00 | 6192.41 | 2.0118 | 89.1311 | 74.6386 | 1814.8162
2032-06-21 05:00 | 6779.35 | 2.3197 | 88.7539 | 74.6386 | 1986.8314
2032-06-22 06:00 | 6992.71 | 2.2332 | 89.2673 | 74.6386 | 2049.361
2032-06-23 07:00 | 7206.09 | 2.3592 | 89.1007 | 74.6386 | 2111.8965
2032-06-24 08:00 | 6880.54 | 2.0874 | 89.6959 | 74.6386 | 2016.4872
2032-06-25 09:00 | 8464.1 | 2.664 | 89.3909 | 74.6386 | 2480.5828
2032-06-26 10:00 | 9062.27 | 3.0095 | 89.0911 | 74.6386 | 2655.8892
2032-06-27 11:00 | 10904.9 | 3.6715 | 89.0846 | 74.6386 | 3195.9107
2032-06-28 12:00 | 11348.2 | 3.753 | 89.3901 | 74.6386 | 3325.8291
2032-06-29 13:00 | 12030.6 | 3.8832 | 89.704 | 74.6386 | 3525.8208
2032-06-30 14:00 | 11801.2 | 3.7688 | 89.9276 | 74.6386 | 3458.5903
2032-07-01 15:00 | 13553.1 | 4.3377 | 89.9883 | 74.6386 | 3972.0215
2032-07-02 16:00 | 13607.1 | 4.3896 | 90.115 | 74.6386 | 3987.8474
2032-07-03 17:00 | 13847.5 | 4.4512 | 90.2581 | 74.6386 | 4058.3016
2032-07-04 18:00 | 12955.8 | 4.0493 | 90.5692 | 74.6386 | 3796.9702
2032-07-05 19:00 | 11289.2 | 3.6085 | 90.4249 | 74.6386 | 3308.5379
2032-07-06 20:00 | 9523.57 | 2.9036 | 90.7151 | 74.6386 | 2791.0829
2032-07-07 21:00 | 8634.35 | 2.6456 | 90.5161 | 74.6386 | 2530.4782
2032-07-08 22:00 | 6908.22 | 2.0313 | 90.6994 | 74.6386 | 2024.5994
2032-07-09 23:00 | 6240.51 | 1.8797 | 90.295 | 74.6386 | 1828.9129
2032-07-11 | 5973.9 | 1.8087 | 90.0743 | 74.6386 | 1750.7773
2032-07-12 01:00 | 5942.05 | 1.8114 | 89.8936 | 74.6386 | 1741.443
2032-07-13 02:00 | 5546.2 | 1.7573 | 89.5164 | 74.6386 | 1625.4308
2032-07-14 03:00 | 5830.66 | 1.8578 | 89.3664 | 74.6386 | 1708.7978
2032-07-15 04:00 | 6120.71 | 1.9391 | 89.355 | 74.6386 | 1793.803
2032-07-16 05:00 | 7120.53 | 2.3464 | 89.0374 | 74.6386 | 2086.8213
2032-07-17 06:00 | 7727.73 | 2.5238 | 89.1377 | 74.6386 | 2264.7741
2032-07-18 07:00 | 8783.79 | 2.8403 | 89.2603 | 74.6386 | 2574.2747
2032-07-19 08:00 | 8591.58 | 2.6511 | 89.7206 | 74.6386 | 2517.9435
2032-07-20 09:00 | 10170.2 | 3.354 | 89.2695 | 74.6386 | 2980.5914
2032-07-21 10:00 | 11929.9 | 4.0781 | 89.1675 | 74.6386 | 3496.3086
2032-07-22 11:00 | 13313 | 4.4818 | 89.4942 | 74.6386 | 3901.6552
2032-07-23 12:00 | 14092.2 | 4.6159 | 89.917 | 74.6386 | 4130.0161
2032-07-24 13:00 | 14596.2 | 4.7952 | 90.0892 | 74.6386 | 4277.724
2032-07-25 14:00 | 15759.3 | 5.1482 | 90.3164 | 74.6386 | 4618.5949
2032-07-26 15:00 | 16823.8 | 5.4862 | 90.5465 | 74.6386 | 4930.5691
2032-07-27 16:00 | 16192.4 | 5.1353 | 90.9763 | 74.6386 | 4745.524
2032-07-28 17:00 | 15210.9 | 4.904 | 90.9533 | 74.6386 | 4457.8747
2032-07-29 18:00 | 13969.9 | 4.3041 | 91.3112 | 74.6386 | 4094.1735
2032-07-30 19:00 | 12396.2 | 3.8386 | 91.2347 | 74.6386 | 3632.9676
2032-07-31 20:00 | 10224.5 | 3.139 | 91.1982 | 74.6386 | 2996.5052
2032-08-01 21:00 | 9472.66 | 2.8897 | 91.0344 | 74.6386 | 2776.1626
2032-08-02 22:00 | 8088.44 | 2.3036 | 91.419 | 74.6386 | 2370.4878
2032-08-03 23:00 | 6592.62 | 1.999 | 90.7198 | 74.6386 | 1932.1062
2032-08-05 | 6122.82 | 1.8614 | 90.4631 | 74.6386 | 1794.4214
2032-08-06 01:00 | 5649.17 | 1.7281 | 90.2338 | 74.6386 | 1655.6083
2032-08-07 02:00 | 5396.27 | 1.6579 | 90.0484 | 74.6386 | 1581.4906
2032-08-08 03:00 | 5391.59 | 1.6521 | 89.9224 | 74.6386 | 1580.1191
2032-08-09 04:00 | 5140.86 | 1.5768 | 89.8056 | 74.6386 | 1506.6373
2032-08-10 05:00 | 5232.36 | 1.625 | 89.6069 | 74.6386 | 1533.4533
2032-08-11 06:00 | 7237.73 | 2.462 | 88.865 | 74.6386 | 2121.1693
2032-08-12 07:00 | 8533.39 | 3.0606 | 88.5917 | 74.6386 | 2500.8897
2032-08-13 08:00 | 9147.53 | 3.0048 | 89.3334 | 74.6386 | 2680.8764
2032-08-14 09:00 | 9948.31 | 3.2719 | 89.4226 | 74.6386 | 2915.5619
2032-08-15 10:00 | 11696.2 | 3.837 | 89.5593 | 74.6386 | 3427.8178
2032-08-16 11:00 | 12414.6 | 4.1465 | 89.6445 | 74.6386 | 3638.3601
2032-08-17 12:00 | 13585.9 | 4.4346 | 89.9811 | 74.6386 | 3981.6342
2032-08-18 13:00 | 13527.1 | 4.2852 | 90.3897 | 74.6386 | 3964.4017
2032-08-19 14:00 | 12113.4 | 4.1148 | 90.0106 | 74.6386 | 3550.0871
2032-08-20 15:00 | 12259.7 | 3.9402 | 90.3853 | 74.6386 | 3592.9634
2032-08-21 16:00 | 15403.3 | 4.7872 | 90.6485 | 74.6386 | 4514.2616
2032-08-22 17:00 | 14491.8 | 4.4583 | 90.9954 | 74.6386 | 4247.1273
2032-08-23 18:00 | 12953.9 | 4.0661 | 90.9213 | 74.6386 | 3796.4133
2032-08-24 19:00 | 11624 | 3.6149 | 90.9253 | 74.6386 | 3406.6581
2032-08-25 20:00 | 10339.5 | 3.2748 | 90.712 | 74.6386 | 3030.2083
2032-08-26 21:00 | 9533.3 | 2.9781 | 90.7123 | 74.6386 | 2793.9344
2032-08-27 22:00 | 9096.49 | 2.7997 | 90.6844 | 74.6386 | 2665.9181
2032-08-28 23:00 | 6428.77 | 1.935 | 90.7496 | 74.6386 | 1884.0865
2032-08-30 | 5850.5 | 1.8145 | 90.2505 | 74.6386 | 1714.6123
2032-08-31 01:00 | 6089.99 | 1.7536 | 90.6382 | 74.6386 | 1784.7999
2032-09-01 02:00 | 5839.78 | 1.8046 | 89.9929 | 74.6386 | 1711.4706
2032-09-02 03:00 | 6018.77 | 1.911 | 89.6975 | 74.6386 | 1763.9274
2032-09-03 04:00 | 6306.34 | 2.0082 | 89.5867 | 74.6386 | 1848.2058
2032-09-04 05:00 | 7132.05 | 2.3597 | 89.2774 | 74.6386 | 2090.1975
2032-09-05 06:00 | 7976.38 | 2.5734 | 89.4866 | 74.6386 | 2337.6462
2032-09-06 07:00 | 9095.45 | 2.9796 | 89.4326 | 74.6386 | 2665.6133
2032-09-07 08:00 | 9741.33 | 3.158 | 89.6189 | 74.6386 | 2854.902
2032-09-08 09:00 | 11548.9 | 3.7958 | 89.623 | 74.6386 | 3384.6485
2032-09-09 10:00 | 12305.3 | 4.2137 | 89.5226 | 74.6386 | 3606.3274
2032-09-10 11:00 | 14139.5 | 4.725 | 89.8698 | 74.6386 | 4143.8784
2032-09-11 12:00 | 14532.1 | 4.7062 | 90.3389 | 74.6386 | 4258.9381
2032-09-12 13:00 | 15129.1 | 4.8601 | 90.5815 | 74.6386 | 4433.9015
2032-09-13 14:00 | 16826.9 | 5.3313 | 90.8616 | 74.6386 | 4931.4776
2032-09-14 15:00 | 17719 | 5.5323 | 91.2264 | 74.6386 | 5192.9263
2032-09-15 16:00 | 16747.7 | 5.4018 | 91.2206 | 74.6386 | 4908.2664
2032-09-16 17:00 | 14807.2 | 4.7651 | 91.3167 | 74.6386 | 4339.5619
2032-09-17 18:00 | 13232.1 | 4.0999 | 91.5436 | 74.6386 | 3877.9457
2032-09-18 19:00 | 11381.9 | 3.5672 | 91.3542 | 74.6386 | 3335.7056
2032-09-19 20:00 | 9093.34 | 2.7868 | 91.3529 | 74.6386 | 2664.9949
2032-09-20 21:00 | 8217.3 | 2.5571 | 90.9595 | 74.6386 | 2408.2529
2032-09-21 22:00 | 6500.33 | 1.9118 | 91.1782 | 74.6386 | 1905.0587
2032-09-22 23:00 | 5947.15 | 1.7685 | 90.8341 | 74.6386 | 1742.9376
2032-09-24 | 5428.12 | 1.7066 | 90.1975 | 74.6386 | 1590.8249
2032-09-25 01:00 | 5391.97 | 1.6211 | 90.3662 | 74.6386 | 1580.2304
2032-09-26 02:00 | 5458.8 | 1.6478 | 90.2028 | 74.6386 | 1599.8164
2032-09-27 03:00 | 5656.67 | 1.7872 | 89.7431 | 74.6386 | 1657.8063
2032-09-28 04:00 | 5922.73 | 1.9192 | 89.4862 | 74.6386 | 1735.7808
2032-09-29 05:00 | 6437.23 | 2.1991 | 89.0687 | 74.6386 | 1886.5659
2032-09-30 06:00 | 7106.87 | 2.3372 | 89.3317 | 74.6386 | 2082.818
2032-10-01 07:00 | 8369.14 | 2.7038 | 89.4899 | 74.6386 | 2452.7528
2032-10-02 08:00 | 8815.42 | 2.8665 | 89.5476 | 74.6386 | 2583.5446
2032-10-03 09:00 | 10458.8 | 3.5343 | 89.353 | 74.6386 | 3065.1717
2032-10-04 10:00 | 12291 | 4.181 | 89.4741 | 74.6386 | 3602.1365
2032-10-05 11:00 | 14053.9 | 4.6477 | 89.9061 | 74.6386 | 4118.7915
2032-10-06 12:00 | 14536.6 | 4.8452 | 90.1206 | 74.6386 | 4260.2569
2032-10-07 13:00 | 16023.8 | 5.044 | 90.7364 | 74.6386 | 4696.1122
2032-10-08 14:00 | 16792.1 | 5.3819 | 90.8554 | 74.6386 | 4921.2787
2032-10-09 15:00 | 18244.9 | 5.8291 | 91.1067 | 74.6386 | 5347.0524
2032-10-10 16:00 | 18547.3 | 5.8232 | 91.4957 | 74.6386 | 5435.6771
2032-10-11 17:00 | 17959.5 | 5.7157 | 91.5973 | 74.6386 | 5263.4099
2032-10-12 18:00 | 15128.8 | 4.7294 | 91.8525 | 74.6386 | 4433.8136
2032-10-13 19:00 | 12758.8 | 4.079 | 91.5866 | 74.6386 | 3739.2352
2032-10-14 20:00 | 10732.1 | 3.2622 | 91.7917 | 74.6386 | 3145.268
2032-10-15 21:00 | 9447.9 | 2.9465 | 91.3678 | 74.6386 | 2768.9062
2032-10-16 22:00 | 7726.01 | 2.2991 | 91.5106 | 74.6386 | 2264.27
2032-10-17 23:00 | 6455.29 | 1.9316 | 91.1969 | 74.6386 | 1891.8587
2032-10-19 | 5903.02 | 1.7508 | 91.0153 | 74.6386 | 1730.0044
2032-10-20 01:00 | 5446.95 | 1.6622 | 90.5914 | 74.6386 | 1596.3435
2032-10-21 02:00 | 4907.04 | 1.5608 | 90.1055 | 74.6386 | 1438.1115
2032-10-22 03:00 | 4865.53 | 1.4806 | 90.2597 | 74.6386 | 1425.9461
2032-10-23 04:00 | 4586.44 | 1.4345 | 89.908 | 74.6386 | 1344.1529
2032-10-24 05:00 | 4571.44 | 1.4362 | 89.7383 | 74.6386 | 1339.7568
2032-10-25 06:00 | 6759.02 | 2.282 | 89.1082 | 74.6386 | 1980.8732
2032-10-26 07:00 | 8566.16 | 3.0609 | 88.7998 | 74.6386 | 2510.4937
2032-10-27 08:00 | 9585 | 3.11 | 89.633 | 74.6386 | 2809.0862
2032-10-28 09:00 | 11021.5 | 3.5487 | 89.828 | 74.6386 | 3230.0828
2032-10-29 10:00 | 12426.6 | 4.1839 | 89.6946 | 74.6386 | 3641.877
2032-10-30 11:00 | 14087.5 | 4.682 | 90.0141 | 74.6386 | 4128.6387
2032-10-31 12:00 | 14999.7 | 4.9092 | 90.3782 | 74.6386 | 4395.9781
2032-11-01 13:00 | 15863.8 | 5.0537 | 90.7939 | 74.6386 | 4649.2208
2032-11-02 14:00 | 16226.2 | 5.3941 | 90.6924 | 74.6386 | 4755.4298
2032-11-03 15:00 | 16552.5 | 5.3809 | 91.0186 | 74.6386 | 4851.0589
2032-11-04 16:00 | 18963.9 | 5.9287 | 91.4539 | 74.6386 | 5557.7705
2032-11-05 17:00 | 17312.4 | 5.3566 | 91.8306 | 74.6386 | 5073.7636
2032-11-06 18:00 | 15389.4 | 4.7572 | 91.9167 | 74.6386 | 4510.1879
2032-11-07 19:00 | 13638.5 | 4.1913 | 91.891 | 74.6386 | 3997.0498
2032-11-08 20:00 | 12115.4 | 3.8278 | 91.572 | 74.6386 | 3550.6732
2032-11-09 21:00 | 11260.9 | 3.5466 | 91.4565 | 74.6386 | 3300.244
2032-11-10 22:00 | 10650.2 | 3.3107 | 91.4035 | 74.6386 | 3121.2655
2032-11-11 23:00 | 7446.95 | 2.2444 | 91.5186 | 74.6386 | 2182.4856
2032-11-13 | 6902.34 | 2.0506 | 91.3214 | 74.6386 | 2022.8762
2032-11-14 01:00 | 6185.51 | 1.8958 | 90.8572 | 74.6386 | 1812.794
2032-11-15 02:00 | 6068.63 | 1.7671 | 91.0855 | 74.6386 | 1778.5399
2032-11-16 03:00 | 5822.01 | 1.7674 | 90.6089 | 74.6386 | 1706.2627
2032-11-17 04:00 | 5160.33 | 1.6633 | 90.0039 | 74.6386 | 1512.3434
2032-11-18 05:00 | 5376.11 | 1.6628 | 90.1695 | 74.6386 | 1575.5823
2032-11-19 06:00 | 7772.51 | 2.7195 | 89.189 | 74.6386 | 2277.8978
2032-11-20 07:00 | 9702.2 | 3.2912 | 89.5065 | 74.6386 | 2843.4341
2032-11-21 08:00 | 10058 | 3.289 | 89.9449 | 74.6386 | 2947.7088
2032-11-22 09:00 | 11155.7 | 3.6416 | 90.0556 | 74.6386 | 3269.4129
2032-11-23 10:00 | 12636.3 | 4.2097 | 90.0453 | 74.6386 | 3703.334
2032-11-24 11:00 | 13768.1 | 4.642 | 90.1762 | 74.6386 | 4035.0318
2032-11-25 12:00 | 14889.2 | 4.8672 | 90.598 | 74.6386 | 4363.5938
2032-11-26 13:00 | 15863.1 | 5.0873 | 90.935 | 74.6386 | 4649.0157
2032-11-27 14:00 | 16447.6 | 5.3303 | 91.0671 | 74.6386 | 4820.3157
2032-11-28 15:00 | 16777.6 | 5.488 | 91.1847 | 74.6386 | 4917.0292
2032-11-29 16:00 | 18547.8 | 5.9417 | 91.4836 | 74.6386 | 5435.8236
2032-11-30 17:00 | 18856.7 | 5.5935 | 92.3247 | 74.6386 | 5526.3532
2032-12-01 18:00 | 16331.9 | 5.0315 | 92.2262 | 74.6386 | 4786.4074
2032-12-02 19:00 | 13988.2 | 4.5335 | 91.797 | 74.6386 | 4099.5367
2032-12-03 20:00 | 12582.1 | 4.0606 | 91.6737 | 74.6386 | 3687.4495
2032-12-04 21:00 | 11651.1 | 3.6512 | 91.7474 | 74.6386 | 3414.6003
2032-12-05 22:00 | 10709.9 | 3.4071 | 91.4825 | 74.6386 | 3138.7619
2032-12-06 23:00 | 8426.4 | 2.5115 | 91.8205 | 74.6386 | 2469.5341
2032-12-08 | 7880.82 | 2.3244 | 91.6428 | 74.6386 | 2309.6403
2032-12-09 01:00 | 7413.49 | 2.2442 | 91.2517 | 74.6386 | 2172.6794
2032-12-10 02:00 | 7032.55 | 2.1406 | 91.0649 | 74.6386 | 2061.037
2032-12-11 03:00 | 7135.5 | 2.2409 | 90.6882 | 74.6386 | 2091.2086
2032-12-12 04:00 | 7315.09 | 2.3288 | 90.4806 | 74.6386 | 2143.8413
2032-12-13 05:00 | 8102.47 | 2.6289 | 90.2781 | 74.6386 | 2374.5996
2032-12-14 06:00 | 8894.84 | 2.8357 | 90.4064 | 74.6386 | 2606.8203
2032-12-15 07:00 | 9851.27 | 3.2358 | 90.229 | 74.6386 | 2887.1222
2032-12-16 08:00 | 10496.7 | 3.4279 | 90.3549 | 74.6386 | 3076.2791
2032-12-17 09:00 | 11915 | 3.9578 | 90.3166 | 74.6386 | 3491.9418
2032-12-18 10:00 | 13435 | 4.4194 | 90.5344 | 74.6386 | 3937.4098
2032-12-19 11:00 | 14851.9 | 4.8124 | 90.8456 | 74.6386 | 4352.6622
2032-12-20 12:00 | 13274.3 | 4.4792 | 90.7786 | 74.6386 | 3890.3133
2032-12-21 13:00 | 11804.8 | 3.8471 | 91.0416 | 74.6386 | 3459.6454
2032-12-22 14:00 | 12774.7 | 4.0814 | 91.1016 | 74.6386 | 3743.895
2032-12-23 15:00 | 13825.9 | 4.3921 | 91.1883 | 74.6386 | 4051.9713
2032-12-24 16:00 | 14229.6 | 4.4053 | 91.4742 | 74.6386 | 4170.2841
2032-12-25 17:00 | 14333 | 4.4471 | 91.5095 | 74.6386 | 4200.5876
2032-12-26 18:00 | 12875.5 | 4.0191 | 91.5199 | 74.6386 | 3773.4366
2032-12-27 19:00 | 11976.4 | 3.6579 | 91.6462 | 74.6386 | 3509.9364
2032-12-28 20:00 | 9894.6 | 3.0018 | 91.627 | 74.6386 | 2899.821
2032-12-29 21:00 | 9152.61 | 2.8037 | 91.3619 | 74.6386 | 2682.3652
2032-12-30 22:00 | 7253.76 | 2.1629 | 91.4005 | 74.6386 | 2125.8672
2032-12-31 23:00 | 6822.63 | 2.0324 | 91.1578 | 74.6386 | 1999.5155
2033-01-02 | 6305.92 | 1.9354 | 90.7477 | 74.6386 | 1848.0827
2033-01-03 01:00 | 6047.47 | 1.8861 | 90.4831 | 74.6386 | 1772.3385
2033-01-04 02:00 | 6191.71 | 1.8921 | 90.5233 | 74.6386 | 1814.6111
2033-01-05 03:00 | 6309.26 | 2.0151 | 90.1045 | 74.6386 | 1849.0616
2033-01-06 04:00 | 6649.25 | 2.1273 | 90.0384 | 74.6386 | 1948.7028
2033-01-07 05:00 | 7474.87 | 2.4757 | 89.7542 | 74.6386 | 2190.6681
2033-01-08 06:00 | 7798.46 | 2.5921 | 89.754 | 74.6386 | 2285.503
2033-01-09 07:00 | 8768.92 | 2.8045 | 90.0513 | 74.6386 | 2569.9168
2033-01-10 08:00 | 8670.35 | 2.6331 | 90.5176 | 74.6386 | 2541.0288
2033-01-11 09:00 | 10064.6 | 3.2714 | 90.0303 | 74.6386 | 2949.6431
2033-01-12 10:00 | 11594.8 | 4.0708 | 89.6043 | 74.6386 | 3398.1004
2033-01-13 11:00 | 11778.1 | 3.894 | 90.1927 | 74.6386 | 3451.8204
2033-01-14 12:00 | 11836 | 3.8804 | 90.3647 | 74.6386 | 3468.7892
2033-01-15 13:00 | 10557.1 | 3.4718 | 90.4149 | 74.6386 | 3093.9806
2033-01-16 14:00 | 10857.4 | 3.4723 | 90.5832 | 74.6386 | 3181.9898
2033-01-17 15:00 | 11981.7 | 3.851 | 90.5489 | 74.6386 | 3511.4896
2033-01-18 16:00 | 12548.1 | 3.9636 | 90.7547 | 74.6386 | 3677.4851
2033-01-19 17:00 | 12661.2 | 3.9971 | 90.8303 | 74.6386 | 3710.6314
2033-01-20 18:00 | 11376.4 | 3.6052 | 90.8524 | 74.6386 | 3334.0937
2033-01-21 19:00 | 10538 | 3.3155 | 90.8641 | 74.6386 | 3088.3829
2033-01-22 20:00 | 8715.76 | 2.6276 | 91.1325 | 74.6386 | 2554.3371
2033-01-23 21:00 | 8007.65 | 2.4442 | 90.8718 | 74.6386 | 2346.8106
2033-01-24 22:00 | 6421.11 | 1.8702 | 91.092 | 74.6386 | 1881.8416
2033-01-25 23:00 | 6090.79 | 1.787 | 90.822 | 74.6386 | 1785.0343
2033-01-27 | 5590.59 | 1.7156 | 90.3156 | 74.6386 | 1638.4402
2033-01-28 01:00 | 5415.66 | 1.6446 | 90.2677 | 74.6386 | 1587.1733
2033-01-29 02:00 | 5119.04 | 1.6684 | 89.6376 | 74.6386 | 1500.2425
2033-01-30 03:00 | 5675.97 | 1.7594 | 89.9063 | 74.6386 | 1663.4626
2033-01-31 04:00 | 5912.81 | 1.9524 | 89.404 | 74.6386 | 1732.8736
2033-02-01 05:00 | 6759.89 | 2.3043 | 89.1502 | 74.6386 | 1981.1282
2033-02-02 06:00 | 7469.74 | 2.4335 | 89.4977 | 74.6386 | 2189.1647
2033-02-03 07:00 | 9111.03 | 2.9379 | 89.6211 | 74.6386 | 2670.1793
2033-02-04 08:00 | 9800.09 | 3.113 | 89.8807 | 74.6386 | 2872.1229
2033-02-05 09:00 | 10844.7 | 3.7004 | 89.4911 | 74.6386 | 3178.2678
2033-02-06 10:00 | 12539.3 | 4.1374 | 89.8757 | 74.6386 | 3674.9061
2033-02-07 11:00 | 13141.3 | 4.3181 | 90.1219 | 74.6386 | 3851.3349
2033-02-08 12:00 | 14038.5 | 4.6322 | 90.276 | 74.6386 | 4114.2782
2033-02-09 13:00 | 12729.7 | 3.8959 | 91.0235 | 74.6386 | 3730.7068
2033-02-10 14:00 | 11250.4 | 3.5643 | 90.7993 | 74.6386 | 3297.1668
2033-02-11 15:00 | 13133.1 | 4.2849 | 90.5099 | 74.6386 | 3848.9317
2033-02-12 16:00 | 13085 | 4.2269 | 90.6971 | 74.6386 | 3834.835
2033-02-13 17:00 | 12848.4 | 4.0925 | 90.8687 | 74.6386 | 3765.4943
2033-02-14 18:00 | 11646.1 | 3.6762 | 90.9452 | 74.6386 | 3413.135
2033-02-15 19:00 | 10811.9 | 3.4071 | 90.8966 | 74.6386 | 3168.6551
2033-02-16 20:00 | 8659.21 | 2.6802 | 90.9771 | 74.6386 | 2537.7639
2033-02-17 21:00 | 7769.85 | 2.4334 | 90.6916 | 74.6386 | 2277.1183
2033-02-18 22:00 | 6300.62 | 1.7952 | 91.2603 | 74.6386 | 1846.5294
2033-02-19 23:00 | 5457.91 | 1.6292 | 90.6638 | 74.6386 | 1599.5555
2033-02-21 | 4904.43 | 1.5131 | 90.2016 | 74.6386 | 1437.3465
2033-02-22 01:00 | 4457.18 | 1.3784 | 90.0108 | 74.6386 | 1306.2705
2033-02-23 02:00 | 4347.48 | 1.3819 | 89.6677 | 74.6386 | 1274.1206
2033-02-24 03:00 | 4437.74 | 1.4164 | 89.5158 | 74.6386 | 1300.5732
2033-02-25 04:00 | 4713.29 | 1.5301 | 89.3059 | 74.6386 | 1381.3289
2033-02-26 05:00 | 5642.37 | 1.8244 | 89.278 | 74.6386 | 1653.6154
2033-02-27 06:00 | 6426.21 | 2.0357 | 89.4408 | 74.6386 | 1883.3362
2033-02-28 07:00 | 7624.29 | 2.5487 | 89.0879 | 74.6386 | 2234.4588
2033-03-01 08:00 | 8433.63 | 2.5912 | 89.8095 | 74.6386 | 2471.653
2033-03-02 09:00 | 10064.5 | 3.2908 | 89.4493 | 74.6386 | 2949.6138
2033-03-03 10:00 | 11426.3 | 3.7479 | 89.6029 | 74.6386 | 3348.718
2033-03-04 11:00 | 12996.1 | 4.109 | 90.0745 | 74.6386 | 3808.7809
2033-03-05 12:00 | 11255.3 | 3.7664 | 89.8996 | 74.6386 | 3298.6028
2033-03-06 13:00 | 10291.4 | 3.3355 | 90.1524 | 74.6386 | 3016.1116
2033-03-07 14:00 | 10555.5 | 3.3076 | 90.3712 | 74.6386 | 3093.5117
2033-03-08 15:00 | 11503.5 | 3.6879 | 90.2235 | 74.6386 | 3371.3431
2033-03-09 16:00 | 11690.4 | 3.7504 | 90.3011 | 74.6386 | 3426.118
2033-03-10 17:00 | 11310.7 | 3.7508 | 90.0979 | 74.6386 | 3314.839
2033-03-11 18:00 | 10534.2 | 3.3171 | 90.487 | 74.6386 | 3087.2693
2033-03-12 19:00 | 9516.09 | 3.0015 | 90.4457 | 74.6386 | 2788.8907
2033-03-13 20:00 | 7673.94 | 2.357 | 90.577 | 74.6386 | 2249.0098
2033-03-14 21:00 | 7065.59 | 2.1478 | 90.4762 | 74.6386 | 2070.72
2033-03-15 22:00 | 5325.89 | 1.5385 | 90.7314 | 74.6386 | 1560.8643
2033-03-16 23:00 | 4679.36 | 1.4243 | 90.0857 | 74.6386 | 1371.385
2033-03-18 | 4201.22 | 1.2927 | 89.8161 | 74.6386 | 1231.256
2033-03-19 01:00 | 3971.94 | 1.2484 | 89.5062 | 74.6386 | 1164.0607
2033-03-20 02:00 | 4169.65 | 1.2987 | 89.4594 | 74.6386 | 1222.0038
2033-03-21 03:00 | 4683.61 | 1.4456 | 89.4445 | 74.6386 | 1372.6306
2033-03-22 04:00 | 4870.05 | 1.4709 | 89.5851 | 74.6386 | 1427.2708
2033-03-23 05:00 | 5557.89 | 1.9525 | 88.4592 | 74.6386 | 1628.8568
2033-03-24 06:00 | 6000.07 | 1.8861 | 89.266 | 74.6386 | 1758.4469
2033-03-25 07:00 | 6464.05 | 2.0744 | 89.1352 | 74.6386 | 1894.4261
2033-03-26 08:00 | 5366.25 | 1.6279 | 89.5993 | 74.6386 | 1572.6926
2033-03-27 09:00 | 5885.11 | 1.935 | 88.9152 | 74.6386 | 1724.7555
2033-03-28 10:00 | 6538.08 | 2.1241 | 88.9864 | 74.6386 | 1916.1221
2033-03-29 11:00 | 7796.19 | 2.6446 | 88.7039 | 74.6386 | 2284.8377
2033-03-30 12:00 | 8142.43 | 2.5875 | 89.267 | 74.6386 | 2386.3107
2033-03-31 13:00 | 7982.48 | 2.5332 | 89.345 | 74.6386 | 2339.434
2033-04-01 14:00 | 8814.97 | 2.8401 | 89.2666 | 74.6386 | 2583.4127
2033-04-02 15:00 | 10451.7 | 3.5456 | 88.9758 | 74.6386 | 3063.0909
2033-04-03 16:00 | 11157.4 | 3.6886 | 89.3273 | 74.6386 | 3269.9112
2033-04-04 17:00 | 11346.2 | 3.6872 | 89.5883 | 74.6386 | 3325.243
2033-04-05 18:00 | 10524.1 | 3.27 | 90.0201 | 74.6386 | 3084.3092
2033-04-06 19:00 | 9647.53 | 2.9921 | 90.0556 | 74.6386 | 2827.4119
2033-04-07 20:00 | 7780.56 | 2.3011 | 90.4131 | 74.6386 | 2280.257
2033-04-08 21:00 | 6709.49 | 2.0966 | 89.8537 | 74.6386 | 1966.3574
2033-04-09 22:00 | 4944.61 | 1.4424 | 90.2531 | 74.6386 | 1449.1221
2033-04-10 23:00 | 3718.85 | 1.1004 | 89.928 | 74.6386 | 1089.8873
2033-04-12 | 3220.59 | 1.0323 | 89.0984 | 74.6386 | 943.8618
2033-04-13 01:00 | 3135.93 | 1 | 89.5912 | 74.6386 | 919.0504
2033-04-14 02:00 | 3147.33 | 1 | 90.2085 | 74.6386 | 922.3914
2033-04-15 03:00 | 3155.38 | 1 | 90.3919 | 74.6386 | 924.7506
2033-04-16 04:00 | 3181.15 | 1 | 90.8768 | 74.6386 | 932.303
2033-04-17 05:00 | 3149.91 | 1 | 90.1831 | 74.6386 | 923.1475
2033-04-18 06:00 | 5629.22 | 1.6936 | 88.9623 | 74.6386 | 1649.7615
2033-04-19 07:00 | 7352.02 | 2.5119 | 88.1463 | 74.6386 | 2154.6644
2033-04-20 08:00 | 8057.6 | 2.6382 | 88.6365 | 74.6386 | 2361.4495
2033-04-21 09:00 | 9579.33 | 3.1433 | 88.7601 | 74.6386 | 2807.4245
2033-04-22 10:00 | 10915.5 | 3.6736 | 88.7843 | 74.6386 | 3199.0173
2033-04-23 11:00 | 11474.7 | 3.9021 | 88.9573 | 74.6386 | 3362.9026
2033-04-24 12:00 | 12625.3 | 4.1103 | 89.4564 | 74.6386 | 3700.1102
2033-04-25 13:00 | 13027 | 4.1777 | 89.7816 | 74.6386 | 3817.8368
2033-04-26 14:00 | 13474.6 | 4.5326 | 89.624 | 74.6386 | 3949.0154
2033-04-27 15:00 | 14614.3 | 4.722 | 90.0704 | 74.6386 | 4283.0285
2033-04-28 16:00 | 14767.9 | 4.8385 | 90.1709 | 74.6386 | 4328.0443
2033-04-29 17:00 | 12973.3 | 4.1981 | 90.4241 | 74.6386 | 3802.0989
2033-04-30 18:00 | 12262.7 | 3.7618 | 90.8006 | 74.6386 | 3593.8426
2033-05-01 19:00 | 10623.3 | 3.3556 | 90.5445 | 74.6386 | 3113.3819
2033-05-02 20:00 | 9996.35 | 3.0701 | 90.658 | 74.6386 | 2929.641
2033-05-03 21:00 | 9017.62 | 2.7827 | 90.5206 | 74.6386 | 2642.8035
2033-05-04 22:00 | 8276.65 | 2.5979 | 90.2681 | 74.6386 | 2425.6467
2033-05-05 23:00 | 5615.88 | 1.5951 | 90.9486 | 74.6386 | 1645.852
2033-05-07 | 4784.44 | 1.4238 | 90.3015 | 74.6386 | 1402.181
2033-05-08 01:00 | 4345.41 | 1.3379 | 89.8238 | 74.6386 | 1273.514
2033-05-09 02:00 | 4082.04 | 1.2659 | 89.6052 | 74.6386 | 1196.3278
2033-05-10 03:00 | 3933.19 | 1.2322 | 89.3776 | 74.6386 | 1152.7042
2033-05-11 04:00 | 3732.06 | 1.1541 | 89.3392 | 74.6386 | 1093.7588
2033-05-12 05:00 | 3744.31 | 1.1791 | 89.1019 | 74.6386 | 1097.3489
2033-05-13 06:00 | 6469.75 | 2.123 | 88.7138 | 74.6386 | 1896.0966
2033-05-14 07:00 | 8225.5 | 2.7994 | 88.5883 | 74.6386 | 2410.6561
2033-05-15 08:00 | 8712.46 | 2.8445 | 89.0685 | 74.6386 | 2553.37
2033-05-16 09:00 | 10467.9 | 3.3725 | 89.28 | 74.6386 | 3067.8387
2033-05-17 10:00 | 11443.6 | 3.7936 | 89.2729 | 74.6386 | 3353.7881
2033-05-18 11:00 | 12859 | 4.2669 | 89.4866 | 74.6386 | 3768.6009
2033-05-19 12:00 | 13422.5 | 4.3288 | 89.9212 | 74.6386 | 3933.7464
2033-05-20 13:00 | 13202.5 | 4.198 | 90.2141 | 74.6386 | 3869.2708
2033-05-21 14:00 | 9900.1 | 3.3108 | 89.9702 | 74.6386 | 2901.4329
2033-05-22 15:00 | 9386.4 | 2.9755 | 90.1958 | 74.6386 | 2750.8823
2033-05-23 16:00 | 11630.7 | 3.8547 | 89.7621 | 74.6386 | 3408.6217
2033-05-24 17:00 | 10725 | 3.3656 | 90.2932 | 74.6386 | 3143.1872
2033-05-25 18:00 | 9689.57 | 3.1001 | 90.1309 | 74.6386 | 2839.7326
2033-05-26 19:00 | 9125.14 | 2.7633 | 90.4381 | 74.6386 | 2674.3145
2033-05-27 20:00 | 8454.74 | 2.6782 | 90.0375 | 74.6386 | 2477.8397
2033-05-28 21:00 | 8057.93 | 2.4865 | 90.1674 | 74.6386 | 2361.5462
2033-05-29 22:00 | 7761.42 | 2.3639 | 90.1736 | 74.6386 | 2274.6477
2033-05-30 23:00 | 5579.68 | 1.5721 | 90.7265 | 74.6386 | 1635.2428
2033-06-01 | 4970.44 | 1.5016 | 89.9502 | 74.6386 | 1456.6922
2033-06-02 01:00 | 4514.34 | 1.4244 | 89.4466 | 74.6386 | 1323.0225
2033-06-03 02:00 | 4412.72 | 1.3686 | 89.4618 | 74.6386 | 1293.2406
2033-06-04 03:00 | 4578.23 | 1.4499 | 89.2159 | 74.6386 | 1341.7468
2033-06-05 04:00 | 4866.2 | 1.5759 | 88.9777 | 74.6386 | 1426.1424
2033-06-06 05:00 | 5842.05 | 1.8737 | 89.026 | 74.6386 | 1712.1358
2033-06-07 06:00 | 6732.28 | 2.2292 | 88.8334 | 74.6386 | 1973.0365
2033-06-08 07:00 | 8651.46 | 2.733 | 89.2462 | 74.6386 | 2535.4926
2033-06-09 08:00 | 9073.55 | 3.0122 | 89.0536 | 74.6386 | 2659.195
2033-06-10 09:00 | 11364.3 | 3.6315 | 89.4451 | 74.6386 | 3330.5476
2033-06-11 10:00 | 12516.4 | 4.1441 | 89.4166 | 74.6386 | 3668.1947
2033-06-12 11:00 | 13825.9 | 4.5474 | 89.6951 | 74.6386 | 4051.9713
2033-06-13 12:00 | 14684.9 | 4.8148 | 89.9575 | 74.6386 | 4303.7194
2033-06-14 13:00 | 14838.4 | 4.7962 | 90.2817 | 74.6386 | 4348.7058
2033-06-15 14:00 | 15444.7 | 5.021 | 90.4241 | 74.6386 | 4526.3948
2033-06-16 15:00 | 14198.5 | 4.4837 | 90.817 | 74.6386 | 4161.1696
2033-06-17 16:00 | 13131.5 | 4.2881 | 90.6069 | 74.6386 | 3848.4628
2033-06-18 17:00 | 12452.7 | 4.0047 | 90.6854 | 74.6386 | 3649.5261
2033-06-19 18:00 | 11176.4 | 3.5593 | 90.7203 | 74.6386 | 3275.4795
2033-06-20 19:00 | 10002.5 | 3.1717 | 90.6528 | 74.6386 | 2931.4434
2033-06-21 20:00 | 8404.52 | 2.4857 | 91.0504 | 74.6386 | 2463.1217
2033-06-22 21:00 | 7700.28 | 2.3234 | 90.6966 | 74.6386 | 2256.7293
2033-06-23 22:00 | 5829.86 | 1.676 | 90.92 | 74.6386 | 1708.5633
2033-06-24 23:00 | 5106.82 | 1.5905 | 90.0459 | 74.6386 | 1496.6612
2033-06-26 | 4583.39 | 1.4163 | 89.8978 | 74.6386 | 1343.259
2033-06-27 01:00 | 4431.96 | 1.3546 | 89.8081 | 74.6386 | 1298.8793
2033-06-28 02:00 | 4188.91 | 1.3525 | 89.2577 | 74.6386 | 1227.6483
2033-06-29 03:00 | 4924.78 | 1.4977 | 89.584 | 74.6386 | 1443.3105
2033-06-30 04:00 | 4948.84 | 1.6065 | 89.0637 | 74.6386 | 1450.3618
2033-07-01 05:00 | 6220.05 | 2.0046 | 89.0798 | 74.6386 | 1822.9167
2033-07-02 06:00 | 7399.45 | 2.3197 | 89.3366 | 74.6386 | 2168.5647
2033-07-03 07:00 | 8550.23 | 2.7734 | 89.1832 | 74.6386 | 2505.8251
2033-07-04 08:00 | 9616.24 | 2.9778 | 89.6667 | 74.6386 | 2818.2417
2033-07-05 09:00 | 10647.5 | 3.5558 | 89.2543 | 74.6386 | 3120.4742
2033-07-06 10:00 | 12019.4 | 4.0969 | 89.282 | 74.6386 | 3522.5384
2033-07-07 11:00 | 13984.6 | 4.5852 | 89.7583 | 74.6386 | 4098.4817
2033-07-08 12:00 | 14648.9 | 4.8208 | 90.0044 | 74.6386 | 4293.1688
2033-07-09 13:00 | 15338.1 | 4.9925 | 90.3057 | 74.6386 | 4495.1534
2033-07-10 14:00 | 16067.8 | 5.2935 | 90.4246 | 74.6386 | 4709.0073
2033-07-11 15:00 | 17254.7 | 5.4526 | 90.9421 | 74.6386 | 5056.8534
2033-07-12 16:00 | 14817.4 | 5.0332 | 90.6697 | 74.6386 | 4342.5513
2033-07-13 17:00 | 14931 | 4.8252 | 91.0081 | 74.6386 | 4375.8441
2033-07-14 18:00 | 13498 | 4.1353 | 91.4459 | 74.6386 | 3955.8733
2033-07-15 19:00 | 12000.4 | 3.8149 | 91.1271 | 74.6386 | 3516.9701
2033-07-16 20:00 | 10097.8 | 3.0236 | 91.4695 | 74.6386 | 2959.3731
2033-07-17 21:00 | 8686.06 | 2.7746 | 90.7713 | 74.6386 | 2545.6329
2033-07-18 22:00 | 7520.76 | 2.1607 | 91.4082 | 74.6386 | 2204.1172
2033-07-19 23:00 | 6371.97 | 1.9713 | 90.6152 | 74.6386 | 1867.4401
2033-07-21 | 5901.2 | 1.7557 | 90.7085 | 74.6386 | 1729.471
2033-07-22 01:00 | 6152.95 | 1.7788 | 90.7664 | 74.6386 | 1803.2516
2033-07-23 02:00 | 6086.55 | 1.8621 | 90.2192 | 74.6386 | 1783.7917
2033-07-24 03:00 | 6252.2 | 2.0011 | 89.7859 | 74.6386 | 1832.3389
2033-07-25 04:00 | 6594.65 | 2.1104 | 89.7333 | 74.6386 | 1932.7011
2033-07-26 05:00 | 7336.21 | 2.4501 | 89.4008 | 74.6386 | 2150.0309
2033-07-27 06:00 | 8174.22 | 2.6579 | 89.6184 | 74.6386 | 2395.6274
2033-07-28 07:00 | 9488.45 | 3.0553 | 89.7463 | 74.6386 | 2780.7902
2033-07-29 08:00 | 9903.48 | 3.2125 | 89.8171 | 74.6386 | 2902.4235
2033-07-30 09:00 | 11229 | 3.8117 | 89.5897 | 74.6386 | 3290.895
2033-07-31 10:00 | 12451.4 | 4.2799 | 89.6569 | 74.6386 | 3649.1451
2033-08-01 11:00 | 14018.5 | 4.7817 | 89.8947 | 74.6386 | 4108.4168
2033-08-02 12:00 | 15592 | 5.0459 | 90.4968 | 74.6386 | 4569.5641
2033-08-03 13:00 | 15627.4 | 5.0651 | 90.7399 | 74.6386 | 4579.9388
2033-08-04 14:00 | 16387.7 | 5.2891 | 90.9394 | 74.6386 | 4802.7608
2033-08-05 15:00 | 17761 | 5.7416 | 91.1012 | 74.6386 | 5205.2353
2033-08-06 16:00 | 18732.4 | 5.7771 | 91.6982 | 74.6386 | 5489.9245
2033-08-07 17:00 | 18376.6 | 5.6735 | 91.9282 | 74.6386 | 5385.6498
2033-08-08 18:00 | 15684.7 | 4.9242 | 91.9397 | 74.6386 | 4596.7318
2033-08-09 19:00 | 13864.7 | 4.3363 | 91.8949 | 74.6386 | 4063.3425
2033-08-10 20:00 | 12126.5 | 3.5484 | 92.2927 | 74.6386 | 3553.9263
2033-08-11 21:00 | 10810.6 | 3.2852 | 91.8285 | 74.6386 | 3168.2741
2033-08-12 22:00 | 8528.19 | 2.5917 | 91.6428 | 74.6386 | 2499.3658
2033-08-13 23:00 | 7823.62 | 2.3811 | 91.3481 | 74.6386 | 2292.8767
2033-08-15 | 7037.43 | 2.1994 | 90.933 | 74.6386 | 2062.4671
2033-08-16 01:00 | 6363.1 | 2.0301 | 90.5956 | 74.6386 | 1864.8405
2033-08-17 02:00 | 6316.72 | 1.9904 | 90.5108 | 74.6386 | 1851.2479
2033-08-18 03:00 | 6735.75 | 2.0707 | 90.5587 | 74.6386 | 1974.0535
2033-08-19 04:00 | 6937.01 | 2.1954 | 90.267 | 74.6386 | 2033.0369
2033-08-20 05:00 | 7468.17 | 2.48 | 89.8541 | 74.6386 | 2188.7046
2033-08-21 06:00 | 8682.56 | 2.7679 | 90.1343 | 74.6386 | 2544.6071
2033-08-22 07:00 | 9968.09 | 3.2705 | 89.9899 | 74.6386 | 2921.3588
2033-08-23 08:00 | 10254.7 | 3.3462 | 90.1532 | 74.6386 | 3005.3559
2033-08-24 09:00 | 11809.5 | 4.0422 | 89.8914 | 74.6386 | 3461.0228
2033-08-25 10:00 | 13565.9 | 4.4389 | 90.3741 | 74.6386 | 3975.7728
2033-08-26 11:00 | 15083.4 | 5.0144 | 90.4914 | 74.6386 | 4420.5082
2033-08-27 12:00 | 15790.6 | 5.0737 | 90.9821 | 74.6386 | 4627.768
2033-08-28 13:00 | 17421.6 | 5.3067 | 91.5886 | 74.6386 | 5105.767
2033-08-29 14:00 | 16143 | 5.1441 | 91.5192 | 74.6386 | 4731.0463
2033-08-30 15:00 | 17724.8 | 5.7227 | 91.5038 | 74.6386 | 5194.6261
2033-08-31 16:00 | 18340.9 | 5.8188 | 91.8191 | 74.6386 | 5375.1872
2033-09-01 17:00 | 16909.5 | 5.4382 | 91.9056 | 74.6386 | 4955.6853
2033-09-02 18:00 | 14827 | 4.727 | 91.9954 | 74.6386 | 4345.3648
2033-09-03 19:00 | 13710.9 | 4.1666 | 92.2399 | 74.6386 | 4018.2681
2033-09-04 20:00 | 11028.1 | 3.389 | 92.0675 | 74.6386 | 3232.0171
2033-09-05 21:00 | 10319.2 | 3.0996 | 92.0076 | 74.6386 | 3024.259
2033-09-06 22:00 | 8568.87 | 2.4797 | 92.1125 | 74.6386 | 2511.2879
2033-09-07 23:00 | 7549.19 | 2.3382 | 91.3377 | 74.6386 | 2212.4492
2033-09-09 | 6820.87 | 2.1565 | 90.9625 | 74.6386 | 1998.9997
2033-09-10 01:00 | 6588.05 | 2.0024 | 91.0584 | 74.6386 | 1930.7669
2033-09-11 02:00 | 6474.88 | 2.0242 | 90.7052 | 74.6386 | 1897.6
2033-09-12 03:00 | 6495.4 | 2.0807 | 90.396 | 74.6386 | 1903.6138
2033-09-13 04:00 | 6761.13 | 2.1521 | 90.3419 | 74.6386 | 1981.4916
2033-09-14 05:00 | 7438.46 | 2.4629 | 89.9931 | 74.6386 | 2179.9974
2033-09-15 06:00 | 8626.35 | 2.7695 | 90.2133 | 74.6386 | 2528.1336
2033-09-16 07:00 | 10250.6 | 3.2942 | 90.2674 | 74.6386 | 3004.1543
2033-09-17 08:00 | 10701.9 | 3.5157 | 90.2584 | 74.6386 | 3136.4173
2033-09-18 09:00 | 12099.4 | 4.0225 | 90.2785 | 74.6386 | 3545.9841
2033-09-19 10:00 | 13190.7 | 4.2777 | 90.6221 | 74.6386 | 3865.8126
2033-09-20 11:00 | 12706.2 | 4.1488 | 90.756 | 74.6386 | 3723.8196
2033-09-21 12:00 | 13869.5 | 4.4406 | 90.9695 | 74.6386 | 4064.7492
2033-09-22 13:00 | 14256.1 | 4.5848 | 91.0652 | 74.6386 | 4178.0505
2033-09-23 14:00 | 15440 | 4.8661 | 91.3432 | 74.6386 | 4525.0173
2033-09-24 15:00 | 16324.3 | 5.387 | 91.1648 | 74.6386 | 4784.1801
2033-09-25 16:00 | 15874.7 | 5.192 | 91.3925 | 74.6386 | 4652.4153
2033-09-26 17:00 | 16298.4 | 5.1616 | 91.7147 | 74.6386 | 4776.5895
2033-09-27 18:00 | 14373.7 | 4.4798 | 91.9414 | 74.6386 | 4212.5156
2033-09-28 19:00 | 12638.8 | 3.9939 | 91.7858 | 74.6386 | 3704.0666
2033-09-29 20:00 | 10309.2 | 3.1781 | 91.839 | 74.6386 | 3021.3283
2033-09-30 21:00 | 9191.97 | 2.8103 | 91.6678 | 74.6386 | 2693.9005
2033-10-01 22:00 | 7225.92 | 2.1674 | 91.6143 | 74.6386 | 2117.7081
2033-10-02 23:00 | 5970.48 | 1.798 | 91.3142 | 74.6386 | 1749.775
2033-10-04 | 5461.15 | 1.6306 | 91.1226 | 74.6386 | 1600.5051
2033-10-05 01:00 | 4933.11 | 1.5614 | 90.4746 | 74.6386 | 1445.7518
2033-10-06 02:00 | 4711.87 | 1.4301 | 90.6181 | 74.6386 | 1380.9128
2033-10-07 03:00 | 4551.65 | 1.3818 | 90.4553 | 74.6386 | 1333.9569
2033-10-08 04:00 | 4410.8 | 1.3636 | 90.1861 | 74.6386 | 1292.6779
2033-10-09 05:00 | 4235.76 | 1.352 | 89.8239 | 74.6386 | 1241.3787
2033-10-10 06:00 | 6742.24 | 2.3047 | 89.2168 | 74.6386 | 1975.9555
2033-10-11 07:00 | 8782.66 | 2.9831 | 89.3524 | 74.6386 | 2573.9436
2033-10-12 08:00 | 9112.31 | 3.0043 | 89.7483 | 74.6386 | 2670.5544
2033-10-13 09:00 | 10495.9 | 3.5636 | 89.6395 | 74.6386 | 3076.0446
2033-10-14 10:00 | 12233.8 | 4.0698 | 89.9438 | 74.6386 | 3585.3729
2033-10-15 11:00 | 13165.4 | 4.435 | 90.1048 | 74.6386 | 3858.3979
2033-10-16 12:00 | 14345.7 | 4.761 | 90.4154 | 74.6386 | 4204.3096
2033-10-17 13:00 | 15174.5 | 4.8442 | 90.9024 | 74.6386 | 4447.207
2033-10-18 14:00 | 15052.1 | 4.9151 | 90.9445 | 74.6386 | 4411.3351
2033-10-19 15:00 | 15674.5 | 4.8167 | 91.5236 | 74.6386 | 4593.7425
2033-10-20 16:00 | 17656.3 | 5.6168 | 91.4033 | 74.6386 | 5174.5507
2033-10-21 17:00 | 15997.2 | 5.0842 | 91.6773 | 74.6386 | 4688.3165
2033-10-22 18:00 | 14500.4 | 4.5847 | 91.7628 | 74.6386 | 4249.6477
2033-10-23 19:00 | 12488.4 | 3.9384 | 91.7157 | 74.6386 | 3659.9888
2033-10-24 20:00 | 11800.2 | 3.6059 | 91.8291 | 74.6386 | 3458.2972
2033-10-25 21:00 | 10471.4 | 3.2886 | 91.5235 | 74.6386 | 3068.8644
2033-10-26 22:00 | 9821.99 | 3.0505 | 91.4453 | 74.6386 | 2878.5411
2033-10-27 23:00 | 7125.77 | 2.0514 | 91.9111 | 74.6386 | 2088.357
2033-10-29 | 6293.32 | 1.8947 | 91.2728 | 74.6386 | 1844.39
2033-10-30 01:00 | 5776.68 | 1.7166 | 91.1547 | 74.6386 | 1692.9778
2033-10-31 02:00 | 5537.52 | 1.6765 | 90.8344 | 74.6386 | 1622.8869
2033-11-01 03:00 | 5038.08 | 1.6012 | 90.3188 | 74.6386 | 1476.5155
2033-11-02 04:00 | 4930.81 | 1.4925 | 90.5197 | 74.6386 | 1445.0778
2033-11-03 05:00 | 4731.23 | 1.5406 | 89.8535 | 74.6386 | 1386.5866
2033-11-04 06:00 | 7137.01 | 2.3709 | 89.6002 | 74.6386 | 2091.6512
2033-11-05 07:00 | 8874.15 | 3.1289 | 89.2778 | 74.6386 | 2600.7566
2033-11-06 08:00 | 9527.74 | 3.2125 | 89.7387 | 74.6386 | 2792.305
2033-11-07 09:00 | 10772.9 | 3.6656 | 89.7837 | 74.6386 | 3157.2253
2033-11-08 10:00 | 12423.8 | 4.0943 | 90.1549 | 74.6386 | 3641.0564
2033-11-09 11:00 | 13763.5 | 4.4986 | 90.4486 | 74.6386 | 4033.6837
2033-11-10 12:00 | 15055.3 | 4.8673 | 90.7563 | 74.6386 | 4412.2729
2033-11-11 13:00 | 14658.4 | 4.7817 | 90.9215 | 74.6386 | 4295.953
2033-11-12 14:00 | 15384.3 | 4.9116 | 91.2038 | 74.6386 | 4508.6933
2033-11-13 15:00 | 15998.7 | 4.9913 | 91.5259 | 74.6386 | 4688.7561
2033-11-14 16:00 | 17855.2 | 5.6844 | 91.5276 | 74.6386 | 5232.8426
2033-11-15 17:00 | 16582 | 5.2034 | 91.8884 | 74.6386 | 4859.7045
2033-11-16 18:00 | 15065.6 | 4.6792 | 92.0312 | 74.6386 | 4415.2915
2033-11-17 19:00 | 13002.3 | 4.1079 | 91.8631 | 74.6386 | 3810.598
2033-11-18 20:00 | 11915.4 | 3.7107 | 91.8424 | 74.6386 | 3492.059
2033-11-19 21:00 | 11110.2 | 3.4189 | 91.8074 | 74.6386 | 3256.0782
2033-11-20 22:00 | 10117.5 | 3.1816 | 91.5036 | 74.6386 | 2965.1466
2033-11-21 23:00 | 7748.58 | 2.2575 | 91.9519 | 74.6386 | 2270.8846
2033-11-23 | 7233.45 | 2.1318 | 91.5922 | 74.6386 | 2119.9149
2033-11-24 01:00 | 6417.27 | 2.0213 | 90.8972 | 74.6386 | 1880.7162
2033-11-25 02:00 | 6327.4 | 1.9813 | 90.7722 | 74.6386 | 1854.3779
2033-11-26 03:00 | 6127 | 2.0227 | 90.2508 | 74.6386 | 1795.6464
2033-11-27 04:00 | 6474.41 | 2.0512 | 90.423 | 74.6386 | 1897.4623
2033-11-28 05:00 | 7059.13 | 2.362 | 89.9703 | 74.6386 | 2068.8268
2033-11-29 06:00 | 7820.53 | 2.5561 | 90.1213 | 74.6386 | 2291.9711
2033-11-30 07:00 | 9153.67 | 3.0804 | 89.9414 | 74.6386 | 2682.6759
2033-12-01 08:00 | 10244.1 | 3.2093 | 90.5614 | 74.6386 | 3002.2493
2033-12-02 09:00 | 11607.5 | 3.7927 | 90.3743 | 74.6386 | 3401.8224
2033-12-03 10:00 | 13616.9 | 4.4784 | 90.4869 | 74.6386 | 3990.7195
2033-12-04 11:00 | 14788.7 | 4.8399 | 90.7705 | 74.6386 | 4334.1401
2033-12-05 12:00 | 16251 | 5.2442 | 91.107 | 74.6386 | 4762.698
2033-12-06 13:00 | 15970.5 | 5.1246 | 91.4059 | 74.6386 | 4680.4915
2033-12-07 14:00 | 17266 | 5.4261 | 91.7147 | 74.6386 | 5060.1651
2033-12-08 15:00 | 18719.4 | 5.8621 | 91.9542 | 74.6386 | 5486.1146
2033-12-09 16:00 | 16673.1 | 5.3221 | 92.0618 | 74.6386 | 4886.4033
2033-12-10 17:00 | 15332 | 4.905 | 92.0595 | 74.6386 | 4493.3656
2033-12-11 18:00 | 12654 | 4.1568 | 91.8028 | 74.6386 | 3708.5213
2033-12-12 19:00 | 12550.5 | 3.746 | 92.346 | 74.6386 | 3678.1885
2033-12-13 20:00 | 9781.05 | 3.0165 | 91.9974 | 74.6386 | 2866.5428
2033-12-14 21:00 | 9016.19 | 2.7941 | 91.6897 | 74.6386 | 2642.3845
2033-12-15 22:00 | 7097.79 | 2.1308 | 91.7156 | 74.6386 | 2080.1569
2033-12-16 23:00 | 6375.25 | 1.9413 | 91.3387 | 74.6386 | 1868.4013
2033-12-18 | 5984.22 | 1.8351 | 91.0679 | 74.6386 | 1753.8018
2033-12-19 01:00 | 5902.35 | 1.789 | 90.9783 | 74.6386 | 1729.808
2033-12-20 02:00 | 5660.97 | 1.7716 | 90.6004 | 74.6386 | 1659.0665
2033-12-21 03:00 | 5860.75 | 1.8704 | 90.3152 | 74.6386 | 1717.6163
2033-12-22 04:00 | 6311.64 | 2.014 | 90.2378 | 74.6386 | 1849.7591
2033-12-23 05:00 | 7158.78 | 2.3454 | 90.0135 | 74.6386 | 2098.0313
2033-12-24 06:00 | 7982.02 | 2.502 | 90.3687 | 74.6386 | 2339.2991
2033-12-25 07:00 | 9082.65 | 2.9721 | 90.099 | 74.6386 | 2661.862
2033-12-26 08:00 | 9788.79 | 3.2056 | 90.1991 | 74.6386 | 2868.8112
2033-12-27 09:00 | 11872.2 | 3.9048 | 90.2692 | 74.6386 | 3479.3984
2033-12-28 10:00 | 13091.2 | 4.3712 | 90.3738 | 74.6386 | 3836.652
2033-12-29 11:00 | 14332.5 | 4.7875 | 90.5844 | 74.6386 | 4200.4411
2033-12-30 12:00 | 15268.2 | 4.9926 | 90.95 | 74.6386 | 4474.6677
2033-12-31 13:00 | 15791.1 | 5.109 | 91.2365 | 74.6386 | 4627.9146
2034-01-01 14:00 | 15727.2 | 4.9587 | 91.6095 | 74.6386 | 4609.1873
2034-01-02 15:00 | 16762.6 | 5.3504 | 91.6265 | 74.6386 | 4912.6331
2034-01-03 16:00 | 13927.2 | 4.4258 | 91.8259 | 74.6386 | 4081.6594
2034-01-04 17:00 | 13385.4 | 4.2487 | 91.7384 | 74.6386 | 3922.8735
2034-01-05 18:00 | 11522.5 | 3.5975 | 91.7918 | 74.6386 | 3376.9114
2034-01-06 19:00 | 10467.3 | 3.2605 | 91.6607 | 74.6386 | 3067.6628
2034-01-07 20:00 | 8737.19 | 2.5896 | 91.898 | 74.6386 | 2560.6176
2034-01-08 21:00 | 7989.32 | 2.3992 | 91.5602 | 74.6386 | 2341.4386
2034-01-09 22:00 | 5873.11 | 1.7855 | 91.2879 | 74.6386 | 1721.2386
2034-01-10 23:00 | 5321.41 | 1.5878 | 91.1607 | 74.6386 | 1559.5513
2034-01-12 | 4794.38 | 1.4614 | 90.7789 | 74.6386 | 1405.0941
2034-01-13 01:00 | 4645.26 | 1.4556 | 90.3832 | 74.6386 | 1361.3913
2034-01-14 02:00 | 4478.81 | 1.4131 | 90.1869 | 74.6386 | 1312.6096
2034-01-15 03:00 | 4850.55 | 1.5188 | 90.1032 | 74.6386 | 1421.5559
2034-01-16 04:00 | 5144.45 | 1.6401 | 89.9069 | 74.6386 | 1507.6895
2034-01-17 05:00 | 6078.3 | 2.032 | 89.5221 | 74.6386 | 1781.3739
2034-01-18 06:00 | 7030.96 | 2.3205 | 89.6382 | 74.6386 | 2060.571
2034-01-19 07:00 | 8483.36 | 2.7624 | 89.7974 | 74.6386 | 2486.2274
2034-01-20 08:00 | 9226.06 | 2.945 | 90.0762 | 74.6386 | 2703.8913
2034-01-21 09:00 | 10950.9 | 3.6123 | 89.9512 | 74.6386 | 3209.392
2034-01-22 10:00 | 12814.7 | 4.2509 | 90.1056 | 74.6386 | 3755.6178
2034-01-23 11:00 | 13913 | 4.6357 | 90.3257 | 74.6386 | 4077.4978
2034-01-24 12:00 | 14597.9 | 4.8353 | 90.596 | 74.6386 | 4278.2222
2034-01-25 13:00 | 15173.6 | 4.9927 | 90.8342 | 74.6386 | 4446.9432
2034-01-26 14:00 | 16193.2 | 5.2392 | 91.1369 | 74.6386 | 4745.7585
2034-01-27 15:00 | 15922.4 | 5.0929 | 91.4174 | 74.6386 | 4666.3948
2034-01-28 16:00 | 14410.9 | 4.5386 | 91.6515 | 74.6386 | 4223.4179
2034-01-29 17:00 | 13508.4 | 4.2016 | 91.7243 | 74.6386 | 3958.9212
2034-01-30 18:00 | 11410.5 | 3.6823 | 91.4104 | 74.6386 | 3344.0874
2034-01-31 19:00 | 10505.1 | 3.2912 | 91.4791 | 74.6386 | 3078.7409
2034-02-01 20:00 | 8659.55 | 2.6034 | 91.6538 | 74.6386 | 2537.8636
2034-02-02 21:00 | 8173.07 | 2.4501 | 91.4595 | 74.6386 | 2395.2904
2034-02-03 22:00 | 6508.3 | 1.8639 | 91.669 | 74.6386 | 1907.3944
2034-02-04 23:00 | 5735.85 | 1.7355 | 91.0027 | 74.6386 | 1681.0117
2034-02-06 | 5342.33 | 1.6963 | 90.4395 | 74.6386 | 1565.6824
2034-02-07 01:00 | 5065.52 | 1.5767 | 90.4285 | 74.6386 | 1484.5574
2034-02-08 02:00 | 5205.1 | 1.5787 | 90.4905 | 74.6386 | 1525.4642
2034-02-09 03:00 | 5418.85 | 1.7306 | 89.9948 | 74.6386 | 1588.1082
2034-02-10 04:00 | 5585.06 | 1.8 | 89.8707 | 74.6386 | 1636.8195
2034-02-11 05:00 | 6423.29 | 2.1037 | 89.7103 | 74.6386 | 1882.4805
2034-02-12 06:00 | 6933.98 | 2.2588 | 89.7714 | 74.6386 | 2032.1489
2034-02-13 07:00 | 8297.16 | 2.7077 | 89.79 | 74.6386 | 2431.6576
2034-02-14 08:00 | 8762.79 | 2.8213 | 89.9976 | 74.6386 | 2568.1202
2034-02-15 09:00 | 10781.6 | 3.4732 | 90.0741 | 74.6386 | 3159.775
2034-02-16 10:00 | 11792.7 | 4.1762 | 89.6032 | 74.6386 | 3456.0992
2034-02-17 11:00 | 14527.4 | 4.7809 | 90.294 | 74.6386 | 4257.5607
2034-02-18 12:00 | 15134.7 | 4.9007 | 90.7221 | 74.6386 | 4435.5427
2034-02-19 13:00 | 14312.9 | 4.6137 | 90.9894 | 74.6386 | 4194.6969
2034-02-20 14:00 | 13319.4 | 4.3741 | 90.9439 | 74.6386 | 3903.5308
2034-02-21 15:00 | 14306.6 | 4.5695 | 91.1456 | 74.6386 | 4192.8506
2034-02-22 16:00 | 14788.3 | 4.5599 | 91.5247 | 74.6386 | 4334.0229
2034-02-23 17:00 | 14355.5 | 4.4411 | 91.6034 | 74.6386 | 4207.1817
2034-02-24 18:00 | 12358.9 | 3.9618 | 91.3758 | 74.6386 | 3622.036
2034-02-25 19:00 | 11151.4 | 3.5174 | 91.3971 | 74.6386 | 3268.1527
2034-02-26 20:00 | 9408.6 | 2.8211 | 91.6871 | 74.6386 | 2757.3885
2034-02-27 21:00 | 8453.01 | 2.5946 | 91.3276 | 74.6386 | 2477.3327
2034-02-28 22:00 | 6642.56 | 1.9324 | 91.5795 | 74.6386 | 1946.7422
2034-03-01 23:00 | 5993.28 | 1.7863 | 91.1312 | 74.6386 | 1756.457
2034-03-03 | 5630.05 | 1.6632 | 90.9992 | 74.6386 | 1650.0048
2034-03-04 01:00 | 5156.03 | 1.6066 | 90.4313 | 74.6386 | 1511.0832
2034-03-05 02:00 | 4963.11 | 1.5791 | 90.139 | 74.6386 | 1454.544
2034-03-06 03:00 | 5042.84 | 1.6162 | 89.9602 | 74.6386 | 1477.9105
2034-03-07 04:00 | 5297.43 | 1.6937 | 89.8925 | 74.6386 | 1552.5235
2034-03-08 05:00 | 6065.82 | 2.0131 | 89.5626 | 74.6386 | 1777.7164
2034-03-09 06:00 | 6500.71 | 2.1301 | 89.657 | 74.6386 | 1905.17
2034-03-10 07:00 | 7720.33 | 2.5335 | 89.6574 | 74.6386 | 2262.6054
2034-03-11 08:00 | 8231.69 | 2.5912 | 90.0486 | 74.6386 | 2412.4702
2034-03-12 09:00 | 10274.6 | 3.4659 | 89.6168 | 74.6386 | 3011.188
2034-03-13 10:00 | 11290.7 | 3.8747 | 89.6836 | 74.6386 | 3308.9775
2034-03-14 11:00 | 13348.5 | 4.4096 | 90.1217 | 74.6386 | 3912.0592
2034-03-15 12:00 | 14158.1 | 4.6404 | 90.426 | 74.6386 | 4149.3295
2034-03-16 13:00 | 14925.7 | 4.9024 | 90.625 | 74.6386 | 4374.2909
2034-03-17 14:00 | 15853 | 5.149 | 90.9101 | 74.6386 | 4646.0557
2034-03-18 15:00 | 16352.1 | 5.0286 | 91.522 | 74.6386 | 4792.3274
2034-03-19 16:00 | 15048.6 | 4.7704 | 91.4778 | 74.6386 | 4410.3093
2034-03-20 17:00 | 14337.4 | 4.4998 | 91.5795 | 74.6386 | 4201.8772
2034-03-21 18:00 | 12549.4 | 3.9262 | 91.6082 | 74.6386 | 3677.8661
2034-03-22 19:00 | 11550 | 3.5126 | 91.73 | 74.6386 | 3384.9709
2034-03-23 20:00 | 9230.5 | 2.8292 | 91.5663 | 74.6386 | 2705.1925
2034-03-24 21:00 | 8308.59 | 2.5852 | 91.2231 | 74.6386 | 2435.0074
2034-03-25 22:00 | 6622.95 | 1.8893 | 91.7272 | 74.6386 | 1940.995
2034-03-26 23:00 | 5245.07 | 1.5777 | 91.0602 | 74.6386 | 1537.1783
2034-03-28 | 4794.06 | 1.4606 | 90.7078 | 74.6386 | 1405.0003
2034-03-29 01:00 | 4463.27 | 1.4065 | 90.2486 | 74.6386 | 1308.0553
2034-03-30 02:00 | 4300.34 | 1.3485 | 90.124 | 74.6386 | 1260.3052
2034-03-31 03:00 | 4077.33 | 1.272 | 90.0149 | 74.6386 | 1194.9475
2034-04-01 04:00 | 3906.63 | 1.2272 | 89.8379 | 74.6386 | 1144.9202
2034-04-02 05:00 | 3921.3 | 1.2253 | 89.7667 | 74.6386 | 1149.2196
2034-04-03 06:00 | 6025.65 | 2.0224 | 89.1571 | 74.6386 | 1765.9437
2034-04-04 07:00 | 7717.69 | 2.6276 | 89.1354 | 74.6386 | 2261.8317
2034-04-05 08:00 | 7983.48 | 2.5509 | 89.744 | 74.6386 | 2339.727
2034-04-06 09:00 | 9509.29 | 3.1338 | 89.5941 | 74.6386 | 2786.8978
2034-04-07 10:00 | 11143.5 | 3.6246 | 89.8459 | 74.6386 | 3265.8375
2034-04-08 11:00 | 12317 | 4.1145 | 89.8792 | 74.6386 | 3609.7564
2034-04-09 12:00 | 13233 | 4.4385 | 90.0557 | 74.6386 | 3878.2095
2034-04-10 13:00 | 13868.6 | 4.5556 | 90.3899 | 74.6386 | 4064.4854
2034-04-11 14:00 | 14481.8 | 4.7445 | 90.5873 | 74.6386 | 4244.1966
2034-04-12 15:00 | 14860.1 | 4.8522 | 90.7762 | 74.6386 | 4355.0654
2034-04-13 16:00 | 17146.9 | 5.6606 | 90.845 | 74.6386 | 5025.2603
2034-04-14 17:00 | 15998.4 | 4.9777 | 91.5688 | 74.6386 | 4688.6682
2034-04-15 18:00 | 14008.4 | 4.4102 | 91.5867 | 74.6386 | 4105.4568
2034-04-16 19:00 | 11915.6 | 3.6989 | 91.6302 | 74.6386 | 3492.1176
2034-04-17 20:00 | 10513.9 | 3.3091 | 91.3921 | 74.6386 | 3081.3199
2034-04-18 21:00 | 9890.76 | 3.0257 | 91.4633 | 74.6386 | 2898.6956
2034-04-19 22:00 | 9279.93 | 2.8565 | 91.2788 | 74.6386 | 2719.679
2034-04-20 23:00 | 6227.27 | 1.8372 | 91.4898 | 74.6386 | 1825.0327
2034-04-22 | 5829.5 | 1.6574 | 91.4902 | 74.6386 | 1708.4578
2034-04-23 01:00 | 5085.08 | 1.5578 | 90.6932 | 74.6386 | 1490.2898
2034-04-24 02:00 | 4662.19 | 1.4556 | 90.3797 | 74.6386 | 1366.353
2034-04-25 03:00 | 4444.16 | 1.3976 | 90.1603 | 74.6386 | 1302.4547
2034-04-26 04:00 | 4187.3 | 1.3319 | 89.9144 | 74.6386 | 1227.1765
2034-04-27 05:00 | 4208.62 | 1.323 | 89.8811 | 74.6386 | 1233.4248
2034-04-28 06:00 | 6627 | 2.1442 | 89.567 | 74.6386 | 1942.182
2034-04-29 07:00 | 8217.47 | 2.7839 | 89.3404 | 74.6386 | 2408.3027
2034-04-30 08:00 | 8431.04 | 2.7155 | 89.8603 | 74.6386 | 2470.8939
2034-05-01 09:00 | 10084.3 | 3.2233 | 89.9897 | 74.6386 | 2955.4166
2034-05-02 10:00 | 11279.3 | 3.758 | 89.8493 | 74.6386 | 3305.6365
2034-05-03 11:00 | 12586.9 | 4.1947 | 90.053 | 74.6386 | 3688.8563
2034-05-04 12:00 | 13485.6 | 4.2744 | 90.6195 | 74.6386 | 3952.2392
2034-05-05 13:00 | 13475.1 | 4.4533 | 90.5008 | 74.6386 | 3949.162
2034-05-06 14:00 | 14305.4 | 4.7733 | 90.5608 | 74.6386 | 4192.4989
2034-05-07 15:00 | 14953.5 | 4.8496 | 90.9176 | 74.6386 | 4382.4382
2034-05-08 16:00 | 17234.9 | 5.6637 | 90.9783 | 74.6386 | 5051.0506
2034-05-09 17:00 | 15954.4 | 5.1612 | 91.3765 | 74.6386 | 4675.7731
2034-05-10 18:00 | 15116 | 4.4035 | 92.2705 | 74.6386 | 4430.0623
2034-05-11 19:00 | 11384.5 | 3.7082 | 91.4347 | 74.6386 | 3336.4676
2034-05-12 20:00 | 10310.8 | 3.2725 | 91.413 | 74.6386 | 3021.7972
2034-05-13 21:00 | 9449.07 | 3.0061 | 91.22 | 74.6386 | 2769.2491
2034-05-14 22:00 | 9200.28 | 2.7893 | 91.4211 | 74.6386 | 2696.3359
2034-05-15 23:00 | 6803.72 | 1.9827 | 91.6216 | 74.6386 | 1993.9735
2034-05-17 | 6192.15 | 1.8361 | 91.217 | 74.6386 | 1814.74
2034-05-18 01:00 | 5769.22 | 1.7578 | 90.8236 | 74.6386 | 1690.7915
2034-05-19 02:00 | 5734.77 | 1.748 | 90.6836 | 74.6386 | 1680.6952
2034-05-20 03:00 | 6100.38 | 1.8946 | 90.4324 | 74.6386 | 1787.8449
2034-05-21 04:00 | 6300.63 | 2.026 | 90.092 | 74.6386 | 1846.5324
2034-05-22 05:00 | 7238.59 | 2.3477 | 89.9908 | 74.6386 | 2121.4213
2034-05-23 06:00 | 7815.27 | 2.5056 | 90.0952 | 74.6386 | 2290.4295
2034-05-24 07:00 | 8300.54 | 2.7363 | 89.9416 | 74.6386 | 2432.6481
2034-05-25 08:00 | 9358.38 | 2.8244 | 90.658 | 74.6386 | 2742.6704
2034-05-26 09:00 | 10411.9 | 3.3999 | 90.1637 | 74.6386 | 3051.4267
2034-05-27 10:00 | 10826.3 | 3.6497 | 90.0651 | 74.6386 | 3172.8753
2034-05-28 11:00 | 11589.2 | 4.028 | 89.9544 | 74.6386 | 3396.4592
2034-05-29 12:00 | 13595.2 | 4.3176 | 90.7118 | 74.6386 | 3984.3598
2034-05-30 13:00 | 12823.4 | 4.0371 | 91.0093 | 74.6386 | 3758.1676
2034-05-31 14:00 | 11679.3 | 3.8093 | 90.8286 | 74.6386 | 3422.8649
2034-06-01 15:00 | 12342.6 | 4.1133 | 90.6336 | 74.6386 | 3617.259
2034-06-02 16:00 | 12833 | 4.0965 | 90.9872 | 74.6386 | 3760.981
2034-06-03 17:00 | 12823.6 | 4.0575 | 91.1241 | 74.6386 | 3758.2262
2034-06-04 18:00 | 11713.8 | 3.6436 | 91.2748 | 74.6386 | 3432.9759
2034-06-05 19:00 | 10628 | 3.3203 | 91.1946 | 74.6386 | 3114.7593
2034-06-06 20:00 | 8869.65 | 2.6697 | 91.4033 | 74.6386 | 2599.4378
2034-06-07 21:00 | 8037.38 | 2.4638 | 91.0939 | 74.6386 | 2355.5236
2034-06-08 22:00 | 6224.54 | 1.8674 | 91.1039 | 74.6386 | 1824.2326
2034-06-09 23:00 | 5839.96 | 1.7233 | 91.008 | 74.6386 | 1711.5233
2034-06-11 | 5452.57 | 1.6832 | 90.4767 | 74.6386 | 1597.9905
2034-06-12 01:00 | 5384.66 | 1.6334 | 90.473 | 74.6386 | 1578.0881
2034-06-13 02:00 | 5280.05 | 1.6393 | 90.1999 | 74.6386 | 1547.4299
2034-06-14 03:00 | 5623.11 | 1.8185 | 89.8088 | 74.6386 | 1647.9709
2034-06-15 04:00 | 5747.94 | 1.9407 | 89.4637 | 74.6386 | 1684.5549
2034-06-16 05:00 | 6650.16 | 2.2306 | 89.4744 | 74.6386 | 1948.9695
2034-06-17 06:00 | 7034.85 | 2.3229 | 89.6134 | 74.6386 | 2061.711
2034-06-18 07:00 | 8391.47 | 2.6977 | 89.8344 | 74.6386 | 2459.2971
2034-06-19 08:00 | 8632.54 | 2.5141 | 90.7066 | 74.6386 | 2529.9477
2034-06-20 09:00 | 9968.39 | 3.2127 | 89.9929 | 74.6386 | 2921.4467
2034-06-21 10:00 | 11748.1 | 3.8436 | 90.0259 | 74.6386 | 3443.0282
2034-06-22 11:00 | 12603.1 | 4.0435 | 90.383 | 74.6386 | 3693.604
2034-06-23 12:00 | 11308.2 | 3.7984 | 90.2392 | 74.6386 | 3314.1063
2034-06-24 13:00 | 10336.2 | 3.3618 | 90.4826 | 74.6386 | 3029.2412
2034-06-25 14:00 | 9608.39 | 3.1194 | 90.4578 | 74.6386 | 2815.9411
2034-06-26 15:00 | 10863.3 | 3.5661 | 90.3159 | 74.6386 | 3183.719
2034-06-27 16:00 | 11111.9 | 3.6627 | 90.335 | 74.6386 | 3256.5764
2034-06-28 17:00 | 11415.8 | 3.599 | 90.6898 | 74.6386 | 3345.6407
2034-06-29 18:00 | 10569 | 3.2432 | 90.9368 | 74.6386 | 3097.4681
2034-06-30 19:00 | 9701.62 | 3.0025 | 90.8489 | 74.6386 | 2843.2642
2034-07-01 20:00 | 8168.22 | 2.4139 | 91.1607 | 74.6386 | 2393.869
2034-07-02 21:00 | 7483.64 | 2.2943 | 90.731 | 74.6386 | 2193.2384
2034-07-03 22:00 | 5845.29 | 1.6858 | 91.0828 | 74.6386 | 1713.0854
2034-07-04 23:00 | 5231.93 | 1.5832 | 90.4882 | 74.6386 | 1533.3273
2034-07-06 | 5009.49 | 1.5682 | 90.0582 | 74.6386 | 1468.1366
2034-07-07 01:00 | 4597.33 | 1.4881 | 89.6925 | 74.6386 | 1347.3444
2034-07-08 02:00 | 4575.84 | 1.4672 | 89.6565 | 74.6386 | 1341.0463
2034-07-09 03:00 | 4922.43 | 1.5849 | 89.535 | 74.6386 | 1442.6218
2034-07-10 04:00 | 5184.41 | 1.6595 | 89.5403 | 74.6386 | 1519.4006
2034-07-11 05:00 | 5903.45 | 1.9492 | 89.287 | 74.6386 | 1730.1304
2034-07-12 06:00 | 6728.92 | 2.1647 | 89.4917 | 74.6386 | 1972.0518
2034-07-13 07:00 | 8030.66 | 2.66 | 89.3338 | 74.6386 | 2353.5541
2034-07-14 08:00 | 9182.21 | 2.9168 | 89.7589 | 74.6386 | 2691.0401
2034-07-15 09:00 | 10609.1 | 3.6947 | 89.2466 | 74.6386 | 3109.2203
2034-07-16 10:00 | 12732.3 | 4.2818 | 89.6761 | 74.6386 | 3731.4688
2034-07-17 11:00 | 13749.4 | 4.5916 | 89.9961 | 74.6386 | 4029.5514
2034-07-18 12:00 | 13976.5 | 4.251 | 90.9338 | 74.6386 | 4096.1078
2034-07-19 13:00 | 13599.3 | 4.6688 | 90.2263 | 74.6386 | 3985.5614
2034-07-20 14:00 | 14930.7 | 4.7046 | 90.9559 | 74.6386 | 4375.7562
2034-07-21 15:00 | 16705.9 | 5.2875 | 91.117 | 74.6386 | 4896.016
2034-07-22 16:00 | 17155.5 | 5.379 | 91.4523 | 74.6386 | 5027.7807
2034-07-23 17:00 | 16710.3 | 5.3425 | 91.5078 | 74.6386 | 4897.3055
2034-07-24 18:00 | 13660.3 | 4.5298 | 91.362 | 74.6386 | 4003.4387
2034-07-25 19:00 | 12567.3 | 3.954 | 91.6424 | 74.6386 | 3683.1121
2034-07-26 20:00 | 11042 | 3.2659 | 92.0241 | 74.6386 | 3236.0908
2034-07-27 21:00 | 9791.4 | 2.99 | 91.6256 | 74.6386 | 2869.5761
2034-07-28 22:00 | 7416.63 | 2.2516 | 91.4897 | 74.6386 | 2173.5997
2034-07-29 23:00 | 6418.65 | 2.0384 | 90.8576 | 74.6386 | 1881.1206
2034-07-31 | 5963.48 | 1.8542 | 90.7898 | 74.6386 | 1747.7235
2034-08-01 01:00 | 5889.84 | 1.8083 | 90.7198 | 74.6386 | 1726.1417
2034-08-02 02:00 | 6027.76 | 1.8179 | 90.7311 | 74.6386 | 1766.5621
2034-08-03 03:00 | 6209.16 | 1.9264 | 90.4088 | 74.6386 | 1819.7252
2034-08-04 04:00 | 6373.04 | 2.0428 | 90.0989 | 74.6386 | 1867.7537
2034-08-05 05:00 | 7186.84 | 2.3307 | 89.9628 | 74.6386 | 2106.2549
2034-08-06 06:00 | 7322.04 | 2.3983 | 89.9122 | 74.6386 | 2145.8781
2034-08-07 07:00 | 8595.08 | 2.7963 | 89.9632 | 74.6386 | 2518.9693
2034-08-08 08:00 | 9316.16 | 2.9218 | 90.3166 | 74.6386 | 2730.297
2034-08-09 09:00 | 10482.1 | 3.4331 | 90.0873 | 74.6386 | 3072.0003
2034-08-10 10:00 | 11352.8 | 3.8657 | 89.9463 | 74.6386 | 3327.1772
2034-08-11 11:00 | 12797.3 | 4.2778 | 90.2142 | 74.6386 | 3750.5184
2034-08-12 12:00 | 13934.1 | 4.4352 | 90.7687 | 74.6386 | 4083.6816
2034-08-13 13:00 | 13623.8 | 4.3291 | 90.9918 | 74.6386 | 3992.7416
2034-08-14 14:00 | 13145.2 | 4.0313 | 91.3702 | 74.6386 | 3852.4778
2034-08-15 15:00 | 12480.6 | 4.1761 | 90.764 | 74.6386 | 3657.7028
2034-08-16 16:00 | 11995.1 | 3.8258 | 91.1044 | 74.6386 | 3515.4168
2034-08-17 17:00 | 11549.2 | 3.7924 | 90.8566 | 74.6386 | 3384.7364
2034-08-18 18:00 | 10827.8 | 3.3623 | 91.2274 | 74.6386 | 3173.3149
2034-08-19 19:00 | 10047.2 | 3.1132 | 91.1736 | 74.6386 | 2944.5437
2034-08-20 20:00 | 8091.38 | 2.4665 | 91.2126 | 74.6386 | 2371.3494
2034-08-21 21:00 | 7538.93 | 2.2802 | 91.0834 | 74.6386 | 2209.4423
2034-08-22 22:00 | 6017.34 | 1.7286 | 91.3537 | 74.6386 | 1763.5083
2034-08-23 23:00 | 5438.54 | 1.6858 | 90.55 | 74.6386 | 1593.8787
2034-08-25 | 5214.1 | 1.5954 | 90.4685 | 74.6386 | 1528.1019
2034-08-26 01:00 | 5069.1 | 1.5904 | 90.1392 | 74.6386 | 1485.6066
2034-08-27 02:00 | 5187.64 | 1.5874 | 90.2264 | 74.6386 | 1520.3472
2034-08-28 03:00 | 5341.75 | 1.7263 | 89.7393 | 74.6386 | 1565.5124
2034-08-29 04:00 | 5763.36 | 1.8239 | 89.8502 | 74.6386 | 1689.0741
2034-08-30 05:00 | 6418.44 | 2.1499 | 89.4231 | 74.6386 | 1881.0591
2034-08-31 06:00 | 6876.16 | 2.3144 | 89.4133 | 74.6386 | 2015.2036
2034-09-01 07:00 | 8228.82 | 2.7286 | 89.5476 | 74.6386 | 2411.6291
2034-09-02 08:00 | 8952.45 | 2.9002 | 89.826 | 74.6386 | 2623.7041
2034-09-03 09:00 | 10674.5 | 3.5786 | 89.6874 | 74.6386 | 3128.3871
2034-09-04 10:00 | 12749.3 | 4.1331 | 90.1145 | 74.6386 | 3736.451
2034-09-05 11:00 | 13505 | 4.4318 | 90.289 | 74.6386 | 3957.9248
2034-09-06 12:00 | 13991.9 | 4.3391 | 90.9196 | 74.6386 | 4100.6211
2034-09-07 13:00 | 14373.3 | 4.4666 | 91.075 | 74.6386 | 4212.3984
2034-09-08 14:00 | 13021.5 | 4.0302 | 91.2676 | 74.6386 | 3816.2249
2034-09-09 15:00 | 14033.7 | 4.7118 | 90.683 | 74.6386 | 4112.8715
2034-09-10 16:00 | 13894.8 | 4.4797 | 91.0707 | 74.6386 | 4072.1639
2034-09-11 17:00 | 13294.6 | 4.2958 | 91.1219 | 74.6386 | 3896.2626
2034-09-12 18:00 | 11752.9 | 3.7832 | 91.158 | 74.6386 | 3444.435
2034-09-13 19:00 | 11061 | 3.4137 | 91.3787 | 74.6386 | 3241.6591
2034-09-14 20:00 | 8891.61 | 2.8002 | 91.1623 | 74.6386 | 2605.8737
2034-09-15 21:00 | 8480.34 | 2.5464 | 91.3328 | 74.6386 | 2485.3423
2034-09-16 22:00 | 6641.28 | 2.0076 | 91.1353 | 74.6386 | 1946.367
2034-09-17 23:00 | 5648.65 | 1.67 | 91.0882 | 74.6386 | 1655.4559
2034-09-19 | 5021.09 | 1.5548 | 90.5123 | 74.6386 | 1471.5362
2034-09-20 01:00 | 4773.91 | 1.433 | 90.5652 | 74.6386 | 1399.0949
2034-09-21 02:00 | 4449.32 | 1.4221 | 89.9533 | 74.6386 | 1303.967
2034-09-22 03:00 | 4338.15 | 1.38 | 89.8489 | 74.6386 | 1271.3863
2034-09-23 04:00 | 4198.84 | 1.3319 | 89.759 | 74.6386 | 1230.5585
2034-09-24 05:00 | 4256.61 | 1.3126 | 89.8725 | 74.6386 | 1247.4892
2034-09-25 06:00 | 6225.25 | 2.1323 | 89.0331 | 74.6386 | 1824.4407
2034-09-26 07:00 | 8562.02 | 2.8022 | 89.4302 | 74.6386 | 2509.2804
2034-09-27 08:00 | 8868.74 | 2.9025 | 89.6335 | 74.6386 | 2599.1711
2034-09-28 09:00 | 10547.9 | 3.4668 | 89.7122 | 74.6386 | 3091.2843
2034-09-29 10:00 | 11507.6 | 4.018 | 89.4764 | 74.6386 | 3372.5446
2034-09-30 11:00 | 13298.9 | 4.4036 | 90.0443 | 74.6386 | 3897.5229
2034-10-01 12:00 | 14459.5 | 4.6742 | 90.4663 | 74.6386 | 4237.6611
2034-10-02 13:00 | 15068.2 | 4.8858 | 90.6775 | 74.6386 | 4416.0535
2034-10-03 14:00 | 15863.6 | 5.1285 | 90.9117 | 74.6386 | 4649.1622
2034-10-04 15:00 | 15953.1 | 5.0896 | 91.2166 | 74.6386 | 4675.3921
2034-10-05 16:00 | 15121.5 | 4.8418 | 91.3577 | 74.6386 | 4431.6742
2034-10-06 17:00 | 12974.5 | 4.2549 | 91.2506 | 74.6386 | 3802.4506
2034-10-07 18:00 | 12085.6 | 3.6405 | 91.7987 | 74.6386 | 3541.9397
2034-10-08 19:00 | 10258.9 | 3.2821 | 91.2476 | 74.6386 | 3006.5868
2034-10-09 20:00 | 9448.49 | 2.9474 | 91.2759 | 74.6386 | 2769.0791
2034-10-10 21:00 | 8938.98 | 2.7434 | 91.2434 | 74.6386 | 2619.7564
2034-10-11 22:00 | 8225.65 | 2.5667 | 90.9973 | 74.6386 | 2410.7
2034-10-12 23:00 | 5586.14 | 1.558 | 91.7765 | 74.6386 | 1637.136
2034-10-14 | 4834.6 | 1.4344 | 90.9852 | 74.6386 | 1416.8814
2034-10-15 01:00 | 4533.22 | 1.4243 | 90.3206 | 74.6386 | 1328.5556
2034-10-16 02:00 | 4273.05 | 1.35 | 90.1156 | 74.6386 | 1252.3073
2034-10-17 03:00 | 4021.34 | 1.2554 | 90.0511 | 74.6386 | 1178.5384
2034-10-18 04:00 | 4023.84 | 1.2379 | 90.0168 | 74.6386 | 1179.2711
2034-10-19 05:00 | 4072.47 | 1.282 | 89.7545 | 74.6386 | 1193.5231
2034-10-20 06:00 | 5874.54 | 2.0179 | 89.0539 | 74.6386 | 1721.6577
2034-10-21 07:00 | 7789.41 | 2.5624 | 89.4241 | 74.6386 | 2282.8507
2034-10-22 08:00 | 8159.86 | 2.6526 | 89.6682 | 74.6386 | 2391.4189
2034-10-23 09:00 | 9850.51 | 3.2898 | 89.5621 | 74.6386 | 2886.8995
2034-10-24 10:00 | 11474.2 | 3.9074 | 89.5892 | 74.6386 | 3362.7561
2034-10-25 11:00 | 13194.6 | 4.2984 | 90.138 | 74.6386 | 3866.9555
2034-10-26 12:00 | 13586.9 | 4.6075 | 90.1105 | 74.6386 | 3981.9273
2034-10-27 13:00 | 15341.9 | 4.8396 | 90.8108 | 74.6386 | 4496.267
2034-10-28 14:00 | 14512.4 | 4.4522 | 91.2832 | 74.6386 | 4253.1646
2034-10-29 15:00 | 13927.8 | 4.5009 | 91.0049 | 74.6386 | 4081.8352
2034-10-30 16:00 | 14092.6 | 4.5546 | 91.0453 | 74.6386 | 4130.1334
2034-10-31 17:00 | 12013.8 | 3.8708 | 91.1426 | 74.6386 | 3520.8972
2034-11-01 18:00 | 10766 | 3.3047 | 91.4221 | 74.6386 | 3155.2031
2034-11-02 19:00 | 9276.39 | 2.9969 | 90.8955 | 74.6386 | 2718.6415
2034-11-03 20:00 | 8586.3 | 2.7088 | 90.912 | 74.6386 | 2516.3961
2034-11-04 21:00 | 8197.92 | 2.5592 | 90.8498 | 74.6386 | 2402.5732
2034-11-05 22:00 | 7859.15 | 2.4649 | 90.6895 | 74.6386 | 2303.2895
2034-11-06 23:00 | 5960.37 | 1.7068 | 91.3104 | 74.6386 | 1746.812
2034-11-08 | 5529.23 | 1.6544 | 90.749 | 74.6386 | 1620.4574
2034-11-09 01:00 | 5304.14 | 1.6262 | 90.3965 | 74.6386 | 1554.49
2034-11-10 02:00 | 5580.57 | 1.6622 | 90.5082 | 74.6386 | 1635.5036
2034-11-11 03:00 | 5867.87 | 1.8398 | 90.042 | 74.6386 | 1719.7029
2034-11-12 04:00 | 6190.4 | 1.9718 | 89.8765 | 74.6386 | 1814.2272
2034-11-13 05:00 | 6772.33 | 2.3417 | 89.2903 | 74.6386 | 1984.774
2034-11-14 06:00 | 7345.06 | 2.3556 | 89.8549 | 74.6386 | 2152.6246
2034-11-15 07:00 | 8562.84 | 2.7937 | 89.7774 | 74.6386 | 2509.5207
2034-11-16 08:00 | 9260.11 | 3.017 | 89.8982 | 74.6386 | 2713.8703
2034-11-17 09:00 | 11214.2 | 3.7228 | 89.8657 | 74.6386 | 3286.5576
2034-11-18 10:00 | 12617 | 4.252 | 89.955 | 74.6386 | 3697.6777
2034-11-19 11:00 | 14154.6 | 4.6809 | 90.3102 | 74.6386 | 4148.3038
2034-11-20 12:00 | 15133.4 | 4.9257 | 90.672 | 74.6386 | 4435.1617
2034-11-21 13:00 | 15811.6 | 5.086 | 90.9843 | 74.6386 | 4633.9225
2034-11-22 14:00 | 16740.1 | 5.2734 | 91.3472 | 74.6386 | 4906.039
2034-11-23 15:00 | 16187.8 | 5.1742 | 91.4528 | 74.6386 | 4744.1759
2034-11-24 16:00 | 15266.7 | 4.9341 | 91.4817 | 74.6386 | 4474.2281
2034-11-25 17:00 | 14705.6 | 4.7242 | 91.5538 | 74.6386 | 4309.7859
2034-11-26 18:00 | 13478 | 4.1827 | 91.8284 | 74.6386 | 3950.0119
2034-11-27 19:00 | 12341.6 | 3.7858 | 91.8691 | 74.6386 | 3616.9659
2034-11-28 20:00 | 9804.87 | 3.0686 | 91.6215 | 74.6386 | 2873.5237
2034-11-29 21:00 | 8620.33 | 2.7495 | 91.2494 | 74.6386 | 2526.3693
2034-11-30 22:00 | 7174.38 | 2.0938 | 91.7256 | 74.6386 | 2102.6032
2034-12-01 23:00 | 6515.44 | 1.9358 | 91.3546 | 74.6386 | 1909.487
2034-12-03 | 6094.05 | 1.8528 | 90.9777 | 74.6386 | 1785.9898
2034-12-04 01:00 | 5914.77 | 1.8139 | 90.7431 | 74.6386 | 1733.448
2034-12-05 02:00 | 5845.32 | 1.8381 | 90.4223 | 74.6386 | 1713.0942
2034-12-06 03:00 | 6465.06 | 1.99 | 90.4808 | 74.6386 | 1894.7221
2034-12-07 04:00 | 6254.95 | 2.1002 | 89.813 | 74.6386 | 1833.1449
2034-12-08 05:00 | 6994.55 | 2.3161 | 89.8585 | 74.6386 | 2049.9003
2034-12-09 06:00 | 7517.06 | 2.4343 | 90.0236 | 74.6386 | 2203.0328
2034-12-10 07:00 | 9102.33 | 2.8537 | 90.2887 | 74.6386 | 2667.6296
2034-12-11 08:00 | 9537.61 | 3.0789 | 90.1997 | 74.6386 | 2795.1976
2034-12-12 09:00 | 11506.7 | 3.7821 | 90.1586 | 74.6386 | 3372.2809
2034-12-13 10:00 | 12856.5 | 4.2696 | 90.2825 | 74.6386 | 3767.8682
2034-12-14 11:00 | 13109.4 | 4.4034 | 90.4181 | 74.6386 | 3841.9859
2034-12-15 12:00 | 11368.5 | 3.5294 | 91.1409 | 74.6386 | 3331.7785
2034-12-16 13:00 | 9754.91 | 3.1915 | 90.7079 | 74.6386 | 2858.8819
2034-12-17 14:00 | 9731.71 | 3.0472 | 90.9101 | 74.6386 | 2852.0827
2034-12-18 15:00 | 11226 | 3.6728 | 90.5177 | 74.6386 | 3290.0158
2034-12-19 16:00 | 12376.9 | 3.9413 | 90.7797 | 74.6386 | 3627.3113
2034-12-20 17:00 | 12944.1 | 4.0964 | 90.9281 | 74.6386 | 3793.5412
2034-12-21 18:00 | 10883.1 | 3.5115 | 90.8937 | 74.6386 | 3189.5218
2034-12-22 19:00 | 9998.26 | 3.1688 | 90.956 | 74.6386 | 2930.2008
2034-12-23 20:00 | 8242.04 | 2.4341 | 91.4282 | 74.6386 | 2415.5035
2034-12-24 21:00 | 7412.9 | 2.2803 | 90.9425 | 74.6386 | 2172.5065
2034-12-25 22:00 | 5727.15 | 1.6717 | 91.1852 | 74.6386 | 1678.462
2034-12-26 23:00 | 5190.52 | 1.5632 | 90.6931 | 74.6386 | 1521.1913
2034-12-28 | 4843.44 | 1.4899 | 90.3549 | 74.6386 | 1419.4721
2034-12-29 01:00 | 4808.91 | 1.4623 | 90.3157 | 74.6386 | 1409.3524
2034-12-30 02:00 | 5171.24 | 1.5891 | 90.1469 | 74.6386 | 1515.5408
2034-12-31 03:00 | 5424.01 | 1.7567 | 89.6999 | 74.6386 | 1589.6204
2035-01-01 04:00 | 5695.87 | 1.8618 | 89.6026 | 74.6386 | 1669.2947
2035-01-02 05:00 | 6528.91 | 2.1648 | 89.474 | 74.6386 | 1913.4346
2035-01-03 06:00 | 7185.29 | 2.3293 | 89.6731 | 74.6386 | 2105.8006
2035-01-04 07:00 | 8665.27 | 2.7874 | 89.7805 | 74.6386 | 2539.54
2035-01-05 08:00 | 9252.87 | 2.9696 | 89.9276 | 74.6386 | 2711.7485
2035-01-06 09:00 | 11156.9 | 3.6222 | 89.9489 | 74.6386 | 3269.7646
2035-01-07 10:00 | 12848.2 | 4.1841 | 90.1289 | 74.6386 | 3765.4357
2035-01-08 11:00 | 11413.7 | 4.0025 | 89.8592 | 74.6386 | 3345.0253
2035-01-09 12:00 | 14427.5 | 4.4879 | 90.7622 | 74.6386 | 4228.2829
2035-01-10 13:00 | 14002.3 | 4.6299 | 90.5843 | 74.6386 | 4103.669
2035-01-11 14:00 | 14175.3 | 4.6663 | 90.7777 | 74.6386 | 4154.3703
2035-01-12 15:00 | 15485.1 | 5.0034 | 91.0117 | 74.6386 | 4538.2348
2035-01-13 16:00 | 15276.8 | 4.881 | 91.2714 | 74.6386 | 4477.1881
2035-01-14 17:00 | 14699.9 | 4.6338 | 91.5024 | 74.6386 | 4308.1154
2035-01-15 18:00 | 13047.2 | 4.1269 | 91.5137 | 74.6386 | 3823.7569
2035-01-16 19:00 | 11482.7 | 3.7012 | 91.3106 | 74.6386 | 3365.2472
2035-01-17 20:00 | 9659.8 | 2.9229 | 91.6755 | 74.6386 | 2831.0079
2035-01-18 21:00 | 8766.7 | 2.6753 | 91.4145 | 74.6386 | 2569.2661
2035-01-19 22:00 | 7284.09 | 2.1084 | 91.6612 | 74.6386 | 2134.7561
2035-01-20 23:00 | 6796.06 | 2.0235 | 91.2322 | 74.6386 | 1991.7286
2035-01-22 | 6567.39 | 1.9757 | 90.9804 | 74.6386 | 1924.712
2035-01-23 01:00 | 6232.66 | 1.9211 | 90.6718 | 74.6386 | 1826.6123
2035-01-24 02:00 | 5899.29 | 1.8846 | 90.2945 | 74.6386 | 1728.9112
2035-01-25 03:00 | 6121.87 | 1.969 | 90.1273 | 74.6386 | 1794.143
2035-01-26 04:00 | 6207.69 | 2.0221 | 89.9703 | 74.6386 | 1819.2944
2035-01-27 05:00 | 6737.96 | 2.2657 | 89.6908 | 74.6386 | 1974.7011
2035-01-28 06:00 | 7212.72 | 2.3489 | 89.9083 | 74.6386 | 2113.8396
2035-01-29 07:00 | 8394.63 | 2.7545 | 89.8639 | 74.6386 | 2460.2232
2035-01-30 08:00 | 9288.08 | 2.9017 | 90.3139 | 74.6386 | 2722.0675
2035-01-31 09:00 | 11173.3 | 3.5989 | 90.1857 | 74.6386 | 3274.571
2035-02-01 10:00 | 12251.1 | 4.1682 | 89.9858 | 74.6386 | 3590.443
2035-02-02 11:00 | 13437.8 | 4.3343 | 90.5616 | 74.6386 | 3938.2304
2035-02-03 12:00 | 10539.1 | 3.4718 | 90.6122 | 74.6386 | 3088.7053
2035-02-04 13:00 | 9552 | 2.972 | 90.9484 | 74.6386 | 2799.4149
2035-02-05 14:00 | 9309.52 | 2.9098 | 90.8117 | 74.6386 | 2728.351
2035-02-06 15:00 | 10453.1 | 3.4017 | 90.4465 | 74.6386 | 3063.5012
2035-02-07 16:00 | 10886 | 3.522 | 90.5213 | 74.6386 | 3190.3717
2035-02-08 17:00 | 11042 | 3.4607 | 90.7752 | 74.6386 | 3236.0908
2035-02-09 18:00 | 9879.53 | 3.1471 | 90.6933 | 74.6386 | 2895.4044
2035-02-10 19:00 | 9191.52 | 2.8981 | 90.7216 | 74.6386 | 2693.7686
2035-02-11 20:00 | 7498.08 | 2.2244 | 91.1336 | 74.6386 | 2197.4703
2035-02-12 21:00 | 6706.32 | 2.0729 | 90.6477 | 74.6386 | 1965.4284
2035-02-13 22:00 | 5215.35 | 1.4766 | 91.1878 | 74.6386 | 1528.4682
2035-02-14 23:00 | 4464.32 | 1.3977 | 90.1662 | 74.6386 | 1308.363
2035-02-16 | 4111.14 | 1.3057 | 89.8776 | 74.6386 | 1204.8562
2035-02-17 01:00 | 3888.56 | 1.2138 | 89.8672 | 74.6386 | 1139.6244
2035-02-18 02:00 | 4047.74 | 1.2484 | 89.8498 | 74.6386 | 1186.2755
2035-02-19 03:00 | 4448.72 | 1.4111 | 89.5559 | 74.6386 | 1303.7911
2035-02-20 04:00 | 4939.35 | 1.5339 | 89.678 | 74.6386 | 1447.5806
2035-02-21 05:00 | 6024.98 | 1.9665 | 89.2972 | 74.6386 | 1765.7473
2035-02-22 06:00 | 6187.14 | 1.9871 | 89.4721 | 74.6386 | 1813.2717
2035-02-23 07:00 | 6621.3 | 2.1116 | 89.5486 | 74.6386 | 1940.5115
2035-02-24 08:00 | 5647.41 | 1.71 | 89.9792 | 74.6386 | 1655.0925
2035-02-25 09:00 | 5881.51 | 1.8401 | 89.6609 | 74.6386 | 1723.7004
2035-02-26 10:00 | 6021.01 | 1.9762 | 89.2763 | 74.6386 | 1764.5838
2035-02-27 11:00 | 6617.28 | 2.1864 | 89.2061 | 74.6386 | 1939.3333
2035-02-28 12:00 | 7678.62 | 2.5205 | 89.2702 | 74.6386 | 2250.3814
2035-03-01 13:00 | 8908.94 | 2.9861 | 89.1965 | 74.6386 | 2610.9526
2035-03-02 14:00 | 9963.76 | 3.3388 | 89.3335 | 74.6386 | 2920.0898
2035-03-03 15:00 | 12447.1 | 4.2152 | 89.4042 | 74.6386 | 3647.8849
2035-03-04 16:00 | 13640.7 | 4.4657 | 89.9169 | 74.6386 | 3997.6945
2035-03-05 17:00 | 13727.4 | 4.4714 | 90.2051 | 74.6386 | 4023.1038
2035-03-06 18:00 | 11999.8 | 3.8366 | 90.509 | 74.6386 | 3516.7942
2035-03-07 19:00 | 10578.3 | 3.36 | 90.5563 | 74.6386 | 3100.1937
2035-03-08 20:00 | 8688.46 | 2.627 | 90.8803 | 74.6386 | 2546.3363
2035-03-09 21:00 | 7842.91 | 2.3627 | 90.7631 | 74.6386 | 2298.53
2035-03-10 22:00 | 6156.67 | 1.7769 | 90.9779 | 74.6386 | 1804.3419
2035-03-11 23:00 | 5053.92 | 1.475 | 90.6913 | 74.6386 | 1481.1577
2035-03-13 | 4548.27 | 1.3883 | 90.1438 | 74.6386 | 1332.9664
2035-03-14 01:00 | 4130.36 | 1.3171 | 89.6606 | 74.6386 | 1210.489
2035-03-15 02:00 | 3700.97 | 1.1942 | 89.444 | 74.6386 | 1084.6472
2035-03-16 03:00 | 3683.73 | 1.2006 | 89.2237 | 74.6386 | 1079.5947
2035-03-17 04:00 | 3410.87 | 1.1077 | 89.1357 | 74.6386 | 999.6273
2035-03-18 05:00 | 3480.36 | 1.0805 | 89.352 | 74.6386 | 1019.9928
2035-03-19 06:00 | 5691.27 | 1.7789 | 89.2102 | 74.6386 | 1667.9466
2035-03-20 07:00 | 7614.8 | 2.4478 | 89.091 | 74.6386 | 2231.6776
2035-03-21 08:00 | 7213.78 | 2.2728 | 89.4246 | 74.6386 | 2114.1502
2035-03-22 09:00 | 8218.92 | 2.7532 | 89.0274 | 74.6386 | 2408.7277
2035-03-23 10:00 | 10065.6 | 3.3736 | 89.135 | 74.6386 | 2949.9362
2035-03-24 11:00 | 11285.7 | 3.7156 | 89.4904 | 74.6386 | 3307.5122
2035-03-25 12:00 | 10449.6 | 3.3345 | 89.9398 | 74.6386 | 3062.4755
2035-03-26 13:00 | 9184.21 | 2.8486 | 90.215 | 74.6386 | 2691.6263
2035-03-27 14:00 | 9690.75 | 3.15 | 89.8396 | 74.6386 | 2840.0785
2035-03-28 15:00 | 10550.2 | 3.4723 | 89.7941 | 74.6386 | 3091.9584
2035-03-29 16:00 | 12864.1 | 4.4648 | 89.5125 | 74.6386 | 3770.0956
2035-03-30 17:00 | 12715.1 | 4.111 | 90.2265 | 74.6386 | 3726.428
2035-03-31 18:00 | 11445 | 3.6042 | 90.5404 | 74.6386 | 3354.1984
2035-04-01 19:00 | 10054.2 | 3.1167 | 90.6539 | 74.6386 | 2946.5952
2035-04-02 20:00 | 9081.89 | 2.8482 | 90.505 | 74.6386 | 2661.6392
2035-04-03 21:00 | 8391.63 | 2.6015 | 90.5138 | 74.6386 | 2459.344
2035-04-04 22:00 | 8091.79 | 2.4639 | 90.5472 | 74.6386 | 2371.4696
2035-04-05 23:00 | 5212.57 | 1.4773 | 91.0377 | 74.6386 | 1527.6535
2035-04-07 | 4483.96 | 1.386 | 90.0856 | 74.6386 | 1314.119
2035-04-08 01:00 | 4024.98 | 1.2477 | 89.8739 | 74.6386 | 1179.6052
2035-04-09 02:00 | 3518.16 | 1.1207 | 89.5324 | 74.6386 | 1031.0709
2035-04-10 03:00 | 3423.95 | 1.0961 | 89.3513 | 74.6386 | 1003.4607
2035-04-11 04:00 | 3317.59 | 1.0229 | 89.4954 | 74.6386 | 972.2897
2035-04-12 05:00 | 3317.95 | 1.0358 | 89.3018 | 74.6386 | 972.3952
2035-04-13 06:00 | 5442.11 | 1.7311 | 89.0747 | 74.6386 | 1594.925
2035-04-14 07:00 | 6984.93 | 2.3739 | 88.682 | 74.6386 | 2047.0809
2035-04-15 08:00 | 7393.17 | 2.47 | 88.9503 | 74.6386 | 2166.7242
2035-04-16 09:00 | 8965.22 | 2.9267 | 89.2041 | 74.6386 | 2627.4466
2035-04-17 10:00 | 10726.1 | 3.5173 | 89.3321 | 74.6386 | 3143.5096
2035-04-18 11:00 | 11911.7 | 3.9702 | 89.466 | 74.6386 | 3490.9747
2035-04-19 12:00 | 13127.6 | 4.3431 | 89.7491 | 74.6386 | 3847.3198
2035-04-20 13:00 | 13672.4 | 4.5029 | 90.0189 | 74.6386 | 4006.9849
2035-04-21 14:00 | 14234.8 | 4.559 | 90.4342 | 74.6386 | 4171.8081
2035-04-22 15:00 | 15128.9 | 4.7781 | 90.7247 | 74.6386 | 4433.8429
2035-04-23 16:00 | 16921.3 | 5.6023 | 90.5759 | 74.6386 | 4959.1435
2035-04-24 17:00 | 15089.6 | 4.8531 | 91.0677 | 74.6386 | 4422.3252
2035-04-25 18:00 | 13787.6 | 4.255 | 91.4258 | 74.6386 | 4040.7467
2035-04-26 19:00 | 12479.5 | 3.7602 | 91.5764 | 74.6386 | 3657.3804
2035-04-27 20:00 | 11314.8 | 3.4961 | 91.3225 | 74.6386 | 3316.0405
2035-04-28 21:00 | 10277.5 | 3.2695 | 91.0054 | 74.6386 | 3012.0379
2035-04-29 22:00 | 9752.55 | 3.0342 | 91.0294 | 74.6386 | 2858.1903
2035-04-30 23:00 | 7365.2 | 2.177 | 91.3296 | 74.6386 | 2158.527
2035-05-02 | 6793.76 | 2.0459 | 90.9492 | 74.6386 | 1991.0545
2035-05-03 01:00 | 6456.63 | 1.9498 | 90.7529 | 74.6386 | 1892.2515
2035-05-04 02:00 | 6139.38 | 1.9666 | 90.1826 | 74.6386 | 1799.2747
2035-05-05 03:00 | 6589.61 | 2.0665 | 90.2236 | 74.6386 | 1931.2241
2035-05-06 04:00 | 6925.23 | 2.1707 | 90.1562 | 74.6386 | 2029.5846
2035-05-07 05:00 | 7475.76 | 2.4549 | 89.8008 | 74.6386 | 2190.929
2035-05-08 06:00 | 8060.07 | 2.5804 | 90 | 74.6386 | 2362.1733
2035-05-09 07:00 | 9230.36 | 2.972 | 89.9945 | 74.6386 | 2705.1515
2035-05-10 08:00 | 9745.38 | 3.1325 | 90.1132 | 74.6386 | 2856.0889
2035-05-11 09:00 | 10730.4 | 3.6054 | 89.8835 | 74.6386 | 3144.7698
2035-05-12 10:00 | 12091.2 | 4.0564 | 90.0081 | 74.6386 | 3543.5809
2035-05-13 11:00 | 12744 | 4.3942 | 89.9942 | 74.6386 | 3734.8977
2035-05-14 12:00 | 13200.5 | 4.5203 | 90.2021 | 74.6386 | 3868.6847
2035-05-15 13:00 | 14724.3 | 4.4959 | 91.1759 | 74.6386 | 4315.2664
2035-05-16 14:00 | 15357.7 | 4.7129 | 91.3542 | 74.6386 | 4500.8976
2035-05-17 15:00 | 16964.4 | 5.4025 | 91.2626 | 74.6386 | 4971.7749
2035-05-18 16:00 | 17477.4 | 5.4166 | 91.6997 | 74.6386 | 5122.1203
2035-05-19 17:00 | 16646.6 | 5.3203 | 91.6728 | 74.6386 | 4878.6369
2035-05-20 18:00 | 14172.6 | 4.3774 | 92.0237 | 74.6386 | 4153.579
2035-05-21 19:00 | 12906 | 4.0008 | 91.8984 | 74.6386 | 3782.3752
2035-05-22 20:00 | 10605.9 | 3.2428 | 91.9014 | 74.6386 | 3108.2825
2035-05-23 21:00 | 9511.18 | 2.938 | 91.6106 | 74.6386 | 2787.4517
2035-05-24 22:00 | 7806.38 | 2.2589 | 91.9176 | 74.6386 | 2287.8241
2035-05-25 23:00 | 7233.07 | 2.1478 | 91.4686 | 74.6386 | 2119.8036
2035-05-27 | 6709.27 | 2.04 | 91.1056 | 74.6386 | 1966.2929
2035-05-28 01:00 | 6233.13 | 1.9328 | 90.7969 | 74.6386 | 1826.7501
2035-05-29 02:00 | 5966.3 | 1.9057 | 90.4349 | 74.6386 | 1748.5499
2035-05-30 03:00 | 6619.93 | 2.0334 | 90.5969 | 74.6386 | 1940.11
2035-05-31 04:00 | 6655.63 | 2.1542 | 90.1556 | 74.6386 | 1950.5726
2035-06-01 05:00 | 7465.46 | 2.5029 | 89.8509 | 74.6386 | 2187.9104
2035-06-02 06:00 | 7726.15 | 2.4692 | 90.2087 | 74.6386 | 2264.311
2035-06-03 07:00 | 8401.04 | 2.6622 | 90.2834 | 74.6386 | 2462.1018
2035-06-04 08:00 | 8191.32 | 2.3666 | 91.0611 | 74.6386 | 2400.6389
2035-06-05 09:00 | 9763.06 | 3.1505 | 90.209 | 74.6386 | 2861.2704
2035-06-06 10:00 | 9037.22 | 3.0723 | 89.9588 | 74.6386 | 2648.5477
2035-06-07 11:00 | 9514.93 | 3.1139 | 90.2363 | 74.6386 | 2788.5507
2035-06-08 12:00 | 9409.5 | 3.0685 | 90.2938 | 74.6386 | 2757.6522
2035-06-09 13:00 | 11250 | 3.6197 | 90.4015 | 74.6386 | 3297.0495
2035-06-10 14:00 | 12739.5 | 4.0879 | 90.565 | 74.6386 | 3733.5789
2035-06-11 15:00 | 15457.9 | 5.0111 | 90.658 | 74.6386 | 4530.2633
2035-06-12 16:00 | 15732.6 | 5.1487 | 90.8857 | 74.6386 | 4610.7699
2035-06-13 17:00 | 14281.1 | 4.9254 | 90.7152 | 74.6386 | 4185.3773
2035-06-14 18:00 | 14163 | 4.3028 | 91.6811 | 74.6386 | 4150.7656
2035-06-15 19:00 | 11674.2 | 3.7948 | 91.224 | 74.6386 | 3421.3703
2035-06-16 20:00 | 10014.7 | 3.0236 | 91.6707 | 74.6386 | 2935.0188
2035-06-17 21:00 | 8933.42 | 2.75 | 91.3255 | 74.6386 | 2618.127
2035-06-18 22:00 | 7166.06 | 2.1199 | 91.4706 | 74.6386 | 2100.1649
2035-06-19 23:00 | 6676.44 | 1.9631 | 91.3058 | 74.6386 | 1956.6714
2035-06-21 | 6354.93 | 1.9082 | 90.9711 | 74.6386 | 1862.4461
2035-06-22 01:00 | 6028.45 | 1.8797 | 90.5593 | 74.6386 | 1766.7643
2035-06-23 02:00 | 5812.72 | 1.8382 | 90.3407 | 74.6386 | 1703.5401
2035-06-24 03:00 | 6039.92 | 1.9337 | 90.1297 | 74.6386 | 1770.1258
2035-06-25 04:00 | 6258.96 | 2.0299 | 89.9658 | 74.6386 | 1834.3201
2035-06-26 05:00 | 7097.17 | 2.3368 | 89.8123 | 74.6386 | 2079.9752
2035-06-27 06:00 | 7484.37 | 2.4407 | 89.8908 | 74.6386 | 2193.4523
2035-06-28 07:00 | 8962.75 | 2.8432 | 90.1141 | 74.6386 | 2626.7227
2035-06-29 08:00 | 9763.81 | 3.0822 | 90.2685 | 74.6386 | 2861.4902
2035-06-30 09:00 | 9940.66 | 3.3518 | 89.9113 | 74.6386 | 2913.3199
2035-07-01 10:00 | 11497.9 | 3.8517 | 90.0438 | 74.6386 | 3369.7019
2035-07-02 11:00 | 13350.3 | 4.19 | 90.691 | 74.6386 | 3912.5867
2035-07-03 12:00 | 11197.2 | 3.6493 | 90.671 | 74.6386 | 3281.5754
2035-07-04 13:00 | 10329 | 3.1797 | 91.0806 | 74.6386 | 3027.1311
2035-07-05 14:00 | 9484.49 | 3.0649 | 90.6523 | 74.6386 | 2779.6296
2035-07-06 15:00 | 11246.2 | 3.739 | 90.3706 | 74.6386 | 3295.9359
2035-07-07 16:00 | 13689.2 | 4.4136 | 90.6666 | 74.6386 | 4011.9085
2035-07-08 17:00 | 13052.9 | 4.1599 | 90.9509 | 74.6386 | 3825.4274
2035-07-09 18:00 | 11924.8 | 3.7836 | 91.0549 | 74.6386 | 3494.8139
2035-07-10 19:00 | 10615.2 | 3.414 | 90.9271 | 74.6386 | 3111.008
2035-07-11 20:00 | 8912.67 | 2.6845 | 91.3624 | 74.6386 | 2612.0457
2035-07-12 21:00 | 8262.51 | 2.5007 | 91.1778 | 74.6386 | 2421.5026
2035-07-13 22:00 | 6308.21 | 1.879 | 91.1556 | 74.6386 | 1848.7539
2035-07-14 23:00 | 5701.02 | 1.7094 | 90.8609 | 74.6386 | 1670.804
2035-07-16 | 5406.49 | 1.6327 | 90.6215 | 74.6386 | 1584.4858
2035-07-17 01:00 | 5227.54 | 1.5911 | 90.4357 | 74.6386 | 1532.0407
2035-07-18 02:00 | 5053.74 | 1.6143 | 89.9801 | 74.6386 | 1481.105
2035-07-19 03:00 | 5170.45 | 1.7029 | 89.6613 | 74.6386 | 1515.3093
2035-07-20 04:00 | 5465.57 | 1.7575 | 89.7655 | 74.6386 | 1601.8004
2035-07-21 05:00 | 6344.29 | 2.0908 | 89.5458 | 74.6386 | 1859.3279
2035-07-22 06:00 | 6815.06 | 2.2038 | 89.7045 | 74.6386 | 1997.2969
2035-07-23 07:00 | 8304.36 | 2.6255 | 89.8968 | 74.6386 | 2433.7677
2035-07-24 08:00 | 8870.5 | 2.9031 | 89.7605 | 74.6386 | 2599.6869
2035-07-25 09:00 | 10488.5 | 3.5093 | 89.7043 | 74.6386 | 3073.8759
2035-07-26 10:00 | 12289.1 | 4.1471 | 89.8245 | 74.6386 | 3601.5797
2035-07-27 11:00 | 13803.9 | 4.5737 | 90.1946 | 74.6386 | 4045.5237
2035-07-28 12:00 | 14384.4 | 4.7542 | 90.4812 | 74.6386 | 4215.6515
2035-07-29 13:00 | 15258.3 | 4.9032 | 90.898 | 74.6386 | 4471.7663
2035-07-30 14:00 | 16067 | 4.8929 | 91.5301 | 74.6386 | 4708.7729
2035-07-31 15:00 | 16163.9 | 5.2656 | 91.2406 | 74.6386 | 4737.1715
2035-08-01 16:00 | 15406.4 | 4.9674 | 91.4639 | 74.6386 | 4515.1701
2035-08-02 17:00 | 15644.1 | 4.9407 | 91.6698 | 74.6386 | 4584.8331
2035-08-03 18:00 | 13665 | 4.2986 | 91.7883 | 74.6386 | 4004.8162
2035-08-04 19:00 | 12009.9 | 3.8558 | 91.5718 | 74.6386 | 3519.7542
2035-08-05 20:00 | 10359.2 | 3.0975 | 91.9782 | 74.6386 | 3035.9818
2035-08-06 21:00 | 9431.34 | 2.8944 | 91.5962 | 74.6386 | 2764.0529
2035-08-07 22:00 | 7742.34 | 2.2907 | 91.7272 | 74.6386 | 2269.0559
2035-08-08 23:00 | 6913.59 | 2.1108 | 91.2485 | 74.6386 | 2026.1732
2035-08-10 | 6225.79 | 1.983 | 90.7282 | 74.6386 | 1824.5989
2035-08-11 01:00 | 5975.56 | 1.8274 | 90.8599 | 74.6386 | 1751.2638
2035-08-12 02:00 | 5869.46 | 1.8599 | 90.4486 | 74.6386 | 1720.1689
2035-08-13 03:00 | 5986.16 | 1.9057 | 90.2958 | 74.6386 | 1754.3703
2035-08-14 04:00 | 6048.98 | 1.9684 | 90.058 | 74.6386 | 1772.781
2035-08-15 05:00 | 6908.05 | 2.2546 | 89.9667 | 74.6386 | 2024.5496
2035-08-16 06:00 | 7363.46 | 2.3558 | 90.1218 | 74.6386 | 2158.0171
2035-08-17 07:00 | 8519.17 | 2.7145 | 90.1715 | 74.6386 | 2496.7223
2035-08-18 08:00 | 9251.7 | 2.9311 | 90.2989 | 74.6386 | 2711.4056
2035-08-19 09:00 | 10799.4 | 3.5959 | 90.0289 | 74.6386 | 3164.9917
2035-08-20 10:00 | 12582.4 | 4.1762 | 90.2158 | 74.6386 | 3687.5374
2035-08-21 11:00 | 12856.3 | 4.4247 | 90.1844 | 74.6386 | 3767.8096
2035-08-22 12:00 | 14215.2 | 4.633 | 90.7268 | 74.6386 | 4166.0639
2035-08-23 13:00 | 14918.6 | 4.8206 | 90.992 | 74.6386 | 4372.2101
2035-08-24 14:00 | 15500 | 4.9694 | 91.2471 | 74.6386 | 4542.6016
2035-08-25 15:00 | 17024.4 | 5.577 | 91.258 | 74.6386 | 4989.3591
2035-08-26 16:00 | 18041.2 | 5.7506 | 91.6856 | 74.6386 | 5287.3538
2035-08-27 17:00 | 17295.2 | 5.6014 | 91.8062 | 74.6386 | 5068.7228
2035-08-28 18:00 | 15406.7 | 4.8005 | 92.2057 | 74.6386 | 4515.2581
2035-08-29 19:00 | 14549.8 | 4.3252 | 92.5356 | 74.6386 | 4264.1255
2035-08-30 20:00 | 11428.7 | 3.529 | 92.2123 | 74.6386 | 3349.4213
2035-08-31 21:00 | 10444.7 | 3.203 | 92.0407 | 74.6386 | 3061.0394
2035-09-01 22:00 | 8479.38 | 2.5378 | 92.0328 | 74.6386 | 2485.061
2035-09-02 23:00 | 6861.4 | 2.0958 | 91.6296 | 74.6386 | 2010.8778
2035-09-04 | 6101.7 | 1.8766 | 91.3094 | 74.6386 | 1788.2317
2035-09-05 01:00 | 5836.75 | 1.7519 | 91.2699 | 74.6386 | 1710.5826
2035-09-06 02:00 | 5497.24 | 1.6966 | 90.8961 | 74.6386 | 1611.082
2035-09-07 03:00 | 5208.03 | 1.6091 | 90.7289 | 74.6386 | 1526.3229
2035-09-08 04:00 | 4925.38 | 1.5355 | 90.5128 | 74.6386 | 1443.4864
2035-09-09 05:00 | 4782.43 | 1.5141 | 90.2634 | 74.6386 | 1401.5919
2035-09-10 06:00 | 6277.85 | 2.1597 | 89.5567 | 74.6386 | 1839.8562
2035-09-11 07:00 | 8023.26 | 2.7388 | 89.624 | 74.6386 | 2351.3854
2035-09-12 08:00 | 8656.66 | 2.8234 | 90.0695 | 74.6386 | 2537.0166
2035-09-13 09:00 | 10057.1 | 3.2985 | 90.1165 | 74.6386 | 2947.4451
2035-09-14 10:00 | 11991 | 4.009 | 90.1278 | 74.6386 | 3514.2152
2035-09-15 11:00 | 12969 | 4.3717 | 90.317 | 74.6386 | 3800.8387
2035-09-16 12:00 | 14433.1 | 4.5911 | 90.9486 | 74.6386 | 4229.9241
2035-09-17 13:00 | 14874.7 | 4.8624 | 90.9791 | 74.6386 | 4359.3442
2035-09-18 14:00 | 15744.9 | 5.133 | 91.1877 | 74.6386 | 4614.3747
2035-09-19 15:00 | 15105.5 | 4.5922 | 91.9016 | 74.6386 | 4426.985
2035-09-20 16:00 | 15715.4 | 4.6646 | 92.1689 | 74.6386 | 4605.7291
2035-09-21 17:00 | 12191.4 | 4.0699 | 91.4089 | 74.6386 | 3572.9466
2035-09-22 18:00 | 10946.1 | 3.4523 | 91.653 | 74.6386 | 3207.9852
2035-09-23 19:00 | 9544.69 | 3.1033 | 91.2542 | 74.6386 | 2797.2725
2035-09-24 20:00 | 9252.64 | 2.8016 | 91.6165 | 74.6386 | 2711.6811
2035-09-25 21:00 | 8390.84 | 2.7069 | 91.0141 | 74.6386 | 2459.1125
2035-09-26 22:00 | 7992.83 | 2.535 | 90.9793 | 74.6386 | 2342.4672
2035-09-27 23:00 | 5670.5 | 1.5753 | 91.9226 | 74.6386 | 1661.8595
2035-09-29 | 4992.58 | 1.5272 | 90.8913 | 74.6386 | 1463.1808
2035-09-30 01:00 | 4720.6 | 1.3936 | 90.9686 | 74.6386 | 1383.4713
2035-10-01 02:00 | 4434.57 | 1.3696 | 90.4567 | 74.6386 | 1299.6442
2035-10-02 03:00 | 4347.77 | 1.3731 | 90.145 | 74.6386 | 1274.2056
2035-10-03 04:00 | 4358.77 | 1.3574 | 90.1175 | 74.6386 | 1277.4294
2035-10-04 05:00 | 4284.05 | 1.3762 | 89.8106 | 74.6386 | 1255.5311
2035-10-05 06:00 | 5927.69 | 2.0907 | 89.0845 | 74.6386 | 1737.2345
2035-10-06 07:00 | 7449.43 | 2.6294 | 89.1394 | 74.6386 | 2183.2124
2035-10-07 08:00 | 8057.14 | 2.6181 | 89.8435 | 74.6386 | 2361.3146
2035-10-08 09:00 | 9803.15 | 3.1283 | 90.0672 | 74.6386 | 2873.0197
2035-10-09 10:00 | 11451.7 | 3.6544 | 90.2336 | 74.6386 | 3356.162
2035-10-10 11:00 | 11658.2 | 3.8222 | 90.2717 | 74.6386 | 3416.6811
2035-10-11 12:00 | 12544.6 | 4.1361 | 90.3756 | 74.6386 | 3676.4593
2035-10-12 13:00 | 13407.5 | 4.38 | 90.5966 | 74.6386 | 3929.3504
2035-10-13 14:00 | 11413.3 | 3.5402 | 91.1615 | 74.6386 | 3344.908
2035-10-14 15:00 | 10561.7 | 3.248 | 91.187 | 74.6386 | 3095.3287
2035-10-15 16:00 | 11548.3 | 3.917 | 90.3836 | 74.6386 | 3384.4726
2035-10-16 17:00 | 10734.6 | 3.3889 | 90.9677 | 74.6386 | 3146.0007
2035-10-17 18:00 | 9430.04 | 3.048 | 90.7689 | 74.6386 | 2763.6719
2035-10-18 19:00 | 8736.28 | 2.6962 | 90.9859 | 74.6386 | 2560.3509
2035-10-19 20:00 | 8135.17 | 2.5585 | 90.7466 | 74.6386 | 2384.183
2035-10-20 21:00 | 7554.23 | 2.3753 | 90.659 | 74.6386 | 2213.9263
2035-10-21 22:00 | 6976.18 | 2.1958 | 90.5338 | 74.6386 | 2044.5165
2035-10-22 23:00 | 5093.4 | 1.4242 | 91.367 | 74.6386 | 1492.7282
2035-10-24 | 4300.61 | 1.3242 | 90.3798 | 74.6386 | 1260.3844
2035-10-25 01:00 | 4186.4 | 1.2655 | 90.3297 | 74.6386 | 1226.9127
2035-10-26 02:00 | 3992.44 | 1.2732 | 89.8021 | 74.6386 | 1170.0687
2035-10-27 03:00 | 4585.64 | 1.4116 | 89.9667 | 74.6386 | 1343.9184
2035-10-28 04:00 | 4978.85 | 1.5306 | 89.9284 | 74.6386 | 1459.1569
2035-10-29 05:00 | 5585.39 | 1.8932 | 89.2092 | 74.6386 | 1636.9162
2035-10-30 06:00 | 6244.14 | 1.9878 | 89.688 | 74.6386 | 1829.9768
2035-10-31 07:00 | 7220.95 | 2.3939 | 89.4384 | 74.6386 | 2116.2515
2035-11-01 08:00 | 7988.79 | 2.6019 | 89.6565 | 74.6386 | 2341.2832
2035-11-02 09:00 | 9692.99 | 3.2166 | 89.6125 | 74.6386 | 2840.735
2035-11-03 10:00 | 11728 | 3.9292 | 89.7103 | 74.6386 | 3437.1375
2035-11-04 11:00 | 13197 | 4.3862 | 90.0185 | 74.6386 | 3867.6589
2035-11-05 12:00 | 13277.6 | 4.1685 | 90.6924 | 74.6386 | 3891.2804
2035-11-06 13:00 | 11240.6 | 3.6047 | 90.6962 | 74.6386 | 3294.2947
2035-11-07 14:00 | 10986.5 | 3.4453 | 90.8349 | 74.6386 | 3219.8253
2035-11-08 15:00 | 11851.8 | 3.8327 | 90.5991 | 74.6386 | 3473.4197
2035-11-09 16:00 | 12079.1 | 3.8139 | 90.8492 | 74.6386 | 3540.0348
2035-11-10 17:00 | 12131.4 | 4.0217 | 90.5478 | 74.6386 | 3555.3624
2035-11-11 18:00 | 10922.5 | 3.5363 | 90.7577 | 74.6386 | 3201.0688
2035-11-12 19:00 | 10014.2 | 3.1646 | 90.9039 | 74.6386 | 2934.8723
2035-11-13 20:00 | 8648.55 | 2.5444 | 91.3967 | 74.6386 | 2534.6398
2035-11-14 21:00 | 7836.59 | 2.3935 | 90.9703 | 74.6386 | 2296.6778
2035-11-15 22:00 | 6204.86 | 1.809 | 91.1959 | 74.6386 | 1818.465
2035-11-16 23:00 | 5720.76 | 1.7197 | 90.7377 | 74.6386 | 1676.5893
2035-11-18 | 5379.48 | 1.6176 | 90.5716 | 74.6386 | 1576.57
2035-11-19 01:00 | 5137.69 | 1.5766 | 90.2958 | 74.6386 | 1505.7083
2035-11-20 02:00 | 5068.18 | 1.6117 | 89.9304 | 74.6386 | 1485.3369
2035-11-21 03:00 | 5478.44 | 1.724 | 89.9246 | 74.6386 | 1605.5723
2035-11-22 04:00 | 5567.88 | 1.823 | 89.6039 | 74.6386 | 1631.7845
2035-11-23 05:00 | 6334.34 | 2.1126 | 89.4415 | 74.6386 | 1856.4118
2035-11-24 06:00 | 6637.06 | 2.2007 | 89.506 | 74.6386 | 1945.1303
2035-11-25 07:00 | 7372.27 | 2.2986 | 89.9799 | 74.6386 | 2160.5991
2035-11-26 08:00 | 6689.47 | 2.0475 | 90.1794 | 74.6386 | 1960.4901
2035-11-27 09:00 | 7906.63 | 2.5109 | 89.8666 | 74.6386 | 2317.2045
2035-11-28 10:00 | 9814.94 | 3.225 | 89.6817 | 74.6386 | 2876.475
2035-11-29 11:00 | 11330.9 | 3.7874 | 89.7315 | 74.6386 | 3320.759
2035-11-30 12:00 | 12272.3 | 4.0157 | 90.0824 | 74.6386 | 3596.6561
2035-12-01 13:00 | 11663 | 3.818 | 90.2611 | 74.6386 | 3418.0879
2035-12-02 14:00 | 10445 | 3.4136 | 90.3625 | 74.6386 | 3061.1273
2035-12-03 15:00 | 12974.3 | 4.355 | 90.1477 | 74.6386 | 3802.392
2035-12-04 16:00 | 13765.6 | 4.4066 | 90.6803 | 74.6386 | 4034.2991
2035-12-05 17:00 | 13411.6 | 4.2547 | 90.9196 | 74.6386 | 3930.552
2035-12-06 18:00 | 11563.1 | 3.7209 | 90.8825 | 74.6386 | 3388.8101
2035-12-07 19:00 | 10735.9 | 3.3179 | 91.1177 | 74.6386 | 3146.3817
2035-12-08 20:00 | 8463.42 | 2.6469 | 90.991 | 74.6386 | 2480.3836
2035-12-09 21:00 | 7690 | 2.3857 | 90.8699 | 74.6386 | 2253.7165
2035-12-10 22:00 | 6123.57 | 1.8086 | 91.0868 | 74.6386 | 1794.6412
2035-12-11 23:00 | 5604.49 | 1.6889 | 90.71 | 74.6386 | 1642.5139
2035-12-13 | 5490.96 | 1.5994 | 90.8099 | 74.6386 | 1609.2415
2035-12-14 01:00 | 5304.62 | 1.5999 | 90.4139 | 74.6386 | 1554.6307
2035-12-15 02:00 | 5395.16 | 1.6775 | 90.098 | 74.6386 | 1581.1653
2035-12-16 03:00 | 5545.67 | 1.7728 | 89.8154 | 74.6386 | 1625.2754
2035-12-17 04:00 | 5677.03 | 1.9138 | 89.3841 | 74.6386 | 1663.7733
2035-12-18 05:00 | 6786.45 | 2.1975 | 89.6322 | 74.6386 | 1988.9122
2035-12-19 06:00 | 7064.99 | 2.2269 | 89.8774 | 74.6386 | 2070.5442
2035-12-20 07:00 | 8312.91 | 2.6832 | 89.7327 | 74.6386 | 2436.2734
2035-12-21 08:00 | 8833.1 | 2.8825 | 89.763 | 74.6386 | 2588.7261
2035-12-22 09:00 | 10553.1 | 3.4606 | 89.8262 | 74.6386 | 3092.8083
2035-12-23 10:00 | 11978.6 | 4.0501 | 89.795 | 74.6386 | 3510.5811
2035-12-24 11:00 | 13042.5 | 4.3596 | 90.0868 | 74.6386 | 3822.3794
2035-12-25 12:00 | 13889.9 | 4.6274 | 90.3169 | 74.6386 | 4070.7279
2035-12-26 13:00 | 14153.5 | 4.6236 | 90.6569 | 74.6386 | 4147.9814
2035-12-27 14:00 | 15097.9 | 4.7256 | 91.1408 | 74.6386 | 4424.7577
2035-12-28 15:00 | 15298.7 | 4.8373 | 91.247 | 74.6386 | 4483.6064
2035-12-29 16:00 | 13527.8 | 4.2858 | 91.3738 | 74.6386 | 3964.6068
2035-12-30 17:00 | 12570.4 | 4.0527 | 91.211 | 74.6386 | 3684.0206
2035-12-31 18:00 | 11158.1 | 3.4625 | 91.4393 | 74.6386 | 3270.1163
2036-01-01 19:00 | 9920.5 | 3.2098 | 91.0223 | 74.6386 | 2907.4115
2036-01-02 20:00 | 8112.88 | 2.4872 | 91.2866 | 74.6386 | 2377.6504
2036-01-03 21:00 | 7699.32 | 2.2837 | 91.3246 | 74.6386 | 2256.448
2036-01-04 22:00 | 6175.83 | 1.7447 | 91.5741 | 74.6386 | 1809.9571
2036-01-05 23:00 | 5408.95 | 1.6636 | 90.6857 | 74.6386 | 1585.2068
2036-01-07 | 5119.51 | 1.5687 | 90.521 | 74.6386 | 1500.3803
2036-01-08 01:00 | 4858.99 | 1.5143 | 90.2434 | 74.6386 | 1424.0294
2036-01-09 02:00 | 4868.73 | 1.5231 | 90.0882 | 74.6386 | 1426.8839
2036-01-10 03:00 | 5216.89 | 1.6579 | 89.8605 | 74.6386 | 1528.9195
2036-01-11 04:00 | 5752.05 | 1.8204 | 89.8424 | 74.6386 | 1685.7594
2036-01-12 05:00 | 6339.95 | 2.204 | 89.1645 | 74.6386 | 1858.0559
2036-01-13 06:00 | 6556.31 | 2.0978 | 89.7752 | 74.6386 | 1921.4648
2036-01-14 07:00 | 7773.02 | 2.5397 | 89.6344 | 74.6386 | 2278.0473
2036-01-15 08:00 | 8613.81 | 2.7369 | 89.9366 | 74.6386 | 2524.4585
2036-01-16 09:00 | 9933.04 | 3.2623 | 89.8014 | 74.6386 | 2911.0867
2036-01-17 10:00 | 10978.5 | 3.7496 | 89.6761 | 74.6386 | 3217.4807
2036-01-18 11:00 | 12417.6 | 4.0165 | 90.226 | 74.6386 | 3639.2393
2036-01-19 12:00 | 13191.2 | 4.2516 | 90.4609 | 74.6386 | 3865.9591
2036-01-20 13:00 | 13465.9 | 4.4396 | 90.4858 | 74.6386 | 3946.4657
2036-01-21 14:00 | 14754.9 | 4.8375 | 90.6741 | 74.6386 | 4324.2343
2036-01-22 15:00 | 16615.6 | 5.1592 | 91.275 | 74.6386 | 4869.5517
2036-01-23 16:00 | 14363.6 | 4.6128 | 91.3032 | 74.6386 | 4209.5556
2036-01-24 17:00 | 13197.1 | 4.2992 | 91.2074 | 74.6386 | 3867.6882
2036-01-25 18:00 | 11569.5 | 3.6566 | 91.3842 | 74.6386 | 3390.6857
2036-01-26 19:00 | 10808.6 | 3.2869 | 91.583 | 74.6386 | 3167.688
2036-01-27 20:00 | 8808.38 | 2.5861 | 91.7717 | 74.6386 | 2581.4814
2036-01-28 21:00 | 7618.52 | 2.4034 | 90.9988 | 74.6386 | 2232.7678
2036-01-29 22:00 | 5841.13 | 1.7601 | 91.155 | 74.6386 | 1711.8662
2036-01-30 23:00 | 5423.8 | 1.5995 | 91.0806 | 74.6386 | 1589.5589
2036-02-01 | 5003.96 | 1.5525 | 90.5038 | 74.6386 | 1466.5159
2036-02-02 01:00 | 4849.1 | 1.4747 | 90.5025 | 74.6386 | 1421.1309
2036-02-03 02:00 | 4836.5 | 1.5062 | 90.1911 | 74.6386 | 1417.4382
2036-02-04 03:00 | 5193.52 | 1.6249 | 90.0401 | 74.6386 | 1522.0705
2036-02-05 04:00 | 5351.14 | 1.776 | 89.5567 | 74.6386 | 1568.2643
2036-02-06 05:00 | 6186.03 | 2.1096 | 89.324 | 74.6386 | 1812.9464
2036-02-07 06:00 | 6232.76 | 2.0246 | 89.693 | 74.6386 | 1826.6416
2036-02-08 07:00 | 7655.94 | 2.4819 | 89.7031 | 74.6386 | 2243.7345
2036-02-09 08:00 | 8406.62 | 2.8114 | 89.5749 | 74.6386 | 2463.7371
2036-02-10 09:00 | 10484 | 3.3952 | 89.9055 | 74.6386 | 3072.5571
2036-02-11 10:00 | 11926.4 | 4.0729 | 89.7354 | 74.6386 | 3495.2828
2036-02-12 11:00 | 13871.3 | 4.5674 | 90.214 | 74.6386 | 4065.2767
2036-02-13 12:00 | 14808.7 | 4.8056 | 90.6001 | 74.6386 | 4340.0016
2036-02-14 13:00 | 15633.1 | 5.0493 | 90.8808 | 74.6386 | 4581.6093
2036-02-15 14:00 | 15720.3 | 5.223 | 90.9045 | 74.6386 | 4607.1651
2036-02-16 15:00 | 18058.3 | 5.6814 | 91.4565 | 74.6386 | 5292.3653
2036-02-17 16:00 | 18799.3 | 5.7611 | 91.9602 | 74.6386 | 5509.531
2036-02-18 17:00 | 16691.5 | 5.2551 | 92.0161 | 74.6386 | 4891.7958
2036-02-19 18:00 | 14913.4 | 4.6018 | 92.1995 | 74.6386 | 4370.6861
2036-02-20 19:00 | 12816.8 | 4.0726 | 91.9128 | 74.6386 | 3756.2333
2036-02-21 20:00 | 10394.7 | 3.2087 | 92.0093 | 74.6386 | 3046.3859
2036-02-22 21:00 | 9190.92 | 2.8733 | 91.6691 | 74.6386 | 2693.5928
2036-02-23 22:00 | 7278.39 | 2.1845 | 91.7576 | 74.6386 | 2133.0855
2036-02-24 23:00 | 6094.8 | 1.8106 | 91.5686 | 74.6386 | 1786.2096
2036-02-26 | 5783.31 | 1.7133 | 91.3335 | 74.6386 | 1694.9208
2036-02-27 01:00 | 5109.75 | 1.6157 | 90.6456 | 74.6386 | 1497.5199
2036-02-28 02:00 | 4817.49 | 1.5202 | 90.4882 | 74.6386 | 1411.8669
2036-02-29 03:00 | 4736.05 | 1.4587 | 90.5021 | 74.6386 | 1387.9992
2036-03-01 04:00 | 4548.2 | 1.4088 | 90.3227 | 74.6386 | 1332.9458
2036-03-02 05:00 | 4558.79 | 1.4152 | 90.1877 | 74.6386 | 1336.0495
2036-03-03 06:00 | 6336.7 | 2.0716 | 89.7074 | 74.6386 | 1857.1034
2036-03-04 07:00 | 7817.66 | 2.7267 | 89.3101 | 74.6386 | 2291.13
2036-03-05 08:00 | 8806.44 | 2.7706 | 90.1742 | 74.6386 | 2580.9128
2036-03-06 09:00 | 9610.46 | 3.206 | 89.8653 | 74.6386 | 2816.5478
2036-03-07 10:00 | 11154.2 | 3.7677 | 89.9045 | 74.6386 | 3268.9733
2036-03-08 11:00 | 12608 | 4.1722 | 90.2466 | 74.6386 | 3695.0401
2036-03-09 12:00 | 13185.3 | 4.4932 | 90.2579 | 74.6386 | 3864.23
2036-03-10 13:00 | 12166.3 | 3.8171 | 91.0252 | 74.6386 | 3565.5906
2036-03-11 14:00 | 11289.9 | 3.4834 | 91.1856 | 74.6386 | 3308.7431
2036-03-12 15:00 | 11068.2 | 3.3621 | 91.2712 | 74.6386 | 3243.7692
2036-03-13 16:00 | 12698.3 | 4.3907 | 90.3031 | 74.6386 | 3721.5044
2036-03-14 17:00 | 12178.5 | 3.9392 | 90.8916 | 74.6386 | 3569.166
2036-03-15 18:00 | 11154.6 | 3.5142 | 91.1077 | 74.6386 | 3269.0906
2036-03-16 19:00 | 9984.94 | 3.1742 | 90.9822 | 74.6386 | 2926.297
2036-03-17 20:00 | 9415.47 | 2.96 | 90.9802 | 74.6386 | 2759.4019
2036-03-18 21:00 | 9122.92 | 2.7885 | 91.1267 | 74.6386 | 2673.6639
2036-03-19 22:00 | 8299.36 | 2.6472 | 90.7357 | 74.6386 | 2432.3023
2036-03-20 23:00 | 5970.13 | 1.7048 | 91.4955 | 74.6386 | 1749.6724
2036-03-22 | 5475.87 | 1.5874 | 91.1291 | 74.6386 | 1604.8191
2036-03-23 01:00 | 4927.05 | 1.5404 | 90.3706 | 74.6386 | 1443.9758
2036-03-24 02:00 | 4784.85 | 1.4653 | 90.3952 | 74.6386 | 1402.3011
2036-03-25 03:00 | 4558.06 | 1.4597 | 89.9441 | 74.6386 | 1335.8355
2036-03-26 04:00 | 4393.18 | 1.3852 | 89.945 | 74.6386 | 1287.514
2036-03-27 05:00 | 4523.75 | 1.3872 | 90.0691 | 74.6386 | 1325.7803
2036-03-28 06:00 | 6151.64 | 2.0404 | 89.4245 | 74.6386 | 1802.8677
2036-03-29 07:00 | 8146.73 | 2.6746 | 89.5638 | 74.6386 | 2387.5709
2036-03-30 08:00 | 8392.18 | 2.7988 | 89.6154 | 74.6386 | 2459.5052
2036-03-31 09:00 | 9713.53 | 3.2512 | 89.675 | 74.6386 | 2846.7546
2036-04-01 10:00 | 11378.5 | 3.7956 | 89.8363 | 74.6386 | 3334.7092
2036-04-02 11:00 | 12571.1 | 4.2355 | 89.9874 | 74.6386 | 3684.2257
2036-04-03 12:00 | 13571.5 | 4.1723 | 90.8721 | 74.6386 | 3977.414
2036-04-04 13:00 | 11105.8 | 3.6105 | 90.6529 | 74.6386 | 3254.7887
2036-04-05 14:00 | 10805.5 | 3.4435 | 90.7554 | 74.6386 | 3166.7794
2036-04-06 15:00 | 12113 | 3.7306 | 90.985 | 74.6386 | 3549.9699
2036-04-07 16:00 | 14928.5 | 4.8892 | 90.6297 | 74.6386 | 4375.1115
2036-04-08 17:00 | 13973.9 | 4.4516 | 91.1061 | 74.6386 | 4095.3458
2036-04-09 18:00 | 12151.4 | 3.9055 | 91.1131 | 74.6386 | 3561.2238
2036-04-10 19:00 | 10820.8 | 3.4129 | 91.1911 | 74.6386 | 3171.2634
2036-04-11 20:00 | 9746.5 | 3.0989 | 91.0535 | 74.6386 | 2856.4172
2036-04-12 21:00 | 8941.99 | 2.8436 | 90.9488 | 74.6386 | 2620.6386
2036-04-13 22:00 | 8787.8 | 2.709 | 91.0395 | 74.6386 | 2575.4499
2036-04-14 23:00 | 6586.13 | 1.9306 | 91.3414 | 74.6386 | 1930.2042
2036-04-16 | 6151.82 | 1.8544 | 90.8973 | 74.6386 | 1802.9205
2036-04-17 01:00 | 5749.2 | 1.7787 | 90.5498 | 74.6386 | 1684.9242
2036-04-18 02:00 | 5714.45 | 1.7618 | 90.4718 | 74.6386 | 1674.74
2036-04-19 03:00 | 5938.92 | 1.8894 | 90.1509 | 74.6386 | 1740.5256
2036-04-20 04:00 | 6333.66 | 1.9824 | 90.1998 | 74.6386 | 1856.2125
2036-04-21 05:00 | 6960.16 | 2.3428 | 89.6531 | 74.6386 | 2039.8215
2036-04-22 06:00 | 7120.42 | 2.3103 | 89.9378 | 74.6386 | 2086.7891
2036-04-23 07:00 | 8520.01 | 2.8166 | 89.811 | 74.6386 | 2496.9684
2036-04-24 08:00 | 10160.4 | 3.1778 | 90.3203 | 74.6386 | 2977.7193
2036-04-25 09:00 | 11539.4 | 3.7715 | 90.1683 | 74.6386 | 3381.8643
2036-04-26 10:00 | 13132 | 4.3618 | 90.2393 | 74.6386 | 3848.6093
2036-04-27 11:00 | 13899.8 | 4.6855 | 90.3659 | 74.6386 | 4073.6293
2036-04-28 12:00 | 15607.6 | 5.0575 | 90.8564 | 74.6386 | 4574.136
2036-04-29 13:00 | 15009 | 4.8433 | 91.1644 | 74.6386 | 4398.7037
2036-04-30 14:00 | 15553.6 | 4.9679 | 91.3846 | 74.6386 | 4558.3102
2036-05-01 15:00 | 17168.9 | 5.4426 | 91.5887 | 74.6386 | 5031.7079
2036-05-02 16:00 | 15081 | 4.8852 | 91.6622 | 74.6386 | 4419.8048
2036-05-03 17:00 | 15396.3 | 4.928 | 91.754 | 74.6386 | 4512.2101
2036-05-04 18:00 | 13510.3 | 4.238 | 91.9548 | 74.6386 | 3959.4781
2036-05-05 19:00 | 12103.2 | 3.812 | 91.8676 | 74.6386 | 3547.0978
2036-05-06 20:00 | 10075.3 | 3.0418 | 92.0711 | 74.6386 | 2952.779
2036-05-07 21:00 | 9158.5 | 2.7954 | 91.7661 | 74.6386 | 2684.0914
2036-05-08 22:00 | 7452.18 | 2.1952 | 91.8683 | 74.6386 | 2184.0184
2036-05-09 23:00 | 6821.46 | 2.0735 | 91.3835 | 74.6386 | 1999.1726
2036-05-11 | 6321.41 | 1.9318 | 91.1456 | 74.6386 | 1852.6224
2036-05-12 01:00 | 6054.11 | 1.864 | 90.9291 | 74.6386 | 1774.2845
2036-05-13 02:00 | 5994.88 | 1.8651 | 90.7215 | 74.6386 | 1756.9259
2036-05-14 03:00 | 6196.95 | 1.9726 | 90.4355 | 74.6386 | 1816.1468
2036-05-15 04:00 | 6546.99 | 2.0711 | 90.4232 | 74.6386 | 1918.7334
2036-05-16 05:00 | 7160.37 | 2.4062 | 89.9507 | 74.6386 | 2098.4973
2036-05-17 06:00 | 7527.42 | 2.3576 | 90.4758 | 74.6386 | 2206.069
2036-05-18 07:00 | 9176.37 | 2.8749 | 90.4886 | 74.6386 | 2689.3286
2036-05-19 08:00 | 10144.4 | 3.1694 | 90.6342 | 74.6386 | 2973.0302
2036-05-20 09:00 | 11067.6 | 3.7656 | 90.1494 | 74.6386 | 3243.5934
2036-05-21 10:00 | 12834.7 | 4.2426 | 90.4907 | 74.6386 | 3761.4793
2036-05-22 11:00 | 13659.1 | 4.4433 | 90.8194 | 74.6386 | 4003.0871
2036-05-23 12:00 | 11617.8 | 3.7989 | 90.9759 | 74.6386 | 3404.8411
2036-05-24 13:00 | 10448.7 | 3.3476 | 91.0904 | 74.6386 | 3062.2117
2036-05-25 14:00 | 10465.7 | 3.3476 | 91.014 | 74.6386 | 3067.1939
2036-05-26 15:00 | 12447 | 4.0977 | 90.7699 | 74.6386 | 3647.8556
2036-05-27 16:00 | 13387.4 | 4.3232 | 91.0245 | 74.6386 | 3923.4596
2036-05-28 17:00 | 13413.8 | 4.2688 | 91.2444 | 74.6386 | 3931.1967
2036-05-29 18:00 | 12332.4 | 3.808 | 91.5536 | 74.6386 | 3614.2697
2036-05-30 19:00 | 11543.6 | 3.5357 | 91.6096 | 74.6386 | 3383.0952
2036-05-31 20:00 | 9279.9 | 2.872 | 91.5029 | 74.6386 | 2719.6702
2036-06-01 21:00 | 8616.44 | 2.6373 | 91.4092 | 74.6386 | 2525.2293
2036-06-02 22:00 | 6848.37 | 2.0097 | 91.5836 | 74.6386 | 2007.0591
2036-06-03 23:00 | 6287.89 | 1.9074 | 91.0945 | 74.6386 | 1842.7987
2036-06-05 | 5828.38 | 1.863 | 90.5266 | 74.6386 | 1708.1296
2036-06-06 01:00 | 5948.82 | 1.7822 | 90.8868 | 74.6386 | 1743.427
2036-06-07 02:00 | 5851.67 | 1.8227 | 90.5135 | 74.6386 | 1714.9552
2036-06-08 03:00 | 6215.58 | 1.9516 | 90.374 | 74.6386 | 1821.6067
2036-06-09 04:00 | 6265.21 | 2.063 | 89.9886 | 74.6386 | 1836.1518
2036-06-10 05:00 | 7199.79 | 2.3818 | 89.917 | 74.6386 | 2110.0502
2036-06-11 06:00 | 7302.17 | 2.3493 | 90.1521 | 74.6386 | 2140.0548
2036-06-12 07:00 | 8673.94 | 2.7924 | 90.1515 | 74.6386 | 2542.0809
2036-06-13 08:00 | 9908.15 | 3.1631 | 90.31 | 74.6386 | 2903.7921
2036-06-14 09:00 | 11300.8 | 3.7665 | 90.1361 | 74.6386 | 3311.9375
2036-06-15 10:00 | 12987.7 | 4.3375 | 90.3008 | 74.6386 | 3806.3191
2036-06-16 11:00 | 12811.5 | 4.2495 | 90.5751 | 74.6386 | 3754.68
2036-06-17 12:00 | 13211.2 | 4.2168 | 90.9911 | 74.6386 | 3871.8205
2036-06-18 13:00 | 11228.2 | 3.6344 | 91.0163 | 74.6386 | 3290.6606
2036-06-19 14:00 | 10794.1 | 3.3677 | 91.2429 | 74.6386 | 3163.4384
2036-06-20 15:00 | 11868.7 | 3.919 | 90.7696 | 74.6386 | 3478.3726
2036-06-21 16:00 | 13822.7 | 4.3372 | 91.1988 | 74.6386 | 4051.0335
2036-06-22 17:00 | 13798.9 | 4.4941 | 91.0971 | 74.6386 | 4044.0584
2036-06-23 18:00 | 12964.1 | 3.983 | 91.6264 | 74.6386 | 3799.4027
2036-06-24 19:00 | 11559.7 | 3.7167 | 91.3008 | 74.6386 | 3387.8136
2036-06-25 20:00 | 10077.3 | 3.0007 | 91.8344 | 74.6386 | 2953.3651
2036-06-26 21:00 | 9293.32 | 2.8185 | 91.5658 | 74.6386 | 2723.6032
2036-06-27 22:00 | 7368.87 | 2.2107 | 91.5163 | 74.6386 | 2159.6026
2036-06-28 23:00 | 6928.96 | 2.0839 | 91.2751 | 74.6386 | 2030.6777
2036-06-30 | 6302.12 | 1.9722 | 90.8008 | 74.6386 | 1846.9691
2036-07-01 01:00 | 6139.75 | 1.8913 | 90.7871 | 74.6386 | 1799.3831
2036-07-02 02:00 | 6116.35 | 1.9061 | 90.6019 | 74.6386 | 1792.5252
2036-07-03 03:00 | 6327.52 | 1.9972 | 90.4263 | 74.6386 | 1854.4131
2036-07-04 04:00 | 6600.12 | 2.1159 | 90.2625 | 74.6386 | 1934.3042
2036-07-05 05:00 | 7223.53 | 2.4204 | 89.911 | 74.6386 | 2117.0077
2036-07-06 06:00 | 7703.81 | 2.4107 | 90.423 | 74.6386 | 2257.7638
2036-07-07 07:00 | 9051.65 | 2.8895 | 90.2985 | 74.6386 | 2652.7768
2036-07-08 08:00 | 9873.89 | 3.16 | 90.3846 | 74.6386 | 2893.7515
2036-07-09 09:00 | 11207.8 | 3.7202 | 90.2295 | 74.6386 | 3284.6819
2036-07-10 10:00 | 12696.2 | 4.2973 | 90.2498 | 74.6386 | 3720.8889
2036-07-11 11:00 | 13873 | 4.5463 | 90.6846 | 74.6386 | 4065.775
2036-07-12 12:00 | 14537.2 | 4.7673 | 90.9006 | 74.6386 | 4260.4328
2036-07-13 13:00 | 15546.9 | 4.9294 | 91.3471 | 74.6386 | 4556.3466
2036-07-14 14:00 | 16249.2 | 5.1774 | 91.5337 | 74.6386 | 4762.1704
2036-07-15 15:00 | 17407.1 | 5.6085 | 91.6571 | 74.6386 | 5101.5174
2036-07-16 16:00 | 17931 | 5.6905 | 91.9912 | 74.6386 | 5255.0574
2036-07-17 17:00 | 16809.4 | 5.4226 | 92.0655 | 74.6386 | 4926.3488
2036-07-18 18:00 | 14703.6 | 4.6103 | 92.3439 | 74.6386 | 4309.1998
2036-07-19 19:00 | 13100.5 | 4.1195 | 92.2411 | 74.6386 | 3839.3776
2036-07-20 20:00 | 10916.2 | 3.3146 | 92.3901 | 74.6386 | 3199.2224
2036-07-21 21:00 | 9714.38 | 3.0058 | 92.0325 | 74.6386 | 2847.0037
2036-07-22 22:00 | 8111.44 | 2.3687 | 92.2779 | 74.6386 | 2377.2284
2036-07-23 23:00 | 7186.58 | 2.2031 | 91.6528 | 74.6386 | 2106.1787
2036-07-25 | 6806.04 | 2.0934 | 91.416 | 74.6386 | 1994.6534
2036-07-26 01:00 | 6593.02 | 2.0196 | 91.2812 | 74.6386 | 1932.2234
2036-07-27 02:00 | 6415.04 | 2.0002 | 91.0166 | 74.6386 | 1880.0626
2036-07-28 03:00 | 6396.67 | 2.0673 | 90.627 | 74.6386 | 1874.6789
2036-07-29 04:00 | 6678.7 | 2.1343 | 90.6113 | 74.6386 | 1957.3338
2036-07-30 05:00 | 7384.26 | 2.4463 | 90.2903 | 74.6386 | 2164.113
2036-07-31 06:00 | 7595.55 | 2.4004 | 90.6367 | 74.6386 | 2226.036
2036-08-01 07:00 | 9163.69 | 2.8896 | 90.6473 | 74.6386 | 2685.6124
2036-08-02 08:00 | 10278.2 | 3.2227 | 90.7929 | 74.6386 | 3012.2431
2036-08-03 09:00 | 11200 | 3.7365 | 90.4734 | 74.6386 | 3282.396
2036-08-04 10:00 | 12938.8 | 4.1919 | 90.8201 | 74.6386 | 3791.988
2036-08-05 11:00 | 13474.3 | 4.4997 | 90.8116 | 74.6386 | 3948.9275
2036-08-06 12:00 | 14510.7 | 4.6441 | 91.2923 | 74.6386 | 4252.6664
2036-08-07 13:00 | 14777 | 4.7123 | 91.5026 | 74.6386 | 4330.7112
2036-08-08 14:00 | 15082.9 | 4.9779 | 91.3986 | 74.6386 | 4420.3616
2036-08-09 15:00 | 16952.9 | 5.5418 | 91.5887 | 74.6386 | 4968.4045
2036-08-10 16:00 | 15899.9 | 5.1311 | 91.9052 | 74.6386 | 4659.8007
2036-08-11 17:00 | 15881.7 | 5.0777 | 92.044 | 74.6386 | 4654.4668
2036-08-12 18:00 | 13704.4 | 4.3548 | 92.1528 | 74.6386 | 4016.3632
2036-08-13 19:00 | 12656.4 | 3.8875 | 92.3236 | 74.6386 | 3709.2247
2036-08-14 20:00 | 10227.4 | 3.1298 | 92.2573 | 74.6386 | 2997.3551
2036-08-15 21:00 | 9096.88 | 2.8253 | 91.9161 | 74.6386 | 2666.0324
2036-08-16 22:00 | 7386.54 | 2.1924 | 92.0652 | 74.6386 | 2164.7812
2036-08-17 23:00 | 6023.32 | 1.829 | 91.635 | 74.6386 | 1765.2608
2036-08-19 | 5440.14 | 1.6735 | 91.2802 | 74.6386 | 1594.3477
2036-08-20 01:00 | 4957.35 | 1.5531 | 90.9306 | 74.6386 | 1452.8559
2036-08-21 02:00 | 4452.18 | 1.4421 | 90.5107 | 74.6386 | 1304.8052
2036-08-22 03:00 | 4068.29 | 1.2929 | 90.4676 | 74.6386 | 1192.2981
2036-08-23 04:00 | 3947.69 | 1.2711 | 90.2097 | 74.6386 | 1156.9537
2036-08-24 05:00 | 3953.8 | 1.2621 | 90.1383 | 74.6386 | 1158.7444
2036-08-25 06:00 | 5669.77 | 1.8323 | 89.9421 | 74.6386 | 1661.6456
2036-08-26 07:00 | 7381.82 | 2.4758 | 89.7064 | 74.6386 | 2163.3979
2036-08-27 08:00 | 6962.92 | 2.3022 | 89.9307 | 74.6386 | 2040.6304
2036-08-28 09:00 | 8137.65 | 2.658 | 90.027 | 74.6386 | 2384.9098
2036-08-29 10:00 | 9659.86 | 3.2126 | 89.9776 | 74.6386 | 2831.0255
2036-08-30 11:00 | 11035.2 | 3.7057 | 90.0791 | 74.6386 | 3234.0979
2036-08-31 12:00 | 11854.3 | 3.844 | 90.5124 | 74.6386 | 3474.1524
2036-09-01 13:00 | 11038.7 | 3.5384 | 90.7495 | 74.6386 | 3235.1236
2036-09-02 14:00 | 12248.3 | 3.9544 | 90.7408 | 74.6386 | 3589.6224
2036-09-03 15:00 | 13538.7 | 4.3001 | 90.9846 | 74.6386 | 3967.8013
2036-09-04 16:00 | 15842.1 | 5.1923 | 90.9356 | 74.6386 | 4642.8612
2036-09-05 17:00 | 14475.1 | 4.4783 | 91.6429 | 74.6386 | 4242.233
2036-09-06 18:00 | 12444.1 | 3.9476 | 91.5226 | 74.6386 | 3647.0057
2036-09-07 19:00 | 10672.4 | 3.4723 | 91.2579 | 74.6386 | 3127.7717
2036-09-08 20:00 | 9514.04 | 3.053 | 91.2374 | 74.6386 | 2788.2899
2036-09-09 21:00 | 8758.7 | 2.7314 | 91.3187 | 74.6386 | 2566.9216
2036-09-10 22:00 | 8105.62 | 2.522 | 91.1887 | 74.6386 | 2375.5227
2036-09-11 23:00 | 5686.38 | 1.6291 | 91.7075 | 74.6386 | 1666.5135
2036-09-13 | 4803.41 | 1.4298 | 91.1367 | 74.6386 | 1407.7405
2036-09-14 01:00 | 4098.29 | 1.3069 | 90.4003 | 74.6386 | 1201.0902
2036-09-15 02:00 | 3595.47 | 1.1582 | 90.147 | 74.6386 | 1053.7282
2036-09-16 03:00 | 3442.45 | 1.042 | 90.4419 | 74.6386 | 1008.8825
2036-09-17 04:00 | 3158.79 | 1.0044 | 89.9017 | 74.6386 | 925.75
2036-09-18 05:00 | 3149.81 | 1.0317 | 89.5502 | 74.6386 | 923.1182
2036-09-19 06:00 | 5087.11 | 1.5861 | 89.8081 | 74.6386 | 1490.8848
2036-09-20 07:00 | 6798.64 | 2.3381 | 89.1556 | 74.6386 | 1992.4847
2036-09-21 08:00 | 7272.27 | 2.3799 | 89.6433 | 74.6386 | 2131.292
2036-09-22 09:00 | 8645.37 | 2.9592 | 89.4072 | 74.6386 | 2533.7078
2036-09-23 10:00 | 10504.7 | 3.5792 | 89.5746 | 74.6386 | 3078.6237
2036-09-24 11:00 | 12395.6 | 4.1211 | 89.9809 | 74.6386 | 3632.7918
2036-09-25 12:00 | 12969.8 | 4.2795 | 90.3039 | 74.6386 | 3801.0732
2036-09-26 13:00 | 13278.6 | 4.4497 | 90.3983 | 74.6386 | 3891.5735
2036-09-27 14:00 | 14055.2 | 4.6686 | 90.6277 | 74.6386 | 4119.1725
2036-09-28 15:00 | 14704.6 | 4.8281 | 90.8909 | 74.6386 | 4309.4929
2036-09-29 16:00 | 16883.6 | 5.5382 | 91.0666 | 74.6386 | 4948.0947
2036-09-30 17:00 | 15454.7 | 4.9481 | 91.5247 | 74.6386 | 4529.3255
2036-10-01 18:00 | 13505.3 | 4.1714 | 91.8784 | 74.6386 | 3958.0127
2036-10-02 19:00 | 11371.3 | 3.5924 | 91.6413 | 74.6386 | 3332.5991
2036-10-03 20:00 | 9808.91 | 3.1168 | 91.4556 | 74.6386 | 2874.7077
2036-10-04 21:00 | 8736.58 | 2.772 | 91.2979 | 74.6386 | 2560.4388
2036-10-05 22:00 | 7723.13 | 2.3701 | 91.3579 | 74.6386 | 2263.426
2036-10-06 23:00 | 4781.11 | 1.353 | 91.8209 | 74.6386 | 1401.205
2036-10-08 | 3246.27 | 1 | 90.8476 | 74.6386 | 951.3878
2036-10-09 01:00 | 3117.26 | 1 | 90.8636 | 74.6386 | 913.5787
2036-10-10 02:00 | 3106.87 | 1 | 93.7135 | 74.6386 | 910.5337
2036-10-11 03:00 | 3142.16 | 1 | 80.9547 | 74.6386 | 920.8762
2036-10-12 04:00 | 3139.45 | 1 | 80.8097 | 74.6386 | 920.082
2036-10-13 05:00 | 3207.92 | 1 | 80.6725 | 74.6386 | 940.1485
2036-10-14 06:00 | 3765.62 | 1.1339 | 90.0066 | 74.6386 | 1103.5943
2036-10-15 07:00 | 5852.82 | 1.9492 | 89.2084 | 74.6386 | 1715.2922
2036-10-16 08:00 | 6285.6 | 2.0716 | 89.3986 | 74.6386 | 1842.1275
2036-10-17 09:00 | 7921.12 | 2.6793 | 89.2834 | 74.6386 | 2321.4511
2036-10-18 10:00 | 10316 | 3.461 | 89.476 | 74.6386 | 3023.3212
2036-10-19 11:00 | 11652.3 | 3.9242 | 89.7145 | 74.6386 | 3414.952
2036-10-20 12:00 | 12483.9 | 4.1874 | 90.0012 | 74.6386 | 3658.6699
2036-10-21 13:00 | 13453.4 | 4.3644 | 90.4486 | 74.6386 | 3942.8023
2036-10-22 14:00 | 14017.6 | 4.583 | 90.6117 | 74.6386 | 4108.153
2036-10-23 15:00 | 15158.6 | 4.8175 | 91.0095 | 74.6386 | 4442.5471
2036-10-24 16:00 | 17398.5 | 5.587 | 91.1299 | 74.6386 | 5098.997
2036-10-25 17:00 | 15899.9 | 5.098 | 91.4547 | 74.6386 | 4659.8007
2036-10-26 18:00 | 14382.9 | 4.2822 | 92.1267 | 74.6386 | 4215.2119
2036-10-27 19:00 | 12300.3 | 3.8049 | 91.8094 | 74.6386 | 3604.8621
2036-10-28 20:00 | 10794.4 | 3.4452 | 91.4729 | 74.6386 | 3163.5264
2036-10-29 21:00 | 9768.41 | 3.1 | 91.3755 | 74.6386 | 2862.8384
2036-10-30 22:00 | 9020.47 | 2.7973 | 91.3807 | 74.6386 | 2643.6388
2036-10-31 23:00 | 6688.99 | 1.9885 | 91.5717 | 74.6386 | 1960.3495
2036-11-02 | 5886.67 | 1.7464 | 91.3362 | 74.6386 | 1725.2127
2036-11-03 01:00 | 5556.6 | 1.6717 | 91.0233 | 74.6386 | 1628.4787
2036-11-04 02:00 | 5321.4 | 1.5882 | 90.9453 | 74.6386 | 1559.5484
2036-11-05 03:00 | 5437.33 | 1.6911 | 90.4978 | 74.6386 | 1593.5241
2036-11-06 04:00 | 5508.85 | 1.8271 | 89.9156 | 74.6386 | 1614.4846
2036-11-07 05:00 | 6098.93 | 2.0254 | 89.8411 | 74.6386 | 1787.4199
2036-11-08 06:00 | 6176.49 | 1.9683 | 90.1299 | 74.6386 | 1810.1505
2036-11-09 07:00 | 7660.52 | 2.5072 | 89.9148 | 74.6386 | 2245.0768
2036-11-10 08:00 | 8460.4 | 2.7511 | 90.0502 | 74.6386 | 2479.4985
2036-11-11 09:00 | 10073.9 | 3.5269 | 89.6287 | 74.6386 | 2952.3687
2036-11-12 10:00 | 12347.3 | 4.1977 | 89.9863 | 74.6386 | 3618.6364
2036-11-13 11:00 | 14147.5 | 4.7155 | 90.3862 | 74.6386 | 4146.223
2036-11-14 12:00 | 15350.9 | 5.072 | 90.7432 | 74.6386 | 4498.9047
2036-11-15 13:00 | 15909.5 | 5.1334 | 91.1804 | 74.6386 | 4662.6142
2036-11-16 14:00 | 16315.5 | 5.292 | 91.3661 | 74.6386 | 4781.601
2036-11-17 15:00 | 17569.2 | 5.7271 | 91.5161 | 74.6386 | 5149.0242
2036-11-18 16:00 | 18128.7 | 5.7457 | 91.9425 | 74.6386 | 5312.9975
2036-11-19 17:00 | 17497.8 | 5.6012 | 92.0645 | 74.6386 | 5128.099
2036-11-20 18:00 | 15180.2 | 4.7792 | 92.2904 | 74.6386 | 4448.8775
2036-11-21 19:00 | 14108.3 | 4.2051 | 92.6426 | 74.6386 | 4134.7346
2036-11-22 20:00 | 11439 | 3.4569 | 92.4682 | 74.6386 | 3352.44
2036-11-23 21:00 | 9678.96 | 3.0615 | 91.9097 | 74.6386 | 2836.6232
2036-11-24 22:00 | 7588.53 | 2.2822 | 92.0425 | 74.6386 | 2223.9786
2036-11-25 23:00 | 6991.91 | 2.0971 | 91.7671 | 74.6386 | 2049.1265
2036-11-27 | 6386.07 | 1.956 | 91.389 | 74.6386 | 1871.5724
2036-11-28 01:00 | 6042.9 | 1.863 | 91.1491 | 74.6386 | 1770.9992
2036-11-29 02:00 | 5671.62 | 1.7405 | 91.0317 | 74.6386 | 1662.1877
2036-11-30 03:00 | 5686.29 | 1.8688 | 90.3767 | 74.6386 | 1666.4871
2036-12-01 04:00 | 5834.44 | 1.8689 | 90.4612 | 74.6386 | 1709.9056
2036-12-02 05:00 | 6447.41 | 2.0689 | 90.3718 | 74.6386 | 1889.5493
2036-12-03 06:00 | 6481.42 | 2.0606 | 90.4254 | 74.6386 | 1899.5167
2036-12-04 07:00 | 7958.89 | 2.575 | 90.262 | 74.6386 | 2332.5204
2036-12-05 08:00 | 8694.23 | 2.858 | 90.2303 | 74.6386 | 2548.0273
2036-12-06 09:00 | 11027.3 | 3.6237 | 90.3255 | 74.6386 | 3231.7826
2036-12-07 10:00 | 12580.2 | 4.2669 | 90.3183 | 74.6386 | 3686.8927
2036-12-08 11:00 | 14195.3 | 4.743 | 90.6571 | 74.6386 | 4160.2318
2036-12-09 12:00 | 15264.2 | 5.0707 | 90.9589 | 74.6386 | 4473.4954
2036-12-10 13:00 | 15832.2 | 5.0985 | 91.4265 | 74.6386 | 4639.9598
2036-12-11 14:00 | 16538.1 | 5.3469 | 91.6088 | 74.6386 | 4846.8387
2036-12-12 15:00 | 17943.2 | 5.6889 | 91.942 | 74.6386 | 5258.6328
2036-12-13 16:00 | 17605.1 | 5.6681 | 92.0636 | 74.6386 | 5159.5455
2036-12-14 17:00 | 17222.2 | 5.3312 | 92.4909 | 74.6386 | 5047.3286
2036-12-15 18:00 | 14722.1 | 4.6305 | 92.4569 | 74.6386 | 4314.6216
2036-12-16 19:00 | 13678.4 | 4.2498 | 92.4571 | 74.6386 | 4008.7433
2036-12-17 20:00 | 11367.2 | 3.4785 | 92.4876 | 74.6386 | 3331.3975
2036-12-18 21:00 | 10104.9 | 3.1728 | 92.0863 | 74.6386 | 2961.4539
2036-12-19 22:00 | 8259.37 | 2.4524 | 92.315 | 74.6386 | 2420.5824
2036-12-20 23:00 | 7456.99 | 2.2636 | 91.8827 | 74.6386 | 2185.428
2036-12-22 | 6582.28 | 2.0611 | 91.4379 | 74.6386 | 1929.0758
2036-12-23 01:00 | 6255.48 | 1.9286 | 91.3544 | 74.6386 | 1833.3002
2036-12-24 02:00 | 6202.5 | 1.8882 | 91.2955 | 74.6386 | 1817.7733
2036-12-25 03:00 | 6548.25 | 2.0532 | 90.9426 | 74.6386 | 1919.1026
2036-12-26 04:00 | 6417.84 | 2.1082 | 90.5325 | 74.6386 | 1880.8832
2036-12-27 05:00 | 7371.86 | 2.3761 | 90.5919 | 74.6386 | 2160.4789
2036-12-28 06:00 | 7453.95 | 2.3716 | 90.704 | 74.6386 | 2184.5371
2036-12-29 07:00 | 8825.82 | 2.7512 | 90.8536 | 74.6386 | 2586.5925
2036-12-30 08:00 | 8051.44 | 2.4814 | 91.0313 | 74.6386 | 2359.6441
2036-12-31 09:00 | 9345.89 | 3.1569 | 90.3378 | 74.6386 | 2739.01
2037-01-01 10:00 | 11295.4 | 3.7737 | 90.4926 | 74.6386 | 3310.355
2037-01-02 11:00 | 13489.1 | 4.3832 | 90.8732 | 74.6386 | 3953.265
2037-01-03 12:00 | 14513.8 | 4.6386 | 91.2554 | 74.6386 | 4253.5749
2037-01-04 13:00 | 14476 | 4.8214 | 91.1713 | 74.6386 | 4242.4968
2037-01-05 14:00 | 14823.7 | 4.8938 | 91.3796 | 74.6386 | 4344.3976
2037-01-06 15:00 | 17078.6 | 5.4365 | 91.7709 | 74.6386 | 5005.2436
2037-01-07 16:00 | 15941.4 | 5.3911 | 91.5964 | 74.6386 | 4671.9632
2037-01-08 17:00 | 15381.5 | 4.9977 | 91.9492 | 74.6386 | 4507.8727
2037-01-09 18:00 | 13283.4 | 4.2207 | 92.1315 | 74.6386 | 3892.9803
2037-01-10 19:00 | 11454.7 | 3.6602 | 91.9874 | 74.6386 | 3357.0412
2037-01-11 20:00 | 9363.06 | 2.9224 | 92.0135 | 74.6386 | 2744.042
2037-01-12 21:00 | 8623.6 | 2.6153 | 91.9944 | 74.6386 | 2527.3277
2037-01-13 22:00 | 7097.92 | 2.0329 | 92.2713 | 74.6386 | 2080.195
2037-01-14 23:00 | 6522.19 | 1.9253 | 91.7903 | 74.6386 | 1911.4652
2037-01-16 | 5965.85 | 1.8285 | 91.3047 | 74.6386 | 1748.418
2037-01-17 01:00 | 5641.18 | 1.7316 | 91.1326 | 74.6386 | 1653.2667
2037-01-18 02:00 | 5564.61 | 1.7312 | 90.898 | 74.6386 | 1630.8262
2037-01-19 03:00 | 5831.02 | 1.8334 | 90.6946 | 74.6386 | 1708.9033
2037-01-20 04:00 | 5843.88 | 1.956 | 90.1716 | 74.6386 | 1712.6722
2037-01-21 05:00 | 6669.53 | 2.2442 | 90.067 | 74.6386 | 1954.6463
2037-01-22 06:00 | 6964.47 | 2.1928 | 90.5583 | 74.6386 | 2041.0847
2037-01-23 07:00 | 8388.11 | 2.6961 | 90.4153 | 74.6386 | 2458.3124
2037-01-24 08:00 | 8953.96 | 3.0458 | 90.1193 | 74.6386 | 2624.1466
2037-01-25 09:00 | 11409.4 | 3.7863 | 90.3853 | 74.6386 | 3343.7651
2037-01-26 10:00 | 13368 | 4.379 | 90.7097 | 74.6386 | 3917.7741
2037-01-27 11:00 | 14464 | 4.868 | 90.7907 | 74.6386 | 4238.98
2037-01-28 12:00 | 14944.5 | 4.5586 | 91.7586 | 74.6386 | 4379.8006
2037-01-29 13:00 | 13476.8 | 4.3031 | 91.6011 | 74.6386 | 3949.6602
2037-01-30 14:00 | 14119 | 4.6483 | 91.4094 | 74.6386 | 4137.8704
2037-01-31 15:00 | 16318.6 | 5.2892 | 91.5956 | 74.6386 | 4782.5096
2037-02-01 16:00 | 15582.7 | 4.9391 | 91.9866 | 74.6386 | 4566.8386
2037-02-02 17:00 | 14201.2 | 4.5352 | 92.005 | 74.6386 | 4161.9609
2037-02-03 18:00 | 12819.6 | 4.0138 | 92.1086 | 74.6386 | 3757.0539
2037-02-04 19:00 | 11848 | 3.6915 | 92.0735 | 74.6386 | 3472.306
2037-02-05 20:00 | 9732.19 | 2.9742 | 92.1476 | 74.6386 | 2852.2233
2037-02-06 21:00 | 8516.2 | 2.7383 | 91.5489 | 74.6386 | 2495.8518
2037-02-07 22:00 | 7118.18 | 2.0619 | 92.1418 | 74.6386 | 2086.1326
2037-02-08 23:00 | 5781.35 | 1.7369 | 91.6214 | 74.6386 | 1694.3464
2037-02-10 | 5344.94 | 1.6091 | 91.362 | 74.6386 | 1566.4473
2037-02-11 01:00 | 5200.32 | 1.5724 | 91.1439 | 74.6386 | 1524.0633
2037-02-12 02:00 | 4602.02 | 1.447 | 90.7119 | 74.6386 | 1348.7189
2037-02-13 03:00 | 4358.08 | 1.3885 | 90.4488 | 74.6386 | 1277.2272
2037-02-14 04:00 | 3967.98 | 1.3204 | 89.9935 | 74.6386 | 1162.9001
2037-02-15 05:00 | 4059.67 | 1.2917 | 90.1895 | 74.6386 | 1189.7718
2037-02-16 06:00 | 5882.03 | 1.8583 | 90.1483 | 74.6386 | 1723.8528
2037-02-17 07:00 | 6921.86 | 2.3056 | 89.8119 | 74.6386 | 2028.5969
2037-02-18 08:00 | 6875.14 | 2.1694 | 90.2947 | 74.6386 | 2014.9046
2037-02-19 09:00 | 7886.04 | 2.5846 | 90.0305 | 74.6386 | 2311.1702
2037-02-20 10:00 | 8720.73 | 2.9747 | 89.8235 | 74.6386 | 2555.7937
2037-02-21 11:00 | 11204.4 | 3.6928 | 90.1712 | 74.6386 | 3283.6855
2037-02-22 12:00 | 11964.4 | 3.9436 | 90.3945 | 74.6386 | 3506.4195
2037-02-23 13:00 | 12211.2 | 3.8624 | 90.876 | 74.6386 | 3578.7494
2037-02-24 14:00 | 12193.3 | 4.0103 | 90.7177 | 74.6386 | 3573.5035
2037-02-25 15:00 | 11141.8 | 3.6762 | 90.7759 | 74.6386 | 3265.3392
2037-02-26 16:00 | 13470.5 | 4.4205 | 90.8067 | 74.6386 | 3947.8138
2037-02-27 17:00 | 12202.3 | 3.8449 | 91.2827 | 74.6386 | 3576.1411
2037-02-28 18:00 | 10674.1 | 3.446 | 91.1202 | 74.6386 | 3128.2699
2037-03-01 19:00 | 9873.19 | 3.0391 | 91.3725 | 74.6386 | 2893.5464
2037-03-02 20:00 | 9138.05 | 2.9001 | 91.0616 | 74.6386 | 2678.0981
2037-03-03 21:00 | 8554.82 | 2.6886 | 91.0683 | 74.6386 | 2507.1703
2037-03-04 22:00 | 8051.65 | 2.5202 | 91.0015 | 74.6386 | 2359.7057
2037-03-05 23:00 | 5744.41 | 1.5869 | 91.9099 | 74.6386 | 1683.5204
2037-03-07 | 5132.1 | 1.5269 | 91.0701 | 74.6386 | 1504.07
2037-03-08 01:00 | 4645.7 | 1.4568 | 90.4831 | 74.6386 | 1361.5203
2037-03-09 02:00 | 4177.52 | 1.2933 | 90.4384 | 74.6386 | 1224.3103
2037-03-10 03:00 | 3950.5 | 1.2489 | 90.1431 | 74.6386 | 1157.7773
2037-03-11 04:00 | 3768.78 | 1.2054 | 89.9191 | 74.6386 | 1104.5204
2037-03-12 05:00 | 4022.14 | 1.2373 | 90.1124 | 74.6386 | 1178.7729
2037-03-13 06:00 | 5654.88 | 1.8385 | 89.6376 | 74.6386 | 1657.2817
2037-03-14 07:00 | 7100.63 | 2.388 | 89.4579 | 74.6386 | 2080.9892
2037-03-15 08:00 | 6874.9 | 2.2477 | 89.7844 | 74.6386 | 2014.8343
2037-03-16 09:00 | 8027.28 | 2.6596 | 89.7156 | 74.6386 | 2352.5635
2037-03-17 10:00 | 10213.8 | 3.3779 | 89.8196 | 74.6386 | 2993.3693
2037-03-18 11:00 | 11386.7 | 3.893 | 89.8112 | 74.6386 | 3337.1124
2037-03-19 12:00 | 12721.5 | 4.274 | 90.1347 | 74.6386 | 3728.3036
2037-03-20 13:00 | 13123.4 | 4.2831 | 90.5518 | 74.6386 | 3846.0889
2037-03-21 14:00 | 13512.1 | 4.3164 | 90.8887 | 74.6386 | 3960.0056
2037-03-22 15:00 | 13944.8 | 4.6018 | 90.8078 | 74.6386 | 4086.8175
2037-03-23 16:00 | 16130.1 | 5.1735 | 91.1495 | 74.6386 | 4727.2657
2037-03-24 17:00 | 14815.8 | 4.7603 | 91.4084 | 74.6386 | 4342.0824
2037-03-25 18:00 | 13071.8 | 4.125 | 91.6204 | 74.6386 | 3830.9664
2037-03-26 19:00 | 11667.2 | 3.7024 | 91.5159 | 74.6386 | 3419.3188
2037-03-27 20:00 | 10989.6 | 3.4049 | 91.6121 | 74.6386 | 3220.7338
2037-03-28 21:00 | 10419.8 | 3.2142 | 91.5802 | 74.6386 | 3053.7419
2037-03-29 22:00 | 9417.56 | 2.9978 | 91.2473 | 74.6386 | 2760.0144
2037-03-30 23:00 | 7656.78 | 2.1914 | 91.9604 | 74.6386 | 2243.9807
2037-04-01 | 6840.13 | 2.0403 | 91.4312 | 74.6386 | 2004.6442
2037-04-02 01:00 | 6026.66 | 1.9268 | 90.7367 | 74.6386 | 1766.2397
2037-04-03 02:00 | 6029.41 | 1.7998 | 91.1051 | 74.6386 | 1767.0456
2037-04-04 03:00 | 5862.5 | 1.9191 | 90.2963 | 74.6386 | 1718.1291
2037-04-05 04:00 | 6219.82 | 1.9849 | 90.3752 | 74.6386 | 1822.8493
2037-04-06 05:00 | 6977.08 | 2.3029 | 90.083 | 74.6386 | 2044.7803
2037-04-07 06:00 | 6802.89 | 2.1953 | 90.2618 | 74.6386 | 1993.7303
2037-04-08 07:00 | 8534.36 | 2.6529 | 90.5217 | 74.6386 | 2501.174
2037-04-09 08:00 | 9119.34 | 2.9342 | 90.373 | 74.6386 | 2672.6147
2037-04-10 09:00 | 10913.8 | 3.7289 | 90.0456 | 74.6386 | 3198.519
2037-04-11 10:00 | 12516.7 | 4.2619 | 90.2459 | 74.6386 | 3668.2827
2037-04-12 11:00 | 14053.7 | 4.6969 | 90.5974 | 74.6386 | 4118.7329
2037-04-13 12:00 | 14912.1 | 4.8274 | 91.0806 | 74.6386 | 4370.3051
2037-04-14 13:00 | 14764.9 | 4.8025 | 91.268 | 74.6386 | 4327.165
2037-04-15 14:00 | 15464 | 5.0101 | 91.4421 | 74.6386 | 4532.051
2037-04-16 15:00 | 17171.8 | 5.6055 | 91.5501 | 74.6386 | 5032.5578
2037-04-17 16:00 | 15934.7 | 5.1947 | 91.8006 | 74.6386 | 4669.9996
2037-04-18 17:00 | 16078.5 | 5.1639 | 91.9717 | 74.6386 | 4712.1432
2037-04-19 18:00 | 14392.4 | 4.1742 | 92.8425 | 74.6386 | 4217.9961
2037-04-20 19:00 | 11889.4 | 3.7066 | 92.2455 | 74.6386 | 3484.4392
2037-04-21 20:00 | 9908.3 | 2.8653 | 92.663 | 74.6386 | 2903.8361
2037-04-22 21:00 | 8335.11 | 2.6468 | 91.6894 | 74.6386 | 2442.7796
2037-04-23 22:00 | 6607.02 | 1.9918 | 91.846 | 74.6386 | 1936.3264
2037-04-24 23:00 | 6015.9 | 1.8247 | 91.5131 | 74.6386 | 1763.0863
2037-04-26 | 5628.75 | 1.7053 | 91.297 | 74.6386 | 1649.6238
2037-04-27 01:00 | 5236.86 | 1.665 | 90.7638 | 74.6386 | 1534.7722
2037-04-28 02:00 | 5442.1 | 1.7226 | 90.646 | 74.6386 | 1594.9221
2037-04-29 03:00 | 5839.1 | 1.7966 | 90.7546 | 74.6386 | 1711.2713
2037-04-30 04:00 | 6120.63 | 1.932 | 90.5143 | 74.6386 | 1793.7796
2037-05-01 05:00 | 6652.43 | 2.2652 | 89.9296 | 74.6386 | 1949.6348
2037-05-02 06:00 | 6883.71 | 2.1849 | 90.4339 | 74.6386 | 2017.4163
2037-05-03 07:00 | 7989.95 | 2.6437 | 90.1344 | 74.6386 | 2341.6232
2037-05-04 08:00 | 8904.36 | 2.829 | 90.5093 | 74.6386 | 2609.6103
2037-05-05 09:00 | 10622.9 | 3.5689 | 90.2079 | 74.6386 | 3113.2647
2037-05-06 10:00 | 12391.5 | 4.1853 | 90.3504 | 74.6386 | 3631.5902
2037-05-07 11:00 | 14456.5 | 4.7782 | 90.734 | 74.6386 | 4236.7819
2037-05-08 12:00 | 15505.1 | 5.1375 | 91.0091 | 74.6386 | 4544.0962
2037-05-09 13:00 | 14649.6 | 4.6544 | 91.5787 | 74.6386 | 4293.3739
2037-05-10 14:00 | 16544.9 | 4.972 | 92.1128 | 74.6386 | 4848.8315
2037-05-11 15:00 | 16593.2 | 5.4566 | 91.6624 | 74.6386 | 4862.9869
2037-05-12 16:00 | 14879.3 | 4.8048 | 91.9583 | 74.6386 | 4360.6924
2037-05-13 17:00 | 14641.3 | 4.618 | 92.1013 | 74.6386 | 4290.9415
2037-05-14 18:00 | 12899.6 | 4.1082 | 92.0291 | 74.6386 | 3780.4996
2037-05-15 19:00 | 11985.5 | 3.7296 | 92.127 | 74.6386 | 3512.6033
2037-05-16 20:00 | 10019.2 | 3.0241 | 92.2563 | 74.6386 | 2936.3377
2037-05-17 21:00 | 9058.82 | 2.8221 | 91.8155 | 74.6386 | 2654.8781
2037-05-18 22:00 | 7075.23 | 2.1638 | 91.7863 | 74.6386 | 2073.5452
2037-05-19 23:00 | 6654.65 | 1.9899 | 91.7049 | 74.6386 | 1950.2854
2037-05-21 | 6326.39 | 1.9156 | 91.4171 | 74.6386 | 1854.0819
2037-05-22 01:00 | 5804.57 | 1.8112 | 91.043 | 74.6386 | 1701.1515
2037-05-23 02:00 | 5731.21 | 1.7922 | 90.8753 | 74.6386 | 1679.6518
2037-05-24 03:00 | 6197.33 | 1.9525 | 90.6952 | 74.6386 | 1816.2581
2037-05-25 04:00 | 6168.92 | 2.0433 | 90.2881 | 74.6386 | 1807.932
2037-05-26 05:00 | 7059.69 | 2.3271 | 90.2696 | 74.6386 | 2068.9909
2037-05-27 06:01 | 7063.74 | 2.2646 | 90.4911 | 74.6386 | 2070.1778
2037-05-28 07:01 | 8329.01 | 2.6974 | 90.4126 | 74.6386 | 2440.9919
2037-05-29 08:01 | 8731.82 | 2.7335 | 90.7486 | 74.6386 | 2559.0438
2037-05-30 09:01 | 9984.24 | 3.2851 | 90.4464 | 74.6386 | 2926.0919
2037-05-31 10:01 | 10087.4 | 3.2482 | 90.7294 | 74.6386 | 2956.3251
2037-06-01 11:01 | 12383.4 | 4.1334 | 90.5353 | 74.6386 | 3629.2163
2037-06-02 12:01 | 13457.4 | 4.4017 | 90.8894 | 74.6386 | 3943.9746
2037-06-03 13:01 | 13302.6 | 4.3617 | 91.0782 | 74.6386 | 3898.6072
2037-06-04 14:01 | 14528.5 | 4.5639 | 91.4981 | 74.6386 | 4257.883
2037-06-05 15:01 | 14602.2 | 4.8578 | 91.2391 | 74.6386 | 4279.4824
2037-06-06 16:01 | 14925.4 | 4.7075 | 91.7631 | 74.6386 | 4374.2029
2037-06-07 17:01 | 14582.4 | 4.6844 | 91.7274 | 74.6386 | 4273.6796
2037-06-08 18:01 | 12434.2 | 3.9018 | 91.9629 | 74.6386 | 3644.1043
2037-06-09 19:01 | 11737.4 | 3.5804 | 92.0831 | 74.6386 | 3439.8924
2037-06-10 20:01 | 9678.92 | 2.9545 | 91.9973 | 74.6386 | 2836.6114
2037-06-11 21:01 | 9186.75 | 2.8037 | 91.8226 | 74.6386 | 2692.3707
2037-06-12 22:01 | 7458.91 | 2.199 | 91.9662 | 74.6386 | 2185.9907
2037-06-13 23:01 | 7000.9 | 2.1003 | 91.6162 | 74.6386 | 2051.7613
2037-06-15 00:01 | 6564.67 | 2.0472 | 91.1584 | 74.6386 | 1923.9149
2037-06-16 01:01 | 6057.69 | 1.9611 | 90.7485 | 74.6386 | 1775.3337
2037-06-17 02:01 | 6112.86 | 1.8944 | 90.9452 | 74.6386 | 1791.5024
2037-06-18 03:01 | 6160.52 | 2.0189 | 90.4336 | 74.6386 | 1805.4702
2037-06-19 04:01 | 6302.26 | 2.0825 | 90.3086 | 74.6386 | 1847.0101
2037-06-20 05:01 | 7085.06 | 2.3542 | 90.2149 | 74.6386 | 2076.4261
2037-06-21 06:01 | 7222.17 | 2.2768 | 90.616 | 74.6386 | 2116.6091
2037-06-22 07:01 | 8605.74 | 2.7545 | 90.505 | 74.6386 | 2522.0934
2037-06-23 08:01 | 9050.5 | 2.8783 | 90.6506 | 74.6386 | 2652.4397
2037-06-24 09:01 | 10792 | 3.5641 | 90.4539 | 74.6386 | 3162.823
2037-06-25 10:01 | 12072.8 | 4.0956 | 90.4381 | 74.6386 | 3538.1884
2037-06-26 11:01 | 13399.8 | 4.345 | 90.9481 | 74.6386 | 3927.0937
2037-06-27 12:01 | 14539 | 4.6383 | 91.2771 | 74.6386 | 4260.9603
2037-06-28 13:01 | 14789 | 4.7692 | 91.4149 | 74.6386 | 4334.2281
2037-06-29 14:01 | 15461.9 | 4.9807 | 91.5847 | 74.6386 | 4531.4356
2037-06-30 15:01 | 16319.1 | 5.2712 | 91.7234 | 74.6386 | 4782.6561
2037-07-01 16:01 | 16387.7 | 5.2393 | 91.9798 | 74.6386 | 4802.7608
2037-07-02 17:01 | 15567.5 | 4.9839 | 92.0971 | 74.6386 | 4562.3839
2037-07-03 18:01 | 13465.9 | 4.1944 | 92.3465 | 74.6386 | 3946.4657
2037-07-04 19:01 | 12125.9 | 3.8021 | 92.1989 | 74.6386 | 3553.7505
2037-07-05 20:01 | 10168.5 | 3.1145 | 92.2608 | 74.6386 | 2980.0932
2037-07-06 21:01 | 9276.19 | 2.8678 | 91.9882 | 74.6386 | 2718.5829
2037-07-07 22:01 | 7771.5 | 2.2384 | 92.3695 | 74.6386 | 2277.6018
2037-07-08 23:01 | 7394.35 | 2.1643 | 92.0154 | 74.6386 | 2167.0701
2037-07-10 00:01 | 6729.68 | 2.0746 | 91.444 | 74.6386 | 1972.2745
2037-07-11 01:01 | 6448.31 | 1.9947 | 91.2629 | 74.6386 | 1889.8131
2037-07-12 02:01 | 6492.4 | 1.9979 | 91.1746 | 74.6386 | 1902.7346
2037-07-13 03:01 | 6733.06 | 2.1272 | 90.8768 | 74.6386 | 1973.2651
2037-07-14 04:01 | 6938.37 | 2.2713 | 90.5582 | 74.6386 | 2033.4355
2037-07-15 05:01 | 7708.16 | 2.5909 | 90.3235 | 74.6386 | 2259.0387
2037-07-16 06:01 | 7944.37 | 2.5716 | 90.6161 | 74.6386 | 2328.265
2037-07-17 07:01 | 9366.14 | 2.9968 | 90.7162 | 74.6386 | 2744.9447
2037-07-18 08:01 | 9946.85 | 3.1101 | 90.9987 | 74.6386 | 2915.134
2037-07-19 09:01 | 11545.8 | 3.7403 | 90.8331 | 74.6386 | 3383.74
2037-07-20 10:01 | 12807.5 | 4.2605 | 90.8165 | 74.6386 | 3753.5077
2037-07-21 11:01 | 12449.6 | 4.1281 | 91.031 | 74.6386 | 3648.6176
2037-07-22 12:01 | 12654.8 | 4.0159 | 91.4391 | 74.6386 | 3708.7558
2037-07-23 13:01 | 12731.5 | 3.8446 | 91.8923 | 74.6386 | 3731.2343
2037-07-24 14:01 | 12563.6 | 4.1744 | 91.2475 | 74.6386 | 3682.0277
2037-07-25 15:01 | 12506.5 | 4.0332 | 91.486 | 74.6386 | 3665.2933
2037-07-26 16:01 | 13276.6 | 4.359 | 91.3601 | 74.6386 | 3890.9874
2037-07-27 17:01 | 12890.7 | 4.1186 | 91.6303 | 74.6386 | 3777.8912
2037-07-28 18:01 | 11187.6 | 3.5494 | 91.7101 | 74.6386 | 3278.7619
2037-07-29 19:01 | 10463.7 | 3.3161 | 91.6124 | 74.6386 | 3066.6078
2037-07-30 20:01 | 8756.28 | 2.5729 | 92.1096 | 74.6386 | 2566.2123
2037-07-31 21:01 | 7943.31 | 2.4399 | 91.593 | 74.6386 | 2327.9544
2037-08-01 22:01 | 6214.85 | 1.7786 | 91.9888 | 74.6386 | 1821.3927
2037-08-02 23:01 | 4956.19 | 1.4841 | 91.3916 | 74.6386 | 1452.5159
2037-08-04 00:01 | 4739.81 | 1.4555 | 90.9618 | 74.6386 | 1389.1012
2037-08-05 01:01 | 4396.91 | 1.4105 | 90.467 | 74.6386 | 1288.6071
2037-08-06 02:01 | 4267.41 | 1.3609 | 90.3713 | 74.6386 | 1250.6544
2037-08-07 03:01 | 4153.52 | 1.3448 | 90.135 | 74.6386 | 1217.2766
2037-08-08 04:01 | 3902.37 | 1.3081 | 89.7793 | 74.6386 | 1143.6718
2037-08-09 05:01 | 4071.86 | 1.3054 | 89.9943 | 74.6386 | 1193.3444
2037-08-10 06:01 | 5597.97 | 1.9071 | 89.4878 | 74.6386 | 1640.6031
2037-08-11 07:01 | 6691.25 | 2.2786 | 89.5352 | 74.6386 | 1961.0118
2037-08-12 08:01 | 5553.99 | 1.6536 | 90.618 | 74.6386 | 1627.7138
2037-08-13 09:01 | 5289.91 | 1.6081 | 90.3843 | 74.6386 | 1550.3196
2037-08-14 10:01 | 5688.12 | 1.9672 | 89.3751 | 74.6386 | 1667.0234
2037-08-15 11:01 | 6687.91 | 2.3077 | 89.3855 | 74.6386 | 1960.0329
2037-08-16 12:01 | 7399.14 | 2.5262 | 89.499 | 74.6386 | 2168.4739
2037-08-17 13:01 | 8090.46 | 2.6708 | 89.7803 | 74.6386 | 2371.0798
2037-08-18 14:01 | 9321.62 | 3.0766 | 89.8489 | 74.6386 | 2731.8971
2037-08-19 15:01 | 8895.06 | 2.9574 | 89.9245 | 74.6386 | 2606.8848
2037-08-20 16:01 | 12725.2 | 4.3045 | 89.8401 | 74.6386 | 3729.388
2037-08-21 17:01 | 11238.3 | 3.6939 | 90.3538 | 74.6386 | 3293.6206
2037-08-22 18:01 | 10243.9 | 3.2767 | 90.6286 | 74.6386 | 3002.1907
2037-08-23 19:01 | 8955.14 | 2.8755 | 90.5653 | 74.6386 | 2624.4925
2037-08-24 20:01 | 8524.18 | 2.6319 | 90.7895 | 74.6386 | 2498.1906
2037-08-25 21:01 | 7907.4 | 2.4506 | 90.7305 | 74.6386 | 2317.4302
2037-08-26 22:01 | 7593.37 | 2.3801 | 90.5653 | 74.6386 | 2225.3971
2037-08-27 23:01 | 4635.72 | 1.3638 | 91.0021 | 74.6386 | 1358.5954
2037-08-29 00:01 | 3989.51 | 1.2165 | 90.4692 | 74.6386 | 1169.21
2037-08-30 01:01 | 3479.8 | 1.0851 | 90.1127 | 74.6386 | 1019.8287
2037-08-31 02:01 | 3057.04 | 1 | 89.6693 | 74.6386 | 895.93
2037-09-01 03:01 | 3089.33 | 1 | 93.3947 | 74.6386 | 905.3932
2037-09-02 04:01 | 3070.12 | 1 | 80.6183 | 74.6386 | 899.7634
2037-09-03 05:01 | 3119.49 | 1 | 80.5096 | 74.6386 | 914.2323
2037-09-04 06:01 | 3421.87 | 1.0602 | 89.5827 | 74.6386 | 1002.8511
2037-09-05 07:01 | 5734.51 | 1.8232 | 89.3298 | 74.6386 | 1680.619
2037-09-06 08:01 | 6069.31 | 2.0712 | 88.951 | 74.6386 | 1778.7392
2037-09-07 09:01 | 8061.88 | 2.7648 | 88.9926 | 74.6386 | 2362.7038
2037-09-08 10:01 | 10556.7 | 3.412 | 89.5832 | 74.6386 | 3093.8634
2037-09-09 11:01 | 12546.5 | 4.0605 | 89.8755 | 74.6386 | 3677.0162
2037-09-10 12:01 | 13393 | 4.3377 | 90.204 | 74.6386 | 3925.1008
2037-09-11 13:01 | 13832.1 | 4.591 | 90.287 | 74.6386 | 4053.7883
2037-09-12 14:01 | 14045.1 | 4.6518 | 90.5244 | 74.6386 | 4116.2125
2037-09-13 15:01 | 14388.1 | 4.7156 | 90.7836 | 74.6386 | 4216.7359
2037-09-14 16:01 | 16519.3 | 5.4853 | 90.8382 | 74.6386 | 4841.3289
2037-09-15 17:01 | 14975.9 | 4.8253 | 91.3329 | 74.6386 | 4389.003
2037-09-16 18:01 | 12972.3 | 4.1158 | 91.5291 | 74.6386 | 3801.8058
2037-09-17 19:01 | 11369.3 | 3.6176 | 91.4318 | 74.6386 | 3332.0129
2037-09-18 20:01 | 9988.95 | 3.2279 | 91.2148 | 74.6386 | 2927.4723
2037-09-19 21:01 | 8896.16 | 2.8195 | 91.2264 | 74.6386 | 2607.2071
2037-09-20 22:01 | 8231.63 | 2.5289 | 91.2844 | 74.6386 | 2412.4526
2037-09-21 23:01 | 5656.21 | 1.6644 | 91.4761 | 74.6386 | 1657.6715
2037-09-23 00:01 | 4621.55 | 1.3607 | 91.1935 | 74.6386 | 1354.4426
2037-09-24 01:01 | 4010.12 | 1.2159 | 90.7188 | 74.6386 | 1175.2502
2037-09-25 02:01 | 3952.02 | 1.222 | 90.3783 | 74.6386 | 1158.2227
2037-09-26 03:01 | 4189.22 | 1.3217 | 90.0838 | 74.6386 | 1227.7392
2037-09-27 04:01 | 4354.12 | 1.3661 | 90.0098 | 74.6386 | 1276.0666
2037-09-28 05:01 | 5089.07 | 1.6287 | 89.7929 | 74.6386 | 1491.4592
2037-09-29 06:01 | 5138.64 | 1.6127 | 89.9378 | 74.6386 | 1505.9867
2037-09-30 07:01 | 6347.28 | 2.2023 | 89.2011 | 74.6386 | 1860.2041
2037-10-01 08:01 | 7229.62 | 2.4351 | 89.4756 | 74.6386 | 2118.7925
2037-10-02 09:01 | 9454.31 | 3.1647 | 89.611 | 74.6386 | 2770.7847
2037-10-03 10:01 | 12010.1 | 3.9192 | 89.9939 | 74.6386 | 3519.8129
2037-10-04 11:01 | 13437.3 | 4.497 | 90.1188 | 74.6386 | 3938.0839
2037-10-05 12:01 | 14756.6 | 4.9058 | 90.4575 | 74.6386 | 4324.7326
2037-10-06 13:01 | 15869 | 4.9829 | 91.1586 | 74.6386 | 4650.7448
2037-10-07 14:01 | 15505.3 | 4.8975 | 91.3994 | 74.6386 | 4544.1549
2037-10-08 15:01 | 16237.4 | 5.2049 | 91.4559 | 74.6386 | 4758.7122
2037-10-09 16:01 | 17055.4 | 5.3006 | 91.8517 | 74.6386 | 4998.4443
2037-10-10 17:01 | 16689.3 | 5.1003 | 92.1768 | 74.6386 | 4891.151
2037-10-11 18:01 | 13788.2 | 4.337 | 92.0806 | 74.6386 | 4040.9225
2037-10-12 19:01 | 12656.9 | 3.8949 | 92.1333 | 74.6386 | 3709.3712
2037-10-13 20:01 | 10308 | 3.1575 | 92.0741 | 74.6386 | 3020.9766
2037-10-14 21:01 | 9419.68 | 2.8622 | 91.9365 | 74.6386 | 2760.6357
2037-10-15 22:01 | 7607.71 | 2.2528 | 91.9459 | 74.6386 | 2229.5997
2037-10-16 23:01 | 7178.85 | 2.1952 | 91.4448 | 74.6386 | 2103.9133
2037-10-18 00:01 | 6759.67 | 2.0667 | 91.2731 | 74.6386 | 1981.0637
2037-10-19 01:01 | 6319.43 | 1.9869 | 90.9138 | 74.6386 | 1852.0421
2037-10-20 02:01 | 6259.97 | 1.9401 | 90.8977 | 74.6386 | 1834.6161
2037-10-21 03:01 | 6506.62 | 2.0781 | 90.5692 | 74.6386 | 1906.9021
2037-10-22 04:01 | 6589 | 2.1376 | 90.3983 | 74.6386 | 1931.0453
2037-10-23 05:01 | 7103.94 | 2.3302 | 90.2661 | 74.6386 | 2081.9593
2037-10-24 06:01 | 6891.77 | 2.3062 | 90.1254 | 74.6386 | 2019.7784
2037-10-25 07:01 | 7113.02 | 2.2181 | 90.6127 | 74.6386 | 2084.6204
2037-10-26 08:01 | 6247.09 | 1.9827 | 90.4757 | 74.6386 | 1830.8414
2037-10-27 09:01 | 7245.5 | 2.1302 | 90.9845 | 74.6386 | 2123.4464
2037-10-28 10:01 | 8121.7 | 2.6922 | 90.0868 | 74.6386 | 2380.2353
2037-10-29 11:01 | 9224.21 | 2.9707 | 90.3474 | 74.6386 | 2703.3491
2037-10-30 12:01 | 9289.9 | 2.9623 | 90.5076 | 74.6386 | 2722.6009
2037-10-31 13:01 | 9703.88 | 3.0672 | 90.6094 | 74.6386 | 2843.9265
2037-11-01 14:01 | 8806.64 | 2.9054 | 90.3529 | 74.6386 | 2580.9714
2037-11-02 15:01 | 10331.7 | 3.3584 | 90.4158 | 74.6386 | 3027.9224
2037-11-03 16:01 | 10651.4 | 3.4647 | 90.4849 | 74.6386 | 3121.6172
2037-11-04 17:01 | 10900.2 | 3.5411 | 90.5486 | 74.6386 | 3194.5333
2037-11-05 18:01 | 9853 | 3.1562 | 90.7017 | 74.6386 | 2887.6293
2037-11-06 19:01 | 9358.42 | 2.9114 | 90.8786 | 74.6386 | 2742.6822
2037-11-07 20:01 | 7825.27 | 2.3241 | 91.2175 | 74.6386 | 2293.3603
2037-11-08 21:01 | 6840.47 | 2.1506 | 90.655 | 74.6386 | 2004.7439
2037-11-09 22:01 | 5326.57 | 1.5725 | 91.0044 | 74.6386 | 1561.0636
2037-11-10 23:01 | 4862.07 | 1.4935 | 90.4954 | 74.6386 | 1424.9321
2037-11-12 00:01 | 4629.96 | 1.4371 | 90.2675 | 74.6386 | 1356.9073
2037-11-13 01:01 | 4635.83 | 1.4456 | 90.1155 | 74.6386 | 1358.6277
2037-11-14 02:01 | 4642.25 | 1.4893 | 89.8292 | 74.6386 | 1360.5092
2037-11-15 03:01 | 5052.91 | 1.5758 | 89.9725 | 74.6386 | 1480.8617
2037-11-16 04:01 | 5538.88 | 1.7204 | 89.9819 | 74.6386 | 1623.2855
2037-11-17 05:01 | 6000.23 | 2.0642 | 89.247 | 74.6386 | 1758.4938
2037-11-18 06:01 | 6048.17 | 1.9519 | 89.7261 | 74.6386 | 1772.5437
2037-11-19 07:01 | 6631.54 | 2.1416 | 89.7233 | 74.6386 | 1943.5125
2037-11-20 08:01 | 6703.12 | 2.1358 | 89.8708 | 74.6386 | 1964.4906
2037-11-21 09:01 | 8724.1 | 2.7888 | 89.8735 | 74.6386 | 2556.7813
2037-11-22 10:01 | 9093.31 | 2.9877 | 89.8363 | 74.6386 | 2664.9861
2037-11-23 11:01 | 10636.8 | 3.5112 | 89.9172 | 74.6386 | 3117.3384
2037-11-24 12:01 | 11937.2 | 4.0165 | 89.9605 | 74.6386 | 3498.448
2037-11-25 13:01 | 12618.1 | 4.1223 | 90.3819 | 74.6386 | 3698.0001
2037-11-26 14:01 | 11689.4 | 3.7801 | 90.6492 | 74.6386 | 3425.825
2037-11-27 15:01 | 11992.2 | 3.7641 | 90.9123 | 74.6386 | 3514.5669
2037-11-28 16:01 | 11590.7 | 3.7245 | 90.8062 | 74.6386 | 3396.8989
2037-11-29 17:01 | 11621.5 | 3.6256 | 91.0524 | 74.6386 | 3405.9254
2037-11-30 18:01 | 10306.4 | 3.2194 | 91.0708 | 74.6386 | 3020.5077
2037-12-01 19:01 | 9442.44 | 3.0377 | 90.7794 | 74.6386 | 2767.306
2037-12-02 20:01 | 8084.72 | 2.4045 | 91.3043 | 74.6386 | 2369.3975
2037-12-03 21:01 | 7615.28 | 2.2867 | 91.0909 | 74.6386 | 2231.8183
2037-12-04 22:01 | 5970.41 | 1.7445 | 91.2077 | 74.6386 | 1749.7544
2037-12-05 23:01 | 5584.41 | 1.6881 | 90.7462 | 74.6386 | 1636.629
2037-12-07 00:01 | 5390.64 | 1.6629 | 90.4413 | 74.6386 | 1579.8406
2037-12-08 01:01 | 5099.16 | 1.6125 | 90.1423 | 74.6386 | 1494.4163
2037-12-09 02:01 | 4859.15 | 1.5948 | 89.7734 | 74.6386 | 1424.0763
2037-12-10 03:01 | 5402.95 | 1.6949 | 90.0065 | 74.6386 | 1583.4483
2037-12-11 04:01 | 5730.42 | 1.8295 | 89.8509 | 74.6386 | 1679.4203
2037-12-12 05:01 | 6688.57 | 2.2094 | 89.5932 | 74.6386 | 1960.2264
2037-12-13 06:01 | 6632.36 | 2.1492 | 89.7847 | 74.6386 | 1943.7528
2037-12-14 07:01 | 7010.77 | 2.2477 | 89.8789 | 74.6386 | 2054.6539
2037-12-15 08:01 | 6836.95 | 2.0366 | 90.4818 | 74.6386 | 2003.7123
2037-12-16 09:01 | 7482.33 | 2.369 | 90.0136 | 74.6386 | 2192.8545
2037-12-17 10:01 | 8635.38 | 2.8295 | 89.8124 | 74.6386 | 2530.7801
2037-12-18 11:01 | 9218.28 | 3.1157 | 89.6934 | 74.6386 | 2701.6112
2037-12-19 12:01 | 9811.08 | 3.2436 | 89.943 | 74.6386 | 2875.3437
2037-12-20 13:01 | 10042.3 | 3.4173 | 89.8311 | 74.6386 | 2943.1076
2037-12-21 14:01 | 10267.4 | 3.3377 | 90.243 | 74.6386 | 3009.0779
2037-12-22 15:01 | 11502.3 | 3.82 | 90.1583 | 74.6386 | 3370.9914
2037-12-23 16:01 | 11265.5 | 3.7009 | 90.3706 | 74.6386 | 3301.5921
2037-12-24 17:01 | 11459.5 | 3.6619 | 90.6328 | 74.6386 | 3358.4479
2037-12-25 18:01 | 10486.6 | 3.2505 | 90.9224 | 74.6386 | 3073.3191
2037-12-26 19:01 | 10012 | 3.0101 | 91.1442 | 74.6386 | 2934.2276
2037-12-27 20:01 | 8249.4 | 2.407 | 91.3676 | 74.6386 | 2417.6605
2037-12-28 21:01 | 7203.94 | 2.2514 | 90.6989 | 74.6386 | 2111.2664
2037-12-29 22:01 | 5821.96 | 1.6824 | 91.1753 | 74.6386 | 1706.248
2037-12-30 23:01 | 5349.26 | 1.6204 | 90.6173 | 74.6386 | 1567.7134
2038-01-01 00:01 | 5025.08 | 1.5336 | 90.4174 | 74.6386 | 1472.7056
2038-01-02 01:01 | 4695.68 | 1.5053 | 89.9267 | 74.6386 | 1376.168
2038-01-03 02:01 | 4710.06 | 1.5173 | 89.7876 | 74.6386 | 1380.3823
2038-01-04 03:01 | 5309.33 | 1.6807 | 89.834 | 74.6386 | 1556.011
2038-01-05 04:01 | 5553.67 | 1.8294 | 89.5277 | 74.6386 | 1627.62
2038-01-06 05:01 | 6513.75 | 2.17 | 89.4316 | 74.6386 | 1908.9917
2038-01-07 06:01 | 6409.41 | 2.1561 | 89.4116 | 74.6386 | 1878.4126
2038-01-08 07:01 | 7764.14 | 2.6134 | 89.4156 | 74.6386 | 2275.4448
2038-01-09 08:01 | 8056.17 | 2.6441 | 89.7016 | 74.6386 | 2361.0304
2038-01-10 09:01 | 8709.54 | 2.7616 | 90.0326 | 74.6386 | 2552.5142
2038-01-11 10:01 | 9043.01 | 2.8941 | 90.0549 | 74.6386 | 2650.2446
2038-01-12 11:01 | 9283.85 | 2.945 | 90.1956 | 74.6386 | 2720.8279
2038-01-13 12:01 | 11575.3 | 3.9157 | 89.7989 | 74.6386 | 3392.3856
2038-01-14 13:01 | 12622.6 | 3.9838 | 90.5113 | 74.6386 | 3699.3189
2038-01-15 14:01 | 11766.8 | 3.7234 | 90.7015 | 74.6386 | 3448.5087
2038-01-16 15:01 | 12474.9 | 4.06 | 90.5444 | 74.6386 | 3656.0323
2038-01-17 16:01 | 12258.3 | 4.0477 | 90.5462 | 74.6386 | 3592.5531
2038-01-18 17:01 | 12053.6 | 3.8691 | 90.8262 | 74.6386 | 3532.5614
2038-01-19 18:01 | 10751.8 | 3.3812 | 91.0118 | 74.6386 | 3151.0415
2038-01-20 19:01 | 9513.25 | 3.0722 | 90.7425 | 74.6386 | 2788.0584
2038-01-21 20:01 | 7535.98 | 2.3037 | 91.0548 | 74.6386 | 2208.5777
2038-01-22 21:01 | 6791.51 | 2.0846 | 90.8274 | 74.6386 | 1990.3951
2038-01-23 22:01 | 4928.94 | 1.4732 | 90.88 | 74.6386 | 1444.5297
2038-01-24 23:01 | 3690.72 | 1.1662 | 90.2208 | 74.6386 | 1081.6433
2038-01-26 00:01 | 3205.53 | 1 | 90.6336 | 74.6386 | 939.4481
2038-01-27 01:01 | 3184.01 | 1 | 91.7353 | 74.6386 | 933.1412
2038-01-28 02:01 | 3137.83 | 1 | 92.779 | 74.6386 | 919.6072
2038-01-29 03:01 | 3156.32 | 1 | 93.0762 | 74.6386 | 925.0261
2038-01-30 04:01 | 3141.24 | 1 | 94.3788 | 74.6386 | 920.6066
2038-01-31 05:01 | 3099.98 | 1 | 94.3084 | 74.6386 | 908.5145
2038-02-01 06:01 | 3436.96 | 1.1428 | 88.8829 | 74.6386 | 1007.2735
2038-02-02 07:01 | 5160.46 | 1.6482 | 89.1345 | 74.6386 | 1512.3815
2038-02-03 08:01 | 5089.52 | 1.6714 | 89.02 | 74.6386 | 1491.5911
2038-02-04 09:01 | 6722.61 | 2.3359 | 88.6469 | 74.6386 | 1970.2025
2038-02-05 10:01 | 8703.05 | 2.9681 | 88.8977 | 74.6386 | 2550.6122
2038-02-06 11:01 | 10214 | 3.4413 | 89.2103 | 74.6386 | 2993.4279
2038-02-07 12:01 | 10587.7 | 3.5481 | 89.4876 | 74.6386 | 3102.9486
2038-02-08 13:01 | 11263 | 3.6821 | 89.8209 | 74.6386 | 3300.8595
2038-02-09 14:01 | 12056.5 | 3.9106 | 90.0492 | 74.6386 | 3533.4114
2038-02-10 15:01 | 11998.9 | 3.8609 | 90.2845 | 74.6386 | 3516.5305
2038-02-11 16:01 | 14033 | 4.6123 | 90.2393 | 74.6386 | 4112.6663
2038-02-12 17:01 | 12313.1 | 3.9905 | 90.5748 | 74.6386 | 3608.6134
2038-02-13 18:01 | 10649.7 | 3.3495 | 90.8371 | 74.6386 | 3121.119
2038-02-14 19:01 | 9543.46 | 2.9221 | 90.9574 | 74.6386 | 2796.912
2038-02-15 20:01 | 8554.26 | 2.6204 | 90.8729 | 74.6386 | 2507.0061
2038-02-16 21:01 | 7726.39 | 2.3673 | 90.7779 | 74.6386 | 2264.3814
2038-02-17 22:01 | 7065.16 | 2.1675 | 90.6363 | 74.6386 | 2070.594
2038-02-18 23:01 | 3821.38 | 1.1559 | 90.6278 | 74.6386 | 1119.9359
2038-02-20 00:01 | 3170.88 | 1 | 91.2429 | 74.6386 | 929.2932
2038-02-21 01:01 | 3132.03 | 1 | 93.5958 | 74.6386 | 917.9074
2038-02-22 02:01 | 3151.65 | 1 | 80.6046 | 74.6386 | 923.6574
2038-02-23 03:01 | 3041.57 | 1 | 80.5403 | 74.6386 | 891.3962
2038-02-24 04:01 | 3115.13 | 1 | 80.3716 | 74.6386 | 912.9545
2038-02-25 05:01 | 3138.33 | 1 | 80.2858 | 74.6386 | 919.7537
2038-02-26 06:01 | 3152.51 | 1 | 91.6224 | 74.6386 | 923.9095
2038-02-27 07:01 | 4228.39 | 1.2842 | 89.4679 | 74.6386 | 1239.2188
2038-02-28 08:01 | 3486.52 | 1.0845 | 89.3151 | 74.6386 | 1021.7981
2038-03-01 09:01 | 5936.59 | 1.9396 | 88.8858 | 74.6386 | 1739.8428
2038-03-02 10:01 | 8494 | 2.7842 | 88.9822 | 74.6386 | 2489.3457
2038-03-03 11:01 | 10128.4 | 3.3878 | 89.1014 | 74.6386 | 2968.341
2038-03-04 12:01 | 11075.6 | 3.6004 | 89.5646 | 74.6386 | 3245.9379
2038-03-05 13:01 | 9978.12 | 3.2654 | 89.7287 | 74.6386 | 2924.2983
2038-03-06 14:01 | 12235 | 3.8254 | 90.1411 | 74.6386 | 3585.7245
2038-03-07 15:01 | 12162.5 | 3.8853 | 90.2125 | 74.6386 | 3564.4769
2038-03-08 16:01 | 14030.9 | 4.6233 | 90.1226 | 74.6386 | 4112.0509
2038-03-09 17:01 | 12071.3 | 3.9035 | 90.4834 | 74.6386 | 3537.7488
2038-03-10 18:01 | 10071.7 | 3.2158 | 90.5916 | 74.6386 | 2951.7239
2038-03-11 19:01 | 9065.45 | 2.7933 | 90.7628 | 74.6386 | 2656.8211
2038-03-12 20:01 | 8179.99 | 2.5667 | 90.5358 | 74.6386 | 2397.3184
2038-03-13 21:01 | 7675.36 | 2.3134 | 90.7493 | 74.6386 | 2249.426
2038-03-14 22:01 | 7184.11 | 2.1956 | 90.521 | 74.6386 | 2105.4548
2038-03-15 23:01 | 4899.16 | 1.4105 | 90.9014 | 74.6386 | 1435.8021
2038-03-17 00:01 | 4104.3 | 1.3003 | 89.9305 | 74.6386 | 1202.8516
2038-03-18 01:01 | 3756.73 | 1.1726 | 89.8635 | 74.6386 | 1100.9889
2038-03-19 02:01 | 3469.93 | 1.12 | 89.4732 | 74.6386 | 1016.9361
2038-03-20 03:01 | 3858.03 | 1.2079 | 89.5707 | 74.6386 | 1130.677
2038-03-21 04:01 | 4435.86 | 1.4164 | 89.3332 | 74.6386 | 1300.0222
2038-03-22 05:01 | 5432.8 | 1.7371 | 89.3104 | 74.6386 | 1592.1965
2038-03-23 06:01 | 5577.01 | 1.7764 | 89.3977 | 74.6386 | 1634.4603
2038-03-24 07:01 | 6818.76 | 2.2753 | 89.0907 | 74.6386 | 1998.3813
2038-03-25 08:01 | 7652.76 | 2.5947 | 89.0914 | 74.6386 | 2242.8026
2038-03-26 09:01 | 9343.38 | 3.2412 | 89.054 | 74.6386 | 2738.2744
2038-03-27 10:01 | 11162.3 | 3.7933 | 89.3764 | 74.6386 | 3271.3472
2038-03-28 11:01 | 13028.8 | 4.3811 | 89.6918 | 74.6386 | 3818.3644
2038-03-29 12:01 | 12787.5 | 4.0775 | 90.3683 | 74.6386 | 3747.6463
2038-03-30 13:01 | 13884 | 4.4631 | 90.4773 | 74.6386 | 4068.9987
2038-03-31 14:01 | 14199.7 | 4.5697 | 90.6763 | 74.6386 | 4161.5213
2038-04-01 15:01 | 15133.3 | 4.9022 | 90.8045 | 74.6386 | 4435.1324
2038-04-02 16:01 | 14405.7 | 4.6383 | 91.0289 | 74.6386 | 4221.8939
2038-04-03 17:01 | 13397.1 | 4.2725 | 91.1687 | 74.6386 | 3926.3024
2038-04-04 18:01 | 11861.4 | 3.7263 | 91.292 | 74.6386 | 3476.2332
2038-04-05 19:01 | 10531.6 | 3.3835 | 91.05 | 74.6386 | 3086.5073
2038-04-06 20:01 | 8777.56 | 2.6581 | 91.387 | 74.6386 | 2572.4489
2038-04-07 21:01 | 7906.33 | 2.4115 | 91.1395 | 74.6386 | 2317.1166
2038-04-08 22:01 | 6369.98 | 1.8311 | 91.4381 | 74.6386 | 1866.8569
2038-04-09 23:01 | 5942.54 | 1.739 | 91.0767 | 74.6386 | 1741.5866
2038-04-11 00:01 | 5590.19 | 1.6754 | 90.7292 | 74.6386 | 1638.323
2038-04-12 01:01 | 5368.61 | 1.6493 | 90.4076 | 74.6386 | 1573.3843
2038-04-13 02:01 | 5328.12 | 1.6279 | 90.344 | 74.6386 | 1561.5178
2038-04-14 03:01 | 5377.92 | 1.7498 | 89.7807 | 74.6386 | 1576.1128
2038-04-15 04:01 | 5679.44 | 1.8545 | 89.6945 | 74.6386 | 1664.4796
2038-04-16 05:01 | 6346.04 | 2.0759 | 89.6501 | 74.6386 | 1859.8407
2038-04-17 06:01 | 6438.73 | 2.1189 | 89.6295 | 74.6386 | 1887.0055
2038-04-18 07:01 | 7793.21 | 2.529 | 89.7362 | 74.6386 | 2283.9644
2038-04-19 08:01 | 8536.66 | 2.8256 | 89.6964 | 74.6386 | 2501.8481
2038-04-20 09:01 | 10334.5 | 3.5379 | 89.5679 | 74.6386 | 3028.743
2038-04-21 10:01 | 12630.1 | 4.1806 | 89.9936 | 74.6386 | 3701.5169
2038-04-22 11:01 | 13849 | 4.537 | 90.3451 | 74.6386 | 4058.7412
2038-04-23 12:01 | 14201.3 | 4.6399 | 90.6257 | 74.6386 | 4161.9902
2038-04-24 13:01 | 11632.7 | 3.6641 | 91.0831 | 74.6386 | 3409.2078
2038-04-25 14:01 | 10817.2 | 3.2493 | 91.392 | 74.6386 | 3170.2084
2038-04-26 15:01 | 11688.8 | 3.748 | 90.8237 | 74.6386 | 3425.6491
2038-04-27 16:01 | 11967.8 | 3.8613 | 90.8171 | 74.6386 | 3507.416
2038-04-28 17:01 | 11780.9 | 3.7323 | 90.987 | 74.6386 | 3452.641
2038-04-29 18:01 | 10709.2 | 3.2845 | 91.2342 | 74.6386 | 3138.5567
2038-04-30 19:01 | 9968.83 | 3.076 | 91.1397 | 74.6386 | 2921.5757
2038-05-01 20:01 | 8286.15 | 2.4537 | 91.4109 | 74.6386 | 2428.4308
2038-05-02 21:01 | 7541.72 | 2.3019 | 91.0203 | 74.6386 | 2210.26
2038-05-03 22:01 | 5709.55 | 1.6694 | 91.2092 | 74.6386 | 1673.3039
2038-05-04 23:01 | 5244.91 | 1.5702 | 90.7862 | 74.6386 | 1537.1314
2038-05-06 00:01 | 4917.72 | 1.529 | 90.3107 | 74.6386 | 1441.2415
2038-05-07 01:01 | 4892.89 | 1.5408 | 90.0844 | 74.6386 | 1433.9645
2038-05-08 02:01 | 4927.72 | 1.5351 | 90.0794 | 74.6386 | 1444.1722
2038-05-09 03:01 | 5348.56 | 1.745 | 89.6633 | 74.6386 | 1567.5082
2038-05-10 04:01 | 5504.27 | 1.8046 | 89.6053 | 74.6386 | 1613.1423
2038-05-11 05:01 | 6530.68 | 2.1812 | 89.4507 | 74.6386 | 1913.9534
2038-05-12 06:01 | 6617.07 | 2.1346 | 89.7543 | 74.6386 | 1939.2718
2038-05-13 07:01 | 7006.62 | 2.2294 | 89.8765 | 74.6386 | 2053.4376
2038-05-14 08:01 | 8392.57 | 2.5817 | 90.166 | 74.6386 | 2459.6195
2038-05-15 09:01 | 10040.2 | 3.2904 | 89.8092 | 74.6386 | 2942.4922
2038-05-16 10:01 | 9775.9 | 3.1791 | 90.0522 | 74.6386 | 2865.0335
2038-05-17 11:01 | 10987.2 | 3.6148 | 90.0365 | 74.6386 | 3220.0305
2038-05-18 12:01 | 9864.23 | 3.2608 | 90.1401 | 74.6386 | 2890.9204
2038-05-19 13:01 | 9333.34 | 2.9331 | 90.5311 | 74.6386 | 2735.3319
2038-05-20 14:01 | 8657.49 | 2.8107 | 90.2657 | 74.6386 | 2537.2599
2038-05-21 15:01 | 9845.96 | 3.2081 | 90.1732 | 74.6386 | 2885.566
2038-05-22 16:01 | 10310.6 | 3.2926 | 90.377 | 74.6386 | 3021.7386
2038-05-23 17:01 | 10338.9 | 3.3386 | 90.3439 | 74.6386 | 3030.0325
2038-05-24 18:01 | 9440.43 | 2.9785 | 90.5519 | 74.6386 | 2766.7169
2038-05-25 19:01 | 9201.45 | 2.8247 | 90.7278 | 74.6386 | 2696.6788
2038-05-26 20:01 | 7576.35 | 2.2871 | 90.8459 | 74.6386 | 2220.409
2038-05-27 21:01 | 7081.27 | 2.173 | 90.5871 | 74.6386 | 2075.3154
2038-05-28 22:01 | 5684.17 | 1.6288 | 91.0259 | 74.6386 | 1665.8658
2038-05-29 23:01 | 5503.49 | 1.6555 | 90.4645 | 74.6386 | 1612.9137
2038-05-31 00:01 | 5151.41 | 1.6237 | 89.9975 | 74.6386 | 1509.7292
2038-06-01 01:01 | 5144.71 | 1.5858 | 90.0705 | 74.6386 | 1507.7657
2038-06-02 02:01 | 5174.58 | 1.6172 | 89.9074 | 74.6386 | 1516.5197
2038-06-03 03:01 | 5411.99 | 1.7447 | 89.6251 | 74.6386 | 1586.0977
2038-06-04 04:01 | 5589.01 | 1.8551 | 89.3938 | 74.6386 | 1637.9771
2038-06-05 05:01 | 6612.21 | 2.1978 | 89.366 | 74.6386 | 1937.8475
2038-06-06 06:01 | 6779.2 | 2.1694 | 89.7001 | 74.6386 | 1986.7874
2038-06-07 07:01 | 8381 | 2.668 | 89.7709 | 74.6386 | 2456.2286
2038-06-08 08:01 | 8856.42 | 2.8739 | 89.7643 | 74.6386 | 2595.5605
2038-06-09 09:01 | 10651.8 | 3.5706 | 89.6365 | 74.6386 | 3121.7344
2038-06-10 10:01 | 12852.8 | 4.2427 | 89.9427 | 74.6386 | 3766.7838
2038-06-11 11:01 | 13800.1 | 4.5662 | 90.2041 | 74.6386 | 4044.4101
2038-06-12 12:01 | 15050.1 | 4.767 | 90.7712 | 74.6386 | 4410.7489
2038-06-13 13:01 | 14777.1 | 4.8476 | 90.7719 | 74.6386 | 4330.7405
2038-06-14 14:01 | 14446.9 | 4.4654 | 91.3894 | 74.6386 | 4233.9684
2038-06-15 15:01 | 13905.3 | 4.3503 | 91.4025 | 74.6386 | 4075.2411
2038-06-16 16:01 | 13816.9 | 4.4684 | 91.2041 | 74.6386 | 4049.3337
2038-06-17 17:01 | 13118.7 | 4.1758 | 91.3692 | 74.6386 | 3844.7114
2038-06-18 18:01 | 12027.8 | 3.71 | 91.6052 | 74.6386 | 3525.0002
2038-06-19 19:01 | 11232 | 3.4949 | 91.4744 | 74.6386 | 3291.7743
2038-06-20 20:01 | 9358.66 | 2.8568 | 91.5559 | 74.6386 | 2742.7525
2038-06-21 21:01 | 8250.4 | 2.6862 | 90.9097 | 74.6386 | 2417.9536
2038-06-22 22:01 | 6784.75 | 2.0467 | 91.3091 | 74.6386 | 1988.4139
2038-06-23 23:01 | 5957.11 | 1.89 | 90.7125 | 74.6386 | 1745.8566
2038-06-25 00:01 | 6247.95 | 1.8137 | 91.2066 | 74.6386 | 1831.0934
2038-06-26 01:01 | 5754.84 | 1.8 | 90.5109 | 74.6386 | 1686.5771
2038-06-27 02:01 | 5572.37 | 1.7927 | 90.1875 | 74.6386 | 1633.1004
2038-06-28 03:01 | 6009.47 | 1.8727 | 90.3226 | 74.6386 | 1761.2018
2038-06-29 04:01 | 6229.47 | 2.0073 | 90.0358 | 74.6386 | 1825.6774
2038-06-30 05:01 | 7069.39 | 2.3224 | 89.8734 | 74.6386 | 2071.8337
2038-07-01 06:01 | 7110.03 | 2.3254 | 89.9347 | 74.6386 | 2083.7441
2038-07-02 07:01 | 8918.47 | 2.8114 | 90.2104 | 74.6386 | 2613.7455
2038-07-03 08:01 | 9790.87 | 3.1163 | 90.273 | 74.6386 | 2869.4207
2038-07-04 09:01 | 11693 | 3.9163 | 90.0381 | 74.6386 | 3426.88
2038-07-05 10:01 | 13082.5 | 4.5476 | 89.9954 | 74.6386 | 3834.1023
2038-07-06 11:01 | 15106.5 | 4.9965 | 90.5725 | 74.6386 | 4427.2781
2038-07-07 12:01 | 16675.5 | 5.2237 | 91.2701 | 74.6386 | 4887.1066
2038-07-08 13:01 | 15273.4 | 4.9386 | 91.3443 | 74.6386 | 4476.1917
2038-07-09 14:01 | 16290.2 | 5.1675 | 91.5919 | 74.6386 | 4774.1863
2038-07-10 15:01 | 17401.8 | 5.6212 | 91.6268 | 74.6386 | 5099.9641
2038-07-11 16:01 | 17249.8 | 5.5344 | 91.9067 | 74.6386 | 5055.4173
2038-07-12 17:01 | 15785.3 | 5.043 | 92.0744 | 74.6386 | 4626.2148
2038-07-13 18:01 | 13528 | 4.2298 | 92.2313 | 74.6386 | 3964.6654
2038-07-14 19:01 | 12170.7 | 3.8134 | 92.0995 | 74.6386 | 3566.8801
2038-07-15 20:01 | 9861.89 | 3.0259 | 92.1325 | 74.6386 | 2890.2347
2038-07-16 21:01 | 8949.49 | 2.7507 | 91.8822 | 74.6386 | 2622.8366
2038-07-17 22:01 | 7395.73 | 2.1424 | 92.1465 | 74.6386 | 2167.4745
2038-07-18 23:01 | 6059.9 | 1.8423 | 91.5208 | 74.6386 | 1775.9814
2038-07-20 00:01 | 5676.3 | 1.776 | 91.0438 | 74.6386 | 1663.5593
2038-07-21 01:01 | 5177.5 | 1.6502 | 90.7188 | 74.6386 | 1517.3755
2038-07-22 02:01 | 5033.34 | 1.5519 | 90.8057 | 74.6386 | 1475.1263
2038-07-23 03:01 | 4739.86 | 1.4956 | 90.4817 | 74.6386 | 1389.1158
2038-07-24 04:01 | 4577.92 | 1.3968 | 90.6 | 74.6386 | 1341.6559
2038-07-25 05:01 | 4485.35 | 1.4303 | 90.1482 | 74.6386 | 1314.5263
2038-07-26 06:01 | 6007.46 | 2.0108 | 89.7021 | 74.6386 | 1760.6127
2038-07-27 07:01 | 8104.57 | 2.706 | 89.7505 | 74.6386 | 2375.215
2038-07-28 08:01 | 8626.25 | 2.8141 | 90.0726 | 74.6386 | 2528.1043
2038-07-29 09:01 | 10194.9 | 3.4273 | 89.9562 | 74.6386 | 2987.8303
2038-07-30 10:01 | 11758.1 | 4.0306 | 89.9836 | 74.6386 | 3445.9589
2038-07-31 11:01 | 13713.1 | 4.5606 | 90.4175 | 74.6386 | 4018.9129
2038-08-01 12:01 | 14248.3 | 4.831 | 90.548 | 74.6386 | 4175.7645
2038-08-02 13:01 | 15121.4 | 4.9752 | 90.9595 | 74.6386 | 4431.6449
2038-08-03 14:01 | 15699.6 | 5.106 | 91.2463 | 74.6386 | 4601.0986
2038-08-04 15:01 | 15685.5 | 5.1292 | 91.3945 | 74.6386 | 4596.9663
2038-08-05 16:01 | 17274.3 | 5.6701 | 91.5001 | 74.6386 | 5062.5976
2038-08-06 17:01 | 16526.9 | 4.8176 | 92.633 | 74.6386 | 4843.5563
2038-08-07 18:01 | 13710.1 | 4.2297 | 92.2995 | 74.6386 | 4018.0337
2038-08-08 19:01 | 12176.9 | 3.7452 | 92.1992 | 74.6386 | 3568.6971
2038-08-09 20:01 | 10532.8 | 3.3329 | 91.8487 | 74.6386 | 3086.859
2038-08-10 21:01 | 9415.59 | 3.0237 | 91.5777 | 74.6386 | 2759.437
2038-08-11 22:01 | 9394.73 | 2.8608 | 91.7935 | 74.6386 | 2753.3236
2038-08-12 23:01 | 6520.09 | 1.8579 | 92.2095 | 74.6386 | 1910.8498
2038-08-14 00:01 | 5798.17 | 1.7127 | 91.636 | 74.6386 | 1699.2759
2038-08-15 01:01 | 5342.88 | 1.6031 | 91.2854 | 74.6386 | 1565.8436
2038-08-16 02:01 | 5038.68 | 1.56 | 90.8759 | 74.6386 | 1476.6913
2038-08-17 03:01 | 4584.66 | 1.4398 | 90.6212 | 74.6386 | 1343.6312
2038-08-18 04:01 | 4359.22 | 1.3932 | 90.3174 | 74.6386 | 1277.5613
2038-08-19 05:01 | 4281.6 | 1.3522 | 90.2753 | 74.6386 | 1254.8131
2038-08-20 06:01 | 5746.94 | 1.9725 | 89.5775 | 74.6386 | 1684.2619
2038-08-21 07:01 | 7416.98 | 2.4982 | 89.7314 | 74.6386 | 2173.7023
2038-08-22 08:01 | 8243.88 | 2.6394 | 90.2111 | 74.6386 | 2416.0427
2038-08-23 09:01 | 10400.1 | 3.4129 | 90.1296 | 74.6386 | 3047.9684
2038-08-24 10:01 | 11742.5 | 4.1305 | 89.8464 | 74.6386 | 3441.387
2038-08-25 11:01 | 13773 | 4.5615 | 90.4899 | 74.6386 | 4036.4678
2038-08-26 12:01 | 14734.7 | 4.8805 | 90.7679 | 74.6386 | 4318.3143
2038-08-27 13:01 | 15389.8 | 5.0158 | 91.1283 | 74.6386 | 4510.3052
2038-08-28 14:01 | 13968.1 | 4.4081 | 91.5794 | 74.6386 | 4093.646
2038-08-29 15:01 | 14729.2 | 4.5011 | 91.8627 | 74.6386 | 4316.7024
2038-08-30 16:01 | 15646.6 | 5.0489 | 91.56 | 74.6386 | 4585.5658
2038-08-31 17:01 | 13904.7 | 4.4518 | 91.779 | 74.6386 | 4075.0653
2038-09-01 18:01 | 12198 | 3.784 | 91.9937 | 74.6386 | 3574.8809
2038-09-02 19:01 | 10794.5 | 3.3992 | 91.755 | 74.6386 | 3163.5557
2038-09-03 20:01 | 10078.6 | 3.0953 | 91.8245 | 74.6386 | 2953.7461
2038-09-04 21:01 | 9372.33 | 2.916 | 91.6093 | 74.6386 | 2746.7588
2038-09-05 22:01 | 8863.86 | 2.7411 | 91.52 | 74.6386 | 2597.7409
2038-09-06 23:01 | 6793.14 | 1.96 | 91.9527 | 74.6386 | 1990.8728
2038-09-08 00:01 | 5863.05 | 1.7936 | 91.2622 | 74.6386 | 1718.2903
2038-09-09 01:01 | 5487.11 | 1.6959 | 90.9793 | 74.6386 | 1608.1132
2038-09-10 02:01 | 5352.45 | 1.6323 | 90.9377 | 74.6386 | 1568.6482
2038-09-11 03:01 | 5498.53 | 1.7539 | 90.4775 | 74.6386 | 1611.4601
2038-09-12 04:01 | 5731.22 | 1.8891 | 90.1429 | 74.6386 | 1679.6548
2038-09-13 05:01 | 6600.68 | 2.154 | 90.1715 | 74.6386 | 1934.4684
2038-09-14 06:01 | 6899.6 | 2.2187 | 90.3063 | 74.6386 | 2022.0732
2038-09-15 07:01 | 8431.71 | 2.7375 | 90.2567 | 74.6386 | 2471.0903
2038-09-16 08:01 | 9708.18 | 3.0655 | 90.5761 | 74.6386 | 2845.1867
2038-09-17 09:01 | 10373.7 | 3.3987 | 90.4529 | 74.6386 | 3040.2314
2038-09-18 10:01 | 12546.2 | 4.156 | 90.4929 | 74.6386 | 3676.9283
2038-09-19 11:01 | 13860.9 | 4.7335 | 90.5087 | 74.6386 | 4062.2288
2038-09-20 12:01 | 15518.1 | 5 | 91.1679 | 74.6386 | 4547.9062
2038-09-21 13:01 | 15267.3 | 5.1277 | 91.1376 | 74.6386 | 4474.4039
2038-09-22 14:01 | 15810.9 | 5.1664 | 91.4926 | 74.6386 | 4633.7174
2038-09-23 15:01 | 17818.4 | 5.5525 | 92.0082 | 74.6386 | 5222.0576
2038-09-24 16:01 | 16743.9 | 5.3471 | 92.094 | 74.6386 | 4907.1527
2038-09-25 17:01 | 15466.9 | 4.8856 | 92.2762 | 74.6386 | 4532.9009
2038-09-26 18:01 | 13327.6 | 4.0605 | 92.54 | 74.6386 | 3905.934
2038-09-27 19:01 | 11882.3 | 3.7071 | 92.2464 | 74.6386 | 3482.3584
2038-09-28 20:01 | 10263 | 2.9449 | 92.7704 | 74.6386 | 3007.7884
2038-09-29 21:01 | 8639.33 | 2.7655 | 91.7191 | 74.6386 | 2531.9377
2038-09-30 22:01 | 6958.39 | 2.0778 | 92.012 | 74.6386 | 2039.3028
2038-10-01 23:01 | 6408.45 | 1.935 | 91.66 | 74.6386 | 1878.1313
2038-10-03 00:01 | 5846.58 | 1.8079 | 91.2751 | 74.6386 | 1713.4635
2038-10-04 01:01 | 5851.93 | 1.7764 | 91.2465 | 74.6386 | 1715.0314
2038-10-05 02:01 | 5932.87 | 1.8198 | 91.0412 | 74.6386 | 1738.7526
2038-10-06 03:01 | 5835.73 | 1.9203 | 90.4183 | 74.6386 | 1710.2836
2038-10-07 04:01 | 6371.86 | 2.0357 | 90.5508 | 74.6386 | 1867.4078
2038-10-08 05:01 | 7240.91 | 2.3794 | 90.3152 | 74.6386 | 2122.1012
2038-10-09 06:01 | 7349.59 | 2.3954 | 90.413 | 74.6386 | 2153.9522
2038-10-10 07:01 | 8785.4 | 2.8622 | 90.4235 | 74.6386 | 2574.7466
2038-10-11 08:01 | 9759.86 | 3.1395 | 90.6159 | 74.6386 | 2860.3326
2038-10-12 09:01 | 10549.3 | 3.4805 | 90.5613 | 74.6386 | 3091.6946
2038-10-13 10:01 | 13316.4 | 4.2991 | 90.8416 | 74.6386 | 3902.6516
2038-10-14 11:01 | 14580.6 | 4.8068 | 90.9621 | 74.6386 | 4273.152
2038-10-15 12:01 | 14850.9 | 4.8948 | 91.224 | 74.6386 | 4352.3692
2038-10-16 13:01 | 15176.6 | 4.8955 | 91.5503 | 74.6386 | 4447.8224
2038-10-17 14:01 | 14355.4 | 4.7114 | 91.5737 | 74.6386 | 4207.1524
2038-10-18 15:01 | 15361.6 | 4.7175 | 92.1207 | 74.6386 | 4502.0405
2038-10-19 16:01 | 15895.7 | 5.0945 | 91.9105 | 74.6386 | 4658.5698
2038-10-20 17:01 | 14152.7 | 4.5351 | 92.0369 | 74.6386 | 4147.7469
2038-10-21 18:01 | 11919 | 3.8063 | 92.0268 | 74.6386 | 3493.1141
2038-10-22 19:01 | 10927.7 | 3.4385 | 91.9722 | 74.6386 | 3202.5927
2038-10-23 20:01 | 9074.44 | 2.7345 | 92.1812 | 74.6386 | 2659.4558
2038-10-24 21:01 | 7443.22 | 2.5249 | 91.1059 | 74.6386 | 2181.3924
2038-10-25 22:01 | 6220.63 | 1.8372 | 91.88 | 74.6386 | 1823.0867
2038-10-26 23:01 | 5374.15 | 1.6849 | 91.1677 | 74.6386 | 1575.0079
2038-10-28 00:01 | 4415.91 | 1.5626 | 90.0983 | 74.6386 | 1294.1755
2038-10-29 01:01 | 4422.29 | 1.4097 | 90.6116 | 74.6386 | 1296.0453
2038-10-30 02:01 | 4097.5 | 1.3972 | 89.9812 | 74.6386 | 1200.8587
2038-10-31 03:01 | 4290 | 1.4428 | 89.9392 | 74.6386 | 1257.2749
2038-11-01 04:01 | 6029.96 | 1.4988 | 92.3151 | 74.6386 | 1767.2068
2038-11-02 05:01 | 6646.33 | 2.0533 | 90.4998 | 74.6386 | 1947.847
2038-11-03 06:01 | 6894.08 | 2.0879 | 90.7132 | 74.6386 | 2020.4554
2038-11-04 07:01 | 8372.61 | 2.6882 | 90.2902 | 74.6386 | 2453.7698
2038-11-05 08:01 | 9371.33 | 2.9732 | 90.5018 | 74.6386 | 2746.4657
2038-11-06 09:01 | 11841.6 | 3.8145 | 90.5379 | 74.6386 | 3470.4304
2038-11-07 10:01 | 13728.5 | 4.5559 | 90.5701 | 74.6386 | 4023.4262
2038-11-08 11:01 | 15157.3 | 4.8937 | 91.0515 | 74.6386 | 4442.1661
2038-11-09 12:01 | 12568.2 | 4.175 | 91.1303 | 74.6386 | 3683.3758
2038-11-10 13:01 | 13581 | 4.4664 | 91.1884 | 74.6386 | 3980.1982
2038-11-11 14:01 | 11862.3 | 3.7465 | 91.5944 | 74.6386 | 3476.497
2038-11-12 15:01 | 15233.8 | 4.9535 | 91.3345 | 74.6386 | 4464.5861
2038-11-13 16:01 | 13265.8 | 4.2215 | 91.7045 | 74.6386 | 3887.8222
2038-11-14 17:01 | 13592.4 | 4.2938 | 91.733 | 74.6386 | 3983.5392
2038-11-15 18:01 | 11679.2 | 3.7112 | 91.7313 | 74.6386 | 3422.8356
2038-11-16 19:01 | 10657.8 | 3.3509 | 91.7199 | 74.6386 | 3123.4928
2038-11-17 20:01 | 8684.58 | 2.6214 | 91.9453 | 74.6386 | 2545.1992
2038-11-18 21:01 | 7921.08 | 2.4178 | 91.6399 | 74.6386 | 2321.4394
2038-11-19 22:01 | 6214.95 | 1.8253 | 91.7706 | 74.6386 | 1821.422
2038-11-20 23:01 | 5663.61 | 1.6963 | 91.3661 | 74.6386 | 1659.8402
2038-11-22 00:01 | 5391.01 | 1.6181 | 91.1733 | 74.6386 | 1579.9491
2038-11-23 01:01 | 5333.45 | 1.6355 | 90.8662 | 74.6386 | 1563.0799
2038-11-24 02:01 | 5005.65 | 1.5749 | 90.5827 | 74.6386 | 1467.0112
2038-11-25 03:01 | 5054.2 | 1.648 | 90.2013 | 74.6386 | 1481.2398
2038-11-26 04:01 | 5547.31 | 1.7749 | 90.2648 | 74.6386 | 1625.7561
2038-11-27 05:01 | 6317.72 | 2.0708 | 90.0562 | 74.6386 | 1851.541
2038-11-28 06:01 | 6401.04 | 2.0817 | 90.1364 | 74.6386 | 1875.9596
2038-11-29 07:01 | 7031.42 | 2.2961 | 90.1009 | 74.6386 | 2060.7058
2038-11-30 08:01 | 6765.42 | 2.0518 | 90.6917 | 74.6386 | 1982.7489
2038-12-01 09:01 | 8007 | 2.7011 | 89.8905 | 74.6386 | 2346.6201
2038-12-02 10:01 | 7319.87 | 2.4022 | 90.1571 | 74.6386 | 2145.2421
2038-12-03 11:01 | 8400.29 | 2.5457 | 90.7214 | 74.6386 | 2461.882
2038-12-04 12:01 | 7729.84 | 2.4733 | 90.365 | 74.6386 | 2265.3925
2038-12-05 13:01 | 9912.37 | 3.2888 | 90.0743 | 74.6386 | 2905.0289
2038-12-06 14:01 | 10856.8 | 3.5612 | 90.3084 | 74.6386 | 3181.814
2038-12-07 15:01 | 12117.9 | 4.2534 | 89.9744 | 74.6386 | 3551.4059
2038-12-08 16:01 | 11699.4 | 3.8198 | 90.6528 | 74.6386 | 3428.7557
2038-12-09 17:01 | 11748.1 | 3.7198 | 90.9452 | 74.6386 | 3443.0282
2038-12-10 18:01 | 10386.8 | 3.2513 | 91.1116 | 74.6386 | 3044.0706
2038-12-11 19:01 | 9534.36 | 3.0385 | 90.9355 | 74.6386 | 2794.2451
2038-12-12 20:01 | 7616.25 | 2.2556 | 91.4364 | 74.6386 | 2232.1025
2038-12-13 21:01 | 7003.2 | 2.1323 | 91.0435 | 74.6386 | 2052.4353
2038-12-14 22:01 | 5658.34 | 1.6269 | 91.3756 | 74.6386 | 1658.2958
2038-12-15 23:01 | 5152.85 | 1.4782 | 91.22 | 74.6386 | 1510.1513
2038-12-17 00:01 | 4938.22 | 1.5049 | 90.6034 | 74.6386 | 1447.2494
2038-12-18 01:01 | 4463.57 | 1.4438 | 90.0447 | 74.6386 | 1308.1432
2038-12-19 02:01 | 4804.66 | 1.4862 | 90.2683 | 74.6386 | 1408.1068
2038-12-20 03:01 | 5131.94 | 1.6273 | 90.0145 | 74.6386 | 1504.0231
2038-12-21 04:01 | 5600.46 | 1.8333 | 89.7528 | 74.6386 | 1641.3328
2038-12-22 05:01 | 6704.31 | 2.2048 | 89.7115 | 74.6386 | 1964.8393
2038-12-23 06:01 | 6707.54 | 2.2072 | 89.7719 | 74.6386 | 1965.7859
2038-12-24 07:01 | 7784.53 | 2.6392 | 89.5868 | 74.6386 | 2281.4205
2038-12-25 08:01 | 7786.07 | 2.5328 | 89.974 | 74.6386 | 2281.8719
2038-12-26 09:01 | 7476.94 | 2.4643 | 89.9282 | 74.6386 | 2191.2748
2038-12-27 10:01 | 10148.9 | 3.451 | 89.7104 | 74.6386 | 2974.349
2038-12-28 11:01 | 12378.2 | 4.2428 | 89.8523 | 74.6386 | 3627.6923
2038-12-29 12:01 | 12353.4 | 4.0068 | 90.538 | 74.6386 | 3620.4242
2038-12-30 13:01 | 11725.5 | 3.7336 | 90.825 | 74.6386 | 3436.4048
2038-12-31 14:01 | 12031.6 | 4.0949 | 90.4063 | 74.6386 | 3526.1139
2039-01-01 15:01 | 12738.6 | 4.0004 | 91.0822 | 74.6386 | 3733.3151
2039-01-02 16:01 | 12877.7 | 4.0844 | 91.1256 | 74.6386 | 3774.0813
2039-01-03 17:01 | 12441.8 | 3.9557 | 91.1744 | 74.6386 | 3646.3316
2039-01-04 18:01 | 11128.6 | 3.478 | 91.3292 | 74.6386 | 3261.4707
2039-01-05 19:01 | 10294.8 | 3.2277 | 91.2499 | 74.6386 | 3017.1081
2039-01-06 20:01 | 8410.98 | 2.6066 | 91.2775 | 74.6386 | 2465.0149
2039-01-07 21:01 | 7911.81 | 2.3865 | 91.3317 | 74.6386 | 2318.7226
2039-01-08 22:01 | 6536.78 | 1.8671 | 91.644 | 74.6386 | 1915.7411
2039-01-09 23:01 | 5300.31 | 1.5579 | 91.226 | 74.6386 | 1553.3675
2039-01-11 00:01 | 4762.56 | 1.4867 | 90.5503 | 74.6386 | 1395.7686
2039-01-12 01:01 | 4510.06 | 1.3735 | 90.5742 | 74.6386 | 1321.7681
2039-01-13 02:01 | 4271.41 | 1.3419 | 90.2128 | 74.6386 | 1251.8267
2039-01-14 03:01 | 4271.72 | 1.3631 | 89.9742 | 74.6386 | 1251.9176
2039-01-15 04:01 | 4120.42 | 1.2876 | 90.0342 | 74.6386 | 1207.5759
2039-01-16 05:01 | 4420.59 | 1.3663 | 90.0263 | 74.6386 | 1295.547
2039-01-17 06:01 | 5963.75 | 2.0229 | 89.298 | 74.6386 | 1747.8026
2039-01-18 07:01 | 7091.73 | 2.4062 | 89.36 | 74.6386 | 2078.3809
2039-01-19 08:01 | 6264.04 | 1.8627 | 90.4517 | 74.6386 | 1835.8089
2039-01-20 09:01 | 7437.43 | 2.5771 | 89.3046 | 74.6386 | 2179.6956
2039-01-21 10:01 | 8578.58 | 2.9246 | 89.4924 | 74.6386 | 2514.1336
2039-01-22 11:01 | 9861.92 | 3.2725 | 89.8156 | 74.6386 | 2890.2434
2039-01-23 12:01 | 11176.7 | 3.7251 | 89.9404 | 74.6386 | 3275.5674
2039-01-24 13:01 | 11262.7 | 3.5387 | 90.5517 | 74.6386 | 3300.7715
2039-01-25 14:01 | 10219.6 | 3.3798 | 90.3064 | 74.6386 | 2995.0691
2039-01-26 15:01 | 9589.54 | 2.9895 | 90.7446 | 74.6386 | 2810.4167
2039-01-27 16:01 | 10748.2 | 3.7839 | 89.8484 | 74.6386 | 3149.9865
2039-01-28 17:01 | 10062.3 | 3.1993 | 90.6551 | 74.6386 | 2948.969
2039-01-29 18:01 | 9388.23 | 2.8925 | 90.884 | 74.6386 | 2751.4186
2039-01-30 19:01 | 8430.51 | 2.7054 | 90.5158 | 74.6386 | 2470.7386
2039-01-31 20:01 | 8580.31 | 2.5401 | 91.0641 | 74.6386 | 2514.6406
2039-02-01 21:01 | 8011.58 | 2.4703 | 90.7347 | 74.6386 | 2347.9623
2039-02-02 22:01 | 7621.49 | 2.4185 | 90.4647 | 74.6386 | 2233.6382
2039-02-03 23:01 | 5159.62 | 1.4475 | 91.3808 | 74.6386 | 1512.1354
2039-02-05 00:01 | 4478.25 | 1.3735 | 90.4397 | 74.6386 | 1312.4455
2039-02-06 01:01 | 4325.23 | 1.3346 | 90.2195 | 74.6386 | 1267.5998
2039-02-07 02:01 | 4042.95 | 1.2848 | 89.8848 | 74.6386 | 1184.8717
2039-02-08 03:01 | 3974.31 | 1.2626 | 89.7816 | 74.6386 | 1164.7553
2039-02-09 04:01 | 4010.54 | 1.2667 | 89.7216 | 74.6386 | 1175.3732
2039-02-10 05:01 | 4018.23 | 1.2774 | 89.612 | 74.6386 | 1177.627
2039-02-11 06:01 | 5540.34 | 1.8963 | 89.0294 | 74.6386 | 1623.7134
2039-02-12 07:01 | 6656.57 | 2.1921 | 89.3634 | 74.6386 | 1950.8481
2039-02-13 08:01 | 6489.1 | 2.0058 | 89.9351 | 74.6386 | 1901.7675
2039-02-14 09:01 | 7385.08 | 2.347 | 89.7487 | 74.6386 | 2164.3533
2039-02-15 10:01 | 7369.44 | 2.3701 | 89.7283 | 74.6386 | 2159.7697
2039-02-16 11:01 | 8621.11 | 3.0087 | 89.1985 | 74.6386 | 2526.5979
2039-02-17 12:01 | 9728.64 | 2.925 | 90.395 | 74.6386 | 2851.1829
2039-02-18 13:01 | 7978.09 | 2.6458 | 89.7989 | 74.6386 | 2338.1474
2039-02-19 14:01 | 10930.9 | 3.9252 | 89.2084 | 74.6386 | 3203.5306
2039-02-20 15:01 | 11935.7 | 3.8222 | 90.2074 | 74.6386 | 3498.0084
2039-02-21 16:01 | 13090.3 | 4.2595 | 90.303 | 74.6386 | 3836.3882
2039-02-22 17:01 | 11803.2 | 3.855 | 90.4771 | 74.6386 | 3459.1765
2039-02-23 18:01 | 10581.8 | 3.3279 | 90.7873 | 74.6386 | 3101.2194
2039-02-24 19:01 | 9554.99 | 3.0436 | 90.6699 | 74.6386 | 2800.2911
2039-02-25 20:01 | 9060.51 | 2.8504 | 90.6956 | 74.6386 | 2655.3734
2039-02-26 21:01 | 8597.15 | 2.6925 | 90.6654 | 74.6386 | 2519.5759
2039-02-27 22:01 | 8433.4 | 2.5434 | 90.8822 | 74.6386 | 2471.5856
2039-02-28 23:01 | 5877.81 | 1.6103 | 91.6313 | 74.6386 | 1722.6161
2039-03-02 00:01 | 5036.31 | 1.4969 | 90.7467 | 74.6386 | 1475.9968
2039-03-03 01:01 | 4477.08 | 1.4183 | 90.0924 | 74.6386 | 1312.1026
2039-03-04 02:01 | 3983.22 | 1.2858 | 89.8121 | 74.6386 | 1167.3665
2039-03-05 03:01 | 3820.43 | 1.2134 | 89.7857 | 74.6386 | 1119.6575
2039-03-06 04:01 | 3404.43 | 1.1056 | 89.4845 | 74.6386 | 997.7399
2039-03-07 05:01 | 3576.21 | 1.1619 | 89.3662 | 74.6386 | 1048.0837
2039-03-08 06:01 | 5307.35 | 1.7377 | 89.2342 | 74.6386 | 1555.4307
2039-03-09 07:01 | 7507.55 | 2.4218 | 89.4066 | 74.6386 | 2200.2457
2039-03-10 08:01 | 7918.68 | 2.537 | 89.6421 | 74.6386 | 2320.736
2039-03-11 09:01 | 9516.34 | 3.2204 | 89.3604 | 74.6386 | 2788.9639
2039-03-12 10:01 | 10873.5 | 3.6516 | 89.5963 | 74.6386 | 3186.7083
2039-03-13 11:01 | 10997.5 | 3.5857 | 90.0402 | 74.6386 | 3223.0491
2039-03-14 12:01 | 13150.5 | 4.3193 | 90.1328 | 74.6386 | 3854.0311
2039-03-15 13:01 | 11671.1 | 3.7397 | 90.5731 | 74.6386 | 3420.4618
2039-03-16 14:01 | 10925 | 3.2485 | 91.2119 | 74.6386 | 3201.8014
2039-03-17 15:01 | 9542.55 | 3.1215 | 90.4811 | 74.6386 | 2796.6453
2039-03-18 16:01 | 12494.3 | 4.4244 | 89.849 | 74.6386 | 3661.7179
2039-03-19 17:01 | 11733.8 | 3.6434 | 90.9916 | 74.6386 | 3438.8373
2039-03-20 18:01 | 10401.8 | 3.2965 | 90.8864 | 74.6386 | 3048.4667
2039-03-21 19:01 | 9358.74 | 3.0143 | 90.6943 | 74.6386 | 2742.7759
2039-03-22 20:01 | 9110.33 | 2.7885 | 90.9928 | 74.6386 | 2669.9742
2039-03-23 21:01 | 8456.98 | 2.6295 | 90.8373 | 74.6386 | 2478.4962
2039-03-24 22:01 | 8290.91 | 2.5265 | 90.892 | 74.6386 | 2429.8259
2039-03-25 23:01 | 6262.79 | 1.7679 | 91.4446 | 74.6386 | 1835.4426
2039-03-27 00:01 | 5626.27 | 1.6658 | 90.8611 | 74.6386 | 1648.897
2039-03-28 01:01 | 5321.41 | 1.6399 | 90.3993 | 74.6386 | 1559.5513
2039-03-29 02:01 | 5279.23 | 1.6634 | 90.1277 | 74.6386 | 1547.1896
2039-03-30 03:01 | 5599.72 | 1.8163 | 89.8456 | 74.6386 | 1641.1159
2039-03-31 04:01 | 6173.38 | 1.9717 | 89.9068 | 74.6386 | 1809.2391
2039-04-01 05:01 | 6793.03 | 2.3755 | 89.2757 | 74.6386 | 1990.8406
2039-04-02 06:01 | 6941.32 | 2.316 | 89.643 | 74.6386 | 2034.3001
2039-04-03 07:01 | 8396.96 | 2.7582 | 89.7765 | 74.6386 | 2460.9061
2039-04-04 08:01 | 8408.52 | 2.8141 | 89.7603 | 74.6386 | 2464.294
2039-04-05 09:01 | 10479.3 | 3.4787 | 89.8796 | 74.6386 | 3071.1797
2039-04-06 10:01 | 12319.9 | 4.0729 | 90.0851 | 74.6386 | 3610.6063
2039-04-07 11:01 | 14485.9 | 4.7446 | 90.4023 | 74.6386 | 4245.3982
2039-04-08 12:01 | 14551 | 4.6108 | 90.9557 | 74.6386 | 4264.4771
2039-04-09 13:01 | 15323.3 | 4.8844 | 91.1151 | 74.6386 | 4490.8159
2039-04-10 14:01 | 15878.9 | 5.1299 | 91.2321 | 74.6386 | 4653.6462
2039-04-11 15:01 | 17233.3 | 5.5441 | 91.4682 | 74.6386 | 5050.5817
2039-04-12 16:01 | 17124.8 | 5.4618 | 91.7701 | 74.6386 | 5018.7835
2039-04-13 17:01 | 15483.4 | 4.8431 | 92.0673 | 74.6386 | 4537.7366
2039-04-14 18:01 | 13753.7 | 4.2165 | 92.2318 | 74.6386 | 4030.8116
2039-04-15 19:01 | 12498.5 | 3.8798 | 92.0574 | 74.6386 | 3662.9488
2039-04-16 20:01 | 10237.9 | 3.1346 | 92.0723 | 74.6386 | 3000.4323
2039-04-17 21:01 | 9351.73 | 2.895 | 91.7712 | 74.6386 | 2740.7215
2039-04-18 22:01 | 7105.51 | 2.2255 | 91.4874 | 74.6386 | 2082.4194
2039-04-19 23:01 | 6538.25 | 2.0166 | 91.3281 | 74.6386 | 1916.1719
2039-04-21 00:01 | 6226.29 | 1.9255 | 91.1017 | 74.6386 | 1824.7455
2039-04-22 01:01 | 6056.2 | 1.8217 | 91.1609 | 74.6386 | 1774.897
2039-04-23 02:01 | 5771.56 | 1.8272 | 90.6478 | 74.6386 | 1691.4773
2039-04-24 03:01 | 6299.85 | 1.9579 | 90.6574 | 74.6386 | 1846.3038
2039-04-25 04:01 | 6385.65 | 2.0529 | 90.3541 | 74.6386 | 1871.4493
2039-04-26 05:01 | 7305.49 | 2.3641 | 90.2661 | 74.6386 | 2141.0278
2039-04-27 06:01 | 7414.61 | 2.3691 | 90.3868 | 74.6386 | 2173.0077
2039-04-28 07:01 | 8761.83 | 2.8714 | 90.206 | 74.6386 | 2567.8389
2039-04-29 08:01 | 9452.08 | 3.1164 | 90.2661 | 74.6386 | 2770.1312
2039-04-30 09:01 | 11631.5 | 3.9216 | 90.2065 | 74.6386 | 3408.8562
2039-05-01 10:01 | 13164.3 | 4.2973 | 90.6564 | 74.6386 | 3858.0755
2039-05-02 11:01 | 14188.6 | 4.6615 | 90.8469 | 74.6386 | 4158.2682
2039-05-03 12:01 | 15517.7 | 5.1269 | 91.0273 | 74.6386 | 4547.7889
2039-05-04 13:01 | 16077.4 | 5.3296 | 91.2473 | 74.6386 | 4711.8208
2039-05-05 14:01 | 17042 | 5.5228 | 91.629 | 74.6386 | 4994.5172
2039-05-06 15:01 | 18244.6 | 5.7918 | 91.9962 | 74.6386 | 5346.9644
2039-05-07 16:01 | 17984.5 | 5.6621 | 92.2984 | 74.6386 | 5270.7367
2039-05-08 17:01 | 16147.3 | 4.9824 | 92.6051 | 74.6386 | 4732.3065
2039-05-09 18:01 | 14045.3 | 4.3631 | 92.5454 | 74.6386 | 4116.2711
2039-05-10 19:01 | 12735.4 | 3.948 | 92.4477 | 74.6386 | 3732.3773
2039-05-11 20:01 | 10450.7 | 3.1724 | 92.4901 | 74.6386 | 3062.7978
2039-05-12 21:01 | 9219.75 | 2.8718 | 92.0564 | 74.6386 | 2702.042
2039-05-13 22:01 | 7442.61 | 2.2019 | 92.2281 | 74.6386 | 2181.2137
2039-05-14 23:01 | 6859.68 | 2.0709 | 91.8098 | 74.6386 | 2010.3738
2039-05-16 00:01 | 6542.37 | 1.9871 | 91.5611 | 74.6386 | 1917.3794
2039-05-17 01:01 | 6158.76 | 1.912 | 91.2341 | 74.6386 | 1804.9544
2039-05-18 02:01 | 6124.75 | 1.9185 | 91.0234 | 74.6386 | 1794.987
2039-05-19 03:01 | 6228.51 | 1.9846 | 90.7745 | 74.6386 | 1825.3961
2039-05-20 04:01 | 6455.63 | 2.0768 | 90.6204 | 74.6386 | 1891.9584
2039-05-21 05:01 | 7193.61 | 2.4146 | 90.2611 | 74.6386 | 2108.239
2039-05-22 06:01 | 7300.54 | 2.3103 | 90.6971 | 74.6386 | 2139.5771
2039-05-23 07:01 | 8292.77 | 2.7332 | 90.3922 | 74.6386 | 2430.371
2039-05-24 08:01 | 8303.36 | 2.5981 | 90.8385 | 74.6386 | 2433.4746
2039-05-25 09:01 | 8484.98 | 2.6686 | 90.8245 | 74.6386 | 2486.7022
2039-05-26 10:01 | 9528.39 | 3.111 | 90.5669 | 74.6386 | 2792.4955
2039-05-27 11:01 | 12660.4 | 4.3455 | 90.2911 | 74.6386 | 3710.397
2039-05-28 12:01 | 13960.9 | 4.7239 | 90.6656 | 74.6386 | 4091.5359
2039-05-29 13:01 | 14903.4 | 4.7265 | 91.3765 | 74.6386 | 4367.7554
2039-05-30 14:01 | 14543.5 | 4.5691 | 91.6559 | 74.6386 | 4262.2791
2039-05-31 15:01 | 14816.6 | 4.7553 | 91.6131 | 74.6386 | 4342.3168
2039-06-01 16:01 | 13979.2 | 4.5192 | 91.6764 | 74.6386 | 4096.8991
2039-06-02 17:01 | 13135.1 | 4.1963 | 91.7797 | 74.6386 | 3849.5178
2039-06-03 18:01 | 11598.8 | 3.6497 | 91.8606 | 74.6386 | 3399.2727
2039-06-04 19:01 | 10815.1 | 3.372 | 91.8129 | 74.6386 | 3169.5929
2039-06-05 20:01 | 8885.88 | 2.6776 | 91.9813 | 74.6386 | 2604.1944
2039-06-06 21:01 | 7848.83 | 2.4665 | 91.473 | 74.6386 | 2300.265
2039-06-07 22:01 | 6226.09 | 1.8319 | 91.8114 | 74.6386 | 1824.6869
2039-06-08 23:01 | 5667.6 | 1.7212 | 91.329 | 74.6386 | 1661.0096
2039-06-10 00:01 | 5494.58 | 1.6863 | 91.0581 | 74.6386 | 1610.3024
2039-06-11 01:01 | 5254.04 | 1.6172 | 90.8875 | 74.6386 | 1539.8071
2039-06-12 02:01 | 5279.15 | 1.6388 | 90.7001 | 74.6386 | 1547.1661
2039-06-13 03:01 | 5572.52 | 1.7761 | 90.4027 | 74.6386 | 1633.1444
2039-06-14 04:01 | 5836.68 | 1.904 | 90.1842 | 74.6386 | 1710.5621
2039-06-15 05:01 | 6742.25 | 2.2486 | 89.9956 | 74.6386 | 1975.9584
2039-06-16 06:01 | 6881.52 | 2.2277 | 90.2447 | 74.6386 | 2016.7744
2039-06-17 07:01 | 7953.62 | 2.7166 | 89.8751 | 74.6386 | 2330.9759
2039-06-18 08:01 | 9249.74 | 3.0186 | 90.2797 | 74.6386 | 2710.8312
2039-06-19 09:01 | 11745.8 | 3.9277 | 90.2446 | 74.6386 | 3442.3542
2039-06-20 10:01 | 12763.7 | 4.3109 | 90.4433 | 74.6386 | 3740.6712
2039-06-21 11:01 | 14576.5 | 4.6147 | 91.1327 | 74.6386 | 4271.9505
2039-06-22 12:01 | 12476.3 | 3.8568 | 91.5851 | 74.6386 | 3656.4426
2039-06-23 13:01 | 14651.9 | 4.7277 | 91.284 | 74.6386 | 4294.048
2039-06-24 14:01 | 12555 | 3.9088 | 91.7523 | 74.6386 | 3679.5073
2039-06-25 15:01 | 14653.8 | 4.7659 | 91.4038 | 74.6386 | 4294.6048
2039-06-26 16:01 | 13774.5 | 4.4546 | 91.5928 | 74.6386 | 4036.9075
2039-06-27 17:01 | 13316.2 | 4.2278 | 91.7604 | 74.6386 | 3902.593
2039-06-28 18:01 | 11820.5 | 3.6345 | 92.0237 | 74.6386 | 3464.2466
2039-06-29 19:01 | 10847.9 | 3.3891 | 91.8118 | 74.6386 | 3179.2057
2039-06-30 20:01 | 8904.19 | 2.6962 | 91.9742 | 74.6386 | 2609.5605
2039-07-01 21:01 | 8213.54 | 2.5152 | 91.6838 | 74.6386 | 2407.151
2039-07-02 22:01 | 6452.95 | 1.927 | 91.7194 | 74.6386 | 1891.173
2039-07-03 23:01 | 5394.18 | 1.6219 | 91.4281 | 74.6386 | 1580.8781
2039-07-05 00:01 | 5051.15 | 1.5404 | 91.1028 | 74.6386 | 1480.3459
2039-07-06 01:01 | 4677.16 | 1.4446 | 90.831 | 74.6386 | 1370.7403
2039-07-07 02:01 | 4290.39 | 1.3523 | 90.5441 | 74.6386 | 1257.3892
2039-07-08 03:01 | 3896.24 | 1.2624 | 90.1902 | 74.6386 | 1141.8752
2039-07-09 04:01 | 3733.96 | 1.2349 | 89.9068 | 74.6386 | 1094.3157
2039-07-10 05:01 | 3797.39 | 1.2013 | 90.1148 | 74.6386 | 1112.9052
2039-07-11 06:01 | 5706.27 | 1.7678 | 90.1854 | 74.6386 | 1672.3427
2039-07-12 07:01 | 6715.1 | 2.2917 | 89.5452 | 74.6386 | 1968.0015
2039-07-13 08:01 | 6712.14 | 2.1806 | 89.9872 | 74.6386 | 1967.1341
2039-07-14 09:01 | 7316.07 | 2.2833 | 90.3067 | 74.6386 | 2144.1285
2039-07-15 10:01 | 7853.56 | 2.5543 | 90.0542 | 74.6386 | 2301.6512
2039-07-16 11:01 | 8444.54 | 2.7544 | 90.1018 | 74.6386 | 2474.8504
2039-07-17 12:01 | 7685.43 | 2.42 | 90.4284 | 74.6386 | 2252.3772
2039-07-18 13:01 | 7955.81 | 2.6105 | 90.0863 | 74.6386 | 2331.6177
2039-07-19 14:01 | 8196.93 | 2.6314 | 90.2489 | 74.6386 | 2402.283
2039-07-20 15:01 | 9118.69 | 3.0033 | 90.0761 | 74.6386 | 2672.4242
2039-07-21 16:01 | 11585.5 | 3.9161 | 89.9611 | 74.6386 | 3395.3749
2039-07-22 17:01 | 10612.7 | 3.428 | 90.5063 | 74.6386 | 3110.2753
2039-07-23 18:01 | 9429 | 2.9838 | 90.7156 | 74.6386 | 2763.3671
2039-07-24 19:01 | 8719.14 | 2.7316 | 90.7385 | 74.6386 | 2555.3277
2039-07-25 20:01 | 8429.48 | 2.6088 | 90.79 | 74.6386 | 2470.4367
2039-07-26 21:01 | 7960.79 | 2.476 | 90.7237 | 74.6386 | 2333.0772
2039-07-27 22:01 | 7531.01 | 2.4013 | 90.4721 | 74.6386 | 2207.1212
2039-07-28 23:01 | 4876.09 | 1.3859 | 91.3129 | 74.6386 | 1429.0409
2039-07-30 00:01 | 4180.89 | 1.2899 | 90.4365 | 74.6386 | 1225.2979
2039-07-31 01:01 | 3758.71 | 1.1618 | 90.2507 | 74.6386 | 1101.5692
2039-08-01 02:01 | 3255.78 | 1.0168 | 90.044 | 74.6386 | 954.1749
2039-08-02 03:01 | 3070.3 | 1 | 89.9422 | 74.6386 | 899.8161
2039-08-03 04:01 | 3095.85 | 1 | 90.7309 | 74.6386 | 907.3041
2039-08-04 05:01 | 3091.47 | 1 | 90.1997 | 74.6386 | 906.0204
2039-08-05 06:01 | 4396.75 | 1.4121 | 89.3965 | 74.6386 | 1288.5602
2039-08-06 07:01 | 5926.75 | 1.9685 | 89.1817 | 74.6386 | 1736.959
2039-08-07 08:01 | 4784.73 | 1.4439 | 90.0072 | 74.6386 | 1402.2659
2039-08-08 09:01 | 6236.19 | 2.0454 | 89.3255 | 74.6386 | 1827.6469
2039-08-09 10:01 | 7134.33 | 2.3958 | 89.2175 | 74.6386 | 2090.8657
2039-08-10 11:01 | 10321.9 | 3.543 | 89.1781 | 74.6386 | 3025.0503
2039-08-11 12:01 | 10811.2 | 3.6681 | 89.5501 | 74.6386 | 3168.45
2039-08-12 13:01 | 10364.4 | 3.3215 | 90.1492 | 74.6386 | 3037.5058
2039-08-13 14:01 | 10242.1 | 3.2685 | 90.279 | 74.6386 | 3001.6632
2039-08-14 15:01 | 10739.8 | 3.4737 | 90.2505 | 74.6386 | 3147.5247
2039-08-15 16:01 | 12934.6 | 4.3244 | 90.1139 | 74.6386 | 3790.7571
2039-08-16 17:01 | 11108.7 | 3.5312 | 90.7017 | 74.6386 | 3255.6386
2039-08-17 18:01 | 9622.4 | 3.0461 | 90.7308 | 74.6386 | 2820.0471
2039-08-18 19:01 | 8495.73 | 2.6823 | 90.6532 | 74.6386 | 2489.8527
2039-08-19 20:01 | 7799.29 | 2.3627 | 90.883 | 74.6386 | 2285.7463
2039-08-20 21:01 | 6898.66 | 2.1394 | 90.6155 | 74.6386 | 2021.7977
2039-08-21 22:01 | 6308.89 | 1.9451 | 90.522 | 74.6386 | 1848.9531
2039-08-22 23:01 | 3481.23 | 1.0449 | 90.6038 | 74.6386 | 1020.2478
2039-08-24 00:01 | 3167.59 | 1 | 92.2591 | 74.6386 | 928.329
2039-08-25 01:01 | 3150.09 | 1 | 94.3231 | 74.6386 | 923.2002
2039-08-26 02:01 | 3091.09 | 1 | 80.6395 | 74.6386 | 905.9091
2039-08-27 03:01 | 3106.2 | 1 | 94.5266 | 74.6386 | 910.3374
2039-08-28 04:01 | 3103.66 | 1 | 93.042 | 74.6386 | 909.593
2039-08-29 05:01 | 3381.69 | 1.0578 | 89.4155 | 74.6386 | 991.0755
2039-08-30 06:01 | 3479.57 | 1.1078 | 89.2528 | 74.6386 | 1019.7613
2039-08-31 07:01 | 5292.74 | 1.6809 | 89.2337 | 74.6386 | 1551.149
2039-09-01 08:01 | 6528.12 | 2.1249 | 89.1536 | 74.6386 | 1913.2031
2039-09-02 09:01 | 8580.27 | 2.9633 | 88.8703 | 74.6386 | 2514.6289
2039-09-03 10:01 | 10917.7 | 3.7026 | 89.2115 | 74.6386 | 3199.662
2039-09-04 11:01 | 11587.3 | 3.8429 | 89.6731 | 74.6386 | 3395.9024
2039-09-05 12:01 | 12440.6 | 4.0641 | 90.0224 | 74.6386 | 3645.98
2039-09-06 13:01 | 12672.8 | 4.1813 | 90.1691 | 74.6386 | 3714.0311
2039-09-07 14:01 | 14052.4 | 4.4973 | 90.57 | 74.6386 | 4118.3519
2039-09-08 15:01 | 14934.5 | 4.8341 | 90.7175 | 74.6386 | 4376.8699
2039-09-09 16:01 | 14767.1 | 4.6949 | 91.0594 | 74.6386 | 4327.8098
2039-09-10 17:01 | 13053.7 | 4.1368 | 91.2252 | 74.6386 | 3825.6618
2039-09-11 18:01 | 10999.5 | 3.385 | 91.4452 | 74.6386 | 3223.6352
2039-09-12 19:01 | 9647.75 | 3.0039 | 91.2466 | 74.6386 | 2827.4764
2039-09-13 20:01 | 7382.94 | 2.2199 | 91.3818 | 74.6386 | 2163.7261
2039-09-14 21:01 | 6167.43 | 1.8838 | 91.015 | 74.6386 | 1807.4953
2039-09-15 22:01 | 3853.63 | 1.1552 | 90.9142 | 74.6386 | 1129.3875
2039-09-16 23:01 | 3152.05 | 1 | 91.1745 | 74.6386 | 923.7747
2039-09-18 00:01 | 3061.46 | 1 | 93.258 | 74.6386 | 897.2254
2039-09-19 01:01 | 3083.48 | 1 | 80.818 | 74.6386 | 903.6788
2039-09-20 02:01 | 3072.99 | 1 | 80.6975 | 74.6386 | 900.6045
2039-09-21 03:01 | 3159.08 | 1 | 80.5382 | 74.6386 | 925.835
2039-09-22 04:01 | 3111.88 | 1 | 80.4802 | 74.6386 | 912.002
2039-09-23 05:01 | 3081.54 | 1 | 92.1105 | 74.6386 | 903.1102
2039-09-24 06:01 | 3203.48 | 1 | 92.468 | 74.6386 | 938.8473
2039-09-25 07:01 | 4703.82 | 1.4827 | 89.2976 | 74.6386 | 1378.5536
2039-09-26 08:01 | 6013.83 | 2.0311 | 88.8706 | 74.6386 | 1762.4796
2039-09-27 09:01 | 8104.04 | 2.875 | 88.6488 | 74.6386 | 2375.0597
2039-09-28 10:01 | 10130.1 | 3.4777 | 89.0785 | 74.6386 | 2968.8392
2039-09-29 11:01 | 12168.2 | 4.0203 | 89.6127 | 74.6386 | 3566.1474
2039-09-30 12:01 | 13058.1 | 4.3212 | 89.9143 | 74.6386 | 3826.9513
2039-10-01 13:01 | 13594.9 | 4.4163 | 90.305 | 74.6386 | 3984.2719
2039-10-02 14:01 | 14276.9 | 4.6037 | 90.5714 | 74.6386 | 4184.1464
2039-10-03 15:01 | 15370.5 | 4.9542 | 90.7728 | 74.6386 | 4504.6489
2039-10-04 16:01 | 14511.8 | 4.6608 | 91.0202 | 74.6386 | 4252.9888
2039-10-05 17:01 | 12666.7 | 4.0367 | 91.1703 | 74.6386 | 3712.2433
2039-10-06 18:01 | 10663.8 | 3.2387 | 91.4937 | 74.6386 | 3125.2513
2039-10-07 19:01 | 9155.63 | 2.8514 | 91.1719 | 74.6386 | 2683.2503
2039-10-08 20:01 | 6910.3 | 2.0698 | 91.323 | 74.6386 | 2025.209
2039-10-09 21:01 | 5889.06 | 1.8146 | 90.8456 | 74.6386 | 1725.9131
2039-10-10 22:01 | 3587.92 | 1.1153 | 90.5527 | 74.6386 | 1051.5156
2039-10-11 23:01 | 3264.1 | 1 | 92.3739 | 74.6386 | 956.6133
2039-10-13 00:01 | 3152.51 | 1 | 94.6364 | 74.6386 | 923.9095
2039-10-14 01:01 | 3137.86 | 1 | 80.7479 | 74.6386 | 919.616
2039-10-15 02:01 | 3083.44 | 1 | 80.6533 | 74.6386 | 903.6671
2039-10-16 03:01 | 3199.77 | 1 | 80.478 | 74.6386 | 937.76
2039-10-17 04:01 | 3239.11 | 1 | 95.1924 | 74.6386 | 949.2894
2039-10-18 05:01 | 3205.76 | 1.0198 | 89.3166 | 74.6386 | 939.5155
2039-10-19 06:01 | 3163.68 | 1 | 89.9324 | 74.6386 | 927.1831
2039-10-20 07:01 | 5187.36 | 1.606 | 89.4184 | 74.6386 | 1520.2651
2039-10-21 08:01 | 6461.66 | 2.2158 | 88.7861 | 74.6386 | 1893.7256
2039-10-22 09:01 | 9038.16 | 3.2248 | 88.6544 | 74.6386 | 2648.8232
2039-10-23 10:01 | 11336.9 | 3.9426 | 89.0816 | 74.6386 | 3322.5174
2039-10-24 11:01 | 13246.4 | 4.4073 | 89.7061 | 74.6386 | 3882.1366
2039-10-25 12:01 | 14193.9 | 4.6637 | 90.1336 | 74.6386 | 4159.8215
2039-10-26 13:01 | 14800.4 | 4.7655 | 90.5586 | 74.6386 | 4337.5691
2039-10-27 14:01 | 14879 | 4.8707 | 90.6749 | 74.6386 | 4360.6045
2039-10-28 15:01 | 15860.9 | 5.1489 | 90.9011 | 74.6386 | 4648.3709
2039-10-29 16:01 | 15287.9 | 4.903 | 91.1878 | 74.6386 | 4480.4412
2039-10-30 17:01 | 13629.3 | 4.2181 | 91.5637 | 74.6386 | 3994.3535
2039-10-31 18:01 | 11431.6 | 3.5134 | 91.5991 | 74.6386 | 3350.2712
2039-11-01 19:01 | 9902.4 | 3.0661 | 91.4086 | 74.6386 | 2902.107
2039-11-02 20:01 | 7504.73 | 2.274 | 91.4305 | 74.6386 | 2199.4193
2039-11-03 21:01 | 6536.01 | 1.9489 | 91.2966 | 74.6386 | 1915.5154
2039-11-04 22:01 | 4444.51 | 1.3321 | 91.0327 | 74.6386 | 1302.5573
2039-11-05 23:01 | 3470.92 | 1.0921 | 90.3668 | 74.6386 | 1017.2262
2039-11-07 00:01 | 3137.54 | 1 | 90.7891 | 74.6386 | 919.5222
2039-11-08 01:01 | 3167.98 | 1 | 92.5057 | 74.6386 | 928.4433
2039-11-09 02:01 | 3111.12 | 1 | 93.5523 | 74.6386 | 911.7793
2039-11-10 03:01 | 3111.23 | 1 | 91.6573 | 74.6386 | 911.8115
2039-11-11 04:01 | 3177.13 | 1 | 91.626 | 74.6386 | 931.1249
2039-11-12 05:01 | 3593.11 | 1.1324 | 89.4667 | 74.6386 | 1053.0366
2039-11-13 06:01 | 3609.36 | 1.1534 | 89.3434 | 74.6386 | 1057.799
2039-11-14 07:01 | 5567.04 | 1.7295 | 89.5166 | 74.6386 | 1631.5384
2039-11-15 08:01 | 6559.23 | 2.2597 | 88.8817 | 74.6386 | 1922.3206
2039-11-16 09:01 | 8971.18 | 3.1073 | 88.9632 | 74.6386 | 2629.1933
2039-11-17 10:01 | 10977 | 3.7946 | 89.2085 | 74.6386 | 3217.0411
2039-11-18 11:01 | 13058.7 | 4.3959 | 89.6699 | 74.6386 | 3827.1272
2039-11-19 12:01 | 14260.8 | 4.6865 | 90.1636 | 74.6386 | 4179.4279
2039-11-20 13:01 | 13721.9 | 4.4504 | 90.5419 | 74.6386 | 4021.4919
2039-11-21 14:01 | 13868.4 | 4.3882 | 90.8746 | 74.6386 | 4064.4268
2039-11-22 15:01 | 15569.9 | 5.0047 | 90.8765 | 74.6386 | 4563.0873
2039-11-23 16:01 | 14287.5 | 4.5535 | 91.1695 | 74.6386 | 4187.2529
2039-11-24 17:01 | 12853.6 | 4.0744 | 91.2678 | 74.6386 | 3767.0183
2039-11-25 18:01 | 11070 | 3.3622 | 91.5478 | 74.6386 | 3244.2967
2039-11-26 19:01 | 9690.88 | 2.9995 | 91.2942 | 74.6386 | 2840.1166
2039-11-27 20:01 | 7482.86 | 2.2202 | 91.5007 | 74.6386 | 2193.0098
2039-11-28 21:01 | 6284.85 | 1.9299 | 90.9872 | 74.6386 | 1841.9077
2039-11-29 22:01 | 4421.02 | 1.3225 | 90.9677 | 74.6386 | 1295.6731
2039-11-30 23:01 | 3574.19 | 1.1295 | 90.2715 | 74.6386 | 1047.4917
2039-12-02 00:01 | 3203.05 | 1 | 90.2395 | 74.6386 | 938.7213
2039-12-03 01:01 | 3146.96 | 1 | 90.4863 | 74.6386 | 922.2829
2039-12-04 02:01 | 3191.74 | 1 | 92.0957 | 74.6386 | 935.4067
2039-12-05 03:01 | 3127.71 | 1 | 89.8854 | 74.6386 | 916.6413
2039-12-06 04:01 | 3723.63 | 1.1578 | 89.6253 | 74.6386 | 1091.2882
2039-12-07 05:01 | 4941.8 | 1.5063 | 89.7502 | 74.6386 | 1448.2986
2039-12-08 06:01 | 4899.81 | 1.5156 | 89.7 | 74.6386 | 1435.9926
2039-12-09 07:01 | 6547.78 | 2.1552 | 89.247 | 74.6386 | 1918.9649
2039-12-10 08:01 | 7725.36 | 2.6372 | 89.1082 | 74.6386 | 2264.0795
2039-12-11 09:01 | 8850.38 | 2.8943 | 89.5623 | 74.6386 | 2593.7903
2039-12-12 10:01 | 11611.8 | 3.8619 | 89.5989 | 74.6386 | 3403.0827
2039-12-13 11:01 | 13081.1 | 4.373 | 89.8505 | 74.6386 | 3833.692
2039-12-14 12:01 | 11667.1 | 3.8344 | 90.2608 | 74.6386 | 3419.2895
2039-12-15 13:01 | 11458.8 | 3.631 | 90.589 | 74.6386 | 3358.2428
2039-12-16 14:01 | 11073.3 | 3.447 | 90.7679 | 74.6386 | 3245.2639
2039-12-17 15:01 | 11886.9 | 3.8905 | 90.4235 | 74.6386 | 3483.7065
2039-12-18 16:01 | 12233.7 | 3.9746 | 90.5495 | 74.6386 | 3585.3435
2039-12-19 17:01 | 11251.6 | 3.6398 | 90.6439 | 74.6386 | 3297.5185
2039-12-20 18:01 | 10207.7 | 3.2013 | 90.8662 | 74.6386 | 2991.5816
2039-12-21 19:01 | 9363.23 | 2.9245 | 90.8349 | 74.6386 | 2744.0918
2039-12-22 20:01 | 7450.23 | 2.2133 | 91.1612 | 74.6386 | 2183.4469
2039-12-23 21:01 | 6841.17 | 2.0949 | 90.7512 | 74.6386 | 2004.949
2039-12-24 22:01 | 5444.17 | 1.5666 | 91.0956 | 74.6386 | 1595.5287
2039-12-25 23:01 | 4290.15 | 1.2794 | 90.6133 | 74.6386 | 1257.3189
2039-12-27 00:01 | 4041.04 | 1.2802 | 89.9477 | 74.6386 | 1184.3119
2039-12-28 01:01 | 3927.93 | 1.2464 | 89.7917 | 74.6386 | 1151.1626
2039-12-29 02:01 | 3978.08 | 1.2295 | 89.8933 | 74.6386 | 1165.8602
2039-12-30 03:01 | 3821.63 | 1.1757 | 89.846 | 74.6386 | 1120.0092
2039-12-31 04:01 | 3379.51 | 1.1219 | 89.2031 | 74.6386 | 990.4366
2040-01-01 05:01 | 3411.4 | 1.0719 | 89.5121 | 74.6386 | 999.7826
2040-01-02 06:01 | 4961.81 | 1.5771 | 89.3602 | 74.6386 | 1454.163
2040-01-03 07:01 | 7141.81 | 2.4296 | 88.9277 | 74.6386 | 2093.0579
2040-01-04 08:01 | 8103.25 | 2.7502 | 89.1219 | 74.6386 | 2374.8281
2040-01-05 09:01 | 10267.8 | 3.4616 | 89.3154 | 74.6386 | 3009.1951
2040-01-06 10:01 | 12242.8 | 4.1758 | 89.474 | 74.6386 | 3588.0105
2040-01-07 11:01 | 12786.6 | 4.3049 | 89.8648 | 74.6386 | 3747.3825
2040-01-08 12:01 | 14293.9 | 4.8064 | 90.0952 | 74.6386 | 4189.1286
2040-01-09 13:01 | 13579.4 | 4.3068 | 90.7737 | 74.6386 | 3979.7293
2040-01-10 14:01 | 15280.3 | 4.9322 | 90.7741 | 74.6386 | 4478.2139
2040-01-11 15:01 | 14957 | 4.57 | 91.4078 | 74.6386 | 4383.464
2040-01-12 16:01 | 14876 | 4.7205 | 91.2557 | 74.6386 | 4359.7252
2040-01-13 17:01 | 13045.6 | 4.1078 | 91.4215 | 74.6386 | 3823.288
2040-01-14 18:01 | 11710.7 | 3.6095 | 91.5407 | 74.6386 | 3432.0674
2040-01-15 19:01 | 10664.4 | 3.2808 | 91.4719 | 74.6386 | 3125.4271
2040-01-16 20:01 | 9665.75 | 3.0488 | 91.182 | 74.6386 | 2832.7517
2040-01-17 21:01 | 8891.35 | 2.7943 | 91.0875 | 74.6386 | 2605.7975
2040-01-18 22:01 | 8418.57 | 2.6373 | 90.9807 | 74.6386 | 2467.2393
2040-01-19 23:01 | 5728.61 | 1.6232 | 91.6803 | 74.6386 | 1678.8899
2040-01-21 00:01 | 4987.11 | 1.475 | 91.0664 | 74.6386 | 1461.5777
2040-01-22 01:01 | 4493.28 | 1.4345 | 90.2722 | 74.6386 | 1316.8504
2040-01-23 02:01 | 4295.89 | 1.3527 | 90.2076 | 74.6386 | 1259.0011
2040-01-24 03:01 | 4187.61 | 1.323 | 90.042 | 74.6386 | 1227.2673
2040-01-25 04:01 | 4032.17 | 1.2759 | 89.9036 | 74.6386 | 1181.7124
2040-01-26 05:01 | 3911.94 | 1.2216 | 89.9151 | 74.6386 | 1146.4764
2040-01-27 06:01 | 5436.82 | 1.8045 | 89.3891 | 74.6386 | 1593.3747
2040-01-28 07:01 | 6979.19 | 2.2523 | 89.6376 | 74.6386 | 2045.3987
2040-01-29 08:01 | 7650.42 | 2.378 | 90.037 | 74.6386 | 2242.1168
2040-01-30 09:01 | 9112.62 | 3.1222 | 89.4193 | 74.6386 | 2670.6453
2040-01-31 10:01 | 9673 | 3.1923 | 89.8235 | 74.6386 | 2834.8765
2040-02-01 11:01 | 10266.3 | 3.4789 | 89.7722 | 74.6386 | 3008.7555
2040-02-02 12:01 | 10361.2 | 3.4795 | 89.9534 | 74.6386 | 3036.568
2040-02-03 13:01 | 11565.6 | 3.7678 | 90.251 | 74.6386 | 3389.5428
2040-02-04 14:01 | 11544.9 | 3.6748 | 90.5671 | 74.6386 | 3383.4762
2040-02-05 15:01 | 10801.1 | 3.3425 | 90.8647 | 74.6386 | 3165.4899
2040-02-06 16:01 | 12541.4 | 4.1073 | 90.4428 | 74.6386 | 3675.5215
2040-02-07 17:01 | 10882.6 | 3.4686 | 90.8005 | 74.6386 | 3189.3752
2040-02-08 18:01 | 9493.34 | 3.0606 | 90.7055 | 74.6386 | 2782.2233
2040-02-09 19:01 | 9159.35 | 2.7411 | 91.1562 | 74.6386 | 2684.3405
2040-02-10 20:01 | 8189.25 | 2.5549 | 90.7734 | 74.6386 | 2400.0323
2040-02-11 21:01 | 7538.05 | 2.3717 | 90.6174 | 74.6386 | 2209.1844
2040-02-12 22:01 | 7201.38 | 2.2236 | 90.6351 | 74.6386 | 2110.5161
2040-02-13 23:01 | 4984.02 | 1.4338 | 91.1152 | 74.6386 | 1460.6721
2040-02-15 00:01 | 4209.76 | 1.2974 | 90.3618 | 74.6386 | 1233.7589
2040-02-16 01:01 | 3995.43 | 1.2944 | 89.7987 | 74.6386 | 1170.9449
2040-02-17 02:01 | 3981.34 | 1.2617 | 89.8355 | 74.6386 | 1166.8156
2040-02-18 03:01 | 4451.93 | 1.3913 | 89.8474 | 74.6386 | 1304.7319
2040-02-19 04:01 | 4921.85 | 1.5456 | 89.7526 | 74.6386 | 1442.4518
2040-02-20 05:01 | 5765.25 | 1.9053 | 89.3796 | 74.6386 | 1689.628
2040-02-21 06:01 | 5805.04 | 1.8672 | 89.6288 | 74.6386 | 1701.2893
2040-02-22 07:01 | 7176.46 | 2.3943 | 89.378 | 74.6386 | 2103.2128
2040-02-23 08:01 | 6657.48 | 2.0822 | 89.9542 | 74.6386 | 1951.1148
2040-02-24 09:01 | 7280.33 | 2.2934 | 89.9064 | 74.6386 | 2133.6541
2040-02-25 10:01 | 8483.18 | 2.6541 | 89.9907 | 74.6386 | 2486.1746
2040-02-26 11:01 | 9863.11 | 3.3079 | 89.5954 | 74.6386 | 2890.5922
2040-02-27 12:01 | 11610.4 | 4.0316 | 89.5221 | 74.6386 | 3402.6724
2040-02-28 13:01 | 11571.2 | 3.8081 | 90.113 | 74.6386 | 3391.184
2040-02-29 14:01 | 13204 | 4.3396 | 90.2569 | 74.6386 | 3869.7104
2040-03-01 15:01 | 13216.9 | 4.2199 | 90.6855 | 74.6386 | 3873.491
2040-03-02 16:01 | 12579.9 | 3.9394 | 90.9744 | 74.6386 | 3686.8048
2040-03-03 17:01 | 11666.6 | 3.7662 | 90.8001 | 74.6386 | 3419.1429
2040-03-04 18:01 | 10443.6 | 3.2723 | 91.011 | 74.6386 | 3060.717
2040-03-05 19:01 | 9930.08 | 3.0384 | 91.125 | 74.6386 | 2910.2192
2040-03-06 20:01 | 8309.94 | 2.4485 | 91.3616 | 74.6386 | 2435.403
2040-03-07 21:01 | 7312.07 | 2.2278 | 90.9545 | 74.6386 | 2142.9562
2040-03-08 22:01 | 5719.5 | 1.6174 | 91.4015 | 74.6386 | 1676.22
2040-03-09 23:01 | 5252.82 | 1.5808 | 90.7011 | 74.6386 | 1539.4496
2040-03-11 00:01 | 4721.7 | 1.5149 | 90.0618 | 74.6386 | 1383.7937
2040-03-12 01:01 | 4671.53 | 1.4648 | 90.0927 | 74.6386 | 1369.0903
2040-03-13 02:01 | 4490.76 | 1.4808 | 89.6151 | 74.6386 | 1316.1118
2040-03-14 03:01 | 4911.03 | 1.5847 | 89.6735 | 74.6386 | 1439.2808
2040-03-15 04:01 | 5405.01 | 1.7325 | 89.6845 | 74.6386 | 1584.0521
2040-03-16 05:01 | 6201.33 | 2.1029 | 89.2786 | 74.6386 | 1817.4304
2040-03-17 06:01 | 6446.35 | 2.0516 | 89.7819 | 74.6386 | 1889.2387
2040-03-18 07:01 | 7008.89 | 2.1499 | 90.0854 | 74.6386 | 2054.1029
2040-03-19 08:01 | 6285.87 | 1.9387 | 90.0999 | 74.6386 | 1842.2066
2040-03-20 09:01 | 6813.47 | 2.0926 | 90.1061 | 74.6386 | 1996.8309
2040-03-21 10:01 | 7968 | 2.6867 | 89.4415 | 74.6386 | 2335.1903
2040-03-22 11:01 | 10325.5 | 3.5105 | 89.4765 | 74.6386 | 3026.1053
2040-03-23 12:01 | 10391.6 | 3.3629 | 90.0483 | 74.6386 | 3045.4773
2040-03-24 13:01 | 10444.9 | 3.2847 | 90.3803 | 74.6386 | 3061.098
2040-03-25 14:01 | 10368.1 | 3.3194 | 90.329 | 74.6386 | 3038.5902
2040-03-26 15:01 | 11318.2 | 3.7077 | 90.2246 | 74.6386 | 3317.037
2040-03-27 16:01 | 11225.2 | 3.7194 | 90.2613 | 74.6386 | 3289.7814
2040-03-28 17:01 | 11451 | 3.5978 | 90.7058 | 74.6386 | 3355.9568
2040-03-29 18:01 | 10204.8 | 3.2548 | 90.6563 | 74.6386 | 2990.7317
2040-03-30 19:01 | 9760.86 | 3.045 | 90.7848 | 74.6386 | 2860.6257
2040-03-31 20:01 | 8222.05 | 2.4133 | 91.2396 | 74.6386 | 2409.645
2040-04-01 21:01 | 7641.17 | 2.3633 | 90.7184 | 74.6386 | 2239.4059
2040-04-02 22:01 | 6062.87 | 1.7548 | 91.1478 | 74.6386 | 1776.8518
2040-04-03 23:01 | 5070.92 | 1.5959 | 90.3128 | 74.6386 | 1486.14
2040-04-05 00:01 | 4524.62 | 1.429 | 90.1127 | 74.6386 | 1326.0352
2040-04-06 01:01 | 4244.11 | 1.3317 | 90.013 | 74.6386 | 1243.8259
2040-04-07 02:01 | 4389.06 | 1.339 | 90.1146 | 74.6386 | 1286.3065
2040-04-08 03:01 | 4865.65 | 1.4891 | 90.0065 | 74.6386 | 1425.9813
2040-04-09 04:01 | 5097.2 | 1.574 | 89.9094 | 74.6386 | 1493.8419
2040-04-10 05:01 | 4731.48 | 1.6131 | 89.1675 | 74.6386 | 1386.6599
2040-04-11 06:01 | 3036.77 | 1.1164 | 88.6127 | 74.6386 | 889.9894
2040-04-12 07:01 | 2897.94 | 1 | 91.7512 | 74.6386 | 849.3024
2040-04-13 08:01 | 2702.3 | 1 | 80.5837 | 74.6386 | 791.966
2040-04-14 09:01 | 0 | 0 | 81.7891 | 74.6386 | 0
2040-04-15 10:01 | 161.186 | 1 | 81.4113 | 74.6386 | 47.239
2040-04-16 11:01 | -85.9952 | 0.69696 | 80.9979 | 74.6386 | -25.2027
2040-04-17 12:01 | -221.813 | 0.97168 | 80.5982 | 74.6386 | -65.007
2040-04-18 13:01 | 3028.11 | 1.2249 | 86.8397 | 74.6386 | 887.4514
2040-04-19 14:01 | 5180.57 | 1.7833 | 87.9567 | 74.6386 | 1518.2752
2040-04-20 15:01 | 7125.28 | 2.3963 | 88.3096 | 74.6386 | 2088.2134
2040-04-21 16:01 | 6722.96 | 2.3392 | 88.2825 | 74.6386 | 1970.3051
2040-04-22 17:01 | 5454.8 | 1.8048 | 88.7175 | 74.6386 | 1598.6441
2040-04-23 18:01 | 3693.7 | 1.2529 | 88.5256 | 74.6386 | 1082.5166
2040-04-24 19:01 | 3028.81 | 1 | 89.3917 | 74.6386 | 887.6566
2040-04-25 20:01 | 2837.12 | 1 | 79.9181 | 74.6386 | 831.4778
2040-04-26 21:01 | 1236.43 | 1 | 80.6041 | 74.6386 | 362.3619
2040-04-27 22:01 | -714.811 | 2.1112 | 80.2204 | 74.6386 | -209.4904
2040-04-28 23:01 | -1241.98 | 3.1427 | 79.8378 | 74.6386 | -363.9884
2040-04-30 00:01 | -1523.75 | 3.7041 | 79.6299 | 74.6386 | -446.567
2040-05-01 01:01 | -1791.34 | 4.2701 | 79.4627 | 74.6386 | -524.9899
2040-05-02 02:01 | -1884.12 | 4.4442 | 79.2917 | 74.6386 | -552.1811
2040-05-03 03:01 | -2014.99 | 4.734 | 79.1398 | 74.6386 | -590.5353
2040-05-04 04:01 | -2078.64 | 4.8626 | 79.0113 | 74.6386 | -609.1892
2040-05-05 05:01 | -1783.72 | 4.1896 | 78.9068 | 74.6386 | -522.7567
2040-05-06 06:01 | -1780.83 | 4.2369 | 78.8565 | 74.6386 | -521.9098
2040-05-07 07:01 | -1264.72 | 3.0677 | 78.8091 | 74.6386 | -370.6528
2040-05-08 08:01 | -1081.48 | 2.7428 | 78.8219 | 74.6386 | -316.9505
2040-05-09 09:01 | 2526.61 | 1 | 78.5203 | 74.6386 | 740.4763
2040-05-10 10:01 | 3168.73 | 1 | 88.6287 | 74.6386 | 928.6631
2040-05-11 11:01 | 4603.08 | 1.4749 | 87.5492 | 74.6386 | 1349.0296
2040-05-12 12:01 | 5085.46 | 1.6487 | 87.6631 | 74.6386 | 1490.4012
2040-05-13 13:01 | 6149.76 | 1.9598 | 87.951 | 74.6386 | 1802.3167
2040-05-14 14:01 | 6655.14 | 2.145 | 88.0584 | 74.6386 | 1950.429
2040-05-15 15:01 | 7389.6 | 2.4276 | 88.0541 | 74.6386 | 2165.678
2040-05-16 16:01 | 6703.13 | 2.1783 | 88.2792 | 74.6386 | 1964.4935
2040-05-17 17:01 | 4679.72 | 1.5025 | 88.4156 | 74.6386 | 1371.4905
2040-05-18 18:01 | 3101.14 | 1 | 89.1966 | 74.6386 | 908.8544
2040-05-19 19:01 | 3019.3 | 1 | 79.3464 | 74.6386 | 884.8695
2040-05-20 20:01 | 0 | 0 | 80.7363 | 74.6386 | 0
2040-05-21 21:01 | -481.007 | 1.5752 | 79.7209 | 74.6386 | -140.9692
2040-05-22 22:01 | -1323.71 | 3.3819 | 79.3004 | 74.6386 | -387.9411
2040-05-23 23:01 | -1693.87 | 4.0925 | 79.0615 | 74.6386 | -496.4243
2040-05-25 00:01 | -1891.25 | 4.4931 | 78.8866 | 74.6386 | -554.2707
2040-05-26 01:01 | -2203.26 | 5.1795 | 78.7265 | 74.6386 | -645.7118
2040-05-27 02:01 | -2297.37 | 5.3486 | 78.5919 | 74.6386 | -673.2927
2040-05-28 03:01 | -2349.73 | 5.462 | 78.4725 | 74.6386 | -688.6379
2040-05-29 04:01 | -2306.02 | 5.3591 | 78.3737 | 74.6386 | -675.8277
2040-05-30 05:01 | -1952.38 | 4.5629 | 78.3037 | 74.6386 | -572.1861
2040-05-31 06:01 | -1918.88 | 4.549 | 78.2839 | 74.6386 | -562.3682
2040-06-01 07:01 | -1041.09 | 2.5535 | 78.2743 | 74.6386 | -305.1134
2040-06-02 08:01 | -218.852 | 0.84431 | 78.662 | 74.6386 | -64.1392
2040-06-03 09:01 | 2823.91 | 1 | 90.9692 | 74.6386 | 827.6063
2040-06-04 10:01 | 3936.3 | 1.3429 | 86.5216 | 74.6386 | 1153.6157
2040-06-05 11:01 | 5567.28 | 1.871 | 86.8483 | 74.6386 | 1631.6087
2040-06-06 12:01 | 6821.47 | 2.2763 | 87.1428 | 74.6386 | 1999.1755
2040-06-07 13:01 | 7806.58 | 2.5952 | 87.4195 | 74.6386 | 2287.8828
2040-06-08 14:01 | 8913.13 | 2.9706 | 87.6388 | 74.6386 | 2612.1805
2040-06-09 15:01 | 9791.85 | 3.2824 | 87.8198 | 74.6386 | 2869.708
2040-06-10 16:01 | 8810.78 | 3.0337 | 87.8586 | 74.6386 | 2582.1847
2040-06-11 17:01 | 6836.64 | 2.2661 | 88.2143 | 74.6386 | 2003.6214
2040-06-12 18:01 | 4838.53 | 1.5351 | 88.481 | 74.6386 | 1418.0332
2040-06-13 19:01 | 3607.2 | 1.1383 | 88.3821 | 74.6386 | 1057.166
2040-06-14 20:01 | 3016.35 | 1 | 79.2926 | 74.6386 | 884.0049
2040-06-15 21:01 | 0 | 0 | 80.6202 | 74.6386 | 0
2040-06-16 22:01 | -823.454 | 2.2588 | 79.4522 | 74.6386 | -241.3305
2040-06-17 23:01 | -1475.47 | 3.6808 | 79.1235 | 74.6386 | -432.4176
2040-06-19 00:01 | -1762.61 | 4.2326 | 78.897 | 74.6386 | -516.57
2040-06-20 01:01 | -2009.6 | 4.7593 | 78.7192 | 74.6386 | -588.9556
2040-06-21 02:01 | -2156.73 | 5.0627 | 78.5499 | 74.6386 | -632.0752
2040-06-22 03:01 | -2292.04 | 5.3554 | 78.4198 | 74.6386 | -671.7306
2040-06-23 04:01 | -2435 | 5.6666 | 78.3053 | 74.6386 | -713.6281
2040-06-24 05:01 | -2510.68 | 5.8221 | 78.2053 | 74.6386 | -735.8077
2040-06-25 06:01 | -1931.09 | 4.4869 | 78.1279 | 74.6386 | -565.9466
2040-06-26 07:01 | -618.295 | 1.6021 | 78.2086 | 74.6386 | -181.2044
2040-06-27 08:01 | 226.804 | 1 | 79.0753 | 74.6386 | 66.4697
2040-06-28 09:01 | 2668.95 | 1 | 87.8277 | 74.6386 | 782.192
2040-06-29 10:01 | 5134.75 | 1.6185 | 86.9747 | 74.6386 | 1504.8467
2040-06-30 11:01 | 7246.26 | 2.315 | 87.1744 | 74.6386 | 2123.6692
2040-07-01 12:01 | 8218.3 | 2.6539 | 87.4208 | 74.6386 | 2408.546
2040-07-02 13:01 | 9078.76 | 2.9323 | 87.6851 | 74.6386 | 2660.7219
2040-07-03 14:01 | 9820.18 | 3.1619 | 87.9541 | 74.6386 | 2878.0107
2040-07-04 15:01 | 9403.95 | 3.1189 | 87.9619 | 74.6386 | 2756.0257
2040-07-05 16:01 | 11172.8 | 3.6488 | 88.1965 | 74.6386 | 3274.4245
2040-07-06 17:01 | 8256.23 | 2.6688 | 88.5133 | 74.6386 | 2419.6622
2040-07-07 18:01 | 6578.31 | 2.0485 | 88.7584 | 74.6386 | 1927.9124
2040-07-08 19:01 | 5089.08 | 1.5833 | 88.6486 | 74.6386 | 1491.4621
2040-07-09 20:01 | 3815.19 | 1.2017 | 88.4296 | 74.6386 | 1118.1218
2040-07-10 21:01 | 3048.28 | 1 | 88.4649 | 74.6386 | 893.3627
2040-07-11 22:01 | 3112.57 | 1 | 93.1609 | 74.6386 | 912.2042
2040-07-12 23:01 | 0 | 0 | 80.5315 | 74.6386 | 0
2040-07-14 00:01 | -575.754 | 1.6564 | 79.4173 | 74.6386 | -168.7368
2040-07-15 01:01 | -982.812 | 2.6167 | 79.1288 | 74.6386 | -288.0338
2040-07-16 02:01 | -1185.02 | 3.0071 | 78.9214 | 74.6386 | -347.2951
2040-07-17 03:01 | -1327.48 | 3.3046 | 78.7607 | 74.6386 | -389.046
2040-07-18 04:01 | -1462.99 | 3.5948 | 78.5973 | 74.6386 | -428.76
2040-07-19 05:01 | -1436.93 | 3.5173 | 78.4983 | 74.6386 | -421.1226
2040-07-20 06:01 | -1503.75 | 3.6776 | 78.4277 | 74.6386 | -440.7056
2040-07-21 07:01 | 0 | 1 | 79.3313 | 74.6386 | 0
2040-07-22 08:01 | 3039.41 | 1.1802 | 85.4873 | 74.6386 | 890.7631
2040-07-23 09:01 | 3945.18 | 1.3108 | 86.7438 | 74.6386 | 1156.2181
2040-07-24 10:01 | 5587 | 1.8804 | 86.8218 | 74.6386 | 1637.3881
2040-07-25 11:01 | 7264.54 | 2.4835 | 86.931 | 74.6386 | 2129.0265
2040-07-26 12:01 | 8572 | 2.8908 | 87.3017 | 74.6386 | 2512.2052
2040-07-27 13:01 | 9205.22 | 2.9615 | 87.9075 | 74.6386 | 2697.7837
2040-07-28 14:01 | 9264.21 | 2.9857 | 88.0938 | 74.6386 | 2715.0719
2040-07-29 15:01 | 8445.67 | 2.7496 | 88.1669 | 74.6386 | 2475.1815
2040-07-30 16:01 | 7398.85 | 2.3374 | 88.4356 | 74.6386 | 2168.3889
2040-07-31 17:01 | 7651.54 | 2.508 | 88.1491 | 74.6386 | 2242.445
2040-08-01 18:01 | 6078.71 | 1.9457 | 88.3707 | 74.6386 | 1781.494
2040-08-02 19:01 | 4969.11 | 1.5627 | 88.4326 | 74.6386 | 1456.3024
2040-08-03 20:01 | 3842.44 | 1.2237 | 88.2156 | 74.6386 | 1126.108
2040-08-04 21:01 | 3141.84 | 1 | 88.2724 | 74.6386 | 920.7824
2040-08-05 22:01 | 3108.93 | 1 | 90.0541 | 74.6386 | 911.1374
2040-08-06 23:01 | 3054.19 | 1 | 78.9837 | 74.6386 | 895.0947
2040-08-08 00:01 | 0 | 0 | 80.4054 | 74.6386 | 0
2040-08-09 01:01 | -605.679 | 1.769 | 79.3211 | 74.6386 | -177.507
2040-08-10 02:01 | -786.123 | 2.1692 | 79.067 | 74.6386 | -230.3899
2040-08-11 03:01 | -967.933 | 2.5522 | 78.8992 | 74.6386 | -283.6732
2040-08-12 04:01 | -911.19 | 2.399 | 78.7811 | 74.6386 | -267.0434
2040-08-13 05:01 | -912.193 | 2.4152 | 78.6819 | 74.6386 | -267.3374
2040-08-14 06:01 | -521.393 | 1.5336 | 78.7154 | 74.6386 | -152.8052
2040-08-15 07:01 | 2210.38 | 1 | 78.4328 | 74.6386 | 647.7984
2040-08-16 08:01 | 3367.66 | 1.0768 | 87.0802 | 74.6386 | 986.9637
2040-08-17 09:01 | 4910.52 | 1.545 | 87.3516 | 74.6386 | 1439.1314
2040-08-18 10:01 | 7139.79 | 2.3273 | 87.2702 | 74.6386 | 2092.4659
2040-08-19 11:01 | 8323.4 | 2.7946 | 87.328 | 74.6386 | 2439.3477
2040-08-20 12:01 | 9534.96 | 3.1426 | 87.7272 | 74.6386 | 2794.4209
2040-08-21 13:01 | 9844.87 | 3.2533 | 87.9526 | 74.6386 | 2885.2466
2040-08-22 14:01 | 9838.19 | 3.1994 | 88.26 | 74.6386 | 2883.2889
2040-08-23 15:01 | 9163.93 | 2.9645 | 88.4413 | 74.6386 | 2685.6828
2040-08-24 16:01 | 9119.25 | 2.9365 | 88.5322 | 74.6386 | 2672.5884
2040-08-25 17:01 | 7376.95 | 2.3351 | 88.7262 | 74.6386 | 2161.9706
2040-08-26 18:01 | 6327.39 | 2.0056 | 88.6566 | 74.6386 | 1854.375
2040-08-27 19:01 | 4970.11 | 1.5237 | 88.8117 | 74.6386 | 1456.5955
2040-08-28 20:01 | 3923.24 | 1.2438 | 88.4241 | 74.6386 | 1149.7881
2040-08-29 21:01 | 3013.41 | 1 | 79.3623 | 74.6386 | 883.1433
2040-08-30 22:01 | 3033.66 | 1 | 79.1843 | 74.6386 | 889.078
2040-08-31 23:01 | -395.364 | 1.409 | 79.8866 | 74.6386 | -115.8698
2040-09-02 00:01 | -805.958 | 2.2322 | 79.3709 | 74.6386 | -236.203
2040-09-03 01:01 | -1012.42 | 2.6425 | 79.0882 | 74.6386 | -296.711
2040-09-04 02:01 | -1238.55 | 3.1263 | 78.9043 | 74.6386 | -362.9832
2040-09-05 03:01 | -1232.72 | 3.0817 | 78.7557 | 74.6386 | -361.2746
2040-09-06 04:01 | -1146.45 | 2.8938 | 78.6367 | 74.6386 | -335.9913
2040-09-07 05:01 | -1086.81 | 2.7748 | 78.5837 | 74.6386 | -318.5126
2040-09-08 06:01 | -575.969 | 1.6307 | 78.6231 | 74.6386 | -168.7999
2040-09-09 07:01 | 1184.09 | 1 | 78.8704 | 74.6386 | 347.0225
2040-09-10 08:01 | 3064.44 | 1 | 78.0616 | 74.6386 | 898.0987
2040-09-11 09:01 | 3024.14 | 1 | 78.2542 | 74.6386 | 886.2879
2040-09-12 10:01 | 3112.65 | 1 | 78.2758 | 74.6386 | 912.2277
2040-09-13 11:01 | 3200.45 | 1 | 91.043 | 74.6386 | 937.9593
2040-09-14 12:01 | 6207.48 | 2.0525 | 87.0153 | 74.6386 | 1819.2328
2040-09-15 13:01 | 4837.03 | 1.5189 | 87.6404 | 74.6386 | 1417.5936
2040-09-16 14:01 | 7052.85 | 2.2448 | 87.5551 | 74.6386 | 2066.9863
2040-09-17 15:01 | 5988.15 | 1.9107 | 87.7108 | 74.6386 | 1754.9535
2040-09-18 16:01 | 7070 | 2.3304 | 87.5238 | 74.6386 | 2072.0125
2040-09-19 17:01 | 6484.96 | 2.1086 | 87.7525 | 74.6386 | 1900.5542
2040-09-20 18:01 | 6197.55 | 1.9592 | 87.9986 | 74.6386 | 1816.3226
2040-09-21 19:01 | 5378.07 | 1.6187 | 88.403 | 74.6386 | 1576.1567
2040-09-22 20:01 | 4707.84 | 1.469 | 88.0775 | 74.6386 | 1379.7317
2040-09-23 21:01 | 3069.24 | 1 | 89.817 | 74.6386 | 899.5055
2040-09-24 22:01 | 3027.15 | 1 | 91.2582 | 74.6386 | 887.1701
2040-09-25 23:01 | 2977.14 | 1 | 78.8036 | 74.6386 | 872.5136
2040-09-27 00:01 | 0 | 0 | 80.1984 | 74.6386 | 0
2040-09-28 01:01 | -159.037 | 0.76435 | 79.457 | 74.6386 | -46.6091
2040-09-29 02:01 | -396.979 | 1.3711 | 79.0942 | 74.6386 | -116.3431
2040-09-30 03:01 | -352.909 | 1.2297 | 79.002 | 74.6386 | -103.4274
2040-10-01 04:01 | -358.147 | 1.2527 | 78.9135 | 74.6386 | -104.9625
2040-10-02 05:01 | -226.445 | 0.9564 | 78.9454 | 74.6386 | -66.3645
2040-10-03 06:01 | 0 | 1 | 79.4678 | 74.6386 | 0
2040-10-04 07:01 | 2897.27 | 1 | 78.0384 | 74.6386 | 849.106
2040-10-05 08:01 | 4429.35 | 1.4345 | 86.9301 | 74.6386 | 1298.1143
2040-10-06 09:01 | 5828.45 | 1.8885 | 87.1197 | 74.6386 | 1708.1501
2040-10-07 10:01 | 7984.4 | 2.6833 | 87.0578 | 74.6386 | 2339.9967
2040-10-08 11:01 | 9714.5 | 3.2562 | 87.3601 | 74.6386 | 2847.0389
2040-10-09 12:01 | 8799.02 | 2.914 | 87.7707 | 74.6386 | 2578.7382
2040-10-10 13:01 | 10473.3 | 3.464 | 87.9058 | 74.6386 | 3069.4212
2040-10-11 14:01 | 8929.6 | 2.8252 | 88.4546 | 74.6386 | 2617.0074
2040-10-12 15:01 | 7705.42 | 2.3503 | 88.7904 | 74.6386 | 2258.2357
2040-10-13 16:01 | 9824.72 | 3.1938 | 88.2602 | 74.6386 | 2879.3412
2040-10-14 17:01 | 8544.38 | 2.6802 | 88.6882 | 74.6386 | 2504.1106
2040-10-15 18:01 | 8224.45 | 2.5685 | 88.7584 | 74.6386 | 2410.3484
2040-10-16 19:01 | 7018.11 | 2.1814 | 88.7745 | 74.6386 | 2056.805
2040-10-17 20:01 | 6144.86 | 1.8747 | 88.8567 | 74.6386 | 1800.8807
2040-10-18 21:01 | 4062.85 | 1.2412 | 88.7777 | 74.6386 | 1190.7038
2040-10-19 22:01 | 3245.44 | 1.0208 | 88.3403 | 74.6386 | 951.1446
2040-10-20 23:01 | 3169.32 | 1 | 79.1095 | 74.6386 | 928.836
2040-10-22 00:01 | 3124.14 | 1 | 79.0323 | 74.6386 | 915.5951
2040-10-23 01:01 | 3132.6 | 1 | 78.948 | 74.6386 | 918.0744
2040-10-24 02:01 | 3139.07 | 1 | 78.8903 | 74.6386 | 919.9706
2040-10-25 03:01 | 3254.17 | 1 | 78.8151 | 74.6386 | 953.7031
2040-10-26 04:01 | 3158.41 | 1 | 78.847 | 74.6386 | 925.6386
2040-10-27 05:01 | 3159.95 | 1 | 78.8295 | 74.6386 | 926.0899
2040-10-28 06:01 | 3192.75 | 1 | 78.7995 | 74.6386 | 935.7027
2040-10-29 07:01 | 3662.33 | 1.1354 | 87.9642 | 74.6386 | 1073.323
2040-10-30 08:01 | 6452.57 | 2.095 | 87.6207 | 74.6386 | 1891.0616
2040-10-31 09:01 | 7595.47 | 2.5241 | 87.6702 | 74.6386 | 2226.0125
2040-11-01 10:01 | 9517.98 | 3.1514 | 87.9003 | 74.6386 | 2789.4446
2040-11-02 11:01 | 8409.99 | 2.5583 | 88.7856 | 74.6386 | 2464.7248
2040-11-03 12:01 | 11077.9 | 3.7233 | 88.1305 | 74.6386 | 3246.612
2040-11-04 13:01 | 11498.7 | 3.7679 | 88.5859 | 74.6386 | 3369.9363
2040-11-05 14:01 | 11215.8 | 3.6492 | 88.8451 | 74.6386 | 3287.0265
2040-11-06 15:01 | 8996.78 | 2.7882 | 89.32 | 74.6386 | 2636.6959
2040-11-07 16:01 | 10332.2 | 3.3945 | 88.8001 | 74.6386 | 3028.0689
2040-11-08 17:01 | 9359.19 | 2.9431 | 89.2329 | 74.6386 | 2742.9078
2040-11-09 18:01 | 8927.13 | 2.8177 | 89.2113 | 74.6386 | 2616.2835
2040-11-10 19:01 | 8040.91 | 2.4332 | 89.5115 | 74.6386 | 2356.5581
2040-11-11 20:01 | 7369.29 | 2.2475 | 89.3839 | 74.6386 | 2159.7257
2040-11-12 21:01 | 5675.1 | 1.6769 | 89.5836 | 74.6386 | 1663.2076
2040-11-13 22:01 | 4817.66 | 1.5136 | 88.9425 | 74.6386 | 1411.9168
2040-11-14 23:01 | 3257.72 | 1 | 90.7432 | 74.6386 | 954.7435
2040-11-16 00:01 | 3154.15 | 1 | 79.5417 | 74.6386 | 924.3901
2040-11-17 01:01 | 3125.89 | 1 | 79.4175 | 74.6386 | 916.1079
2040-11-18 02:01 | 3152.74 | 1 | 79.3064 | 74.6386 | 923.9769
2040-11-19 03:01 | 3229.86 | 1 | 79.2112 | 74.6386 | 946.5785
2040-11-20 04:01 | 3230.55 | 1 | 79.1611 | 74.6386 | 946.7807
2040-11-21 05:01 | 3229.72 | 1 | 91.5453 | 74.6386 | 946.5375
2040-11-22 06:01 | 3792.77 | 1.1773 | 88.2818 | 74.6386 | 1111.5512
2040-11-23 07:01 | 4855.25 | 1.5089 | 88.2903 | 74.6386 | 1422.9333
2040-11-24 08:01 | 7437.28 | 2.5715 | 87.5883 | 74.6386 | 2179.6516
2040-11-25 09:01 | 8847.11 | 2.912 | 88.1544 | 74.6386 | 2592.832
2040-11-26 10:01 | 9717.53 | 3.2985 | 88.1553 | 74.6386 | 2847.9269
2040-11-27 11:01 | 11320.6 | 3.6824 | 88.6583 | 74.6386 | 3317.7404
2040-11-28 12:01 | 12215.1 | 3.9931 | 88.8743 | 74.6386 | 3579.8924
2040-11-29 13:01 | 12358.6 | 3.9628 | 89.2503 | 74.6386 | 3621.9481
2040-11-30 14:01 | 9359.03 | 2.8569 | 89.7805 | 74.6386 | 2742.8609
2040-12-01 15:01 | 10523.3 | 3.3348 | 89.3938 | 74.6386 | 3084.0748
2040-12-02 16:01 | 10162.8 | 3.2494 | 89.3886 | 74.6386 | 2978.4227
2040-12-03 17:01 | 9424.18 | 2.988 | 89.4928 | 74.6386 | 2761.9545
2040-12-04 18:01 | 9111.52 | 2.8552 | 89.5443 | 74.6386 | 2670.3229
2040-12-05 19:01 | 8108.52 | 2.5199 | 89.575 | 74.6386 | 2376.3726
2040-12-06 20:01 | 7443.59 | 2.2829 | 89.62 | 74.6386 | 2181.5009
2040-12-07 21:01 | 5699.61 | 1.6627 | 89.9331 | 74.6386 | 1670.3908
2040-12-08 22:01 | 4765.1 | 1.4652 | 89.3462 | 74.6386 | 1396.513
2040-12-09 23:01 | 3084.48 | 1 | 90.8735 | 74.6386 | 903.9719
2040-12-11 00:01 | 3019.86 | 1 | 79.798 | 74.6386 | 885.0336
2040-12-12 01:01 | 3076.79 | 1 | 79.6177 | 74.6386 | 901.7181
2040-12-13 02:01 | 3138.83 | 1 | 79.499 | 74.6386 | 919.9003
2040-12-14 03:01 | 3071.41 | 1 | 79.4614 | 74.6386 | 900.1414
2040-12-15 04:01 | 3195.18 | 1 | 79.3374 | 74.6386 | 936.4148
2040-12-16 05:01 | 3170.11 | 1 | 79.3212 | 74.6386 | 929.0675
2040-12-17 06:01 | 3202.6 | 1 | 79.2732 | 74.6386 | 938.5894
2040-12-18 07:01 | 3877.38 | 1.1711 | 88.6275 | 74.6386 | 1136.3479
2040-12-19 08:01 | 7110.35 | 2.3335 | 87.998 | 74.6386 | 2083.8379
2040-12-20 09:01 | 7767.4 | 2.5364 | 88.2693 | 74.6386 | 2276.4002
2040-12-21 10:01 | 7948.06 | 2.5704 | 88.5062 | 74.6386 | 2329.3464
2040-12-22 11:01 | 9614.21 | 3.2824 | 88.2247 | 74.6386 | 2817.6468
2040-12-23 12:01 | 8306.9 | 2.642 | 88.9366 | 74.6386 | 2434.5121
2040-12-24 13:01 | 7661.63 | 2.4244 | 89.012 | 74.6386 | 2245.4021
2040-12-25 14:01 | 6803.48 | 2.0434 | 89.3772 | 74.6386 | 1993.9032
2040-12-26 15:01 | 6525.48 | 2.0669 | 88.906 | 74.6386 | 1912.4294
2040-12-27 16:01 | 6281.73 | 1.9817 | 88.8877 | 74.6386 | 1840.9933
2040-12-28 17:01 | 8218.48 | 2.8191 | 88.2272 | 74.6386 | 2408.5987
2040-12-29 18:01 | 7427.89 | 2.3807 | 88.8343 | 74.6386 | 2176.8997
2040-12-30 19:01 | 6790.65 | 2.0986 | 89.1229 | 74.6386 | 1990.1431
2040-12-31 20:01 | 6191.74 | 1.8926 | 89.1577 | 74.6386 | 1814.6199
2041-01-01 21:01 | 5772.38 | 1.7581 | 89.1359 | 74.6386 | 1691.7176
2041-01-02 22:01 | 5416.99 | 1.6592 | 89.0489 | 74.6386 | 1587.5631
2041-01-03 23:01 | 5074.14 | 1.5871 | 88.8173 | 74.6386 | 1487.0836
2041-01-05 00:01 | 3107.75 | 1 | 79.6987 | 74.6386 | 910.7916
2041-01-06 01:01 | 3078.78 | 1 | 79.5372 | 74.6386 | 902.3013
2041-01-07 02:01 | 3109.25 | 1 | 79.4248 | 74.6386 | 911.2312
2041-01-08 03:01 | 3148.37 | 1 | 79.3562 | 74.6386 | 922.6962
2041-01-09 04:01 | 3084.11 | 1 | 79.3456 | 74.6386 | 903.8634
2041-01-10 05:01 | 1076.73 | 1 | 80.2588 | 74.6386 | 315.5584
2041-01-11 06:01 | 3219.75 | 1 | 79.0438 | 74.6386 | 943.6156
2041-01-12 07:01 | 3167.13 | 1 | 91.2555 | 74.6386 | 928.1942
2041-01-13 08:01 | 4240.89 | 1.2871 | 88.4299 | 74.6386 | 1242.8822
2041-01-14 09:01 | 3250.8 | 1 | 88.647 | 74.6386 | 952.7154
2041-01-15 10:01 | 3237.05 | 1 | 88.5788 | 74.6386 | 948.6857
2041-01-16 11:01 | 3877.63 | 1.2229 | 88.0556 | 74.6386 | 1136.4212
2041-01-17 12:01 | 4610.68 | 1.4609 | 88.0302 | 74.6386 | 1351.2569
2041-01-18 13:01 | 4544.05 | 1.4862 | 87.844 | 74.6386 | 1331.7296
2041-01-19 14:01 | 3685.68 | 1.1621 | 88.1147 | 74.6386 | 1080.1662
2041-01-20 15:01 | 3979.92 | 1.2463 | 88.1011 | 74.6386 | 1166.3994
2041-01-21 16:01 | 3572.61 | 1.1501 | 87.8814 | 74.6386 | 1047.0286
2041-01-22 17:01 | 6377.4 | 2.1932 | 87.3755 | 74.6386 | 1869.0314
2041-01-23 18:01 | 5871.35 | 1.8648 | 88.1108 | 74.6386 | 1720.7228
2041-01-24 19:01 | 5277.04 | 1.6449 | 88.3049 | 74.6386 | 1546.5478
2041-01-25 20:01 | 4931.36 | 1.4983 | 88.4813 | 74.6386 | 1445.239
2041-01-26 21:01 | 4262.75 | 1.4131 | 87.8225 | 74.6386 | 1249.2887
2041-01-27 22:01 | 4101.73 | 1.2977 | 88.1349 | 74.6386 | 1202.0984
2041-01-28 23:01 | 3972.35 | 1.2711 | 88.0029 | 74.6386 | 1164.1809
2041-01-30 00:01 | 3138.56 | 1 | 79.0648 | 74.6386 | 919.8211
2041-01-31 01:01 | 3140.2 | 1 | 78.9865 | 74.6386 | 920.3018
2041-02-01 02:01 | 3284.3 | 1 | 78.8763 | 74.6386 | 962.5333
2041-02-02 03:01 | 3136.85 | 1 | 78.9404 | 74.6386 | 919.32
2041-02-03 04:01 | 3216.95 | 1 | 78.8836 | 74.6386 | 942.795
2041-02-04 05:01 | 3114.72 | 1 | 78.913 | 74.6386 | 912.8343
2041-02-05 06:01 | 3098.12 | 1 | 91.1611 | 74.6386 | 907.9693
2041-02-06 07:01 | 3224.22 | 1 | 89.7311 | 74.6386 | 944.9256
2041-02-07 08:01 | 3143.79 | 1 | 87.8561 | 74.6386 | 921.3539
2041-02-08 09:01 | 3184.9 | 1 | 92.9203 | 74.6386 | 933.4021
2041-02-09 10:01 | 3257.31 | 1 | 88.9977 | 74.6386 | 954.6233
2041-02-10 11:01 | 3836 | 1.1992 | 87.8572 | 74.6386 | 1124.2206
2041-02-11 12:01 | 4400.73 | 1.4943 | 87.2823 | 74.6386 | 1289.7266
2041-02-12 13:01 | 4284.35 | 1.4673 | 87.27 | 74.6386 | 1255.619
2041-02-13 14:01 | 5488.98 | 1.8722 | 87.3106 | 74.6386 | 1608.6612
2041-02-14 15:01 | 5532.56 | 1.835 | 87.6061 | 74.6386 | 1621.4333
2041-02-15 16:01 | 7070.39 | 2.3316 | 87.7125 | 74.6386 | 2072.1268
2041-02-16 17:01 | 5934.31 | 1.9374 | 87.9262 | 74.6386 | 1739.1746
2041-02-17 18:01 | 5628.58 | 1.8316 | 87.9525 | 74.6386 | 1649.574
2041-02-18 19:01 | 4778.46 | 1.5143 | 88.1386 | 74.6386 | 1400.4284
2041-02-19 20:01 | 3859.16 | 1.2577 | 87.8795 | 74.6386 | 1131.0082
2041-02-20 21:01 | 3071.7 | 1 | 79.0522 | 74.6386 | 900.2264
2041-02-21 22:01 | 3002.9 | 1 | 78.9678 | 74.6386 | 880.0631
2041-02-22 23:01 | -188.511 | 0.94122 | 79.8751 | 74.6386 | -55.2471
2041-02-24 00:01 | -539.003 | 1.6711 | 79.2992 | 74.6386 | -157.9662
2041-02-25 01:01 | -722.501 | 2.0347 | 79.0231 | 74.6386 | -211.7441
2041-02-26 02:01 | -845.917 | 2.2889 | 78.8516 | 74.6386 | -247.9138
2041-02-27 03:01 | -1003.53 | 2.6289 | 78.6989 | 74.6386 | -294.1056
2041-02-28 04:01 | -927.661 | 2.4359 | 78.5633 | 74.6386 | -271.8706
2041-03-01 05:01 | -803.107 | 2.1704 | 78.5154 | 74.6386 | -235.3674
2041-03-02 06:01 | -431.369 | 1.3518 | 78.5747 | 74.6386 | -126.4218
2041-03-03 07:01 | 2514.66 | 1 | 78.083 | 74.6386 | 736.9741
2041-03-04 08:01 | 3342.33 | 1.0352 | 87.1244 | 74.6386 | 979.5402
2041-03-05 09:01 | 4861.73 | 1.532 | 87.1301 | 74.6386 | 1424.8324
2041-03-06 10:01 | 7237.42 | 2.3493 | 87.089 | 74.6386 | 2121.0784
2041-03-07 11:01 | 6927.19 | 2.2771 | 87.3076 | 74.6386 | 2030.159
2041-03-08 12:01 | 7685.13 | 2.4735 | 87.636 | 74.6386 | 2252.2893
2041-03-09 13:01 | 6945.8 | 2.252 | 87.7435 | 74.6386 | 2035.613
2041-03-10 14:01 | 6595.26 | 2.0607 | 88.0954 | 74.6386 | 1932.8799
2041-03-11 15:01 | 8045.35 | 2.6504 | 87.7443 | 74.6386 | 2357.8593
2041-03-12 16:01 | 8416.58 | 2.7589 | 87.9206 | 74.6386 | 2466.6561
2041-03-13 17:01 | 7021.47 | 2.1802 | 88.4558 | 74.6386 | 2057.7897
2041-03-14 18:01 | 6132.53 | 1.9263 | 88.3471 | 74.6386 | 1797.2671
2041-03-15 19:01 | 4538.85 | 1.4425 | 88.204 | 74.6386 | 1330.2056
2041-03-16 20:01 | 3153.17 | 1.0467 | 87.7697 | 74.6386 | 924.1029
2041-03-17 21:01 | 2996.17 | 1 | 79.0193 | 74.6386 | 878.0907
2041-03-18 22:01 | 0 | 0 | 80.3333 | 74.6386 | 0
2041-03-19 23:01 | -815.06 | 2.3022 | 79.1968 | 74.6386 | -238.8705
2041-03-21 00:01 | -1162.08 | 2.9808 | 78.8591 | 74.6386 | -340.572
2041-03-22 01:01 | -1434.02 | 3.5514 | 78.6556 | 74.6386 | -420.2698
2041-03-23 02:01 | -1543.83 | 3.7634 | 78.4957 | 74.6386 | -452.4519
2041-03-24 03:01 | -1575.04 | 3.8241 | 78.3474 | 74.6386 | -461.5987
2041-03-25 04:01 | -1528.56 | 3.7177 | 78.2461 | 74.6386 | -447.9767
2041-03-26 05:01 | -1419.61 | 3.4805 | 78.1762 | 74.6386 | -416.0466
2041-03-27 06:01 | -968.667 | 2.4744 | 78.1531 | 74.6386 | -283.8883
2041-03-28 07:01 | 2051.27 | 1 | 78.0605 | 74.6386 | 601.1679
2041-03-29 08:01 | 3115.92 | 1.2636 | 85.0809 | 74.6386 | 913.186
2041-03-30 09:01 | 5075.81 | 1.725 | 86.3608 | 74.6386 | 1487.5731
2041-03-31 10:01 | 7563.58 | 2.594 | 86.524 | 74.6386 | 2216.6665
2041-04-01 11:01 | 9369.69 | 3.1753 | 86.9435 | 74.6386 | 2745.9851
2041-04-02 12:01 | 10518.9 | 3.5782 | 87.2679 | 74.6386 | 3082.7853
2041-04-03 13:01 | 11418.3 | 3.7242 | 87.8669 | 74.6386 | 3346.3734
2041-04-04 14:01 | 11291.8 | 3.6921 | 88.1331 | 74.6386 | 3309.2999
2041-04-05 15:01 | 11064.2 | 3.5768 | 88.4115 | 74.6386 | 3242.5969
2041-04-06 16:01 | 10910.5 | 3.4693 | 88.6632 | 74.6386 | 3197.5519
2041-04-07 17:01 | 8660.93 | 2.7214 | 88.8619 | 74.6386 | 2538.268
2041-04-08 18:01 | 7737.41 | 2.3538 | 89.0442 | 74.6386 | 2267.611
2041-04-09 19:01 | 6008.08 | 1.8365 | 88.9227 | 74.6386 | 1760.7944
2041-04-10 20:01 | 4981.41 | 1.539 | 88.6994 | 74.6386 | 1459.9072
2041-04-11 21:01 | 3106.26 | 1 | 91.1304 | 74.6386 | 910.3549
2041-04-12 22:01 | 3048.98 | 1 | 79.1834 | 74.6386 | 893.5678
2041-04-13 23:01 | 0 | 0 | 80.5232 | 74.6386 | 0
2041-04-15 00:01 | -318.231 | 1.0783 | 79.5037 | 74.6386 | -93.2643
2041-04-16 01:01 | -657.175 | 1.9272 | 79.1655 | 74.6386 | -192.599
2041-04-17 02:01 | -842.823 | 2.2881 | 78.9283 | 74.6386 | -247.007
2041-04-18 03:01 | -1057.44 | 2.7492 | 78.7454 | 74.6386 | -309.9051
2041-04-19 04:01 | -973.303 | 2.5289 | 78.5979 | 74.6386 | -285.247
2041-04-20 05:01 | -938.92 | 2.4695 | 78.5324 | 74.6386 | -275.1703
2041-04-21 06:01 | -453.41 | 1.3785 | 78.5872 | 74.6386 | -132.8814
2041-04-22 07:01 | 2335.14 | 1 | 78.2062 | 74.6386 | 684.362
2041-04-23 08:01 | 4298.16 | 1.3943 | 86.801 | 74.6386 | 1259.6664
2041-04-24 09:01 | 6223.08 | 2.1203 | 86.6643 | 74.6386 | 1823.8047
2041-04-25 10:01 | 8235.64 | 2.8941 | 86.6938 | 74.6386 | 2413.6278
2041-04-26 11:01 | 9882.7 | 3.4324 | 87.0807 | 74.6386 | 2896.3335
2041-04-27 12:01 | 11572.8 | 3.8873 | 87.6346 | 74.6386 | 3391.6529
2041-04-28 13:01 | 12049 | 3.9595 | 88.1161 | 74.6386 | 3531.2133
2041-04-29 14:01 | 12364.6 | 4.0149 | 88.458 | 74.6386 | 3623.7066
2041-04-30 15:01 | 11837.8 | 3.8487 | 88.6564 | 74.6386 | 3469.3167
2041-05-01 16:01 | 11696.4 | 3.7682 | 88.8449 | 74.6386 | 3427.8765
2041-05-02 17:01 | 9721.33 | 3.0646 | 89.1148 | 74.6386 | 2849.0406
2041-05-03 18:01 | 8462.95 | 2.5723 | 89.3472 | 74.6386 | 2480.2458
2041-05-04 19:01 | 6824.97 | 2.0712 | 89.2682 | 74.6386 | 2000.2013
2041-05-05 20:01 | 5735.95 | 1.7621 | 89.0259 | 74.6386 | 1681.041
2041-05-06 21:01 | 3268.59 | 1.0496 | 88.5401 | 74.6386 | 957.9292
2041-05-07 22:01 | 3167 | 1 | 92.375 | 74.6386 | 928.1561
2041-05-08 23:01 | 0 | 0 | 80.7345 | 74.6386 | 0
2041-05-10 00:01 | 50.4192 | 1 | 80.3643 | 74.6386 | 14.7764
2041-05-11 01:01 | -221.202 | 0.99596 | 79.6418 | 74.6386 | -64.8279
2041-05-12 02:01 | -414.4 | 1.3897 | 79.2916 | 74.6386 | -121.4487
2041-05-13 03:01 | -598.186 | 1.7759 | 79.0584 | 74.6386 | -175.311
2041-05-14 04:01 | -470.071 | 1.4628 | 78.9525 | 74.6386 | -137.7642
2041-05-15 05:01 | -481.179 | 1.5115 | 78.8888 | 74.6386 | -141.0196
2041-05-16 06:01 | -69.6744 | 0.58518 | 79.6591 | 74.6386 | -20.4196
2041-05-17 07:01 | 2518.54 | 1 | 89.1749 | 74.6386 | 738.1112
2041-05-18 08:01 | 4961.67 | 1.6934 | 86.6108 | 74.6386 | 1454.1219
2041-05-19 09:01 | 6278.18 | 2.1729 | 86.7679 | 74.6386 | 1839.9529
2041-05-20 10:01 | 8636.98 | 2.9699 | 87.0236 | 74.6386 | 2531.249
2041-05-21 11:01 | 10582.1 | 3.5275 | 87.5549 | 74.6386 | 3101.3074
2041-05-22 12:01 | 11759.5 | 3.8986 | 87.9419 | 74.6386 | 3446.3692
2041-05-23 13:01 | 12419.3 | 4.0537 | 88.3509 | 74.6386 | 3639.7375
2041-05-24 14:01 | 12072.1 | 3.9184 | 88.6327 | 74.6386 | 3537.9833
2041-05-25 15:01 | 11530.9 | 3.7425 | 88.7919 | 74.6386 | 3379.3732
2041-05-26 16:01 | 11495.6 | 3.6648 | 89.0074 | 74.6386 | 3369.0278
2041-05-27 17:01 | 8975.23 | 2.8963 | 89.0104 | 74.6386 | 2630.3803
2041-05-28 18:01 | 8183.15 | 2.6096 | 88.9988 | 74.6386 | 2398.2445
2041-05-29 19:01 | 6662.9 | 2.0035 | 89.3532 | 74.6386 | 1952.7032
2041-05-30 20:01 | 5714.2 | 1.7604 | 89.023 | 74.6386 | 1674.6667
2041-05-31 21:01 | 3228.04 | 1.0181 | 88.7059 | 74.6386 | 946.0451
2041-06-01 22:01 | 3080.34 | 1 | 79.4373 | 74.6386 | 902.7585
2041-06-02 23:01 | 0 | 0 | 80.7671 | 74.6386 | 0
2041-06-04 00:01 | -326.555 | 1.2261 | 79.7978 | 74.6386 | -95.7038
2041-06-05 01:01 | -628.683 | 1.8497 | 79.3771 | 74.6386 | -184.2488
2041-06-06 02:01 | -863.366 | 2.3352 | 79.1215 | 74.6386 | -253.0276
2041-06-07 03:01 | -1079.49 | 2.7901 | 78.9298 | 74.6386 | -316.3673
2041-06-08 04:01 | -1254.39 | 3.1561 | 78.7521 | 74.6386 | -367.6254
2041-06-09 05:01 | -1508.58 | 3.7081 | 78.6299 | 74.6386 | -442.1212
2041-06-10 06:01 | -1545.7 | 3.7549 | 78.5152 | 74.6386 | -453
2041-06-11 07:01 | 0 | 1 | 79.3935 | 74.6386 | 0
2041-06-12 08:01 | 2700.93 | 1.1838 | 84.8202 | 74.6386 | 791.5644
2041-06-13 09:01 | 4321.12 | 1.5763 | 86.0902 | 74.6386 | 1266.3953
2041-06-14 10:01 | 6354.9 | 2.2809 | 86.3814 | 74.6386 | 1862.4373
2041-06-15 11:01 | 8130.61 | 2.8253 | 86.849 | 74.6386 | 2382.8466
2041-06-16 12:01 | 9332.32 | 3.1753 | 87.2796 | 74.6386 | 2735.033
2041-06-17 13:01 | 10216.2 | 3.3372 | 87.8308 | 74.6386 | 2994.0727
2041-06-18 14:01 | 10431.9 | 3.3989 | 88.0763 | 74.6386 | 3057.2881
2041-06-19 15:01 | 10138.7 | 3.3035 | 88.2501 | 74.6386 | 2971.3597
2041-06-20 16:01 | 8694.48 | 2.8184 | 88.3919 | 74.6386 | 2548.1006
2041-06-21 17:01 | 8830.22 | 2.8608 | 88.3873 | 74.6386 | 2587.882
2041-06-22 18:01 | 7054.19 | 2.202 | 88.7079 | 74.6386 | 2067.379
2041-06-23 19:01 | 5496.94 | 1.6841 | 88.7718 | 74.6386 | 1610.9941
2041-06-24 20:01 | 4495.53 | 1.3547 | 88.7432 | 74.6386 | 1317.5098
2041-06-25 21:01 | 3428.54 | 1.0785 | 88.2704 | 74.6386 | 1004.8059
2041-06-26 22:01 | 3112.67 | 1 | 90.7633 | 74.6386 | 912.2335
2041-06-27 23:01 | 3124.06 | 1 | 92.2504 | 74.6386 | 915.5716
2041-06-29 00:01 | 0 | 0 | 80.4026 | 74.6386 | 0
2041-06-30 01:01 | -817.67 | 2.2738 | 79.2598 | 74.6386 | -239.6354
2041-07-01 02:01 | -1136.23 | 2.9219 | 78.9484 | 74.6386 | -332.9961
2041-07-02 03:01 | -1320.87 | 3.2963 | 78.7559 | 74.6386 | -387.1088
2041-07-03 04:01 | -1502.95 | 3.6859 | 78.6 | 74.6386 | -440.4712
2041-07-04 05:01 | -1622.12 | 3.933 | 78.4473 | 74.6386 | -475.3964
2041-07-05 06:01 | -1767.66 | 4.2496 | 78.3474 | 74.6386 | -518.05
2041-07-06 07:01 | -269.94 | 0.83108 | 78.4756 | 74.6386 | -79.1116
2041-07-07 08:01 | 2448.13 | 1.0649 | 84.7197 | 74.6386 | 717.4761
2041-07-08 09:01 | 4793.83 | 1.6277 | 86.4319 | 74.6386 | 1404.9329
2041-07-09 10:01 | 6737.17 | 2.4112 | 86.3182 | 74.6386 | 1974.4696
2041-07-10 11:01 | 8661.12 | 3.0459 | 86.6924 | 74.6386 | 2538.3237
2041-07-11 12:01 | 9936.7 | 3.3904 | 87.211 | 74.6386 | 2912.1593
2041-07-12 13:01 | 10686.6 | 3.5002 | 87.793 | 74.6386 | 3131.9333
2041-07-13 14:01 | 10592.8 | 3.4341 | 88.1081 | 74.6386 | 3104.4432
2041-07-14 15:01 | 10213.7 | 3.3381 | 88.2085 | 74.6386 | 2993.34
2041-07-15 16:01 | 9027.15 | 2.9045 | 88.4233 | 74.6386 | 2645.5965
2041-07-16 17:01 | 9302.94 | 2.9327 | 88.5804 | 74.6386 | 2726.4226
2041-07-17 18:01 | 7342.98 | 2.2675 | 88.802 | 74.6386 | 2152.015
2041-07-18 19:01 | 6090.03 | 1.8581 | 88.815 | 74.6386 | 1784.8116
2041-07-19 20:01 | 4896.01 | 1.5043 | 88.6329 | 74.6386 | 1434.8789
2041-07-20 21:01 | 3850.87 | 1.2345 | 88.171 | 74.6386 | 1128.5786
2041-07-21 22:01 | 3059.07 | 1 | 89.8343 | 74.6386 | 896.5249
2041-07-22 23:01 | 3111.55 | 1 | 93.0528 | 74.6386 | 911.9053
2041-07-24 00:01 | 0 | 0 | 80.3812 | 74.6386 | 0
2041-07-25 01:01 | -591.167 | 1.6925 | 79.2542 | 74.6386 | -173.2539
2041-07-26 02:01 | -704.148 | 1.9921 | 79.0144 | 74.6386 | -206.3654
2041-07-27 03:01 | -890.379 | 2.3926 | 78.8267 | 74.6386 | -260.9443
2041-07-28 04:01 | -1091.51 | 2.8206 | 78.6672 | 74.6386 | -319.89
2041-07-29 05:01 | -1249.58 | 3.1509 | 78.5118 | 74.6386 | -366.2157
2041-07-30 06:01 | -1240.23 | 3.1076 | 78.422 | 74.6386 | -363.4755
2041-07-31 07:01 | 1466.28 | 1 | 78.5909 | 74.6386 | 429.7242
2041-08-01 08:01 | 3408.04 | 1.142 | 86.5009 | 74.6386 | 998.7979
2041-08-02 09:01 | 4450.15 | 1.5181 | 86.5587 | 74.6386 | 1304.2102
2041-08-03 10:01 | 5967.17 | 2.0653 | 86.6136 | 74.6386 | 1748.8049
2041-08-04 11:01 | 6916.36 | 2.3445 | 86.9478 | 74.6386 | 2026.985
2041-08-05 12:01 | 8070.81 | 2.5934 | 87.537 | 74.6386 | 2365.3209
2041-08-06 13:01 | 8989.25 | 2.9492 | 87.5854 | 74.6386 | 2634.4891
2041-08-07 14:01 | 9265.12 | 3.0148 | 87.8367 | 74.6386 | 2715.3386
2041-08-08 15:01 | 9047.38 | 2.9251 | 88.0351 | 74.6386 | 2651.5253
2041-08-09 16:01 | 8406.96 | 2.6132 | 88.4255 | 74.6386 | 2463.8368
2041-08-10 17:01 | 8646.94 | 2.7346 | 88.3338 | 74.6386 | 2534.168
2041-08-11 18:01 | 7211.35 | 2.1801 | 88.7564 | 74.6386 | 2113.4381
2041-08-12 19:01 | 6037.65 | 1.8157 | 88.7504 | 74.6386 | 1769.4605
2041-08-13 20:01 | 4721.96 | 1.4582 | 88.4411 | 74.6386 | 1383.8699
2041-08-14 21:01 | 3683.38 | 1.1771 | 88.0477 | 74.6386 | 1079.4921
2041-08-15 22:01 | 3181.1 | 1 | 88.3742 | 74.6386 | 932.2884
2041-08-16 23:01 | 3156.87 | 1 | 90.4067 | 74.6386 | 925.1873
2041-08-18 00:01 | 938.131 | 1 | 79.8346 | 74.6386 | 274.9391
2041-08-19 01:01 | -97.4128 | 0.75284 | 79.7603 | 74.6386 | -28.5489
2041-08-20 02:01 | -315.959 | 1.1898 | 79.224 | 74.6386 | -92.5984
2041-08-21 03:01 | -391.744 | 1.3293 | 79.0154 | 74.6386 | -114.8088
2041-08-22 04:01 | -240.817 | 0.98215 | 79.0253 | 74.6386 | -70.5765
2041-08-23 05:01 | -176.035 | 0.86282 | 79.0329 | 74.6386 | -51.5908
2041-08-24 06:01 | 1596.23 | 1 | 78.6943 | 74.6386 | 467.8088
2041-08-25 07:01 | 2979.88 | 1 | 78.1116 | 74.6386 | 873.3166
2041-08-26 08:01 | 5031.1 | 1.5947 | 87.1539 | 74.6386 | 1474.4699
2041-08-27 09:01 | 6303.66 | 2.0934 | 87.0114 | 74.6386 | 1847.4204
2041-08-28 10:01 | 4625.67 | 1.5049 | 87.3656 | 74.6386 | 1355.6501
2041-08-29 11:01 | 4856.06 | 1.5207 | 87.6371 | 74.6386 | 1423.1707
2041-08-30 12:01 | 4486.18 | 1.31 | 88.2036 | 74.6386 | 1314.7696
2041-08-31 13:01 | 6475.77 | 2.1383 | 87.267 | 74.6386 | 1897.8608
2041-09-01 14:01 | 4447.2 | 1.3373 | 88.1052 | 74.6386 | 1303.3457
2041-09-02 15:01 | 3933.96 | 1.2367 | 87.6728 | 74.6386 | 1152.9299
2041-09-03 16:01 | 5964 | 1.946 | 87.3189 | 74.6386 | 1747.8759
2041-09-04 17:01 | 5792.71 | 1.8436 | 87.6299 | 74.6386 | 1697.6757
2041-09-05 18:01 | 5953.65 | 1.8942 | 87.6953 | 74.6386 | 1744.8426
2041-09-06 19:01 | 5080.19 | 1.5827 | 87.8692 | 74.6386 | 1488.8567
2041-09-07 20:01 | 4302.34 | 1.3847 | 87.5947 | 74.6386 | 1260.8914
2041-09-08 21:01 | 3091.75 | 1 | 91.1948 | 74.6386 | 906.1025
2041-09-09 22:01 | 3147.07 | 1 | 78.5421 | 74.6386 | 922.3152
2041-09-10 23:01 | 1968.93 | 1 | 79.0523 | 74.6386 | 577.0364
2041-09-12 00:01 | 203.3 | 1 | 79.7889 | 74.6386 | 59.5813
2041-09-13 01:01 | -76.9853 | 0.68331 | 79.409 | 74.6386 | -22.5622
2041-09-14 02:01 | -174.586 | 0.88148 | 79.0764 | 74.6386 | -51.1661
2041-09-15 03:01 | -58.6836 | 0.60794 | 79.5363 | 74.6386 | -17.1985
2041-09-16 04:01 | 3300.49 | 1 | 77.8038 | 74.6386 | 967.2781
2041-09-17 05:01 | 1908 | 1 | 78.6748 | 74.6386 | 559.1796
2041-09-18 06:01 | 2710.59 | 1 | 78.286 | 74.6386 | 794.3955
2041-09-19 07:01 | 2926.52 | 1 | 78.2188 | 74.6386 | 857.6783
2041-09-20 08:01 | 3052.22 | 1 | 78.2067 | 74.6386 | 894.5174
2041-09-21 09:01 | 3256.42 | 1 | 87.8128 | 74.6386 | 954.3625
2041-09-22 10:01 | 3145.25 | 1 | 87.9713 | 74.6386 | 921.7818
2041-09-23 11:01 | 3769.14 | 1.1272 | 87.622 | 74.6386 | 1104.6259
2041-09-24 12:01 | 3583.96 | 1.1059 | 87.4265 | 74.6386 | 1050.355
2041-09-25 13:01 | 4331.59 | 1.3549 | 87.3307 | 74.6386 | 1269.4637
2041-09-26 14:01 | 3172.82 | 1 | 87.8204 | 74.6386 | 929.8618
2041-09-27 15:01 | 2971.01 | 1 | 87.8571 | 74.6386 | 870.7171
2041-09-28 16:01 | 4302.08 | 1.3928 | 87.0263 | 74.6386 | 1260.8152
2041-09-29 17:01 | 4620.35 | 1.5203 | 86.977 | 74.6386 | 1354.0909
2041-09-30 18:01 | 5077.49 | 1.6494 | 87.1246 | 74.6386 | 1488.0654
2041-10-01 19:01 | 4500.81 | 1.4461 | 87.255 | 74.6386 | 1319.0572
2041-10-02 20:01 | 4083.42 | 1.3068 | 87.29 | 74.6386 | 1196.7323
2041-10-03 21:01 | 3034.62 | 1 | 91.9556 | 74.6386 | 889.3593
2041-10-04 22:01 | 3115.87 | 1 | 78.3068 | 74.6386 | 913.1714
2041-10-05 23:01 | 0 | 0 | 79.7804 | 74.6386 | 0
2041-10-07 00:01 | 131.504 | 1 | 79.471 | 74.6386 | 38.54
2041-10-08 01:01 | -97.6562 | 0.73518 | 79.0867 | 74.6386 | -28.6202
2041-10-09 02:01 | -105.624 | 0.72502 | 78.9748 | 74.6386 | -30.9553
2041-10-10 03:01 | -49.0844 | 0.59919 | 79.3137 | 74.6386 | -14.3852
2041-10-11 04:01 | 226.426 | 1 | 79.0738 | 74.6386 | 66.3589
2041-10-12 05:01 | 2765.05 | 1 | 77.8347 | 74.6386 | 810.3562
2041-10-13 06:01 | 3014.75 | 1 | 77.8743 | 74.6386 | 883.536
2041-10-14 07:01 | 3093.56 | 1 | 91.8017 | 74.6386 | 906.6329
2041-10-15 08:01 | 3149.71 | 1 | 89.9917 | 74.6386 | 923.0889
2041-10-16 09:01 | 3146.42 | 1 | 77.9802 | 74.6386 | 922.1247
2041-10-17 10:01 | 3111.45 | 1 | 78.0297 | 74.6386 | 911.876
2041-10-18 11:01 | 3309.55 | 1 | 77.9431 | 74.6386 | 969.9334
2041-10-19 12:01 | 3150.6 | 1 | 87.4456 | 74.6386 | 923.3497
2041-10-20 13:01 | 3177.95 | 1 | 88.3417 | 74.6386 | 931.3652
2041-10-21 14:01 | 3137.91 | 1 | 89.9841 | 74.6386 | 919.6306
2041-10-22 15:01 | 3152.2 | 1 | 92.2057 | 74.6386 | 923.8186
2041-10-23 16:01 | 4388.8 | 1.3847 | 87.0614 | 74.6386 | 1286.2303
2041-10-24 17:01 | 4494.99 | 1.4828 | 86.8176 | 74.6386 | 1317.3515
2041-10-25 18:01 | 4808.88 | 1.6014 | 86.7966 | 74.6386 | 1409.3436
2041-10-26 19:01 | 4003.44 | 1.3273 | 86.8761 | 74.6386 | 1173.2924
2041-10-27 20:01 | 3490.99 | 1.1309 | 87.0224 | 74.6386 | 1023.1082
2041-10-28 21:01 | 2969.73 | 1 | 78.2525 | 74.6386 | 870.3419
2041-10-29 22:01 | 3128.96 | 1 | 78.1206 | 74.6386 | 917.0077
2041-10-30 23:01 | 0 | 0 | 79.6242 | 74.6386 | 0
2041-11-01 00:01 | -96.9713 | 0.73371 | 79.0731 | 74.6386 | -28.4195
2041-11-02 01:01 | -289.82 | 1.1395 | 78.6458 | 74.6386 | -84.9379
2041-11-03 02:01 | -425.226 | 1.4156 | 78.4544 | 74.6386 | -124.6214
2041-11-04 03:01 | -522.564 | 1.6169 | 78.3221 | 74.6386 | -153.1484
2041-11-05 04:01 | -520.08 | 1.5982 | 78.2231 | 74.6386 | -152.4204
2041-11-06 05:01 | -301.257 | 1.1053 | 78.2937 | 74.6386 | -88.2897
2041-11-07 06:01 | 1198.72 | 1 | 78.3216 | 74.6386 | 351.3102
2041-11-08 07:01 | 2421.23 | 1 | 77.8018 | 74.6386 | 709.5925
2041-11-09 08:01 | 3091.7 | 1 | 86.9789 | 74.6386 | 906.0878
2041-11-10 09:01 | 4726.16 | 1.4548 | 86.8667 | 74.6386 | 1385.1008
2041-11-11 10:01 | 7137.17 | 2.3312 | 86.5995 | 74.6386 | 2091.698
2041-11-12 11:01 | 8839.25 | 2.9335 | 86.7931 | 74.6386 | 2590.5285
2041-11-13 12:01 | 10343.7 | 3.3613 | 87.2551 | 74.6386 | 3031.4392
2041-11-14 13:01 | 10933.1 | 3.5683 | 87.5319 | 74.6386 | 3204.1753
2041-11-15 14:01 | 11001.7 | 3.5906 | 87.7997 | 74.6386 | 3224.28
2041-11-16 15:01 | 10689.2 | 3.4287 | 88.1324 | 74.6386 | 3132.6953
2041-11-17 16:01 | 10489.8 | 3.3377 | 88.3245 | 74.6386 | 3074.2569
2041-11-18 17:01 | 8423.91 | 2.622 | 88.5936 | 74.6386 | 2468.8043
2041-11-19 18:01 | 7462.79 | 2.3748 | 88.3579 | 74.6386 | 2187.1279
2041-11-20 19:01 | 5723.88 | 1.8236 | 88.2662 | 74.6386 | 1677.5036
2041-11-21 20:01 | 4662.65 | 1.4948 | 88.0738 | 74.6386 | 1366.4878
2041-11-22 21:01 | 3073.98 | 1 | 90.0349 | 74.6386 | 900.8946
2041-11-23 22:01 | 3044.51 | 1 | 78.8503 | 74.6386 | 892.2578
2041-11-24 23:01 | 2602.99 | 1 | 78.9442 | 74.6386 | 762.8611
2041-11-26 00:01 | -173.025 | 0.92797 | 79.6403 | 74.6386 | -50.7086
2041-11-27 01:01 | -375.941 | 1.3118 | 79.1075 | 74.6386 | -110.1774
2041-11-28 02:01 | -603.313 | 1.7978 | 78.7902 | 74.6386 | -176.8136
2041-11-29 03:01 | -722.729 | 2.0347 | 78.6072 | 74.6386 | -211.811
2041-11-30 04:01 | -827.907 | 2.2579 | 78.4465 | 74.6386 | -242.6356
2041-12-01 05:01 | -888.004 | 2.3803 | 78.3119 | 74.6386 | -260.2483
2041-12-02 06:01 | -926.723 | 2.4612 | 78.2197 | 74.6386 | -271.5957
2041-12-03 07:01 | 2010.04 | 1 | 78.0655 | 74.6386 | 589.0846
2041-12-04 08:01 | 3819.47 | 1.2072 | 86.6835 | 74.6386 | 1119.3762
2041-12-05 09:01 | 5543.71 | 1.6623 | 87.28 | 74.6386 | 1624.701
2041-12-06 10:01 | 7076.23 | 2.4263 | 86.5049 | 74.6386 | 2073.8383
2041-12-07 11:01 | 6703.8 | 2.1081 | 87.369 | 74.6386 | 1964.6898
2041-12-08 12:01 | 7187.2 | 2.3784 | 87.1368 | 74.6386 | 2106.3604
2041-12-09 13:01 | 9250.84 | 3.0574 | 87.2676 | 74.6386 | 2711.1536
2041-12-10 14:01 | 9384 | 3.1115 | 87.4951 | 74.6386 | 2750.1789
2041-12-11 15:01 | 9407.76 | 2.988 | 87.976 | 74.6386 | 2757.1423
2041-12-12 16:01 | 7546.95 | 2.268 | 88.5031 | 74.6386 | 2211.7927
2041-12-13 17:01 | 8440.05 | 2.7483 | 87.8681 | 74.6386 | 2473.5345
2041-12-14 18:01 | 7000.56 | 2.2078 | 88.2007 | 74.6386 | 2051.6616
2041-12-15 19:01 | 6030.34 | 1.8061 | 88.5551 | 74.6386 | 1767.3182
2041-12-16 20:01 | 5044.68 | 1.5195 | 88.4146 | 74.6386 | 1478.4498
2041-12-17 21:01 | 4349.47 | 1.4051 | 87.769 | 74.6386 | 1274.7038
2041-12-18 22:01 | 3939.69 | 1.2211 | 87.9748 | 74.6386 | 1154.6092
2041-12-19 23:01 | 3208.92 | 1.0636 | 87.3854 | 74.6386 | 940.4416
2041-12-21 00:01 | 0 | 0 | 80.1528 | 74.6386 | 0
2041-12-22 01:01 | -207.743 | 0.94974 | 79.3235 | 74.6386 | -60.8835
2041-12-23 02:01 | -316.692 | 1.1792 | 79.0067 | 74.6386 | -92.8133
2041-12-24 03:01 | -342.634 | 1.2224 | 78.8489 | 74.6386 | -100.4161
2041-12-25 04:01 | -216.362 | 0.93689 | 78.8561 | 74.6386 | -63.4094
2041-12-26 05:01 | -203.839 | 0.93044 | 78.7917 | 74.6386 | -59.7393
2041-12-27 06:01 | -172.656 | 0.86129 | 78.7873 | 74.6386 | -50.6005
2041-12-28 07:01 | 2161.11 | 1.1425 | 83.6906 | 74.6386 | 633.3588
2041-12-29 08:01 | 5132.92 | 1.9912 | 85.4316 | 74.6386 | 1504.3104
2041-12-30 09:01 | 4966.41 | 1.713 | 86.4598 | 74.6386 | 1455.5111
2041-12-31 10:01 | 6164.42 | 2.039 | 86.8613 | 74.6386 | 1806.6132
2042-01-01 11:01 | 8974.58 | 3.139 | 86.6221 | 74.6386 | 2630.1898
2042-01-02 12:01 | 10293.6 | 3.5105 | 87.1397 | 74.6386 | 3016.7564
2042-01-03 13:01 | 10674.1 | 3.5776 | 87.5573 | 74.6386 | 3128.2699
2042-01-04 14:01 | 10260 | 3.2902 | 88.0698 | 74.6386 | 3006.9092
2042-01-05 15:01 | 8264.49 | 2.5564 | 88.4688 | 74.6386 | 2422.0829
2042-01-06 16:01 | 7271.94 | 2.1765 | 88.6966 | 74.6386 | 2131.1952
2042-01-07 17:01 | 8595.03 | 2.7975 | 87.993 | 74.6386 | 2518.9546
2042-01-08 18:01 | 7077.29 | 2.2756 | 88.1752 | 74.6386 | 2074.149
2042-01-09 19:01 | 6166.18 | 1.8041 | 88.8449 | 74.6386 | 1807.129
2042-01-10 20:01 | 4963.27 | 1.5096 | 88.4243 | 74.6386 | 1454.5908
2042-01-11 21:01 | 3986.13 | 1.2738 | 87.937 | 74.6386 | 1168.2194
2042-01-12 22:01 | 3172.18 | 1.0327 | 87.6765 | 74.6386 | 929.6742
2042-01-13 23:01 | 3121.65 | 1 | 89.8614 | 74.6386 | 914.8653
2042-01-15 00:01 | 199.122 | 1 | 80.0593 | 74.6386 | 58.3569
2042-01-16 01:01 | 1006.19 | 1 | 79.3803 | 74.6386 | 294.8852
2042-01-17 02:01 | 172.616 | 1 | 79.6668 | 74.6386 | 50.5888
2042-01-18 03:01 | 215.715 | 1 | 79.5223 | 74.6386 | 63.2198
2042-01-19 04:01 | 3090.18 | 1 | 78.0405 | 74.6386 | 905.6424
2042-01-20 05:01 | 1976.36 | 1 | 78.709 | 74.6386 | 579.2139
2042-01-21 06:01 | 2662.46 | 1 | 78.3777 | 74.6386 | 780.29
2042-01-22 07:01 | 3055.28 | 1 | 88.4162 | 74.6386 | 895.4142
2042-01-23 08:01 | 5041.33 | 1.5946 | 87.2015 | 74.6386 | 1477.468
2042-01-24 09:01 | 5058.88 | 1.5468 | 87.6366 | 74.6386 | 1482.6114
2042-01-25 10:01 | 6073.68 | 2.0304 | 87.0445 | 74.6386 | 1780.0199
2042-01-26 11:01 | 5582.8 | 1.7675 | 87.5521 | 74.6386 | 1636.1572
2042-01-27 12:01 | 5531.98 | 1.848 | 87.2079 | 74.6386 | 1621.2633
2042-01-28 13:01 | 6003.43 | 1.9089 | 87.5905 | 74.6386 | 1759.4317
2042-01-29 14:01 | 5978.64 | 1.7831 | 88.1341 | 74.6386 | 1752.1664
2042-01-30 15:01 | 5753.28 | 1.8284 | 87.6882 | 74.6386 | 1686.1199
2042-01-31 16:01 | 6328.22 | 2.0385 | 87.5805 | 74.6386 | 1854.6182
2042-02-01 17:01 | 6501.68 | 2.0668 | 87.7287 | 74.6386 | 1905.4543
2042-02-02 18:01 | 6290.42 | 2.0631 | 87.5539 | 74.6386 | 1843.5401
2042-02-03 19:01 | 5522.5 | 1.7186 | 87.9616 | 74.6386 | 1618.485
2042-02-04 20:01 | 4966.11 | 1.5488 | 87.9033 | 74.6386 | 1455.4232
2042-02-05 21:01 | 3129.3 | 1 | 88.0309 | 74.6386 | 917.1073
2042-02-06 22:01 | 3091.77 | 1 | 89.6505 | 74.6386 | 906.1083
2042-02-07 23:01 | 2942.6 | 1 | 78.5919 | 74.6386 | 862.3909
2042-02-09 00:01 | 0 | 0 | 79.9647 | 74.6386 | 0
2042-02-10 01:01 | 665.327 | 1 | 79.3798 | 74.6386 | 194.9881
2042-02-11 02:01 | -79.6703 | 0.70538 | 79.3263 | 74.6386 | -23.3491
2042-02-12 03:01 | -186.989 | 0.9082 | 79.0022 | 74.6386 | -54.8011
2042-02-13 04:01 | 0 | 0 | 79.3765 | 74.6386 | 0
2042-02-14 05:01 | -37.1985 | 0.59333 | 79.3427 | 74.6386 | -10.9018
2042-02-15 06:01 | 2018.61 | 1 | 78.2751 | 74.6386 | 591.5962
2042-02-16 07:01 | 2843.24 | 1 | 88.2903 | 74.6386 | 833.2714
2042-02-17 08:01 | 3948.58 | 1.254 | 86.8815 | 74.6386 | 1157.2146
2042-02-18 09:01 | 6078.14 | 2.0075 | 86.719 | 74.6386 | 1781.327
2042-02-19 10:01 | 8493.62 | 2.9386 | 86.6175 | 74.6386 | 2489.2343
2042-02-20 11:01 | 10189.3 | 3.5114 | 86.9597 | 74.6386 | 2986.1891
2042-02-21 12:01 | 11306.1 | 3.8254 | 87.4027 | 74.6386 | 3313.4908
2042-02-22 13:01 | 11856.7 | 3.9146 | 87.8596 | 74.6386 | 3474.8558
2042-02-23 14:01 | 11626.9 | 3.875 | 88.0421 | 74.6386 | 3407.508
2042-02-24 15:01 | 11136.5 | 3.6713 | 88.2912 | 74.6386 | 3263.786
2042-02-25 16:01 | 10977.8 | 3.5232 | 88.5852 | 74.6386 | 3217.2756
2042-02-26 17:01 | 8944.26 | 2.8422 | 88.7433 | 74.6386 | 2621.3038
2042-02-27 18:01 | 8533.3 | 2.6641 | 88.7976 | 74.6386 | 2500.8634
2042-02-28 19:01 | 7272.12 | 2.2115 | 88.9506 | 74.6386 | 2131.248
2042-03-01 20:01 | 6405.08 | 1.9763 | 88.7472 | 74.6386 | 1877.1436
2042-03-02 21:01 | 4274.42 | 1.2954 | 88.7794 | 74.6386 | 1252.7088
2042-03-03 22:01 | 3256.59 | 1.0417 | 88.1404 | 74.6386 | 954.4123
2042-03-04 23:01 | 3013.14 | 1 | 79.085 | 74.6386 | 883.0642
2042-03-06 00:01 | 1894.93 | 1 | 79.4897 | 74.6386 | 555.3492
2042-03-07 01:01 | -17.0547 | 0.5748 | 80.2403 | 74.6386 | -4.9982
2042-03-08 02:01 | -252.325 | 1.0542 | 79.3779 | 74.6386 | -73.9492
2042-03-09 03:01 | -334.104 | 1.2092 | 79.1102 | 74.6386 | -97.9162
2042-03-10 04:01 | -304.359 | 1.1331 | 78.9949 | 74.6386 | -89.1988
2042-03-11 05:01 | -138.446 | 0.7676 | 79.0978 | 74.6386 | -40.5745
2042-03-12 06:01 | 584.883 | 1 | 79.1581 | 74.6386 | 171.4123
2042-03-13 07:01 | 2968.9 | 1 | 77.9969 | 74.6386 | 870.0987
2042-03-14 08:01 | 4452.95 | 1.4083 | 87.0646 | 74.6386 | 1305.0308
2042-03-15 09:01 | 6402.23 | 2.1227 | 86.882 | 74.6386 | 1876.3084
2042-03-16 10:01 | 8599.22 | 2.9717 | 86.8183 | 74.6386 | 2520.1826
2042-03-17 11:01 | 10352.8 | 3.5136 | 87.2406 | 74.6386 | 3034.1062
2042-03-18 12:01 | 11388.7 | 3.8104 | 87.6585 | 74.6386 | 3337.6985
2042-03-19 13:01 | 11905.9 | 3.9131 | 88.0623 | 74.6386 | 3489.2749
2042-03-20 14:01 | 11915.6 | 3.8628 | 88.3954 | 74.6386 | 3492.1176
2042-03-21 15:01 | 11638.7 | 3.7601 | 88.5966 | 74.6386 | 3410.9663
2042-03-22 16:01 | 11526.1 | 3.6909 | 88.7788 | 74.6386 | 3377.9665
2042-03-23 17:01 | 9436.09 | 2.8218 | 89.4018 | 74.6386 | 2765.445
2042-03-24 18:01 | 8325.1 | 2.5593 | 89.1215 | 74.6386 | 2439.846
2042-03-25 19:01 | 6692.64 | 2.0678 | 88.9876 | 74.6386 | 1961.4192
2042-03-26 20:01 | 5650.28 | 1.7192 | 88.9562 | 74.6386 | 1655.9336
2042-03-27 21:01 | 3225.58 | 1.0215 | 88.498 | 74.6386 | 945.3242
2042-03-28 22:01 | 3120.87 | 1 | 91.9872 | 74.6386 | 914.6367
2042-03-29 23:01 | 1195.12 | 1 | 79.9955 | 74.6386 | 350.2551
2042-03-31 00:01 | -231.18 | 1.0496 | 79.7978 | 74.6386 | -67.7522
2042-04-01 01:01 | -375.392 | 1.2983 | 79.3578 | 74.6386 | -110.0165
2042-04-02 02:01 | -575.253 | 1.731 | 79.0648 | 74.6386 | -168.59
2042-04-03 03:01 | -638.021 | 1.8435 | 78.8911 | 74.6386 | -186.9855
2042-04-04 04:01 | -809.9 | 2.2252 | 78.7122 | 74.6386 | -237.3583
2042-04-05 05:01 | -1090.6 | 2.8343 | 78.5568 | 74.6386 | -319.6233
2042-04-06 06:01 | -1041.99 | 2.6819 | 78.446 | 74.6386 | -305.3771
2042-04-07 07:01 | 1566.99 | 1 | 78.5244 | 74.6386 | 459.2394
2042-04-08 08:01 | 4594.07 | 1.5345 | 86.4882 | 74.6386 | 1346.389
2042-04-09 09:01 | 5543.15 | 1.8085 | 86.9158 | 74.6386 | 1624.5369
2042-04-10 10:01 | 7064.36 | 2.4388 | 86.704 | 74.6386 | 2070.3595
2042-04-11 11:01 | 7059.94 | 2.3389 | 87.2119 | 74.6386 | 2069.0642
2042-04-12 12:01 | 9128.57 | 3.119 | 87.1492 | 74.6386 | 2675.3198
2042-04-13 13:01 | 10128.7 | 3.3848 | 87.5526 | 74.6386 | 2968.4289
2042-04-14 14:01 | 10465.7 | 3.3743 | 88.0336 | 74.6386 | 3067.1939
2042-04-15 15:01 | 9570.3 | 3.0635 | 88.2556 | 74.6386 | 2804.7781
2042-04-16 16:01 | 9106.77 | 2.7761 | 88.6794 | 74.6386 | 2668.9308
2042-04-17 17:01 | 9552.21 | 3.0546 | 88.3681 | 74.6386 | 2799.4764
2042-04-18 18:01 | 7994.33 | 2.4954 | 88.6457 | 74.6386 | 2342.9068
2042-04-19 19:01 | 6688.84 | 2.0777 | 88.635 | 74.6386 | 1960.3055
2042-04-20 20:01 | 5452.14 | 1.6663 | 88.6361 | 74.6386 | 1597.8645
2042-04-21 21:01 | 4643 | 1.4459 | 88.3637 | 74.6386 | 1360.729
2042-04-22 22:01 | 3887.17 | 1.2255 | 88.1442 | 74.6386 | 1139.2171
2042-04-23 23:01 | 3341.9 | 1.0611 | 87.9589 | 74.6386 | 979.4142
2042-04-25 00:01 | 2990.48 | 1 | 78.9462 | 74.6386 | 876.4232
2042-04-26 01:01 | 0 | 0 | 80.2907 | 74.6386 | 0
2042-04-27 02:01 | 381.606 | 1 | 79.8144 | 74.6386 | 111.8377
2042-04-28 03:01 | 74.7416 | 1 | 79.8167 | 74.6386 | 21.9046
2042-04-29 04:01 | 61.6143 | 1 | 79.7096 | 74.6386 | 18.0574
2042-04-30 05:01 | 140.717 | 1 | 79.5638 | 74.6386 | 41.2401
2042-05-01 06:01 | 2799.93 | 1 | 78.1964 | 74.6386 | 820.5785
2042-05-02 07:01 | 3102.62 | 1 | 90.5463 | 74.6386 | 909.2882
2042-05-03 08:01 | 5931.84 | 1.8727 | 87.2613 | 74.6386 | 1738.4507
2042-05-04 09:01 | 7299.54 | 2.3937 | 87.2192 | 74.6386 | 2139.284
2042-05-05 10:01 | 9261.38 | 3.1466 | 87.2056 | 74.6386 | 2714.2425
2042-05-06 11:01 | 11029.7 | 3.6587 | 87.6628 | 74.6386 | 3232.486
2042-05-07 12:01 | 11374.9 | 3.7418 | 88.0176 | 74.6386 | 3333.6541
2042-05-08 13:01 | 10760.7 | 3.4489 | 88.4459 | 74.6386 | 3153.6499
2042-05-09 14:01 | 11139 | 3.5924 | 88.5078 | 74.6386 | 3264.5186
2042-05-10 15:01 | 8720.36 | 2.6929 | 88.9713 | 74.6386 | 2555.6852
2042-05-11 16:01 | 8904.04 | 2.6992 | 89.0433 | 74.6386 | 2609.5165
2042-05-12 17:01 | 8732.7 | 2.6606 | 88.996 | 74.6386 | 2559.3017
2042-05-13 18:01 | 8532.17 | 2.6729 | 88.7886 | 74.6386 | 2500.5322
2042-05-14 19:01 | 7367.15 | 2.3213 | 88.7517 | 74.6386 | 2159.0985
2042-05-15 20:01 | 6535.43 | 2.0114 | 88.8415 | 74.6386 | 1915.3455
2042-05-16 21:01 | 4361.88 | 1.3173 | 88.9079 | 74.6386 | 1278.3408
2042-05-17 22:01 | 3386.55 | 1.0875 | 88.2322 | 74.6386 | 992.4998
2042-05-18 23:01 | 3048.55 | 1 | 79.1943 | 74.6386 | 893.4418
2042-05-20 00:01 | 3018.71 | 1 | 79.0618 | 74.6386 | 884.6966
2042-05-21 01:01 | 0 | 0 | 80.4263 | 74.6386 | 0
2042-05-22 02:01 | 576.336 | 1 | 79.8402 | 74.6386 | 168.9074
2042-05-23 03:01 | -105.471 | 0.75659 | 79.6642 | 74.6386 | -30.9105
2042-05-24 04:01 | -246.738 | 1.0348 | 79.3045 | 74.6386 | -72.3118
2042-05-25 05:01 | -413.242 | 1.3878 | 79.0441 | 74.6386 | -121.1093
2042-05-26 06:01 | -450.616 | 1.4486 | 78.8883 | 74.6386 | -132.0625
2042-05-27 07:01 | 1980.76 | 1 | 85.5674 | 74.6386 | 580.5035
2042-05-28 08:01 | 5052.23 | 1.7707 | 86.3851 | 74.6386 | 1480.6625
2042-05-29 09:01 | 6224.18 | 2.0616 | 87.0386 | 74.6386 | 1824.1271
2042-05-30 10:01 | 6823.99 | 2.2328 | 87.3299 | 74.6386 | 1999.9141
2042-05-31 11:01 | 9031.89 | 3.1121 | 87.1151 | 74.6386 | 2646.9857
2042-06-01 12:01 | 10569 | 3.5938 | 87.4772 | 74.6386 | 3097.4681
2042-06-02 13:01 | 11358.1 | 3.7332 | 88.0115 | 74.6386 | 3328.7305
2042-06-03 14:01 | 11682.8 | 3.6867 | 88.5295 | 74.6386 | 3423.8907
2042-06-04 15:01 | 10728.3 | 3.4107 | 88.6632 | 74.6386 | 3144.1544
2042-06-05 16:01 | 8373.34 | 2.5272 | 89.1453 | 74.6386 | 2453.9837
2042-06-06 17:01 | 9714.41 | 3.1283 | 88.5586 | 74.6386 | 2847.0125
2042-06-07 18:01 | 8210.32 | 2.5901 | 88.7972 | 74.6386 | 2406.2073
2042-06-08 19:01 | 7223.65 | 2.2087 | 88.9912 | 74.6386 | 2117.0428
2042-06-09 20:01 | 6124.55 | 1.8834 | 88.8328 | 74.6386 | 1794.9284
2042-06-10 21:01 | 5442.42 | 1.6771 | 88.6944 | 74.6386 | 1595.0159
2042-06-11 22:01 | 5096.18 | 1.5444 | 88.7347 | 74.6386 | 1493.5429
2042-06-12 23:01 | 4491.78 | 1.4292 | 88.2631 | 74.6386 | 1316.4108
2042-06-14 00:01 | 2928.09 | 1 | 79.3059 | 74.6386 | 858.1385
2042-06-15 01:01 | 3046.38 | 1 | 79.0697 | 74.6386 | 892.8058
2042-06-16 02:01 | 3150.87 | 1 | 78.9182 | 74.6386 | 923.4288
2042-06-17 03:01 | 84.6708 | 1 | 80.3497 | 74.6386 | 24.8146
2042-06-18 04:01 | 430.685 | 1 | 79.9142 | 74.6386 | 126.2213
2042-06-19 05:01 | -74.3445 | 0.68357 | 79.7167 | 74.6386 | -21.7882
2042-06-20 06:01 | -66.8918 | 0.63864 | 79.9307 | 74.6386 | -19.6041
2042-06-21 07:01 | 2031.53 | 1.1222 | 84.0371 | 74.6386 | 595.3827
2042-06-22 08:01 | 5314.88 | 2.1221 | 85.7223 | 74.6386 | 1557.6376
2042-06-23 09:01 | 6398.24 | 2.2778 | 86.7052 | 74.6386 | 1875.139
2042-06-24 10:01 | 8152.77 | 2.8645 | 86.9855 | 74.6386 | 2389.341
2042-06-25 11:01 | 9805.68 | 3.3492 | 87.4064 | 74.6386 | 2873.7611
2042-06-26 12:01 | 11179.5 | 3.7675 | 87.7805 | 74.6386 | 3276.388
2042-06-27 13:01 | 10960.7 | 3.5962 | 88.2403 | 74.6386 | 3212.2641
2042-06-28 14:01 | 11035.2 | 3.5942 | 88.4271 | 74.6386 | 3234.0979
2042-06-29 15:01 | 10760.9 | 3.5049 | 88.5599 | 74.6386 | 3153.7085
2042-06-30 16:01 | 9719.23 | 3.0593 | 88.9098 | 74.6386 | 2848.4251
2042-07-01 17:01 | 9924.65 | 3.1646 | 88.8186 | 74.6386 | 2908.6278
2042-07-02 18:01 | 8346.47 | 2.5536 | 89.1809 | 74.6386 | 2446.1089
2042-07-03 19:01 | 7143.86 | 2.1702 | 89.1753 | 74.6386 | 2093.6587
2042-07-04 20:01 | 5976.94 | 1.8702 | 88.827 | 74.6386 | 1751.6682
2042-07-05 21:01 | 5444.26 | 1.6119 | 89.1196 | 74.6386 | 1595.5551
2042-07-06 22:01 | 4840.94 | 1.4848 | 88.7294 | 74.6386 | 1418.7395
2042-07-07 23:01 | 4086.27 | 1.2894 | 88.3867 | 74.6386 | 1197.5675
2042-07-09 00:01 | 3124.37 | 1 | 79.2467 | 74.6386 | 915.6625
2042-07-10 01:01 | 3088.58 | 1 | 79.1124 | 74.6386 | 905.1734
2042-07-11 02:01 | 3118.76 | 1 | 78.9999 | 74.6386 | 914.0183
2042-07-12 03:01 | 3114.6 | 1 | 78.9452 | 74.6386 | 912.7992
2042-07-13 04:01 | 3200.2 | 1 | 78.8601 | 74.6386 | 937.886
2042-07-14 05:01 | 3186.08 | 1 | 78.8396 | 74.6386 | 933.7479
2042-07-15 06:01 | 3225.27 | 1 | 92.2524 | 74.6386 | 945.2333
2042-07-16 07:01 | 4053.39 | 1.2644 | 87.9318 | 74.6386 | 1187.9313
2042-07-17 08:01 | 6872.6 | 2.24 | 87.6467 | 74.6386 | 2014.1602
2042-07-18 09:01 | 8143.95 | 2.7156 | 87.7036 | 74.6386 | 2386.7561
2042-07-19 10:01 | 7106.4 | 2.2455 | 88.3025 | 74.6386 | 2082.6803
2042-07-20 11:01 | 7529.45 | 2.4425 | 88.1359 | 74.6386 | 2206.664
2042-07-21 12:01 | 9401.39 | 3.164 | 87.9373 | 74.6386 | 2755.2754
2042-07-22 13:01 | 10181.7 | 3.3435 | 88.3136 | 74.6386 | 2983.9617
2042-07-23 14:01 | 10235.5 | 3.3541 | 88.4854 | 74.6386 | 2999.7289
2042-07-24 15:01 | 10974.9 | 3.6066 | 88.553 | 74.6386 | 3216.4257
2042-07-25 16:01 | 11066.8 | 3.596 | 88.7831 | 74.6386 | 3243.3589
2042-07-26 17:01 | 9178.74 | 2.8624 | 89.2115 | 74.6386 | 2690.0232
2042-07-27 18:01 | 8674.98 | 2.695 | 89.1882 | 74.6386 | 2542.3857
2042-07-28 19:01 | 7382.48 | 2.246 | 89.3087 | 74.6386 | 2163.5913
2042-07-29 20:01 | 6507.2 | 1.9685 | 89.2555 | 74.6386 | 1907.0721
2042-07-30 21:01 | 4365.91 | 1.3295 | 89.0776 | 74.6386 | 1279.5219
2042-07-31 22:01 | 3600.24 | 1.1418 | 88.5406 | 74.6386 | 1055.1262
2042-08-01 23:01 | 3066.43 | 1 | 79.4255 | 74.6386 | 898.6819
2042-08-03 00:01 | 3070.41 | 1 | 79.2745 | 74.6386 | 899.8483
2042-08-04 01:01 | 0 | 0 | 80.6522 | 74.6386 | 0
2042-08-05 02:01 | 388.737 | 1 | 80.1464 | 74.6386 | 113.9276
2042-08-06 03:01 | 1306.27 | 1 | 79.5391 | 74.6386 | 382.8299
2042-08-07 04:01 | 1774.53 | 1 | 79.2723 | 74.6386 | 520.0634
2042-08-08 05:01 | 2630.97 | 1 | 78.837 | 74.6386 | 771.0612
2042-08-09 06:01 | 2947.49 | 1 | 78.696 | 74.6386 | 863.824
2042-08-10 07:01 | 3173.08 | 1 | 78.6272 | 74.6386 | 929.938
2042-08-11 08:01 | 5570.77 | 1.6796 | 88.0275 | 74.6386 | 1632.6315
2042-08-12 09:01 | 6927.45 | 2.3438 | 87.3379 | 74.6386 | 2030.2352
2042-08-13 10:01 | 9013.59 | 3.1669 | 87.2763 | 74.6386 | 2641.6225
2042-08-14 11:01 | 10515.6 | 3.6239 | 87.661 | 74.6386 | 3081.8181
2042-08-15 12:01 | 11670 | 3.9209 | 88.1001 | 74.6386 | 3420.1394
2042-08-16 13:01 | 12314.1 | 3.9572 | 88.6982 | 74.6386 | 3608.9065
2042-08-17 14:01 | 12450.1 | 3.996 | 88.9355 | 74.6386 | 3648.7641
2042-08-18 15:01 | 11968.6 | 3.8559 | 89.0816 | 74.6386 | 3507.6504
2042-08-19 16:01 | 11758.8 | 3.7742 | 89.2014 | 74.6386 | 3446.1641
2042-08-20 17:01 | 9243.51 | 2.9053 | 89.4286 | 74.6386 | 2709.0054
2042-08-21 18:01 | 8385.93 | 2.6345 | 89.3159 | 74.6386 | 2457.6735
2042-08-22 19:01 | 6987.15 | 2.1282 | 89.4525 | 74.6386 | 2047.7315
2042-08-23 20:01 | 6090.22 | 1.8937 | 89.1515 | 74.6386 | 1784.8673
2042-08-24 21:01 | 3778.04 | 1.175 | 89.009 | 74.6386 | 1107.2342
2042-08-25 22:01 | 3147.04 | 1 | 89.4182 | 74.6386 | 922.3064
2042-08-26 23:01 | 2999.39 | 1 | 79.4875 | 74.6386 | 879.0344
2042-08-28 00:01 | 3025.11 | 1 | 79.3357 | 74.6386 | 886.5722
2042-08-29 01:01 | -22.5337 | 0.5847 | 80.7271 | 74.6386 | -6.604
2042-08-30 02:01 | -90.5181 | 0.69203 | 80.0729 | 74.6386 | -26.5282
2042-08-31 03:01 | -197.996 | 0.92771 | 79.6804 | 74.6386 | -58.0269
2042-09-01 04:01 | -125.281 | 0.74964 | 79.6534 | 74.6386 | -36.7162
2042-09-02 05:01 | -46.8394 | 0.58879 | 79.9935 | 74.6386 | -13.7273
2042-09-03 06:01 | 2045.07 | 1 | 78.8481 | 74.6386 | 599.3509
2042-09-04 07:01 | 2887.67 | 1 | 78.5366 | 74.6386 | 846.2925
2042-09-05 08:01 | 4804.76 | 1.4615 | 87.7997 | 74.6386 | 1408.1362
2042-09-06 09:01 | 6507.08 | 2.2409 | 87.049 | 74.6386 | 1907.0369
2042-09-07 10:01 | 8289.74 | 2.787 | 87.4345 | 74.6386 | 2429.483
2042-09-08 11:01 | 9004.75 | 3.0024 | 87.7474 | 74.6386 | 2639.0317
2042-09-09 12:01 | 10841.5 | 3.6313 | 87.8998 | 74.6386 | 3177.33
2042-09-10 13:01 | 10582.1 | 3.447 | 88.3717 | 74.6386 | 3101.3074
2042-09-11 14:01 | 11212 | 3.6594 | 88.5135 | 74.6386 | 3285.9128
2042-09-12 15:01 | 9577.66 | 3.0423 | 88.8712 | 74.6386 | 2806.9351
2042-09-13 16:01 | 10540.6 | 3.354 | 88.8558 | 74.6386 | 3089.1449
2042-09-14 17:01 | 8707.19 | 2.7426 | 89.0445 | 74.6386 | 2551.8255
2042-09-15 18:01 | 8193.75 | 2.5515 | 89.0736 | 74.6386 | 2401.3511
2042-09-16 19:01 | 6950.64 | 2.1053 | 89.2362 | 74.6386 | 2037.0315
2042-09-17 20:01 | 6015.45 | 1.8161 | 89.1536 | 74.6386 | 1762.9544
2042-09-18 21:01 | 3683.16 | 1.1448 | 88.8219 | 74.6386 | 1079.4276
2042-09-19 22:01 | 3141.57 | 1 | 89.3711 | 74.6386 | 920.7033
2042-09-20 23:01 | 3058.82 | 1 | 79.3054 | 74.6386 | 896.4517
2042-09-22 00:01 | 2989.34 | 1 | 79.2132 | 74.6386 | 876.0891
2042-09-23 01:01 | 104.351 | 1 | 80.5195 | 74.6386 | 30.5823
2042-09-24 02:01 | 247.291 | 1 | 80.1553 | 74.6386 | 72.4738
2042-09-25 03:01 | 1069.88 | 1 | 79.6073 | 74.6386 | 313.5509
2042-09-26 04:01 | 1874.69 | 1 | 79.1807 | 74.6386 | 549.4174
2042-09-27 05:01 | 2595.44 | 1 | 78.8384 | 74.6386 | 760.6484
2042-09-28 06:01 | 3000 | 1 | 78.6589 | 74.6386 | 879.2132
2042-09-29 07:01 | 3080 | 1 | 90.8555 | 74.6386 | 902.6589
2042-09-30 08:01 | 6226.06 | 2.0692 | 87.2817 | 74.6386 | 1824.6781
2042-10-01 09:01 | 7491.36 | 2.4935 | 87.5148 | 74.6386 | 2195.5009
2042-10-02 10:01 | 5839.7 | 1.7711 | 88.4253 | 74.6386 | 1711.4471
2042-10-03 11:01 | 8470.32 | 2.8468 | 87.639 | 74.6386 | 2482.4057
2042-10-04 12:01 | 8359.42 | 2.737 | 88.0169 | 74.6386 | 2449.9042
2042-10-05 13:01 | 9808.13 | 3.2532 | 88.0704 | 74.6386 | 2874.4792
2042-10-06 14:01 | 10482 | 3.488 | 88.2149 | 74.6386 | 3071.971
2042-10-07 15:01 | 9633.3 | 3.1469 | 88.5084 | 74.6386 | 2823.2415
2042-10-08 16:01 | 10552.9 | 3.4914 | 88.4771 | 74.6386 | 3092.7497
2042-10-09 17:01 | 8843.9 | 2.7248 | 89.1224 | 74.6386 | 2591.8912
2042-10-10 18:01 | 8263.06 | 2.5916 | 88.965 | 74.6386 | 2421.6638
2042-10-11 19:01 | 6890.68 | 2.1303 | 89.0343 | 74.6386 | 2019.459
2042-10-12 20:01 | 5857.2 | 1.822 | 88.8718 | 74.6386 | 1716.5759
2042-10-13 21:01 | 3519.73 | 1.1076 | 88.6613 | 74.6386 | 1031.531
2042-10-14 22:01 | 3150.56 | 1 | 90.4566 | 74.6386 | 923.338
2042-10-15 23:01 | 3025.29 | 1 | 79.2747 | 74.6386 | 886.625
2042-10-17 00:01 | 0 | 0 | 80.6264 | 74.6386 | 0
2042-10-18 01:01 | 146.317 | 1 | 80.2475 | 74.6386 | 42.8813
2042-10-19 02:01 | 0 | 0 | 80.1275 | 74.6386 | 0
2042-10-20 03:01 | -109.707 | 0.75206 | 79.666 | 74.6386 | -32.1519
2042-10-21 04:01 | -36.0448 | 0.56487 | 79.9298 | 74.6386 | -10.5637
2042-10-22 05:01 | 1145.88 | 1 | 79.2266 | 74.6386 | 335.8243
2042-10-23 06:01 | 1870.8 | 1 | 78.8986 | 74.6386 | 548.2774
2042-10-24 07:01 | 2723 | 1 | 78.5286 | 74.6386 | 798.0325
2042-10-25 08:01 | 4985.19 | 1.4976 | 87.7795 | 74.6386 | 1461.015
2042-10-26 09:01 | 6807.59 | 2.2578 | 87.2167 | 74.6386 | 1995.1077
2042-10-27 10:01 | 8652.34 | 3.0413 | 87.0604 | 74.6386 | 2535.7505
2042-10-28 11:01 | 8065.59 | 2.7179 | 87.6125 | 74.6386 | 2363.7911
2042-10-29 12:01 | 9309.76 | 3.1356 | 87.7438 | 74.6386 | 2728.4213
2042-10-30 13:01 | 8543.93 | 2.7677 | 88.2123 | 74.6386 | 2503.9787
2042-10-31 14:01 | 11129.2 | 3.6868 | 88.1219 | 74.6386 | 3261.6466
2042-11-01 15:01 | 11621 | 3.7786 | 88.508 | 74.6386 | 3405.7789
2042-11-02 16:01 | 11782.1 | 3.8552 | 88.656 | 74.6386 | 3452.9927
2042-11-03 17:01 | 9773.73 | 2.9843 | 89.3251 | 74.6386 | 2864.3975
2042-11-04 18:01 | 8944.05 | 2.7784 | 89.16 | 74.6386 | 2621.2423
2042-11-05 19:01 | 7622.88 | 2.3203 | 89.2943 | 74.6386 | 2234.0456
2042-11-06 20:01 | 6371.2 | 2.0114 | 88.9168 | 74.6386 | 1867.2144
2042-11-07 21:01 | 4232.28 | 1.2872 | 89.0608 | 74.6386 | 1240.3588
2042-11-08 22:01 | 3381.68 | 1.0639 | 88.5522 | 74.6386 | 991.0726
2042-11-09 23:01 | 3109.55 | 1 | 79.3422 | 74.6386 | 911.3191
2042-11-11 00:01 | 0 | 0 | 80.7135 | 74.6386 | 0
2042-11-12 01:01 | -135.254 | 0.80493 | 80.0009 | 74.6386 | -39.639
2042-11-13 02:01 | -301.222 | 1.1497 | 79.556 | 74.6386 | -88.2795
2042-11-14 03:01 | -512.067 | 1.5969 | 79.2684 | 74.6386 | -150.072
2042-11-15 04:01 | -654.511 | 1.8871 | 79.0573 | 74.6386 | -191.8182
2042-11-16 05:01 | -782.407 | 2.1564 | 78.8795 | 74.6386 | -229.3009
2042-11-17 06:01 | -770.025 | 2.111 | 78.774 | 74.6386 | -225.6721
2042-11-18 07:01 | 1929.77 | 1 | 78.6199 | 74.6386 | 565.5598
2042-11-19 08:01 | 4201.2 | 1.4212 | 86.6682 | 74.6386 | 1231.2502
2042-11-20 09:01 | 3383.14 | 1.1176 | 87.0362 | 74.6386 | 991.5005
2042-11-21 10:01 | 3539.35 | 1.1287 | 87.3175 | 74.6386 | 1037.2811
2042-11-22 11:01 | 6123.58 | 1.9532 | 87.3336 | 74.6386 | 1794.6441
2042-11-23 12:01 | 7037.32 | 2.321 | 87.3296 | 74.6386 | 2062.4349
2042-11-24 13:01 | 7292.76 | 2.3727 | 87.6195 | 74.6386 | 2137.297
2042-11-25 14:01 | 6434.22 | 2.0262 | 87.956 | 74.6386 | 1885.6837
2042-11-26 15:01 | 6008.23 | 1.8864 | 87.9956 | 74.6386 | 1760.8384
2042-11-27 16:01 | 5889.55 | 1.8322 | 88.069 | 74.6386 | 1726.0567
2042-11-28 17:01 | 7888.4 | 2.5856 | 87.6858 | 74.6386 | 2311.8618
2042-11-29 18:01 | 6939.64 | 2.153 | 88.2544 | 74.6386 | 2033.8077
2042-11-30 19:01 | 6330.49 | 1.8783 | 88.6173 | 74.6386 | 1855.2835
2042-12-01 20:01 | 5355.81 | 1.59 | 88.5775 | 74.6386 | 1569.633
2042-12-02 21:01 | 4694.01 | 1.4281 | 88.337 | 74.6386 | 1375.6785
2042-12-03 22:01 | 4126.51 | 1.2893 | 88.0822 | 74.6386 | 1209.3607
2042-12-04 23:01 | 3827.9 | 1.2479 | 87.6734 | 74.6386 | 1121.8467
2042-12-06 00:01 | 2903.38 | 1 | 78.9509 | 74.6386 | 850.8967
2042-12-07 01:01 | 2.6266 | 1 | 80.248 | 74.6386 | 0.76979
2042-12-08 02:01 | -231.847 | 1.0474 | 79.452 | 74.6386 | -67.9476
2042-12-09 03:01 | -493.867 | 1.5668 | 79.0606 | 74.6386 | -144.7381
2042-12-10 04:01 | -624.794 | 1.8261 | 78.879 | 74.6386 | -183.109
2042-12-11 05:01 | -842.91 | 2.3012 | 78.6965 | 74.6386 | -247.0325
2042-12-12 06:01 | -991.173 | 2.6044 | 78.5443 | 74.6386 | -290.4841
2042-12-13 07:01 | 0 | 0 | 79.3542 | 74.6386 | 0
2042-12-14 08:01 | 2352.31 | 1 | 85.2819 | 74.6386 | 689.394
2042-12-15 09:01 | 2941.72 | 1 | 89.0579 | 74.6386 | 862.133
2042-12-16 10:01 | 3698.82 | 1.2245 | 86.7204 | 74.6386 | 1084.0171
2042-12-17 11:01 | 4687.04 | 1.5502 | 86.8126 | 74.6386 | 1373.6358
2042-12-18 12:01 | 4718.02 | 1.5696 | 86.8943 | 74.6386 | 1382.7152
2042-12-19 13:01 | 7032.95 | 2.3334 | 86.9992 | 74.6386 | 2061.1542
2042-12-20 14:01 | 7642.16 | 2.468 | 87.4059 | 74.6386 | 2239.696
2042-12-21 15:01 | 7472.34 | 2.4504 | 87.4757 | 74.6386 | 2189.9267
2042-12-22 16:01 | 6502.37 | 2.1006 | 87.6811 | 74.6386 | 1905.6565
2042-12-23 17:01 | 6674.57 | 2.0859 | 87.9309 | 74.6386 | 1956.1234
2042-12-24 18:01 | 4032.07 | 1.2914 | 87.8044 | 74.6386 | 1181.6831
2042-12-25 19:01 | 3143.98 | 1 | 90.9795 | 74.6386 | 921.4096
2042-12-26 20:01 | 2983.67 | 1 | 78.654 | 74.6386 | 874.4274
2042-12-27 21:01 | 290.357 | 1 | 79.8658 | 74.6386 | 85.0952
2042-12-28 22:01 | -116.115 | 0.79373 | 79.3967 | 74.6386 | -34.0299
2042-12-29 23:01 | -357.13 | 1.2831 | 78.8718 | 74.6386 | -104.6645
2042-12-31 00:01 | -1667.47 | 4.2098 | 78.4697 | 74.6386 | -488.6872
2043-01-01 01:01 | -1983.6 | 4.7277 | 78.2147 | 74.6386 | -581.3358
2043-01-02 02:01 | -2161.71 | 5.1052 | 78.0272 | 74.6386 | -633.5347
2043-01-03 03:01 | -2290.1 | 5.3778 | 77.9015 | 74.6386 | -671.1621
2043-01-04 04:01 | -2106.6 | 4.9408 | 77.7934 | 74.6386 | -617.3835
2043-01-05 05:01 | -1928.24 | 4.5688 | 77.7207 | 74.6386 | -565.1114
2043-01-06 06:01 | -1449.36 | 3.5005 | 77.7002 | 74.6386 | -424.7655
2043-01-07 07:01 | -1225.42 | 3.0701 | 77.724 | 74.6386 | -359.1352
2043-01-08 08:01 | -178.306 | 0.71792 | 78.056 | 74.6386 | -52.2563
2043-01-09 09:01 | 2291 | 1 | 77.5927 | 74.6386 | 671.4258
2043-01-10 10:01 | 4123.34 | 1.3416 | 86.1809 | 74.6386 | 1208.4317
2043-01-11 11:01 | 3868.47 | 1.2292 | 86.5776 | 74.6386 | 1133.7366
2043-01-12 12:01 | 5660.52 | 1.8548 | 86.4596 | 74.6386 | 1658.9347
2043-01-13 13:01 | 6469.11 | 2.0771 | 86.8153 | 74.6386 | 1895.909
2043-01-14 14:01 | 7937.14 | 2.6736 | 86.6738 | 74.6386 | 2326.1461
2043-01-15 15:01 | 8532.96 | 2.8131 | 87.054 | 74.6386 | 2500.7637
2043-01-16 16:01 | 8365.52 | 2.6834 | 87.4424 | 74.6386 | 2451.6919
2043-01-17 17:01 | 6611.23 | 2.0876 | 87.689 | 74.6386 | 1937.5603
2043-01-18 18:01 | 5819.23 | 1.8151 | 87.7577 | 74.6386 | 1705.448
2043-01-19 19:01 | 4237.02 | 1.3109 | 87.7883 | 74.6386 | 1241.748
2043-01-20 20:01 | 3208.28 | 1 | 87.8362 | 74.6386 | 940.2541
2043-01-21 21:01 | 2888.18 | 1 | 78.4953 | 74.6386 | 846.442
2043-01-22 22:01 | 124.319 | 1 | 79.7244 | 74.6386 | 36.4343
2043-01-23 23:01 | -865.068 | 2.4404 | 78.6828 | 74.6386 | -253.5264
2043-01-25 00:01 | -1382.11 | 3.486 | 78.3474 | 74.6386 | -405.0565
2043-01-26 01:01 | -1720.18 | 4.1848 | 78.1423 | 74.6386 | -504.135
2043-01-27 02:01 | -1951.97 | 4.6695 | 77.9695 | 74.6386 | -572.0659
2043-01-28 03:01 | -2194.02 | 5.1962 | 77.8074 | 74.6386 | -643.0038
2043-01-29 04:01 | -2201.77 | 5.1801 | 77.6795 | 74.6386 | -645.2751
2043-01-30 05:01 | -2210.84 | 5.2072 | 77.5934 | 74.6386 | -647.9332
2043-01-31 06:01 | -1949.38 | 4.6064 | 77.5231 | 74.6386 | -571.3069
2043-02-01 07:01 | -1154.98 | 2.83 | 77.5157 | 74.6386 | -338.4912
2043-02-02 08:01 | 2248.33 | 1 | 77.4053 | 74.6386 | 658.9205
2043-02-03 09:01 | 3229.88 | 1 | 77.1624 | 74.6386 | 946.5844
2043-02-04 10:01 | 4781.35 | 1.4724 | 86.6061 | 74.6386 | 1401.2754
2043-02-05 11:01 | 7333.87 | 2.3152 | 86.6237 | 74.6386 | 2149.3451
2043-02-06 12:01 | 8527.05 | 2.7936 | 86.6879 | 74.6386 | 2499.0317
2043-02-07 13:01 | 9154.48 | 3 | 86.9895 | 74.6386 | 2682.9132
2043-02-08 14:01 | 9183.58 | 2.9884 | 87.2566 | 74.6386 | 2691.4416
2043-02-09 15:01 | 8908.74 | 2.8805 | 87.4658 | 74.6386 | 2610.894
2043-02-10 16:01 | 8897.43 | 2.8305 | 87.6967 | 74.6386 | 2607.5793
2043-02-11 17:01 | 6575.88 | 2.0267 | 88.0304 | 74.6386 | 1927.2002
2043-02-12 18:01 | 4951.08 | 1.5769 | 87.6971 | 74.6386 | 1451.0183
2043-02-13 19:01 | 2967.06 | 1 | 87.6861 | 74.6386 | 869.5594
2043-02-14 20:01 | 3046.9 | 1 | 78.4479 | 74.6386 | 892.9582
2043-02-15 21:01 | 0 | 0 | 79.8143 | 74.6386 | 0
2043-02-16 22:01 | -629.231 | 1.7637 | 78.668 | 74.6386 | -184.4094
2043-02-17 23:01 | -1468.41 | 3.734 | 78.3428 | 74.6386 | -430.3485
2043-02-19 00:01 | -1797.66 | 4.3452 | 78.0908 | 74.6386 | -526.8421
2043-02-20 01:01 | -1930.99 | 4.6119 | 77.9128 | 74.6386 | -565.9173
2043-02-21 02:01 | -1867.67 | 4.4534 | 77.7612 | 74.6386 | -547.36
2043-02-22 03:01 | -1856.05 | 4.4433 | 77.6716 | 74.6386 | -543.9546
2043-02-23 04:01 | -1791.28 | 4.2991 | 77.5892 | 74.6386 | -524.9723
2043-02-24 05:01 | -1491.42 | 3.6238 | 77.5446 | 74.6386 | -437.0921
2043-02-25 06:01 | -1097.34 | 2.7729 | 77.5586 | 74.6386 | -321.5986
2043-02-26 07:01 | -824.667 | 2.2141 | 77.6184 | 74.6386 | -241.686
2043-02-27 08:01 | 0 | 1 | 78.4911 | 74.6386 | 0
2043-02-28 09:01 | -45.835 | 0.64536 | 78.5871 | 74.6386 | -13.4329
2043-03-01 10:01 | 1934.3 | 1 | 77.6137 | 74.6386 | 566.8874
2043-03-02 11:01 | 2821.1 | 1 | 77.3207 | 74.6386 | 826.7828
2043-03-03 12:01 | 2995.33 | 1 | 89.0641 | 74.6386 | 877.8446
2043-03-04 13:01 | 4591.78 | 1.4741 | 86.2487 | 74.6386 | 1345.7179
2043-03-05 14:01 | 5571.51 | 1.7552 | 86.5491 | 74.6386 | 1632.8484
2043-03-06 15:01 | 4587.6 | 1.4164 | 86.8815 | 74.6386 | 1344.4928
2043-03-07 16:01 | 5726.57 | 1.8256 | 86.6575 | 74.6386 | 1678.292
2043-03-08 17:01 | 5900.07 | 1.8099 | 87.0616 | 74.6386 | 1729.1398
2043-03-09 18:01 | 5890.77 | 1.8322 | 87.0678 | 74.6386 | 1726.4143
2043-03-10 19:01 | 4950.37 | 1.5455 | 87.1123 | 74.6386 | 1450.8102
2043-03-11 20:01 | 4292.16 | 1.3576 | 86.9976 | 74.6386 | 1257.9079
2043-03-12 21:01 | 3137.28 | 1 | 92.2447 | 74.6386 | 919.446
2043-03-13 22:01 | 3046.07 | 1 | 77.9546 | 74.6386 | 892.715
2043-03-14 23:01 | 0 | 0 | 79.3863 | 74.6386 | 0
2043-03-16 00:01 | -433.572 | 1.3912 | 78.4015 | 74.6386 | -127.0674
2043-03-17 01:01 | -674.897 | 1.9656 | 78.1513 | 74.6386 | -197.7928
2043-03-18 02:01 | -911.609 | 2.4643 | 77.9695 | 74.6386 | -267.1662
2043-03-19 03:01 | -785.58 | 2.1428 | 77.8778 | 74.6386 | -230.2308
2043-03-20 04:01 | -695.428 | 1.9634 | 77.8232 | 74.6386 | -203.8098
2043-03-21 05:01 | -542.954 | 1.6305 | 77.8336 | 74.6386 | -159.1241
2043-03-22 06:01 | -216.234 | 0.91362 | 78.031 | 74.6386 | -63.3719
2043-03-23 07:01 | -204.367 | 0.93989 | 78.0695 | 74.6386 | -59.8941
2043-03-24 08:01 | 2347.29 | 1 | 77.4282 | 74.6386 | 687.9228
2043-03-25 09:01 | 4687.33 | 1.5185 | 86.0399 | 74.6386 | 1373.7208
2043-03-26 10:01 | 5620.61 | 1.8357 | 86.2227 | 74.6386 | 1647.2382
2043-03-27 11:01 | 8014.71 | 2.8664 | 85.8032 | 74.6386 | 2348.8796
2043-03-28 12:01 | 10216.8 | 3.5205 | 86.3666 | 74.6386 | 2994.2485
2043-03-29 13:01 | 11534.7 | 3.864 | 86.9425 | 74.6386 | 3380.4869
2043-03-30 14:01 | 11344.2 | 3.7214 | 87.4224 | 74.6386 | 3324.6568
2043-03-31 15:01 | 11008.1 | 3.5083 | 87.8397 | 74.6386 | 3226.1556
2043-04-01 16:01 | 10611.9 | 3.3339 | 88.0928 | 74.6386 | 3110.0409
2043-04-02 17:01 | 9340.96 | 2.9269 | 88.2156 | 74.6386 | 2737.5651
2043-04-03 18:01 | 8930.78 | 2.7071 | 88.4704 | 74.6386 | 2617.3533
2043-04-04 19:01 | 7449.98 | 2.2879 | 88.3773 | 74.6386 | 2183.3736
2043-04-05 20:01 | 6300.6 | 1.9264 | 88.3335 | 74.6386 | 1846.5236
2043-04-06 21:01 | 3790.81 | 1.1598 | 88.2197 | 74.6386 | 1110.9767
2043-04-07 22:01 | 3154.56 | 1 | 88.6965 | 74.6386 | 924.5103
2043-04-08 23:01 | 2994.66 | 1 | 78.6395 | 74.6386 | 877.6482
2043-04-10 00:01 | 0 | 0 | 79.9685 | 74.6386 | 0
2043-04-11 01:01 | 0 | 1 | 79.652 | 74.6386 | 0
2043-04-12 02:01 | -6.7586 | 0.51826 | 79.4593 | 74.6386 | -1.9808
2043-04-13 03:01 | -168.395 | 0.87762 | 78.8829 | 74.6386 | -49.3517
2043-04-14 04:01 | -154.711 | 0.82543 | 78.7787 | 74.6386 | -45.3413
2043-04-15 05:01 | 31.6245 | 1 | 79.1079 | 74.6386 | 9.2682
2043-04-16 06:01 | 1896.41 | 1 | 78.1627 | 74.6386 | 555.7829
2043-04-17 07:01 | 2809.28 | 1 | 77.821 | 74.6386 | 823.3187
2043-04-18 08:01 | 2989.82 | 1 | 77.8356 | 74.6386 | 876.2297
2043-04-19 09:01 | 3026.52 | 1 | 77.8764 | 74.6386 | 886.9855
2043-04-20 10:01 | 3188.13 | 1 | 77.8331 | 74.6386 | 934.3487
2043-04-21 11:01 | 3259.79 | 1 | 91.6095 | 74.6386 | 955.3501
2043-04-22 12:01 | 3327.28 | 1 | 91.5825 | 74.6386 | 975.1295
2043-04-23 13:01 | 3036.17 | 1 | 77.9484 | 74.6386 | 889.8136
2043-04-24 14:01 | 3724.76 | 1.1757 | 86.8877 | 74.6386 | 1091.6194
2043-04-25 15:01 | 4240.05 | 1.3318 | 86.9421 | 74.6386 | 1242.636
2043-04-26 16:01 | 4301.62 | 1.3655 | 86.9127 | 74.6386 | 1260.6804
2043-04-27 17:01 | 4401.11 | 1.3798 | 87.0358 | 74.6386 | 1289.838
2043-04-28 18:01 | 4953.31 | 1.5478 | 87.0751 | 74.6386 | 1451.6719
2043-04-29 19:01 | 4084.59 | 1.2919 | 87.0432 | 74.6386 | 1197.0752
2043-04-30 20:01 | 3737.05 | 1.1606 | 87.1512 | 74.6386 | 1095.2212
2043-05-01 21:01 | 3055.81 | 1 | 78.0247 | 74.6386 | 895.5695
2043-05-02 22:01 | 3166.49 | 1 | 77.917 | 74.6386 | 928.0066
2043-05-03 23:01 | 0 | 0 | 79.4319 | 74.6386 | 0
2043-05-05 00:01 | -314.769 | 1.2079 | 78.5736 | 74.6386 | -92.2497
2043-05-06 01:01 | -446.092 | 1.4598 | 78.3135 | 74.6386 | -130.7367
2043-05-07 02:01 | -526.472 | 1.6249 | 78.1777 | 74.6386 | -154.2937
2043-05-08 03:01 | -532.187 | 1.6272 | 78.0883 | 74.6386 | -155.9686
2043-05-09 04:01 | -613.444 | 1.8127 | 77.982 | 74.6386 | -179.7827
2043-05-10 05:01 | -879.205 | 2.4044 | 77.8717 | 74.6386 | -257.6696
2043-05-11 06:01 | -1313.08 | 3.3532 | 77.7405 | 74.6386 | -384.8258
2043-05-12 07:01 | -697.766 | 1.8788 | 77.6977 | 74.6386 | -204.495
2043-05-13 08:01 | 1877.53 | 1 | 77.6406 | 74.6386 | 550.2497
2043-05-14 09:01 | 3075.38 | 1 | 77.2151 | 74.6386 | 901.3049
2043-05-15 10:01 | 2887.62 | 1 | 77.4524 | 74.6386 | 846.2779
2043-05-16 11:01 | 2902.76 | 1 | 86.0122 | 74.6386 | 850.715
2043-05-17 12:01 | 4108.47 | 1.4637 | 85.5972 | 74.6386 | 1204.0737
2043-05-18 13:01 | 4256.95 | 1.5145 | 85.7418 | 74.6386 | 1247.5889
2043-05-19 14:01 | 4196.9 | 1.5006 | 85.7813 | 74.6386 | 1229.99
2043-05-20 15:01 | 3760.99 | 1.3472 | 85.7941 | 74.6386 | 1102.2374
2043-05-21 16:01 | 2757.73 | 1 | 87.9266 | 74.6386 | 808.2109
2043-05-22 17:01 | 2945.68 | 1.0612 | 85.6861 | 74.6386 | 863.2936
2043-05-23 18:01 | 2830.55 | 1 | 77.7347 | 74.6386 | 829.5523
2043-05-24 19:01 | 2776.98 | 1 | 77.7492 | 74.6386 | 813.8525
2043-05-25 20:01 | -120.541 | 0.81532 | 78.7113 | 74.6386 | -35.3271
2043-05-26 21:01 | -594.225 | 1.8266 | 78.0534 | 74.6386 | -174.1502
2043-05-27 22:01 | -984.59 | 2.6457 | 77.7774 | 74.6386 | -288.5548
2043-05-28 23:01 | -1303.21 | 3.317 | 77.6129 | 74.6386 | -381.9331
2043-05-30 00:01 | -3054.63 | 6.5195 | 77.3171 | 74.6386 | -895.2237
2043-05-31 01:01 | -3409.04 | 6.5195 | 76.9564 | 74.6386 | -999.091
2043-06-01 02:01 | -3665.79 | 6.5195 | 76.7031 | 74.6386 | -1074.337
2043-06-02 03:01 | -3824.26 | 6.5195 | 76.5198 | 74.6386 | -1120.78
2043-06-03 04:01 | -3965.78 | 6.5195 | 76.3571 | 74.6386 | -1162.2554
2043-06-04 05:01 | -4185.87 | 6.5195 | 76.1682 | 74.6386 | -1226.7574
2043-06-05 06:01 | -4097.16 | 6.5195 | 76.1026 | 74.6386 | -1200.7591
2043-06-06 07:01 | -2648.48 | 6.2169 | 76.5005 | 74.6386 | -776.1929
2043-06-07 08:01 | -1162.87 | 2.7506 | 76.5486 | 74.6386 | -340.8036
2043-06-08 09:01 | -550.182 | 1.6032 | 76.8446 | 74.6386 | -161.2424
2043-06-09 10:01 | 2552.01 | 1 | 76.5075 | 74.6386 | 747.9203
2043-06-10 11:01 | 2875.28 | 1 | 88.4189 | 74.6386 | 842.6614
2043-06-11 12:01 | 3251.82 | 1.1777 | 84.7327 | 74.6386 | 953.0144
2043-06-12 13:01 | 3698.25 | 1.3315 | 84.9087 | 74.6386 | 1083.8501
2043-06-13 14:01 | 3709.53 | 1.3455 | 84.9911 | 74.6386 | 1087.1559
2043-06-14 15:01 | 3688.99 | 1.341 | 85.0828 | 74.6386 | 1081.1362
2043-06-15 16:01 | 2752.53 | 1 | 85.5915 | 74.6386 | 806.6869
2043-06-16 17:01 | 2803.28 | 1.0074 | 85.2012 | 74.6386 | 821.5603
2043-06-17 18:01 | 2739.32 | 1 | 77.3073 | 74.6386 | 802.8154
2043-06-18 19:01 | 0 | 0 | 78.644 | 74.6386 | 0
2043-06-19 20:01 | -497.954 | 1.5866 | 77.7068 | 74.6386 | -145.9359
2043-06-20 21:01 | -1202.55 | 3.1718 | 77.4094 | 74.6386 | -352.4326
2043-06-21 22:01 | -1645.58 | 4.0789 | 77.2175 | 74.6386 | -482.2719
2043-06-22 23:01 | -2099.86 | 5.0663 | 77.0616 | 74.6386 | -615.4082
2043-06-24 00:01 | -3285.51 | 6.5195 | 76.7181 | 74.6386 | -962.8879
2043-06-25 01:01 | -3649.35 | 6.5195 | 76.422 | 74.6386 | -1069.5189
2043-06-26 02:01 | -4019.14 | 6.5195 | 76.1495 | 74.6386 | -1177.8937
2043-06-27 03:01 | -4178.81 | 6.5195 | 75.9691 | 74.6386 | -1224.6883
2043-06-28 04:01 | -4167.47 | 6.5195 | 75.8696 | 74.6386 | -1221.3649
2043-06-29 05:01 | -3967.62 | 6.5195 | 75.8581 | 74.6386 | -1162.7946
2043-06-30 06:01 | -3454.29 | 6.5195 | 75.9939 | 74.6386 | -1012.3525
2043-07-01 07:01 | -2643.18 | 6.2077 | 76.2375 | 74.6386 | -774.6396
2043-07-02 08:01 | -687.484 | 1.6581 | 76.2973 | 74.6386 | -201.4817
2043-07-03 09:01 | 2658.36 | 1 | 76.1441 | 74.6386 | 779.0884
2043-07-04 10:01 | 3355.92 | 1.059 | 85.2521 | 74.6386 | 983.5231
2043-07-05 11:01 | 6090.78 | 1.9321 | 85.4226 | 74.6386 | 1785.0314
2043-07-06 12:01 | 7391.14 | 2.3994 | 85.5915 | 74.6386 | 2166.1293
2043-07-07 13:01 | 8290.63 | 2.7024 | 85.8889 | 74.6386 | 2429.7438
2043-07-08 14:01 | 8805.74 | 2.8536 | 86.2107 | 74.6386 | 2580.7076
2043-07-09 15:01 | 8967.55 | 2.8618 | 86.5487 | 74.6386 | 2628.1295
2043-07-10 16:01 | 8623.49 | 2.7627 | 86.721 | 74.6386 | 2527.2954
2043-07-11 17:01 | 6354.49 | 1.9942 | 87.0002 | 74.6386 | 1862.3172
2043-07-12 18:01 | 4886.28 | 1.5153 | 87.033 | 74.6386 | 1432.0273
2043-07-13 19:01 | 3106.51 | 1.0083 | 86.5971 | 74.6386 | 910.4282
2043-07-14 20:01 | 3167.64 | 1 | 77.6258 | 74.6386 | 928.3436
2043-07-15 21:01 | 0 | 0 | 79.0756 | 74.6386 | 0
2043-07-16 22:01 | -539.099 | 1.6472 | 78.0124 | 74.6386 | -157.9943
2043-07-17 23:01 | -1520.07 | 3.8854 | 77.6454 | 74.6386 | -445.4885
2043-07-19 00:01 | -1905.52 | 4.6144 | 77.4015 | 74.6386 | -558.4528
2043-07-20 01:01 | -2187.63 | 5.2187 | 77.225 | 74.6386 | -641.1311
2043-07-21 02:01 | -2336.38 | 5.5257 | 77.0618 | 74.6386 | -684.7254
2043-07-22 03:01 | -2607.83 | 6.1399 | 76.9483 | 74.6386 | -764.2795
2043-07-23 04:01 | -2297.63 | 5.3766 | 76.8315 | 74.6386 | -673.3689
2043-07-24 05:01 | -2263.94 | 5.3608 | 76.7942 | 74.6386 | -663.4953
2043-07-25 06:01 | -1941.93 | 4.6155 | 76.7573 | 74.6386 | -569.1235
2043-07-26 07:01 | -1281.6 | 3.144 | 76.7735 | 74.6386 | -375.5999
2043-07-27 08:01 | 2665.7 | 1 | 76.4687 | 74.6386 | 781.2396
2043-07-28 09:01 | 3709.87 | 1.1435 | 85.7418 | 74.6386 | 1087.2556
2043-07-29 10:01 | 6360.71 | 2.0824 | 85.5124 | 74.6386 | 1864.1401
2043-07-30 11:01 | 8229.39 | 2.7291 | 85.7415 | 74.6386 | 2411.7961
2043-07-31 12:01 | 9200.1 | 3.0239 | 86.1577 | 74.6386 | 2696.2832
2043-08-01 13:01 | 9586.06 | 3.131 | 86.5094 | 74.6386 | 2809.3969
2043-08-02 14:01 | 8420.77 | 2.6921 | 86.884 | 74.6386 | 2467.8841
2043-08-03 15:01 | 8609.75 | 2.7702 | 86.9226 | 74.6386 | 2523.2686
2043-08-04 16:01 | 9538.61 | 3.0676 | 87.0227 | 74.6386 | 2795.4906
2043-08-05 17:01 | 7629.24 | 2.3846 | 87.4036 | 74.6386 | 2235.9095
2043-08-06 18:01 | 6481.1 | 1.9751 | 87.5784 | 74.6386 | 1899.4229
2043-08-07 19:01 | 5215.64 | 1.5488 | 87.7208 | 74.6386 | 1528.5532
2043-08-08 20:01 | 3945.37 | 1.2418 | 87.1776 | 74.6386 | 1156.2738
2043-08-09 21:01 | 3064.18 | 1 | 78.0583 | 74.6386 | 898.0225
2043-08-10 22:01 | 3052.08 | 1 | 77.9133 | 74.6386 | 894.4764
2043-08-11 23:01 | -270.101 | 1.1442 | 78.7459 | 74.6386 | -79.1588
2043-08-13 00:01 | -774.326 | 2.2069 | 78.169 | 74.6386 | -226.9325
2043-08-14 01:01 | -969.323 | 2.5797 | 77.8871 | 74.6386 | -284.0805
2043-08-15 02:01 | -1108.2 | 2.8725 | 77.7298 | 74.6386 | -324.7814
2043-08-16 03:01 | -1430.63 | 3.5926 | 77.5834 | 74.6386 | -419.2763
2043-08-17 04:01 | -1207.3 | 3.0306 | 77.4428 | 74.6386 | -353.8247
2043-08-18 05:01 | -1105.38 | 2.8414 | 77.4085 | 74.6386 | -323.9549
2043-08-19 06:01 | -700.601 | 1.9298 | 77.4325 | 74.6386 | -205.3259
2043-08-20 07:01 | -451.091 | 1.4289 | 77.5364 | 74.6386 | -132.2017
2043-08-21 08:01 | 0 | 0 | 78.2706 | 74.6386 | 0
2043-08-22 09:01 | 2114.46 | 1 | 83.5042 | 74.6386 | 619.6871
2043-08-23 10:01 | 5553.81 | 2.1096 | 84.6363 | 74.6386 | 1627.661
2043-08-24 11:01 | 7380.86 | 2.6236 | 85.3884 | 74.6386 | 2163.1165
2043-08-25 12:01 | 8583.81 | 2.9903 | 85.8306 | 74.6386 | 2515.6664
2043-08-26 13:01 | 9717.98 | 3.2111 | 86.469 | 74.6386 | 2848.0588
2043-08-27 14:01 | 9439.79 | 3.081 | 86.8388 | 74.6386 | 2766.5294
2043-08-28 15:01 | 9647 | 3.1272 | 87.0649 | 74.6386 | 2827.2566
2043-08-29 16:01 | 9510.72 | 3.065 | 87.2405 | 74.6386 | 2787.3169
2043-08-30 17:01 | 7767.35 | 2.4505 | 87.5071 | 74.6386 | 2276.3856
2043-08-31 18:01 | 6681.36 | 2.0574 | 87.6569 | 74.6386 | 1958.1133
2043-09-01 19:01 | 5498.88 | 1.6564 | 87.7608 | 74.6386 | 1611.5626
2043-09-02 20:01 | 4090.36 | 1.3016 | 87.26 | 74.6386 | 1198.7662
2043-09-03 21:01 | 3142.01 | 1 | 92.045 | 74.6386 | 920.8322
2043-09-04 22:01 | 3089.43 | 1 | 78.037 | 74.6386 | 905.4226
2043-09-05 23:01 | 0 | 0 | 79.4472 | 74.6386 | 0
2043-09-07 00:01 | -512.923 | 1.5775 | 78.3874 | 74.6386 | -150.3229
2043-09-08 01:01 | -730.018 | 2.0778 | 78.1055 | 74.6386 | -213.9472
2043-09-09 02:01 | -773.165 | 2.1423 | 77.9422 | 74.6386 | -226.5923
2043-09-10 03:01 | -1033.73 | 2.7339 | 77.7864 | 74.6386 | -302.9564
2043-09-11 04:01 | -835.865 | 2.2414 | 77.6695 | 74.6386 | -244.9678
2043-09-12 05:01 | -761.707 | 2.1105 | 77.6426 | 74.6386 | -223.2343
2043-09-13 06:01 | -272.265 | 1.006 | 77.8168 | 74.6386 | -79.793
2043-09-14 07:01 | 565.479 | 1 | 78.1836 | 74.6386 | 165.7255
2043-09-15 08:01 | 2135.14 | 1 | 86.5475 | 74.6386 | 625.7478
2043-09-16 09:01 | 2773.33 | 1 | 88.2048 | 74.6386 | 812.7828
2043-09-17 10:01 | 5734.3 | 1.9579 | 85.6434 | 74.6386 | 1680.5574
2043-09-18 11:01 | 8028.12 | 2.7753 | 85.8333 | 74.6386 | 2352.8097
2043-09-19 12:01 | 9753.25 | 3.3436 | 86.2231 | 74.6386 | 2858.3954
2043-09-20 13:01 | 8462.93 | 2.6786 | 87.117 | 74.6386 | 2480.24
2043-09-21 14:01 | 9280.17 | 3.0497 | 86.9474 | 74.6386 | 2719.7494
2043-09-22 15:01 | 9030.95 | 2.9251 | 87.222 | 74.6386 | 2646.7102
2043-09-23 16:01 | 9921.65 | 3.2577 | 87.2329 | 74.6386 | 2907.7486
2043-09-24 17:01 | 8290.67 | 2.6024 | 87.7146 | 74.6386 | 2429.7555
2043-09-25 18:01 | 7444.15 | 2.3073 | 87.7936 | 74.6386 | 2181.665
2043-09-26 19:01 | 5933.98 | 1.804 | 87.9159 | 74.6386 | 1739.0779
2043-09-27 20:01 | 4906.11 | 1.4949 | 87.8022 | 74.6386 | 1437.8389
2043-09-28 21:01 | 3115.8 | 1 | 89.7202 | 74.6386 | 913.1508
2043-09-29 22:01 | 3025.95 | 1 | 78.2637 | 74.6386 | 886.8184
2043-09-30 23:01 | -257.526 | 1.096 | 79.0528 | 74.6386 | -75.4734
2043-10-02 00:01 | -643.473 | 1.9085 | 78.4844 | 74.6386 | -188.5833
2043-10-03 01:01 | -862.341 | 2.3512 | 78.1932 | 74.6386 | -252.7272
2043-10-04 02:01 | -1121.23 | 2.9113 | 77.9957 | 74.6386 | -328.6001
2043-10-05 03:01 | -1355.74 | 3.4091 | 77.8323 | 74.6386 | -397.3282
2043-10-06 04:01 | -1358.44 | 3.3828 | 77.6783 | 74.6386 | -398.1195
2043-10-07 05:01 | -1418.52 | 3.5254 | 77.5951 | 74.6386 | -415.7272
2043-10-08 06:01 | -1144.85 | 2.8899 | 77.5355 | 74.6386 | -335.5224
2043-10-09 07:01 | -555.252 | 1.5917 | 77.6042 | 74.6386 | -162.7283
2043-10-10 08:01 | 2629.21 | 1 | 77.1564 | 74.6386 | 770.5454
2043-10-11 09:01 | 3153.14 | 1.0021 | 86.0977 | 74.6386 | 924.0941
2043-10-12 10:01 | 5930.97 | 1.941 | 86.001 | 74.6386 | 1738.1957
2043-10-13 11:01 | 7698.59 | 2.6113 | 86.0185 | 74.6386 | 2256.234
2043-10-14 12:01 | 9117 | 3.0592 | 86.3917 | 74.6386 | 2671.9289
2043-10-15 13:01 | 9605.31 | 3.2415 | 86.6431 | 74.6386 | 2815.0385
2043-10-16 14:01 | 10260.4 | 3.3 | 87.1969 | 74.6386 | 3007.0264
2043-10-17 15:01 | 9797.68 | 3.1891 | 87.321 | 74.6386 | 2871.4166
2043-10-18 16:01 | 9580.07 | 3.1209 | 87.4242 | 74.6386 | 2807.6414
2043-10-19 17:01 | 7367.41 | 2.3043 | 87.8101 | 74.6386 | 2159.1747
2043-10-20 18:01 | 6002.54 | 1.8223 | 87.9559 | 74.6386 | 1759.1708
2043-10-21 19:01 | 4283.22 | 1.3183 | 87.737 | 74.6386 | 1255.2879
2043-10-22 20:01 | 3189.8 | 1 | 88.5985 | 74.6386 | 934.8381
2043-10-23 21:01 | 3008.61 | 1 | 78.2495 | 74.6386 | 881.7366
2043-10-24 22:01 | -81.8119 | 0.72002 | 79.3055 | 74.6386 | -23.9767
2043-10-25 23:01 | -1110.3 | 2.9893 | 78.3899 | 74.6386 | -325.3968
2043-10-27 00:01 | -1787.06 | 4.3806 | 78.0334 | 74.6386 | -523.7356
2043-10-28 01:01 | -2141.39 | 5.0983 | 77.7956 | 74.6386 | -627.5795
2043-10-29 02:01 | -2470.66 | 5.8128 | 77.5994 | 74.6386 | -724.079
2043-10-30 03:01 | -2554.03 | 5.9615 | 77.4125 | 74.6386 | -748.5123
2043-10-31 04:01 | -2670.63 | 6.2288 | 77.2836 | 74.6386 | -782.6844
2043-11-01 05:01 | -2852.26 | 6.5195 | 77.1616 | 74.6386 | -835.9149
2043-11-02 06:01 | -2861.42 | 6.5195 | 77.0627 | 74.6386 | -838.5994
2043-11-03 07:01 | -1825.76 | 4.2438 | 77.0057 | 74.6386 | -535.0774
2043-11-04 08:01 | 0 | 1 | 78.0249 | 74.6386 | 0
2043-11-05 09:01 | 2672.75 | 1 | 76.8386 | 74.6386 | 783.3057
2043-11-06 10:01 | 3782.22 | 1.2301 | 85.6494 | 74.6386 | 1108.4593
2043-11-07 11:01 | 5489.99 | 1.7721 | 85.8907 | 74.6386 | 1608.9572
2043-11-08 12:01 | 6451.18 | 2.138 | 85.9384 | 74.6386 | 1890.6542
2043-11-09 13:01 | 6815.09 | 2.2361 | 86.2354 | 74.6386 | 1997.3057
2043-11-10 14:01 | 7341.33 | 2.4451 | 86.2944 | 74.6386 | 2151.5314
2043-11-11 15:01 | 6751.79 | 2.1813 | 86.6589 | 74.6386 | 1978.7543
2043-11-12 16:01 | 5687.45 | 1.8031 | 86.8597 | 74.6386 | 1666.8271
2043-11-13 17:01 | 6323.78 | 2.025 | 86.7649 | 74.6386 | 1853.317
2043-11-14 18:01 | 4163.61 | 1.2978 | 87.0346 | 74.6386 | 1220.2336
2043-11-15 19:01 | 3128.51 | 1 | 90.0113 | 74.6386 | 916.8758
2043-11-16 20:01 | 3034.76 | 1 | 77.7497 | 74.6386 | 889.4004
2043-11-17 21:01 | 2139.06 | 1 | 78.1148 | 74.6386 | 626.8966
2043-11-18 22:01 | -61.232 | 0.68138 | 78.8358 | 74.6386 | -17.9453
2043-11-19 23:01 | -388.448 | 1.3704 | 78.1348 | 74.6386 | -113.8429
2043-11-21 00:01 | -1807.24 | 4.5586 | 77.7122 | 74.6386 | -529.6498
2043-11-22 01:01 | -2204.05 | 5.2479 | 77.4583 | 74.6386 | -645.9433
2043-11-23 02:01 | -2479.2 | 5.8418 | 77.2701 | 74.6386 | -726.5818
2043-11-24 03:01 | -2642.28 | 6.1835 | 77.1203 | 74.6386 | -774.3758
2043-11-25 04:01 | -2700.95 | 6.3004 | 77.0124 | 74.6386 | -791.5703
2043-11-26 05:01 | -2868.92 | 6.5195 | 76.8876 | 74.6386 | -840.7975
2043-11-27 06:01 | -2983.4 | 6.5195 | 76.771 | 74.6386 | -874.3482
2043-11-28 07:01 | -1737.88 | 4.0529 | 76.7683 | 74.6386 | -509.3224
2043-11-29 08:01 | -789.721 | 2.0513 | 76.8943 | 74.6386 | -231.4444
2043-11-30 09:01 | 2425.76 | 1 | 76.6888 | 74.6386 | 710.9201
2043-12-01 10:01 | 4212.87 | 1.3716 | 85.3838 | 74.6386 | 1234.6703
2043-12-02 11:01 | 5935.42 | 2.0014 | 85.3803 | 74.6386 | 1739.4999
2043-12-03 12:01 | 6406.41 | 2.1275 | 85.7629 | 74.6386 | 1877.5334
2043-12-04 13:01 | 5207.03 | 1.6816 | 86.1705 | 74.6386 | 1526.0299
2043-12-05 14:01 | 6131.19 | 2.0115 | 86.1092 | 74.6386 | 1796.8744
2043-12-06 15:01 | 6468.14 | 2.1027 | 86.2915 | 74.6386 | 1895.6247
2043-12-07 16:01 | 5527.94 | 1.745 | 86.625 | 74.6386 | 1620.0793
2043-12-08 17:01 | 6560.53 | 2.118 | 86.4576 | 74.6386 | 1922.7015
2043-12-09 18:01 | 5045.96 | 1.5499 | 86.938 | 74.6386 | 1478.8249
2043-12-10 19:01 | 3511.6 | 1.1205 | 86.6413 | 74.6386 | 1029.1484
2043-12-11 20:01 | 3030.3 | 1 | 89.239 | 74.6386 | 888.0933
2043-12-12 21:01 | 3069.02 | 1 | 77.5451 | 74.6386 | 899.441
2043-12-13 22:01 | 3061.29 | 1 | 77.5215 | 74.6386 | 897.1755
2043-12-14 23:01 | 0 | 0 | 78.9594 | 74.6386 | 0
2043-12-16 00:01 | -993.309 | 2.6828 | 77.8319 | 74.6386 | -291.1101
2043-12-17 01:01 | -1316.68 | 3.3464 | 77.5772 | 74.6386 | -385.8808
2043-12-18 02:01 | -1739.14 | 4.2722 | 77.4126 | 74.6386 | -509.6916
2043-12-19 03:01 | -1774.73 | 4.2897 | 77.2598 | 74.6386 | -520.122
2043-12-20 04:01 | -1817.64 | 4.3927 | 77.1457 | 74.6386 | -532.6977
2043-12-21 05:01 | -1449.61 | 3.5382 | 77.0801 | 74.6386 | -424.8388
2043-12-22 06:01 | -1039.9 | 2.661 | 77.1017 | 74.6386 | -304.7646
2043-12-23 07:01 | -620.512 | 1.7652 | 77.1983 | 74.6386 | -181.8541
2043-12-24 08:01 | 2495 | 1 | 76.8427 | 74.6386 | 731.2123
2043-12-25 09:01 | 3248.59 | 1.0629 | 85.5051 | 74.6386 | 952.0677
2043-12-26 10:01 | 5249.6 | 1.7538 | 85.501 | 74.6386 | 1538.5059
2043-12-27 11:01 | 7532.89 | 2.5564 | 85.6198 | 74.6386 | 2207.6721
2043-12-28 12:01 | 8449.51 | 2.8529 | 85.977 | 74.6386 | 2476.3069
2043-12-29 13:01 | 9819.24 | 3.192 | 86.5292 | 74.6386 | 2877.7352
2043-12-30 14:01 | 10090.8 | 3.264 | 86.8375 | 74.6386 | 2957.3216
2043-12-31 15:01 | 10096.7 | 3.259 | 87.0763 | 74.6386 | 2959.0507
2044-01-01 16:01 | 9999.1 | 3.1876 | 87.3358 | 74.6386 | 2930.4469
2044-01-02 17:01 | 7920.46 | 2.4586 | 87.657 | 74.6386 | 2321.2577
2044-01-03 18:01 | 6606.97 | 2.0545 | 87.6045 | 74.6386 | 1936.3118
2044-01-04 19:01 | 5251.2 | 1.6207 | 87.5795 | 74.6386 | 1538.9748
2044-01-05 20:01 | 4009.05 | 1.2734 | 87.2385 | 74.6386 | 1174.9366
2044-01-06 21:01 | 2977.37 | 1 | 78.2016 | 74.6386 | 872.581
2044-01-07 22:01 | 3068.17 | 1 | 77.9857 | 74.6386 | 899.1919
2044-01-08 23:01 | -340.016 | 1.2993 | 78.7621 | 74.6386 | -99.6489
2044-01-10 00:01 | -850.952 | 2.3683 | 78.2208 | 74.6386 | -249.3894
2044-01-11 01:01 | -1026.46 | 2.6962 | 77.938 | 74.6386 | -300.8257
2044-01-12 02:01 | -1136.05 | 2.926 | 77.7723 | 74.6386 | -332.9434
2044-01-13 03:01 | -1230.58 | 3.1289 | 77.6332 | 74.6386 | -360.6474
2044-01-14 04:01 | -1101.98 | 2.8231 | 77.5123 | 74.6386 | -322.9585
2044-01-15 05:01 | -1155.2 | 2.9699 | 77.458 | 74.6386 | -338.5557
2044-01-16 06:01 | -787.409 | 2.1179 | 77.448 | 74.6386 | -230.7668
2044-01-17 07:01 | -483.956 | 1.4894 | 77.5418 | 74.6386 | -141.8335
2044-01-18 08:01 | 2479.88 | 1 | 84.3497 | 74.6386 | 726.7811
2044-01-19 09:01 | 4851.31 | 1.6041 | 85.6521 | 74.6386 | 1421.7786
2044-01-20 10:01 | 7180.69 | 2.4543 | 85.6797 | 74.6386 | 2104.4525
2044-01-21 11:01 | 6009.39 | 1.9034 | 86.545 | 74.6386 | 1761.1784
2044-01-22 12:01 | 8309.86 | 2.8292 | 86.1261 | 74.6386 | 2435.3796
2044-01-23 13:01 | 6505.15 | 2.1312 | 86.6631 | 74.6386 | 1906.4713
2044-01-24 14:01 | 7604.19 | 2.4863 | 86.7133 | 74.6386 | 2228.5681
2044-01-25 15:01 | 6529.26 | 2.0498 | 87.1165 | 74.6386 | 1913.5372
2044-01-26 16:01 | 7876.8 | 2.5492 | 86.8836 | 74.6386 | 2308.4622
2044-01-27 17:01 | 6788.11 | 2.1516 | 87.1692 | 74.6386 | 1989.3987
2044-01-28 18:01 | 6306.58 | 1.9956 | 87.1861 | 74.6386 | 1848.2761
2044-01-29 19:01 | 5365.33 | 1.6169 | 87.5662 | 74.6386 | 1572.423
2044-01-30 20:01 | 4460.13 | 1.3782 | 87.3161 | 74.6386 | 1307.1351
2044-01-31 21:01 | 3148.88 | 1 | 91.3647 | 74.6386 | 922.8456
2044-02-01 22:01 | 3115 | 1 | 77.911 | 74.6386 | 912.9164
2044-02-02 23:01 | 0 | 0 | 79.3479 | 74.6386 | 0
2044-02-04 00:01 | -235.119 | 0.87386 | 78.4254 | 74.6386 | -68.9066
2044-02-05 01:01 | -265.61 | 1.0785 | 78.3007 | 74.6386 | -77.8426
2044-02-06 02:01 | -324.042 | 1.1965 | 78.1344 | 74.6386 | -94.9673
2044-02-07 03:01 | -632.726 | 1.889 | 77.8994 | 74.6386 | -185.4337
2044-02-08 04:01 | -1027.52 | 2.7413 | 77.6923 | 74.6386 | -301.1364
2044-02-09 05:01 | -1259.85 | 3.2122 | 77.5653 | 74.6386 | -369.2256
2044-02-10 06:01 | -1226.49 | 3.1028 | 77.4768 | 74.6386 | -359.4487
2044-02-11 07:01 | -1594.44 | 3.9586 | 77.3987 | 74.6386 | -467.2842
2044-02-12 08:01 | -1792.06 | 4.353 | 77.2812 | 74.6386 | -525.2009
2044-02-13 09:01 | -2371.23 | 5.668 | 77.1654 | 74.6386 | -694.9389
2044-02-14 10:01 | -2402.19 | 5.6463 | 77.0096 | 74.6386 | -704.0124
2044-02-15 11:01 | -2519.99 | 5.9283 | 76.9119 | 74.6386 | -738.5362
2044-02-16 12:01 | -2544.42 | 5.9699 | 76.8045 | 74.6386 | -745.6959
2044-02-17 13:01 | -2522.96 | 5.9227 | 76.7104 | 74.6386 | -739.4066
2044-02-18 14:01 | -2821.36 | 6.5195 | 76.6031 | 74.6386 | -826.859
2044-02-19 15:01 | -2429.32 | 5.6739 | 76.5125 | 74.6386 | -711.9634
2044-02-20 16:01 | -2128.28 | 5.04 | 76.4634 | 74.6386 | -623.7373
2044-02-21 17:01 | -2522.36 | 6.0132 | 76.4337 | 74.6386 | -739.2307
2044-02-22 18:01 | -2311.51 | 5.448 | 76.345 | 74.6386 | -677.4367
2044-02-23 19:01 | -2771.95 | 6.5195 | 76.2976 | 74.6386 | -812.3784
2044-02-24 20:01 | -3352.82 | 6.5195 | 76.0178 | 74.6386 | -982.6145
2044-02-25 21:01 | -4405.59 | 6.5195 | 75.5385 | 74.6386 | -1291.151
2044-02-26 22:01 | -4828.15 | 6.5195 | 75.234 | 74.6386 | -1414.9911
2044-02-27 23:01 | -5676.63 | 6.5195 | 74.8098 | 74.6386 | -1663.656
2044-02-29 00:01 | -6247.41 | 6.5195 | 74.4562 | 74.6386 | -1830.9351
2044-03-01 01:01 | -6255.24 | 6.5195 | 74.3054 | 74.6386 | -1833.2299
2044-03-02 02:01 | -6495.96 | 6.5195 | 74.1136 | 74.6386 | -1903.7779
2044-03-03 03:01 | -6710.76 | 6.5195 | 73.9363 | 74.6386 | -1966.7296
2044-03-04 04:01 | -6574.53 | 6.5195 | 73.8826 | 74.6386 | -1926.8045
2044-03-05 05:01 | -6486.42 | 6.5195 | 73.8472 | 74.6386 | -1900.982
2044-03-06 06:01 | -6141.86 | 6.5195 | 73.9168 | 74.6386 | -1800.0015
2044-03-07 07:01 | -6168.13 | 6.5195 | 73.8744 | 74.6386 | -1807.7005
2044-03-08 08:01 | -5839.31 | 6.5195 | 73.9473 | 74.6386 | -1711.3328
2044-03-09 09:01 | -6106.85 | 6.5195 | 73.8264 | 74.6386 | -1789.7411
2044-03-10 10:01 | -5787.35 | 6.5195 | 73.8827 | 74.6386 | -1696.1049
2044-03-11 11:01 | -5074.07 | 6.5195 | 74.1122 | 74.6386 | -1487.0631
2044-03-12 12:01 | -4760.49 | 6.5195 | 74.2402 | 74.6386 | -1395.1619
2044-03-13 13:01 | -4089.66 | 6.5195 | 74.4968 | 74.6386 | -1198.561
2044-03-14 14:01 | -3509.91 | 6.5195 | 74.7437 | 74.6386 | -1028.6531
2044-03-15 15:01 | -3652.29 | 6.5195 | 74.7499 | 74.6386 | -1070.3805
2044-03-16 16:01 | -2769.45 | 6.5195 | 75.0797 | 74.6386 | -811.6457
2044-03-17 17:01 | -2803 | 6.5195 | 75.1307 | 74.6386 | -821.4782
2044-03-18 18:01 | -2758.55 | 6.5195 | 75.1783 | 74.6386 | -808.4512
2044-03-19 19:01 | -3286.36 | 6.5195 | 75.0024 | 74.6386 | -963.137
2044-03-20 20:01 | -3511.33 | 6.5195 | 74.8907 | 74.6386 | -1029.0692
2044-03-21 21:01 | -4424.82 | 6.5195 | 74.5373 | 74.6386 | -1296.7867
2044-03-22 22:01 | -4731.83 | 6.5195 | 74.3406 | 74.6386 | -1386.7625
2044-03-23 23:01 | -5635.37 | 6.5195 | 73.9443 | 74.6386 | -1651.5639
2044-03-25 00:01 | -5671.98 | 6.5195 | 73.8225 | 74.6386 | -1662.2932
2044-03-26 01:01 | -5892.65 | 6.5195 | 73.6683 | 74.6386 | -1726.9652
2044-03-27 02:01 | -5852.3 | 6.5195 | 73.6112 | 74.6386 | -1715.1398
2044-03-28 03:01 | -5575.41 | 6.5195 | 73.6646 | 74.6386 | -1633.9914
2044-03-29 04:01 | -5240.91 | 6.5195 | 73.7613 | 74.6386 | -1535.9591
2044-03-30 05:01 | -4675.53 | 6.5195 | 73.9692 | 74.6386 | -1370.2626
2044-03-31 06:01 | -4182.78 | 6.5195 | 74.1762 | 74.6386 | -1225.8518
2044-04-01 07:01 | -4033.56 | 6.5195 | 74.2775 | 74.6386 | -1182.1197
2044-04-02 08:01 | -3963.08 | 6.5195 | 74.3317 | 74.6386 | -1161.4641
2044-04-03 09:01 | -4126.8 | 6.5195 | 74.2951 | 74.6386 | -1209.4457
2044-04-04 10:01 | -3717.44 | 6.5195 | 74.4426 | 74.6386 | -1089.4741
2044-04-05 11:01 | -3394.82 | 6.5195 | 74.5872 | 74.6386 | -994.9235
2044-04-06 12:01 | -2818.65 | 6.5195 | 74.8302 | 74.6386 | -826.0648
2044-04-07 13:01 | -2364.06 | 5.6208 | 74.9137 | 74.6386 | -692.8376
2044-04-08 14:01 | -2234.86 | 5.38 | 74.9886 | 74.6386 | -654.9728
2044-04-09 15:01 | -1940.8 | 4.699 | 75.0416 | 74.6386 | -568.7923
2044-04-10 16:01 | -812.906 | 2.0922 | 75.1453 | 74.6386 | -238.2392
2044-04-11 17:01 | -675.633 | 1.9718 | 75.3695 | 74.6386 | -198.0085
2044-04-12 18:01 | -493.063 | 1.5531 | 75.5044 | 74.6386 | -144.5025
2044-04-13 19:01 | -856.036 | 2.431 | 75.4832 | 74.6386 | -250.8794
2044-04-14 20:01 | -1205.85 | 3.1835 | 75.4463 | 74.6386 | -353.3997
2044-04-15 21:01 | -2114.65 | 5.2648 | 75.4037 | 74.6386 | -619.7427
2044-04-16 22:01 | -2342.18 | 5.6431 | 75.3172 | 74.6386 | -686.4252
2044-04-17 23:01 | -3180.91 | 6.5195 | 75.113 | 74.6386 | -932.2327
2044-04-19 00:01 | -3848.84 | 6.5195 | 74.7953 | 74.6386 | -1127.9837
2044-04-20 01:01 | -3944.3 | 6.5195 | 74.6684 | 74.6386 | -1155.9602
2044-04-21 02:01 | -3921.9 | 6.5195 | 74.6184 | 74.6386 | -1149.3954
2044-04-22 03:01 | -4200.87 | 6.5195 | 74.4857 | 74.6386 | -1231.1535
2044-04-23 04:01 | -4310.66 | 6.5195 | 74.3886 | 74.6386 | -1263.3297
2044-04-24 05:01 | -4406.88 | 6.5195 | 74.3043 | 74.6386 | -1291.529
2044-04-25 06:01 | -4343.5 | 6.5195 | 74.2841 | 74.6386 | -1272.9542
2044-04-26 07:01 | -2917.59 | 6.5195 | 74.7716 | 74.6386 | -855.0612
2044-04-27 08:01 | -2363.57 | 5.622 | 74.9101 | 74.6386 | -692.694
2044-04-28 09:01 | -1876.8 | 4.53 | 75.002 | 74.6386 | -550.0358
2044-04-29 10:01 | 0 | 1 | 76.0514 | 74.6386 | 0
2044-04-30 11:01 | 2252.46 | 1 | 75.1519 | 74.6386 | 660.1309
2044-05-01 12:01 | 3533.42 | 1.1886 | 83.5731 | 74.6386 | 1035.5432
2044-05-02 13:01 | 3017.26 | 1 | 86.3015 | 74.6386 | 884.2716
2044-05-03 14:01 | 2987.98 | 1 | 75.4717 | 74.6386 | 875.6905
2044-05-04 15:01 | 3067.98 | 1 | 75.5486 | 74.6386 | 899.1362
2044-05-05 16:01 | 3105.7 | 1 | 87.2022 | 74.6386 | 910.1908
2044-05-06 17:01 | 3930.13 | 1.2436 | 84.6802 | 74.6386 | 1151.8074
2044-05-07 18:01 | 3144.42 | 1 | 89.4964 | 74.6386 | 921.5385
2044-05-08 19:01 | 3194.86 | 1 | 75.8166 | 74.6386 | 936.321
2044-05-09 20:01 | 0 | 0 | 77.4094 | 74.6386 | 0
2044-05-10 21:01 | -288.426 | 1.1488 | 76.6344 | 74.6386 | -84.5293
2044-05-11 22:01 | -542.991 | 1.7158 | 76.3679 | 74.6386 | -159.135
2044-05-12 23:01 | -770.269 | 2.202 | 76.2108 | 74.6386 | -225.7436
2044-05-14 00:01 | -2085.79 | 5.2362 | 76.0195 | 74.6386 | -611.2847
2044-05-15 01:01 | -2435.18 | 5.8336 | 75.8132 | 74.6386 | -713.6808
2044-05-16 02:01 | -2619.36 | 6.2276 | 75.7048 | 74.6386 | -767.6586
2044-05-17 03:01 | -2746.29 | 6.5017 | 75.6258 | 74.6386 | -804.8581
2044-05-18 04:01 | -2895.3 | 6.5195 | 75.5056 | 74.6386 | -848.5287
2044-05-19 05:01 | -3190.86 | 6.5195 | 75.3228 | 74.6386 | -935.1488
2044-05-20 06:01 | -3340.08 | 6.5195 | 75.1979 | 74.6386 | -978.8808
2044-05-21 07:01 | -2293.93 | 5.4384 | 75.3412 | 74.6386 | -672.2845
2044-05-22 08:01 | -408.642 | 1.0835 | 75.4853 | 74.6386 | -119.7611
2044-05-23 09:01 | -541.753 | 1.7278 | 75.7895 | 74.6386 | -158.7721
2044-05-24 10:01 | 13.3286 | 1 | 76.5861 | 74.6386 | 3.9062
2044-05-25 11:01 | 2855.11 | 1.4148 | 81.4412 | 74.6386 | 836.7501
2044-05-26 12:01 | 3816.96 | 1.425 | 83.2723 | 74.6386 | 1118.6406
2044-05-27 13:01 | 5728.74 | 1.9959 | 83.9581 | 74.6386 | 1678.928
2044-05-28 14:01 | 6364.04 | 2.1309 | 84.505 | 74.6386 | 1865.116
2044-05-29 15:01 | 5810.14 | 1.8982 | 84.9242 | 74.6386 | 1702.7839
2044-05-30 16:01 | 5824.58 | 1.84 | 85.3084 | 74.6386 | 1707.0159
2044-05-31 17:01 | 6124.58 | 1.9909 | 85.2038 | 74.6386 | 1794.9372
2044-06-01 18:01 | 4334.45 | 1.3538 | 85.6332 | 74.6386 | 1270.3019
2044-06-02 19:01 | 3115.1 | 1 | 85.9283 | 74.6386 | 912.9457
2044-06-03 20:01 | 3037.78 | 1 | 76.454 | 74.6386 | 890.2854
2044-06-04 21:01 | 3121.22 | 1 | 76.4003 | 74.6386 | 914.7393
2044-06-05 22:01 | 3019.26 | 1 | 76.4652 | 74.6386 | 884.8578
2044-06-06 23:01 | 98.6138 | 1 | 77.8641 | 74.6386 | 28.9009
2044-06-08 00:01 | -668.571 | 2.0659 | 76.936 | 74.6386 | -195.9388
2044-06-09 01:01 | -1124.1 | 2.9819 | 76.6415 | 74.6386 | -329.4412
2044-06-10 02:01 | -1466.6 | 3.7108 | 76.4736 | 74.6386 | -429.818
2044-06-11 03:01 | -1571.27 | 3.903 | 76.338 | 74.6386 | -460.4938
2044-06-12 04:01 | -1642.21 | 4.0579 | 76.2282 | 74.6386 | -481.2842
2044-06-13 05:01 | -1264.39 | 3.1681 | 76.1772 | 74.6386 | -370.5561
2044-06-14 06:01 | -642.239 | 1.793 | 76.2642 | 74.6386 | -188.2217
2044-06-15 07:01 | -469.177 | 1.4975 | 76.4044 | 74.6386 | -137.5022
2044-06-16 08:01 | 21.6229 | 1 | 77.1533 | 74.6386 | 6.337
2044-06-17 09:01 | 2551.44 | 1.3023 | 81.8412 | 74.6386 | 747.7533
2044-06-18 10:01 | 4908.59 | 1.8851 | 83.5668 | 74.6386 | 1438.5657
2044-06-19 11:01 | 5577.44 | 1.9829 | 84.3532 | 74.6386 | 1634.5863
2044-06-20 12:01 | 9028.5 | 3.248 | 84.4866 | 74.6386 | 2645.9922
2044-06-21 13:01 | 8781.75 | 2.9689 | 85.313 | 74.6386 | 2573.6769
2044-06-22 14:01 | 7789.37 | 2.4991 | 85.9462 | 74.6386 | 2282.839
2044-06-23 15:01 | 9020.66 | 2.9691 | 85.8535 | 74.6386 | 2643.6945
2044-06-24 16:01 | 9734.38 | 3.1786 | 86.1051 | 74.6386 | 2852.8652
2044-06-25 17:01 | 7898.86 | 2.5405 | 86.4311 | 74.6386 | 2314.9274
2044-06-26 18:01 | 6997.58 | 2.2109 | 86.553 | 74.6386 | 2050.7883
2044-06-27 19:01 | 5535.72 | 1.7252 | 86.6291 | 74.6386 | 1622.3594
2044-06-28 20:01 | 4246.92 | 1.3714 | 86.3058 | 74.6386 | 1244.6494
2044-06-29 21:01 | 3031.89 | 1 | 77.3918 | 74.6386 | 888.5592
2044-06-30 22:01 | 2963.02 | 1 | 77.256 | 74.6386 | 868.3754
2044-07-01 23:01 | -591.873 | 1.8903 | 77.8623 | 74.6386 | -173.4609
2044-07-03 00:01 | -1219.8 | 3.1907 | 77.3662 | 74.6386 | -357.4881
2044-07-04 01:01 | -1701.62 | 4.2133 | 77.0714 | 74.6386 | -498.6956
2044-07-05 02:01 | -2277.22 | 5.4784 | 76.8751 | 74.6386 | -667.3873
2044-07-06 03:01 | -2395.61 | 5.6664 | 76.6813 | 74.6386 | -702.084
2044-07-07 04:01 | -2598.98 | 6.1373 | 76.5176 | 74.6386 | -761.6858
2044-07-08 05:01 | -2493.95 | 5.8614 | 76.4054 | 74.6386 | -730.9046
2044-07-09 06:01 | -2338.9 | 5.5251 | 76.3308 | 74.6386 | -685.4639
2044-07-10 07:01 | -1496.24 | 3.5875 | 76.2905 | 74.6386 | -438.5047
2044-07-11 08:01 | -495.813 | 1.419 | 76.462 | 74.6386 | -145.3084
2044-07-12 09:01 | -230.105 | 0.9723 | 76.7881 | 74.6386 | -67.4371
2044-07-13 10:01 | 186.924 | 1 | 77.2829 | 74.6386 | 54.782
2044-07-14 11:01 | 2556.11 | 1 | 76.1801 | 74.6386 | 749.1219
2044-07-15 12:01 | 2982.46 | 1 | 89.0341 | 74.6386 | 874.0727
2044-07-16 13:01 | 3049.96 | 1 | 76.2617 | 74.6386 | 893.855
2044-07-17 14:01 | 3289.94 | 1.0327 | 85.3544 | 74.6386 | 964.1862
2044-07-18 15:01 | 4307.53 | 1.3766 | 85.2803 | 74.6386 | 1262.4124
2044-07-19 16:01 | 3103.74 | 1 | 87.0876 | 74.6386 | 909.6164
2044-07-20 17:01 | 4517.36 | 1.4522 | 85.3491 | 74.6386 | 1323.9075
2044-07-21 18:01 | 3066.07 | 1 | 86.4578 | 74.6386 | 898.5764
2044-07-22 19:01 | 3051.92 | 1 | 76.6007 | 74.6386 | 894.4295
2044-07-23 20:01 | 2955.46 | 1 | 76.6394 | 74.6386 | 866.1598
2044-07-24 21:01 | 0 | 0 | 78.0681 | 74.6386 | 0
2044-07-25 22:01 | -162.34 | 0.83313 | 77.3999 | 74.6386 | -47.5772
2044-07-26 23:01 | -343.245 | 1.2713 | 77.0835 | 74.6386 | -100.5952
2044-07-28 00:01 | -1454.74 | 3.7978 | 76.7453 | 74.6386 | -426.3422
2044-07-29 01:01 | -1719.8 | 4.2325 | 76.5463 | 74.6386 | -504.0236
2044-07-30 02:01 | -1937.32 | 4.7112 | 76.4116 | 74.6386 | -567.7724
2044-07-31 03:01 | -1858.19 | 4.4932 | 76.3278 | 74.6386 | -544.5817
2044-08-01 04:01 | -1641.8 | 4.0079 | 76.2872 | 74.6386 | -481.1641
2044-08-02 05:01 | -1377.63 | 3.4321 | 76.2674 | 74.6386 | -403.7435
2044-08-03 06:01 | -992.543 | 2.5823 | 76.3016 | 74.6386 | -290.8856
2044-08-04 07:01 | -730.868 | 2.0411 | 76.3735 | 74.6386 | -214.1963
2044-08-05 08:01 | 2361.72 | 1 | 76.0916 | 74.6386 | 692.1518
2044-08-06 09:01 | 3508.88 | 1.1128 | 84.9427 | 74.6386 | 1028.3512
2044-08-07 10:01 | 6332.38 | 2.021 | 85.0975 | 74.6386 | 1855.8374
2044-08-08 11:01 | 7643.06 | 2.5589 | 85.0719 | 74.6386 | 2239.9598
2044-08-09 12:01 | 7297.45 | 2.4125 | 85.4646 | 74.6386 | 2138.6715
2044-08-10 13:01 | 9450.16 | 3.2316 | 85.4063 | 74.6386 | 2769.5685
2044-08-11 14:01 | 10852.7 | 3.6307 | 85.8519 | 74.6386 | 3180.6124
2044-08-12 15:01 | 10940.5 | 3.5701 | 86.3474 | 74.6386 | 3206.344
2044-08-13 16:01 | 10418.8 | 3.3895 | 86.5738 | 74.6386 | 3053.4489
2044-08-14 17:01 | 8942.96 | 2.8119 | 86.9416 | 74.6386 | 2620.9229
2044-08-15 18:01 | 7919.47 | 2.4499 | 87.0922 | 74.6386 | 2320.9675
2044-08-16 19:01 | 6895.93 | 2.0669 | 87.318 | 74.6386 | 2020.9976
2044-08-17 20:01 | 5829.87 | 1.702 | 87.4597 | 74.6386 | 1708.5662
2044-08-18 21:01 | 3177.32 | 1.003 | 86.7576 | 74.6386 | 931.1806
2044-08-19 22:01 | 3147.13 | 1 | 91.2579 | 74.6386 | 922.3328
2044-08-20 23:01 | 2833.54 | 1 | 77.5116 | 74.6386 | 830.4286
2044-08-22 00:01 | 169.969 | 1 | 78.7168 | 74.6386 | 49.813
2044-08-23 01:01 | 58.4256 | 1 | 78.4966 | 74.6386 | 17.1229
2044-08-24 02:01 | -117.93 | 0.77714 | 77.979 | 74.6386 | -34.5619
2044-08-25 03:01 | -43.2454 | 0.58748 | 78.2783 | 74.6386 | -12.674
2044-08-26 04:01 | 35.9589 | 1 | 78.1152 | 74.6386 | 10.5385
2044-08-27 05:01 | 1853.91 | 1 | 77.1624 | 74.6386 | 543.3274
2044-08-28 06:01 | 2711.36 | 1 | 76.8467 | 74.6386 | 794.6212
2044-08-29 07:01 | 2978.35 | 1 | 76.8271 | 74.6386 | 872.8682
2044-08-30 08:01 | 3107.31 | 1 | 76.8276 | 74.6386 | 910.6627
2044-08-31 09:01 | 1184.26 | 1 | 77.8159 | 74.6386 | 347.0723
2044-09-01 10:01 | 3259.3 | 1 | 76.7062 | 74.6386 | 955.2065
2044-09-02 11:01 | 3235.24 | 1 | 76.7949 | 74.6386 | 948.1552
2044-09-03 12:01 | 7325 | 2.5326 | 85.2595 | 74.6386 | 2146.7456
2044-09-04 13:01 | 8115.63 | 2.7458 | 85.7113 | 74.6386 | 2378.4564
2044-09-05 14:01 | 8361.78 | 2.7249 | 86.2164 | 74.6386 | 2450.5958
2044-09-06 15:01 | 9374.04 | 3.1056 | 86.2727 | 74.6386 | 2747.2599
2044-09-07 16:01 | 10115.1 | 3.3075 | 86.5734 | 74.6386 | 2964.4432
2044-09-08 17:01 | 8683.83 | 2.6853 | 87.2065 | 74.6386 | 2544.9793
2044-09-09 18:01 | 7901.66 | 2.4088 | 87.3329 | 74.6386 | 2315.748
2044-09-10 19:01 | 6524.59 | 1.9567 | 87.4423 | 74.6386 | 1912.1686
2044-09-11 20:01 | 5627.18 | 1.7115 | 87.2609 | 74.6386 | 1649.1637
2044-09-12 21:01 | 3244.52 | 1.0206 | 86.937 | 74.6386 | 950.8749
2044-09-13 22:01 | 2998.94 | 1 | 91.3938 | 74.6386 | 878.9026
2044-09-14 23:01 | 0 | 0 | 79.0836 | 74.6386 | 0
2044-09-16 00:01 | 37.9087 | 1 | 78.7664 | 74.6386 | 11.1099
2044-09-17 01:01 | -150.362 | 0.84905 | 78.1819 | 74.6386 | -44.0668
2044-09-18 02:01 | -226.567 | 0.99623 | 77.9325 | 74.6386 | -66.4002
2044-09-19 03:01 | -226.419 | 0.98545 | 77.82 | 74.6386 | -66.3569
2044-09-20 04:01 | -33.8932 | 0.55011 | 78.3055 | 74.6386 | -9.9331
2044-09-21 05:01 | 897.715 | 1 | 77.7814 | 74.6386 | 263.0943
2044-09-22 06:01 | 1829.99 | 1 | 77.3499 | 74.6386 | 536.3171
2044-09-23 07:01 | 2642.27 | 1 | 77.0235 | 74.6386 | 774.3729
2044-09-24 08:01 | 2929.05 | 1 | 76.9659 | 74.6386 | 858.4198
2044-09-25 09:01 | 2913.61 | 1 | 77.0492 | 74.6386 | 853.8948
2044-09-26 10:01 | 3237.13 | 1 | 88.1676 | 74.6386 | 948.7092
2044-09-27 11:01 | 4595.45 | 1.4004 | 86.3089 | 74.6386 | 1346.7934
2044-09-28 12:01 | 8488.49 | 2.9668 | 85.4407 | 74.6386 | 2487.7308
2044-09-29 13:01 | 9962.03 | 3.4393 | 85.8806 | 74.6386 | 2919.5828
2044-09-30 14:01 | 10244.5 | 3.4593 | 86.3475 | 74.6386 | 3002.3666
2044-10-01 15:01 | 8381.58 | 2.6732 | 86.9689 | 74.6386 | 2456.3986
2044-10-02 16:01 | 9612.63 | 3.0879 | 86.9387 | 74.6386 | 2817.1838
2044-10-03 17:01 | 8626.14 | 2.6866 | 87.3265 | 74.6386 | 2528.0721
2044-10-04 18:01 | 7806.37 | 2.4239 | 87.3775 | 74.6386 | 2287.8212
2044-10-05 19:01 | 6865.78 | 2.0511 | 87.6351 | 74.6386 | 2012.1615
2044-10-06 20:01 | 5719.46 | 1.7605 | 87.3332 | 74.6386 | 1676.2083
2044-10-07 21:01 | 3868.3 | 1.1841 | 87.3041 | 74.6386 | 1133.6868
2044-10-08 22:01 | 3069.1 | 1 | 89.1967 | 74.6386 | 899.4644
2044-10-09 23:01 | 3034.35 | 1 | 77.7961 | 74.6386 | 889.2802
2044-10-11 00:01 | 0 | 0 | 79.1731 | 74.6386 | 0
2044-10-12 01:01 | -153.864 | 0.8587 | 78.4479 | 74.6386 | -45.0931
2044-10-13 02:01 | -332.122 | 1.2326 | 78.0317 | 74.6386 | -97.3353
2044-10-14 03:01 | -443.205 | 1.4585 | 77.8324 | 74.6386 | -129.8906
2044-10-15 04:01 | -606.331 | 1.8152 | 77.645 | 74.6386 | -177.6981
2044-10-16 05:01 | -647.744 | 1.8858 | 77.5015 | 74.6386 | -189.835
2044-10-17 06:01 | -602.875 | 1.7795 | 77.4345 | 74.6386 | -176.6852
2044-10-18 07:01 | 2335.84 | 1 | 77.0431 | 74.6386 | 684.5671
2044-10-19 08:01 | 3659.33 | 1.6612 | 83.5536 | 74.6386 | 1072.4438
2044-10-20 09:01 | 4580.93 | 1.5865 | 85.3529 | 74.6386 | 1342.5381
2044-10-21 10:01 | 6819.21 | 2.4151 | 85.3585 | 74.6386 | 1998.5132
2044-10-22 11:01 | 7727.84 | 2.6353 | 85.8847 | 74.6386 | 2264.8063
2044-10-23 12:01 | 9666.88 | 3.2897 | 86.1467 | 74.6386 | 2833.0829
2044-10-24 13:01 | 9366.17 | 3.1452 | 86.5221 | 74.6386 | 2744.9535
2044-10-25 14:01 | 9695.03 | 3.1669 | 86.8826 | 74.6386 | 2841.3328
2044-10-26 15:01 | 9629.26 | 3.0871 | 87.1722 | 74.6386 | 2822.0575
2044-10-27 16:01 | 8835.85 | 2.8069 | 87.3519 | 74.6386 | 2589.532
2044-10-28 17:01 | 9445.82 | 3.0891 | 87.1792 | 74.6386 | 2768.2966
2044-10-29 18:01 | 7899.58 | 2.3726 | 87.9164 | 74.6386 | 2315.1384
2044-10-30 19:01 | 6532.58 | 1.9737 | 87.8326 | 74.6386 | 1914.5102
2044-10-31 20:01 | 5293.99 | 1.5949 | 87.7456 | 74.6386 | 1551.5153
2044-11-01 21:01 | 4292.23 | 1.3525 | 87.2773 | 74.6386 | 1257.9284
2044-11-02 22:01 | 3595.96 | 1.1374 | 87.1144 | 74.6386 | 1053.8718
2044-11-03 23:01 | 3080.07 | 1 | 87.464 | 74.6386 | 902.6794
2044-11-05 00:01 | 0 | 0 | 79.3769 | 74.6386 | 0
2044-11-06 01:01 | -134.01 | 0.80877 | 78.6797 | 74.6386 | -39.2745
2044-11-07 02:01 | -272.44 | 1.0989 | 78.2917 | 74.6386 | -79.8443
2044-11-08 03:01 | -279.967 | 1.0955 | 78.1467 | 74.6386 | -82.0502
2044-11-09 04:01 | -267.707 | 1.0691 | 78.0523 | 74.6386 | -78.4572
2044-11-10 05:01 | -200.291 | 0.91931 | 78.0278 | 74.6386 | -58.6995
2044-11-11 06:01 | -157.743 | 0.8346 | 78.0461 | 74.6386 | -46.2299
2044-11-12 07:01 | 1764.1 | 1 | 77.5917 | 74.6386 | 517.0067
2044-11-13 08:01 | 2724.47 | 1 | 85.2181 | 74.6386 | 798.4633
2044-11-14 09:01 | 3001.87 | 1 | 87.9132 | 74.6386 | 879.7613
2044-11-15 10:01 | 5189.21 | 1.7061 | 85.8919 | 74.6386 | 1520.8073
2044-11-16 11:01 | 5811.87 | 1.9902 | 85.7961 | 74.6386 | 1703.291
2044-11-17 12:01 | 6684.91 | 2.2746 | 86.0077 | 74.6386 | 1959.1537
2044-11-18 13:01 | 7620.52 | 2.5185 | 86.3588 | 74.6386 | 2233.354
2044-11-19 14:01 | 6913.22 | 2.176 | 86.8796 | 74.6386 | 2026.0648
2044-11-20 15:01 | 8469.36 | 2.7563 | 86.6955 | 74.6386 | 2482.1244
2044-11-21 16:01 | 7398.56 | 2.4904 | 86.6144 | 74.6386 | 2168.3039
2044-11-22 17:01 | 8780.01 | 2.8515 | 86.9055 | 74.6386 | 2573.1669
2044-11-23 18:01 | 7860.95 | 2.4137 | 87.4661 | 74.6386 | 2303.817
2044-11-24 19:01 | 6750.49 | 2.0841 | 87.4549 | 74.6386 | 1978.3733
2044-11-25 20:01 | 5703.09 | 1.7086 | 87.6491 | 74.6386 | 1671.4107
2044-11-26 21:01 | 5102.44 | 1.5625 | 87.3984 | 74.6386 | 1495.3776
2044-11-27 22:01 | 4484.94 | 1.3777 | 87.3078 | 74.6386 | 1314.4062
2044-11-28 23:01 | 3825.32 | 1.2241 | 86.9054 | 74.6386 | 1121.0906
2044-11-30 00:01 | 3021.15 | 1 | 77.9653 | 74.6386 | 885.4117
2044-12-01 01:01 | 2994.97 | 1 | 77.8708 | 74.6386 | 877.7391
2044-12-02 02:01 | 35.5867 | 1 | 79.2458 | 74.6386 | 10.4294
2044-12-03 03:01 | 967.171 | 1 | 78.5309 | 74.6386 | 283.4498
2044-12-04 04:01 | 1705.56 | 1 | 78.0887 | 74.6386 | 499.8503
2044-12-05 05:01 | 1852.26 | 1 | 78.0138 | 74.6386 | 542.8438
2044-12-06 06:01 | 2670.13 | 1 | 77.5998 | 74.6386 | 782.5379
2044-12-07 07:01 | 3000 | 1 | 77.4607 | 74.6386 | 879.2132
2044-12-08 08:01 | 3158.81 | 1 | 77.438 | 74.6386 | 925.7558
2044-12-09 09:01 | 3635.21 | 1.1236 | 86.6577 | 74.6386 | 1065.3749
2044-12-10 10:01 | 5050.01 | 1.5782 | 86.5984 | 74.6386 | 1480.0118
2044-12-11 11:01 | 6439.55 | 2.2049 | 86.0618 | 74.6386 | 1887.2458
2044-12-12 12:01 | 9913.89 | 3.542 | 85.9345 | 74.6386 | 2905.4744
2044-12-13 13:01 | 10883.9 | 3.7272 | 86.5667 | 74.6386 | 3189.7562
2044-12-14 14:01 | 10624.3 | 3.53 | 87.0795 | 74.6386 | 3113.675
2044-12-15 15:01 | 9595.95 | 3.0837 | 87.4882 | 74.6386 | 2812.2953
2044-12-16 16:01 | 11301.7 | 3.6367 | 87.5378 | 74.6386 | 3312.2013
2044-12-17 17:01 | 9418.82 | 2.9985 | 87.8224 | 74.6386 | 2760.3837
2044-12-18 18:01 | 9007 | 2.7506 | 88.1234 | 74.6386 | 2639.6911
2044-12-19 19:01 | 7711.58 | 2.3272 | 88.1903 | 74.6386 | 2260.041
2044-12-20 20:01 | 6616.43 | 2.0143 | 88.0556 | 74.6386 | 1939.0842
2044-12-21 21:01 | 4506.13 | 1.3517 | 88.0869 | 74.6386 | 1320.6163
2044-12-22 22:01 | 3138.06 | 1.0182 | 87.2793 | 74.6386 | 919.6746
2044-12-23 23:01 | 3095.28 | 1 | 78.2869 | 74.6386 | 907.137
[5 empty] | 15166239.8013 | 1731.3059

## Knoxville (2)
| Property | Soil | [6 empty] | Property | Soil
| Thermal conductivity [W/m K] | 1.72 |  | W/M-K | 0.57779 | BTU/HR-FT-R |  |  | Thermal conductivity [Btu/Hr-ft-R] | 0.99379
| Specific heat [J/kg K] | 1900
| Density [kg/m3] | 1300
| Volumeric specific heat [MJ/K-M3] | 2.47
| Thermal diffusivity [m2/hr] | 0.0025069 |  | m2/hr | 10.7639 | ft2/hr |  |  | Thermal diffusivity [ft2/hr] | 0.026984
VBGHE design and performance
| Borehole number | 2
| Borehole depth | 200 | ft | 61 | m
| Annual Max. LFT | 95.6 | F
| Annual Min. LFT | 39.2 | F
Time | Thermal load | Fluid flow | Outlet temperature | Far field ground temperature | Load |  |  |  | 31536000
| Btu/hr | GPM | F | F | W
2020-01-01 | -7074.78 | 6.108 | 54.5272 | 59.8258 | -2073.4133 |  | 0 | 0 | 31536000 | 63072000 | 94608000
2020-01-02 01:00 | -6997.43 | 6.108 | 53.6128 | 59.8258 | -2050.7443 |  | 1 | 3600 | 31539600 | 63075600 | 94611600
2020-01-03 02:00 | -7141.19 | 6.108 | 52.948 | 59.8258 | -2092.8762 |  | 2 | 7200 | 31543200 | 63079200 | 94615200
2020-01-04 03:00 | -7239.66 | 6.108 | 52.5369 | 59.8258 | -2121.7349 |  | 3 | 10800 | 31546800 | 63082800 | 94618800
2020-01-05 04:00 | -7197.76 | 6.108 | 52.2231 | 59.8258 | -2109.4552 |  | 4 | 14400 | 31550400 | 63086400 | 94622400
2020-01-06 05:00 | -7129.36 | 6.108 | 51.9458 | 59.8258 | -2089.4092 |  | 5 | 18000 | 31554000 | 63090000 | 94626000
2020-01-07 06:00 | -7038.92 | 6.108 | 51.8572 | 59.8258 | -2062.9038 |  | 6 | 21600 | 31557600 | 63093600 | 94629600
2020-01-08 07:00 | -5991.28 | 6.108 | 52.4921 | 59.8258 | -1755.8708 |  | 7 | 25200 | 31561200 | 63097200 | 94633200
2020-01-09 08:00 | -5374.99 | 6.108 | 52.944 | 59.8258 | -1575.2541 |  | 8 | 28800 | 31564800 | 63100800 | 94636800
2020-01-10 09:00 | -5798.15 | 6.108 | 52.6396 | 59.8258 | -1699.27 |  | 9 | 32400 | 31568400 | 63104400 | 94640400
2020-01-11 10:00 | -5405.92 | 6.108 | 52.8153 | 59.8258 | -1584.3188 |  | 10 | 36000 | 31572000 | 63108000 | 94644000
2020-01-12 11:00 | -4429.77 | 6.108 | 53.4848 | 59.8258 | -1298.2374 |  | 11 | 39600 | 31575600 | 63111600 | 94647600
2020-01-13 12:00 | -4147.5 | 6.108 | 53.8393 | 59.8258 | -1215.5123 |  | 12 | 43200 | 31579200 | 63115200 | 94651200
2020-01-14 13:00 | -3866.8 | 6.108 | 54.1366 | 59.8258 | -1133.2472 |  | 13 | 46800 | 31582800 | 63118800 | 94654800
2020-01-15 14:00 | -3257.75 | 6.108 | 54.6563 | 59.8258 | -954.7523 |  | 14 | 50400 | 31586400 | 63122400 | 94658400
2020-01-16 15:00 | -3501.43 | 6.108 | 54.6057 | 59.8258 | -1026.1678 |  | 15 | 54000 | 31590000 | 63126000 | 94662000
2020-01-17 16:00 | -3525.34 | 6.108 | 54.6321 | 59.8258 | -1033.1752 |  | 16 | 57600 | 31593600 | 63129600 | 94665600
2020-01-18 17:00 | -2763.62 | 6.108 | 55.2137 | 59.8258 | -809.9371 |  | 17 | 61200 | 31597200 | 63133200 | 94669200
2020-01-19 18:00 | -3731.99 | 6.108 | 54.6064 | 59.8258 | -1093.7383 |  | 18 | 64800 | 31600800 | 63136800 | 94672800
2020-01-20 19:00 | -4246.19 | 6.108 | 54.1445 | 59.8258 | -1244.4354 |  | 19 | 68400 | 31604400 | 63140400 | 94676400
2020-01-21 20:00 | -4724.24 | 6.108 | 53.6472 | 59.8258 | -1384.5381 |  | 20 | 72000 | 31608000 | 63144000 | 94680000
2020-01-22 21:00 | -4962.11 | 6.108 | 53.3374 | 59.8258 | -1454.2509 |  | 21 | 75600 | 31611600 | 63147600 | 94683600
2020-01-23 22:00 | -5370.61 | 6.108 | 52.9082 | 59.8258 | -1573.9704 |  | 22 | 79200 | 31615200 | 63151200 | 94687200
2020-01-24 23:00 | -5656.02 | 6.108 | 52.5165 | 59.8258 | -1657.6158 |  | 23 | 82800 | 31618800 | 63154800 | 94690800
2020-01-26 | -7030.53 | 6.108 | 51.3595 | 59.8258 | -2060.4449 |  | 24 | 86400 | 31622400 | 63158400 | 94694400
2020-01-27 01:00 | -7468.95 | 6.108 | 50.7525 | 59.8258 | -2188.9332 |  | 25 | 90000 | 31626000 | 63162000 | 94698000
2020-01-28 02:00 | -7720.58 | 6.108 | 50.3197 | 59.8258 | -2262.6786 |  | 26 | 93600 | 31629600 | 63165600 | 94701600
2020-01-29 03:00 | -7938.21 | 6.108 | 49.9594 | 59.8258 | -2326.4597 |  | 27 | 97200 | 31633200 | 63169200 | 94705200
2020-01-30 04:00 | -7841.1 | 6.108 | 49.8445 | 59.8258 | -2297.9996 |  | 28 | 100800 | 31636800 | 63172800 | 94708800
2020-01-31 05:00 | -7681.29 | 6.108 | 49.8091 | 59.8258 | -2251.1639 |  | 29 | 104400 | 31640400 | 63176400 | 94712400
2020-02-01 06:00 | -7239.94 | 6.108 | 50.0512 | 59.8258 | -2121.817 |  | 30 | 108000 | 31644000 | 63180000 | 94716000
2020-02-02 07:00 | -7146.47 | 6.108 | 50.0905 | 59.8258 | -2094.4236 |  | 31 | 111600 | 31647600 | 63183600 | 94719600
2020-02-03 08:00 | -6992.11 | 6.108 | 50.1648 | 59.8258 | -2049.1852 |  | 32 | 115200 | 31651200 | 63187200 | 94723200
2020-02-04 09:00 | -7485.33 | 6.108 | 49.7637 | 59.8258 | -2193.7337 |  | 33 | 118800 | 31654800 | 63190800 | 94726800
2020-02-05 10:00 | -7036.72 | 6.108 | 49.9892 | 59.8258 | -2062.2591 |  | 34 | 122400 | 31658400 | 63194400 | 94730400
2020-02-06 11:00 | -6442.11 | 6.108 | 50.4043 | 59.8258 | -1887.9961 |  | 35 | 126000 | 31662000 | 63198000 | 94734000
2020-02-07 12:00 | -5852.82 | 6.108 | 50.8925 | 59.8258 | -1715.2922 |  | 36 | 129600 | 31665600 | 63201600 | 94737600
2020-02-08 13:00 | -5095.48 | 6.108 | 51.5393 | 59.8258 | -1493.3378 |  | 37 | 133200 | 31669200 | 63205200 | 94741200
2020-02-09 14:00 | -4090.07 | 6.108 | 52.4176 | 59.8258 | -1198.6812 |  | 38 | 136800 | 31672800 | 63208800 | 94744800
2020-02-10 15:00 | -3570.9 | 6.108 | 53.0206 | 59.8258 | -1046.5275 |  | 39 | 140400 | 31676400 | 63212400 | 94748400
2020-02-11 16:00 | -3189.07 | 6.108 | 53.4965 | 59.8258 | -934.6242 |  | 40 | 144000 | 31680000 | 63216000 | 94752000
2020-02-12 17:00 | -3472.43 | 6.108 | 53.4422 | 59.8258 | -1017.6688 |  | 41 | 147600 | 31683600 | 63219600 | 94755600
2020-02-13 18:00 | -3607.62 | 6.108 | 53.4069 | 59.8258 | -1057.2891 |  | 42 | 151200 | 31687200 | 63223200 | 94759200
2020-02-14 19:00 | -4081.88 | 6.108 | 53.0867 | 59.8258 | -1196.2809 |  | 43 | 154800 | 31690800 | 63226800 | 94762800
2020-02-15 20:00 | -4372.64 | 6.108 | 52.8341 | 59.8258 | -1281.4943 |  | 44 | 158400 | 31694400 | 63230400 | 94766400
2020-02-16 21:00 | -5257.86 | 6.108 | 52.1228 | 59.8258 | -1540.9267 |  | 45 | 162000 | 31698000 | 63234000 | 94770000
2020-02-17 22:00 | -5509.49 | 6.108 | 51.7857 | 59.8258 | -1614.6721 |  | 46 | 165600 | 31701600 | 63237600 | 94773600
2020-02-18 23:00 | -6154.98 | 6.108 | 51.181 | 59.8258 | -1803.8466 |  | 47 | 169200 | 31705200 | 63241200 | 94777200
2020-02-20 | -6307.31 | 6.108 | 50.9264 | 59.8258 | -1848.4901 |  | 48 | 172800 | 31708800 | 63244800 | 94780800
2020-02-21 01:00 | -6351.69 | 6.108 | 50.7826 | 59.8258 | -1861.4966 |  | 49 | 176400 | 31712400 | 63248400 | 94784400
2020-02-22 02:00 | -6415.77 | 6.108 | 50.6459 | 59.8258 | -1880.2766 |  | 50 | 180000 | 31716000 | 63252000 | 94788000
2020-02-23 03:00 | -6355.62 | 6.108 | 50.6173 | 59.8258 | -1862.6484 |  | 51 | 183600 | 31719600 | 63255600 | 94791600
2020-02-24 04:00 | -6108.47 | 6.108 | 50.7434 | 59.8258 | -1790.2158 |  | 52 | 187200 | 31723200 | 63259200 | 94795200
2020-02-25 05:00 | -5734.26 | 6.108 | 51.0147 | 59.8258 | -1680.5457 |  | 53 | 190800 | 31726800 | 63262800 | 94798800
2020-02-26 06:00 | -5115.71 | 6.108 | 51.5068 | 59.8258 | -1499.2666 |  | 54 | 194400 | 31730400 | 63266400 | 94802400
2020-02-27 07:00 | -4982.68 | 6.108 | 51.6927 | 59.8258 | -1460.2794 |  | 55 | 198000 | 31734000 | 63270000 | 94806000
2020-02-28 08:00 | -4946.92 | 6.108 | 51.7773 | 59.8258 | -1449.7991 |  | 56 | 201600 | 31737600 | 63273600 | 94809600
2020-02-29 09:00 | -5504.81 | 6.108 | 51.4052 | 59.8258 | -1613.3006 |  | 57 | 205200 | 31741200 | 63277200 | 94813200
2020-03-01 10:00 | -5418.65 | 6.108 | 51.426 | 59.8258 | -1588.0496 |  | 58 | 208800 | 31744800 | 63280800 | 94816800
2020-03-02 11:00 | -5285.65 | 6.108 | 51.5177 | 59.8258 | -1549.0711 |  | 59 | 212400 | 31748400 | 63284400 | 94820400
2020-03-03 12:00 | -5406.47 | 6.108 | 51.435 | 59.8258 | -1584.4799 |  | 60 | 216000 | 31752000 | 63288000 | 94824000
2020-03-04 13:00 | -5283.16 | 6.108 | 51.5004 | 59.8258 | -1548.3414 |  | 61 | 219600 | 31755600 | 63291600 | 94827600
2020-03-05 14:00 | -5491.4 | 6.108 | 51.329 | 59.8258 | -1609.3705 |  | 62 | 223200 | 31759200 | 63295200 | 94831200
2020-03-06 15:00 | -5655.93 | 6.108 | 51.1683 | 59.8258 | -1657.5895 |  | 63 | 226800 | 31762800 | 63298800 | 94834800
2020-03-07 16:00 | -4980.57 | 6.108 | 51.6161 | 59.8258 | -1459.661 |  | 64 | 230400 | 31766400 | 63302400 | 94838400
2020-03-08 17:00 | -4865.92 | 6.108 | 51.7453 | 59.8258 | -1426.0604 |  | 65 | 234000 | 31770000 | 63306000 | 94842000
2020-03-09 18:00 | -4770.49 | 6.108 | 51.8417 | 59.8258 | -1398.0926 |  | 66 | 237600 | 31773600 | 63309600 | 94845600
2020-03-10 19:00 | -5472.27 | 6.108 | 51.3231 | 59.8258 | -1603.764 |  | 67 | 241200 | 31777200 | 63313200 | 94849200
2020-03-11 20:00 | -6172.09 | 6.108 | 50.7066 | 59.8258 | -1808.861 |  | 68 | 244800 | 31780800 | 63316800 | 94852800
2020-03-12 21:00 | -7404.13 | 6.108 | 49.6468 | 59.8258 | -2169.9363 |  | 69 | 248400 | 31784400 | 63320400 | 94856400
2020-03-13 22:00 | -7703.75 | 6.108 | 49.1667 | 59.8258 | -2257.7463 |  | 70 | 252000 | 31788000 | 63324000 | 94860000
2020-03-14 23:00 | -8660.55 | 6.108 | 48.2479 | 59.8258 | -2538.1567 |  | 71 | 255600 | 31791600 | 63327600 | 94863600
2020-03-16 | -8843.29 | 6.108 | 47.8412 | 59.8258 | -2591.7125 |  | 72 | 259200 | 31795200 | 63331200 | 94867200
2020-03-17 01:00 | -8969.57 | 6.108 | 47.5347 | 59.8258 | -2628.7215 |  | 73 | 262800 | 31798800 | 63334800 | 94870800
2020-03-18 02:00 | -9219.86 | 6.108 | 47.1805 | 59.8258 | -2702.0742 |  | 74 | 266400 | 31802400 | 63338400 | 94874400
2020-03-19 03:00 | -9247.6 | 6.108 | 47.003 | 59.8258 | -2710.204 |  | 75 | 270000 | 31806000 | 63342000 | 94878000
2020-03-20 04:00 | -9387.22 | 6.108 | 46.754 | 59.8258 | -2751.1226 |  | 76 | 273600 | 31809600 | 63345600 | 94881600
2020-03-21 05:00 | -9369.36 | 6.108 | 46.6323 | 59.8258 | -2745.8884 |  | 77 | 277200 | 31813200 | 63349200 | 94885200
2020-03-22 06:00 | -9249.6 | 6.108 | 46.5973 | 59.8258 | -2710.7902 |  | 78 | 280800 | 31816800 | 63352800 | 94888800
2020-03-23 07:00 | -9294.83 | 6.108 | 46.4686 | 59.8258 | -2724.0458 |  | 79 | 284400 | 31820400 | 63356400 | 94892400
2020-03-24 08:00 | -8897.08 | 6.108 | 46.6722 | 59.8258 | -2607.4768 |  | 80 | 288000 | 31824000 | 63360000 | 94896000
2020-03-25 09:00 | -8152.91 | 6.108 | 47.2099 | 59.8258 | -2389.3821 |  | 81 | 291600 | 31827600 | 63363600 | 94899600
2020-03-26 10:00 | -6943.22 | 6.108 | 48.184 | 59.8258 | -2034.8569 |  | 82 | 295200 | 31831200 | 63367200 | 94903200
2020-03-27 11:00 | -5779.29 | 6.108 | 49.2415 | 59.8258 | -1693.7427 |  | 83 | 298800 | 31834800 | 63370800 | 94906800
2020-03-28 12:00 | -4823.28 | 6.108 | 50.2051 | 59.8258 | -1413.5638 |  | 84 | 302400 | 31838400 | 63374400 | 94910400
2020-03-29 13:00 | -4127.73 | 6.108 | 50.9949 | 59.8258 | -1209.7182 |  | 85 | 306000 | 31842000 | 63378000 | 94914000
2020-03-30 14:00 | -3729.6 | 6.108 | 51.5538 | 59.8258 | -1093.0379 |  | 86 | 309600 | 31845600 | 63381600 | 94917600
2020-03-31 15:00 | -3485.01 | 6.108 | 51.9619 | 59.8258 | -1021.3556 |  | 87 | 313200 | 31849200 | 63385200 | 94921200
2020-04-01 16:00 | -3601.76 | 6.108 | 52.0548 | 59.8258 | -1055.5717 |  | 88 | 316800 | 31852800 | 63388800 | 94924800
2020-04-02 17:00 | -4990.97 | 6.108 | 51.1227 | 59.8258 | -1462.7089 |  | 89 | 320400 | 31856400 | 63392400 | 94928400
2020-04-03 18:00 | -5828.5 | 6.108 | 50.3871 | 59.8258 | -1708.1647 |  | 90 | 324000 | 31860000 | 63396000 | 94932000
2020-04-04 19:00 | -6726.67 | 6.108 | 49.5641 | 59.8258 | -1971.3924 |  | 91 | 327600 | 31863600 | 63399600 | 94935600
2020-04-05 20:00 | -7558.53 | 6.108 | 48.7539 | 59.8258 | -2215.1865 |  | 92 | 331200 | 31867200 | 63403200 | 94939200
2020-04-06 21:00 | -8760.53 | 6.108 | 47.6264 | 59.8258 | -2567.4579 |  | 93 | 334800 | 31870800 | 63406800 | 94942800
2020-04-07 22:00 | -9309.37 | 6.108 | 46.8928 | 59.8258 | -2728.307 |  | 94 | 338400 | 31874400 | 63410400 | 94946400
2020-04-08 23:00 | -10565.5 | 6.108 | 45.6757 | 59.8258 | -3096.4424 |  | 95 | 342000 | 31878000 | 63414000 | 94950000
2020-04-10 | -11025.4 | 6.108 | 44.9749 | 59.8258 | -3231.2258 |  | 96 | 345600 | 31881600 | 63417600 | 94953600
2020-04-11 01:00 | -11340.6 | 6.108 | 44.4259 | 59.8258 | -3323.6018 |  | 97 | 349200 | 31885200 | 63421200 | 94957200
2020-04-12 02:00 | -11620.9 | 6.108 | 43.9462 | 59.8258 | -3405.7496 |  | 98 | 352800 | 31888800 | 63424800 | 94960800
2020-04-13 03:00 | -11771.3 | 6.108 | 43.5846 | 59.8258 | -3449.8275 |  | 99 | 356400 | 31892400 | 63428400 | 94964400
2020-04-14 04:00 | -11607.9 | 6.108 | 43.4803 | 59.8258 | -3401.9397 |  | 100 | 360000 | 31896000 | 63432000 | 94968000
2020-04-15 05:00 | -11617.4 | 6.108 | 43.3309 | 59.8258 | -3404.7238 |  | 101 | 363600 | 31899600 | 63435600 | 94971600
2020-04-16 06:00 | -11158.6 | 6.108 | 43.5463 | 59.8258 | -3270.2628 |  | 102 | 367200 | 31903200 | 63439200 | 94975200
2020-04-17 07:00 | -10866.5 | 6.108 | 43.7114 | 59.8258 | -3184.6568 |  | 103 | 370800 | 31906800 | 63442800 | 94978800
2020-04-18 08:00 | -10195.8 | 6.108 | 44.1884 | 59.8258 | -2988.094 |  | 104 | 374400 | 31910400 | 63446400 | 94982400
2020-04-19 09:00 | -10418.9 | 6.108 | 44.0676 | 59.8258 | -3053.4782 |  | 105 | 378000 | 31914000 | 63450000 | 94986000
2020-04-20 10:00 | -8734.92 | 6.108 | 45.2967 | 59.8258 | -2559.9524 |  | 106 | 381600 | 31917600 | 63453600 | 94989600
2020-04-21 11:00 | -7681.27 | 6.108 | 46.2822 | 59.8258 | -2251.158 |  | 107 | 385200 | 31921200 | 63457200 | 94993200
2020-04-22 12:00 | -7035.22 | 6.108 | 47.004 | 59.8258 | -2061.8195 |  | 108 | 388800 | 31924800 | 63460800 | 94996800
2020-04-23 13:00 | -6680.79 | 6.108 | 47.4679 | 59.8258 | -1957.9463 |  | 109 | 392400 | 31928400 | 63464400 | 95000400
2020-04-24 14:00 | -6226.67 | 6.108 | 47.9667 | 59.8258 | -1824.8568 |  | 110 | 396000 | 31932000 | 63468000 | 95004000
2020-04-25 15:00 | -6509.98 | 6.108 | 47.9375 | 59.8258 | -1907.8868 |  | 111 | 399600 | 31935600 | 63471600 | 95007600
2020-04-26 16:00 | -5393.98 | 6.108 | 48.84 | 59.8258 | -1580.8195 |  | 112 | 403200 | 31939200 | 63475200 | 95011200
2020-04-27 17:00 | -6037.3 | 6.108 | 48.5587 | 59.8258 | -1769.358 |  | 113 | 406800 | 31942800 | 63478800 | 95014800
2020-04-28 18:00 | -6550.52 | 6.108 | 48.2164 | 59.8258 | -1919.7679 |  | 114 | 410400 | 31946400 | 63482400 | 95018400
2020-04-29 19:00 | -7246.76 | 6.108 | 47.6607 | 59.8258 | -2123.8157 |  | 115 | 414000 | 31950000 | 63486000 | 95022000
2020-04-30 20:00 | -7787.2 | 6.108 | 47.1668 | 59.8258 | -2282.203 |  | 116 | 417600 | 31953600 | 63489600 | 95025600
2020-05-01 21:00 | -8871.28 | 6.108 | 46.267 | 59.8258 | -2599.9155 |  | 117 | 421200 | 31957200 | 63493200 | 95029200
2020-05-02 22:00 | -9327.63 | 6.108 | 45.7032 | 59.8258 | -2733.6585 |  | 118 | 424800 | 31960800 | 63496800 | 95032800
2020-05-03 23:00 | -10238 | 6.108 | 44.8295 | 59.8258 | -3000.4616 |  | 119 | 428400 | 31964400 | 63500400 | 95036400
2020-05-05 | -10857 | 6.108 | 44.1212 | 59.8258 | -3181.8726 |  | 120 | 432000 | 31968000 | 63504000 | 95040000
2020-05-06 01:00 | -11158.4 | 6.108 | 43.65 | 59.8258 | -3270.2042 |  | 121 | 435600 | 31971600 | 63507600 | 95043600
2020-05-07 02:00 | -11218.6 | 6.108 | 43.3968 | 59.8258 | -3287.8471 |  | 122 | 439200 | 31975200 | 63511200 | 95047200
2020-05-08 03:00 | -11416.3 | 6.108 | 43.1004 | 59.8258 | -3345.7873 |  | 123 | 442800 | 31978800 | 63514800 | 95050800
2020-05-09 04:00 | -11547.2 | 6.108 | 42.8376 | 59.8258 | -3384.1503 |  | 124 | 446400 | 31982400 | 63518400 | 95054400
2020-05-10 05:00 | -11733.8 | 6.108 | 42.5562 | 59.8258 | -3438.8373 |  | 125 | 450000 | 31986000 | 63522000 | 95058000
2020-05-11 06:00 | -11836.5 | 6.108 | 42.3431 | 59.8258 | -3468.9357 |  | 126 | 453600 | 31989600 | 63525600 | 95061600
2020-05-12 07:00 | -10872.4 | 6.108 | 42.9495 | 59.8258 | -3186.3859 |  | 127 | 457200 | 31993200 | 63529200 | 95065200
2020-05-13 08:00 | -9438.72 | 6.108 | 44.0608 | 59.8258 | -2766.2158 |  | 128 | 460800 | 31996800 | 63532800 | 95068800
2020-05-14 09:00 | -8773.37 | 6.108 | 44.7555 | 59.8258 | -2571.2209 |  | 129 | 464400 | 32000400 | 63536400 | 95072400
2020-05-15 10:00 | -7263.54 | 6.108 | 46.0538 | 59.8258 | -2128.7334 |  | 130 | 468000 | 32004000 | 63540000 | 95076000
2020-05-16 11:00 | -5493.84 | 6.108 | 47.6721 | 59.8258 | -1610.0856 |  | 131 | 471600 | 32007600 | 63543600 | 95079600
2020-05-17 12:00 | -4074.81 | 6.108 | 49.1606 | 59.8258 | -1194.2089 |  | 132 | 475200 | 32011200 | 63547200 | 95083200
2020-05-18 13:00 | -3282.77 | 6.108 | 50.1942 | 59.8258 | -962.0849 |  | 133 | 478800 | 32014800 | 63550800 | 95086800
2020-05-19 14:00 | -2791.85 | 6.108 | 50.9302 | 59.8258 | -818.2105 |  | 134 | 482400 | 32018400 | 63554400 | 95090400
2020-05-20 15:00 | -2555.17 | 6.108 | 51.4356 | 59.8258 | -748.8464 |  | 135 | 486000 | 32022000 | 63558000 | 95094000
2020-05-21 16:00 | -3104.05 | 6.108 | 51.2892 | 59.8258 | -909.7073 |  | 136 | 489600 | 32025600 | 63561600 | 95097600
2020-05-22 17:00 | -2709.06 | 6.108 | 51.7145 | 59.8258 | -793.9471 |  | 137 | 493200 | 32029200 | 63565200 | 95101200
2020-05-23 18:00 | -3880.67 | 6.108 | 51.0168 | 59.8258 | -1137.3121 |  | 138 | 496800 | 32032800 | 63568800 | 95104800
2020-05-24 19:00 | -4867.68 | 6.108 | 50.2701 | 59.8258 | -1426.5762 |  | 139 | 500400 | 32036400 | 63572400 | 95108400
2020-05-25 20:00 | -5710.72 | 6.108 | 49.527 | 59.8258 | -1673.6468 |  | 140 | 504000 | 32040000 | 63576000 | 95112000
2020-05-26 21:00 | -6481.21 | 6.108 | 48.8168 | 59.8258 | -1899.4551 |  | 141 | 507600 | 32043600 | 63579600 | 95115600
2020-05-27 22:00 | -6965.41 | 6.108 | 48.2976 | 59.8258 | -2041.3602 |  | 142 | 511200 | 32047200 | 63583200 | 95119200
2020-05-28 23:00 | -7440.76 | 6.108 | 47.7722 | 59.8258 | -2180.6715 |  | 143 | 514800 | 32050800 | 63586800 | 95122800
2020-05-30 | -9037.51 | 6.108 | 46.4081 | 59.8258 | -2648.6327 |  | 144 | 518400 | 32054400 | 63590400 | 95126400
2020-05-31 01:00 | -9372.32 | 6.108 | 45.8301 | 59.8258 | -2746.7559 |  | 145 | 522000 | 32058000 | 63594000 | 95130000
2020-06-01 02:00 | -9631.8 | 6.108 | 45.3881 | 59.8258 | -2822.8019 |  | 146 | 525600 | 32061600 | 63597600 | 95133600
2020-06-02 03:00 | -9751.55 | 6.108 | 45.1064 | 59.8258 | -2857.8972 |  | 147 | 529200 | 32065200 | 63601200 | 95137200
2020-06-03 04:00 | -9719.33 | 6.108 | 44.9668 | 59.8258 | -2848.4544 |  | 148 | 532800 | 32068800 | 63604800 | 95140800
2020-06-04 05:00 | -9745.35 | 6.108 | 44.811 | 59.8258 | -2856.0802 |  | 149 | 536400 | 32072400 | 63608400 | 95144400
2020-06-05 06:00 | -9623.76 | 6.108 | 44.8132 | 59.8258 | -2820.4456 |  | 150 | 540000 | 32076000 | 63612000 | 95148000
2020-06-06 07:00 | -8771.56 | 6.108 | 45.3957 | 59.8258 | -2570.6905 |  | 151 | 543600 | 32079600 | 63615600 | 95151600
2020-06-07 08:00 | -8179.48 | 6.108 | 45.9003 | 59.8258 | -2397.169 |  | 152 | 547200 | 32083200 | 63619200 | 95155200
2020-06-08 09:00 | -8258.02 | 6.108 | 45.9371 | 59.8258 | -2420.1868 |  | 153 | 550800 | 32086800 | 63622800 | 95158800
2020-06-09 10:00 | -7603.65 | 6.108 | 46.441 | 59.8258 | -2228.4098 |  | 154 | 554400 | 32090400 | 63626400 | 95162400
2020-06-10 11:00 | -7442.96 | 6.108 | 46.6415 | 59.8258 | -2181.3163 |  | 155 | 558000 | 32094000 | 63630000 | 95166000
2020-06-11 12:00 | -7396.21 | 6.108 | 46.7484 | 59.8258 | -2167.6152 |  | 156 | 561600 | 32097600 | 63633600 | 95169600
2020-06-12 13:00 | -7139.33 | 6.108 | 46.9664 | 59.8258 | -2092.3311 |  | 157 | 565200 | 32101200 | 63637200 | 95173200
2020-06-13 14:00 | -7025.72 | 6.108 | 47.0897 | 59.8258 | -2059.0353 |  | 158 | 568800 | 32104800 | 63640800 | 95176800
2020-06-14 15:00 | -6853.28 | 6.108 | 47.2591 | 59.8258 | -2008.4981 |  | 159 | 572400 | 32108400 | 63644400 | 95180400
2020-06-15 16:00 | -6645.23 | 6.108 | 47.4474 | 59.8258 | -1947.5247 |  | 160 | 576000 | 32112000 | 63648000 | 95184000
2020-06-16 17:00 | -5272.31 | 6.108 | 48.5221 | 59.8258 | -1545.1615 |  | 161 | 579600 | 32115600 | 63651600 | 95187600
2020-06-17 18:00 | -5650.56 | 6.108 | 48.4582 | 59.8258 | -1656.0157 |  | 162 | 583200 | 32119200 | 63655200 | 95191200
2020-06-18 19:00 | -5922.52 | 6.108 | 48.3276 | 59.8258 | -1735.7193 |  | 163 | 586800 | 32122800 | 63658800 | 95194800
2020-06-19 20:00 | -6127.07 | 6.108 | 48.1826 | 59.8258 | -1795.667 |  | 164 | 590400 | 32126400 | 63662400 | 95198400
2020-06-20 21:00 | -6249.91 | 6.108 | 48.1057 | 59.8258 | -1831.6678 |  | 165 | 594000 | 32130000 | 63666000 | 95202000
2020-06-21 22:00 | -6427.66 | 6.108 | 47.9842 | 59.8258 | -1883.7612 |  | 166 | 597600 | 32133600 | 63669600 | 95205600
2020-06-22 23:00 | -6645.86 | 6.108 | 47.7952 | 59.8258 | -1947.7093 |  | 167 | 601200 | 32137200 | 63673200 | 95209200
2020-06-24 | -7723.7 | 6.108 | 46.9636 | 59.8258 | -2263.593 |  | 168 | 604800 | 32140800 | 63676800 | 95212800
2020-06-25 01:00 | -7940.57 | 6.108 | 46.6542 | 59.8258 | -2327.1513 |  | 169 | 608400 | 32144400 | 63680400 | 95216400
2020-06-26 02:00 | -8063.38 | 6.108 | 46.4617 | 59.8258 | -2363.1434 |  | 170 | 612000 | 32148000 | 63684000 | 95220000
2020-06-27 03:00 | -8148.1 | 6.108 | 46.333 | 59.8258 | -2387.9724 |  | 171 | 615600 | 32151600 | 63687600 | 95223600
2020-06-28 04:00 | -8252.3 | 6.108 | 46.1946 | 59.8258 | -2418.5104 |  | 172 | 619200 | 32155200 | 63691200 | 95227200
2020-06-29 05:00 | -8362.08 | 6.108 | 46.0366 | 59.8258 | -2450.6837 |  | 173 | 622800 | 32158800 | 63694800 | 95230800
2020-06-30 06:00 | -8263.86 | 6.108 | 46.0574 | 59.8258 | -2421.8983 |  | 174 | 626400 | 32162400 | 63698400 | 95234400
2020-07-01 07:00 | -8428.29 | 6.108 | 45.9049 | 59.8258 | -2470.088 |  | 175 | 630000 | 32166000 | 63702000 | 95238000
2020-07-02 08:00 | -8633.49 | 6.108 | 45.6937 | 59.8258 | -2530.2262 |  | 176 | 633600 | 32169600 | 63705600 | 95241600
2020-07-03 09:00 | -9222.76 | 6.108 | 45.1719 | 59.8258 | -2702.9241 |  | 177 | 637200 | 32173200 | 63709200 | 95245200
2020-07-04 10:00 | -8803.36 | 6.108 | 45.3395 | 59.8258 | -2580.0101 |  | 178 | 640800 | 32176800 | 63712800 | 95248800
2020-07-05 11:00 | -8444.73 | 6.108 | 45.5596 | 59.8258 | -2474.9061 |  | 179 | 644400 | 32180400 | 63716400 | 95252400
2020-07-06 12:00 | -7988.17 | 6.108 | 45.9032 | 59.8258 | -2341.1015 |  | 180 | 648000 | 32184000 | 63720000 | 95256000
2020-07-07 13:00 | -7920.98 | 6.108 | 45.9833 | 59.8258 | -2321.4101 |  | 181 | 651600 | 32187600 | 63723600 | 95259600
2020-07-08 14:00 | -7666.83 | 6.108 | 46.1774 | 59.8258 | -2246.9261 |  | 182 | 655200 | 32191200 | 63727200 | 95263200
2020-07-09 15:00 | -7650.92 | 6.108 | 46.2204 | 59.8258 | -2242.2633 |  | 183 | 658800 | 32194800 | 63730800 | 95266800
2020-07-10 16:00 | -7617.08 | 6.108 | 46.2538 | 59.8258 | -2232.3458 |  | 184 | 662400 | 32198400 | 63734400 | 95270400
2020-07-11 17:00 | -7851.38 | 6.108 | 46.0666 | 59.8258 | -2301.0123 |  | 185 | 666000 | 32202000 | 63738000 | 95274000
2020-07-12 18:00 | -8169.55 | 6.108 | 45.7761 | 59.8258 | -2394.2588 |  | 186 | 669600 | 32205600 | 63741600 | 95277600
2020-07-13 19:00 | -8745.71 | 6.108 | 45.2657 | 59.8258 | -2563.1146 |  | 187 | 673200 | 32209200 | 63745200 | 95281200
2020-07-14 20:00 | -9070.99 | 6.108 | 44.8916 | 59.8258 | -2658.4447 |  | 188 | 676800 | 32212800 | 63748800 | 95284800
2020-07-15 21:00 | -10018.9 | 6.108 | 44.0593 | 59.8258 | -2936.2497 |  | 189 | 680400 | 32216400 | 63752400 | 95288400
2020-07-16 22:00 | -10467.1 | 6.108 | 43.5068 | 59.8258 | -3067.6042 |  | 190 | 684000 | 32220000 | 63756000 | 95292000
2020-07-17 23:00 | -11573.1 | 6.108 | 42.4688 | 59.8258 | -3391.7408 |  | 191 | 687600 | 32223600 | 63759600 | 95295600
2020-07-19 | -11964.9 | 6.108 | 41.891 | 59.8258 | -3506.566 |  | 192 | 691200 | 32227200 | 63763200 | 95299200
2020-07-20 01:00 | -12124.2 | 6.108 | 41.5309 | 59.8258 | -3553.2523 |  | 193 | 694800 | 32230800 | 63766800 | 95302800
2020-07-21 02:00 | -12361.7 | 6.108 | 41.1579 | 59.8258 | -3622.8566 |  | 194 | 698400 | 32234400 | 63770400 | 95306400
2020-07-22 03:00 | -12537.8 | 6.108 | 40.8435 | 59.8258 | -3674.4665 |  | 195 | 702000 | 32238000 | 63774000 | 95310000
2020-07-23 04:00 | -12648.4 | 6.108 | 40.5838 | 59.8258 | -3706.8801 |  | 196 | 705600 | 32241600 | 63777600 | 95313600
2020-07-24 05:00 | -12662.3 | 6.108 | 40.4292 | 59.8258 | -3710.9538 |  | 197 | 709200 | 32245200 | 63781200 | 95317200
2020-07-25 06:00 | -12597.2 | 6.108 | 40.3564 | 59.8258 | -3691.8749 |  | 198 | 712800 | 32248800 | 63784800 | 95320800
2020-07-26 07:00 | -12398.7 | 6.108 | 40.4059 | 59.8258 | -3633.7003 |  | 199 | 716400 | 32252400 | 63788400 | 95324400
2020-07-27 08:00 | -11925.6 | 6.108 | 40.6949 | 59.8258 | -3495.0484 |  | 200 | 720000 | 32256000 | 63792000 | 95328000
2020-07-28 09:00 | -10549.1 | 6.108 | 41.7381 | 59.8258 | -3091.636 |  | 201 | 723600 | 32259600 | 63795600 | 95331600
2020-07-29 10:00 | -9039.01 | 6.108 | 43.0402 | 59.8258 | -2649.0723 |  | 202 | 727200 | 32263200 | 63799200 | 95335200
2020-07-30 11:00 | -7382.16 | 6.108 | 44.5717 | 59.8258 | -2163.4975 |  | 203 | 730800 | 32266800 | 63802800 | 95338800
2020-07-31 12:00 | -6645.41 | 6.108 | 45.501 | 59.8258 | -1947.5774 |  | 204 | 734400 | 32270400 | 63806400 | 95342400
2020-08-01 13:00 | -5583.47 | 6.108 | 46.6223 | 59.8258 | -1636.3535 |  | 205 | 738000 | 32274000 | 63810000 | 95346000
2020-08-02 14:00 | -5166.34 | 6.108 | 47.2938 | 59.8258 | -1514.1048 |  | 206 | 741600 | 32277600 | 63813600 | 95349600
2020-08-03 15:00 | -4836.49 | 6.108 | 47.8404 | 59.8258 | -1417.4353 |  | 207 | 745200 | 32281200 | 63817200 | 95353200
2020-08-04 16:00 | -4565.42 | 6.108 | 48.2917 | 59.8258 | -1337.9925 |  | 208 | 748800 | 32284800 | 63820800 | 95356800
2020-08-05 17:00 | -5817.44 | 6.108 | 47.5628 | 59.8258 | -1704.9234 |  | 209 | 752400 | 32288400 | 63824400 | 95360400
2020-08-06 18:00 | -6423.73 | 6.108 | 47.1049 | 59.8258 | -1882.6094 |  | 210 | 756000 | 32292000 | 63828000 | 95364000
2020-08-07 19:00 | -7242.6 | 6.108 | 46.4454 | 59.8258 | -2122.5965 |  | 211 | 759600 | 32295600 | 63831600 | 95367600
2020-08-08 20:00 | -7916.89 | 6.108 | 45.8477 | 59.8258 | -2320.2114 |  | 212 | 763200 | 32299200 | 63835200 | 95371200
2020-08-09 21:00 | -9014.05 | 6.108 | 44.8908 | 59.8258 | -2641.7573 |  | 213 | 766800 | 32302800 | 63838800 | 95374800
2020-08-10 22:00 | -9474.18 | 6.108 | 44.3082 | 59.8258 | -2776.6081 |  | 214 | 770400 | 32306400 | 63842400 | 95378400
2020-08-11 23:00 | -10557.3 | 6.108 | 43.2983 | 59.8258 | -3094.0392 |  | 215 | 774000 | 32310000 | 63846000 | 95382000
2020-08-13 | -10931 | 6.108 | 42.7483 | 59.8258 | -3203.5599 |  | 216 | 777600 | 32313600 | 63849600 | 95385600
2020-08-14 01:00 | -11010.6 | 6.108 | 42.4574 | 59.8258 | -3226.8883 |  | 217 | 781200 | 32317200 | 63853200 | 95389200
2020-08-15 02:00 | -11046.9 | 6.108 | 42.2609 | 59.8258 | -3237.5268 |  | 218 | 784800 | 32320800 | 63856800 | 95392800
2020-08-16 03:00 | -10976.6 | 6.108 | 42.1804 | 59.8258 | -3216.9239 |  | 219 | 788400 | 32324400 | 63860400 | 95396400
2020-08-17 04:00 | -11035.8 | 6.108 | 42.0257 | 59.8258 | -3234.2737 |  | 220 | 792000 | 32328000 | 63864000 | 95400000
2020-08-18 05:00 | -11101 | 6.108 | 41.8947 | 59.8258 | -3253.3819 |  | 221 | 795600 | 32331600 | 63867600 | 95403600
2020-08-19 06:00 | -10894 | 6.108 | 41.9758 | 59.8258 | -3192.7162 |  | 222 | 799200 | 32335200 | 63871200 | 95407200
2020-08-20 07:00 | -10588.4 | 6.108 | 42.1758 | 59.8258 | -3103.1537 |  | 223 | 802800 | 32338800 | 63874800 | 95410800
2020-08-21 08:00 | -9456.61 | 6.108 | 43.036 | 59.8258 | -2771.4588 |  | 224 | 806400 | 32342400 | 63878400 | 95414400
2020-08-22 09:00 | -8649 | 6.108 | 43.7888 | 59.8258 | -2534.7717 |  | 225 | 810000 | 32346000 | 63882000 | 95418000
2020-08-23 10:00 | -7528.48 | 6.108 | 44.8057 | 59.8258 | -2206.3797 |  | 226 | 813600 | 32349600 | 63885600 | 95421600
2020-08-24 11:00 | -5568.31 | 6.108 | 46.5232 | 59.8258 | -1631.9106 |  | 227 | 817200 | 32353200 | 63889200 | 95425200
2020-08-25 12:00 | -3873.81 | 6.108 | 48.2082 | 59.8258 | -1135.3016 |  | 228 | 820800 | 32356800 | 63892800 | 95428800
2020-08-26 13:00 | -3115.53 | 6.108 | 49.2553 | 59.8258 | -913.0717 |  | 229 | 824400 | 32360400 | 63896400 | 95432400
2020-08-27 14:00 | -2568.62 | 6.108 | 50.0522 | 59.8258 | -752.7882 |  | 230 | 828000 | 32364000 | 63900000 | 95436000
2020-08-28 15:00 | -2783.32 | 6.108 | 50.2287 | 59.8258 | -815.7106 |  | 231 | 831600 | 32367600 | 63903600 | 95439600
2020-08-29 16:00 | -2906.05 | 6.108 | 50.361 | 59.8258 | -851.6792 |  | 232 | 835200 | 32371200 | 63907200 | 95443200
2020-08-30 17:00 | -3628.2 | 6.108 | 49.9836 | 59.8258 | -1063.3205 |  | 233 | 838800 | 32374800 | 63910800 | 95446800
2020-08-31 18:00 | -3934.29 | 6.108 | 49.7983 | 59.8258 | -1153.0266 |  | 234 | 842400 | 32378400 | 63914400 | 95450400
2020-09-01 19:00 | -4777.61 | 6.108 | 49.2006 | 59.8258 | -1400.1793 |  | 235 | 846000 | 32382000 | 63918000 | 95454000
2020-09-02 20:00 | -5520.26 | 6.108 | 48.585 | 59.8258 | -1617.8285 |  | 236 | 849600 | 32385600 | 63921600 | 95457600
2020-09-03 21:00 | -6785.09 | 6.108 | 47.5399 | 59.8258 | -1988.5136 |  | 237 | 853200 | 32389200 | 63925200 | 95461200
2020-09-04 22:00 | -7281.18 | 6.108 | 46.9635 | 59.8258 | -2133.9032 |  | 238 | 856800 | 32392800 | 63928800 | 95464800
2020-09-05 23:00 | -8361.33 | 6.108 | 45.983 | 59.8258 | -2450.4639 |  | 239 | 860400 | 32396400 | 63932400 | 95468400
2020-09-07 | -8708.5 | 6.108 | 45.469 | 59.8258 | -2552.2094 |  | 240 | 864000 | 32400000 | 63936000 | 95472000
2020-09-08 01:00 | -8765.35 | 6.108 | 45.2181 | 59.8258 | -2568.8705 |  | 241 | 867600 | 32403600 | 63939600 | 95475600
2020-09-09 02:00 | -8911.88 | 6.108 | 44.9617 | 59.8258 | -2611.8142 |  | 242 | 871200 | 32407200 | 63943200 | 95479200
2020-09-10 03:00 | -8799.73 | 6.108 | 44.9267 | 59.8258 | -2578.9463 |  | 243 | 874800 | 32410800 | 63946800 | 95482800
2020-09-11 04:00 | -8512.15 | 6.108 | 45.0634 | 59.8258 | -2494.6649 |  | 244 | 878400 | 32414400 | 63950400 | 95486400
2020-09-12 05:00 | -8286.96 | 6.108 | 45.2248 | 59.8258 | -2428.6682 |  | 245 | 882000 | 32418000 | 63954000 | 95490000
2020-09-13 06:00 | -7691.92 | 6.108 | 45.6846 | 59.8258 | -2254.2792 |  | 246 | 885600 | 32421600 | 63957600 | 95493600
2020-09-14 07:00 | -7559.17 | 6.108 | 45.8634 | 59.8258 | -2215.374 |  | 247 | 889200 | 32425200 | 63961200 | 95497200
2020-09-15 08:00 | -7169.92 | 6.108 | 46.2138 | 59.8258 | -2101.2961 |  | 248 | 892800 | 32428800 | 63964800 | 95500800
2020-09-16 09:00 | -7554.87 | 6.108 | 46.0114 | 59.8258 | -2214.1138 |  | 249 | 896400 | 32432400 | 63968400 | 95504400
2020-09-17 10:00 | -6997.38 | 6.108 | 46.4242 | 59.8258 | -2050.7296 |  | 250 | 900000 | 32436000 | 63972000 | 95508000
2020-09-18 11:00 | -6549.52 | 6.108 | 46.8323 | 59.8258 | -1919.4748 |  | 251 | 903600 | 32439600 | 63975600 | 95511600
2020-09-19 12:00 | -6633.95 | 6.108 | 46.8613 | 59.8258 | -1944.2188 |  | 252 | 907200 | 32443200 | 63979200 | 95515200
2020-09-20 13:00 | -6311.04 | 6.108 | 47.1291 | 59.8258 | -1849.5832 |  | 253 | 910800 | 32446800 | 63982800 | 95518800
2020-09-21 14:00 | -6334.7 | 6.108 | 47.1591 | 59.8258 | -1856.5173 |  | 254 | 914400 | 32450400 | 63986400 | 95522400
2020-09-22 15:00 | -6317.81 | 6.108 | 47.2079 | 59.8258 | -1851.5673 |  | 255 | 918000 | 32454000 | 63990000 | 95526000
2020-09-23 16:00 | -5368.3 | 6.108 | 47.9335 | 59.8258 | -1573.2934 |  | 256 | 921600 | 32457600 | 63993600 | 95529600
2020-09-24 17:00 | -5011.01 | 6.108 | 48.3381 | 59.8258 | -1468.5821 |  | 257 | 925200 | 32461200 | 63997200 | 95533200
2020-09-25 18:00 | -4779.04 | 6.108 | 48.641 | 59.8258 | -1400.5984 |  | 258 | 928800 | 32464800 | 64000800 | 95536800
2020-09-26 19:00 | -5192.04 | 6.108 | 48.4371 | 59.8258 | -1521.6367 |  | 259 | 932400 | 32468400 | 64004400 | 95540400
2020-09-27 20:00 | -5386.79 | 6.108 | 48.3171 | 59.8258 | -1578.7123 |  | 260 | 936000 | 32472000 | 64008000 | 95544000
2020-09-28 21:00 | -6303.69 | 6.108 | 47.6591 | 59.8258 | -1847.4292 |  | 261 | 939600 | 32475600 | 64011600 | 95547600
2020-09-29 22:00 | -6564.64 | 6.108 | 47.3687 | 59.8258 | -1923.9061 |  | 262 | 943200 | 32479200 | 64015200 | 95551200
2020-09-30 23:00 | -7415.45 | 6.108 | 46.6559 | 59.8258 | -2173.2539 |  | 263 | 946800 | 32482800 | 64018800 | 95554800
2020-10-02 | -7647.17 | 6.108 | 46.3373 | 59.8258 | -2241.1643 |  | 264 | 950400 | 32486400 | 64022400 | 95558400
2020-10-03 01:00 | -7834.94 | 6.108 | 46.0854 | 59.8258 | -2296.1942 |  | 265 | 954000 | 32490000 | 64026000 | 95562000
2020-10-04 02:00 | -7850.31 | 6.108 | 45.986 | 59.8258 | -2300.6988 |  | 266 | 957600 | 32493600 | 64029600 | 95565600
2020-10-05 03:00 | -7939.96 | 6.108 | 45.8679 | 59.8258 | -2326.9726 |  | 267 | 961200 | 32497200 | 64033200 | 95569200
2020-10-06 04:00 | -7713 | 6.108 | 45.9767 | 59.8258 | -2260.4572 |  | 268 | 964800 | 32500800 | 64036800 | 95572800
2020-10-07 05:00 | -7393.22 | 6.108 | 46.2073 | 59.8258 | -2166.7389 |  | 269 | 968400 | 32504400 | 64040400 | 95576400
2020-10-08 06:00 | -6847.64 | 6.108 | 46.6404 | 59.8258 | -2006.8452 |  | 270 | 972000 | 32508000 | 64044000 | 95580000
2020-10-09 07:00 | -7037.13 | 6.108 | 46.5773 | 59.8258 | -2062.3792 |  | 271 | 975600 | 32511600 | 64047600 | 95583600
2020-10-10 08:00 | -7150.23 | 6.108 | 46.4994 | 59.8258 | -2095.5256 |  | 272 | 979200 | 32515200 | 64051200 | 95587200
2020-10-11 09:00 | -7680.69 | 6.108 | 46.0967 | 59.8258 | -2250.988 |  | 273 | 982800 | 32518800 | 64054800 | 95590800
2020-10-12 10:00 | -6522.11 | 6.108 | 46.894 | 59.8258 | -1911.4418 |  | 274 | 986400 | 32522400 | 64058400 | 95594400
2020-10-13 11:00 | -4957.35 | 6.108 | 48.1852 | 59.8258 | -1452.8559 |  | 275 | 990000 | 32526000 | 64062000 | 95598000
2020-10-14 12:00 | -3142.13 | 6.108 | 49.8148 | 59.8258 | -920.8674 |  | 276 | 993600 | 32529600 | 64065600 | 95601600
2020-10-15 13:00 | -2741.5 | 6.108 | 50.5024 | 59.8258 | -803.4543 |  | 277 | 997200 | 32533200 | 64069200 | 95605200
2020-10-16 14:00 | -1489.14 | 4.7885 | 51.4164 | 59.8258 | -436.4239 |  | 278 | 1000800 | 32536800 | 64072800 | 95608800
2020-10-17 15:00 | -1977.49 | 6.108 | 51.7437 | 59.8258 | -579.5451 |  | 279 | 1004400 | 32540400 | 64076400 | 95612400
2020-10-18 16:00 | -2445.09 | 6.108 | 51.5906 | 59.8258 | -716.5851 |  | 280 | 1008000 | 32544000 | 64080000 | 95616000
2020-10-19 17:00 | -2875.48 | 6.108 | 51.3476 | 59.8258 | -842.72 |  | 281 | 1011600 | 32547600 | 64083600 | 95619600
2020-10-20 18:00 | -3852.92 | 6.108 | 50.6317 | 59.8258 | -1129.1794 |  | 282 | 1015200 | 32551200 | 64087200 | 95623200
2020-10-21 19:00 | -4766.32 | 6.108 | 49.8687 | 59.8258 | -1396.8705 |  | 283 | 1018800 | 32554800 | 64090800 | 95626800
2020-10-22 20:00 | -5515.94 | 6.108 | 49.1504 | 59.8258 | -1616.5624 |  | 284 | 1022400 | 32558400 | 64094400 | 95630400
2020-10-23 21:00 | -6755.14 | 6.108 | 48.0752 | 59.8258 | -1979.7361 |  | 285 | 1026000 | 32562000 | 64098000 | 95634000
2020-10-24 22:00 | -7082.15 | 6.108 | 47.5895 | 59.8258 | -2075.5733 |  | 286 | 1029600 | 32565600 | 64101600 | 95637600
2020-10-25 23:00 | -7802.76 | 6.108 | 46.8632 | 59.8258 | -2286.7632 |  | 287 | 1033200 | 32569200 | 64105200 | 95641200
2020-10-27 | -8158.75 | 6.108 | 46.3773 | 59.8258 | -2391.0936 |  | 288 | 1036800 | 32572800 | 64108800 | 95644800
2020-10-28 01:00 | -8275.23 | 6.108 | 46.0936 | 59.8258 | -2425.2305 |  | 289 | 1040400 | 32576400 | 64112400 | 95648400
2020-10-29 02:00 | -8362.25 | 6.108 | 45.8657 | 59.8258 | -2450.7336 |  | 290 | 1044000 | 32580000 | 64116000 | 95652000
2020-10-30 03:00 | -8415.28 | 6.108 | 45.705 | 59.8258 | -2466.2751 |  | 291 | 1047600 | 32583600 | 64119600 | 95655600
2020-10-31 04:00 | -8289.93 | 6.108 | 45.691 | 59.8258 | -2429.5387 |  | 292 | 1051200 | 32587200 | 64123200 | 95659200
2020-11-01 05:00 | -8168.5 | 6.108 | 45.7167 | 59.8258 | -2393.951 |  | 293 | 1054800 | 32590800 | 64126800 | 95662800
2020-11-02 06:00 | -7975.55 | 6.108 | 45.8217 | 59.8258 | -2337.403 |  | 294 | 1058400 | 32594400 | 64130400 | 95666400
2020-11-03 07:00 | -7281.34 | 6.108 | 46.3326 | 59.8258 | -2133.9501 |  | 295 | 1062000 | 32598000 | 64134000 | 95670000
2020-11-04 08:00 | -6946.13 | 6.108 | 46.6633 | 59.8258 | -2035.7098 |  | 296 | 1065600 | 32601600 | 64137600 | 95673600
2020-11-05 09:00 | -7622.52 | 6.108 | 46.2499 | 59.8258 | -2233.9401 |  | 297 | 1069200 | 32605200 | 64141200 | 95677200
2020-11-06 10:00 | -7032.43 | 6.108 | 46.6404 | 59.8258 | -2061.0018 |  | 298 | 1072800 | 32608800 | 64144800 | 95680800
2020-11-07 11:00 | -6211.78 | 6.108 | 47.3068 | 59.8258 | -1820.493 |  | 299 | 1076400 | 32612400 | 64148400 | 95684400
2020-11-08 12:00 | -5215.35 | 6.108 | 48.1956 | 59.8258 | -1528.4682 |  | 300 | 1080000 | 32616000 | 64152000 | 95688000
2020-11-09 13:00 | -4812.96 | 6.108 | 48.6876 | 59.8258 | -1410.5393 |  | 301 | 1083600 | 32619600 | 64155600 | 95691600
2020-11-10 14:00 | -4536.33 | 6.108 | 49.0398 | 59.8258 | -1329.4671 |  | 302 | 1087200 | 32623200 | 64159200 | 95695200
2020-11-11 15:00 | -3893.96 | 6.108 | 49.6655 | 59.8258 | -1141.207 |  | 303 | 1090800 | 32626800 | 64162800 | 95698800
2020-11-12 16:00 | -3668.06 | 6.108 | 50.021 | 59.8258 | -1075.0023 |  | 304 | 1094400 | 32630400 | 64166400 | 95702400
2020-11-13 17:00 | -1958.31 | 6.108 | 51.4579 | 59.8258 | -573.924 |  | 305 | 1098000 | 32634000 | 64170000 | 95706000
2020-11-14 18:00 | -2250.47 | 6.108 | 51.5736 | 59.8258 | -659.5477 |  | 306 | 1101600 | 32637600 | 64173600 | 95709600
2020-11-15 19:00 | -2536.9 | 6.108 | 51.5387 | 59.8258 | -743.492 |  | 307 | 1105200 | 32641200 | 64177200 | 95713200
2020-11-16 20:00 | -2922.54 | 6.108 | 51.3438 | 59.8258 | -856.5119 |  | 308 | 1108800 | 32644800 | 64180800 | 95716800
2020-11-17 21:00 | -3196.53 | 6.108 | 51.2111 | 59.8258 | -936.8105 |  | 309 | 1112400 | 32648400 | 64184400 | 95720400
2020-11-18 22:00 | -3759.1 | 6.108 | 50.848 | 59.8258 | -1101.6835 |  | 310 | 1116000 | 32652000 | 64188000 | 95724000
2020-11-19 23:00 | -4312.11 | 6.108 | 50.4037 | 59.8258 | -1263.7547 |  | 311 | 1119600 | 32655600 | 64191600 | 95727600
2020-11-21 | -6243.89 | 6.108 | 48.8889 | 59.8258 | -1829.9035 |  | 312 | 1123200 | 32659200 | 64195200 | 95731200
2020-11-22 01:00 | -6683.26 | 6.108 | 48.2809 | 59.8258 | -1958.6702 |  | 313 | 1126800 | 32662800 | 64198800 | 95734800
2020-11-23 02:00 | -7037.71 | 6.108 | 47.8139 | 59.8258 | -2062.5492 |  | 314 | 1130400 | 32666400 | 64202400 | 95738400
2020-11-24 03:00 | -7220.31 | 6.108 | 47.5187 | 59.8258 | -2116.064 |  | 315 | 1134000 | 32670000 | 64206000 | 95742000
2020-11-25 04:00 | -7329.32 | 6.108 | 47.2985 | 59.8258 | -2148.0117 |  | 316 | 1137600 | 32673600 | 64209600 | 95745600
2020-11-26 05:00 | -7600.57 | 6.108 | 46.9558 | 59.8258 | -2227.5072 |  | 317 | 1141200 | 32677200 | 64213200 | 95749200
2020-11-27 06:00 | -7679.67 | 6.108 | 46.7772 | 59.8258 | -2250.6891 |  | 318 | 1144800 | 32680800 | 64216800 | 95752800
2020-11-28 07:00 | -6972.91 | 6.108 | 47.2072 | 59.8258 | -2043.5582 |  | 319 | 1148400 | 32684400 | 64220400 | 95756400
2020-11-29 08:00 | -6158.35 | 6.108 | 47.8386 | 59.8258 | -1804.8342 |  | 320 | 1152000 | 32688000 | 64224000 | 95760000
2020-11-30 09:00 | -5700.38 | 6.108 | 48.2872 | 59.8258 | -1670.6165 |  | 321 | 1155600 | 32691600 | 64227600 | 95763600
2020-12-01 10:00 | -4648.71 | 6.108 | 49.1725 | 59.8258 | -1362.4024 |  | 322 | 1159200 | 32695200 | 64231200 | 95767200
2020-12-02 11:00 | -3333.67 | 6.108 | 50.345 | 59.8258 | -977.0022 |  | 323 | 1162800 | 32698800 | 64234800 | 95770800
2020-12-03 12:00 | -2293.26 | 6.108 | 51.4246 | 59.8258 | -672.0882 |  | 324 | 1166400 | 32702400 | 64238400 | 95774400
2020-12-04 13:00 | -1669.81 | 5.3055 | 52.0153 | 59.8258 | -489.373 |  | 325 | 1170000 | 32706000 | 64242000 | 95778000
2020-12-05 14:00 | -1333.37 | 4.2781 | 52.3013 | 59.8258 | -390.7722 |  | 326 | 1173600 | 32709600 | 64245600 | 95781600
2020-12-06 15:00 | -1057.66 | 3.5012 | 52.5817 | 59.8258 | -309.9695 |  | 327 | 1177200 | 32713200 | 64249200 | 95785200
2020-12-07 16:00 | -1524.63 | 5.0445 | 52.7957 | 59.8258 | -446.8249 |  | 328 | 1180800 | 32716800 | 64252800 | 95788800
2020-12-08 17:00 | -1570.98 | 5.0252 | 52.8347 | 59.8258 | -460.4088 |  | 329 | 1184400 | 32720400 | 64256400 | 95792400
2020-12-09 18:00 | -2884.4 | 6.108 | 52.1856 | 59.8258 | -845.3342 |  | 330 | 1188000 | 32724000 | 64260000 | 95796000
2020-12-10 19:00 | -3863.14 | 6.108 | 51.3539 | 59.8258 | -1132.1746 |  | 331 | 1191600 | 32727600 | 64263600 | 95799600
2020-12-11 20:00 | -4551.82 | 6.108 | 50.6703 | 59.8258 | -1334.0068 |  | 332 | 1195200 | 32731200 | 64267200 | 95803200
2020-12-12 21:00 | -5184.75 | 6.108 | 50.031 | 59.8258 | -1519.5002 |  | 333 | 1198800 | 32734800 | 64270800 | 95806800
2020-12-13 22:00 | -5680.54 | 6.108 | 49.4844 | 59.8258 | -1664.8019 |  | 334 | 1202400 | 32738400 | 64274400 | 95810400
2020-12-14 23:00 | -6254.3 | 6.108 | 48.8641 | 59.8258 | -1832.9544 |  | 335 | 1206000 | 32742000 | 64278000 | 95814000
2020-12-16 | -7898.98 | 6.108 | 47.4419 | 59.8258 | -2314.9625 |  | 336 | 1209600 | 32745600 | 64281600 | 95817600
2020-12-17 01:00 | -8300.19 | 6.108 | 46.7935 | 59.8258 | -2432.5456 |  | 337 | 1213200 | 32749200 | 64285200 | 95821200
2020-12-18 02:00 | -8479.89 | 6.108 | 46.3871 | 59.8258 | -2485.2104 |  | 338 | 1216800 | 32752800 | 64288800 | 95824800
2020-12-19 03:00 | -8668.48 | 6.108 | 46.042 | 59.8258 | -2540.4807 |  | 339 | 1220400 | 32756400 | 64292400 | 95828400
2020-12-20 04:00 | -9113.95 | 6.108 | 45.5181 | 59.8258 | -2671.0351 |  | 340 | 1224000 | 32760000 | 64296000 | 95832000
2020-12-21 05:00 | -9440.46 | 6.108 | 45.0533 | 59.8258 | -2766.7257 |  | 341 | 1227600 | 32763600 | 64299600 | 95835600
2020-12-22 06:00 | -9888.92 | 6.108 | 44.5355 | 59.8258 | -2898.1564 |  | 342 | 1231200 | 32767200 | 64303200 | 95839200
2020-12-23 07:00 | -8892.01 | 6.108 | 45.0919 | 59.8258 | -2605.9909 |  | 343 | 1234800 | 32770800 | 64306800 | 95842800
2020-12-24 08:00 | -7570.33 | 6.108 | 46.0757 | 59.8258 | -2218.6447 |  | 344 | 1238400 | 32774400 | 64310400 | 95846400
2020-12-25 09:00 | -6656.26 | 6.108 | 46.904 | 59.8258 | -1950.7572 |  | 345 | 1242000 | 32778000 | 64314000 | 95850000
2020-12-26 10:00 | -5174.3 | 6.108 | 48.1801 | 59.8258 | -1516.4376 |  | 346 | 1245600 | 32781600 | 64317600 | 95853600
2020-12-27 11:00 | -3963.07 | 6.108 | 49.3611 | 59.8258 | -1161.4612 |  | 347 | 1249200 | 32785200 | 64321200 | 95857200
2020-12-28 12:00 | -2707.26 | 6.108 | 50.6446 | 59.8258 | -793.4196 |  | 348 | 1252800 | 32788800 | 64324800 | 95860800
2020-12-29 13:00 | -2752.58 | 6.108 | 50.9793 | 59.8258 | -806.7016 |  | 349 | 1256400 | 32792400 | 64328400 | 95864400
2020-12-30 14:00 | -2799.4 | 6.108 | 51.1619 | 59.8258 | -820.4232 |  | 350 | 1260000 | 32796000 | 64332000 | 95868000
2020-12-31 15:00 | -3323.05 | 6.108 | 50.9174 | 59.8258 | -973.8898 |  | 351 | 1263600 | 32799600 | 64335600 | 95871600
2021-01-01 16:00 | -3584.98 | 6.108 | 50.7731 | 59.8258 | -1050.6539 |  | 352 | 1267200 | 32803200 | 64339200 | 95875200
2021-01-02 17:00 | -2785.82 | 6.108 | 51.3905 | 59.8258 | -816.4432 |  | 353 | 1270800 | 32806800 | 64342800 | 95878800
2021-01-03 18:00 | -3677.44 | 6.108 | 50.8674 | 59.8258 | -1077.7513 |  | 354 | 1274400 | 32810400 | 64346400 | 95882400
2021-01-04 19:00 | -4512.81 | 6.108 | 50.2233 | 59.8258 | -1322.5741 |  | 355 | 1278000 | 32814000 | 64350000 | 95886000
2021-01-05 20:00 | -5150.16 | 6.108 | 49.6275 | 59.8258 | -1509.3629 |  | 356 | 1281600 | 32817600 | 64353600 | 95889600
2021-01-06 21:00 | -5780.45 | 6.108 | 49.0352 | 59.8258 | -1694.0827 |  | 357 | 1285200 | 32821200 | 64357200 | 95893200
2021-01-07 22:00 | -5939.67 | 6.108 | 48.769 | 59.8258 | -1740.7454 |  | 358 | 1288800 | 32824800 | 64360800 | 95896800
2021-01-08 23:00 | -5909.86 | 6.108 | 48.6556 | 59.8258 | -1732.009 |  | 359 | 1292400 | 32828400 | 64364400 | 95900400
2021-01-10 | -6844.57 | 6.108 | 47.8748 | 59.8258 | -2005.9455 |  | 360 | 1296000 | 32832000 | 64368000 | 95904000
2021-01-11 01:00 | -7152.31 | 6.108 | 47.4624 | 59.8258 | -2096.1351 |  | 361 | 1299600 | 32835600 | 64371600 | 95907600
2021-01-12 02:00 | -7448.52 | 6.108 | 47.0868 | 59.8258 | -2182.9457 |  | 362 | 1303200 | 32839200 | 64375200 | 95911200
2021-01-13 03:00 | -7637.79 | 6.108 | 46.8229 | 59.8258 | -2238.4153 |  | 363 | 1306800 | 32842800 | 64378800 | 95914800
2021-01-14 04:00 | -7367.14 | 6.108 | 46.916 | 59.8258 | -2159.0956 |  | 364 | 1310400 | 32846400 | 64382400 | 95918400
2021-01-15 05:00 | -7164.64 | 6.108 | 47.0093 | 59.8258 | -2099.7487 |  | 365 | 1314000 | 32850000 | 64386000 | 95922000
2021-01-16 06:00 | -6570.8 | 6.108 | 47.4491 | 59.8258 | -1925.7114 |  | 366 | 1317600 | 32853600 | 64389600 | 95925600
2021-01-17 07:00 | -6464.59 | 6.108 | 47.5927 | 59.8258 | -1894.5843 |  | 367 | 1321200 | 32857200 | 64393200 | 95929200
2021-01-18 08:00 | -6109.22 | 6.108 | 47.901 | 59.8258 | -1790.4356 |  | 368 | 1324800 | 32860800 | 64396800 | 95932800
2021-01-19 09:00 | -6456.72 | 6.108 | 47.7098 | 59.8258 | -1892.2778 |  | 369 | 1328400 | 32864400 | 64400400 | 95936400
2021-01-20 10:00 | -5986.61 | 6.108 | 48.0426 | 59.8258 | -1754.5022 |  | 370 | 1332000 | 32868000 | 64404000 | 95940000
2021-01-21 11:00 | -5528.32 | 6.108 | 48.4216 | 59.8258 | -1620.1907 |  | 371 | 1335600 | 32871600 | 64407600 | 95943600
2021-01-22 12:00 | -5105.08 | 6.108 | 48.8063 | 59.8258 | -1496.1513 |  | 372 | 1339200 | 32875200 | 64411200 | 95947200
2021-01-23 13:00 | -5046.64 | 6.108 | 48.9314 | 59.8258 | -1479.0242 |  | 373 | 1342800 | 32878800 | 64414800 | 95950800
2021-01-24 14:00 | -5176.49 | 6.108 | 48.8754 | 59.8258 | -1517.0795 |  | 374 | 1346400 | 32882400 | 64418400 | 95954400
2021-01-25 15:00 | -5294.95 | 6.108 | 48.8049 | 59.8258 | -1551.7967 |  | 375 | 1350000 | 32886000 | 64422000 | 95958000
2021-01-26 16:00 | -4548.91 | 6.108 | 49.3625 | 59.8258 | -1333.1539 |  | 376 | 1353600 | 32889600 | 64425600 | 95961600
2021-01-27 17:00 | -4523.75 | 6.108 | 49.4767 | 59.8258 | -1325.7803 |  | 377 | 1357200 | 32893200 | 64429200 | 95965200
2021-01-28 18:00 | -4373.97 | 6.108 | 49.6428 | 59.8258 | -1281.8841 |  | 378 | 1360800 | 32896800 | 64432800 | 95968800
2021-01-29 19:00 | -5000.5 | 6.108 | 49.2263 | 59.8258 | -1465.5019 |  | 379 | 1364400 | 32900400 | 64436400 | 95972400
2021-01-30 20:00 | -5390.84 | 6.108 | 48.8966 | 59.8258 | -1579.8992 |  | 380 | 1368000 | 32904000 | 64440000 | 95976000
2021-01-31 21:00 | -6480.32 | 6.108 | 48.0333 | 59.8258 | -1899.1943 |  | 381 | 1371600 | 32907600 | 64443600 | 95979600
2021-02-01 22:00 | -6822.69 | 6.108 | 47.6049 | 59.8258 | -1999.5331 |  | 382 | 1375200 | 32911200 | 64447200 | 95983200
2021-02-02 23:00 | -7561.47 | 6.108 | 46.9056 | 59.8258 | -2216.0481 |  | 383 | 1378800 | 32914800 | 64450800 | 95986800
2021-02-04 | -7818.56 | 6.108 | 46.5282 | 59.8258 | -2291.3937 |  | 384 | 1382400 | 32918400 | 64454400 | 95990400
2021-02-05 01:00 | -8149.94 | 6.108 | 46.1313 | 59.8258 | -2388.5116 |  | 385 | 1386000 | 32922000 | 64458000 | 95994000
2021-02-06 02:00 | -8515.07 | 6.108 | 45.7163 | 59.8258 | -2495.5207 |  | 386 | 1389600 | 32925600 | 64461600 | 95997600
2021-02-07 03:00 | -8797.41 | 6.108 | 45.3692 | 59.8258 | -2578.2664 |  | 387 | 1393200 | 32929200 | 64465200 | 96001200
2021-02-08 04:00 | -8768.5 | 6.108 | 45.2489 | 59.8258 | -2569.7937 |  | 388 | 1396800 | 32932800 | 64468800 | 96004800
2021-02-09 05:00 | -8835.94 | 6.108 | 45.1058 | 59.8258 | -2589.5584 |  | 389 | 1400400 | 32936400 | 64472400 | 96008400
2021-02-10 06:00 | -8536 | 6.108 | 45.2396 | 59.8258 | -2501.6547 |  | 390 | 1404000 | 32940000 | 64476000 | 96012000
2021-02-11 07:00 | -8781.13 | 6.108 | 45.0178 | 59.8258 | -2573.4952 |  | 391 | 1407600 | 32943600 | 64479600 | 96015600
2021-02-12 08:00 | -8891.59 | 6.108 | 44.8535 | 59.8258 | -2605.8678 |  | 392 | 1411200 | 32947200 | 64483200 | 96019200
2021-02-13 09:00 | -9482.45 | 6.108 | 44.3346 | 59.8258 | -2779.0318 |  | 393 | 1414800 | 32950800 | 64486800 | 96022800
2021-02-14 10:00 | -8560.13 | 6.108 | 44.8819 | 59.8258 | -2508.7265 |  | 394 | 1418400 | 32954400 | 64490400 | 96026400
2021-02-15 11:00 | -8009.23 | 6.108 | 45.3187 | 59.8258 | -2347.2736 |  | 395 | 1422000 | 32958000 | 64494000 | 96030000
2021-02-16 12:00 | -6723.58 | 6.108 | 46.3388 | 59.8258 | -1970.4868 |  | 396 | 1425600 | 32961600 | 64497600 | 96033600
2021-02-17 13:00 | -6424.41 | 6.108 | 46.7384 | 59.8258 | -1882.8087 |  | 397 | 1429200 | 32965200 | 64501200 | 96037200
2021-02-18 14:00 | -7322.61 | 6.108 | 46.191 | 59.8258 | -2146.0451 |  | 398 | 1432800 | 32968800 | 64504800 | 96040800
2021-02-19 15:00 | -7140.46 | 6.108 | 46.2869 | 59.8258 | -2092.6623 |  | 399 | 1436400 | 32972400 | 64508400 | 96044400
2021-02-20 16:00 | -7016.51 | 6.108 | 46.3816 | 59.8258 | -2056.3361 |  | 400 | 1440000 | 32976000 | 64512000 | 96048000
2021-02-21 17:00 | -7488.75 | 6.108 | 46.0493 | 59.8258 | -2194.736 |  | 401 | 1443600 | 32979600 | 64515600 | 96051600
2021-02-22 18:00 | -7800.77 | 6.108 | 45.7281 | 59.8258 | -2286.18 |  | 402 | 1447200 | 32983200 | 64519200 | 96055200
2021-02-23 19:00 | -8440.25 | 6.108 | 45.1435 | 59.8258 | -2473.5931 |  | 403 | 1450800 | 32986800 | 64522800 | 96058800
2021-02-24 20:00 | -8805.36 | 6.108 | 44.7378 | 59.8258 | -2580.5963 |  | 404 | 1454400 | 32990400 | 64526400 | 96062400
2021-02-25 21:00 | -9804.81 | 6.108 | 43.8637 | 59.8258 | -2873.5062 |  | 405 | 1458000 | 32994000 | 64530000 | 96066000
2021-02-26 22:00 | -10354.7 | 6.108 | 43.2217 | 59.8258 | -3034.663 |  | 406 | 1461600 | 32997600 | 64533600 | 96069600
2021-02-27 23:00 | -11239.3 | 6.108 | 42.3325 | 59.8258 | -3293.9137 |  | 407 | 1465200 | 33001200 | 64537200 | 96073200
2021-03-01 | -11678 | 6.108 | 41.7221 | 59.8258 | -3422.484 |  | 408 | 1468800 | 33004800 | 64540800 | 96076800
2021-03-02 01:00 | -11941 | 6.108 | 41.2697 | 59.8258 | -3499.5616 |  | 409 | 1472400 | 33008400 | 64544400 | 96080400
2021-03-03 02:00 | -11999.1 | 6.108 | 41.0143 | 59.8258 | -3516.5891 |  | 410 | 1476000 | 33012000 | 64548000 | 96084000
2021-03-04 03:00 | -12122.3 | 6.108 | 40.7562 | 59.8258 | -3552.6954 |  | 411 | 1479600 | 33015600 | 64551600 | 96087600
2021-03-05 04:00 | -12158.9 | 6.108 | 40.5691 | 59.8258 | -3563.4218 |  | 412 | 1483200 | 33019200 | 64555200 | 96091200
2021-03-06 05:00 | -12121.9 | 6.108 | 40.4678 | 59.8258 | -3552.5782 |  | 413 | 1486800 | 33022800 | 64558800 | 96094800
2021-03-07 06:00 | -11939.9 | 6.108 | 40.498 | 59.8258 | -3499.2393 |  | 414 | 1490400 | 33026400 | 64562400 | 96098400
2021-03-08 07:00 | -11758.2 | 6.108 | 40.566 | 59.8258 | -3445.9883 |  | 415 | 1494000 | 33030000 | 64566000 | 96102000
2021-03-09 08:00 | -10481.9 | 6.108 | 41.4774 | 59.8258 | -3071.9416 |  | 416 | 1497600 | 33033600 | 64569600 | 96105600
2021-03-10 09:00 | -9633.49 | 6.108 | 42.2455 | 59.8258 | -2823.2972 |  | 417 | 1501200 | 33037200 | 64573200 | 96109200
2021-03-11 10:00 | -8109.06 | 6.108 | 43.5564 | 59.8258 | -2376.5309 |  | 418 | 1504800 | 33040800 | 64576800 | 96112800
2021-03-12 11:00 | -6671.25 | 6.108 | 44.92 | 59.8258 | -1955.1504 |  | 419 | 1508400 | 33044400 | 64580400 | 96116400
2021-03-13 12:00 | -5523.45 | 6.108 | 46.1335 | 59.8258 | -1618.7634 |  | 420 | 1512000 | 33048000 | 64584000 | 96120000
2021-03-14 13:00 | -4916.71 | 6.108 | 46.9565 | 59.8258 | -1440.9455 |  | 421 | 1515600 | 33051600 | 64587600 | 96123600
2021-03-15 14:00 | -4490.38 | 6.108 | 47.5866 | 59.8258 | -1316.0005 |  | 422 | 1519200 | 33055200 | 64591200 | 96127200
2021-03-16 15:00 | -4382.24 | 6.108 | 47.9424 | 59.8258 | -1284.3078 |  | 423 | 1522800 | 33058800 | 64594800 | 96130800
2021-03-17 16:00 | -4341.79 | 6.108 | 48.1799 | 59.8258 | -1272.453 |  | 424 | 1526400 | 33062400 | 64598400 | 96134400
2021-03-18 17:00 | -5763.49 | 6.108 | 47.2736 | 59.8258 | -1689.1122 |  | 425 | 1530000 | 33066000 | 64602000 | 96138000
2021-03-19 18:00 | -6781.44 | 6.108 | 46.4421 | 59.8258 | -1987.4439 |  | 426 | 1533600 | 33069600 | 64605600 | 96141600
2021-03-20 19:00 | -7714.45 | 6.108 | 45.6057 | 59.8258 | -2260.8821 |  | 427 | 1537200 | 33073200 | 64609200 | 96145200
2021-03-21 20:00 | -8380.54 | 6.108 | 44.9292 | 59.8258 | -2456.0938 |  | 428 | 1540800 | 33076800 | 64612800 | 96148800
2021-03-22 21:00 | -9555.62 | 6.108 | 43.865 | 59.8258 | -2800.4758 |  | 429 | 1544400 | 33080400 | 64616400 | 96152400
2021-03-23 22:00 | -10089.4 | 6.108 | 43.1772 | 59.8258 | -2956.9113 |  | 430 | 1548000 | 33084000 | 64620000 | 96156000
2021-03-24 23:00 | -11221.7 | 6.108 | 42.0811 | 59.8258 | -3288.7556 |  | 431 | 1551600 | 33087600 | 64623600 | 96159600
2021-03-26 | -11635.5 | 6.108 | 41.4555 | 59.8258 | -3410.0284 |  | 432 | 1555200 | 33091200 | 64627200 | 96163200
2021-03-27 01:00 | -11870.6 | 6.108 | 41.0108 | 59.8258 | -3478.9294 |  | 433 | 1558800 | 33094800 | 64630800 | 96166800
2021-03-28 02:00 | -11928.9 | 6.108 | 40.7429 | 59.8258 | -3496.0155 |  | 434 | 1562400 | 33098400 | 64634400 | 96170400
2021-03-29 03:00 | -11987.3 | 6.108 | 40.5228 | 59.8258 | -3513.1308 |  | 435 | 1566000 | 33102000 | 64638000 | 96174000
2021-03-30 04:00 | -11903.2 | 6.108 | 40.4261 | 59.8258 | -3488.4836 |  | 436 | 1569600 | 33105600 | 64641600 | 96177600
2021-03-31 05:00 | -11688.4 | 6.108 | 40.4882 | 59.8258 | -3425.5319 |  | 437 | 1573200 | 33109200 | 64645200 | 96181200
2021-04-01 06:00 | -11311.7 | 6.108 | 40.7192 | 59.8258 | -3315.132 |  | 438 | 1576800 | 33112800 | 64648800 | 96184800
2021-04-02 07:00 | -11054.2 | 6.108 | 40.9117 | 59.8258 | -3239.6662 |  | 439 | 1580400 | 33116400 | 64652400 | 96188400
2021-04-03 08:00 | -9974.27 | 6.108 | 41.7309 | 59.8258 | -2923.17 |  | 440 | 1584000 | 33120000 | 64656000 | 96192000
2021-04-04 09:00 | -8992.04 | 6.108 | 42.61 | 59.8258 | -2635.3068 |  | 441 | 1587600 | 33123600 | 64659600 | 96195600
2021-04-05 10:00 | -7162.05 | 6.108 | 44.1814 | 59.8258 | -2098.9897 |  | 442 | 1591200 | 33127200 | 64663200 | 96199200
2021-04-06 11:00 | -5305.47 | 6.108 | 45.9261 | 59.8258 | -1554.8798 |  | 443 | 1594800 | 33130800 | 64666800 | 96202800
2021-04-07 12:00 | -3790.09 | 6.108 | 47.5117 | 59.8258 | -1110.7657 |  | 444 | 1598400 | 33134400 | 64670400 | 96206400
2021-04-08 13:00 | -3644.89 | 6.108 | 48.0965 | 59.8258 | -1068.2118 |  | 445 | 1602000 | 33138000 | 64674000 | 96210000
2021-04-09 14:00 | -3518.4 | 6.108 | 48.5118 | 59.8258 | -1031.1413 |  | 446 | 1605600 | 33141600 | 64677600 | 96213600
2021-04-10 15:00 | -4570.15 | 6.108 | 47.9769 | 59.8258 | -1339.3788 |  | 447 | 1609200 | 33145200 | 64681200 | 96217200
2021-04-11 16:00 | -4328.71 | 6.108 | 48.2116 | 59.8258 | -1268.6197 |  | 448 | 1612800 | 33148800 | 64684800 | 96220800
2021-04-12 17:00 | -4363.65 | 6.108 | 48.292 | 59.8258 | -1278.8596 |  | 449 | 1616400 | 33152400 | 64688400 | 96224400
2021-04-13 18:00 | -4502.95 | 6.108 | 48.2803 | 59.8258 | -1319.6844 |  | 450 | 1620000 | 33156000 | 64692000 | 96228000
2021-04-14 19:00 | -5085.86 | 6.108 | 47.9123 | 59.8258 | -1490.5184 |  | 451 | 1623600 | 33159600 | 64695600 | 96231600
2021-04-15 20:00 | -5393.14 | 6.108 | 47.6709 | 59.8258 | -1580.5733 |  | 452 | 1627200 | 33163200 | 64699200 | 96235200
2021-04-16 21:00 | -6383.8 | 6.108 | 46.9364 | 59.8258 | -1870.9071 |  | 453 | 1630800 | 33166800 | 64702800 | 96238800
2021-04-17 22:00 | -6728.88 | 6.108 | 46.5661 | 59.8258 | -1972.0401 |  | 454 | 1634400 | 33170400 | 64706400 | 96242400
2021-04-18 23:00 | -7690.16 | 6.108 | 45.7424 | 59.8258 | -2253.7634 |  | 455 | 1638000 | 33174000 | 64710000 | 96246000
2021-04-20 | -8240.32 | 6.108 | 45.1392 | 59.8258 | -2414.9994 |  | 456 | 1641600 | 33177600 | 64713600 | 96249600
2021-04-21 01:00 | -8465.21 | 6.108 | 44.7869 | 59.8258 | -2480.9082 |  | 457 | 1645200 | 33181200 | 64717200 | 96253200
2021-04-22 02:00 | -8717.67 | 6.108 | 44.4549 | 59.8258 | -2554.8969 |  | 458 | 1648800 | 33184800 | 64720800 | 96256800
2021-04-23 03:00 | -8747.93 | 6.108 | 44.323 | 59.8258 | -2563.7652 |  | 459 | 1652400 | 33188400 | 64724400 | 96260400
2021-04-24 04:00 | -8710.36 | 6.108 | 44.2651 | 59.8258 | -2552.7545 |  | 460 | 1656000 | 33192000 | 64728000 | 96264000
2021-04-25 05:00 | -8656.38 | 6.108 | 44.2559 | 59.8258 | -2536.9345 |  | 461 | 1659600 | 33195600 | 64731600 | 96267600
2021-04-26 06:00 | -8599.99 | 6.108 | 44.2651 | 59.8258 | -2520.4083 |  | 462 | 1663200 | 33199200 | 64735200 | 96271200
2021-04-27 07:00 | -8059.64 | 6.108 | 44.652 | 59.8258 | -2362.0473 |  | 463 | 1666800 | 33202800 | 64738800 | 96274800
2021-04-28 08:00 | -7823.8 | 6.108 | 44.8788 | 59.8258 | -2292.9294 |  | 464 | 1670400 | 33206400 | 64742400 | 96278400
2021-04-29 09:00 | -8707.22 | 6.108 | 44.2662 | 59.8258 | -2551.8343 |  | 465 | 1674000 | 33210000 | 64746000 | 96282000
2021-04-30 10:00 | -8649.77 | 6.108 | 44.192 | 59.8258 | -2534.9973 |  | 466 | 1677600 | 33213600 | 64749600 | 96285600
2021-05-01 11:00 | -8301 | 6.108 | 44.3827 | 59.8258 | -2432.783 |  | 467 | 1681200 | 33217200 | 64753200 | 96289200
2021-05-02 12:00 | -7876.5 | 6.108 | 44.6972 | 59.8258 | -2308.3743 |  | 468 | 1684800 | 33220800 | 64756800 | 96292800
2021-05-03 13:00 | -7705.97 | 6.108 | 44.8438 | 59.8258 | -2258.3969 |  | 469 | 1688400 | 33224400 | 64760400 | 96296400
2021-05-04 14:00 | -7691.79 | 6.108 | 44.854 | 59.8258 | -2254.2411 |  | 470 | 1692000 | 33228000 | 64764000 | 96300000
2021-05-05 15:00 | -7465.49 | 6.108 | 45.0279 | 59.8258 | -2187.9191 |  | 471 | 1695600 | 33231600 | 64767600 | 96303600
2021-05-06 16:00 | -7358.71 | 6.108 | 45.1326 | 59.8258 | -2156.625 |  | 472 | 1699200 | 33235200 | 64771200 | 96307200
2021-05-07 17:00 | -5985.12 | 6.108 | 46.1882 | 59.8258 | -1754.0655 |  | 473 | 1702800 | 33238800 | 64774800 | 96310800
2021-05-08 18:00 | -6340.86 | 6.108 | 46.1132 | 59.8258 | -1858.3226 |  | 474 | 1706400 | 33242400 | 64778400 | 96314400
2021-05-09 19:00 | -6710.83 | 6.108 | 45.8916 | 59.8258 | -1966.7501 |  | 475 | 1710000 | 33246000 | 64782000 | 96318000
2021-05-10 20:00 | -6993.69 | 6.108 | 45.6595 | 59.8258 | -2049.6482 |  | 476 | 1713600 | 33249600 | 64785600 | 96321600
2021-05-11 21:00 | -7193.08 | 6.108 | 45.5017 | 59.8258 | -2108.0837 |  | 477 | 1717200 | 33253200 | 64789200 | 96325200
2021-05-12 22:00 | -7332.29 | 6.108 | 45.3921 | 59.8258 | -2148.8821 |  | 478 | 1720800 | 33256800 | 64792800 | 96328800
2021-05-13 23:00 | -7526.02 | 6.108 | 45.219 | 59.8258 | -2205.6587 |  | 479 | 1724400 | 33260400 | 64796400 | 96332400
2021-05-15 | -8857.59 | 6.108 | 44.1857 | 59.8258 | -2595.9034 |  | 480 | 1728000 | 33264000 | 64800000 | 96336000
2021-05-16 01:00 | -9066.39 | 6.108 | 43.8365 | 59.8258 | -2657.0966 |  | 481 | 1731600 | 33267600 | 64803600 | 96339600
2021-05-17 02:00 | -9219.73 | 6.108 | 43.5945 | 59.8258 | -2702.0361 |  | 482 | 1735200 | 33271200 | 64807200 | 96343200
2021-05-18 03:00 | -9273.67 | 6.108 | 43.4672 | 59.8258 | -2717.8444 |  | 483 | 1738800 | 33274800 | 64810800 | 96346800
2021-05-19 04:00 | -9444.67 | 6.108 | 43.2619 | 59.8258 | -2767.9595 |  | 484 | 1742400 | 33278400 | 64814400 | 96350400
2021-05-20 05:00 | -9625.78 | 6.108 | 43.0212 | 59.8258 | -2821.0376 |  | 485 | 1746000 | 33282000 | 64818000 | 96354000
2021-05-21 06:00 | -9824.59 | 6.108 | 42.7863 | 59.8258 | -2879.3031 |  | 486 | 1749600 | 33285600 | 64821600 | 96357600
2021-05-22 07:00 | -9022.92 | 6.108 | 43.2996 | 59.8258 | -2644.3568 |  | 487 | 1753200 | 33289200 | 64825200 | 96361200
2021-05-23 08:00 | -7895.01 | 6.108 | 44.1912 | 59.8258 | -2313.799 |  | 488 | 1756800 | 33292800 | 64828800 | 96364800
2021-05-24 09:00 | -7763.83 | 6.108 | 44.4552 | 59.8258 | -2275.354 |  | 489 | 1760400 | 33296400 | 64832400 | 96368400
2021-05-25 10:00 | -6924.61 | 6.108 | 45.1735 | 59.8258 | -2029.4029 |  | 490 | 1764000 | 33300000 | 64836000 | 96372000
2021-05-26 11:00 | -6624.34 | 6.108 | 45.5532 | 59.8258 | -1941.4024 |  | 491 | 1767600 | 33303600 | 64839600 | 96375600
2021-05-27 12:00 | -6520.71 | 6.108 | 45.7829 | 59.8258 | -1911.0315 |  | 492 | 1771200 | 33307200 | 64843200 | 96379200
2021-05-28 13:00 | -6050.65 | 6.108 | 46.2378 | 59.8258 | -1773.2705 |  | 493 | 1774800 | 33310800 | 64846800 | 96382800
2021-05-29 14:00 | -5134.91 | 6.108 | 47.0531 | 59.8258 | -1504.8936 |  | 494 | 1778400 | 33314400 | 64850400 | 96386400
2021-05-30 15:00 | -3883.01 | 6.108 | 48.2149 | 59.8258 | -1137.9979 |  | 495 | 1782000 | 33318000 | 64854000 | 96390000
2021-05-31 16:00 | -4711.67 | 6.108 | 47.8973 | 59.8258 | -1380.8542 |  | 496 | 1785600 | 33321600 | 64857600 | 96393600
2021-06-01 17:00 | -3856.47 | 6.108 | 48.6132 | 59.8258 | -1130.2198 |  | 497 | 1789200 | 33325200 | 64861200 | 96397200
2021-06-02 18:00 | -4971.32 | 6.108 | 47.9754 | 59.8258 | -1456.9501 |  | 498 | 1792800 | 33328800 | 64864800 | 96400800
2021-06-03 19:00 | -5656.61 | 6.108 | 47.4701 | 59.8258 | -1657.7887 |  | 499 | 1796400 | 33332400 | 64868400 | 96404400
2021-06-04 20:00 | -6191.45 | 6.108 | 46.9877 | 59.8258 | -1814.5349 |  | 500 | 1800000 | 33336000 | 64872000 | 96408000
2021-06-05 21:00 | -6595.18 | 6.108 | 46.5839 | 59.8258 | -1932.8565 |  | 501 | 1803600 | 33339600 | 64875600 | 96411600
2021-06-06 22:00 | -7052.13 | 6.108 | 46.1513 | 59.8258 | -2066.7753 |  | 502 | 1807200 | 33343200 | 64879200 | 96415200
2021-06-07 23:00 | -7537.5 | 6.108 | 45.6586 | 59.8258 | -2209.0232 |  | 503 | 1810800 | 33346800 | 64882800 | 96418800
2021-06-09 | -8956.5 | 6.108 | 44.4719 | 59.8258 | -2624.891 |  | 504 | 1814400 | 33350400 | 64886400 | 96422400
2021-06-10 01:00 | -9259.16 | 6.108 | 43.9839 | 59.8258 | -2713.5919 |  | 505 | 1818000 | 33354000 | 64890000 | 96426000
2021-06-11 02:00 | -9497.1 | 6.108 | 43.6074 | 59.8258 | -2783.3253 |  | 506 | 1821600 | 33357600 | 64893600 | 96429600
2021-06-12 03:00 | -9560.37 | 6.108 | 43.3918 | 59.8258 | -2801.8679 |  | 507 | 1825200 | 33361200 | 64897200 | 96433200
2021-06-13 04:00 | -9692.63 | 6.108 | 43.1612 | 59.8258 | -2840.6294 |  | 508 | 1828800 | 33364800 | 64900800 | 96436800
2021-06-14 05:00 | -9663.85 | 6.108 | 43.0478 | 59.8258 | -2832.1949 |  | 509 | 1832400 | 33368400 | 64904400 | 96440400
2021-06-15 06:00 | -9520.53 | 6.108 | 43.081 | 59.8258 | -2790.1919 |  | 510 | 1836000 | 33372000 | 64908000 | 96444000
2021-06-16 07:00 | -9288.1 | 6.108 | 43.212 | 59.8258 | -2722.0734 |  | 511 | 1839600 | 33375600 | 64911600 | 96447600
2021-06-17 08:00 | -8422.28 | 6.108 | 43.8449 | 59.8258 | -2468.3266 |  | 512 | 1843200 | 33379200 | 64915200 | 96451200
2021-06-18 09:00 | -7649.51 | 6.108 | 44.5157 | 59.8258 | -2241.8501 |  | 513 | 1846800 | 33382800 | 64918800 | 96454800
2021-06-19 10:00 | -6886.94 | 6.108 | 45.2266 | 59.8258 | -2018.3629 |  | 514 | 1850400 | 33386400 | 64922400 | 96458400
2021-06-20 11:00 | -6030.73 | 6.108 | 46.0366 | 59.8258 | -1767.4325 |  | 515 | 1854000 | 33390000 | 64926000 | 96462000
2021-06-21 12:00 | -5604.55 | 6.108 | 46.5783 | 59.8258 | -1642.5315 |  | 516 | 1857600 | 33393600 | 64929600 | 96465600
2021-06-22 13:00 | -4864.87 | 6.108 | 47.3316 | 59.8258 | -1425.7527 |  | 517 | 1861200 | 33397200 | 64933200 | 96469200
2021-06-23 14:00 | -3775.09 | 6.108 | 48.3721 | 59.8258 | -1106.3697 |  | 518 | 1864800 | 33400800 | 64936800 | 96472800
2021-06-24 15:00 | -2815.16 | 6.108 | 49.382 | 59.8258 | -825.042 |  | 519 | 1868400 | 33404400 | 64940400 | 96476400
2021-06-25 16:00 | -2486.93 | 6.108 | 49.9499 | 59.8258 | -728.8472 |  | 520 | 1872000 | 33408000 | 64944000 | 96480000
2021-06-26 17:00 | -3442.88 | 6.108 | 49.4796 | 59.8258 | -1009.0085 |  | 521 | 1875600 | 33411600 | 64947600 | 96483600
2021-06-27 18:00 | -4444.67 | 6.108 | 48.7898 | 59.8258 | -1302.6042 |  | 522 | 1879200 | 33415200 | 64951200 | 96487200
2021-06-28 19:00 | -5396.35 | 6.108 | 48.0305 | 59.8258 | -1581.5141 |  | 523 | 1882800 | 33418800 | 64954800 | 96490800
2021-06-29 20:00 | -6125.02 | 6.108 | 47.3685 | 59.8258 | -1795.0662 |  | 524 | 1886400 | 33422400 | 64958400 | 96494400
2021-06-30 21:00 | -7412.44 | 6.108 | 46.2494 | 59.8258 | -2172.3717 |  | 525 | 1890000 | 33426000 | 64962000 | 96498000
2021-07-01 22:00 | -7725.65 | 6.108 | 45.7469 | 59.8258 | -2264.1645 |  | 526 | 1893600 | 33429600 | 64965600 | 96501600
2021-07-02 23:00 | -8346.84 | 6.108 | 45.0875 | 59.8258 | -2446.2173 |  | 527 | 1897200 | 33433200 | 64969200 | 96505200
2021-07-04 | -8465.94 | 6.108 | 44.8145 | 59.8258 | -2481.1221 |  | 528 | 1900800 | 33436800 | 64972800 | 96508800
2021-07-05 01:00 | -8666.53 | 6.108 | 44.5275 | 59.8258 | -2539.9092 |  | 529 | 1904400 | 33440400 | 64976400 | 96512400
2021-07-06 02:00 | -8984.93 | 6.108 | 44.1585 | 59.8258 | -2633.223 |  | 530 | 1908000 | 33444000 | 64980000 | 96516000
2021-07-07 03:00 | -9054.51 | 6.108 | 43.9677 | 59.8258 | -2653.6149 |  | 531 | 1911600 | 33447600 | 64983600 | 96519600
2021-07-08 04:00 | -9009.61 | 6.108 | 43.8841 | 59.8258 | -2640.456 |  | 532 | 1915200 | 33451200 | 64987200 | 96523200
2021-07-09 05:00 | -8897.24 | 6.108 | 43.8984 | 59.8258 | -2607.5236 |  | 533 | 1918800 | 33454800 | 64990800 | 96526800
2021-07-10 06:00 | -8573.73 | 6.108 | 44.1008 | 59.8258 | -2512.7122 |  | 534 | 1922400 | 33458400 | 64994400 | 96530400
2021-07-11 07:00 | -8328.48 | 6.108 | 44.2918 | 59.8258 | -2440.8365 |  | 535 | 1926000 | 33462000 | 64998000 | 96534000
2021-07-12 08:00 | -7336.87 | 6.108 | 45.0608 | 59.8258 | -2150.2243 |  | 536 | 1929600 | 33465600 | 65001600 | 96537600
2021-07-13 09:00 | -6388.89 | 6.108 | 45.9184 | 59.8258 | -1872.3988 |  | 537 | 1933200 | 33469200 | 65005200 | 96541200
2021-07-14 10:00 | -4597.72 | 6.108 | 47.4663 | 59.8258 | -1347.4587 |  | 538 | 1936800 | 33472800 | 65008800 | 96544800
2021-07-15 11:00 | -3205.61 | 6.108 | 48.8658 | 59.8258 | -939.4716 |  | 539 | 1940400 | 33476400 | 65012400 | 96548400
2021-07-16 12:00 | -1786.81 | 5.8902 | 50.2778 | 59.8258 | -523.6623 |  | 540 | 1944000 | 33480000 | 65016000 | 96552000
2021-07-17 13:00 | -1320.18 | 4.2682 | 50.6885 | 59.8258 | -386.9066 |  | 541 | 1947600 | 33483600 | 65019600 | 96555600
2021-07-18 14:00 | -918.782 | 3.1275 | 51.1052 | 59.8258 | -269.2684 |  | 542 | 1951200 | 33487200 | 65023200 | 96559200
2021-07-19 15:00 | -809.726 | 2.8862 | 51.4642 | 59.8258 | -237.3073 |  | 543 | 1954800 | 33490800 | 65026800 | 96562800
2021-07-20 16:00 | -841.407 | 3.0034 | 51.6995 | 59.8258 | -246.592 |  | 544 | 1958400 | 33494400 | 65030400 | 96566400
2021-07-21 17:00 | -1329.34 | 4.5413 | 51.8218 | 59.8258 | -389.5911 |  | 545 | 1962000 | 33498000 | 65034000 | 96570000
2021-07-22 18:00 | -1567.61 | 5.1397 | 51.8492 | 59.8258 | -459.4211 |  | 546 | 1965600 | 33501600 | 65037600 | 96573600
2021-07-23 19:00 | -2019.16 | 6.108 | 51.808 | 59.8258 | -591.7574 |  | 547 | 1969200 | 33505200 | 65041200 | 96577200
2021-07-24 20:00 | -2425.43 | 6.108 | 51.5325 | 59.8258 | -710.8234 |  | 548 | 1972800 | 33508800 | 65044800 | 96580800
2021-07-25 21:00 | -3324.73 | 6.108 | 50.8624 | 59.8258 | -974.3822 |  | 549 | 1976400 | 33512400 | 65048400 | 96584400
2021-07-26 22:00 | -3625 | 6.108 | 50.5405 | 59.8258 | -1062.3826 |  | 550 | 1980000 | 33516000 | 65052000 | 96588000
2021-07-27 23:00 | -4539.44 | 6.108 | 49.7836 | 59.8258 | -1330.3785 |  | 551 | 1983600 | 33519600 | 65055600 | 96591600
2021-07-29 | -4781.14 | 6.108 | 49.4494 | 59.8258 | -1401.2138 |  | 552 | 1987200 | 33523200 | 65059200 | 96595200
2021-07-30 01:00 | -4942.67 | 6.108 | 49.2128 | 59.8258 | -1448.5536 |  | 553 | 1990800 | 33526800 | 65062800 | 96598800
2021-07-31 02:00 | -5004.31 | 6.108 | 49.0824 | 59.8258 | -1466.6185 |  | 554 | 1994400 | 33530400 | 65066400 | 96602400
2021-08-01 03:00 | -5031.56 | 6.108 | 49.007 | 59.8258 | -1474.6047 |  | 555 | 1998000 | 33534000 | 65070000 | 96606000
2021-08-02 04:00 | -4850.75 | 6.108 | 49.1004 | 59.8258 | -1421.6145 |  | 556 | 2001600 | 33537600 | 65073600 | 96609600
2021-08-03 05:00 | -4548.43 | 6.108 | 49.3393 | 59.8258 | -1333.0132 |  | 557 | 2005200 | 33541200 | 65077200 | 96613200
2021-08-04 06:00 | -4006.59 | 6.108 | 49.7957 | 59.8258 | -1174.2156 |  | 558 | 2008800 | 33544800 | 65080800 | 96616800
2021-08-05 07:00 | -3832.01 | 6.108 | 50.0333 | 59.8258 | -1123.0513 |  | 559 | 2012400 | 33548400 | 65084400 | 96620400
2021-08-06 08:00 | -3655.44 | 6.108 | 50.2521 | 59.8258 | -1071.3037 |  | 560 | 2016000 | 33552000 | 65088000 | 96624000
2021-08-07 09:00 | -3973.58 | 6.108 | 50.1002 | 59.8258 | -1164.5413 |  | 561 | 2019600 | 33555600 | 65091600 | 96627600
2021-08-08 10:00 | -3428.72 | 6.108 | 50.5222 | 59.8258 | -1004.8586 |  | 562 | 2023200 | 33559200 | 65095200 | 96631200
2021-08-09 11:00 | -3044.21 | 6.108 | 50.9034 | 59.8258 | -892.1699 |  | 563 | 2026800 | 33562800 | 65098800 | 96634800
2021-08-10 12:00 | -2824.4 | 6.108 | 51.1734 | 59.8258 | -827.7499 |  | 564 | 2030400 | 33566400 | 65102400 | 96638400
2021-08-11 13:00 | -2666.24 | 6.108 | 51.3793 | 59.8258 | -781.3978 |  | 565 | 2034000 | 33570000 | 65106000 | 96642000
2021-08-12 14:00 | -2419.74 | 6.108 | 51.6386 | 59.8258 | -709.1558 |  | 566 | 2037600 | 33573600 | 65109600 | 96645600
2021-08-13 15:00 | -2193.84 | 6.108 | 51.9035 | 59.8258 | -642.951 |  | 567 | 2041200 | 33577200 | 65113200 | 96649200
2021-08-14 16:00 | -1446.79 | 4.5723 | 52.1881 | 59.8258 | -424.0123 |  | 568 | 2044800 | 33580800 | 65116800 | 96652800
2021-08-15 17:00 | -1250.91 | 4.09 | 52.3994 | 59.8258 | -366.6055 |  | 569 | 2048400 | 33584400 | 65120400 | 96656400
2021-08-16 18:00 | -1118.04 | 3.7132 | 52.5541 | 59.8258 | -327.6652 |  | 570 | 2052000 | 33588000 | 65124000 | 96660000
2021-08-17 19:00 | -1601.7 | 5.2765 | 52.6607 | 59.8258 | -469.4119 |  | 571 | 2055600 | 33591600 | 65127600 | 96663600
2021-08-18 20:00 | -1939.89 | 6.108 | 52.6301 | 59.8258 | -568.5256 |  | 572 | 2059200 | 33595200 | 65131200 | 96667200
2021-08-19 21:00 | -3054.92 | 6.108 | 51.8121 | 59.8258 | -895.3087 |  | 573 | 2062800 | 33598800 | 65134800 | 96670800
2021-08-20 22:00 | -3345.34 | 6.108 | 51.4745 | 59.8258 | -980.4224 |  | 574 | 2066400 | 33602400 | 65138400 | 96674400
2021-08-21 23:00 | -4186.7 | 6.108 | 50.7587 | 59.8258 | -1227.0006 |  | 575 | 2070000 | 33606000 | 65142000 | 96678000
2021-08-23 | -4384.09 | 6.108 | 50.4633 | 59.8258 | -1284.8499 |  | 576 | 2073600 | 33609600 | 65145600 | 96681600
2021-08-24 01:00 | -4480.24 | 6.108 | 50.2867 | 59.8258 | -1313.0287 |  | 577 | 2077200 | 33613200 | 65149200 | 96685200
2021-08-25 02:00 | -4525.61 | 6.108 | 50.1821 | 59.8258 | -1326.3254 |  | 578 | 2080800 | 33616800 | 65152800 | 96688800
2021-08-26 03:00 | -4483.67 | 6.108 | 50.1727 | 59.8258 | -1314.034 |  | 579 | 2084400 | 33620400 | 65156400 | 96692400
2021-08-27 04:00 | -4372.05 | 6.108 | 50.2245 | 59.8258 | -1281.3214 |  | 580 | 2088000 | 33624000 | 65160000 | 96696000
2021-08-28 05:00 | -4233.56 | 6.108 | 50.3263 | 59.8258 | -1240.734 |  | 581 | 2091600 | 33627600 | 65163600 | 96699600
2021-08-29 06:00 | -3852.51 | 6.108 | 50.6204 | 59.8258 | -1129.0592 |  | 582 | 2095200 | 33631200 | 65167200 | 96703200
2021-08-30 07:00 | -3720.48 | 6.108 | 50.7733 | 59.8258 | -1090.3651 |  | 583 | 2098800 | 33634800 | 65170800 | 96706800
2021-08-31 08:00 | -3576.72 | 6.108 | 50.9257 | 59.8258 | -1048.2332 |  | 584 | 2102400 | 33638400 | 65174400 | 96710400
2021-09-01 09:00 | -3768.86 | 6.108 | 50.8358 | 59.8258 | -1104.5438 |  | 585 | 2106000 | 33642000 | 65178000 | 96714000
2021-09-02 10:00 | -3100.44 | 6.108 | 51.3423 | 59.8258 | -908.6493 |  | 586 | 2109600 | 33645600 | 65181600 | 96717600
2021-09-03 11:00 | -2537.1 | 6.108 | 51.867 | 59.8258 | -743.5506 |  | 587 | 2113200 | 33649200 | 65185200 | 96721200
2021-09-04 12:00 | -1462.19 | 4.6205 | 52.4524 | 59.8258 | -428.5256 |  | 588 | 2116800 | 33652800 | 65188800 | 96724800
2021-09-05 13:00 | -1575.96 | 5.0947 | 52.7071 | 59.8258 | -461.8683 |  | 589 | 2120400 | 33656400 | 65192400 | 96728400
2021-09-06 14:00 | -1460.25 | 4.6715 | 52.8104 | 59.8258 | -427.957 |  | 590 | 2124000 | 33660000 | 65196000 | 96732000
2021-09-07 15:00 | -1524.11 | 4.9107 | 52.9253 | 59.8258 | -446.6725 |  | 591 | 2127600 | 33663600 | 65199600 | 96735600
2021-09-08 16:00 | -983.288 | 3.1814 | 53.002 | 59.8258 | -288.1733 |  | 592 | 2131200 | 33667200 | 65203200 | 96739200
2021-09-09 17:00 | -685.671 | 2.4268 | 53.2552 | 59.8258 | -200.9503 |  | 593 | 2134800 | 33670800 | 65206800 | 96742800
2021-09-10 18:00 | -529.338 | 2.0151 | 53.4636 | 59.8258 | -155.1337 |  | 594 | 2138400 | 33674400 | 65210400 | 96746400
2021-09-11 19:00 | -783.257 | 2.8387 | 53.5143 | 59.8258 | -229.55 |  | 595 | 2142000 | 33678000 | 65214000 | 96750000
2021-09-12 20:00 | -869.056 | 3.0215 | 53.5173 | 59.8258 | -254.6952 |  | 596 | 2145600 | 33681600 | 65217600 | 96753600
2021-09-13 21:00 | -1540.34 | 5.0922 | 53.52 | 59.8258 | -451.4291 |  | 597 | 2149200 | 33685200 | 65221200 | 96757200
2021-09-14 22:00 | -1869.15 | 5.9153 | 53.4328 | 59.8258 | -547.7938 |  | 598 | 2152800 | 33688800 | 65224800 | 96760800
2021-09-15 23:00 | -2887.96 | 6.108 | 52.6807 | 59.8258 | -846.3775 |  | 599 | 2156400 | 33692400 | 65228400 | 96764400
2021-09-17 | -3248.83 | 6.108 | 52.2657 | 59.8258 | -952.1381 |  | 600 | 2160000 | 33696000 | 65232000 | 96768000
2021-09-18 01:00 | -3470.9 | 6.108 | 51.9837 | 59.8258 | -1017.2204 |  | 601 | 2163600 | 33699600 | 65235600 | 96771600
2021-09-19 02:00 | -3561.69 | 6.108 | 51.8269 | 59.8258 | -1043.8283 |  | 602 | 2167200 | 33703200 | 65239200 | 96775200
2021-09-20 03:00 | -3627.56 | 6.108 | 51.7175 | 59.8258 | -1063.1329 |  | 603 | 2170800 | 33706800 | 65242800 | 96778800
2021-09-21 04:00 | -3450.69 | 6.108 | 51.7944 | 59.8258 | -1011.2974 |  | 604 | 2174400 | 33710400 | 65246400 | 96782400
2021-09-22 05:00 | -3278.49 | 6.108 | 51.9173 | 59.8258 | -960.8306 |  | 605 | 2178000 | 33714000 | 65250000 | 96786000
2021-09-23 06:00 | -2761.94 | 6.108 | 52.3165 | 59.8258 | -809.4447 |  | 606 | 2181600 | 33717600 | 65253600 | 96789600
2021-09-24 07:00 | -2746.3 | 6.108 | 52.4013 | 59.8258 | -804.8611 |  | 607 | 2185200 | 33721200 | 65257200 | 96793200
2021-09-25 08:00 | -2670.84 | 6.108 | 52.4967 | 59.8258 | -782.7459 |  | 608 | 2188800 | 33724800 | 65260800 | 96796800
2021-09-26 09:00 | -3171.8 | 6.108 | 52.1607 | 59.8258 | -929.5628 |  | 609 | 2192400 | 33728400 | 65264400 | 96800400
2021-09-27 10:00 | -2738.76 | 6.108 | 52.443 | 59.8258 | -802.6513 |  | 610 | 2196000 | 33732000 | 65268000 | 96804000
2021-09-28 11:00 | -2127.71 | 6.108 | 52.9449 | 59.8258 | -623.5702 |  | 611 | 2199600 | 33735600 | 65271600 | 96807600
2021-09-29 12:00 | -1724.91 | 5.3821 | 53.175 | 59.8258 | -505.5212 |  | 612 | 2203200 | 33739200 | 65275200 | 96811200
2021-09-30 13:00 | -1378.39 | 4.3524 | 53.3005 | 59.8258 | -403.9662 |  | 613 | 2206800 | 33742800 | 65278800 | 96814800
2021-10-01 14:00 | -1245.21 | 4.0368 | 53.4468 | 59.8258 | -364.935 |  | 614 | 2210400 | 33746400 | 65282400 | 96818400
2021-10-02 15:00 | -1322.65 | 4.3051 | 53.557 | 59.8258 | -387.6305 |  | 615 | 2214000 | 33750000 | 65286000 | 96822000
2021-10-03 16:00 | -988.579 | 3.2352 | 53.6195 | 59.8258 | -289.7239 |  | 616 | 2217600 | 33753600 | 65289600 | 96825600
2021-10-04 17:00 | -1259.46 | 4.1815 | 53.7274 | 59.8258 | -369.1113 |  | 617 | 2221200 | 33757200 | 65293200 | 96829200
2021-10-05 18:00 | -1859.46 | 5.9583 | 53.6991 | 59.8258 | -544.9539 |  | 618 | 2224800 | 33760800 | 65296800 | 96832800
2021-10-06 19:00 | -2976.48 | 6.108 | 52.8349 | 59.8258 | -872.3202 |  | 619 | 2228400 | 33764400 | 65300400 | 96836400
2021-10-07 20:00 | -3731.12 | 6.108 | 52.096 | 59.8258 | -1093.4833 |  | 620 | 2232000 | 33768000 | 65304000 | 96840000
2021-10-08 21:00 | -5213.46 | 6.108 | 50.8094 | 59.8258 | -1527.9143 |  | 621 | 2235600 | 33771600 | 65307600 | 96843600
2021-10-09 22:00 | -5614.81 | 6.108 | 50.2015 | 59.8258 | -1645.5384 |  | 622 | 2239200 | 33775200 | 65311200 | 96847200
2021-10-10 23:00 | -6641.29 | 6.108 | 49.1902 | 59.8258 | -1946.37 |  | 623 | 2242800 | 33778800 | 65314800 | 96850800
2021-10-12 | -7125.37 | 6.108 | 48.5303 | 59.8258 | -2088.2398 |  | 624 | 2246400 | 33782400 | 65318400 | 96854400
2021-10-13 01:00 | -7354.75 | 6.108 | 48.0918 | 59.8258 | -2155.4645 |  | 625 | 2250000 | 33786000 | 65322000 | 96858000
2021-10-14 02:00 | -7453.11 | 6.108 | 47.8007 | 59.8258 | -2184.2909 |  | 626 | 2253600 | 33789600 | 65325600 | 96861600
2021-10-15 03:00 | -7556.89 | 6.108 | 47.5571 | 59.8258 | -2214.7058 |  | 627 | 2257200 | 33793200 | 65329200 | 96865200
2021-10-16 04:00 | -7610.64 | 6.108 | 47.3543 | 59.8258 | -2230.4584 |  | 628 | 2260800 | 33796800 | 65332800 | 96868800
2021-10-17 05:00 | -7772.38 | 6.108 | 47.097 | 59.8258 | -2277.8597 |  | 629 | 2264400 | 33800400 | 65336400 | 96872400
2021-10-18 06:00 | -7774.75 | 6.108 | 46.9568 | 59.8258 | -2278.5543 |  | 630 | 2268000 | 33804000 | 65340000 | 96876000
2021-10-19 07:00 | -7066.98 | 6.108 | 47.3786 | 59.8258 | -2071.1274 |  | 631 | 2271600 | 33807600 | 65343600 | 96879600
2021-10-20 08:00 | -6817.68 | 6.108 | 47.5676 | 59.8258 | -1998.0648 |  | 632 | 2275200 | 33811200 | 65347200 | 96883200
2021-10-21 09:00 | -7579.57 | 6.108 | 47.0103 | 59.8258 | -2221.3527 |  | 633 | 2278800 | 33814800 | 65350800 | 96886800
2021-10-22 10:00 | -7232.46 | 6.108 | 47.1389 | 59.8258 | -2119.6248 |  | 634 | 2282400 | 33818400 | 65354400 | 96890400
2021-10-23 11:00 | -6872.75 | 6.108 | 47.3685 | 59.8258 | -2014.2042 |  | 635 | 2286000 | 33822000 | 65358000 | 96894000
2021-10-24 12:00 | -6487.12 | 6.108 | 47.6706 | 59.8258 | -1901.1872 |  | 636 | 2289600 | 33825600 | 65361600 | 96897600
2021-10-25 13:00 | -6381.93 | 6.108 | 47.7662 | 59.8258 | -1870.3591 |  | 637 | 2293200 | 33829200 | 65365200 | 96901200
2021-10-26 14:00 | -6486.96 | 6.108 | 47.677 | 59.8258 | -1901.1403 |  | 638 | 2296800 | 33832800 | 65368800 | 96904800
2021-10-27 15:00 | -6398 | 6.108 | 47.7194 | 59.8258 | -1875.0687 |  | 639 | 2300400 | 33836400 | 65372400 | 96908400
2021-10-28 16:00 | -6512.5 | 6.108 | 47.6124 | 59.8258 | -1908.6253 |  | 640 | 2304000 | 33840000 | 65376000 | 96912000
2021-10-29 17:00 | -5168.42 | 6.108 | 48.5792 | 59.8258 | -1514.7144 |  | 641 | 2307600 | 33843600 | 65379600 | 96915600
2021-10-30 18:00 | -5744.7 | 6.108 | 48.2872 | 59.8258 | -1683.6054 |  | 642 | 2311200 | 33847200 | 65383200 | 96919200
2021-10-31 19:00 | -6262.86 | 6.108 | 47.8824 | 59.8258 | -1835.4631 |  | 643 | 2314800 | 33850800 | 65386800 | 96922800
2021-11-01 20:00 | -6942.8 | 6.108 | 47.2761 | 59.8258 | -2034.7338 |  | 644 | 2318400 | 33854400 | 65390400 | 96926400
2021-11-02 21:00 | -7341.98 | 6.108 | 46.8558 | 59.8258 | -2151.7219 |  | 645 | 2322000 | 33858000 | 65394000 | 96930000
2021-11-03 22:00 | -7653.01 | 6.108 | 46.5066 | 59.8258 | -2242.8758 |  | 646 | 2325600 | 33861600 | 65397600 | 96933600
2021-11-04 23:00 | -7964.36 | 6.108 | 46.1371 | 59.8258 | -2334.1235 |  | 647 | 2329200 | 33865200 | 65401200 | 96937200
2021-11-06 | -9413.76 | 6.108 | 44.913 | 59.8258 | -2758.9007 |  | 648 | 2332800 | 33868800 | 65404800 | 96940800
2021-11-07 01:00 | -9712.45 | 6.108 | 44.3938 | 59.8258 | -2846.4381 |  | 649 | 2336400 | 33872400 | 65408400 | 96944400
2021-11-08 02:00 | -9713.05 | 6.108 | 44.1724 | 59.8258 | -2846.614 |  | 650 | 2340000 | 33876000 | 65412000 | 96948000
2021-11-09 03:00 | -9826.19 | 6.108 | 43.9432 | 59.8258 | -2879.772 |  | 651 | 2343600 | 33879600 | 65415600 | 96951600
2021-11-10 04:00 | -9975.33 | 6.108 | 43.6891 | 59.8258 | -2923.4806 |  | 652 | 2347200 | 33883200 | 65419200 | 96955200
2021-11-11 05:00 | -10168.5 | 6.108 | 43.3793 | 59.8258 | -2980.0932 |  | 653 | 2350800 | 33886800 | 65422800 | 96958800
2021-11-12 06:00 | -10286.7 | 6.108 | 43.149 | 59.8258 | -3014.7342 |  | 654 | 2354400 | 33890400 | 65426400 | 96962400
2021-11-13 07:00 | -9443.9 | 6.108 | 43.6515 | 59.8258 | -2767.7339 |  | 655 | 2358000 | 33894000 | 65430000 | 96966000
2021-11-14 08:00 | -8387.05 | 6.108 | 44.4531 | 59.8258 | -2458.0017 |  | 656 | 2361600 | 33897600 | 65433600 | 96969600
2021-11-15 09:00 | -7895.19 | 6.108 | 44.9443 | 59.8258 | -2313.8518 |  | 657 | 2365200 | 33901200 | 65437200 | 96973200
2021-11-16 10:00 | -6591.92 | 6.108 | 46.0252 | 59.8258 | -1931.901 |  | 658 | 2368800 | 33904800 | 65440800 | 96976800
2021-11-17 11:00 | -5097.94 | 6.108 | 47.3671 | 59.8258 | -1494.0587 |  | 659 | 2372400 | 33908400 | 65444400 | 96980400
2021-11-18 12:00 | -3971.1 | 6.108 | 48.5599 | 59.8258 | -1163.8145 |  | 660 | 2376000 | 33912000 | 65448000 | 96984000
2021-11-19 13:00 | -3437.97 | 6.108 | 49.3118 | 59.8258 | -1007.5695 |  | 661 | 2379600 | 33915600 | 65451600 | 96987600
2021-11-20 14:00 | -3227.35 | 6.108 | 49.7534 | 59.8258 | -945.8429 |  | 662 | 2383200 | 33919200 | 65455200 | 96991200
2021-11-21 15:00 | -3184.41 | 6.108 | 50.018 | 59.8258 | -933.2584 |  | 663 | 2386800 | 33922800 | 65458800 | 96994800
2021-11-22 16:00 | -3889.96 | 6.108 | 49.667 | 59.8258 | -1140.0347 |  | 664 | 2390400 | 33926400 | 65462400 | 96998400
2021-11-23 17:00 | -3535.13 | 6.108 | 49.9647 | 59.8258 | -1036.0443 |  | 665 | 2394000 | 33930000 | 65466000 | 97002000
2021-11-24 18:00 | -4500.56 | 6.108 | 49.3408 | 59.8258 | -1318.9839 |  | 666 | 2397600 | 33933600 | 65469600 | 97005600
2021-11-25 19:00 | -5040.09 | 6.108 | 48.8925 | 59.8258 | -1477.1046 |  | 667 | 2401200 | 33937200 | 65473200 | 97009200
2021-11-26 20:00 | -5391.05 | 6.108 | 48.5449 | 59.8258 | -1579.9608 |  | 668 | 2404800 | 33940800 | 65476800 | 97012800
2021-11-27 21:00 | -5579.66 | 6.108 | 48.3373 | 59.8258 | -1635.2369 |  | 669 | 2408400 | 33944400 | 65480400 | 97016400
2021-11-28 22:00 | -5807.55 | 6.108 | 48.118 | 59.8258 | -1702.0249 |  | 670 | 2412000 | 33948000 | 65484000 | 97020000
2021-11-29 23:00 | -5876.92 | 6.108 | 47.9903 | 59.8258 | -1722.3552 |  | 671 | 2415600 | 33951600 | 65487600 | 97023600
2021-12-01 | -7004.5 | 6.108 | 47.0978 | 59.8258 | -2052.8163 |  | 672 | 2419200 | 33955200 | 65491200 | 97027200
2021-12-02 01:00 | -7237.15 | 6.108 | 46.7418 | 59.8258 | -2120.9993 |  | 673 | 2422800 | 33958800 | 65494800 | 97030800
2021-12-03 02:00 | -7455.33 | 6.108 | 46.439 | 59.8258 | -2184.9415 |  | 674 | 2426400 | 33962400 | 65498400 | 97034400
2021-12-04 03:00 | -7563.58 | 6.108 | 46.2459 | 59.8258 | -2216.6665 |  | 675 | 2430000 | 33966000 | 65502000 | 97038000
2021-12-05 04:00 | -7569.82 | 6.108 | 46.1496 | 59.8258 | -2218.4952 |  | 676 | 2433600 | 33969600 | 65505600 | 97041600
2021-12-06 05:00 | -7568.56 | 6.108 | 46.071 | 59.8258 | -2218.126 |  | 677 | 2437200 | 33973200 | 65509200 | 97045200
2021-12-07 06:00 | -7284.78 | 6.108 | 46.2463 | 59.8258 | -2134.9583 |  | 678 | 2440800 | 33976800 | 65512800 | 97048800
2021-12-08 07:00 | -7049.92 | 6.108 | 46.428 | 59.8258 | -2066.1276 |  | 679 | 2444400 | 33980400 | 65516400 | 97052400
2021-12-09 08:00 | -6641.03 | 6.108 | 46.7577 | 59.8258 | -1946.2938 |  | 680 | 2448000 | 33984000 | 65520000 | 97056000
2021-12-10 09:00 | -6948.59 | 6.108 | 46.5861 | 59.8258 | -2036.4307 |  | 681 | 2451600 | 33987600 | 65523600 | 97059600
2021-12-11 10:00 | -6527.97 | 6.108 | 46.8799 | 59.8258 | -1913.1592 |  | 682 | 2455200 | 33991200 | 65527200 | 97063200
2021-12-12 11:00 | -5487.67 | 6.108 | 47.6917 | 59.8258 | -1608.2773 |  | 683 | 2458800 | 33994800 | 65530800 | 97066800
2021-12-13 12:00 | -4229.6 | 6.108 | 48.7938 | 59.8258 | -1239.5734 |  | 684 | 2462400 | 33998400 | 65534400 | 97070400
2021-12-14 13:00 | -4205.27 | 6.108 | 49.0609 | 59.8258 | -1232.443 |  | 685 | 2466000 | 34002000 | 65538000 | 97074000
2021-12-15 14:00 | -3577.23 | 6.108 | 49.6672 | 59.8258 | -1048.3826 |  | 686 | 2469600 | 34005600 | 65541600 | 97077600
2021-12-16 15:00 | -3108.96 | 6.108 | 50.2019 | 59.8258 | -911.1462 |  | 687 | 2473200 | 34009200 | 65545200 | 97081200
2021-12-17 16:00 | -2779.54 | 6.108 | 50.6542 | 59.8258 | -814.6028 |  | 688 | 2476800 | 34012800 | 65548800 | 97084800
2021-12-18 17:00 | -2974.67 | 6.108 | 50.6784 | 59.8258 | -871.7897 |  | 689 | 2480400 | 34016400 | 65552400 | 97088400
2021-12-19 18:00 | -3754.37 | 6.108 | 50.1779 | 59.8258 | -1100.2972 |  | 690 | 2484000 | 34020000 | 65556000 | 97092000
2021-12-20 19:00 | -4483.56 | 6.108 | 49.6098 | 59.8258 | -1314.0017 |  | 691 | 2487600 | 34023600 | 65559600 | 97095600
2021-12-21 20:00 | -5070.66 | 6.108 | 49.0847 | 59.8258 | -1486.0638 |  | 692 | 2491200 | 34027200 | 65563200 | 97099200
2021-12-22 21:00 | -6146.29 | 6.108 | 48.1768 | 59.8258 | -1801.2998 |  | 693 | 2494800 | 34030800 | 65566800 | 97102800
2021-12-23 22:00 | -6628.85 | 6.108 | 47.6151 | 59.8258 | -1942.7242 |  | 694 | 2498400 | 34034400 | 65570400 | 97106400
2021-12-24 23:00 | -7697.57 | 6.108 | 46.6245 | 59.8258 | -2255.9351 |  | 695 | 2502000 | 34038000 | 65574000 | 97110000
2021-12-26 | -8089.77 | 6.108 | 46.075 | 59.8258 | -2370.8775 |  | 696 | 2505600 | 34041600 | 65577600 | 97113600
2021-12-27 01:00 | -8379.46 | 6.108 | 45.6469 | 59.8258 | -2455.7773 |  | 697 | 2509200 | 34045200 | 65581200 | 97117200
2021-12-28 02:00 | -8584.81 | 6.108 | 45.3097 | 59.8258 | -2515.9595 |  | 698 | 2512800 | 34048800 | 65584800 | 97120800
2021-12-29 03:00 | -8723.52 | 6.108 | 45.0452 | 59.8258 | -2556.6113 |  | 699 | 2516400 | 34052400 | 65588400 | 97124400
2021-12-30 04:00 | -8606.95 | 6.108 | 44.9833 | 59.8258 | -2522.448 |  | 700 | 2520000 | 34056000 | 65592000 | 97128000
2021-12-31 05:00 | -8382.8 | 6.108 | 45.0612 | 59.8258 | -2456.7562 |  | 701 | 2523600 | 34059600 | 65595600 | 97131600
2022-01-01 06:00 | -7949.96 | 6.108 | 45.3412 | 59.8258 | -2329.9033 |  | 702 | 2527200 | 34063200 | 65599200 | 97135200
2022-01-02 07:00 | -7610.8 | 6.108 | 45.6045 | 59.8258 | -2230.5053 |  | 703 | 2530800 | 34066800 | 65602800 | 97138800
2022-01-03 08:00 | -6547.62 | 6.108 | 46.4315 | 59.8258 | -1918.918 |  | 704 | 2534400 | 34070400 | 65606400 | 97142400
2022-01-04 09:00 | -5537.97 | 6.108 | 47.3463 | 59.8258 | -1623.0188 |  | 705 | 2538000 | 34074000 | 65610000 | 97146000
2022-01-05 10:00 | -4031.07 | 6.108 | 48.6953 | 59.8258 | -1181.39 |  | 706 | 2541600 | 34077600 | 65613600 | 97149600
2022-01-06 11:00 | -2922.65 | 6.108 | 49.8513 | 59.8258 | -856.5442 |  | 707 | 2545200 | 34081200 | 65617200 | 97153200
2022-01-07 12:00 | -2360.99 | 6.108 | 50.61 | 59.8258 | -691.9379 |  | 708 | 2548800 | 34084800 | 65620800 | 97156800
2022-01-08 13:00 | -1874.19 | 6.0372 | 51.2498 | 59.8258 | -549.2709 |  | 709 | 2552400 | 34088400 | 65624400 | 97160400
2022-01-09 14:00 | -1330.58 | 4.2381 | 51.4916 | 59.8258 | -389.9545 |  | 710 | 2556000 | 34092000 | 65628000 | 97164000
2022-01-10 15:00 | -2013.5 | 6.108 | 51.6852 | 59.8258 | -590.0986 |  | 711 | 2559600 | 34095600 | 65631600 | 97167600
2022-01-11 16:00 | -2024.74 | 6.108 | 51.7621 | 59.8258 | -593.3927 |  | 712 | 2563200 | 34099200 | 65635200 | 97171200
2022-01-12 17:00 | -2482.46 | 6.108 | 51.4962 | 59.8258 | -727.5372 |  | 713 | 2566800 | 34102800 | 65638800 | 97174800
2022-01-13 18:00 | -2784.5 | 6.108 | 51.2996 | 59.8258 | -816.0564 |  | 714 | 2570400 | 34106400 | 65642400 | 97178400
2022-01-14 19:00 | -3587.53 | 6.108 | 50.7057 | 59.8258 | -1051.4013 |  | 715 | 2574000 | 34110000 | 65646000 | 97182000
2022-01-15 20:00 | -4276.96 | 6.108 | 50.1009 | 59.8258 | -1253.4532 |  | 716 | 2577600 | 34113600 | 65649600 | 97185600
2022-01-16 21:00 | -5522.1 | 6.108 | 49.0542 | 59.8258 | -1618.3678 |  | 717 | 2581200 | 34117200 | 65653200 | 97189200
2022-01-17 22:00 | -6135.68 | 6.108 | 48.3639 | 59.8258 | -1798.1903 |  | 718 | 2584800 | 34120800 | 65656800 | 97192800
2022-01-18 23:00 | -7211.04 | 6.108 | 47.3438 | 59.8258 | -2113.3472 |  | 719 | 2588400 | 34124400 | 65660400 | 97196400
2022-01-20 | -7744.09 | 6.108 | 46.6674 | 59.8258 | -2269.5687 |  | 720 | 2592000 | 34128000 | 65664000 | 97200000
2022-01-21 01:00 | -8075.52 | 6.108 | 46.1684 | 59.8258 | -2366.7013 |  | 721 | 2595600 | 34131600 | 65667600 | 97203600
2022-01-22 02:00 | -8371.61 | 6.108 | 45.7301 | 59.8258 | -2453.4767 |  | 722 | 2599200 | 34135200 | 65671200 | 97207200
2022-01-23 03:00 | -8561.35 | 6.108 | 45.4062 | 59.8258 | -2509.084 |  | 723 | 2602800 | 34138800 | 65674800 | 97210800
2022-01-24 04:00 | -8564.06 | 6.108 | 45.2392 | 59.8258 | -2509.8782 |  | 724 | 2606400 | 34142400 | 65678400 | 97214400
2022-01-25 05:00 | -8572.64 | 6.108 | 45.1178 | 59.8258 | -2512.3928 |  | 725 | 2610000 | 34146000 | 65682000 | 97218000
2022-01-26 06:00 | -8264.66 | 6.108 | 45.2525 | 59.8258 | -2422.1327 |  | 726 | 2613600 | 34149600 | 65685600 | 97221600
2022-01-27 07:00 | -7941.57 | 6.108 | 45.4549 | 59.8258 | -2327.4444 |  | 727 | 2617200 | 34153200 | 65689200 | 97225200
2022-01-28 08:00 | -7080.99 | 6.108 | 46.0948 | 59.8258 | -2075.2333 |  | 728 | 2620800 | 34156800 | 65692800 | 97228800
2022-01-29 09:00 | -5909.41 | 6.108 | 47.0721 | 59.8258 | -1731.8771 |  | 729 | 2624400 | 34160400 | 65696400 | 97232400
2022-01-30 10:00 | -4987.05 | 6.108 | 47.957 | 59.8258 | -1461.5601 |  | 730 | 2628000 | 34164000 | 65700000 | 97236000
2022-01-31 11:00 | -3792.35 | 6.108 | 49.0767 | 59.8258 | -1111.4281 |  | 731 | 2631600 | 34167600 | 65703600 | 97239600
2022-02-01 12:00 | -3668.27 | 6.108 | 49.453 | 59.8258 | -1075.0638 |  | 732 | 2635200 | 34171200 | 65707200 | 97243200
2022-02-02 13:00 | -3608.45 | 6.108 | 49.6903 | 59.8258 | -1057.5323 |  | 733 | 2638800 | 34174800 | 65710800 | 97246800
2022-02-03 14:00 | -3514.74 | 6.108 | 49.8917 | 59.8258 | -1030.0686 |  | 734 | 2642400 | 34178400 | 65714400 | 97250400
2022-02-04 15:00 | -3332.52 | 6.108 | 50.1426 | 59.8258 | -976.6652 |  | 735 | 2646000 | 34182000 | 65718000 | 97254000
2022-02-05 16:00 | -2668.69 | 6.108 | 50.7509 | 59.8258 | -782.1158 |  | 736 | 2649600 | 34185600 | 65721600 | 97257600
2022-02-06 17:00 | -2763.28 | 6.108 | 50.8418 | 59.8258 | -809.8374 |  | 737 | 2653200 | 34189200 | 65725200 | 97261200
2022-02-07 18:00 | -2847.03 | 6.108 | 50.8823 | 59.8258 | -834.3821 |  | 738 | 2656800 | 34192800 | 65728800 | 97264800
2022-02-08 19:00 | -3373.08 | 6.108 | 50.565 | 59.8258 | -988.5522 |  | 739 | 2660400 | 34196400 | 65732400 | 97268400
2022-02-09 20:00 | -3575.02 | 6.108 | 50.4215 | 59.8258 | -1047.7349 |  | 740 | 2664000 | 34200000 | 65736000 | 97272000
2022-02-10 21:00 | -4635.97 | 6.108 | 49.6328 | 59.8258 | -1358.6687 |  | 741 | 2667600 | 34203600 | 65739600 | 97275600
2022-02-11 22:00 | -5069.41 | 6.108 | 49.178 | 59.8258 | -1485.6974 |  | 742 | 2671200 | 34207200 | 65743200 | 97279200
2022-02-12 23:00 | -6007.56 | 6.108 | 48.3512 | 59.8258 | -1760.642 |  | 743 | 2674800 | 34210800 | 65746800 | 97282800
2022-02-14 | -6439.26 | 6.108 | 47.8437 | 59.8258 | -1887.1608 |  | 744 | 2678400 | 34214400 | 65750400 | 97286400
2022-02-15 01:00 | -6729.32 | 6.108 | 47.467 | 59.8258 | -1972.169 |  | 745 | 2682000 | 34218000 | 65754000 | 97290000
2022-02-16 02:00 | -6927.4 | 6.108 | 47.1827 | 59.8258 | -2030.2205 |  | 746 | 2685600 | 34221600 | 65757600 | 97293600
2022-02-17 03:00 | -7087.65 | 6.108 | 46.9552 | 59.8258 | -2077.1852 |  | 747 | 2689200 | 34225200 | 65761200 | 97297200
2022-02-18 04:00 | -6954.3 | 6.108 | 46.9498 | 59.8258 | -2038.1041 |  | 748 | 2692800 | 34228800 | 65764800 | 97300800
2022-02-19 05:00 | -7001.53 | 6.108 | 46.8654 | 59.8258 | -2051.9459 |  | 749 | 2696400 | 34232400 | 65768400 | 97304400
2022-02-20 06:00 | -6593.25 | 6.108 | 47.122 | 59.8258 | -1932.2908 |  | 750 | 2700000 | 34236000 | 65772000 | 97308000
2022-02-21 07:00 | -6786.4 | 6.108 | 46.9898 | 59.8258 | -1988.8975 |  | 751 | 2703600 | 34239600 | 65775600 | 97311600
2022-02-22 08:00 | -6634.78 | 6.108 | 47.0648 | 59.8258 | -1944.4621 |  | 752 | 2707200 | 34243200 | 65779200 | 97315200
2022-02-23 09:00 | -7019.75 | 6.108 | 46.7604 | 59.8258 | -2057.2856 |  | 753 | 2710800 | 34246800 | 65782800 | 97318800
2022-02-24 10:00 | -6959.85 | 6.108 | 46.7247 | 59.8258 | -2039.7307 |  | 754 | 2714400 | 34250400 | 65786400 | 97322400
2022-02-25 11:00 | -6794.71 | 6.108 | 46.7931 | 59.8258 | -1991.3329 |  | 755 | 2718000 | 34254000 | 65790000 | 97326000
2022-02-26 12:00 | -6436.93 | 6.108 | 47.0305 | 59.8258 | -1886.478 |  | 756 | 2721600 | 34257600 | 65793600 | 97329600
2022-02-27 13:00 | -6520.38 | 6.108 | 46.9792 | 59.8258 | -1910.9347 |  | 757 | 2725200 | 34261200 | 65797200 | 97333200
2022-02-28 14:00 | -6329.27 | 6.108 | 47.0922 | 59.8258 | -1854.9259 |  | 758 | 2728800 | 34264800 | 65800800 | 97336800
2022-03-01 15:00 | -6508.06 | 6.108 | 46.9576 | 59.8258 | -1907.3241 |  | 759 | 2732400 | 34268400 | 65804400 | 97340400
2022-03-02 16:00 | -5577.42 | 6.108 | 47.6176 | 59.8258 | -1634.5804 |  | 760 | 2736000 | 34272000 | 65808000 | 97344000
2022-03-03 17:00 | -5558.56 | 6.108 | 47.7229 | 59.8258 | -1629.0531 |  | 761 | 2739600 | 34275600 | 65811600 | 97347600
2022-03-04 18:00 | -5587.82 | 6.108 | 47.7361 | 59.8258 | -1637.6284 |  | 762 | 2743200 | 34279200 | 65815200 | 97351200
2022-03-05 19:00 | -5837.79 | 6.108 | 47.557 | 59.8258 | -1710.8874 |  | 763 | 2746800 | 34282800 | 65818800 | 97354800
2022-03-06 20:00 | -6441.31 | 6.108 | 47.0763 | 59.8258 | -1887.7616 |  | 764 | 2750400 | 34286400 | 65822400 | 97358400
2022-03-07 21:00 | -7436.83 | 6.108 | 46.2521 | 59.8258 | -2179.5197 |  | 765 | 2754000 | 34290000 | 65826000 | 97362000
2022-03-08 22:00 | -7613.3 | 6.108 | 45.9319 | 59.8258 | -2231.238 |  | 766 | 2757600 | 34293600 | 65829600 | 97365600
2022-03-09 23:00 | -8415.6 | 6.108 | 45.2028 | 59.8258 | -2466.3689 |  | 767 | 2761200 | 34297200 | 65833200 | 97369200
2022-03-11 | -8607.64 | 6.108 | 44.8692 | 59.8258 | -2522.6503 |  | 768 | 2764800 | 34300800 | 65836800 | 97372800
2022-03-12 01:00 | -8652.82 | 6.108 | 44.6828 | 59.8258 | -2535.8912 |  | 769 | 2768400 | 34304400 | 65840400 | 97376400
2022-03-13 02:00 | -8699.08 | 6.108 | 44.5426 | 59.8258 | -2549.4487 |  | 770 | 2772000 | 34308000 | 65844000 | 97380000
2022-03-14 03:00 | -8571.4 | 6.108 | 44.5628 | 59.8258 | -2512.0294 |  | 771 | 2775600 | 34311600 | 65847600 | 97383600
2022-03-15 04:00 | -8357.3 | 6.108 | 44.6628 | 59.8258 | -2449.2829 |  | 772 | 2779200 | 34315200 | 65851200 | 97387200
2022-03-16 05:00 | -8271.17 | 6.108 | 44.7088 | 59.8258 | -2424.0406 |  | 773 | 2782800 | 34318800 | 65854800 | 97390800
2022-03-17 06:00 | -7851.12 | 6.108 | 45.0017 | 59.8258 | -2300.9361 |  | 774 | 2786400 | 34322400 | 65858400 | 97394400
2022-03-18 07:00 | -7266.99 | 6.108 | 45.4678 | 59.8258 | -2129.7445 |  | 775 | 2790000 | 34326000 | 65862000 | 97398000
2022-03-19 08:00 | -7318.33 | 6.108 | 45.513 | 59.8258 | -2144.7908 |  | 776 | 2793600 | 34329600 | 65865600 | 97401600
2022-03-20 09:00 | -8036.92 | 6.108 | 45.0079 | 59.8258 | -2355.3887 |  | 777 | 2797200 | 34333200 | 65869200 | 97405200
2022-03-21 10:00 | -7549.57 | 6.108 | 45.2858 | 59.8258 | -2212.5606 |  | 778 | 2800800 | 34336800 | 65872800 | 97408800
2022-03-22 11:00 | -7365.14 | 6.108 | 45.4485 | 59.8258 | -2158.5095 |  | 779 | 2804400 | 34340400 | 65876400 | 97412400
2022-03-23 12:00 | -7118.39 | 6.108 | 45.6669 | 59.8258 | -2086.1942 |  | 780 | 2808000 | 34344000 | 65880000 | 97416000
2022-03-24 13:00 | -7666.8 | 6.108 | 45.2809 | 59.8258 | -2246.9173 |  | 781 | 2811600 | 34347600 | 65883600 | 97419600
2022-03-25 14:00 | -7803.9 | 6.108 | 45.1066 | 59.8258 | -2287.0973 |  | 782 | 2815200 | 34351200 | 65887200 | 97423200
2022-03-26 15:00 | -7640.27 | 6.108 | 45.1783 | 59.8258 | -2239.1421 |  | 783 | 2818800 | 34354800 | 65890800 | 97426800
2022-03-27 16:00 | -6796.03 | 6.108 | 45.7904 | 59.8258 | -1991.7198 |  | 784 | 2822400 | 34358400 | 65894400 | 97430400
2022-03-28 17:00 | -6830.38 | 6.108 | 45.8489 | 59.8258 | -2001.7868 |  | 785 | 2826000 | 34362000 | 65898000 | 97434000
2022-03-29 18:00 | -7030.64 | 6.108 | 45.7136 | 59.8258 | -2060.4772 |  | 786 | 2829600 | 34365600 | 65901600 | 97437600
2022-03-30 19:00 | -7745.56 | 6.108 | 45.1463 | 59.8258 | -2269.9996 |  | 787 | 2833200 | 34369200 | 65905200 | 97441200
2022-03-31 20:00 | -8112.82 | 6.108 | 44.7626 | 59.8258 | -2377.6328 |  | 788 | 2836800 | 34372800 | 65908800 | 97444800
2022-04-01 21:00 | -9274.59 | 6.108 | 43.7939 | 59.8258 | -2718.114 |  | 789 | 2840400 | 34376400 | 65912400 | 97448400
2022-04-02 22:00 | -9620.6 | 6.108 | 43.3015 | 59.8258 | -2819.5195 |  | 790 | 2844000 | 34380000 | 65916000 | 97452000
2022-04-03 23:00 | -10594 | 6.108 | 42.3782 | 59.8258 | -3104.7949 |  | 791 | 2847600 | 34383600 | 65919600 | 97455600
2022-04-05 | -11162.7 | 6.108 | 41.6885 | 59.8258 | -3271.4644 |  | 792 | 2851200 | 34387200 | 65923200 | 97459200
2022-04-06 01:00 | -11453.9 | 6.108 | 41.223 | 59.8258 | -3356.8067 |  | 793 | 2854800 | 34390800 | 65926800 | 97462800
2022-04-07 02:00 | -11585 | 6.108 | 40.9168 | 59.8258 | -3395.2283 |  | 794 | 2858400 | 34394400 | 65930400 | 97466400
2022-04-08 03:00 | -11818.8 | 6.108 | 40.5766 | 59.8258 | -3463.7484 |  | 795 | 2862000 | 34398000 | 65934000 | 97470000
2022-04-09 04:00 | -11652.8 | 6.108 | 40.5198 | 59.8258 | -3415.0986 |  | 796 | 2865600 | 34401600 | 65937600 | 97473600
2022-04-10 05:00 | -11670.8 | 6.108 | 40.3883 | 59.8258 | -3420.3738 |  | 797 | 2869200 | 34405200 | 65941200 | 97477200
2022-04-11 06:00 | -11693.2 | 6.108 | 40.2595 | 59.8258 | -3426.9386 |  | 798 | 2872800 | 34408800 | 65944800 | 97480800
2022-04-12 07:00 | -10819 | 6.108 | 40.8119 | 59.8258 | -3170.7359 |  | 799 | 2876400 | 34412400 | 65948400 | 97484400
2022-04-13 08:00 | -10251.3 | 6.108 | 41.2632 | 59.8258 | -3004.3595 |  | 800 | 2880000 | 34416000 | 65952000 | 97488000
2022-04-14 09:00 | -10748.7 | 6.108 | 40.9606 | 59.8258 | -3150.133 |  | 801 | 2883600 | 34419600 | 65955600 | 97491600
2022-04-15 10:00 | -10583.4 | 6.108 | 41.0172 | 59.8258 | -3101.6884 |  | 802 | 2887200 | 34423200 | 65959200 | 97495200
2022-04-16 11:00 | -9501.75 | 6.108 | 41.8071 | 59.8258 | -2784.688 |  | 803 | 2890800 | 34426800 | 65962800 | 97498800
2022-04-17 12:00 | -8983.7 | 6.108 | 42.3337 | 59.8258 | -2632.8626 |  | 804 | 2894400 | 34430400 | 65966400 | 97502400
2022-04-18 13:00 | -8608.78 | 6.108 | 42.7392 | 59.8258 | -2522.9844 |  | 805 | 2898000 | 34434000 | 65970000 | 97506000
2022-04-19 14:00 | -8282.14 | 6.108 | 43.0799 | 59.8258 | -2427.2556 |  | 806 | 2901600 | 34437600 | 65973600 | 97509600
2022-04-20 15:00 | -8268.91 | 6.108 | 43.2041 | 59.8258 | -2423.3783 |  | 807 | 2905200 | 34441200 | 65977200 | 97513200
2022-04-21 16:00 | -8209.33 | 6.108 | 43.3192 | 59.8258 | -2405.9171 |  | 808 | 2908800 | 34444800 | 65980800 | 97516800
2022-04-22 17:00 | -6737.96 | 6.108 | 44.4714 | 59.8258 | -1974.7011 |  | 809 | 2912400 | 34448400 | 65984400 | 97520400
2022-04-23 18:00 | -7539.19 | 6.108 | 44.1034 | 59.8258 | -2209.5185 |  | 810 | 2916000 | 34452000 | 65988000 | 97524000
2022-04-24 19:00 | -7856.46 | 6.108 | 43.8876 | 59.8258 | -2302.5011 |  | 811 | 2919600 | 34455600 | 65991600 | 97527600
2022-04-25 20:00 | -8252.91 | 6.108 | 43.5561 | 59.8258 | -2418.6892 |  | 812 | 2923200 | 34459200 | 65995200 | 97531200
2022-04-26 21:00 | -8542.62 | 6.108 | 43.3143 | 59.8258 | -2503.5948 |  | 813 | 2926800 | 34462800 | 65998800 | 97534800
2022-04-27 22:00 | -8657.17 | 6.108 | 43.1991 | 59.8258 | -2537.1661 |  | 814 | 2930400 | 34466400 | 66002400 | 97538400
2022-04-28 23:00 | -8605.52 | 6.108 | 43.1887 | 59.8258 | -2522.029 |  | 815 | 2934000 | 34470000 | 66006000 | 97542000
2022-04-30 | -9895.18 | 6.108 | 42.2088 | 59.8258 | -2899.991 |  | 816 | 2937600 | 34473600 | 66009600 | 97545600
2022-05-01 01:00 | -10188.1 | 6.108 | 41.8049 | 59.8258 | -2985.8374 |  | 817 | 2941200 | 34477200 | 66013200 | 97549200
2022-05-02 02:00 | -10337.6 | 6.108 | 41.5506 | 59.8258 | -3029.6515 |  | 818 | 2944800 | 34480800 | 66016800 | 97552800
2022-05-03 03:00 | -10715.8 | 6.108 | 41.1727 | 59.8258 | -3140.491 |  | 819 | 2948400 | 34484400 | 66020400 | 97556400
2022-05-04 04:00 | -10784.9 | 6.108 | 40.9942 | 59.8258 | -3160.7422 |  | 820 | 2952000 | 34488000 | 66024000 | 97560000
2022-05-05 05:00 | -10761.7 | 6.108 | 40.8857 | 59.8258 | -3153.9429 |  | 821 | 2955600 | 34491600 | 66027600 | 97563600
2022-05-06 06:00 | -10711.1 | 6.108 | 40.8554 | 59.8258 | -3139.1135 |  | 822 | 2959200 | 34495200 | 66031200 | 97567200
2022-05-07 07:00 | -9355.69 | 6.108 | 41.8211 | 59.8258 | -2741.8821 |  | 823 | 2962800 | 34498800 | 66034800 | 97570800
2022-05-08 08:00 | -9285.22 | 6.108 | 42.0066 | 59.8258 | -2721.2294 |  | 824 | 2966400 | 34502400 | 66038400 | 97574400
2022-05-09 09:00 | -9236.49 | 6.108 | 42.1175 | 59.8258 | -2706.948 |  | 825 | 2970000 | 34506000 | 66042000 | 97578000
2022-05-10 10:00 | -7327.48 | 6.108 | 43.5854 | 59.8258 | -2147.4724 |  | 826 | 2973600 | 34509600 | 66045600 | 97581600
2022-05-11 11:00 | -5367.72 | 6.108 | 45.3403 | 59.8258 | -1573.1234 |  | 827 | 2977200 | 34513200 | 66049200 | 97585200
2022-05-12 12:00 | -4629.28 | 6.108 | 46.3405 | 59.8258 | -1356.708 |  | 828 | 2980800 | 34516800 | 66052800 | 97588800
2022-05-13 13:00 | -3447.67 | 6.108 | 47.5665 | 59.8258 | -1010.4123 |  | 829 | 2984400 | 34520400 | 66056400 | 97592400
2022-05-14 14:00 | -2754.58 | 6.108 | 48.4757 | 59.8258 | -807.2877 |  | 830 | 2988000 | 34524000 | 66060000 | 97596000
2022-05-15 15:00 | -2430.82 | 6.108 | 49.1118 | 59.8258 | -712.403 |  | 831 | 2991600 | 34527600 | 66063600 | 97599600
2022-05-16 16:00 | -2664.55 | 6.108 | 49.2466 | 59.8258 | -780.9025 |  | 832 | 2995200 | 34531200 | 66067200 | 97603200
2022-05-17 17:00 | -2252.06 | 6.108 | 49.7377 | 59.8258 | -660.0136 |  | 833 | 2998800 | 34534800 | 66070800 | 97606800
2022-05-18 18:00 | -3871.96 | 6.108 | 48.7506 | 59.8258 | -1134.7595 |  | 834 | 3002400 | 34538400 | 66074400 | 97610400
2022-05-19 19:00 | -4916.34 | 6.108 | 47.9187 | 59.8258 | -1440.837 |  | 835 | 3006000 | 34542000 | 66078000 | 97614000
2022-05-20 20:00 | -5311.79 | 6.108 | 47.4966 | 59.8258 | -1556.732 |  | 836 | 3009600 | 34545600 | 66081600 | 97617600
2022-05-21 21:00 | -5915.55 | 6.108 | 46.9791 | 59.8258 | -1733.6766 |  | 837 | 3013200 | 34549200 | 66085200 | 97621200
2022-05-22 22:00 | -6061.58 | 6.108 | 46.7671 | 59.8258 | -1776.4737 |  | 838 | 3016800 | 34552800 | 66088800 | 97624800
2022-05-23 23:00 | -6478.8 | 6.108 | 46.3526 | 59.8258 | -1898.7488 |  | 839 | 3020400 | 34556400 | 66092400 | 97628400
2022-05-25 | -7479.47 | 6.108 | 45.51 | 59.8258 | -2192.0163 |  | 840 | 3024000 | 34560000 | 66096000 | 97632000
2022-05-26 01:00 | -7868.94 | 6.108 | 45.0305 | 59.8258 | -2306.1587 |  | 841 | 3027600 | 34563600 | 66099600 | 97635600
2022-05-27 02:00 | -7965.11 | 6.108 | 44.7938 | 59.8258 | -2334.3433 |  | 842 | 3031200 | 34567200 | 66103200 | 97639200
2022-05-28 03:00 | -7756.67 | 6.108 | 44.8439 | 59.8258 | -2273.2556 |  | 843 | 3034800 | 34570800 | 66106800 | 97642800
2022-05-29 04:00 | -7743.2 | 6.108 | 44.8014 | 59.8258 | -2269.3079 |  | 844 | 3038400 | 34574400 | 66110400 | 97646400
2022-05-30 05:00 | -7249.59 | 6.108 | 45.1181 | 59.8258 | -2124.6451 |  | 845 | 3042000 | 34578000 | 66114000 | 97650000
2022-05-31 06:00 | -7176.77 | 6.108 | 45.2195 | 59.8258 | -2103.3037 |  | 846 | 3045600 | 34581600 | 66117600 | 97653600
2022-06-01 07:00 | -7128.78 | 6.108 | 45.2928 | 59.8258 | -2089.2392 |  | 847 | 3049200 | 34585200 | 66121200 | 97657200
2022-06-02 08:00 | -7094.98 | 6.108 | 45.3443 | 59.8258 | -2079.3334 |  | 848 | 3052800 | 34588800 | 66124800 | 97660800
2022-06-03 09:00 | -7754.34 | 6.108 | 44.8772 | 59.8258 | -2272.5727 |  | 849 | 3056400 | 34592400 | 66128400 | 97664400
2022-06-04 10:00 | -7292.29 | 6.108 | 45.1472 | 59.8258 | -2137.1592 |  | 850 | 3060000 | 34596000 | 66132000 | 97668000
2022-06-05 11:00 | -6887.4 | 6.108 | 45.4539 | 59.8258 | -2018.4977 |  | 851 | 3063600 | 34599600 | 66135600 | 97671600
2022-06-06 12:00 | -6023.27 | 6.108 | 46.1605 | 59.8258 | -1765.2462 |  | 852 | 3067200 | 34603200 | 66139200 | 97675200
2022-06-07 13:00 | -5655.85 | 6.108 | 46.5684 | 59.8258 | -1657.566 |  | 853 | 3070800 | 34606800 | 66142800 | 97678800
2022-06-08 14:00 | -6131.35 | 6.108 | 46.3236 | 59.8258 | -1796.9213 |  | 854 | 3074400 | 34610400 | 66146400 | 97682400
2022-06-09 15:00 | -5454.93 | 6.108 | 46.8387 | 59.8258 | -1598.6822 |  | 855 | 3078000 | 34614000 | 66150000 | 97686000
2022-06-10 16:00 | -4973.81 | 6.108 | 47.3054 | 59.8258 | -1457.6798 |  | 856 | 3081600 | 34617600 | 66153600 | 97689600
2022-06-11 17:00 | -4891.13 | 6.108 | 47.494 | 59.8258 | -1433.4487 |  | 857 | 3085200 | 34621200 | 66157200 | 97693200
2022-06-12 18:00 | -4489.56 | 6.108 | 47.8743 | 59.8258 | -1315.7602 |  | 858 | 3088800 | 34624800 | 66160800 | 97696800
2022-06-13 19:00 | -5150.38 | 6.108 | 47.4893 | 59.8258 | -1509.4274 |  | 859 | 3092400 | 34628400 | 66164400 | 97700400
2022-06-14 20:00 | -5343.5 | 6.108 | 47.3533 | 59.8258 | -1566.0253 |  | 860 | 3096000 | 34632000 | 66168000 | 97704000
2022-06-15 21:00 | -5988.27 | 6.108 | 46.8739 | 59.8258 | -1754.9887 |  | 861 | 3099600 | 34635600 | 66171600 | 97707600
2022-06-16 22:00 | -6456.67 | 6.108 | 46.4569 | 59.8258 | -1892.2632 |  | 862 | 3103200 | 34639200 | 66175200 | 97711200
2022-06-17 23:00 | -7295.67 | 6.108 | 45.7376 | 59.8258 | -2138.1498 |  | 863 | 3106800 | 34642800 | 66178800 | 97714800
2022-06-19 | -7428.75 | 6.108 | 45.4741 | 59.8258 | -2177.1517 |  | 864 | 3110400 | 34646400 | 66182400 | 97718400
2022-06-20 01:00 | -7484.01 | 6.108 | 45.3305 | 59.8258 | -2193.3468 |  | 865 | 3114000 | 34650000 | 66186000 | 97722000
2022-06-21 02:00 | -7447.46 | 6.108 | 45.2964 | 59.8258 | -2182.6351 |  | 866 | 3117600 | 34653600 | 66189600 | 97725600
2022-06-22 03:00 | -7488.1 | 6.108 | 45.2241 | 59.8258 | -2194.5455 |  | 867 | 3121200 | 34657200 | 66193200 | 97729200
2022-06-23 04:00 | -7437.53 | 6.108 | 45.2195 | 59.8258 | -2179.7249 |  | 868 | 3124800 | 34660800 | 66196800 | 97732800
2022-06-24 05:00 | -7094.92 | 6.108 | 45.4582 | 59.8258 | -2079.3158 |  | 869 | 3128400 | 34664400 | 66200400 | 97736400
2022-06-25 06:00 | -6546.7 | 6.108 | 45.8948 | 59.8258 | -1918.6484 |  | 870 | 3132000 | 34668000 | 66204000 | 97740000
2022-06-26 07:00 | -6425.1 | 6.108 | 46.068 | 59.8258 | -1883.0109 |  | 871 | 3135600 | 34671600 | 66207600 | 97743600
2022-06-27 08:00 | -6539.18 | 6.108 | 46.0369 | 59.8258 | -1916.4445 |  | 872 | 3139200 | 34675200 | 66211200 | 97747200
2022-06-28 09:00 | -6746.65 | 6.108 | 45.9069 | 59.8258 | -1977.2479 |  | 873 | 3142800 | 34678800 | 66214800 | 97750800
2022-06-29 10:00 | -6475.52 | 6.108 | 46.105 | 59.8258 | -1897.7876 |  | 874 | 3146400 | 34682400 | 66218400 | 97754400
2022-06-30 11:00 | -6056.23 | 6.108 | 46.4609 | 59.8258 | -1774.9058 |  | 875 | 3150000 | 34686000 | 66222000 | 97758000
2022-07-01 12:00 | -5690.36 | 6.108 | 46.8065 | 59.8258 | -1667.6799 |  | 876 | 3153600 | 34689600 | 66225600 | 97761600
2022-07-02 13:00 | -5614.09 | 6.108 | 46.9441 | 59.8258 | -1645.3274 |  | 877 | 3157200 | 34693200 | 66229200 | 97765200
2022-07-03 14:00 | -5504.33 | 6.108 | 47.0838 | 59.8258 | -1613.1599 |  | 878 | 3160800 | 34696800 | 66232800 | 97768800
2022-07-04 15:00 | -5353.55 | 6.108 | 47.2519 | 59.8258 | -1568.9706 |  | 879 | 3164400 | 34700400 | 66236400 | 97772400
2022-07-05 16:00 | -4728.13 | 6.108 | 47.7784 | 59.8258 | -1385.6781 |  | 880 | 3168000 | 34704000 | 66240000 | 97776000
2022-07-06 17:00 | -5007.62 | 6.108 | 47.6836 | 59.8258 | -1467.5886 |  | 881 | 3171600 | 34707600 | 66243600 | 97779600
2022-07-07 18:00 | -5156.13 | 6.108 | 47.596 | 59.8258 | -1511.1125 |  | 882 | 3175200 | 34711200 | 66247200 | 97783200
2022-07-08 19:00 | -5390.57 | 6.108 | 47.4235 | 59.8258 | -1579.8201 |  | 883 | 3178800 | 34714800 | 66250800 | 97786800
2022-07-09 20:00 | -6124.16 | 6.108 | 46.8638 | 59.8258 | -1794.8141 |  | 884 | 3182400 | 34718400 | 66254400 | 97790400
2022-07-10 21:00 | -6884.7 | 6.108 | 46.2076 | 59.8258 | -2017.7064 |  | 885 | 3186000 | 34722000 | 66258000 | 97794000
2022-07-11 22:00 | -7311.81 | 6.108 | 45.7341 | 59.8258 | -2142.88 |  | 886 | 3189600 | 34725600 | 66261600 | 97797600
2022-07-12 23:00 | -8284.93 | 6.108 | 44.8701 | 59.8258 | -2428.0733 |  | 887 | 3193200 | 34729200 | 66265200 | 97801200
2022-07-14 | -8635.23 | 6.108 | 44.3947 | 59.8258 | -2530.7361 |  | 888 | 3196800 | 34732800 | 66268800 | 97804800
2022-07-15 01:00 | -8887.65 | 6.108 | 44.0232 | 59.8258 | -2604.7131 |  | 889 | 3200400 | 34736400 | 66272400 | 97808400
2022-07-16 02:00 | -9214.37 | 6.108 | 43.6308 | 59.8258 | -2700.4653 |  | 890 | 3204000 | 34740000 | 66276000 | 97812000
2022-07-17 03:00 | -9735.83 | 6.108 | 43.0887 | 59.8258 | -2853.2901 |  | 891 | 3207600 | 34743600 | 66279600 | 97815600
2022-07-18 04:00 | -9797.86 | 6.108 | 42.8499 | 59.8258 | -2871.4693 |  | 892 | 3211200 | 34747200 | 66283200 | 97819200
2022-07-19 05:00 | -9729.08 | 6.108 | 42.7656 | 59.8258 | -2851.3119 |  | 893 | 3214800 | 34750800 | 66286800 | 97822800
2022-07-20 06:00 | -9305.03 | 6.108 | 42.9869 | 59.8258 | -2727.0351 |  | 894 | 3218400 | 34754400 | 66290400 | 97826400
2022-07-21 07:00 | -9322.81 | 6.108 | 42.9384 | 59.8258 | -2732.2459 |  | 895 | 3222000 | 34758000 | 66294000 | 97830000
2022-07-22 08:00 | -8549.22 | 6.108 | 43.4705 | 59.8258 | -2505.5291 |  | 896 | 3225600 | 34761600 | 66297600 | 97833600
2022-07-23 09:00 | -7932.13 | 6.108 | 44.0025 | 59.8258 | -2324.6778 |  | 897 | 3229200 | 34765200 | 66301200 | 97837200
2022-07-24 10:00 | -7183.57 | 6.108 | 44.6756 | 59.8258 | -2105.2965 |  | 898 | 3232800 | 34768800 | 66304800 | 97840800
2022-07-25 11:00 | -5700.42 | 6.108 | 45.9453 | 59.8258 | -1670.6282 |  | 899 | 3236400 | 34772400 | 66308400 | 97844400
2022-07-26 12:00 | -4249.82 | 6.108 | 47.3178 | 59.8258 | -1245.4993 |  | 900 | 3240000 | 34776000 | 66312000 | 97848000
2022-07-27 13:00 | -4493.98 | 6.108 | 47.5043 | 59.8258 | -1317.0555 |  | 901 | 3243600 | 34779600 | 66315600 | 97851600
2022-07-28 14:00 | -3979.05 | 6.108 | 48.0775 | 59.8258 | -1166.1444 |  | 902 | 3247200 | 34783200 | 66319200 | 97855200
2022-07-29 15:00 | -3511.82 | 6.108 | 48.639 | 59.8258 | -1029.2128 |  | 903 | 3250800 | 34786800 | 66322800 | 97858800
2022-07-30 16:00 | -4038.82 | 6.108 | 48.4755 | 59.8258 | -1183.6613 |  | 904 | 3254400 | 34790400 | 66326400 | 97862400
2022-07-31 17:00 | -4881.1 | 6.108 | 47.9227 | 59.8258 | -1430.5092 |  | 905 | 3258000 | 34794000 | 66330000 | 97866000
2022-08-01 18:00 | -5739.82 | 6.108 | 47.2188 | 59.8258 | -1682.1752 |  | 906 | 3261600 | 34797600 | 66333600 | 97869600
2022-08-02 19:00 | -6837.89 | 6.108 | 46.2933 | 59.8258 | -2003.9877 |  | 907 | 3265200 | 34801200 | 66337200 | 97873200
2022-08-03 20:00 | -7494.7 | 6.108 | 45.6113 | 59.8258 | -2196.4797 |  | 908 | 3268800 | 34804800 | 66340800 | 97876800
2022-08-04 21:00 | -9115.69 | 6.108 | 44.1962 | 59.8258 | -2671.545 |  | 909 | 3272400 | 34808400 | 66344400 | 97880400
2022-08-05 22:00 | -8932.43 | 6.108 | 43.997 | 59.8258 | -2617.8368 |  | 910 | 3276000 | 34812000 | 66348000 | 97884000
2022-08-06 23:00 | -10854.6 | 6.108 | 42.3676 | 59.8258 | -3181.1692 |  | 911 | 3279600 | 34815600 | 66351600 | 97887600
2022-08-08 | -11162.3 | 6.108 | 41.7363 | 59.8258 | -3271.3472 |  | 912 | 3283200 | 34819200 | 66355200 | 97891200
2022-08-09 01:00 | -11436.3 | 6.108 | 41.2273 | 59.8258 | -3351.6487 |  | 913 | 3286800 | 34822800 | 66358800 | 97894800
2022-08-10 02:00 | -11988.5 | 6.108 | 40.566 | 59.8258 | -3513.4825 |  | 914 | 3290400 | 34826400 | 66362400 | 97898400
2022-08-11 03:00 | -11978.8 | 6.108 | 40.3137 | 59.8258 | -3510.6397 |  | 915 | 3294000 | 34830000 | 66366000 | 97902000
2022-08-12 04:00 | -11869.8 | 6.108 | 40.1835 | 59.8258 | -3478.695 |  | 916 | 3297600 | 34833600 | 66369600 | 97905600
2022-08-13 05:00 | -11985.8 | 6.108 | 39.9696 | 59.8258 | -3512.6912 |  | 917 | 3301200 | 34837200 | 66373200 | 97909200
2022-08-14 06:00 | -11640.5 | 6.108 | 40.0933 | 59.8258 | -3411.4938 |  | 918 | 3304800 | 34840800 | 66376800 | 97912800
2022-08-15 07:00 | -11527 | 6.108 | 40.1105 | 59.8258 | -3378.2302 |  | 919 | 3308400 | 34844400 | 66380400 | 97916400
2022-08-16 08:00 | -9882.39 | 6.108 | 41.2984 | 59.8258 | -2896.2426 |  | 920 | 3312000 | 34848000 | 66384000 | 97920000
2022-08-17 09:00 | -9111.05 | 6.108 | 42.0532 | 59.8258 | -2670.1852 |  | 921 | 3315600 | 34851600 | 66387600 | 97923600
2022-08-18 10:00 | -7651.85 | 6.108 | 43.3172 | 59.8258 | -2242.5359 |  | 922 | 3319200 | 34855200 | 66391200 | 97927200
2022-08-19 11:00 | -6054.09 | 6.108 | 44.7958 | 59.8258 | -1774.2786 |  | 923 | 3322800 | 34858800 | 66394800 | 97930800
2022-08-20 12:00 | -5027.29 | 6.108 | 45.9366 | 59.8258 | -1473.3533 |  | 924 | 3326400 | 34862400 | 66398400 | 97934400
2022-08-21 13:00 | -3865.01 | 6.108 | 47.1764 | 59.8258 | -1132.7226 |  | 925 | 3330000 | 34866000 | 66402000 | 97938000
2022-08-22 14:00 | -3440.01 | 6.108 | 47.8712 | 59.8258 | -1008.1674 |  | 926 | 3333600 | 34869600 | 66405600 | 97941600
2022-08-23 15:00 | -2948.36 | 6.108 | 48.5503 | 59.8258 | -864.079 |  | 927 | 3337200 | 34873200 | 66409200 | 97945200
2022-08-24 16:00 | -2526.34 | 6.108 | 49.1464 | 59.8258 | -740.3972 |  | 928 | 3340800 | 34876800 | 66412800 | 97948800
2022-08-25 17:00 | -3724.58 | 6.108 | 48.5111 | 59.8258 | -1091.5666 |  | 929 | 3344400 | 34880400 | 66416400 | 97952400
2022-08-26 18:00 | -4758.04 | 6.108 | 47.7731 | 59.8258 | -1394.4439 |  | 930 | 3348000 | 34884000 | 66420000 | 97956000
2022-08-27 19:00 | -6503.68 | 6.108 | 46.3923 | 59.8258 | -1906.0405 |  | 931 | 3351600 | 34887600 | 66423600 | 97959600
2022-08-28 20:00 | -7372.44 | 6.108 | 45.507 | 59.8258 | -2160.6489 |  | 932 | 3355200 | 34891200 | 66427200 | 97963200
2022-08-29 21:00 | -8513.85 | 6.108 | 44.4263 | 59.8258 | -2495.1631 |  | 933 | 3358800 | 34894800 | 66430800 | 97966800
2022-08-30 22:00 | -8945.78 | 6.108 | 43.8058 | 59.8258 | -2621.7493 |  | 934 | 3362400 | 34898400 | 66434400 | 97970400
2022-08-31 23:00 | -10333.2 | 6.108 | 42.5269 | 59.8258 | -3028.362 |  | 935 | 3366000 | 34902000 | 66438000 | 97974000
2022-09-02 | -10573.3 | 6.108 | 41.9989 | 59.8258 | -3098.7283 |  | 936 | 3369600 | 34905600 | 66441600 | 97977600
2022-09-03 01:00 | -10998 | 6.108 | 41.4264 | 59.8258 | -3223.1956 |  | 937 | 3373200 | 34909200 | 66445200 | 97981200
2022-09-04 02:00 | -11397.7 | 6.108 | 40.8944 | 59.8258 | -3340.3361 |  | 938 | 3376800 | 34912800 | 66448800 | 97984800
2022-09-05 03:00 | -11236.2 | 6.108 | 40.7856 | 59.8258 | -3293.0052 |  | 939 | 3380400 | 34916400 | 66452400 | 97988400
2022-09-06 04:00 | -11399.6 | 6.108 | 40.4978 | 59.8258 | -3340.893 |  | 940 | 3384000 | 34920000 | 66456000 | 97992000
2022-09-07 05:00 | -11440.2 | 6.108 | 40.3289 | 59.8258 | -3352.7917 |  | 941 | 3387600 | 34923600 | 66459600 | 97995600
2022-09-08 06:00 | -11089.8 | 6.108 | 40.4677 | 59.8258 | -3250.0996 |  | 942 | 3391200 | 34927200 | 66463200 | 97999200
2022-09-09 07:00 | -10927.8 | 6.108 | 40.5512 | 59.8258 | -3202.622 |  | 943 | 3394800 | 34930800 | 66466800 | 98002800
2022-09-10 08:00 | -9792.86 | 6.108 | 41.3797 | 59.8258 | -2870.004 |  | 944 | 3398400 | 34934400 | 66470400 | 98006400
2022-09-11 09:00 | -8725.68 | 6.108 | 42.299 | 59.8258 | -2557.2444 |  | 945 | 3402000 | 34938000 | 66474000 | 98010000
2022-09-12 10:00 | -7005.87 | 6.108 | 43.7823 | 59.8258 | -2053.2178 |  | 946 | 3405600 | 34941600 | 66477600 | 98013600
2022-09-13 11:00 | -5634.76 | 6.108 | 45.1405 | 59.8258 | -1651.3851 |  | 947 | 3409200 | 34945200 | 66481200 | 98017200
2022-09-14 12:00 | -4268.69 | 6.108 | 46.5286 | 59.8258 | -1251.0295 |  | 948 | 3412800 | 34948800 | 66484800 | 98020800
2022-09-15 13:00 | -3061.84 | 6.108 | 47.8397 | 59.8258 | -897.3367 |  | 949 | 3416400 | 34952400 | 66488400 | 98024400
2022-09-16 14:00 | -3644.38 | 6.108 | 47.8209 | 59.8258 | -1068.0623 |  | 950 | 3420000 | 34956000 | 66492000 | 98028000
2022-09-17 15:00 | -3650.77 | 6.108 | 48.0066 | 59.8258 | -1069.9351 |  | 951 | 3423600 | 34959600 | 66495600 | 98031600
2022-09-18 16:00 | -3076.57 | 6.108 | 48.5796 | 59.8258 | -901.6537 |  | 952 | 3427200 | 34963200 | 66499200 | 98035200
2022-09-19 17:00 | -3699.07 | 6.108 | 48.3316 | 59.8258 | -1084.0904 |  | 953 | 3430800 | 34966800 | 66502800 | 98038800
2022-09-20 18:00 | -4605.78 | 6.108 | 47.7239 | 59.8258 | -1349.8209 |  | 954 | 3434400 | 34970400 | 66506400 | 98042400
2022-09-21 19:00 | -5648 | 6.108 | 46.8898 | 59.8258 | -1655.2654 |  | 955 | 3438000 | 34974000 | 66510000 | 98046000
2022-09-22 20:00 | -6005.64 | 6.108 | 46.5079 | 59.8258 | -1760.0793 |  | 956 | 3441600 | 34977600 | 66513600 | 98049600
2022-09-23 21:00 | -7535.64 | 6.108 | 45.2878 | 59.8258 | -2208.4781 |  | 957 | 3445200 | 34981200 | 66517200 | 98053200
2022-09-24 22:00 | -8083.56 | 6.108 | 44.6198 | 59.8258 | -2369.0576 |  | 958 | 3448800 | 34984800 | 66520800 | 98056800
2022-09-25 23:00 | -8803.82 | 6.108 | 43.8622 | 59.8258 | -2580.1449 |  | 959 | 3452400 | 34988400 | 66524400 | 98060400
2022-09-27 | -9518.13 | 6.108 | 43.101 | 59.8258 | -2789.4885 |  | 960 | 3456000 | 34992000 | 66528000 | 98064000
2022-09-28 01:00 | -9812.09 | 6.108 | 42.6315 | 59.8258 | -2875.6397 |  | 961 | 3459600 | 34995600 | 66531600 | 98067600
2022-09-29 02:00 | -10322.4 | 6.108 | 42.044 | 59.8258 | -3025.1968 |  | 962 | 3463200 | 34999200 | 66535200 | 98071200
2022-09-30 03:00 | -9794.27 | 6.108 | 42.2445 | 59.8258 | -2870.4172 |  | 963 | 3466800 | 35002800 | 66538800 | 98074800
2022-10-01 04:00 | -9849.67 | 6.108 | 42.1265 | 59.8258 | -2886.6533 |  | 964 | 3470400 | 35006400 | 66542400 | 98078400
2022-10-02 05:00 | -9991.46 | 6.108 | 41.945 | 59.8258 | -2928.2079 |  | 965 | 3474000 | 35010000 | 66546000 | 98082000
2022-10-03 06:00 | -10235.7 | 6.108 | 41.6737 | 59.8258 | -2999.7876 |  | 966 | 3477600 | 35013600 | 66549600 | 98085600
2022-10-04 07:00 | -9587.18 | 6.108 | 42.0689 | 59.8258 | -2809.7251 |  | 967 | 3481200 | 35017200 | 66553200 | 98089200
2022-10-05 08:00 | -8162.89 | 6.108 | 43.1648 | 59.8258 | -2392.3069 |  | 968 | 3484800 | 35020800 | 66556800 | 98092800
2022-10-06 09:00 | -7337.08 | 6.108 | 43.9751 | 59.8258 | -2150.2859 |  | 969 | 3488400 | 35024400 | 66560400 | 98096400
2022-10-07 10:00 | -6416.84 | 6.108 | 44.8563 | 59.8258 | -1880.5902 |  | 970 | 3492000 | 35028000 | 66564000 | 98100000
2022-10-08 11:00 | -4569.4 | 6.108 | 46.4624 | 59.8258 | -1339.1589 |  | 971 | 3495600 | 35031600 | 66567600 | 98103600
2022-10-09 12:00 | -2848.54 | 6.108 | 48.1463 | 59.8258 | -834.8247 |  | 972 | 3499200 | 35035200 | 66571200 | 98107200
2022-10-10 13:00 | -1996.77 | 6.108 | 49.2525 | 59.8258 | -585.1955 |  | 973 | 3502800 | 35038800 | 66574800 | 98110800
2022-10-11 14:00 | -1547.46 | 5.063 | 49.7445 | 59.8258 | -453.5158 |  | 974 | 3506400 | 35042400 | 66578400 | 98114400
2022-10-12 15:00 | -618.199 | 2.1033 | 50.1171 | 59.8258 | -181.1762 |  | 975 | 3510000 | 35046000 | 66582000 | 98118000
2022-10-13 16:00 | -905.44 | 3.3383 | 50.5917 | 59.8258 | -265.3583 |  | 976 | 3513600 | 35049600 | 66585600 | 98121600
2022-10-14 17:00 | -412.998 | 1.6123 | 50.8866 | 59.8258 | -121.0378 |  | 977 | 3517200 | 35053200 | 66589200 | 98125200
2022-10-15 18:00 | -1965.43 | 6.108 | 50.8431 | 59.8258 | -576.0107 |  | 978 | 3520800 | 35056800 | 66592800 | 98128800
2022-10-16 19:00 | -3724 | 6.108 | 49.5295 | 59.8258 | -1091.3967 |  | 979 | 3524400 | 35060400 | 66596400 | 98132400
2022-10-17 20:00 | -4807.52 | 6.108 | 48.5303 | 59.8258 | -1408.945 |  | 980 | 3528000 | 35064000 | 66600000 | 98136000
2022-10-18 21:00 | -5753.31 | 6.108 | 47.6229 | 59.8258 | -1686.1287 |  | 981 | 3531600 | 35067600 | 66603600 | 98139600
2022-10-19 22:00 | -5759.05 | 6.108 | 47.4157 | 59.8258 | -1687.8109 |  | 982 | 3535200 | 35071200 | 66607200 | 98143200
2022-10-20 23:00 | -6108.46 | 6.108 | 47.0204 | 59.8258 | -1790.2129 |  | 983 | 3538800 | 35074800 | 66610800 | 98146800
2022-10-22 | -8003.85 | 6.108 | 45.4684 | 59.8258 | -2345.6969 |  | 984 | 3542400 | 35078400 | 66614400 | 98150400
2022-10-23 01:00 | -8229.11 | 6.108 | 44.9624 | 59.8258 | -2411.7141 |  | 985 | 3546000 | 35082000 | 66618000 | 98154000
2022-10-24 02:00 | -8664.07 | 6.108 | 44.4155 | 59.8258 | -2539.1883 |  | 986 | 3549600 | 35085600 | 66621600 | 98157600
2022-10-25 03:00 | -8580.79 | 6.108 | 44.2854 | 59.8258 | -2514.7813 |  | 987 | 3553200 | 35089200 | 66625200 | 98161200
2022-10-26 04:00 | -8611.62 | 6.108 | 44.1188 | 59.8258 | -2523.8167 |  | 988 | 3556800 | 35092800 | 66628800 | 98164800
2022-10-27 05:00 | -8711.03 | 6.108 | 43.9094 | 59.8258 | -2552.9509 |  | 989 | 3560400 | 35096400 | 66632400 | 98168400
2022-10-28 06:00 | -8500.84 | 6.108 | 43.9791 | 59.8258 | -2491.3503 |  | 990 | 3564000 | 35100000 | 66636000 | 98172000
2022-10-29 07:00 | -7491.84 | 6.108 | 44.7074 | 59.8258 | -2195.6416 |  | 991 | 3567600 | 35103600 | 66639600 | 98175600
2022-10-30 08:00 | -6893.58 | 6.108 | 45.267 | 59.8258 | -2020.3089 |  | 992 | 3571200 | 35107200 | 66643200 | 98179200
2022-10-31 09:00 | -7312.45 | 6.108 | 45.0779 | 59.8258 | -2143.0675 |  | 993 | 3574800 | 35110800 | 66646800 | 98182800
2022-11-01 10:00 | -7164.88 | 6.108 | 45.1756 | 59.8258 | -2099.819 |  | 994 | 3578400 | 35114400 | 66650400 | 98186400
2022-11-02 11:00 | -6826.33 | 6.108 | 45.43 | 59.8258 | -2000.5998 |  | 995 | 3582000 | 35118000 | 66654000 | 98190000
2022-11-03 12:00 | -6268.66 | 6.108 | 45.9024 | 59.8258 | -1837.1629 |  | 996 | 3585600 | 35121600 | 66657600 | 98193600
2022-11-04 13:00 | -5373.05 | 6.108 | 46.6522 | 59.8258 | -1574.6855 |  | 997 | 3589200 | 35125200 | 66661200 | 98197200
2022-11-05 14:00 | -5519.79 | 6.108 | 46.6871 | 59.8258 | -1617.6908 |  | 998 | 3592800 | 35128800 | 66664800 | 98200800
2022-11-06 15:00 | -4944.6 | 6.108 | 47.1756 | 59.8258 | -1449.1192 |  | 999 | 3596400 | 35132400 | 66668400 | 98204400
2022-11-07 16:00 | -4634.59 | 6.108 | 47.5194 | 59.8258 | -1358.2643 |  | 1000 | 3600000 | 35136000 | 66672000 | 98208000
2022-11-08 17:00 | -3029.94 | 6.108 | 48.8432 | 59.8258 | -887.9878 |  | 1001 | 3603600 | 35139600 | 66675600 | 98211600
2022-11-09 18:00 | -3783.13 | 6.108 | 48.5773 | 59.8258 | -1108.726 |  | 1002 | 3607200 | 35143200 | 66679200 | 98215200
2022-11-10 19:00 | -4001.93 | 6.108 | 48.489 | 59.8258 | -1172.8499 |  | 1003 | 3610800 | 35146800 | 66682800 | 98218800
2022-11-11 20:00 | -4338.83 | 6.108 | 48.2752 | 59.8258 | -1271.5856 |  | 1004 | 3614400 | 35150400 | 66686400 | 98222400
2022-11-12 21:00 | -5375.78 | 6.108 | 47.5323 | 59.8258 | -1575.4856 |  | 1005 | 3618000 | 35154000 | 66690000 | 98226000
2022-11-13 22:00 | -6335.94 | 6.108 | 46.723 | 59.8258 | -1856.8807 |  | 1006 | 3621600 | 35157600 | 66693600 | 98229600
2022-11-14 23:00 | -6838.01 | 6.108 | 46.1632 | 59.8258 | -2004.0229 |  | 1007 | 3625200 | 35161200 | 66697200 | 98233200
2022-11-16 | -8288.74 | 6.108 | 44.9371 | 59.8258 | -2429.1899 |  | 1008 | 3628800 | 35164800 | 66700800 | 98236800
2022-11-17 01:00 | -9011.8 | 6.108 | 44.1155 | 59.8258 | -2641.0979 |  | 1009 | 3632400 | 35168400 | 66704400 | 98240400
2022-11-18 02:00 | -9380.3 | 6.108 | 43.5771 | 59.8258 | -2749.0946 |  | 1010 | 3636000 | 35172000 | 66708000 | 98244000
2022-11-19 03:00 | -9465.6 | 6.108 | 43.3092 | 59.8258 | -2774.0935 |  | 1011 | 3639600 | 35175600 | 66711600 | 98247600
2022-11-20 04:00 | -9528.95 | 6.108 | 43.1116 | 59.8258 | -2792.6596 |  | 1012 | 3643200 | 35179200 | 66715200 | 98251200
2022-11-21 05:00 | -9723.82 | 6.108 | 42.8181 | 59.8258 | -2849.7703 |  | 1013 | 3646800 | 35182800 | 66718800 | 98254800
2022-11-22 06:00 | -9159.73 | 6.108 | 43.1169 | 59.8258 | -2684.4519 |  | 1014 | 3650400 | 35186400 | 66722400 | 98258400
2022-11-23 07:00 | -9116.05 | 6.108 | 43.1265 | 59.8258 | -2671.6505 |  | 1015 | 3654000 | 35190000 | 66726000 | 98262000
2022-11-24 08:00 | -8999.42 | 6.108 | 43.1723 | 59.8258 | -2637.4696 |  | 1016 | 3657600 | 35193600 | 66729600 | 98265600
2022-11-25 09:00 | -9396.38 | 6.108 | 42.8383 | 59.8258 | -2753.8071 |  | 1017 | 3661200 | 35197200 | 66733200 | 98269200
2022-11-26 10:00 | -9040.05 | 6.108 | 43.0132 | 59.8258 | -2649.3771 |  | 1018 | 3664800 | 35200800 | 66736800 | 98272800
2022-11-27 11:00 | -8993.69 | 6.108 | 43.0233 | 59.8258 | -2635.7904 |  | 1019 | 3668400 | 35204400 | 66740400 | 98276400
2022-11-28 12:00 | -8381.22 | 6.108 | 43.4525 | 59.8258 | -2456.2931 |  | 1020 | 3672000 | 35208000 | 66744000 | 98280000
2022-11-29 13:00 | -7960.68 | 6.108 | 43.8047 | 59.8258 | -2333.045 |  | 1021 | 3675600 | 35211600 | 66747600 | 98283600
2022-11-30 14:00 | -8085.21 | 6.108 | 43.7669 | 59.8258 | -2369.5411 |  | 1022 | 3679200 | 35215200 | 66751200 | 98287200
2022-12-01 15:00 | -7658.1 | 6.108 | 44.0842 | 59.8258 | -2244.3676 |  | 1023 | 3682800 | 35218800 | 66754800 | 98290800
2022-12-02 16:00 | -7208 | 6.108 | 44.4623 | 59.8258 | -2112.4563 |  | 1024 | 3686400 | 35222400 | 66758400 | 98294400
2022-12-03 17:00 | -7304.93 | 6.108 | 44.4617 | 59.8258 | -2140.8637 |  | 1025 | 3690000 | 35226000 | 66762000 | 98298000
2022-12-04 18:00 | -7343.45 | 6.108 | 44.4411 | 59.8258 | -2152.1527 |  | 1026 | 3693600 | 35229600 | 66765600 | 98301600
2022-12-05 19:00 | -7968.06 | 6.108 | 43.9637 | 59.8258 | -2335.2079 |  | 1027 | 3697200 | 35233200 | 66769200 | 98305200
2022-12-06 20:00 | -8060.86 | 6.108 | 43.8134 | 59.8258 | -2362.4049 |  | 1028 | 3700800 | 35236800 | 66772800 | 98308800
2022-12-07 21:00 | -8609.62 | 6.108 | 43.3507 | 59.8258 | -2523.2305 |  | 1029 | 3704400 | 35240400 | 66776400 | 98312400
2022-12-08 22:00 | -8873.54 | 6.108 | 43.0449 | 59.8258 | -2600.5779 |  | 1030 | 3708000 | 35244000 | 66780000 | 98316000
2022-12-09 23:00 | -10469.8 | 6.108 | 41.7414 | 59.8258 | -3068.3955 |  | 1031 | 3711600 | 35247600 | 66783600 | 98319600
2022-12-11 | -10537.6 | 6.108 | 41.409 | 59.8258 | -3088.2657 |  | 1032 | 3715200 | 35251200 | 66787200 | 98323200
2022-12-12 01:00 | -10300.5 | 6.108 | 41.4185 | 59.8258 | -3018.7786 |  | 1033 | 3718800 | 35254800 | 66790800 | 98326800
2022-12-13 02:00 | -10559.6 | 6.108 | 41.1538 | 59.8258 | -3094.7133 |  | 1034 | 3722400 | 35258400 | 66794400 | 98330400
2022-12-14 03:00 | -10756.7 | 6.108 | 40.8949 | 59.8258 | -3152.4776 |  | 1035 | 3726000 | 35262000 | 66798000 | 98334000
2022-12-15 04:00 | -10708.4 | 6.108 | 40.8024 | 59.8258 | -3138.3222 |  | 1036 | 3729600 | 35265600 | 66801600 | 98337600
2022-12-16 05:00 | -11065.5 | 6.108 | 40.4704 | 59.8258 | -3242.9779 |  | 1037 | 3733200 | 35269200 | 66805200 | 98341200
2022-12-17 06:00 | -10600.2 | 6.108 | 40.7105 | 59.8258 | -3106.612 |  | 1038 | 3736800 | 35272800 | 66808800 | 98344800
2022-12-18 07:00 | -10882.2 | 6.108 | 40.4701 | 59.8258 | -3189.258 |  | 1039 | 3740400 | 35276400 | 66812400 | 98348400
2022-12-19 08:00 | -10163.2 | 6.108 | 40.9326 | 59.8258 | -2978.5399 |  | 1040 | 3744000 | 35280000 | 66816000 | 98352000
2022-12-20 09:00 | -9406.18 | 6.108 | 41.5393 | 59.8258 | -2756.6792 |  | 1041 | 3747600 | 35283600 | 66819600 | 98355600
2022-12-21 10:00 | -7620.59 | 6.108 | 42.9903 | 59.8258 | -2233.3745 |  | 1042 | 3751200 | 35287200 | 66823200 | 98359200
2022-12-22 11:00 | -6907.73 | 6.108 | 43.8326 | 59.8258 | -2024.4558 |  | 1043 | 3754800 | 35290800 | 66826800 | 98362800
2022-12-23 12:00 | -5611.11 | 6.108 | 45.0627 | 59.8258 | -1644.454 |  | 1044 | 3758400 | 35294400 | 66830400 | 98366400
2022-12-24 13:00 | -5133.81 | 6.108 | 45.7481 | 59.8258 | -1504.5712 |  | 1045 | 3762000 | 35298000 | 66834000 | 98370000
2022-12-25 14:00 | -4552.31 | 6.108 | 46.4659 | 59.8258 | -1334.1504 |  | 1046 | 3765600 | 35301600 | 66837600 | 98373600
2022-12-26 15:00 | -4596.62 | 6.108 | 46.7012 | 59.8258 | -1347.1363 |  | 1047 | 3769200 | 35305200 | 66841200 | 98377200
2022-12-27 16:00 | -4413.92 | 6.108 | 47.0051 | 59.8258 | -1293.5923 |  | 1048 | 3772800 | 35308800 | 66844800 | 98380800
2022-12-28 17:00 | -5227.13 | 6.108 | 46.5527 | 59.8258 | -1531.9206 |  | 1049 | 3776400 | 35312400 | 66848400 | 98384400
2022-12-29 18:00 | -6099.45 | 6.108 | 45.9029 | 59.8258 | -1787.5723 |  | 1050 | 3780000 | 35316000 | 66852000 | 98388000
2022-12-30 19:00 | -7142.08 | 6.108 | 45.0433 | 59.8258 | -2093.137 |  | 1051 | 3783600 | 35319600 | 66855600 | 98391600
2022-12-31 20:00 | -7906.8 | 6.108 | 44.3073 | 59.8258 | -2317.2543 |  | 1052 | 3787200 | 35323200 | 66859200 | 98395200
2023-01-01 21:00 | -8874.46 | 6.108 | 43.4043 | 59.8258 | -2600.8475 |  | 1053 | 3790800 | 35326800 | 66862800 | 98398800
2023-01-02 22:00 | -9385.9 | 6.108 | 42.7712 | 59.8258 | -2750.7358 |  | 1054 | 3794400 | 35330400 | 66866400 | 98402400
2023-01-03 23:00 | -9760.2 | 6.108 | 42.2767 | 59.8258 | -2860.4323 |  | 1055 | 3798000 | 35334000 | 66870000 | 98406000
2023-01-05 | -9857.66 | 6.108 | 42.0136 | 59.8258 | -2888.995 |  | 1056 | 3801600 | 35337600 | 66873600 | 98409600
2023-01-06 01:00 | -10512.3 | 6.108 | 41.3764 | 59.8258 | -3080.851 |  | 1057 | 3805200 | 35341200 | 66877200 | 98413200
2023-01-07 02:00 | -10962.3 | 6.108 | 40.8338 | 59.8258 | -3212.733 |  | 1058 | 3808800 | 35344800 | 66880800 | 98416800
2023-01-08 03:00 | -10652 | 6.108 | 40.8683 | 59.8258 | -3121.793 |  | 1059 | 3812400 | 35348400 | 66884400 | 98420400
2023-01-09 04:00 | -10566.4 | 6.108 | 40.8366 | 59.8258 | -3096.7062 |  | 1060 | 3816000 | 35352000 | 66888000 | 98424000
2023-01-10 05:00 | -10225.6 | 6.108 | 41.0269 | 59.8258 | -2996.8275 |  | 1061 | 3819600 | 35355600 | 66891600 | 98427600
2023-01-11 06:00 | -9875.89 | 6.108 | 41.2638 | 59.8258 | -2894.3376 |  | 1062 | 3823200 | 35359200 | 66895200 | 98431200
2023-01-12 07:00 | -9893.8 | 6.108 | 41.276 | 59.8258 | -2899.5866 |  | 1063 | 3826800 | 35362800 | 66898800 | 98434800
2023-01-13 08:00 | -8895.71 | 6.108 | 42.0321 | 59.8258 | -2607.0752 |  | 1064 | 3830400 | 35366400 | 66902400 | 98438400
2023-01-14 09:00 | -8220.75 | 6.108 | 42.6731 | 59.8258 | -2409.264 |  | 1065 | 3834000 | 35370000 | 66906000 | 98442000
2023-01-15 10:00 | -7363.58 | 6.108 | 43.4773 | 59.8258 | -2158.0523 |  | 1066 | 3837600 | 35373600 | 66909600 | 98445600
2023-01-16 11:00 | -6088.88 | 6.108 | 44.6291 | 59.8258 | -1784.4746 |  | 1067 | 3841200 | 35377200 | 66913200 | 98449200
2023-01-17 12:00 | -5690.33 | 6.108 | 45.2044 | 59.8258 | -1667.6711 |  | 1068 | 3844800 | 35380800 | 66916800 | 98452800
2023-01-18 13:00 | -4400.27 | 6.108 | 46.4036 | 59.8258 | -1289.5918 |  | 1069 | 3848400 | 35384400 | 66920400 | 98456400
2023-01-19 14:00 | -3558.22 | 6.108 | 47.3546 | 59.8258 | -1042.8113 |  | 1070 | 3852000 | 35388000 | 66924000 | 98460000
2023-01-20 15:00 | -3432.57 | 6.108 | 47.7727 | 59.8258 | -1005.987 |  | 1071 | 3855600 | 35391600 | 66927600 | 98463600
2023-01-21 16:00 | -2706.23 | 6.108 | 48.5431 | 59.8258 | -793.1177 |  | 1072 | 3859200 | 35395200 | 66931200 | 98467200
2023-01-22 17:00 | -3073.36 | 6.108 | 48.5271 | 59.8258 | -900.7129 |  | 1073 | 3862800 | 35398800 | 66934800 | 98470800
2023-01-23 18:00 | -4470.91 | 6.108 | 47.6352 | 59.8258 | -1310.2944 |  | 1074 | 3866400 | 35402400 | 66938400 | 98474400
2023-01-24 19:00 | -5399.9 | 6.108 | 46.879 | 59.8258 | -1582.5545 |  | 1075 | 3870000 | 35406000 | 66942000 | 98478000
2023-01-25 20:00 | -5739.11 | 6.108 | 46.5074 | 59.8258 | -1681.9671 |  | 1076 | 3873600 | 35409600 | 66945600 | 98481600
2023-01-26 21:00 | -7016.03 | 6.108 | 45.4846 | 59.8258 | -2056.1954 |  | 1077 | 3877200 | 35413200 | 66949200 | 98485200
2023-01-27 22:00 | -7649.32 | 6.108 | 44.7975 | 59.8258 | -2241.7944 |  | 1078 | 3880800 | 35416800 | 66952800 | 98488800
2023-01-28 23:00 | -8571 | 6.108 | 43.8938 | 59.8258 | -2511.9121 |  | 1079 | 3884400 | 35420400 | 66956400 | 98492400
2023-01-30 | -9055.82 | 6.108 | 43.3029 | 59.8258 | -2653.9989 |  | 1080 | 3888000 | 35424000 | 66960000 | 98496000
2023-01-31 01:00 | -9463.72 | 6.108 | 42.7889 | 59.8258 | -2773.5425 |  | 1081 | 3891600 | 35427600 | 66963600 | 98499600
2023-02-01 02:00 | -10400.4 | 6.108 | 41.882 | 59.8258 | -3048.0564 |  | 1082 | 3895200 | 35431200 | 66967200 | 98503200
2023-02-02 03:00 | -10687.1 | 6.108 | 41.4011 | 59.8258 | -3132.0798 |  | 1083 | 3898800 | 35434800 | 66970800 | 98506800
2023-02-03 04:00 | -10397.4 | 6.108 | 41.3913 | 59.8258 | -3047.1771 |  | 1084 | 3902400 | 35438400 | 66974400 | 98510400
2023-02-04 05:00 | -10659.2 | 6.108 | 41.0804 | 59.8258 | -3123.9031 |  | 1085 | 3906000 | 35442000 | 66978000 | 98514000
2023-02-05 06:00 | -9838.73 | 6.108 | 41.5651 | 59.8258 | -2883.4471 |  | 1086 | 3909600 | 35445600 | 66981600 | 98517600
2023-02-06 07:00 | -10431.2 | 6.108 | 41.1239 | 59.8258 | -3057.0829 |  | 1087 | 3913200 | 35449200 | 66985200 | 98521200
2023-02-07 08:00 | -9126.63 | 6.108 | 42.0062 | 59.8258 | -2674.7512 |  | 1088 | 3916800 | 35452800 | 66988800 | 98524800
2023-02-08 09:00 | -7982.16 | 6.108 | 42.9728 | 59.8258 | -2339.3402 |  | 1089 | 3920400 | 35456400 | 66992400 | 98528400
2023-02-09 10:00 | -6150.61 | 6.108 | 44.5476 | 59.8258 | -1802.5659 |  | 1090 | 3924000 | 35460000 | 66996000 | 98532000
2023-02-10 11:00 | -4823.71 | 6.108 | 45.8872 | 59.8258 | -1413.6899 |  | 1091 | 3927600 | 35463600 | 66999600 | 98535600
2023-02-11 12:00 | -4704.5 | 6.108 | 46.3328 | 59.8258 | -1378.7528 |  | 1092 | 3931200 | 35467200 | 67003200 | 98539200
2023-02-12 13:00 | -3603.56 | 6.108 | 47.4005 | 59.8258 | -1056.0992 |  | 1093 | 3934800 | 35470800 | 67006800 | 98542800
2023-02-13 14:00 | -4028.46 | 6.108 | 47.3944 | 59.8258 | -1180.6251 |  | 1094 | 3938400 | 35474400 | 67010400 | 98546400
2023-02-14 15:00 | -3840.1 | 6.108 | 47.6982 | 59.8258 | -1125.4222 |  | 1095 | 3942000 | 35478000 | 67014000 | 98550000
2023-02-15 16:00 | -3662.52 | 6.108 | 47.9568 | 59.8258 | -1073.3787 |  | 1096 | 3945600 | 35481600 | 67017600 | 98553600
2023-02-16 17:00 | -4802.4 | 6.108 | 47.2294 | 59.8258 | -1407.4445 |  | 1097 | 3949200 | 35485200 | 67021200 | 98557200
2023-02-17 18:00 | -5790.74 | 6.108 | 46.4413 | 59.8258 | -1697.0984 |  | 1098 | 3952800 | 35488800 | 67024800 | 98560800
2023-02-18 19:00 | -7038.1 | 6.108 | 45.3725 | 59.8258 | -2062.6635 |  | 1099 | 3956400 | 35492400 | 67028400 | 98564400
2023-02-19 20:00 | -7601.28 | 6.108 | 44.7417 | 59.8258 | -2227.7153 |  | 1100 | 3960000 | 35496000 | 67032000 | 98568000
2023-02-20 21:00 | -8763.58 | 6.108 | 43.6843 | 59.8258 | -2568.3518 |  | 1101 | 3963600 | 35499600 | 67035600 | 98571600
2023-02-21 22:00 | -9559.59 | 6.108 | 42.7975 | 59.8258 | -2801.6393 |  | 1102 | 3967200 | 35503200 | 67039200 | 98575200
2023-02-22 23:00 | -10682.7 | 6.108 | 41.6602 | 59.8258 | -3130.7903 |  | 1103 | 3970800 | 35506800 | 67042800 | 98578800
2023-02-24 | -11052.5 | 6.108 | 41.0473 | 59.8258 | -3239.168 |  | 1104 | 3974400 | 35510400 | 67046400 | 98582400
2023-02-25 01:00 | -11496 | 6.108 | 40.4436 | 59.8258 | -3369.145 |  | 1105 | 3978000 | 35514000 | 67050000 | 98586000
2023-02-26 02:00 | -11769 | 6.108 | 39.9926 | 59.8258 | -3449.1534 |  | 1106 | 3981600 | 35517600 | 67053600 | 98589600
2023-02-27 03:00 | -11970.6 | 6.108 | 39.6221 | 59.8258 | -3508.2366 |  | 1107 | 3985200 | 35521200 | 67057200 | 98593200
2023-02-28 04:00 | -12130.3 | 6.108 | 39.3011 | 59.8258 | -3555.04 |  | 1108 | 3988800 | 35524800 | 67060800 | 98596800
2023-03-01 05:00 | -12095.7 | 6.108 | 39.1661 | 59.8258 | -3544.8997 |  | 1109 | 3992400 | 35528400 | 67064400 | 98600400
2023-03-02 06:00 | -11847.3 | 6.108 | 39.2276 | 59.8258 | -3472.1009 |  | 1110 | 3996000 | 35532000 | 67068000 | 98604000
2023-03-03 07:00 | -11519.3 | 6.108 | 39.4155 | 59.8258 | -3375.9736 |  | 1111 | 3999600 | 35535600 | 67071600 | 98607600
2023-03-04 08:00 | -9624.35 | 6.108 | 40.8186 | 59.8258 | -2820.6186 |  | 1112 | 4003200 | 35539200 | 67075200 | 98611200
2023-03-05 09:00 | -7732.53 | 6.108 | 42.4647 | 59.8258 | -2266.1808 |  | 1113 | 4006800 | 35542800 | 67078800 | 98614800
2023-03-06 10:00 | -6438.27 | 6.108 | 43.7944 | 59.8258 | -1886.8707 |  | 1114 | 4010400 | 35546400 | 67082400 | 98618400
2023-03-07 11:00 | -4625.82 | 6.108 | 45.5139 | 59.8258 | -1355.694 |  | 1115 | 4014000 | 35550000 | 67086000 | 98622000
2023-03-08 12:00 | -3329.01 | 6.108 | 46.948 | 59.8258 | -975.6365 |  | 1116 | 4017600 | 35553600 | 67089600 | 98625600
2023-03-09 13:00 | -2522.73 | 6.108 | 48.0274 | 59.8258 | -739.3392 |  | 1117 | 4021200 | 35557200 | 67093200 | 98629200
2023-03-10 14:00 | -2212.25 | 6.108 | 48.6672 | 59.8258 | -648.3465 |  | 1118 | 4024800 | 35560800 | 67096800 | 98632800
2023-03-11 15:00 | -2272.65 | 6.108 | 48.9369 | 59.8258 | -666.048 |  | 1119 | 4028400 | 35564400 | 67100400 | 98636400
2023-03-12 16:00 | -2486.4 | 6.108 | 49.0056 | 59.8258 | -728.6919 |  | 1120 | 4032000 | 35568000 | 67104000 | 98640000
2023-03-13 17:00 | -3460.5 | 6.108 | 48.4334 | 59.8258 | -1014.1724 |  | 1121 | 4035600 | 35571600 | 67107600 | 98643600
2023-03-14 18:00 | -3913.84 | 6.108 | 48.1103 | 59.8258 | -1147.0333 |  | 1122 | 4039200 | 35575200 | 67111200 | 98647200
2023-03-15 19:00 | -4841.49 | 6.108 | 47.422 | 59.8258 | -1418.9007 |  | 1123 | 4042800 | 35578800 | 67114800 | 98650800
2023-03-16 20:00 | -5343.83 | 6.108 | 46.9608 | 59.8258 | -1566.122 |  | 1124 | 4046400 | 35582400 | 67118400 | 98654400
2023-03-17 21:00 | -6484.14 | 6.108 | 46.0119 | 59.8258 | -1900.3138 |  | 1125 | 4050000 | 35586000 | 67122000 | 98658000
2023-03-18 22:00 | -6682.52 | 6.108 | 45.6713 | 59.8258 | -1958.4533 |  | 1126 | 4053600 | 35589600 | 67125600 | 98661600
2023-03-19 23:00 | -7699.53 | 6.108 | 44.7855 | 59.8258 | -2256.5095 |  | 1127 | 4057200 | 35593200 | 67129200 | 98665200
2023-03-21 | -8310.77 | 6.108 | 44.1134 | 59.8258 | -2435.6463 |  | 1128 | 4060800 | 35596800 | 67132800 | 98668800
2023-03-22 01:00 | -8634.3 | 6.108 | 43.6553 | 59.8258 | -2530.4635 |  | 1129 | 4064400 | 35600400 | 67136400 | 98672400
2023-03-23 02:00 | -8672.51 | 6.108 | 43.4513 | 59.8258 | -2541.6618 |  | 1130 | 4068000 | 35604000 | 67140000 | 98676000
2023-03-24 03:00 | -9094.85 | 6.108 | 43.0219 | 59.8258 | -2665.4374 |  | 1131 | 4071600 | 35607600 | 67143600 | 98679600
2023-03-25 04:00 | -8847.59 | 6.108 | 43.0585 | 59.8258 | -2592.9727 |  | 1132 | 4075200 | 35611200 | 67147200 | 98683200
2023-03-26 05:00 | -9008.38 | 6.108 | 42.8842 | 59.8258 | -2640.0956 |  | 1133 | 4078800 | 35614800 | 67150800 | 98686800
2023-03-27 06:00 | -8820.65 | 6.108 | 42.9642 | 59.8258 | -2585.0773 |  | 1134 | 4082400 | 35618400 | 67154400 | 98690400
2023-03-28 07:00 | -7954.04 | 6.108 | 43.6016 | 59.8258 | -2331.099 |  | 1135 | 4086000 | 35622000 | 67158000 | 98694000
2023-03-29 08:00 | -7136.4 | 6.108 | 44.3074 | 59.8258 | -2091.4724 |  | 1136 | 4089600 | 35625600 | 67161600 | 98697600
2023-03-30 09:00 | -7378.36 | 6.108 | 44.2778 | 59.8258 | -2162.3839 |  | 1137 | 4093200 | 35629200 | 67165200 | 98701200
2023-03-31 10:00 | -6184.58 | 6.108 | 45.1974 | 59.8258 | -1812.5215 |  | 1138 | 4096800 | 35632800 | 67168800 | 98704800
2023-04-01 11:00 | -5625.82 | 6.108 | 45.7896 | 59.8258 | -1648.7651 |  | 1139 | 4100400 | 35636400 | 67172400 | 98708400
2023-04-02 12:00 | -2984.38 | 6.108 | 47.9555 | 59.8258 | -874.6354 |  | 1140 | 4104000 | 35640000 | 67176000 | 98712000
2023-04-03 13:00 | -1828.24 | 6.108 | 49.2677 | 59.8258 | -535.8043 |  | 1141 | 4107600 | 35643600 | 67179600 | 98715600
2023-04-04 14:00 | -1629.31 | 5.3327 | 49.6501 | 59.8258 | -477.5036 |  | 1142 | 4111200 | 35647200 | 67183200 | 98719200
2023-04-05 15:00 | -1096.76 | 3.6423 | 49.9602 | 59.8258 | -321.4286 |  | 1143 | 4114800 | 35650800 | 67186800 | 98722800
2023-04-06 16:00 | -1088.15 | 3.7829 | 50.3058 | 59.8258 | -318.9053 |  | 1144 | 4118400 | 35654400 | 67190400 | 98726400
2023-04-07 17:00 | -981.7 | 3.4087 | 50.5508 | 59.8258 | -287.7079 |  | 1145 | 4122000 | 35658000 | 67194000 | 98730000
2023-04-08 18:00 | -2456.16 | 6.108 | 50.2191 | 59.8258 | -719.8294 |  | 1146 | 4125600 | 35661600 | 67197600 | 98733600
2023-04-09 19:00 | -3780.67 | 6.108 | 49.1789 | 59.8258 | -1108.005 |  | 1147 | 4129200 | 35665200 | 67201200 | 98737200
2023-04-10 20:00 | -4910.68 | 6.108 | 48.1744 | 59.8258 | -1439.1782 |  | 1148 | 4132800 | 35668800 | 67204800 | 98740800
2023-04-11 21:00 | -5314.3 | 6.108 | 47.6895 | 59.8258 | -1557.4676 |  | 1149 | 4136400 | 35672400 | 67208400 | 98744400
2023-04-12 22:00 | -6211.6 | 6.108 | 46.8798 | 59.8258 | -1820.4403 |  | 1150 | 4140000 | 35676000 | 67212000 | 98748000
2023-04-13 23:00 | -6548.34 | 6.108 | 46.4309 | 59.8258 | -1919.129 |  | 1151 | 4143600 | 35679600 | 67215600 | 98751600
2023-04-15 | -8090.39 | 6.108 | 45.1037 | 59.8258 | -2371.0593 |  | 1152 | 4147200 | 35683200 | 67219200 | 98755200
2023-04-16 01:00 | -8785.69 | 6.108 | 44.2696 | 59.8258 | -2574.8316 |  | 1153 | 4150800 | 35686800 | 67222800 | 98758800
2023-04-17 02:00 | -9223.04 | 6.108 | 43.661 | 59.8258 | -2703.0062 |  | 1154 | 4154400 | 35690400 | 67226400 | 98762400
2023-04-18 03:00 | -9027.94 | 6.108 | 43.5676 | 59.8258 | -2645.828 |  | 1155 | 4158000 | 35694000 | 67230000 | 98766000
2023-04-19 04:00 | -9084.92 | 6.108 | 43.3813 | 59.8258 | -2662.5272 |  | 1156 | 4161600 | 35697600 | 67233600 | 98769600
2023-04-20 05:00 | -8795.06 | 6.108 | 43.4587 | 59.8258 | -2577.5776 |  | 1157 | 4165200 | 35701200 | 67237200 | 98773200
2023-04-21 06:00 | -9211.13 | 6.108 | 43.0912 | 59.8258 | -2699.5157 |  | 1158 | 4168800 | 35704800 | 67240800 | 98776800
2023-04-22 07:00 | -8381 | 6.108 | 43.614 | 59.8258 | -2456.2286 |  | 1159 | 4172400 | 35708400 | 67244400 | 98780400
2023-04-23 08:00 | -7661.05 | 6.108 | 44.195 | 59.8258 | -2245.2321 |  | 1160 | 4176000 | 35712000 | 67248000 | 98784000
2023-04-24 09:00 | -7701.13 | 6.108 | 44.2638 | 59.8258 | -2256.9784 |  | 1161 | 4179600 | 35715600 | 67251600 | 98787600
2023-04-25 10:00 | -7061.45 | 6.108 | 44.7663 | 59.8258 | -2069.5067 |  | 1162 | 4183200 | 35719200 | 67255200 | 98791200
2023-04-26 11:00 | -5422.48 | 6.108 | 46.0729 | 59.8258 | -1589.172 |  | 1163 | 4186800 | 35722800 | 67258800 | 98794800
2023-04-27 12:00 | -5186.49 | 6.108 | 46.5205 | 59.8258 | -1520.0102 |  | 1164 | 4190400 | 35726400 | 67262400 | 98798400
2023-04-28 13:00 | -4856.08 | 6.108 | 46.9315 | 59.8258 | -1423.1766 |  | 1165 | 4194000 | 35730000 | 67266000 | 98802000
2023-04-29 14:00 | -4618.58 | 6.108 | 47.2333 | 59.8258 | -1353.5722 |  | 1166 | 4197600 | 35733600 | 67269600 | 98805600
2023-04-30 15:00 | -4508.09 | 6.108 | 47.4399 | 59.8258 | -1321.1908 |  | 1167 | 4201200 | 35737200 | 67273200 | 98809200
2023-05-01 16:00 | -4472.05 | 6.108 | 47.566 | 59.8258 | -1310.6285 |  | 1168 | 4204800 | 35740800 | 67276800 | 98812800
2023-05-02 17:00 | -3360.83 | 6.108 | 48.4521 | 59.8258 | -984.962 |  | 1169 | 4208400 | 35744400 | 67280400 | 98816400
2023-05-03 18:00 | -4213.27 | 6.108 | 48.0226 | 59.8258 | -1234.7875 |  | 1170 | 4212000 | 35748000 | 67284000 | 98820000
2023-05-04 19:00 | -4606.97 | 6.108 | 47.7506 | 59.8258 | -1350.1696 |  | 1171 | 4215600 | 35751600 | 67287600 | 98823600
2023-05-05 20:00 | -5062.35 | 6.108 | 47.3844 | 59.8258 | -1483.6283 |  | 1172 | 4219200 | 35755200 | 67291200 | 98827200
2023-05-06 21:00 | -5314.55 | 6.108 | 47.1668 | 59.8258 | -1557.5409 |  | 1173 | 4222800 | 35758800 | 67294800 | 98830800
2023-05-07 22:00 | -5850.77 | 6.108 | 46.7394 | 59.8258 | -1714.6914 |  | 1174 | 4226400 | 35762400 | 67298400 | 98834400
2023-05-08 23:00 | -6056.13 | 6.108 | 46.4795 | 59.8258 | -1774.8765 |  | 1175 | 4230000 | 35766000 | 67302000 | 98838000
2023-05-10 | -7535.2 | 6.108 | 45.3027 | 59.8258 | -2208.3491 |  | 1176 | 4233600 | 35769600 | 67305600 | 98841600
2023-05-11 01:00 | -7770.05 | 6.108 | 44.897 | 59.8258 | -2277.1769 |  | 1177 | 4237200 | 35773200 | 67309200 | 98845200
2023-05-12 02:00 | -7764.16 | 6.108 | 44.7462 | 59.8258 | -2275.4507 |  | 1178 | 4240800 | 35776800 | 67312800 | 98848800
2023-05-13 03:00 | -7758.2 | 6.108 | 44.6664 | 59.8258 | -2273.704 |  | 1179 | 4244400 | 35780400 | 67316400 | 98852400
2023-05-14 04:00 | -7563.79 | 6.108 | 44.7482 | 59.8258 | -2216.728 |  | 1180 | 4248000 | 35784000 | 67320000 | 98856000
2023-05-15 05:00 | -7765.88 | 6.108 | 44.5492 | 59.8258 | -2275.9548 |  | 1181 | 4251600 | 35787600 | 67323600 | 98859600
2023-05-16 06:00 | -7689.34 | 6.108 | 44.5641 | 59.8258 | -2253.5231 |  | 1182 | 4255200 | 35791200 | 67327200 | 98863200
2023-05-17 07:00 | -6935.45 | 6.108 | 45.1075 | 59.8258 | -2032.5798 |  | 1183 | 4258800 | 35794800 | 67330800 | 98866800
2023-05-18 08:00 | -6604.35 | 6.108 | 45.4358 | 59.8258 | -1935.5439 |  | 1184 | 4262400 | 35798400 | 67334400 | 98870400
2023-05-19 09:00 | -6925.97 | 6.108 | 45.2742 | 59.8258 | -2029.8014 |  | 1185 | 4266000 | 35802000 | 67338000 | 98874000
2023-05-20 10:00 | -6079.98 | 6.108 | 45.8925 | 59.8258 | -1781.8662 |  | 1186 | 4269600 | 35805600 | 67341600 | 98877600
2023-05-21 11:00 | -5555.26 | 6.108 | 46.3872 | 59.8258 | -1628.086 |  | 1187 | 4273200 | 35809200 | 67345200 | 98881200
2023-05-22 12:00 | -4922.85 | 6.108 | 47.0022 | 59.8258 | -1442.7449 |  | 1188 | 4276800 | 35812800 | 67348800 | 98884800
2023-05-23 13:00 | -4701.39 | 6.108 | 47.3136 | 59.8258 | -1377.8414 |  | 1189 | 4280400 | 35816400 | 67352400 | 98888400
2023-05-24 14:00 | -4403.4 | 6.108 | 47.6491 | 59.8258 | -1290.5091 |  | 1190 | 4284000 | 35820000 | 67356000 | 98892000
2023-05-25 15:00 | -3941.38 | 6.108 | 48.1188 | 59.8258 | -1155.1045 |  | 1191 | 4287600 | 35823600 | 67359600 | 98895600
2023-05-26 16:00 | -4224.78 | 6.108 | 48.045 | 59.8258 | -1238.1608 |  | 1192 | 4291200 | 35827200 | 67363200 | 98899200
2023-05-27 17:00 | -2847.31 | 6.108 | 49.1265 | 59.8258 | -834.4642 |  | 1193 | 4294800 | 35830800 | 67366800 | 98902800
2023-05-28 18:00 | -3604.25 | 6.108 | 48.7914 | 59.8258 | -1056.3014 |  | 1194 | 4298400 | 35834400 | 67370400 | 98906400
2023-05-29 19:00 | -4185.82 | 6.108 | 48.4084 | 59.8258 | -1226.7427 |  | 1195 | 4302000 | 35838000 | 67374000 | 98910000
2023-05-30 20:00 | -4765.78 | 6.108 | 47.939 | 59.8258 | -1396.7122 |  | 1196 | 4305600 | 35841600 | 67377600 | 98913600
2023-05-31 21:00 | -5125.73 | 6.108 | 47.6128 | 59.8258 | -1502.2032 |  | 1197 | 4309200 | 35845200 | 67381200 | 98917200
2023-06-01 22:00 | -5654.63 | 6.108 | 47.1678 | 59.8258 | -1657.2085 |  | 1198 | 4312800 | 35848800 | 67384800 | 98920800
2023-06-02 23:00 | -5689.21 | 6.108 | 47.0288 | 59.8258 | -1667.3429 |  | 1199 | 4316400 | 35852400 | 67388400 | 98924400
2023-06-04 | -6953.62 | 6.108 | 46.0286 | 59.8258 | -2037.9049 |  | 1200 | 4320000 | 35856000 | 67392000 | 98928000
2023-06-05 01:00 | -7113.15 | 6.108 | 45.7188 | 59.8258 | -2084.6585 |  | 1201 | 4323600 | 35859600 | 67395600 | 98931600
2023-06-06 02:00 | -7214.71 | 6.108 | 45.5178 | 59.8258 | -2114.4228 |  | 1202 | 4327200 | 35863200 | 67399200 | 98935200
2023-06-07 03:00 | -7652.11 | 6.108 | 45.1058 | 59.8258 | -2242.6121 |  | 1203 | 4330800 | 35866800 | 67402800 | 98938800
2023-06-08 04:00 | -7463.48 | 6.108 | 45.1302 | 59.8258 | -2187.3301 |  | 1204 | 4334400 | 35870400 | 67406400 | 98942400
2023-06-09 05:00 | -7076.32 | 6.108 | 45.3451 | 59.8258 | -2073.8647 |  | 1205 | 4338000 | 35874000 | 67410000 | 98946000
2023-06-10 06:00 | -6430.68 | 6.108 | 45.8499 | 59.8258 | -1884.6463 |  | 1206 | 4341600 | 35877600 | 67413600 | 98949600
2023-06-11 07:00 | -6416.59 | 6.108 | 45.9424 | 59.8258 | -1880.5169 |  | 1207 | 4345200 | 35881200 | 67417200 | 98953200
2023-06-12 08:00 | -6257.39 | 6.108 | 46.0967 | 59.8258 | -1833.86 |  | 1208 | 4348800 | 35884800 | 67420800 | 98956800
2023-06-13 09:00 | -6601.63 | 6.108 | 45.8848 | 59.8258 | -1934.7468 |  | 1209 | 4352400 | 35888400 | 67424400 | 98960400
2023-06-14 10:00 | -5842.25 | 6.108 | 46.4373 | 59.8258 | -1712.1945 |  | 1210 | 4356000 | 35892000 | 67428000 | 98964000
2023-06-15 11:00 | -5169.17 | 6.108 | 47.0251 | 59.8258 | -1514.9342 |  | 1211 | 4359600 | 35895600 | 67431600 | 98967600
2023-06-16 12:00 | -4623.77 | 6.108 | 47.5699 | 59.8258 | -1355.0932 |  | 1212 | 4363200 | 35899200 | 67435200 | 98971200
2023-06-17 13:00 | -4142.68 | 6.108 | 48.0736 | 59.8258 | -1214.0997 |  | 1213 | 4366800 | 35902800 | 67438800 | 98974800
2023-06-18 14:00 | -1719.11 | 5.7502 | 49.9613 | 59.8258 | -503.8214 |  | 1214 | 4370400 | 35906400 | 67442400 | 98978400
2023-06-19 15:00 | -1098.53 | 3.5791 | 50.3659 | 59.8258 | -321.9474 |  | 1215 | 4374000 | 35910000 | 67446000 | 98982000
2023-06-20 16:00 | -408.391 | 1.5703 | 50.9347 | 59.8258 | -119.6876 |  | 1216 | 4377600 | 35913600 | 67449600 | 98985600
2023-06-21 17:00 | -810.75 | 3.0589 | 51.2158 | 59.8258 | -237.6074 |  | 1217 | 4381200 | 35917200 | 67453200 | 98989200
2023-06-22 18:00 | -1887.32 | 6.108 | 51.1928 | 59.8258 | -553.1189 |  | 1218 | 4384800 | 35920800 | 67456800 | 98992800
2023-06-23 19:00 | -3290.08 | 6.108 | 50.1622 | 59.8258 | -964.2273 |  | 1219 | 4388400 | 35924400 | 67460400 | 98996400
2023-06-24 20:00 | -4345.95 | 6.108 | 49.2217 | 59.8258 | -1273.6722 |  | 1220 | 4392000 | 35928000 | 67464000 | 99000000
2023-06-25 21:00 | -5575.41 | 6.108 | 48.1174 | 59.8258 | -1633.9914 |  | 1221 | 4395600 | 35931600 | 67467600 | 99003600
2023-06-26 22:00 | -6387.35 | 6.108 | 47.2461 | 59.8258 | -1871.9475 |  | 1222 | 4399200 | 35935200 | 67471200 | 99007200
2023-06-27 23:00 | -7558.03 | 6.108 | 46.1052 | 59.8258 | -2215.0399 |  | 1223 | 4402800 | 35938800 | 67474800 | 99010800
2023-06-29 | -7526.79 | 6.108 | 45.8261 | 59.8258 | -2205.8844 |  | 1224 | 4406400 | 35942400 | 67478400 | 99014400
2023-06-30 01:00 | -8220.29 | 6.108 | 45.1318 | 59.8258 | -2409.1292 |  | 1225 | 4410000 | 35946000 | 67482000 | 99018000
2023-07-01 02:00 | -8377.83 | 6.108 | 44.7798 | 59.8258 | -2455.2996 |  | 1226 | 4413600 | 35949600 | 67485600 | 99021600
2023-07-02 03:00 | -8607.38 | 6.108 | 44.4158 | 59.8258 | -2522.5741 |  | 1227 | 4417200 | 35953200 | 67489200 | 99025200
2023-07-03 04:00 | -8624.1 | 6.108 | 44.2218 | 59.8258 | -2527.4742 |  | 1228 | 4420800 | 35956800 | 67492800 | 99028800
2023-07-04 05:00 | -8653.17 | 6.108 | 44.0655 | 59.8258 | -2535.9938 |  | 1229 | 4424400 | 35960400 | 67496400 | 99032400
2023-07-05 06:00 | -8494.27 | 6.108 | 44.0627 | 59.8258 | -2489.4248 |  | 1230 | 4428000 | 35964000 | 67500000 | 99036000
2023-07-06 07:00 | -8304.63 | 6.108 | 44.1361 | 59.8258 | -2433.8468 |  | 1231 | 4431600 | 35967600 | 67503600 | 99039600
2023-07-07 08:00 | -6354.71 | 6.108 | 45.5655 | 59.8258 | -1862.3817 |  | 1232 | 4435200 | 35971200 | 67507200 | 99043200
2023-07-08 09:00 | -5001.84 | 6.108 | 46.8209 | 59.8258 | -1465.8946 |  | 1233 | 4438800 | 35974800 | 67510800 | 99046800
2023-07-09 10:00 | -2821.12 | 6.108 | 48.7633 | 59.8258 | -826.7887 |  | 1234 | 4442400 | 35978400 | 67514400 | 99050400
2023-07-10 11:00 | -1124.39 | 3.6841 | 49.943 | 59.8258 | -329.5262 |  | 1235 | 4446000 | 35982000 | 67518000 | 99054000
2023-07-11 12:00 | 2302.82 | 1 | 51.657 | 59.8258 | 674.8899 |  | 1236 | 4449600 | 35985600 | 67521600 | 99057600
2023-07-12 13:00 | 3127.47 | 1 | 52.3905 | 59.8258 | 916.571 |  | 1237 | 4453200 | 35989200 | 67525200 | 99061200
2023-07-13 14:00 | 3181.9 | 1 | 71.9195 | 59.8258 | 932.5228 |  | 1238 | 4456800 | 35992800 | 67528800 | 99064800
2023-07-14 15:00 | 3155.2 | 1.0082 | 68.0003 | 59.8258 | 924.6978 |  | 1239 | 4460400 | 35996400 | 67532400 | 99068400
2023-07-15 16:00 | 3130.41 | 1 | 70.2634 | 59.8258 | 917.4326 |  | 1240 | 4464000 | 36000000 | 67536000 | 99072000
2023-07-16 17:00 | 2981.21 | 1 | 54.0305 | 59.8258 | 873.7064 |  | 1241 | 4467600 | 36003600 | 67539600 | 99075600
2023-07-17 18:00 | 0 | 0 | 54.4977 | 59.8258 | 0 |  | 1242 | 4471200 | 36007200 | 67543200 | 99079200
2023-07-18 19:00 | -1222.75 | 3.9459 | 52.8651 | 59.8258 | -358.3527 |  | 1243 | 4474800 | 36010800 | 67546800 | 99082800
2023-07-19 20:00 | -1696.55 | 5.5489 | 52.6716 | 59.8258 | -497.2097 |  | 1244 | 4478400 | 36014400 | 67550400 | 99086400
2023-07-20 21:00 | -3378.55 | 6.108 | 51.4254 | 59.8258 | -990.1553 |  | 1245 | 4482000 | 36018000 | 67554000 | 99090000
2023-07-21 22:00 | -3895.04 | 6.108 | 50.745 | 59.8258 | -1141.5235 |  | 1246 | 4485600 | 36021600 | 67557600 | 99093600
2023-07-22 23:00 | -4960.1 | 6.108 | 49.6865 | 59.8258 | -1453.6618 |  | 1247 | 4489200 | 36025200 | 67561200 | 99097200
2023-07-24 | -5249.76 | 6.108 | 49.1852 | 59.8258 | -1538.5528 |  | 1248 | 4492800 | 36028800 | 67564800 | 99100800
2023-07-25 01:00 | -5501.05 | 6.108 | 48.7767 | 59.8258 | -1612.1986 |  | 1249 | 4496400 | 36032400 | 67568400 | 99104400
2023-07-26 02:00 | -5655.44 | 6.108 | 48.4721 | 59.8258 | -1657.4459 |  | 1250 | 4500000 | 36036000 | 67572000 | 99108000
2023-07-27 03:00 | -5607.99 | 6.108 | 48.3632 | 59.8258 | -1643.5396 |  | 1251 | 4503600 | 36039600 | 67575600 | 99111600
2023-07-28 04:00 | -5519.94 | 6.108 | 48.3208 | 59.8258 | -1617.7347 |  | 1252 | 4507200 | 36043200 | 67579200 | 99115200
2023-07-29 05:00 | -5367.83 | 6.108 | 48.3656 | 59.8258 | -1573.1557 |  | 1253 | 4510800 | 36046800 | 67582800 | 99118800
2023-07-30 06:00 | -5179.1 | 6.108 | 48.4903 | 59.8258 | -1517.8444 |  | 1254 | 4514400 | 36050400 | 67586400 | 99122400
2023-07-31 07:00 | -5276.94 | 6.108 | 48.4312 | 59.8258 | -1546.5185 |  | 1255 | 4518000 | 36054000 | 67590000 | 99126000
2023-08-01 08:00 | -3929.92 | 6.108 | 49.4232 | 59.8258 | -1151.7459 |  | 1256 | 4521600 | 36057600 | 67593600 | 99129600
2023-08-02 09:00 | -3352.77 | 6.108 | 50.0327 | 59.8258 | -982.5999 |  | 1257 | 4525200 | 36061200 | 67597200 | 99133200
2023-08-03 10:00 | -2800.04 | 6.108 | 50.6161 | 59.8258 | -820.6107 |  | 1258 | 4528800 | 36064800 | 67600800 | 99136800
2023-08-04 11:00 | -1790.71 | 5.7739 | 51.4538 | 59.8258 | -524.8053 |  | 1259 | 4532400 | 36068400 | 67604400 | 99140400
2023-08-05 12:00 | -1163.95 | 3.7225 | 51.6619 | 59.8258 | -341.1201 |  | 1260 | 4536000 | 36072000 | 67608000 | 99144000
2023-08-06 13:00 | -875.497 | 3.0108 | 51.9907 | 59.8258 | -256.5828 |  | 1261 | 4539600 | 36075600 | 67611600 | 99147600
2023-08-07 14:00 | -185.85 | 0.90509 | 52.5422 | 59.8258 | -54.4673 |  | 1262 | 4543200 | 36079200 | 67615200 | 99151200
2023-08-08 15:00 | 336.643 | 1 | 53.6597 | 59.8258 | 98.6603 |  | 1263 | 4546800 | 36082800 | 67618800 | 99154800
2023-08-09 16:00 | 2676.59 | 1 | 53.6632 | 59.8258 | 784.4311 |  | 1264 | 4550400 | 36086400 | 67622400 | 99158400
2023-08-10 17:00 | 3039.67 | 1 | 54.0816 | 59.8258 | 890.8393 |  | 1265 | 4554000 | 36090000 | 67626000 | 99162000
2023-08-11 18:00 | 2899.29 | 1 | 54.4491 | 59.8258 | 849.698 |  | 1266 | 4557600 | 36093600 | 67629600 | 99165600
2023-08-12 19:00 | -273.042 | 1.444 | 54.0753 | 59.8258 | -80.0207 |  | 1267 | 4561200 | 36097200 | 67633200 | 99169200
2023-08-13 20:00 | -783.163 | 2.8941 | 53.4809 | 59.8258 | -229.5224 |  | 1268 | 4564800 | 36100800 | 67636800 | 99172800
2023-08-14 21:00 | -1841.66 | 6.0751 | 53.2262 | 59.8258 | -539.7373 |  | 1269 | 4568400 | 36104400 | 67640400 | 99176400
2023-08-15 22:00 | -2563.7 | 6.108 | 52.5231 | 59.8258 | -751.3463 |  | 1270 | 4572000 | 36108000 | 67644000 | 99180000
2023-08-16 23:00 | -3765.99 | 6.108 | 51.4217 | 59.8258 | -1103.7027 |  | 1271 | 4575600 | 36111600 | 67647600 | 99183600
2023-08-18 | -4021.27 | 6.108 | 50.9428 | 59.8258 | -1178.5179 |  | 1272 | 4579200 | 36115200 | 67651200 | 99187200
2023-08-19 01:00 | -4457.15 | 6.108 | 50.4608 | 59.8258 | -1306.2617 |  | 1273 | 4582800 | 36118800 | 67654800 | 99190800
2023-08-20 02:00 | -4618.81 | 6.108 | 50.1864 | 59.8258 | -1353.6396 |  | 1274 | 4586400 | 36122400 | 67658400 | 99194400
2023-08-21 03:00 | -4185.62 | 6.108 | 50.3892 | 59.8258 | -1226.6841 |  | 1275 | 4590000 | 36126000 | 67662000 | 99198000
2023-08-22 04:00 | -4406.33 | 6.108 | 50.1743 | 59.8258 | -1291.3678 |  | 1276 | 4593600 | 36129600 | 67665600 | 99201600
2023-08-23 05:00 | -4532.69 | 6.108 | 50.0033 | 59.8258 | -1328.4003 |  | 1277 | 4597200 | 36133200 | 67669200 | 99205200
2023-08-24 06:00 | -3394.22 | 6.108 | 50.767 | 59.8258 | -994.7477 |  | 1278 | 4600800 | 36136800 | 67672800 | 99208800
2023-08-25 07:00 | -3312.6 | 6.108 | 50.9548 | 59.8258 | -970.8272 |  | 1279 | 4604400 | 36140400 | 67676400 | 99212400
2023-08-26 08:00 | -2402.92 | 6.108 | 51.7082 | 59.8258 | -704.2263 |  | 1280 | 4608000 | 36144000 | 67680000 | 99216000
2023-08-27 09:00 | -1931.4 | 6.108 | 52.2082 | 59.8258 | -566.0375 |  | 1281 | 4611600 | 36147600 | 67683600 | 99219600
2023-08-28 10:00 | -1356.04 | 4.2607 | 52.3531 | 59.8258 | -397.4161 |  | 1282 | 4615200 | 36151200 | 67687200 | 99223200
2023-08-29 11:00 | -374.893 | 1.3594 | 52.7256 | 59.8258 | -109.8703 |  | 1283 | 4618800 | 36154800 | 67690800 | 99226800
2023-08-30 12:00 | 2276.11 | 1 | 54.0246 | 59.8258 | 667.062 |  | 1284 | 4622400 | 36158400 | 67694400 | 99230400
2023-08-31 13:00 | 2065.7 | 1 | 54.5564 | 59.8258 | 605.3969 |  | 1285 | 4626000 | 36162000 | 67698000 | 99234000
2023-09-01 14:00 | 3177.9 | 1 | 54.7355 | 59.8258 | 931.3506 |  | 1286 | 4629600 | 36165600 | 67701600 | 99237600
2023-09-02 15:00 | 3162.84 | 1 | 75.2425 | 59.8258 | 926.9369 |  | 1287 | 4633200 | 36169200 | 67705200 | 99241200
2023-09-03 16:00 | 3342.45 | 1.0603 | 70.0018 | 59.8258 | 979.5754 |  | 1288 | 4636800 | 36172800 | 67708800 | 99244800
2023-09-04 17:00 | 3138.99 | 1 | 73.1189 | 59.8258 | 919.9472 |  | 1289 | 4640400 | 36176400 | 67712400 | 99248400
2023-09-05 18:00 | 3009.95 | 1 | 55.6453 | 59.8258 | 882.1293 |  | 1290 | 4644000 | 36180000 | 67716000 | 99252000
2023-09-06 19:00 | 0 | 0 | 56.0474 | 59.8258 | 0 |  | 1291 | 4647600 | 36183600 | 67719600 | 99255600
2023-09-07 20:00 | -437.043 | 1.5534 | 54.4552 | 59.8258 | -128.0847 |  | 1292 | 4651200 | 36187200 | 67723200 | 99259200
2023-09-08 21:00 | -1311.76 | 4.4745 | 54.2295 | 59.8258 | -384.4389 |  | 1293 | 4654800 | 36190800 | 67726800 | 99262800
2023-09-09 22:00 | -1820.35 | 5.7844 | 53.9621 | 59.8258 | -533.4919 |  | 1294 | 4658400 | 36194400 | 67730400 | 99266400
2023-09-10 23:00 | -2564.21 | 6.108 | 53.3112 | 59.8258 | -751.4958 |  | 1295 | 4662000 | 36198000 | 67734000 | 99270000
2023-09-12 | -2681.25 | 6.108 | 52.9871 | 59.8258 | -785.7968 |  | 1296 | 4665600 | 36201600 | 67737600 | 99273600
2023-09-13 01:00 | -2529.71 | 6.108 | 52.9834 | 59.8258 | -741.3848 |  | 1297 | 4669200 | 36205200 | 67741200 | 99277200
2023-09-14 02:00 | -2581 | 6.108 | 52.88 | 59.8258 | -756.4164 |  | 1298 | 4672800 | 36208800 | 67744800 | 99280800
2023-09-15 03:00 | -2525.18 | 6.108 | 52.8636 | 59.8258 | -740.0572 |  | 1299 | 4676400 | 36212400 | 67748400 | 99284400
2023-09-16 04:00 | -2641.67 | 6.108 | 52.7338 | 59.8258 | -774.1971 |  | 1300 | 4680000 | 36216000 | 67752000 | 99288000
2023-09-17 05:00 | -2783 | 6.108 | 52.5869 | 59.8258 | -815.6168 |  | 1301 | 4683600 | 36219600 | 67755600 | 99291600
2023-09-18 06:00 | -2786.84 | 6.108 | 52.5243 | 59.8258 | -816.7422 |  | 1302 | 4687200 | 36223200 | 67759200 | 99295200
2023-09-19 07:00 | -1949.27 | 6.108 | 53.1344 | 59.8258 | -571.2746 |  | 1303 | 4690800 | 36226800 | 67762800 | 99298800
2023-09-20 08:00 | -1402.7 | 4.356 | 53.2157 | 59.8258 | -411.0908 |  | 1304 | 4694400 | 36230400 | 67766400 | 99302400
2023-09-21 09:00 | -1705.46 | 5.4809 | 53.3944 | 59.8258 | -499.821 |  | 1305 | 4698000 | 36234000 | 67770000 | 99306000
2023-09-22 10:00 | -1675.26 | 5.2673 | 53.3891 | 59.8258 | -490.9702 |  | 1306 | 4701600 | 36237600 | 67773600 | 99309600
2023-09-23 11:00 | -1159.03 | 3.6725 | 53.4273 | 59.8258 | -339.6782 |  | 1307 | 4705200 | 36241200 | 67777200 | 99313200
2023-09-24 12:00 | -452.456 | 1.6438 | 53.7007 | 59.8258 | -132.6018 |  | 1308 | 4708800 | 36244800 | 67780800 | 99316800
2023-09-25 13:00 | -89.1343 | 0.73349 | 54.542 | 59.8258 | -26.1227 |  | 1309 | 4712400 | 36248400 | 67784400 | 99320400
2023-09-26 14:00 | -77.2688 | 0.78602 | 54.7517 | 59.8258 | -22.6452 |  | 1310 | 4716000 | 36252000 | 67788000 | 99324000
2023-09-27 15:00 | 60.7128 | 1 | 55.2617 | 59.8258 | 17.7932 |  | 1311 | 4719600 | 36255600 | 67791600 | 99327600
2023-09-28 16:00 | 129.052 | 1 | 55.3166 | 59.8258 | 37.8214 |  | 1312 | 4723200 | 36259200 | 67795200 | 99331200
2023-09-29 17:00 | 2708.61 | 1 | 55.1443 | 59.8258 | 793.8152 |  | 1313 | 4726800 | 36262800 | 67798800 | 99334800
2023-09-30 18:00 | 2998.56 | 1 | 55.5041 | 59.8258 | 878.7912 |  | 1314 | 4730400 | 36266400 | 67802400 | 99338400
2023-10-01 19:00 | 0 | 0 | 56.0551 | 59.8258 | 0 |  | 1315 | 4734000 | 36270000 | 67806000 | 99342000
2023-10-02 20:00 | -471.926 | 1.9689 | 54.7262 | 59.8258 | -138.3079 |  | 1316 | 4737600 | 36273600 | 67809600 | 99345600
2023-10-03 21:00 | -675.168 | 2.4798 | 54.4558 | 59.8258 | -197.8722 |  | 1317 | 4741200 | 36277200 | 67813200 | 99349200
2023-10-04 22:00 | -1031.81 | 3.5227 | 54.3484 | 59.8258 | -302.3937 |  | 1318 | 4744800 | 36280800 | 67816800 | 99352800
2023-10-05 23:00 | -1263 | 4.1363 | 54.203 | 59.8258 | -370.1488 |  | 1319 | 4748400 | 36284400 | 67820400 | 99356400
2023-10-07 | -2676.97 | 6.108 | 53.4912 | 59.8258 | -784.5425 |  | 1320 | 4752000 | 36288000 | 67824000 | 99360000
2023-10-08 01:00 | -3154.48 | 6.108 | 52.9243 | 59.8258 | -924.4868 |  | 1321 | 4755600 | 36291600 | 67827600 | 99363600
2023-10-09 02:00 | -3394.48 | 6.108 | 52.5703 | 59.8258 | -994.8239 |  | 1322 | 4759200 | 36295200 | 67831200 | 99367200
2023-10-10 03:00 | -3514.28 | 6.108 | 52.3517 | 59.8258 | -1029.9338 |  | 1323 | 4762800 | 36298800 | 67834800 | 99370800
2023-10-11 04:00 | -3612.65 | 6.108 | 52.1713 | 59.8258 | -1058.7632 |  | 1324 | 4766400 | 36302400 | 67838400 | 99374400
2023-10-12 05:00 | -3839.96 | 6.108 | 51.8731 | 59.8258 | -1125.3812 |  | 1325 | 4770000 | 36306000 | 67842000 | 99378000
2023-10-13 06:00 | -3910.64 | 6.108 | 51.6959 | 59.8258 | -1146.0954 |  | 1326 | 4773600 | 36309600 | 67845600 | 99381600
2023-10-14 07:00 | -3221.71 | 6.108 | 52.1343 | 59.8258 | -944.19 |  | 1327 | 4777200 | 36313200 | 67849200 | 99385200
2023-10-15 08:00 | -2520.08 | 6.108 | 52.6903 | 59.8258 | -738.5625 |  | 1328 | 4780800 | 36316800 | 67852800 | 99388800
2023-10-16 09:00 | -3124.22 | 6.108 | 52.33 | 59.8258 | -915.6185 |  | 1329 | 4784400 | 36320400 | 67856400 | 99392400
2023-10-17 10:00 | -2696.39 | 6.108 | 52.5959 | 59.8258 | -790.2339 |  | 1330 | 4788000 | 36324000 | 67860000 | 99396000
2023-10-18 11:00 | -2179.43 | 6.108 | 52.9968 | 59.8258 | -638.7279 |  | 1331 | 4791600 | 36327600 | 67863600 | 99399600
2023-10-19 12:00 | -1736.05 | 5.415 | 53.2411 | 59.8258 | -508.786 |  | 1332 | 4795200 | 36331200 | 67867200 | 99403200
2023-10-20 13:00 | -1866.77 | 5.8807 | 53.338 | 59.8258 | -547.0963 |  | 1333 | 4798800 | 36334800 | 67870800 | 99406800
2023-10-21 14:00 | -2085.93 | 6.108 | 53.2323 | 59.8258 | -611.3257 |  | 1334 | 4802400 | 36338400 | 67874400 | 99410400
2023-10-22 15:00 | -2086.78 | 6.108 | 53.2119 | 59.8258 | -611.5748 |  | 1335 | 4806000 | 36342000 | 67878000 | 99414000
2023-10-23 16:00 | -2094.61 | 6.108 | 53.1933 | 59.8258 | -613.8696 |  | 1336 | 4809600 | 36345600 | 67881600 | 99417600
2023-10-24 17:00 | -945.277 | 2.9288 | 53.2517 | 59.8258 | -277.0333 |  | 1337 | 4813200 | 36349200 | 67885200 | 99421200
2023-10-25 18:00 | -1424.03 | 4.7402 | 53.4806 | 59.8258 | -417.342 |  | 1338 | 4816800 | 36352800 | 67888800 | 99424800
2023-10-26 19:00 | -1799.03 | 5.7314 | 53.4373 | 59.8258 | -527.2436 |  | 1339 | 4820400 | 36356400 | 67892400 | 99428400
2023-10-27 20:00 | -2239.81 | 6.108 | 53.1519 | 59.8258 | -656.4235 |  | 1340 | 4824000 | 36360000 | 67896000 | 99432000
2023-10-28 21:00 | -2534.55 | 6.108 | 52.8782 | 59.8258 | -742.8033 |  | 1341 | 4827600 | 36363600 | 67899600 | 99435600
2023-10-29 22:00 | -2476.72 | 6.108 | 52.8667 | 59.8258 | -725.855 |  | 1342 | 4831200 | 36367200 | 67903200 | 99439200
2023-10-30 23:00 | -2781.05 | 6.108 | 52.5972 | 59.8258 | -815.0453 |  | 1343 | 4834800 | 36370800 | 67906800 | 99442800
2023-11-01 | -3758.22 | 6.108 | 51.8043 | 59.8258 | -1101.4256 |  | 1344 | 4838400 | 36374400 | 67910400 | 99446400
2023-11-02 01:00 | -3946.47 | 6.108 | 51.4969 | 59.8258 | -1156.5962 |  | 1345 | 4842000 | 36378000 | 67914000 | 99450000
2023-11-03 02:00 | -4155.69 | 6.108 | 51.2295 | 59.8258 | -1217.9125 |  | 1346 | 4845600 | 36381600 | 67917600 | 99453600
2023-11-04 03:00 | -4138.7 | 6.108 | 51.1543 | 59.8258 | -1212.9332 |  | 1347 | 4849200 | 36385200 | 67921200 | 99457200
2023-11-05 04:00 | -4081.39 | 6.108 | 51.1299 | 59.8258 | -1196.1373 |  | 1348 | 4852800 | 36388800 | 67924800 | 99460800
2023-11-06 05:00 | -3871.52 | 6.108 | 51.2293 | 59.8258 | -1134.6305 |  | 1349 | 4856400 | 36392400 | 67928400 | 99464400
2023-11-07 06:00 | -3247.06 | 6.108 | 51.6929 | 59.8258 | -951.6193 |  | 1350 | 4860000 | 36396000 | 67932000 | 99468000
2023-11-08 07:00 | -3225.59 | 6.108 | 51.7776 | 59.8258 | -945.3271 |  | 1351 | 4863600 | 36399600 | 67935600 | 99471600
2023-11-09 08:00 | -2916.83 | 6.108 | 52.0389 | 59.8258 | -854.8385 |  | 1352 | 4867200 | 36403200 | 67939200 | 99475200
2023-11-10 09:00 | -2927.16 | 6.108 | 52.0868 | 59.8258 | -857.8659 |  | 1353 | 4870800 | 36406800 | 67942800 | 99478800
2023-11-11 10:00 | -2158.83 | 6.108 | 52.6924 | 59.8258 | -632.6906 |  | 1354 | 4874400 | 36410400 | 67946400 | 99482400
2023-11-12 11:00 | -773.175 | 2.4039 | 52.9485 | 59.8258 | -226.5952 |  | 1355 | 4878000 | 36414000 | 67950000 | 99486000
2023-11-13 12:00 | 0 | 1 | 54.6788 | 59.8258 | 0 |  | 1356 | 4881600 | 36417600 | 67953600 | 99489600
2023-11-14 13:00 | 3080.03 | 1 | 54.6628 | 59.8258 | 902.6677 |  | 1357 | 4885200 | 36421200 | 67957200 | 99493200
2023-11-15 14:00 | 3069.09 | 1 | 55.2422 | 59.8258 | 899.4615 |  | 1358 | 4888800 | 36424800 | 67960800 | 99496800
2023-11-16 15:00 | 3145.3 | 1 | 55.6093 | 59.8258 | 921.7964 |  | 1359 | 4892400 | 36428400 | 67964400 | 99500400
2023-11-17 16:00 | 3133.04 | 1 | 55.8677 | 59.8258 | 918.2034 |  | 1360 | 4896000 | 36432000 | 67968000 | 99504000
2023-11-18 17:00 | 3151.17 | 1 | 56.0682 | 59.8258 | 923.5168 |  | 1361 | 4899600 | 36435600 | 67971600 | 99507600
2023-11-19 18:00 | 3054.61 | 1 | 56.258 | 59.8258 | 895.2178 |  | 1362 | 4903200 | 36439200 | 67975200 | 99511200
2023-11-20 19:00 | -374.701 | 1.7059 | 55.6307 | 59.8258 | -109.814 |  | 1363 | 4906800 | 36442800 | 67978800 | 99514800
2023-11-21 20:00 | -962.935 | 3.3585 | 54.9749 | 59.8258 | -282.2084 |  | 1364 | 4910400 | 36446400 | 67982400 | 99518400
2023-11-22 21:00 | -2187.59 | 6.108 | 54.4225 | 59.8258 | -641.1193 |  | 1365 | 4914000 | 36450000 | 67986000 | 99522000
2023-11-23 22:00 | -2567.07 | 6.108 | 53.8865 | 59.8258 | -752.334 |  | 1366 | 4917600 | 36453600 | 67989600 | 99525600
2023-11-24 23:00 | -3255.63 | 6.108 | 53.1449 | 59.8258 | -954.131 |  | 1367 | 4921200 | 36457200 | 67993200 | 99529200
2023-11-26 | -3551.16 | 6.108 | 52.6721 | 59.8258 | -1040.7423 |  | 1368 | 4924800 | 36460800 | 67996800 | 99532800
2023-11-27 01:00 | -4035.89 | 6.108 | 52.1159 | 59.8258 | -1182.8026 |  | 1369 | 4928400 | 36464400 | 68000400 | 99536400
2023-11-28 02:00 | -4044.58 | 6.108 | 51.9063 | 59.8258 | -1185.3494 |  | 1370 | 4932000 | 36468000 | 68004000 | 99540000
2023-11-29 03:00 | -4466.81 | 6.108 | 51.4502 | 59.8258 | -1309.0928 |  | 1371 | 4935600 | 36471600 | 68007600 | 99543600
2023-11-30 04:00 | -4329.16 | 6.108 | 51.3819 | 59.8258 | -1268.7516 |  | 1372 | 4939200 | 36475200 | 68011200 | 99547200
2023-12-01 05:00 | -4385.65 | 6.108 | 51.2271 | 59.8258 | -1285.3071 |  | 1373 | 4942800 | 36478800 | 68014800 | 99550800
2023-12-02 06:00 | -3846.13 | 6.108 | 51.5208 | 59.8258 | -1127.1894 |  | 1374 | 4946400 | 36482400 | 68018400 | 99554400
2023-12-03 07:00 | -3761.73 | 6.108 | 51.5931 | 59.8258 | -1102.4542 |  | 1375 | 4950000 | 36486000 | 68022000 | 99558000
2023-12-04 08:00 | -3521.84 | 6.108 | 51.7659 | 59.8258 | -1032.1494 |  | 1376 | 4953600 | 36489600 | 68025600 | 99561600
2023-12-05 09:00 | -3617.43 | 6.108 | 51.7219 | 59.8258 | -1060.1641 |  | 1377 | 4957200 | 36493200 | 68029200 | 99565200
2023-12-06 10:00 | -3515.94 | 6.108 | 51.7898 | 59.8258 | -1030.4203 |  | 1378 | 4960800 | 36496800 | 68032800 | 99568800
2023-12-07 11:00 | -1965.55 | 6.108 | 52.9532 | 59.8258 | -576.0458 |  | 1379 | 4964400 | 36500400 | 68036400 | 99572400
2023-12-08 12:00 | -1135.21 | 3.523 | 53.1395 | 59.8258 | -332.6972 |  | 1380 | 4968000 | 36504000 | 68040000 | 99576000
2023-12-09 13:00 | -414.811 | 1.5458 | 53.584 | 59.8258 | -121.5691 |  | 1381 | 4971600 | 36507600 | 68043600 | 99579600
2023-12-10 14:00 | 0 | 0 | 55.0091 | 59.8258 | 0 |  | 1382 | 4975200 | 36511200 | 68047200 | 99583200
2023-12-11 15:00 | 2801.39 | 1 | 54.9485 | 59.8258 | 821.0064 |  | 1383 | 4978800 | 36514800 | 68050800 | 99586800
2023-12-12 16:00 | 2857.17 | 1 | 55.4589 | 59.8258 | 837.3539 |  | 1384 | 4982400 | 36518400 | 68054400 | 99590400
2023-12-13 17:00 | 96.1092 | 1 | 56.0113 | 59.8258 | 28.1668 |  | 1385 | 4986000 | 36522000 | 68058000 | 99594000
2023-12-14 18:00 | -856.842 | 3.1345 | 54.5765 | 59.8258 | -251.1156 |  | 1386 | 4989600 | 36525600 | 68061600 | 99597600
2023-12-15 19:00 | -2100.98 | 6.108 | 54.1 | 59.8258 | -615.7365 |  | 1387 | 4993200 | 36529200 | 68065200 | 99601200
2023-12-16 20:00 | -2941.04 | 6.108 | 53.2863 | 59.8258 | -861.9337 |  | 1388 | 4996800 | 36532800 | 68068800 | 99604800
2023-12-17 21:00 | -4253.86 | 6.108 | 52.0532 | 59.8258 | -1246.6833 |  | 1389 | 5000400 | 36536400 | 68072400 | 99608400
2023-12-18 22:00 | -4805.11 | 6.108 | 51.3018 | 59.8258 | -1408.2387 |  | 1390 | 5004000 | 36540000 | 68076000 | 99612000
2023-12-19 23:00 | -6234.63 | 6.108 | 49.9713 | 59.8258 | -1827.1897 |  | 1391 | 5007600 | 36543600 | 68079600 | 99615600
2023-12-21 | -7099.74 | 6.108 | 48.9613 | 59.8258 | -2080.7284 |  | 1392 | 5011200 | 36547200 | 68083200 | 99619200
2023-12-22 01:00 | -7269.66 | 6.108 | 48.4792 | 59.8258 | -2130.527 |  | 1393 | 5014800 | 36550800 | 68086800 | 99622800
2023-12-23 02:00 | -7771.5 | 6.108 | 47.8396 | 59.8258 | -2277.6018 |  | 1394 | 5018400 | 36554400 | 68090400 | 99626400
2023-12-24 03:00 | -8034.8 | 6.108 | 47.3497 | 59.8258 | -2354.7674 |  | 1395 | 5022000 | 36558000 | 68094000 | 99630000
2023-12-25 04:00 | -8001.08 | 6.108 | 47.0929 | 59.8258 | -2344.8851 |  | 1396 | 5025600 | 36561600 | 68097600 | 99633600
2023-12-26 05:00 | -8103.19 | 6.108 | 46.8356 | 59.8258 | -2374.8106 |  | 1397 | 5029200 | 36565200 | 68101200 | 99637200
2023-12-27 06:00 | -8104.49 | 6.108 | 46.6722 | 59.8258 | -2375.1916 |  | 1398 | 5032800 | 36568800 | 68104800 | 99640800
2023-12-28 07:00 | -7614.51 | 6.108 | 46.8993 | 59.8258 | -2231.5926 |  | 1399 | 5036400 | 36572400 | 68108400 | 99644400
2023-12-29 08:00 | -6096.33 | 6.108 | 47.9892 | 59.8258 | -1786.658 |  | 1400 | 5040000 | 36576000 | 68112000 | 99648000
2023-12-30 09:00 | -4925.84 | 6.108 | 49.0214 | 59.8258 | -1443.6212 |  | 1401 | 5043600 | 36579600 | 68115600 | 99651600
2023-12-31 10:00 | -3128.55 | 6.108 | 50.5817 | 59.8258 | -916.8875 |  | 1402 | 5047200 | 36583200 | 68119200 | 99655200
2024-01-01 11:00 | -1331 | 4.2651 | 51.8385 | 59.8258 | -390.0776 |  | 1403 | 5050800 | 36586800 | 68122800 | 99658800
2024-01-02 12:00 | 2233.7 | 1 | 53.5224 | 59.8258 | 654.6328 |  | 1404 | 5054400 | 36590400 | 68126400 | 99662400
2024-01-03 13:00 | 2918.78 | 1 | 54.2081 | 59.8258 | 855.41 |  | 1405 | 5058000 | 36594000 | 68130000 | 99666000
2024-01-04 14:00 | 2922.54 | 1 | 73.4774 | 59.8258 | 856.5119 |  | 1406 | 5061600 | 36597600 | 68133600 | 99669600
2024-01-05 15:00 | 2888.78 | 1 | 70.9696 | 59.8258 | 846.6178 |  | 1407 | 5065200 | 36601200 | 68137200 | 99673200
2024-01-06 16:00 | 3069.35 | 1.0569 | 68.9025 | 59.8258 | 899.5377 |  | 1408 | 5068800 | 36604800 | 68140800 | 99676800
2024-01-07 17:00 | 2888.63 | 1 | 74.5436 | 59.8258 | 846.5739 |  | 1409 | 5072400 | 36608400 | 68144400 | 99680400
2024-01-08 18:00 | 0 | 0 | 56.046 | 59.8258 | 0 |  | 1410 | 5076000 | 36612000 | 68148000 | 99684000
2024-01-09 19:00 | -1391 | 4.7033 | 54.4609 | 59.8258 | -407.6619 |  | 1411 | 5079600 | 36615600 | 68151600 | 99687600
2024-01-10 20:00 | -2675.87 | 6.108 | 53.5515 | 59.8258 | -784.2201 |  | 1412 | 5083200 | 36619200 | 68155200 | 99691200
2024-01-11 21:00 | -4215.02 | 6.108 | 52.14 | 59.8258 | -1235.3004 |  | 1413 | 5086800 | 36622800 | 68158800 | 99694800
2024-01-12 22:00 | -4921.83 | 6.108 | 51.2419 | 59.8258 | -1442.446 |  | 1414 | 5090400 | 36626400 | 68162400 | 99698400
2024-01-13 23:00 | -6121.34 | 6.108 | 50.0048 | 59.8258 | -1793.9877 |  | 1415 | 5094000 | 36630000 | 68166000 | 99702000
2024-01-15 | -6562 | 6.108 | 49.298 | 59.8258 | -1923.1324 |  | 1416 | 5097600 | 36633600 | 68169600 | 99705600
2024-01-16 01:00 | -6938.55 | 6.108 | 48.7 | 59.8258 | -2033.4883 |  | 1417 | 5101200 | 36637200 | 68173200 | 99709200
2024-01-17 02:00 | -7205.42 | 6.108 | 48.2319 | 59.8258 | -2111.7001 |  | 1418 | 5104800 | 36640800 | 68176800 | 99712800
2024-01-18 03:00 | -7372.43 | 6.108 | 47.8777 | 59.8258 | -2160.6459 |  | 1419 | 5108400 | 36644400 | 68180400 | 99716400
2024-01-19 04:00 | -7140.65 | 6.108 | 47.8424 | 59.8258 | -2092.7179 |  | 1420 | 5112000 | 36648000 | 68184000 | 99720000
2024-01-20 05:00 | -6967.56 | 6.108 | 47.845 | 59.8258 | -2041.9903 |  | 1421 | 5115600 | 36651600 | 68187600 | 99723600
2024-01-21 06:00 | -6461.61 | 6.108 | 48.1554 | 59.8258 | -1893.711 |  | 1422 | 5119200 | 36655200 | 68191200 | 99727200
2024-01-22 07:00 | -6028.06 | 6.108 | 48.4838 | 59.8258 | -1766.65 |  | 1423 | 5122800 | 36658800 | 68194800 | 99730800
2024-01-23 08:00 | -5548.5 | 6.108 | 48.8797 | 59.8258 | -1626.1048 |  | 1424 | 5126400 | 36662400 | 68198400 | 99734400
2024-01-24 09:00 | -5803.54 | 6.108 | 48.7619 | 59.8258 | -1700.8497 |  | 1425 | 5130000 | 36666000 | 68202000 | 99738000
2024-01-25 10:00 | -5154.61 | 6.108 | 49.2341 | 59.8258 | -1510.6671 |  | 1426 | 5133600 | 36669600 | 68205600 | 99741600
2024-01-26 11:00 | -4288.63 | 6.108 | 49.9498 | 59.8258 | -1256.8734 |  | 1427 | 5137200 | 36673200 | 68209200 | 99745200
2024-01-27 12:00 | -3218.3 | 6.108 | 50.8762 | 59.8258 | -943.1906 |  | 1428 | 5140800 | 36676800 | 68212800 | 99748800
2024-01-28 13:00 | -2694.47 | 6.108 | 51.4549 | 59.8258 | -789.6712 |  | 1429 | 5144400 | 36680400 | 68216400 | 99752400
2024-01-29 14:00 | -2443.92 | 6.108 | 51.8 | 59.8258 | -716.2422 |  | 1430 | 5148000 | 36684000 | 68220000 | 99756000
2024-01-30 15:00 | -2433.07 | 6.108 | 51.9328 | 59.8258 | -713.0624 |  | 1431 | 5151600 | 36687600 | 68223600 | 99759600
2024-01-31 16:00 | -1484.34 | 4.6911 | 52.3809 | 59.8258 | -435.0171 |  | 1432 | 5155200 | 36691200 | 68227200 | 99763200
2024-02-01 17:00 | -1577.83 | 5.1012 | 52.596 | 59.8258 | -462.4163 |  | 1433 | 5158800 | 36694800 | 68230800 | 99766800
2024-02-02 18:00 | -1788.99 | 5.7218 | 52.6883 | 59.8258 | -524.3012 |  | 1434 | 5162400 | 36698400 | 68234400 | 99770400
2024-02-03 19:00 | -2197.13 | 6.108 | 52.5204 | 59.8258 | -643.9152 |  | 1435 | 5166000 | 36702000 | 68238000 | 99774000
2024-02-04 20:00 | -2773.09 | 6.108 | 52.0946 | 59.8258 | -812.7125 |  | 1436 | 5169600 | 36705600 | 68241600 | 99777600
2024-02-05 21:00 | -3796.25 | 6.108 | 51.3019 | 59.8258 | -1112.571 |  | 1437 | 5173200 | 36709200 | 68245200 | 99781200
2024-02-06 22:00 | -4109.09 | 6.108 | 50.9249 | 59.8258 | -1204.2554 |  | 1438 | 5176800 | 36712800 | 68248800 | 99784800
2024-02-07 23:00 | -4697.11 | 6.108 | 50.3816 | 59.8258 | -1376.5871 |  | 1439 | 5180400 | 36716400 | 68252400 | 99788400
2024-02-09 | -4879.6 | 6.108 | 50.1141 | 59.8258 | -1430.0696 |  | 1440 | 5184000 | 36720000 | 68256000 | 99792000
2024-02-10 01:00 | -5250.75 | 6.108 | 49.7312 | 59.8258 | -1538.8429 |  | 1441 | 5187600 | 36723600 | 68259600 | 99795600
2024-02-11 02:00 | -5275.98 | 6.108 | 49.6015 | 59.8258 | -1546.2371 |  | 1442 | 5191200 | 36727200 | 68263200 | 99799200
2024-02-12 03:00 | -4992.11 | 6.108 | 49.753 | 59.8258 | -1463.043 |  | 1443 | 5194800 | 36730800 | 68266800 | 99802800
2024-02-13 04:00 | -5033.87 | 6.108 | 49.7084 | 59.8258 | -1475.2817 |  | 1444 | 5198400 | 36734400 | 68270400 | 99806400
2024-02-14 05:00 | -4846.21 | 6.108 | 49.8278 | 59.8258 | -1420.284 |  | 1445 | 5202000 | 36738000 | 68274000 | 99810000
2024-02-15 06:00 | -4312.39 | 6.108 | 50.2282 | 59.8258 | -1263.8368 |  | 1446 | 5205600 | 36741600 | 68277600 | 99813600
2024-02-16 07:00 | -4175.53 | 6.108 | 50.404 | 59.8258 | -1223.727 |  | 1447 | 5209200 | 36745200 | 68281200 | 99817200
2024-02-17 08:00 | -3529.13 | 6.108 | 50.942 | 59.8258 | -1034.2859 |  | 1448 | 5212800 | 36748800 | 68284800 | 99820800
2024-02-18 09:00 | -3482.6 | 6.108 | 51.0953 | 59.8258 | -1020.6493 |  | 1449 | 5216400 | 36752400 | 68288400 | 99824400
2024-02-19 10:00 | -2794.03 | 6.108 | 51.6885 | 59.8258 | -818.8494 |  | 1450 | 5220000 | 36756000 | 68292000 | 99828000
2024-02-20 11:00 | -2321.7 | 6.108 | 52.1781 | 59.8258 | -680.4231 |  | 1451 | 5223600 | 36759600 | 68295600 | 99831600
2024-02-21 12:00 | -1872.56 | 5.9103 | 52.5985 | 59.8258 | -548.7932 |  | 1452 | 5227200 | 36763200 | 68299200 | 99835200
2024-02-22 13:00 | -621.293 | 1.9523 | 52.719 | 59.8258 | -182.083 |  | 1453 | 5230800 | 36766800 | 68302800 | 99838800
2024-02-23 14:00 | 308.839 | 1 | 54.4006 | 59.8258 | 90.5118 |  | 1454 | 5234400 | 36770400 | 68306400 | 99842400
2024-02-24 15:00 | 3130.8 | 1 | 54.4347 | 59.8258 | 917.5469 |  | 1455 | 5238000 | 36774000 | 68310000 | 99846000
2024-02-25 16:00 | 3096.73 | 1 | 72.8929 | 59.8258 | 907.562 |  | 1456 | 5241600 | 36777600 | 68313600 | 99849600
2024-02-26 17:00 | 3017.19 | 1 | 55.3225 | 59.8258 | 884.2511 |  | 1457 | 5245200 | 36781200 | 68317200 | 99853200
2024-02-27 18:00 | 0 | 0 | 55.8237 | 59.8258 | 0 |  | 1458 | 5248800 | 36784800 | 68320800 | 99856800
2024-02-28 19:00 | -1374.47 | 4.3624 | 54.1832 | 59.8258 | -402.8174 |  | 1459 | 5252400 | 36788400 | 68324400 | 99860400
2024-02-29 20:00 | -2339.74 | 6.108 | 53.644 | 59.8258 | -685.7101 |  | 1460 | 5256000 | 36792000 | 68328000 | 99864000
2024-03-01 21:00 | -3727.36 | 6.108 | 52.3714 | 59.8258 | -1092.3814 |  | 1461 | 5259600 | 36795600 | 68331600 | 99867600
2024-03-02 22:00 | -4853.28 | 6.108 | 51.2036 | 59.8258 | -1422.356 |  | 1462 | 5263200 | 36799200 | 68335200 | 99871200
2024-03-03 23:00 | -5943.42 | 6.108 | 50.0254 | 59.8258 | -1741.8445 |  | 1463 | 5266800 | 36802800 | 68338800 | 99874800
2024-03-05 | -6627.83 | 6.108 | 49.1803 | 59.8258 | -1942.4252 |  | 1464 | 5270400 | 36806400 | 68342400 | 99878400
2024-03-06 01:00 | -7003.95 | 6.108 | 48.5955 | 59.8258 | -2052.6551 |  | 1465 | 5274000 | 36810000 | 68346000 | 99882000
2024-03-07 02:00 | -7430.51 | 6.108 | 48.0109 | 59.8258 | -2177.6675 |  | 1466 | 5277600 | 36813600 | 68349600 | 99885600
2024-03-08 03:00 | -7398.27 | 6.108 | 47.7562 | 59.8258 | -2168.2189 |  | 1467 | 5281200 | 36817200 | 68353200 | 99889200
2024-03-09 04:00 | -7826.76 | 6.108 | 47.2232 | 59.8258 | -2293.7969 |  | 1468 | 5284800 | 36820800 | 68356800 | 99892800
2024-03-10 05:00 | -7934.98 | 6.108 | 46.9086 | 59.8258 | -2325.5131 |  | 1469 | 5288400 | 36824400 | 68360400 | 99896400
2024-03-11 06:00 | -8283.61 | 6.108 | 46.4659 | 59.8258 | -2427.6864 |  | 1470 | 5292000 | 36828000 | 68364000 | 99900000
2024-03-12 07:00 | -7391.54 | 6.108 | 46.9515 | 59.8258 | -2166.2465 |  | 1471 | 5295600 | 36831600 | 68367600 | 99903600
2024-03-13 08:00 | -5468.7 | 6.108 | 48.3745 | 59.8258 | -1602.7178 |  | 1472 | 5299200 | 36835200 | 68371200 | 99907200
2024-03-14 09:00 | -4591.41 | 6.108 | 49.2514 | 59.8258 | -1345.6094 |  | 1473 | 5302800 | 36838800 | 68374800 | 99910800
2024-03-15 10:00 | -2986.68 | 6.108 | 50.6677 | 59.8258 | -875.3095 |  | 1474 | 5306400 | 36842400 | 68378400 | 99914400
2024-03-16 11:00 | -1587.37 | 5.0935 | 51.8002 | 59.8258 | -465.2122 |  | 1475 | 5310000 | 36846000 | 68382000 | 99918000
2024-03-17 12:00 | 123.681 | 1 | 53.6157 | 59.8258 | 36.2473 |  | 1476 | 5313600 | 36849600 | 68385600 | 99921600
2024-03-18 13:00 | 3109.95 | 1 | 53.8255 | 59.8258 | 911.4364 |  | 1477 | 5317200 | 36853200 | 68389200 | 99925200
2024-03-19 14:00 | 3190.41 | 1 | 77.4749 | 59.8258 | 935.0169 |  | 1478 | 5320800 | 36856800 | 68392800 | 99928800
2024-03-20 15:00 | 3091.24 | 1 | 77.8002 | 59.8258 | 905.953 |  | 1479 | 5324400 | 36860400 | 68396400 | 99932400
2024-03-21 16:00 | 3117.73 | 1 | 78.5722 | 59.8258 | 913.7165 |  | 1480 | 5328000 | 36864000 | 68400000 | 99936000
2024-03-22 17:00 | 3643.96 | 1.168 | 69.9938 | 59.8258 | 1067.9393 |  | 1481 | 5331600 | 36867600 | 68403600 | 99939600
2024-03-23 18:00 | 2997.48 | 1 | 55.7859 | 59.8258 | 878.4747 |  | 1482 | 5335200 | 36871200 | 68407200 | 99943200
2024-03-24 19:00 | 0 | 0 | 56.1864 | 59.8258 | 0 |  | 1483 | 5338800 | 36874800 | 68410800 | 99946800
2024-03-25 20:00 | -972.966 | 3.1454 | 54.4899 | 59.8258 | -285.1482 |  | 1484 | 5342400 | 36878400 | 68414400 | 99950400
2024-03-26 21:00 | -1397.23 | 4.583 | 54.3009 | 59.8258 | -409.4877 |  | 1485 | 5346000 | 36882000 | 68418000 | 99954000
2024-03-27 22:00 | -2232.52 | 6.108 | 53.9045 | 59.8258 | -654.287 |  | 1486 | 5349600 | 36885600 | 68421600 | 99957600
2024-03-28 23:00 | -3069.45 | 6.108 | 53.0824 | 59.8258 | -899.567 |  | 1487 | 5353200 | 36889200 | 68425200 | 99961200
2024-03-30 | -4567.95 | 6.108 | 51.7123 | 59.8258 | -1338.734 |  | 1488 | 5356800 | 36892800 | 68428800 | 99964800
2024-03-31 01:00 | -5438.11 | 6.108 | 50.7206 | 59.8258 | -1593.7527 |  | 1489 | 5360400 | 36896400 | 68432400 | 99968400
2024-04-01 02:00 | -5431.2 | 6.108 | 50.4067 | 59.8258 | -1591.7276 |  | 1490 | 5364000 | 36900000 | 68436000 | 99972000
2024-04-02 03:00 | -4799.31 | 6.108 | 50.6756 | 59.8258 | -1406.5389 |  | 1491 | 5367600 | 36903600 | 68439600 | 99975600
2024-04-03 04:00 | -4560.43 | 6.108 | 50.7879 | 59.8258 | -1336.5301 |  | 1492 | 5371200 | 36907200 | 68443200 | 99979200
2024-04-04 05:00 | -4270.41 | 6.108 | 50.9481 | 59.8258 | -1251.5336 |  | 1493 | 5374800 | 36910800 | 68446800 | 99982800
2024-04-05 06:00 | -4431.45 | 6.108 | 50.8161 | 59.8258 | -1298.7298 |  | 1494 | 5378400 | 36914400 | 68450400 | 99986400
2024-04-06 07:00 | -3225.49 | 6.108 | 51.7098 | 59.8258 | -945.2978 |  | 1495 | 5382000 | 36918000 | 68454000 | 99990000
2024-04-07 08:00 | -2034.29 | 6.108 | 52.7521 | 59.8258 | -596.1915 |  | 1496 | 5385600 | 36921600 | 68457600 | 99993600
2024-04-08 09:00 | -1691.23 | 5.2807 | 53.0411 | 59.8258 | -495.6506 |  | 1497 | 5389200 | 36925200 | 68461200 | 99997200
2024-04-09 10:00 | -645.597 | 2.0816 | 53.2415 | 59.8258 | -189.2058 |  | 1498 | 5392800 | 36928800 | 68464800 | 100000800
2024-04-10 11:00 | 2658.64 | 1 | 54.6659 | 59.8258 | 779.1705 |  | 1499 | 5396400 | 36932400 | 68468400 | 100004400
2024-04-11 12:00 | 3204.29 | 1 | 79.817 | 59.8258 | 939.0847 |  | 1500 | 5400000 | 36936000 | 68472000 | 100008000
2024-04-12 13:00 | 3238.47 | 1 | 73.4962 | 59.8258 | 949.1019 |  | 1501 | 5403600 | 36939600 | 68475600 | 100011600
2024-04-13 14:00 | 3204.21 | 1.0269 | 70.4641 | 59.8258 | 939.0613 |  | 1502 | 5407200 | 36943200 | 68479200 | 100015200
2024-04-14 15:00 | 3165.14 | 1.0377 | 70.3606 | 59.8258 | 927.611 |  | 1503 | 5410800 | 36946800 | 68482800 | 100018800
2024-04-15 16:00 | 3182.21 | 1 | 76.2459 | 59.8258 | 932.6137 |  | 1504 | 5414400 | 36950400 | 68486400 | 100022400
2024-04-16 17:00 | 4241.03 | 1.2958 | 71.635 | 59.8258 | 1242.9232 |  | 1505 | 5418000 | 36954000 | 68490000 | 100026000
2024-04-17 18:00 | 3076.97 | 1 | 81.1532 | 59.8258 | 901.7709 |  | 1506 | 5421600 | 36957600 | 68493600 | 100029600
2024-04-18 19:00 | 3140.6 | 1 | 56.6858 | 59.8258 | 920.419 |  | 1507 | 5425200 | 36961200 | 68497200 | 100033200
2024-04-19 20:00 | 3109.13 | 1 | 56.7789 | 59.8258 | 911.1961 |  | 1508 | 5428800 | 36964800 | 68500800 | 100036800
2024-04-20 21:00 | -537.787 | 2.1806 | 56.037 | 59.8258 | -157.6098 |  | 1509 | 5432400 | 36968400 | 68504400 | 100040400
2024-04-21 22:00 | -1257.96 | 4.187 | 55.4061 | 59.8258 | -368.6717 |  | 1510 | 5436000 | 36972000 | 68508000 | 100044000
2024-04-22 23:00 | -1596.06 | 5.0422 | 55.0054 | 59.8258 | -467.759 |  | 1511 | 5439600 | 36975600 | 68511600 | 100047600
2024-04-24 | -3368.24 | 6.108 | 53.7571 | 59.8258 | -987.1337 |  | 1512 | 5443200 | 36979200 | 68515200 | 100051200
2024-04-25 01:00 | -3887.61 | 6.108 | 52.9982 | 59.8258 | -1139.346 |  | 1513 | 5446800 | 36982800 | 68518800 | 100054800
2024-04-26 02:00 | -4179.65 | 6.108 | 52.4543 | 59.8258 | -1224.9345 |  | 1514 | 5450400 | 36986400 | 68522400 | 100058400
2024-04-27 03:00 | -4595.12 | 6.108 | 51.9491 | 59.8258 | -1346.6967 |  | 1515 | 5454000 | 36990000 | 68526000 | 100062000
2024-04-28 04:00 | -4654.83 | 6.108 | 51.7038 | 59.8258 | -1364.196 |  | 1516 | 5457600 | 36993600 | 68529600 | 100065600
2024-04-29 05:00 | -4859.32 | 6.108 | 51.37 | 59.8258 | -1424.1261 |  | 1517 | 5461200 | 36997200 | 68533200 | 100069200
2024-04-30 06:00 | -4631.2 | 6.108 | 51.4053 | 59.8258 | -1357.2707 |  | 1518 | 5464800 | 37000800 | 68536800 | 100072800
2024-05-01 07:00 | -4497.07 | 6.108 | 51.4157 | 59.8258 | -1317.9611 |  | 1519 | 5468400 | 37004400 | 68540400 | 100076400
2024-05-02 08:00 | -3364.69 | 6.108 | 52.1806 | 59.8258 | -986.0933 |  | 1520 | 5472000 | 37008000 | 68544000 | 100080000
2024-05-03 09:00 | -2715.21 | 6.108 | 52.7711 | 59.8258 | -795.7495 |  | 1521 | 5475600 | 37011600 | 68547600 | 100083600
2024-05-04 10:00 | -1227.95 | 3.8254 | 53.4536 | 59.8258 | -359.8766 |  | 1522 | 5479200 | 37015200 | 68551200 | 100087200
2024-05-05 11:00 | -271.315 | 1.0679 | 53.9892 | 59.8258 | -79.5146 |  | 1523 | 5482800 | 37018800 | 68554800 | 100090800
2024-05-06 12:00 | 2815.67 | 1 | 55.1712 | 59.8258 | 825.1914 |  | 1524 | 5486400 | 37022400 | 68558400 | 100094400
2024-05-07 13:00 | 2939.06 | 1 | 76.6545 | 59.8258 | 861.3535 |  | 1525 | 5490000 | 37026000 | 68562000 | 100098000
2024-05-08 14:00 | 2946.56 | 1 | 71.2039 | 59.8258 | 863.5515 |  | 1526 | 5493600 | 37029600 | 68565600 | 100101600
2024-05-09 15:00 | 2956.12 | 1 | 72.2498 | 59.8258 | 866.3533 |  | 1527 | 5497200 | 37033200 | 68569200 | 100105200
2024-05-10 16:00 | 3055.6 | 1.0447 | 70.1488 | 59.8258 | 895.508 |  | 1528 | 5500800 | 37036800 | 68572800 | 100108800
2024-05-11 17:00 | 2870.68 | 1 | 56.6919 | 59.8258 | 841.3133 |  | 1529 | 5504400 | 37040400 | 68576400 | 100112400
2024-05-12 18:00 | 0 | 0 | 57.0368 | 59.8258 | 0 |  | 1530 | 5508000 | 37044000 | 68580000 | 100116000
2024-05-13 19:00 | -1226.13 | 3.9994 | 55.3364 | 59.8258 | -359.3432 |  | 1531 | 5511600 | 37047600 | 68583600 | 100119600
2024-05-14 20:00 | -2151.28 | 6.108 | 54.8284 | 59.8258 | -630.4779 |  | 1532 | 5515200 | 37051200 | 68587200 | 100123200
2024-05-15 21:00 | -3435.16 | 6.108 | 53.6225 | 59.8258 | -1006.746 |  | 1533 | 5518800 | 37054800 | 68590800 | 100126800
2024-05-16 22:00 | -4375.71 | 6.108 | 52.5795 | 59.8258 | -1282.394 |  | 1534 | 5522400 | 37058400 | 68594400 | 100130400
2024-05-17 23:00 | -5618.27 | 6.108 | 51.2844 | 59.8258 | -1646.5524 |  | 1535 | 5526000 | 37062000 | 68598000 | 100134000
2024-05-19 | -6172.87 | 6.108 | 50.4786 | 59.8258 | -1809.0896 |  | 1536 | 5529600 | 37065600 | 68601600 | 100137600
2024-05-20 01:00 | -6894.34 | 6.108 | 49.608 | 59.8258 | -2020.5316 |  | 1537 | 5533200 | 37069200 | 68605200 | 100141200
2024-05-21 02:00 | -7222.17 | 6.108 | 49.031 | 59.8258 | -2116.6091 |  | 1538 | 5536800 | 37072800 | 68608800 | 100144800
2024-05-22 03:00 | -7594.52 | 6.108 | 48.4655 | 59.8258 | -2225.7341 |  | 1539 | 5540400 | 37076400 | 68612400 | 100148400
2024-05-23 04:00 | -7542.16 | 6.108 | 48.2316 | 59.8258 | -2210.3889 |  | 1540 | 5544000 | 37080000 | 68616000 | 100152000
2024-05-24 05:00 | -7673.39 | 6.108 | 47.9305 | 59.8258 | -2248.8486 |  | 1541 | 5547600 | 37083600 | 68619600 | 100155600
2024-05-25 06:00 | -7533.59 | 6.108 | 47.8681 | 59.8258 | -2207.8773 |  | 1542 | 5551200 | 37087200 | 68623200 | 100159200
2024-05-26 07:00 | -7191.97 | 6.108 | 48.0085 | 59.8258 | -2107.7583 |  | 1543 | 5554800 | 37090800 | 68626800 | 100162800
2024-05-27 08:00 | -6176.48 | 6.108 | 48.706 | 59.8258 | -1810.1476 |  | 1544 | 5558400 | 37094400 | 68630400 | 100166400
2024-05-28 09:00 | -5511.03 | 6.108 | 49.2747 | 59.8258 | -1615.1235 |  | 1545 | 5562000 | 37098000 | 68634000 | 100170000
2024-05-29 10:00 | -3915.61 | 6.108 | 50.5586 | 59.8258 | -1147.552 |  | 1546 | 5565600 | 37101600 | 68637600 | 100173600
2024-05-30 11:00 | -2545.53 | 6.108 | 51.8188 | 59.8258 | -746.0212 |  | 1547 | 5569200 | 37105200 | 68641200 | 100177200
2024-05-31 12:00 | -1222.47 | 3.85 | 52.558 | 59.8258 | -358.2706 |  | 1548 | 5572800 | 37108800 | 68644800 | 100180800
2024-06-01 13:00 | -542.353 | 1.9171 | 53.0458 | 59.8258 | -158.948 |  | 1549 | 5576400 | 37112400 | 68648400 | 100184400
2024-06-02 14:00 | -238.412 | 1.1684 | 53.6887 | 59.8258 | -69.8717 |  | 1550 | 5580000 | 37116000 | 68652000 | 100188000
2024-06-03 15:00 | -165.766 | 1.0166 | 54.1007 | 59.8258 | -48.5812 |  | 1551 | 5583600 | 37119600 | 68655600 | 100191600
2024-06-04 16:00 | 2714.4 | 1 | 54.7684 | 59.8258 | 795.5121 |  | 1552 | 5587200 | 37123200 | 68659200 | 100195200
2024-06-05 17:00 | -58.5808 | 0.78388 | 55.1644 | 59.8258 | -17.1683 |  | 1553 | 5590800 | 37126800 | 68662800 | 100198800
2024-06-06 18:00 | -1102.9 | 3.8954 | 54.1593 | 59.8258 | -323.2281 |  | 1554 | 5594400 | 37130400 | 68666400 | 100202400
2024-06-07 19:00 | -2189.93 | 6.108 | 53.6736 | 59.8258 | -641.8051 |  | 1555 | 5598000 | 37134000 | 68670000 | 100206000
2024-06-08 20:00 | -2922.32 | 6.108 | 52.9764 | 59.8258 | -856.4474 |  | 1556 | 5601600 | 37137600 | 68673600 | 100209600
2024-06-09 21:00 | -4370.62 | 6.108 | 51.751 | 59.8258 | -1280.9023 |  | 1557 | 5605200 | 37141200 | 68677200 | 100213200
2024-06-10 22:00 | -5324.3 | 6.108 | 50.7012 | 59.8258 | -1560.3983 |  | 1558 | 5608800 | 37144800 | 68680800 | 100216800
2024-06-11 23:00 | -6643.27 | 6.108 | 49.4118 | 59.8258 | -1946.9502 |  | 1559 | 5612400 | 37148400 | 68684400 | 100220400
2024-06-13 | -6789.18 | 6.108 | 48.944 | 59.8258 | -1989.7122 |  | 1560 | 5616000 | 37152000 | 68688000 | 100224000
2024-06-14 01:00 | -7493.57 | 6.108 | 48.1703 | 59.8258 | -2196.1486 |  | 1561 | 5619600 | 37155600 | 68691600 | 100227600
2024-06-15 02:00 | -7607.06 | 6.108 | 47.8131 | 59.8258 | -2229.4092 |  | 1562 | 5623200 | 37159200 | 68695200 | 100231200
2024-06-16 03:00 | -8210.05 | 6.108 | 47.1545 | 59.8258 | -2406.1281 |  | 1563 | 5626800 | 37162800 | 68698800 | 100234800
2024-06-17 04:00 | -8260.21 | 6.108 | 46.8475 | 59.8258 | -2420.8286 |  | 1564 | 5630400 | 37166400 | 68702400 | 100238400
2024-06-18 05:00 | -8213.29 | 6.108 | 46.7096 | 59.8258 | -2407.0777 |  | 1565 | 5634000 | 37170000 | 68706000 | 100242000
2024-06-19 06:00 | -7635.5 | 6.108 | 47.0154 | 59.8258 | -2237.7442 |  | 1566 | 5637600 | 37173600 | 68709600 | 100245600
2024-06-20 07:00 | -7148.82 | 6.108 | 47.3564 | 59.8258 | -2095.1123 |  | 1567 | 5641200 | 37177200 | 68713200 | 100249200
2024-06-21 08:00 | -5201.43 | 6.108 | 48.8262 | 59.8258 | -1524.3887 |  | 1568 | 5644800 | 37180800 | 68716800 | 100252800
2024-06-22 09:00 | -3915.06 | 6.108 | 50.0428 | 59.8258 | -1147.3908 |  | 1569 | 5648400 | 37184400 | 68720400 | 100256400
2024-06-23 10:00 | -1915.77 | 6.108 | 51.8369 | 59.8258 | -561.4568 |  | 1570 | 5652000 | 37188000 | 68724000 | 100260000
2024-06-24 11:00 | -637.535 | 1.9942 | 52.2299 | 59.8258 | -186.8431 |  | 1571 | 5655600 | 37191600 | 68727600 | 100263600
2024-06-25 12:00 | 2772.92 | 1 | 53.87 | 59.8258 | 812.6626 |  | 1572 | 5659200 | 37195200 | 68731200 | 100267200
2024-06-26 13:00 | 3026.79 | 1 | 69.6747 | 59.8258 | 887.0646 |  | 1573 | 5662800 | 37198800 | 68734800 | 100270800
2024-06-27 14:00 | 2983.21 | 1 | 69.302 | 59.8258 | 874.2925 |  | 1574 | 5666400 | 37202400 | 68738400 | 100274400
2024-06-28 15:00 | 3159.56 | 1.0399 | 69.5286 | 59.8258 | 925.9756 |  | 1575 | 5670000 | 37206000 | 68742000 | 100278000
2024-06-29 16:00 | 3336.97 | 1.1212 | 69.5126 | 59.8258 | 977.9694 |  | 1576 | 5673600 | 37209600 | 68745600 | 100281600
2024-06-30 17:00 | 2985.55 | 1 | 79.4345 | 59.8258 | 874.9783 |  | 1577 | 5677200 | 37213200 | 68749200 | 100285200
2024-07-01 18:00 | 1574.95 | 1 | 56.1624 | 59.8258 | 461.5723 |  | 1578 | 5680800 | 37216800 | 68752800 | 100288800
2024-07-02 19:00 | -648.096 | 2.5413 | 55.1004 | 59.8258 | -189.9382 |  | 1579 | 5684400 | 37220400 | 68756400 | 100292400
2024-07-03 20:00 | -1442.65 | 4.7634 | 54.6234 | 59.8258 | -422.799 |  | 1580 | 5688000 | 37224000 | 68760000 | 100296000
2024-07-04 21:00 | -2559.07 | 6.108 | 53.895 | 59.8258 | -749.9894 |  | 1581 | 5691600 | 37227600 | 68763600 | 100299600
2024-07-05 22:00 | -3255.77 | 6.108 | 53.1256 | 59.8258 | -954.172 |  | 1582 | 5695200 | 37231200 | 68767200 | 100303200
2024-07-06 23:00 | -4192.65 | 6.108 | 52.1779 | 59.8258 | -1228.7444 |  | 1583 | 5698800 | 37234800 | 68770800 | 100306800
2024-07-08 | -4672.15 | 6.108 | 51.5213 | 59.8258 | -1369.272 |  | 1584 | 5702400 | 37238400 | 68774400 | 100310400
2024-07-09 01:00 | -5008.87 | 6.108 | 51.0391 | 59.8258 | -1467.9549 |  | 1585 | 5706000 | 37242000 | 68778000 | 100314000
2024-07-10 02:00 | -5385.8 | 6.108 | 50.5608 | 59.8258 | -1578.4222 |  | 1586 | 5709600 | 37245600 | 68781600 | 100317600
2024-07-11 03:00 | -5326.67 | 6.108 | 50.4212 | 59.8258 | -1561.0929 |  | 1587 | 5713200 | 37249200 | 68785200 | 100321200
2024-07-12 04:00 | -5142.2 | 6.108 | 50.431 | 59.8258 | -1507.0301 |  | 1588 | 5716800 | 37252800 | 68788800 | 100324800
2024-07-13 05:00 | -5078.14 | 6.108 | 50.4105 | 59.8258 | -1488.2559 |  | 1589 | 5720400 | 37256400 | 68792400 | 100328400
2024-07-14 06:00 | -4725.79 | 6.108 | 50.6258 | 59.8258 | -1384.9923 |  | 1590 | 5724000 | 37260000 | 68796000 | 100332000
2024-07-15 07:00 | -4455.08 | 6.108 | 50.8455 | 59.8258 | -1305.6551 |  | 1591 | 5727600 | 37263600 | 68799600 | 100335600
2024-07-16 08:00 | -3958.93 | 6.108 | 51.2498 | 59.8258 | -1160.2479 |  | 1592 | 5731200 | 37267200 | 68803200 | 100339200
2024-07-17 09:00 | -3232.79 | 6.108 | 51.8681 | 59.8258 | -947.4372 |  | 1593 | 5734800 | 37270800 | 68806800 | 100342800
2024-07-18 10:00 | -2600.43 | 6.108 | 52.4624 | 59.8258 | -762.1108 |  | 1594 | 5738400 | 37274400 | 68810400 | 100346400
2024-07-19 11:00 | -1448.46 | 4.5381 | 53.0875 | 59.8258 | -424.5017 |  | 1595 | 5742000 | 37278000 | 68814000 | 100350000
2024-07-20 12:00 | -1472.51 | 4.7343 | 53.3319 | 59.8258 | -431.5501 |  | 1596 | 5745600 | 37281600 | 68817600 | 100353600
2024-07-21 13:00 | -1127.93 | 3.6312 | 53.4415 | 59.8258 | -330.5637 |  | 1597 | 5749200 | 37285200 | 68821200 | 100357200
2024-07-22 14:00 | -973.241 | 3.2586 | 53.6054 | 59.8258 | -285.2288 |  | 1598 | 5752800 | 37288800 | 68824800 | 100360800
2024-07-23 15:00 | -789.549 | 2.7238 | 53.7384 | 59.8258 | -231.394 |  | 1599 | 5756400 | 37292400 | 68828400 | 100364400
2024-07-24 16:00 | 0 | 1 | 55.1411 | 59.8258 | 0 |  | 1600 | 5760000 | 37296000 | 68832000 | 100368000
2024-07-25 17:00 | 3101.1 | 1 | 55.0149 | 59.8258 | 908.8427 |  | 1601 | 5763600 | 37299600 | 68835600 | 100371600
2024-07-26 18:00 | 3138.25 | 1 | 55.5422 | 59.8258 | 919.7303 |  | 1602 | 5767200 | 37303200 | 68839200 | 100375200
2024-07-27 19:00 | -164.818 | 1.092 | 55.4627 | 59.8258 | -48.3034 |  | 1603 | 5770800 | 37306800 | 68842800 | 100378800
2024-07-28 20:00 | -553.734 | 2.1825 | 54.768 | 59.8258 | -162.2834 |  | 1604 | 5774400 | 37310400 | 68846400 | 100382400
2024-07-29 21:00 | -1415.55 | 4.7229 | 54.4749 | 59.8258 | -414.8568 |  | 1605 | 5778000 | 37314000 | 68850000 | 100386000
2024-07-30 22:00 | -1778.74 | 5.6009 | 54.3103 | 59.8258 | -521.2972 |  | 1606 | 5781600 | 37317600 | 68853600 | 100389600
2024-07-31 23:00 | -2737.05 | 6.108 | 53.5695 | 59.8258 | -802.1502 |  | 1607 | 5785200 | 37321200 | 68857200 | 100393200
2024-08-02 | -3137.94 | 6.108 | 53.049 | 59.8258 | -919.6394 |  | 1608 | 5788800 | 37324800 | 68860800 | 100396800
2024-08-03 01:00 | -3125.84 | 6.108 | 52.927 | 59.8258 | -916.0933 |  | 1609 | 5792400 | 37328400 | 68864400 | 100400400
2024-08-04 02:00 | -3405.59 | 6.108 | 52.6543 | 59.8258 | -998.0799 |  | 1610 | 5796000 | 37332000 | 68868000 | 100404000
2024-08-05 03:00 | -3442.5 | 6.108 | 52.558 | 59.8258 | -1008.8972 |  | 1611 | 5799600 | 37335600 | 68871600 | 100407600
2024-08-06 04:00 | -3578.33 | 6.108 | 52.3964 | 59.8258 | -1048.705 |  | 1612 | 5803200 | 37339200 | 68875200 | 100411200
2024-08-07 05:00 | -3527.19 | 6.108 | 52.3541 | 59.8258 | -1033.7173 |  | 1613 | 5806800 | 37342800 | 68878800 | 100414800
2024-08-08 06:00 | -3126.71 | 6.108 | 52.5942 | 59.8258 | -916.3482 |  | 1614 | 5810400 | 37346400 | 68882400 | 100418400
2024-08-09 07:00 | -3088.64 | 6.108 | 52.6534 | 59.8258 | -905.191 |  | 1615 | 5814000 | 37350000 | 68886000 | 100422000
2024-08-10 08:00 | -2889.03 | 6.108 | 52.8139 | 59.8258 | -846.6911 |  | 1616 | 5817600 | 37353600 | 68889600 | 100425600
2024-08-11 09:00 | -3082.21 | 6.108 | 52.693 | 59.8258 | -903.3066 |  | 1617 | 5821200 | 37357200 | 68893200 | 100429200
2024-08-12 10:00 | -2403.81 | 6.108 | 53.1806 | 59.8258 | -704.4872 |  | 1618 | 5824800 | 37360800 | 68896800 | 100432800
2024-08-13 11:00 | 0 | 0 | 55.0552 | 59.8258 | 0 |  | 1619 | 5828400 | 37364400 | 68900400 | 100436400
2024-08-14 12:00 | 2540.96 | 1 | 73.4378 | 59.8258 | 744.6819 |  | 1620 | 5832000 | 37368000 | 68904000 | 100440000
2024-08-15 13:00 | 2699.51 | 1 | 69.6041 | 59.8258 | 791.1483 |  | 1621 | 5835600 | 37371600 | 68907600 | 100443600
2024-08-16 14:00 | 3180.53 | 1 | 73.3111 | 59.8258 | 932.1213 |  | 1622 | 5839200 | 37375200 | 68911200 | 100447200
2024-08-17 15:00 | 3195.25 | 1.0267 | 70.7905 | 59.8258 | 936.4353 |  | 1623 | 5842800 | 37378800 | 68914800 | 100450800
2024-08-18 16:00 | 3024.25 | 1.0347 | 70.1779 | 59.8258 | 886.3202 |  | 1624 | 5846400 | 37382400 | 68918400 | 100454400
2024-08-19 17:00 | 2947.55 | 1 | 74.9875 | 59.8258 | 863.8416 |  | 1625 | 5850000 | 37386000 | 68922000 | 100458000
2024-08-20 18:00 | 2847.25 | 1 | 56.7603 | 59.8258 | 834.4466 |  | 1626 | 5853600 | 37389600 | 68925600 | 100461600
2024-08-21 19:00 | -662.88 | 2.5399 | 55.922 | 59.8258 | -194.271 |  | 1627 | 5857200 | 37393200 | 68929200 | 100465200
2024-08-22 20:00 | -1574.54 | 5.1192 | 55.3321 | 59.8258 | -461.4521 |  | 1628 | 5860800 | 37396800 | 68932800 | 100468800
2024-08-23 21:00 | -3163.19 | 6.108 | 54.0834 | 59.8258 | -927.0395 |  | 1629 | 5864400 | 37400400 | 68936400 | 100472400
2024-08-24 22:00 | -3828.84 | 6.108 | 53.2531 | 59.8258 | -1122.1222 |  | 1630 | 5868000 | 37404000 | 68940000 | 100476000
2024-08-25 23:00 | -5262.27 | 6.108 | 51.8629 | 59.8258 | -1542.2191 |  | 1631 | 5871600 | 37407600 | 68943600 | 100479600
2024-08-27 | -5982.21 | 6.108 | 50.8802 | 59.8258 | -1753.2127 |  | 1632 | 5875200 | 37411200 | 68947200 | 100483200
2024-08-28 01:00 | -6941.2 | 6.108 | 49.8048 | 59.8258 | -2034.2649 |  | 1633 | 5878800 | 37414800 | 68950800 | 100486800
2024-08-29 02:00 | -7122.67 | 6.108 | 49.2898 | 59.8258 | -2087.4485 |  | 1634 | 5882400 | 37418400 | 68954400 | 100490400
2024-08-30 03:00 | -7444.08 | 6.108 | 48.7619 | 59.8258 | -2181.6445 |  | 1635 | 5886000 | 37422000 | 68958000 | 100494000
2024-08-31 04:00 | -7415.32 | 6.108 | 48.5134 | 59.8258 | -2173.2158 |  | 1636 | 5889600 | 37425600 | 68961600 | 100497600
2024-09-01 05:00 | -7630.07 | 6.108 | 48.1443 | 59.8258 | -2236.1528 |  | 1637 | 5893200 | 37429200 | 68965200 | 100501200
2024-09-02 06:00 | -7979.15 | 6.108 | 47.6672 | 59.8258 | -2338.458 |  | 1638 | 5896800 | 37432800 | 68968800 | 100504800
2024-09-03 07:00 | -6993.77 | 6.108 | 48.2168 | 59.8258 | -2049.6717 |  | 1639 | 5900400 | 37436400 | 68972400 | 100508400
2024-09-04 08:00 | -4870.1 | 6.108 | 49.796 | 59.8258 | -1427.2854 |  | 1640 | 5904000 | 37440000 | 68976000 | 100512000
2024-09-05 09:00 | -4046.87 | 6.108 | 50.6687 | 59.8258 | -1186.0205 |  | 1641 | 5907600 | 37443600 | 68979600 | 100515600
2024-09-06 10:00 | -2163.83 | 6.108 | 52.2906 | 59.8258 | -634.156 |  | 1642 | 5911200 | 37447200 | 68983200 | 100519200
2024-09-07 11:00 | -1304.25 | 4.0805 | 52.7946 | 59.8258 | -382.2379 |  | 1643 | 5914800 | 37450800 | 68986800 | 100522800
2024-09-08 12:00 | -1403.1 | 4.5746 | 53.1837 | 59.8258 | -411.208 |  | 1644 | 5918400 | 37454400 | 68990400 | 100526400
2024-09-09 13:00 | -1564.4 | 5.0182 | 53.3476 | 59.8258 | -458.4804 |  | 1645 | 5922000 | 37458000 | 68994000 | 100530000
2024-09-10 14:00 | -1542.96 | 4.899 | 53.4219 | 59.8258 | -452.1969 |  | 1646 | 5925600 | 37461600 | 68997600 | 100533600
2024-09-11 15:00 | -1371.93 | 4.3708 | 53.5128 | 59.8258 | -402.073 |  | 1647 | 5929200 | 37465200 | 69001200 | 100537200
2024-09-12 16:00 | -545.058 | 1.8563 | 53.667 | 59.8258 | -159.7407 |  | 1648 | 5932800 | 37468800 | 69004800 | 100540800
2024-09-13 17:00 | 2685.23 | 1 | 54.928 | 59.8258 | 786.9632 |  | 1649 | 5936400 | 37472400 | 69008400 | 100544400
2024-09-14 18:00 | -499.651 | 2.0959 | 54.6134 | 59.8258 | -146.4333 |  | 1650 | 5940000 | 37476000 | 69012000 | 100548000
2024-09-15 19:00 | -1564.71 | 5.2065 | 54.2552 | 59.8258 | -458.5712 |  | 1651 | 5943600 | 37479600 | 69015600 | 100551600
2024-09-16 20:00 | -2199.58 | 6.108 | 53.8144 | 59.8258 | -644.6333 |  | 1652 | 5947200 | 37483200 | 69019200 | 100555200
2024-09-17 21:00 | -2606.83 | 6.108 | 53.4251 | 59.8258 | -763.9865 |  | 1653 | 5950800 | 37486800 | 69022800 | 100558800
2024-09-18 22:00 | -2748.7 | 6.108 | 53.2186 | 59.8258 | -805.5645 |  | 1654 | 5954400 | 37490400 | 69026400 | 100562400
2024-09-19 23:00 | -2967.42 | 6.108 | 52.9108 | 59.8258 | -869.665 |  | 1655 | 5958000 | 37494000 | 69030000 | 100566000
2024-09-21 | -4637.98 | 6.108 | 51.5867 | 59.8258 | -1359.2578 |  | 1656 | 5961600 | 37497600 | 69033600 | 100569600
2024-09-22 01:00 | -4733.32 | 6.108 | 51.2633 | 59.8258 | -1387.1992 |  | 1657 | 5965200 | 37501200 | 69037200 | 100573200
2024-09-23 02:00 | -5104.64 | 6.108 | 50.8406 | 59.8258 | -1496.0223 |  | 1658 | 5968800 | 37504800 | 69040800 | 100576800
2024-09-24 03:00 | -5030.2 | 6.108 | 50.7742 | 59.8258 | -1474.2061 |  | 1659 | 5972400 | 37508400 | 69044400 | 100580400
2024-09-25 04:00 | -5233.05 | 6.108 | 50.5294 | 59.8258 | -1533.6556 |  | 1660 | 5976000 | 37512000 | 69048000 | 100584000
2024-09-26 05:00 | -5388.69 | 6.108 | 50.2697 | 59.8258 | -1579.2691 |  | 1661 | 5979600 | 37515600 | 69051600 | 100587600
2024-09-27 06:00 | -5255.64 | 6.108 | 50.2887 | 59.8258 | -1540.276 |  | 1662 | 5983200 | 37519200 | 69055200 | 100591200
2024-09-28 07:00 | -4533.52 | 6.108 | 50.7916 | 59.8258 | -1328.6436 |  | 1663 | 5986800 | 37522800 | 69058800 | 100594800
2024-09-29 08:00 | -3803.95 | 6.108 | 51.3955 | 59.8258 | -1114.8277 |  | 1664 | 5990400 | 37526400 | 69062400 | 100598400
2024-09-30 09:00 | -3891.43 | 6.108 | 51.4365 | 59.8258 | -1140.4656 |  | 1665 | 5994000 | 37530000 | 69066000 | 100602000
2024-10-01 10:00 | -3264.08 | 6.108 | 51.9238 | 59.8258 | -956.6074 |  | 1666 | 5997600 | 37533600 | 69069600 | 100605600
2024-10-02 11:00 | -2043.93 | 6.108 | 52.9124 | 59.8258 | -599.0168 |  | 1667 | 6001200 | 37537200 | 69073200 | 100609200
2024-10-03 12:00 | -461.639 | 1.4265 | 53.166 | 59.8258 | -135.293 |  | 1668 | 6004800 | 37540800 | 69076800 | 100612800
2024-10-04 13:00 | -625.333 | 2.3994 | 53.7751 | 59.8258 | -183.267 |  | 1669 | 6008400 | 37544400 | 69080400 | 100616400
2024-10-05 14:00 | -477.899 | 1.8485 | 53.9331 | 59.8258 | -140.0584 |  | 1670 | 6012000 | 37548000 | 69084000 | 100620000
2024-10-06 15:00 | -373.359 | 1.5799 | 54.1589 | 59.8258 | -109.4207 |  | 1671 | 6015600 | 37551600 | 69087600 | 100623600
2024-10-07 16:00 | 2238.63 | 1 | 55.1689 | 59.8258 | 656.0777 |  | 1672 | 6019200 | 37555200 | 69091200 | 100627200
2024-10-08 17:00 | 2945.31 | 1 | 72.6896 | 59.8258 | 863.1852 |  | 1673 | 6022800 | 37558800 | 69094800 | 100630800
2024-10-09 18:00 | 2891.99 | 1 | 55.8734 | 59.8258 | 847.5586 |  | 1674 | 6026400 | 37562400 | 69098400 | 100634400
2024-10-10 19:00 | 3014.96 | 1 | 56.102 | 59.8258 | 883.5976 |  | 1675 | 6030000 | 37566000 | 69102000 | 100638000
2024-10-11 20:00 | 3061.81 | 1 | 56.3207 | 59.8258 | 897.3279 |  | 1676 | 6033600 | 37569600 | 69105600 | 100641600
2024-10-12 21:00 | 3140.32 | 1 | 56.5459 | 59.8258 | 920.3369 |  | 1677 | 6037200 | 37573200 | 69109200 | 100645200
2024-10-13 22:00 | 50.399 | 1 | 56.9915 | 59.8258 | 14.7705 |  | 1678 | 6040800 | 37576800 | 69112800 | 100648800
2024-10-14 23:00 | 538.481 | 1 | 56.6715 | 59.8258 | 157.8132 |  | 1679 | 6044400 | 37580400 | 69116400 | 100652400
2024-10-16 | -878.094 | 3.1893 | 55.4152 | 59.8258 | -257.3439 |  | 1680 | 6048000 | 37584000 | 69120000 | 100656000
2024-10-17 01:00 | -1297.75 | 4.2262 | 55.1177 | 59.8258 | -380.333 |  | 1681 | 6051600 | 37587600 | 69123600 | 100659600
2024-10-18 02:00 | -1757.26 | 5.5384 | 54.9268 | 59.8258 | -515.0021 |  | 1682 | 6055200 | 37591200 | 69127200 | 100663200
2024-10-19 03:00 | -2066.9 | 6.108 | 54.6918 | 59.8258 | -605.7486 |  | 1683 | 6058800 | 37594800 | 69130800 | 100666800
2024-10-20 04:00 | -2296.33 | 6.108 | 54.4202 | 59.8258 | -672.9879 |  | 1684 | 6062400 | 37598400 | 69134400 | 100670400
2024-10-21 05:00 | -2474.7 | 6.108 | 54.1708 | 59.8258 | -725.263 |  | 1685 | 6066000 | 37602000 | 69138000 | 100674000
2024-10-22 06:00 | -2580.87 | 6.108 | 54.0075 | 59.8258 | -756.3783 |  | 1686 | 6069600 | 37605600 | 69141600 | 100677600
2024-10-23 07:00 | -3268.68 | 6.108 | 53.4115 | 59.8258 | -957.9555 |  | 1687 | 6073200 | 37609200 | 69145200 | 100681200
2024-10-24 08:00 | -2902.29 | 6.108 | 53.5207 | 59.8258 | -850.5772 |  | 1688 | 6076800 | 37612800 | 69148800 | 100684800
2024-10-25 09:00 | -3171.84 | 6.108 | 53.25 | 59.8258 | -929.5745 |  | 1689 | 6080400 | 37616400 | 69152400 | 100688400
2024-10-26 10:00 | -1545.39 | 4.8053 | 54.0794 | 59.8258 | -452.9091 |  | 1690 | 6084000 | 37620000 | 69156000 | 100692000
2024-10-27 11:00 | -294.931 | 1.0334 | 54.3775 | 59.8258 | -86.4357 |  | 1691 | 6087600 | 37623600 | 69159600 | 100695600
2024-10-28 12:00 | 2842.96 | 1 | 55.6748 | 59.8258 | 833.1893 |  | 1692 | 6091200 | 37627200 | 69163200 | 100699200
2024-10-29 13:00 | 2909.47 | 1 | 56.2255 | 59.8258 | 852.6815 |  | 1693 | 6094800 | 37630800 | 69166800 | 100702800
2024-10-30 14:00 | 2922.95 | 1 | 56.5647 | 59.8258 | 856.6321 |  | 1694 | 6098400 | 37634400 | 69170400 | 100706400
2024-10-31 15:00 | 2875.47 | 1 | 56.8076 | 59.8258 | 842.7171 |  | 1695 | 6102000 | 37638000 | 69174000 | 100710000
2024-11-01 16:00 | 2912.16 | 1 | 56.9805 | 59.8258 | 853.4698 |  | 1696 | 6105600 | 37641600 | 69177600 | 100713600
2024-11-02 17:00 | 2868.86 | 1 | 57.1221 | 59.8258 | 840.7799 |  | 1697 | 6109200 | 37645200 | 69181200 | 100717200
2024-11-03 18:00 | -177.217 | 1.1123 | 56.7139 | 59.8258 | -51.9372 |  | 1698 | 6112800 | 37648800 | 69184800 | 100720800
2024-11-04 19:00 | -1288.42 | 4.3453 | 55.7579 | 59.8258 | -377.5986 |  | 1699 | 6116400 | 37652400 | 69188400 | 100724400
2024-11-05 20:00 | -2057.76 | 6.108 | 55.2659 | 59.8258 | -603.0699 |  | 1700 | 6120000 | 37656000 | 69192000 | 100728000
2024-11-06 21:00 | -3447.05 | 6.108 | 53.9874 | 59.8258 | -1010.2306 |  | 1701 | 6123600 | 37659600 | 69195600 | 100731600
2024-11-07 22:00 | -4402.18 | 6.108 | 52.9244 | 59.8258 | -1290.1516 |  | 1702 | 6127200 | 37663200 | 69199200 | 100735200
2024-11-08 23:00 | -5390.71 | 6.108 | 51.7969 | 59.8258 | -1579.8611 |  | 1703 | 6130800 | 37666800 | 69202800 | 100738800
2024-11-10 | -6202.22 | 6.108 | 50.8174 | 59.8258 | -1817.6913 |  | 1704 | 6134400 | 37670400 | 69206400 | 100742400
2024-11-11 01:00 | -6329.05 | 6.108 | 50.3572 | 59.8258 | -1854.8615 |  | 1705 | 6138000 | 37674000 | 69210000 | 100746000
2024-11-12 02:00 | -6646.22 | 6.108 | 49.8399 | 59.8258 | -1947.8148 |  | 1706 | 6141600 | 37677600 | 69213600 | 100749600
2024-11-13 03:00 | -7053.57 | 6.108 | 49.2804 | 59.8258 | -2067.1973 |  | 1707 | 6145200 | 37681200 | 69217200 | 100753200
2024-11-14 04:00 | -6833.65 | 6.108 | 49.182 | 59.8258 | -2002.7451 |  | 1708 | 6148800 | 37684800 | 69220800 | 100756800
2024-11-15 05:00 | -6875.7 | 6.108 | 48.9769 | 59.8258 | -2015.0688 |  | 1709 | 6152400 | 37688400 | 69224400 | 100760400
2024-11-16 06:00 | -6875.08 | 6.108 | 48.852 | 59.8258 | -2014.8871 |  | 1710 | 6156000 | 37692000 | 69228000 | 100764000
2024-11-17 07:00 | -6069.48 | 6.108 | 49.344 | 59.8258 | -1778.789 |  | 1711 | 6159600 | 37695600 | 69231600 | 100767600
2024-11-18 08:00 | -4447.54 | 6.108 | 50.5721 | 59.8258 | -1303.4453 |  | 1712 | 6163200 | 37699200 | 69235200 | 100771200
2024-11-19 09:00 | -3280.56 | 6.108 | 51.6618 | 59.8258 | -961.4372 |  | 1713 | 6166800 | 37702800 | 69238800 | 100774800
2024-11-20 10:00 | -1444.53 | 4.569 | 52.9167 | 59.8258 | -423.35 |  | 1714 | 6170400 | 37706400 | 69242400 | 100778400
2024-11-21 11:00 | 0 | 1 | 54.7372 | 59.8258 | 0 |  | 1715 | 6174000 | 37710000 | 69246000 | 100782000
2024-11-22 12:00 | -60.3983 | 0.76673 | 54.7792 | 59.8258 | -17.701 |  | 1716 | 6177600 | 37713600 | 69249600 | 100785600
2024-11-23 13:00 | -405.559 | 1.7755 | 54.3253 | 59.8258 | -118.8576 |  | 1717 | 6181200 | 37717200 | 69253200 | 100789200
2024-11-24 14:00 | -413.323 | 1.7047 | 54.3658 | 59.8258 | -121.133 |  | 1718 | 6184800 | 37720800 | 69256800 | 100792800
2024-11-25 15:00 | 2497.63 | 1 | 55.3657 | 59.8258 | 731.9831 |  | 1719 | 6188400 | 37724400 | 69260400 | 100796400
2024-11-26 16:00 | 3094.24 | 1 | 71.0047 | 59.8258 | 906.8322 |  | 1720 | 6192000 | 37728000 | 69264000 | 100800000
2024-11-27 17:00 | 3062.39 | 1 | 56.1145 | 59.8258 | 897.4979 |  | 1721 | 6195600 | 37731600 | 69267600 | 100803600
2024-11-28 18:00 | 3144.18 | 1 | 56.3434 | 59.8258 | 921.4682 |  | 1722 | 6199200 | 37735200 | 69271200 | 100807200
2024-11-29 19:00 | 0 | 0 | 56.851 | 59.8258 | 0 |  | 1723 | 6202800 | 37738800 | 69274800 | 100810800
2024-11-30 20:00 | -618.332 | 2.08 | 55.2712 | 59.8258 | -181.2152 |  | 1724 | 6206400 | 37742400 | 69278400 | 100814400
2024-12-01 21:00 | -1494.87 | 4.9362 | 55.0579 | 59.8258 | -438.1032 |  | 1725 | 6210000 | 37746000 | 69282000 | 100818000
2024-12-02 22:00 | -2197.53 | 6.108 | 54.6119 | 59.8258 | -644.0325 |  | 1726 | 6213600 | 37749600 | 69285600 | 100821600
2024-12-03 23:00 | -3389.72 | 6.108 | 53.4982 | 59.8258 | -993.4289 |  | 1727 | 6217200 | 37753200 | 69289200 | 100825200
2024-12-05 | -4035.11 | 6.108 | 52.7095 | 59.8258 | -1182.574 |  | 1728 | 6220800 | 37756800 | 69292800 | 100828800
2024-12-06 01:00 | -4093.54 | 6.108 | 52.4441 | 59.8258 | -1199.6981 |  | 1729 | 6224400 | 37760400 | 69296400 | 100832400
2024-12-07 02:00 | -4064.67 | 6.108 | 52.3326 | 59.8258 | -1191.2372 |  | 1730 | 6228000 | 37764000 | 69300000 | 100836000
2024-12-08 03:00 | -3913.22 | 6.108 | 52.3332 | 59.8258 | -1146.8516 |  | 1731 | 6231600 | 37767600 | 69303600 | 100839600
2024-12-09 04:00 | -3604.92 | 6.108 | 52.4812 | 59.8258 | -1056.4978 |  | 1732 | 6235200 | 37771200 | 69307200 | 100843200
2024-12-10 05:00 | -3306.46 | 6.108 | 52.6833 | 59.8258 | -969.0278 |  | 1733 | 6238800 | 37774800 | 69310800 | 100846800
2024-12-11 06:00 | -3164.13 | 6.108 | 52.8007 | 59.8258 | -927.315 |  | 1734 | 6242400 | 37778400 | 69314400 | 100850400
2024-12-12 07:00 | -3348.26 | 6.108 | 52.698 | 59.8258 | -981.2781 |  | 1735 | 6246000 | 37782000 | 69318000 | 100854000
2024-12-13 08:00 | -3530.8 | 6.108 | 52.5446 | 59.8258 | -1034.7753 |  | 1736 | 6249600 | 37785600 | 69321600 | 100857600
2024-12-14 09:00 | -4344.56 | 6.108 | 51.8971 | 59.8258 | -1273.2648 |  | 1737 | 6253200 | 37789200 | 69325200 | 100861200
2024-12-15 10:00 | -4109.29 | 6.108 | 51.9223 | 59.8258 | -1204.314 |  | 1738 | 6256800 | 37792800 | 69328800 | 100864800
2024-12-16 11:00 | -3727.15 | 6.108 | 52.1353 | 59.8258 | -1092.3198 |  | 1739 | 6260400 | 37796400 | 69332400 | 100868400
2024-12-17 12:00 | -3155.31 | 6.108 | 52.5517 | 59.8258 | -924.7301 |  | 1740 | 6264000 | 37800000 | 69336000 | 100872000
2024-12-18 13:00 | -2676.56 | 6.108 | 52.9518 | 59.8258 | -784.4223 |  | 1741 | 6267600 | 37803600 | 69339600 | 100875600
2024-12-19 14:00 | -2795.27 | 6.108 | 52.9273 | 59.8258 | -819.2128 |  | 1742 | 6271200 | 37807200 | 69343200 | 100879200
2024-12-20 15:00 | -2645.72 | 6.108 | 53.0403 | 59.8258 | -775.384 |  | 1743 | 6274800 | 37810800 | 69346800 | 100882800
2024-12-21 16:00 | -1992.56 | 6.108 | 53.5259 | 59.8258 | -583.9617 |  | 1744 | 6278400 | 37814400 | 69350400 | 100886400
2024-12-22 17:00 | -1940.8 | 6.0186 | 53.6099 | 59.8258 | -568.7923 |  | 1745 | 6282000 | 37818000 | 69354000 | 100890000
2024-12-23 18:00 | -2117.15 | 6.108 | 53.5301 | 59.8258 | -620.4754 |  | 1746 | 6285600 | 37821600 | 69357600 | 100893600
2024-12-24 19:00 | -2781.98 | 6.108 | 53.029 | 59.8258 | -815.3179 |  | 1747 | 6289200 | 37825200 | 69361200 | 100897200
2024-12-25 20:00 | -3517.34 | 6.108 | 52.4042 | 59.8258 | -1030.8306 |  | 1748 | 6292800 | 37828800 | 69364800 | 100900800
2024-12-26 21:00 | -4957.1 | 6.108 | 51.2109 | 59.8258 | -1452.7826 |  | 1749 | 6296400 | 37832400 | 69368400 | 100904400
2024-12-27 22:00 | -5997.23 | 6.108 | 50.1733 | 59.8258 | -1757.6146 |  | 1750 | 6300000 | 37836000 | 69372000 | 100908000
2024-12-28 23:00 | -7004.94 | 6.108 | 49.13 | 59.8258 | -2052.9453 |  | 1751 | 6303600 | 37839600 | 69375600 | 100911600
2024-12-30 | -7067.51 | 6.108 | 48.7732 | 59.8258 | -2071.2827 |  | 1752 | 6307200 | 37843200 | 69379200 | 100915200
2024-12-31 01:00 | -7368.88 | 6.108 | 48.3345 | 59.8258 | -2159.6055 |  | 1753 | 6310800 | 37846800 | 69382800 | 100918800
2025-01-01 02:00 | -7602.22 | 6.108 | 47.963 | 59.8258 | -2227.9907 |  | 1754 | 6314400 | 37850400 | 69386400 | 100922400
2025-01-02 03:00 | -7762.93 | 6.108 | 47.6654 | 59.8258 | -2275.0902 |  | 1755 | 6318000 | 37854000 | 69390000 | 100926000
2025-01-03 04:00 | -7914.15 | 6.108 | 47.3909 | 59.8258 | -2319.4084 |  | 1756 | 6321600 | 37857600 | 69393600 | 100929600
2025-01-04 05:00 | -8051.23 | 6.108 | 47.1446 | 59.8258 | -2359.5826 |  | 1757 | 6325200 | 37861200 | 69397200 | 100933200
2025-01-05 06:00 | -7849.66 | 6.108 | 47.1502 | 59.8258 | -2300.5083 |  | 1758 | 6328800 | 37864800 | 69400800 | 100936800
2025-01-06 07:00 | -7344.47 | 6.108 | 47.4371 | 59.8258 | -2152.4517 |  | 1759 | 6332400 | 37868400 | 69404400 | 100940400
2025-01-07 08:00 | -5671.73 | 6.108 | 48.6722 | 59.8258 | -1662.22 |  | 1760 | 6336000 | 37872000 | 69408000 | 100944000
2025-01-08 09:00 | -4660.96 | 6.108 | 49.6249 | 59.8258 | -1365.9925 |  | 1761 | 6339600 | 37875600 | 69411600 | 100947600
2025-01-09 10:00 | -2979.39 | 6.108 | 51.1115 | 59.8258 | -873.173 |  | 1762 | 6343200 | 37879200 | 69415200 | 100951200
2025-01-10 11:00 | -1348.88 | 4.2908 | 52.2477 | 59.8258 | -395.3177 |  | 1763 | 6346800 | 37882800 | 69418800 | 100954800
2025-01-11 12:00 | -341.407 | 1.2497 | 52.857 | 59.8258 | -100.0565 |  | 1764 | 6350400 | 37886400 | 69422400 | 100958400
2025-01-12 13:00 | 2523.87 | 1 | 54.2945 | 59.8258 | 739.6733 |  | 1765 | 6354000 | 37890000 | 69426000 | 100962000
2025-01-13 14:00 | 2929.02 | 1 | 54.9026 | 59.8258 | 858.411 |  | 1766 | 6357600 | 37893600 | 69429600 | 100965600
2025-01-14 15:00 | 2918.67 | 1 | 55.3738 | 59.8258 | 855.3777 |  | 1767 | 6361200 | 37897200 | 69433200 | 100969200
2025-01-15 16:00 | 2918.35 | 1 | 77.4364 | 59.8258 | 855.284 |  | 1768 | 6364800 | 37900800 | 69436800 | 100972800
2025-01-16 17:00 | 2819.85 | 1 | 55.9256 | 59.8258 | 826.4165 |  | 1769 | 6368400 | 37904400 | 69440400 | 100976400
2025-01-17 18:00 | -255.71 | 1.3348 | 55.5193 | 59.8258 | -74.9412 |  | 1770 | 6372000 | 37908000 | 69444000 | 100980000
2025-01-18 19:00 | -1387.8 | 4.6904 | 54.7885 | 59.8258 | -406.724 |  | 1771 | 6375600 | 37911600 | 69447600 | 100983600
2025-01-19 20:00 | -2251.77 | 6.108 | 54.2032 | 59.8258 | -659.9286 |  | 1772 | 6379200 | 37915200 | 69451200 | 100987200
2025-01-20 21:00 | -3700.22 | 6.108 | 52.9165 | 59.8258 | -1084.4274 |  | 1773 | 6382800 | 37918800 | 69454800 | 100990800
2025-01-21 22:00 | -4588.04 | 6.108 | 51.9322 | 59.8258 | -1344.6218 |  | 1774 | 6386400 | 37922400 | 69458400 | 100994400
2025-01-22 23:00 | -5915.01 | 6.108 | 50.6021 | 59.8258 | -1733.5183 |  | 1775 | 6390000 | 37926000 | 69462000 | 100998000
2025-01-24 | -6203.19 | 6.108 | 50.0325 | 59.8258 | -1817.9755 |  | 1776 | 6393600 | 37929600 | 69465600 | 101001600
2025-01-25 01:00 | -6704.08 | 6.108 | 49.3673 | 59.8258 | -1964.7719 |  | 1777 | 6397200 | 37933200 | 69469200 | 101005200
2025-01-26 02:00 | -7238.26 | 6.108 | 48.6874 | 59.8258 | -2121.3246 |  | 1778 | 6400800 | 37936800 | 69472800 | 101008800
2025-01-27 03:00 | -7397.43 | 6.108 | 48.2884 | 59.8258 | -2167.9727 |  | 1779 | 6404400 | 37940400 | 69476400 | 101012400
2025-01-28 04:00 | -7300.85 | 6.108 | 48.1287 | 59.8258 | -2139.6679 |  | 1780 | 6408000 | 37944000 | 69480000 | 101016000
2025-01-29 05:00 | -7164.82 | 6.108 | 48.0715 | 59.8258 | -2099.8015 |  | 1781 | 6411600 | 37947600 | 69483600 | 101019600
2025-01-30 06:00 | -6774.6 | 6.108 | 48.264 | 59.8258 | -1985.4393 |  | 1782 | 6415200 | 37951200 | 69487200 | 101023200
2025-01-31 07:00 | -6628.11 | 6.108 | 48.3389 | 59.8258 | -1942.5073 |  | 1783 | 6418800 | 37954800 | 69490800 | 101026800
2025-02-01 08:00 | -5166.17 | 6.108 | 49.4065 | 59.8258 | -1514.055 |  | 1784 | 6422400 | 37958400 | 69494400 | 101030400
2025-02-02 09:00 | -4190.8 | 6.108 | 50.3045 | 59.8258 | -1228.2022 |  | 1785 | 6426000 | 37962000 | 69498000 | 101034000
2025-02-03 10:00 | -2899.94 | 6.108 | 51.4776 | 59.8258 | -849.8885 |  | 1786 | 6429600 | 37965600 | 69501600 | 101037600
2025-02-04 11:00 | -1290.91 | 4.0876 | 52.4762 | 59.8258 | -378.3284 |  | 1787 | 6433200 | 37969200 | 69505200 | 101041200
2025-02-05 12:00 | 0 | 1 | 54.2924 | 59.8258 | 0 |  | 1788 | 6436800 | 37972800 | 69508800 | 101044800
2025-02-06 13:00 | 13.7325 | 1 | 54.683 | 59.8258 | 4.0246 |  | 1789 | 6440400 | 37976400 | 69512400 | 101048400
2025-02-07 14:00 | 1078.84 | 1 | 54.8257 | 59.8258 | 316.1768 |  | 1790 | 6444000 | 37980000 | 69516000 | 101052000
2025-02-08 15:00 | 1989.23 | 1 | 55.0612 | 59.8258 | 582.9858 |  | 1791 | 6447600 | 37983600 | 69519600 | 101055600
2025-02-09 16:00 | 2899.72 | 1 | 55.3264 | 59.8258 | 849.824 |  | 1792 | 6451200 | 37987200 | 69523200 | 101059200
2025-02-10 17:00 | 1882.18 | 1 | 55.7577 | 59.8258 | 551.6125 |  | 1793 | 6454800 | 37990800 | 69526800 | 101062800
2025-02-11 18:00 | -183.282 | 1.1601 | 55.305 | 59.8258 | -53.7147 |  | 1794 | 6458400 | 37994400 | 69530400 | 101066400
2025-02-12 19:00 | -1016.46 | 3.5833 | 54.5938 | 59.8258 | -297.895 |  | 1795 | 6462000 | 37998000 | 69534000 | 101070000
2025-02-13 20:00 | -2336.9 | 6.108 | 54.0139 | 59.8258 | -684.8778 |  | 1796 | 6465600 | 38001600 | 69537600 | 101073600
2025-02-14 21:00 | -3728.02 | 6.108 | 52.7624 | 59.8258 | -1092.5748 |  | 1797 | 6469200 | 38005200 | 69541200 | 101077200
2025-02-15 22:00 | -4504.52 | 6.108 | 51.8578 | 59.8258 | -1320.1445 |  | 1798 | 6472800 | 38008800 | 69544800 | 101080800
2025-02-16 23:00 | -5646.6 | 6.108 | 50.7152 | 59.8258 | -1654.8551 |  | 1799 | 6476400 | 38012400 | 69548400 | 101084400
2025-02-18 | -6371.14 | 6.108 | 49.8563 | 59.8258 | -1867.1968 |  | 1800 | 6480000 | 38016000 | 69552000 | 101088000
2025-02-19 01:00 | -6224.36 | 6.108 | 49.6671 | 59.8258 | -1824.1798 |  | 1801 | 6483600 | 38019600 | 69555600 | 101091600
2025-02-20 02:00 | -6605.79 | 6.108 | 49.2059 | 59.8258 | -1935.9659 |  | 1802 | 6487200 | 38023200 | 69559200 | 101095200
2025-02-21 03:00 | -6284.79 | 6.108 | 49.2592 | 59.8258 | -1841.8901 |  | 1803 | 6490800 | 38026800 | 69562800 | 101098800
2025-02-22 04:00 | -6620.46 | 6.108 | 48.8879 | 59.8258 | -1940.2653 |  | 1804 | 6494400 | 38030400 | 69566400 | 101102400
2025-02-23 05:00 | -7224.6 | 6.108 | 48.3001 | 59.8258 | -2117.3213 |  | 1805 | 6498000 | 38034000 | 69570000 | 101106000
2025-02-24 06:00 | -6891.49 | 6.108 | 48.3778 | 59.8258 | -2019.6963 |  | 1806 | 6501600 | 38037600 | 69573600 | 101109600
2025-02-25 07:00 | -5640.66 | 6.108 | 49.241 | 59.8258 | -1653.1143 |  | 1807 | 6505200 | 38041200 | 69577200 | 101113200
2025-02-26 08:00 | -4544.8 | 6.108 | 50.1699 | 59.8258 | -1331.9494 |  | 1808 | 6508800 | 38044800 | 69580800 | 101116800
2025-02-27 09:00 | -3753.21 | 6.108 | 50.9355 | 59.8258 | -1099.9573 |  | 1809 | 6512400 | 38048400 | 69584400 | 101120400
2025-02-28 10:00 | -2383.23 | 6.108 | 52.1379 | 59.8258 | -698.4558 |  | 1810 | 6516000 | 38052000 | 69588000 | 101124000
2025-03-01 11:00 | -1506.39 | 4.7338 | 52.7534 | 59.8258 | -441.4793 |  | 1811 | 6519600 | 38055600 | 69591600 | 101127600
2025-03-02 12:00 | -609.679 | 2.0311 | 53.1228 | 59.8258 | -178.6793 |  | 1812 | 6523200 | 38059200 | 69595200 | 101131200
2025-03-03 13:00 | -209.092 | 1.0649 | 53.8767 | 59.8258 | -61.2788 |  | 1813 | 6526800 | 38062800 | 69598800 | 101134800
2025-03-04 14:00 | 2288.46 | 1 | 54.8027 | 59.8258 | 670.6814 |  | 1814 | 6530400 | 38066400 | 69602400 | 101138400
2025-03-05 15:00 | 2150.43 | 1 | 55.2944 | 59.8258 | 630.2288 |  | 1815 | 6534000 | 38070000 | 69606000 | 101142000
2025-03-06 16:00 | -195.169 | 1.1996 | 55.0062 | 59.8258 | -57.1984 |  | 1816 | 6537600 | 38073600 | 69609600 | 101145600
2025-03-07 17:00 | -162.17 | 0.9948 | 54.8699 | 59.8258 | -47.5273 |  | 1817 | 6541200 | 38077200 | 69613200 | 101149200
2025-03-08 18:00 | -1215.87 | 4.2156 | 54.3023 | 59.8258 | -356.3363 |  | 1818 | 6544800 | 38080800 | 69616800 | 101152800
2025-03-09 19:00 | -2747.98 | 6.108 | 53.4968 | 59.8258 | -805.3534 |  | 1819 | 6548400 | 38084400 | 69620400 | 101156400
2025-03-10 20:00 | -3732.49 | 6.108 | 52.4809 | 59.8258 | -1093.8848 |  | 1820 | 6552000 | 38088000 | 69624000 | 101160000
2025-03-11 21:00 | -4411 | 6.108 | 51.6915 | 59.8258 | -1292.7365 |  | 1821 | 6555600 | 38091600 | 69627600 | 101163600
2025-03-12 22:00 | -5160.4 | 6.108 | 50.9112 | 59.8258 | -1512.3639 |  | 1822 | 6559200 | 38095200 | 69631200 | 101167200
2025-03-13 23:00 | -5592.33 | 6.108 | 50.3411 | 59.8258 | -1638.9501 |  | 1823 | 6562800 | 38098800 | 69634800 | 101170800
2025-03-15 | -7203.95 | 6.108 | 48.9127 | 59.8258 | -2111.2693 |  | 1824 | 6566400 | 38102400 | 69638400 | 101174400
2025-03-16 01:00 | -7782.42 | 6.108 | 48.1185 | 59.8258 | -2280.8022 |  | 1825 | 6570000 | 38106000 | 69642000 | 101178000
2025-03-17 02:00 | -7846.19 | 6.108 | 47.7378 | 59.8258 | -2299.4913 |  | 1826 | 6573600 | 38109600 | 69645600 | 101181600
2025-03-18 03:00 | -8289 | 6.108 | 47.1686 | 59.8258 | -2429.2661 |  | 1827 | 6577200 | 38113200 | 69649200 | 101185200
2025-03-19 04:00 | -8738.31 | 6.108 | 46.6014 | 59.8258 | -2560.9459 |  | 1828 | 6580800 | 38116800 | 69652800 | 101188800
2025-03-20 05:00 | -8720.48 | 6.108 | 46.3634 | 59.8258 | -2555.7204 |  | 1829 | 6584400 | 38120400 | 69656400 | 101192400
2025-03-21 06:00 | -9173.06 | 6.108 | 45.8615 | 59.8258 | -2688.3585 |  | 1830 | 6588000 | 38124000 | 69660000 | 101196000
2025-03-22 07:00 | -7838.32 | 6.108 | 46.6786 | 59.8258 | -2297.1848 |  | 1831 | 6591600 | 38127600 | 69663600 | 101199600
2025-03-23 08:00 | -6665.15 | 6.108 | 47.5867 | 59.8258 | -1953.3626 |  | 1832 | 6595200 | 38131200 | 69667200 | 101203200
2025-03-24 09:00 | -5528.65 | 6.108 | 48.5774 | 59.8258 | -1620.2874 |  | 1833 | 6598800 | 38134800 | 69670800 | 101206800
2025-03-25 10:00 | -4407.95 | 6.108 | 49.6034 | 59.8258 | -1291.8426 |  | 1834 | 6602400 | 38138400 | 69674400 | 101210400
2025-03-26 11:00 | -3041.42 | 6.108 | 50.8547 | 59.8258 | -891.3522 |  | 1835 | 6606000 | 38142000 | 69678000 | 101214000
2025-03-27 12:00 | -2000.76 | 6.108 | 51.9636 | 59.8258 | -586.3649 |  | 1836 | 6609600 | 38145600 | 69681600 | 101217600
2025-03-28 13:00 | -1519.65 | 4.7856 | 52.334 | 59.8258 | -445.3655 |  | 1837 | 6613200 | 38149200 | 69685200 | 101221200
2025-03-29 14:00 | -1554.11 | 5.015 | 52.6115 | 59.8258 | -455.4647 |  | 1838 | 6616800 | 38152800 | 69688800 | 101224800
2025-03-30 15:00 | -1239.95 | 3.9882 | 52.7552 | 59.8258 | -363.3935 |  | 1839 | 6620400 | 38156400 | 69692400 | 101228400
2025-03-31 16:00 | -1303.78 | 4.2868 | 52.9538 | 59.8258 | -382.1002 |  | 1840 | 6624000 | 38160000 | 69696000 | 101232000
2025-04-01 17:00 | -376.438 | 1.3541 | 53.1804 | 59.8258 | -110.3231 |  | 1841 | 6627600 | 38163600 | 69699600 | 101235600
2025-04-02 18:00 | -1415.45 | 4.8667 | 53.3537 | 59.8258 | -414.8274 |  | 1842 | 6631200 | 38167200 | 69703200 | 101239200
2025-04-03 19:00 | -3118.7 | 6.108 | 52.3711 | 59.8258 | -914.0007 |  | 1843 | 6634800 | 38170800 | 69706800 | 101242800
2025-04-04 20:00 | -4252.65 | 6.108 | 51.3343 | 59.8258 | -1246.3287 |  | 1844 | 6638400 | 38174400 | 69710400 | 101246400
2025-04-05 21:00 | -5186.37 | 6.108 | 50.4151 | 59.8258 | -1519.975 |  | 1845 | 6642000 | 38178000 | 69714000 | 101250000
2025-04-06 22:00 | -6077.62 | 6.108 | 49.5198 | 59.8258 | -1781.1746 |  | 1846 | 6645600 | 38181600 | 69717600 | 101253600
2025-04-07 23:00 | -6550.82 | 6.108 | 48.8791 | 59.8258 | -1919.8558 |  | 1847 | 6649200 | 38185200 | 69721200 | 101257200
2025-04-09 | -8071.02 | 6.108 | 47.4949 | 59.8258 | -2365.3825 |  | 1848 | 6652800 | 38188800 | 69724800 | 101260800
2025-04-10 01:00 | -8822.34 | 6.108 | 46.5715 | 59.8258 | -2585.5726 |  | 1849 | 6656400 | 38192400 | 69728400 | 101264400
2025-04-11 02:00 | -9099.47 | 6.108 | 46.0344 | 59.8258 | -2666.7914 |  | 1850 | 6660000 | 38196000 | 69732000 | 101268000
2025-04-12 03:00 | -9329.51 | 6.108 | 45.6107 | 59.8258 | -2734.2095 |  | 1851 | 6663600 | 38199600 | 69735600 | 101271600
2025-04-13 04:00 | -9386.23 | 6.108 | 45.3529 | 59.8258 | -2750.8325 |  | 1852 | 6667200 | 38203200 | 69739200 | 101275200
2025-04-14 05:00 | -9540.23 | 6.108 | 45.0393 | 59.8258 | -2795.9654 |  | 1853 | 6670800 | 38206800 | 69742800 | 101278800
2025-04-15 06:00 | -8728.79 | 6.108 | 45.4906 | 59.8258 | -2558.1558 |  | 1854 | 6674400 | 38210400 | 69746400 | 101282400
2025-04-16 07:00 | -7948.71 | 6.108 | 46.0667 | 59.8258 | -2329.5369 |  | 1855 | 6678000 | 38214000 | 69750000 | 101286000
2025-04-17 08:00 | -6187.8 | 6.108 | 47.4518 | 59.8258 | -1813.4652 |  | 1856 | 6681600 | 38217600 | 69753600 | 101289600
2025-04-18 09:00 | -4232.32 | 6.108 | 49.1572 | 59.8258 | -1240.3706 |  | 1857 | 6685200 | 38221200 | 69757200 | 101293200
2025-04-19 10:00 | -2312.44 | 6.108 | 50.9716 | 59.8258 | -677.7093 |  | 1858 | 6688800 | 38224800 | 69760800 | 101296800
2025-04-20 11:00 | -661.076 | 2.0905 | 51.7089 | 59.8258 | -193.7423 |  | 1859 | 6692400 | 38228400 | 69764400 | 101300400
2025-04-21 12:00 | 2731.69 | 1 | 53.4186 | 59.8258 | 800.5793 |  | 1860 | 6696000 | 38232000 | 69768000 | 101304000
2025-04-22 13:00 | 2933.94 | 1 | 73.6106 | 59.8258 | 859.8529 |  | 1861 | 6699600 | 38235600 | 69771600 | 101307600
2025-04-23 14:00 | 2916.52 | 1 | 70.3848 | 59.8258 | 854.7476 |  | 1862 | 6703200 | 38239200 | 69775200 | 101311200
2025-04-24 15:00 | 3171.31 | 1.0657 | 68.9003 | 59.8258 | 929.4192 |  | 1863 | 6706800 | 38242800 | 69778800 | 101314800
2025-04-25 16:00 | 3970.06 | 1.3073 | 69.509 | 59.8258 | 1163.5097 |  | 1864 | 6710400 | 38246400 | 69782400 | 101318400
2025-04-26 17:00 | 2949.9 | 1 | 71.0263 | 59.8258 | 864.5303 |  | 1865 | 6714000 | 38250000 | 69786000 | 101322000
2025-04-27 18:00 | 2861.46 | 1 | 55.855 | 59.8258 | 838.6111 |  | 1866 | 6717600 | 38253600 | 69789600 | 101325600
2025-04-28 19:00 | -575.416 | 2.3044 | 55.106 | 59.8258 | -168.6378 |  | 1867 | 6721200 | 38257200 | 69793200 | 101329200
2025-04-29 20:00 | -1599.07 | 5.2714 | 54.5623 | 59.8258 | -468.6412 |  | 1868 | 6724800 | 38260800 | 69796800 | 101332800
2025-04-30 21:00 | -3285.31 | 6.108 | 53.2289 | 59.8258 | -962.8293 |  | 1869 | 6728400 | 38264400 | 69800400 | 101336400
2025-05-01 22:00 | -3975.31 | 6.108 | 52.3659 | 59.8258 | -1165.0484 |  | 1870 | 6732000 | 38268000 | 69804000 | 101340000
2025-05-02 23:00 | -5045.44 | 6.108 | 51.265 | 59.8258 | -1478.6725 |  | 1871 | 6735600 | 38271600 | 69807600 | 101343600
2025-05-04 | -5495.31 | 6.108 | 50.5578 | 59.8258 | -1610.5164 |  | 1872 | 6739200 | 38275200 | 69811200 | 101347200
2025-05-05 01:00 | -6160.86 | 6.108 | 49.7958 | 59.8258 | -1805.5698 |  | 1873 | 6742800 | 38278800 | 69814800 | 101350800
2025-05-06 02:00 | -6502.58 | 6.108 | 49.2741 | 59.8258 | -1905.7181 |  | 1874 | 6746400 | 38282400 | 69818400 | 101354400
2025-05-07 03:00 | -6703.83 | 6.108 | 48.9032 | 59.8258 | -1964.6986 |  | 1875 | 6750000 | 38286000 | 69822000 | 101358000
2025-05-08 04:00 | -7040.82 | 6.108 | 48.4536 | 59.8258 | -2063.4607 |  | 1876 | 6753600 | 38289600 | 69825600 | 101361600
2025-05-09 05:00 | -7380.97 | 6.108 | 48.0151 | 59.8258 | -2163.1488 |  | 1877 | 6757200 | 38293200 | 69829200 | 101365200
2025-05-10 06:00 | -6574.28 | 6.108 | 48.4255 | 59.8258 | -1926.7313 |  | 1878 | 6760800 | 38296800 | 69832800 | 101368800
2025-05-11 07:00 | -5931.46 | 6.108 | 48.9023 | 59.8258 | -1738.3393 |  | 1879 | 6764400 | 38300400 | 69836400 | 101372400
2025-05-12 08:00 | -3700.93 | 6.108 | 50.6278 | 59.8258 | -1084.6355 |  | 1880 | 6768000 | 38304000 | 69840000 | 101376000
2025-05-13 09:00 | -2607.53 | 6.108 | 51.7483 | 59.8258 | -764.1916 |  | 1881 | 6771600 | 38307600 | 69843600 | 101379600
2025-05-14 10:00 | -819.752 | 2.5751 | 52.5375 | 59.8258 | -240.2456 |  | 1882 | 6775200 | 38311200 | 69847200 | 101383200
2025-05-15 11:00 | 1320.3 | 1 | 54.2896 | 59.8258 | 386.9417 |  | 1883 | 6778800 | 38314800 | 69850800 | 101386800
2025-05-16 12:00 | 3015.57 | 1 | 72.8674 | 59.8258 | 883.7763 |  | 1884 | 6782400 | 38318400 | 69854400 | 101390400
2025-05-17 13:00 | 3626.58 | 1.1957 | 69.346 | 59.8258 | 1062.8457 |  | 1885 | 6786000 | 38322000 | 69858000 | 101394000
2025-05-18 14:00 | 4408.57 | 1.4326 | 69.9769 | 59.8258 | 1292.0243 |  | 1886 | 6789600 | 38325600 | 69861600 | 101397600
2025-05-19 15:00 | 3030.92 | 1.0008 | 70.1675 | 59.8258 | 888.275 |  | 1887 | 6793200 | 38329200 | 69865200 | 101401200
2025-05-20 16:00 | 4745.04 | 1.5042 | 70.8502 | 59.8258 | 1390.6339 |  | 1888 | 6796800 | 38332800 | 69868800 | 101404800
2025-05-21 17:00 | 3563.13 | 1.1742 | 70.6626 | 59.8258 | 1044.2503 |  | 1889 | 6800400 | 38336400 | 69872400 | 101408400
2025-05-22 18:00 | 2938.39 | 1 | 77.6744 | 59.8258 | 861.1571 |  | 1890 | 6804000 | 38340000 | 69876000 | 101412000
2025-05-23 19:00 | 2797.75 | 1 | 56.6701 | 59.8258 | 819.9396 |  | 1891 | 6807600 | 38343600 | 69879600 | 101415600
2025-05-24 20:00 | -369.235 | 1.6914 | 55.9847 | 59.8258 | -108.2121 |  | 1892 | 6811200 | 38347200 | 69883200 | 101419200
2025-05-25 21:00 | -1611.27 | 5.3097 | 55.2912 | 59.8258 | -472.2166 |  | 1893 | 6814800 | 38350800 | 69886800 | 101422800
2025-05-26 22:00 | -2445.41 | 6.108 | 54.5054 | 59.8258 | -716.6789 |  | 1894 | 6818400 | 38354400 | 69890400 | 101426400
2025-05-27 23:00 | -3680.54 | 6.108 | 53.3145 | 59.8258 | -1078.6598 |  | 1895 | 6822000 | 38358000 | 69894000 | 101430000
2025-05-29 | -4030.71 | 6.108 | 52.7109 | 59.8258 | -1181.2845 |  | 1896 | 6825600 | 38361600 | 69897600 | 101433600
2025-05-30 01:00 | -4481.53 | 6.108 | 52.0858 | 59.8258 | -1313.4068 |  | 1897 | 6829200 | 38365200 | 69901200 | 101437200
2025-05-31 02:00 | -4630.02 | 6.108 | 51.7549 | 59.8258 | -1356.9249 |  | 1898 | 6832800 | 38368800 | 69904800 | 101440800
2025-06-01 03:00 | -4575.68 | 6.108 | 51.6398 | 59.8258 | -1340.9994 |  | 1899 | 6836400 | 38372400 | 69908400 | 101444400
2025-06-02 04:00 | -4479.15 | 6.108 | 51.5899 | 59.8258 | -1312.7093 |  | 1900 | 6840000 | 38376000 | 69912000 | 101448000
2025-06-03 05:00 | -4274.43 | 6.108 | 51.6815 | 59.8258 | -1252.7118 |  | 1901 | 6843600 | 38379600 | 69915600 | 101451600
2025-06-04 06:00 | -3684.94 | 6.108 | 52.0901 | 59.8258 | -1079.9493 |  | 1902 | 6847200 | 38383200 | 69919200 | 101455200
2025-06-05 07:00 | -3480.02 | 6.108 | 52.2797 | 59.8258 | -1019.8932 |  | 1903 | 6850800 | 38386800 | 69922800 | 101458800
2025-06-06 08:00 | -3050.88 | 6.108 | 52.6431 | 59.8258 | -894.1247 |  | 1904 | 6854400 | 38390400 | 69926400 | 101462400
2025-06-07 09:00 | -2931.09 | 6.108 | 52.8005 | 59.8258 | -859.0177 |  | 1905 | 6858000 | 38394000 | 69930000 | 101466000
2025-06-08 10:00 | -2422.89 | 6.108 | 53.2214 | 59.8258 | -710.079 |  | 1906 | 6861600 | 38397600 | 69933600 | 101469600
2025-06-09 11:00 | -2353.69 | 6.108 | 53.3511 | 59.8258 | -689.7984 |  | 1907 | 6865200 | 38401200 | 69937200 | 101473200
2025-06-10 12:00 | -2194.22 | 6.108 | 53.493 | 59.8258 | -643.0624 |  | 1908 | 6868800 | 38404800 | 69940800 | 101476800
2025-06-11 13:00 | -2390.07 | 6.108 | 53.3648 | 59.8258 | -700.4604 |  | 1909 | 6872400 | 38408400 | 69944400 | 101480400
2025-06-12 14:00 | -2466.35 | 6.108 | 53.2718 | 59.8258 | -722.8158 |  | 1910 | 6876000 | 38412000 | 69948000 | 101484000
2025-06-13 15:00 | -2520.07 | 6.108 | 53.1927 | 59.8258 | -738.5596 |  | 1911 | 6879600 | 38415600 | 69951600 | 101487600
2025-06-14 16:00 | -1926.66 | 6.0118 | 53.5571 | 59.8258 | -564.6483 |  | 1912 | 6883200 | 38419200 | 69955200 | 101491200
2025-06-15 17:00 | -1850.72 | 5.7459 | 53.5853 | 59.8258 | -542.3925 |  | 1913 | 6886800 | 38422800 | 69958800 | 101494800
2025-06-16 18:00 | -1861.9 | 5.8087 | 53.6029 | 59.8258 | -545.669 |  | 1914 | 6890400 | 38426400 | 69962400 | 101498400
2025-06-17 19:00 | -2236.49 | 6.108 | 53.3965 | 59.8258 | -655.4505 |  | 1915 | 6894000 | 38430000 | 69966000 | 101502000
2025-06-18 20:00 | -2596.71 | 6.108 | 53.0953 | 59.8258 | -761.0206 |  | 1916 | 6897600 | 38433600 | 69969600 | 101505600
2025-06-19 21:00 | -3759.85 | 6.108 | 52.1785 | 59.8258 | -1101.9033 |  | 1917 | 6901200 | 38437200 | 69973200 | 101509200
2025-06-20 22:00 | -4180.67 | 6.108 | 51.6807 | 59.8258 | -1225.2334 |  | 1918 | 6904800 | 38440800 | 69976800 | 101512800
2025-06-21 23:00 | -4917.75 | 6.108 | 50.9765 | 59.8258 | -1441.2503 |  | 1919 | 6908400 | 38444400 | 69980400 | 101516400
2025-06-23 | -5499.74 | 6.108 | 50.3561 | 59.8258 | -1611.8147 |  | 1920 | 6912000 | 38448000 | 69984000 | 101520000
2025-06-24 01:00 | -5699.64 | 6.108 | 50.0156 | 59.8258 | -1670.3996 |  | 1921 | 6915600 | 38451600 | 69987600 | 101523600
2025-06-25 02:00 | -5799.13 | 6.108 | 49.7933 | 59.8258 | -1699.5572 |  | 1922 | 6919200 | 38455200 | 69991200 | 101527200
2025-06-26 03:00 | -5782.71 | 6.108 | 49.7041 | 59.8258 | -1694.745 |  | 1923 | 6922800 | 38458800 | 69994800 | 101530800
2025-06-27 04:00 | -5785.77 | 6.108 | 49.6189 | 59.8258 | -1695.6418 |  | 1924 | 6926400 | 38462400 | 69998400 | 101534400
2025-06-28 05:00 | -5677.89 | 6.108 | 49.6346 | 59.8258 | -1664.0253 |  | 1925 | 6930000 | 38466000 | 70002000 | 101538000
2025-06-29 06:00 | -5044.86 | 6.108 | 50.0674 | 59.8258 | -1478.5025 |  | 1926 | 6933600 | 38469600 | 70005600 | 101541600
2025-06-30 07:00 | -5009.43 | 6.108 | 50.1368 | 59.8258 | -1468.119 |  | 1927 | 6937200 | 38473200 | 70009200 | 101545200
2025-07-01 08:00 | -4579.95 | 6.108 | 50.4619 | 59.8258 | -1342.2508 |  | 1928 | 6940800 | 38476800 | 70012800 | 101548800
2025-07-02 09:00 | -4397.43 | 6.108 | 50.6449 | 59.8258 | -1288.7595 |  | 1929 | 6944400 | 38480400 | 70016400 | 101552400
2025-07-03 10:00 | -3717.35 | 6.108 | 51.1947 | 59.8258 | -1089.4477 |  | 1930 | 6948000 | 38484000 | 70020000 | 101556000
2025-07-04 11:00 | -3156.5 | 6.108 | 51.7196 | 59.8258 | -925.0788 |  | 1931 | 6951600 | 38487600 | 70023600 | 101559600
2025-07-05 12:00 | -2650.66 | 6.108 | 52.2188 | 59.8258 | -776.8318 |  | 1932 | 6955200 | 38491200 | 70027200 | 101563200
2025-07-06 13:00 | -2340.15 | 6.108 | 52.5848 | 59.8258 | -685.8303 |  | 1933 | 6958800 | 38494800 | 70030800 | 101566800
2025-07-07 14:00 | -1883.19 | 5.9111 | 52.9971 | 59.8258 | -551.9085 |  | 1934 | 6962400 | 38498400 | 70034400 | 101570400
2025-07-08 15:00 | -1806.71 | 5.6542 | 53.1363 | 59.8258 | -529.4944 |  | 1935 | 6966000 | 38502000 | 70038000 | 101574000
2025-07-09 16:00 | -1256.08 | 3.9446 | 53.2311 | 59.8258 | -368.1207 |  | 1936 | 6969600 | 38505600 | 70041600 | 101577600
2025-07-10 17:00 | -1215.14 | 3.9868 | 53.4297 | 59.8258 | -356.1224 |  | 1937 | 6973200 | 38509200 | 70045200 | 101581200
2025-07-11 18:00 | -1255.23 | 4.1025 | 53.5174 | 59.8258 | -367.8716 |  | 1938 | 6976800 | 38512800 | 70048800 | 101584800
2025-07-12 19:00 | -1906.28 | 6.108 | 53.5568 | 59.8258 | -558.6755 |  | 1939 | 6980400 | 38516400 | 70052400 | 101588400
2025-07-13 20:00 | -2377.95 | 6.108 | 53.1778 | 59.8258 | -696.9084 |  | 1940 | 6984000 | 38520000 | 70056000 | 101592000
2025-07-14 21:00 | -3165.98 | 6.108 | 52.5446 | 59.8258 | -927.8571 |  | 1941 | 6987600 | 38523600 | 70059600 | 101595600
2025-07-15 22:00 | -3548.4 | 6.108 | 52.1432 | 59.8258 | -1039.9334 |  | 1942 | 6991200 | 38527200 | 70063200 | 101599200
2025-07-16 23:00 | -4620.2 | 6.108 | 51.236 | 59.8258 | -1354.047 |  | 1943 | 6994800 | 38530800 | 70066800 | 101602800
2025-07-18 | -4860.57 | 6.108 | 50.8554 | 59.8258 | -1424.4925 |  | 1944 | 6998400 | 38534400 | 70070400 | 101606400
2025-07-19 01:00 | -5177.56 | 6.108 | 50.4747 | 59.8258 | -1517.393 |  | 1945 | 7002000 | 38538000 | 70074000 | 101610000
2025-07-20 02:00 | -5398.65 | 6.108 | 50.1802 | 59.8258 | -1582.1881 |  | 1946 | 7005600 | 38541600 | 70077600 | 101613600
2025-07-21 03:00 | -5514.98 | 6.108 | 49.9779 | 59.8258 | -1616.2811 |  | 1947 | 7009200 | 38545200 | 70081200 | 101617200
2025-07-22 04:00 | -5402.38 | 6.108 | 49.9576 | 59.8258 | -1583.2813 |  | 1948 | 7012800 | 38548800 | 70084800 | 101620800
2025-07-23 05:00 | -5217.79 | 6.108 | 50.0445 | 59.8258 | -1529.1833 |  | 1949 | 7016400 | 38552400 | 70088400 | 101624400
2025-07-24 06:00 | -4834.61 | 6.108 | 50.3025 | 59.8258 | -1416.8843 |  | 1950 | 7020000 | 38556000 | 70092000 | 101628000
2025-07-25 07:00 | -4568.99 | 6.108 | 50.5228 | 59.8258 | -1339.0388 |  | 1951 | 7023600 | 38559600 | 70095600 | 101631600
2025-07-26 08:00 | -4240.43 | 6.108 | 50.8005 | 59.8258 | -1242.7474 |  | 1952 | 7027200 | 38563200 | 70099200 | 101635200
2025-07-27 09:00 | -4122.82 | 6.108 | 50.943 | 59.8258 | -1208.2793 |  | 1953 | 7030800 | 38566800 | 70102800 | 101638800
2025-07-28 10:00 | -3533.11 | 6.108 | 51.4192 | 59.8258 | -1035.4523 |  | 1954 | 7034400 | 38570400 | 70106400 | 101642400
2025-07-29 11:00 | -2692.6 | 6.108 | 52.147 | 59.8258 | -789.1232 |  | 1955 | 7038000 | 38574000 | 70110000 | 101646000
2025-07-30 12:00 | -1990.47 | 6.108 | 52.832 | 59.8258 | -583.3492 |  | 1956 | 7041600 | 38577600 | 70113600 | 101649600
2025-07-31 13:00 | -1756.09 | 5.4836 | 53.0371 | 59.8258 | -514.6592 |  | 1957 | 7045200 | 38581200 | 70117200 | 101653200
2025-08-01 14:00 | -1463 | 4.6142 | 53.1859 | 59.8258 | -428.763 |  | 1958 | 7048800 | 38584800 | 70120800 | 101656800
2025-08-02 15:00 | -1306.4 | 4.2058 | 53.3508 | 59.8258 | -382.868 |  | 1959 | 7052400 | 38588400 | 70124400 | 101660400
2025-08-03 16:00 | -669.532 | 2.2614 | 53.5268 | 59.8258 | -196.2205 |  | 1960 | 7056000 | 38592000 | 70128000 | 101664000
2025-08-04 17:00 | -292.382 | 1.2939 | 54.0079 | 59.8258 | -85.6887 |  | 1961 | 7059600 | 38595600 | 70131600 | 101667600
2025-08-05 18:00 | -446.658 | 1.8576 | 54.0949 | 59.8258 | -130.9025 |  | 1962 | 7063200 | 38599200 | 70135200 | 101671200
2025-08-06 19:00 | -1124.41 | 3.8864 | 53.9644 | 59.8258 | -329.532 |  | 1963 | 7066800 | 38602800 | 70138800 | 101674800
2025-08-07 20:00 | -1585.59 | 5.1208 | 53.863 | 59.8258 | -464.6906 |  | 1964 | 7070400 | 38606400 | 70142400 | 101678400
2025-08-08 21:00 | -2546.97 | 6.108 | 53.3509 | 59.8258 | -746.4432 |  | 1965 | 7074000 | 38610000 | 70146000 | 101682000
2025-08-09 22:00 | -3236.16 | 6.108 | 52.7137 | 59.8258 | -948.4249 |  | 1966 | 7077600 | 38613600 | 70149600 | 101685600
2025-08-10 23:00 | -4062.77 | 6.108 | 51.9423 | 59.8258 | -1190.6804 |  | 1967 | 7081200 | 38617200 | 70153200 | 101689200
2025-08-12 | -4494.9 | 6.108 | 51.425 | 59.8258 | -1317.3252 |  | 1968 | 7084800 | 38620800 | 70156800 | 101692800
2025-08-13 01:00 | -4840.79 | 6.108 | 51.0009 | 59.8258 | -1418.6955 |  | 1969 | 7088400 | 38624400 | 70160400 | 101696400
2025-08-14 02:00 | -5186.83 | 6.108 | 50.5921 | 59.8258 | -1520.1098 |  | 1970 | 7092000 | 38628000 | 70164000 | 101700000
2025-08-15 03:00 | -5369.52 | 6.108 | 50.3142 | 59.8258 | -1573.651 |  | 1971 | 7095600 | 38631600 | 70167600 | 101703600
2025-08-16 04:00 | -5491.77 | 6.108 | 50.0965 | 59.8258 | -1609.4789 |  | 1972 | 7099200 | 38635200 | 70171200 | 101707200
2025-08-17 05:00 | -5393.7 | 6.108 | 50.0634 | 59.8258 | -1580.7374 |  | 1973 | 7102800 | 38638800 | 70174800 | 101710800
2025-08-18 06:00 | -5655.77 | 6.108 | 49.7928 | 59.8258 | -1657.5426 |  | 1974 | 7106400 | 38642400 | 70178400 | 101714400
2025-08-19 07:00 | -4515.63 | 6.108 | 50.5501 | 59.8258 | -1323.4005 |  | 1975 | 7110000 | 38646000 | 70182000 | 101718000
2025-08-20 08:00 | -3334.22 | 6.108 | 51.5129 | 59.8258 | -977.1634 |  | 1976 | 7113600 | 38649600 | 70185600 | 101721600
2025-08-21 09:00 | -3758.4 | 6.108 | 51.3882 | 59.8258 | -1101.4783 |  | 1977 | 7117200 | 38653200 | 70189200 | 101725200
2025-08-22 10:00 | -3481.51 | 6.108 | 51.6248 | 59.8258 | -1020.3299 |  | 1978 | 7120800 | 38656800 | 70192800 | 101728800
2025-08-23 11:00 | -2898.71 | 6.108 | 52.1087 | 59.8258 | -849.528 |  | 1979 | 7124400 | 38660400 | 70196400 | 101732400
2025-08-24 12:00 | -981.032 | 3.0777 | 52.9453 | 59.8258 | -287.5121 |  | 1980 | 7128000 | 38664000 | 70200000 | 101736000
2025-08-25 13:00 | -420.618 | 1.6109 | 53.5304 | 59.8258 | -123.271 |  | 1981 | 7131600 | 38667600 | 70203600 | 101739600
2025-08-26 14:00 | -912.837 | 3.2695 | 53.6905 | 59.8258 | -267.5261 |  | 1982 | 7135200 | 38671200 | 70207200 | 101743200
2025-08-27 15:00 | -1150.51 | 3.8424 | 53.6858 | 59.8258 | -337.1812 |  | 1983 | 7138800 | 38674800 | 70210800 | 101746800
2025-08-28 16:00 | -2011.7 | 6.108 | 53.602 | 59.8258 | -589.5711 |  | 1984 | 7142400 | 38678400 | 70214400 | 101750400
2025-08-29 17:00 | -1653.28 | 5.124 | 53.5782 | 59.8258 | -484.5285 |  | 1985 | 7146000 | 38682000 | 70218000 | 101754000
2025-08-30 18:00 | -2186.84 | 6.108 | 53.4341 | 59.8258 | -640.8995 |  | 1986 | 7149600 | 38685600 | 70221600 | 101757600
2025-08-31 19:00 | -2764.28 | 6.108 | 52.9358 | 59.8258 | -810.1305 |  | 1987 | 7153200 | 38689200 | 70225200 | 101761200
2025-09-01 20:00 | -3939.05 | 6.108 | 51.9357 | 59.8258 | -1154.4216 |  | 1988 | 7156800 | 38692800 | 70228800 | 101764800
2025-09-02 21:00 | -4448.75 | 6.108 | 51.345 | 59.8258 | -1303.7999 |  | 1989 | 7160400 | 38696400 | 70232400 | 101768400
2025-09-03 22:00 | -4721.71 | 6.108 | 50.9727 | 59.8258 | -1383.7966 |  | 1990 | 7164000 | 38700000 | 70236000 | 101772000
2025-09-04 23:00 | -5221.52 | 6.108 | 50.4585 | 59.8258 | -1530.2765 |  | 1991 | 7167600 | 38703600 | 70239600 | 101775600
2025-09-06 | -6371.45 | 6.108 | 49.4151 | 59.8258 | -1867.2877 |  | 1992 | 7171200 | 38707200 | 70243200 | 101779200
2025-09-07 01:00 | -6639.91 | 6.108 | 48.9225 | 59.8258 | -1945.9655 |  | 1993 | 7174800 | 38710800 | 70246800 | 101782800
2025-09-08 02:00 | -6659.13 | 6.108 | 48.7001 | 59.8258 | -1951.5984 |  | 1994 | 7178400 | 38714400 | 70250400 | 101786400
2025-09-09 03:00 | -6941.83 | 6.108 | 48.3479 | 59.8258 | -2034.4495 |  | 1995 | 7182000 | 38718000 | 70254000 | 101790000
2025-09-10 04:00 | -6887.03 | 6.108 | 48.237 | 59.8258 | -2018.3893 |  | 1996 | 7185600 | 38721600 | 70257600 | 101793600
2025-09-11 05:00 | -6815.85 | 6.108 | 48.1697 | 59.8258 | -1997.5285 |  | 1997 | 7189200 | 38725200 | 70261200 | 101797200
2025-09-12 06:00 | -7147.68 | 6.108 | 47.8475 | 59.8258 | -2094.7782 |  | 1998 | 7192800 | 38728800 | 70264800 | 101800800
2025-09-13 07:00 | -6107.57 | 6.108 | 48.5084 | 59.8258 | -1789.9521 |  | 1999 | 7196400 | 38732400 | 70268400 | 101804400
2025-09-14 08:00 | -5334 | 6.108 | 49.1345 | 59.8258 | -1563.2411 |  | 2000 | 7200000 | 38736000 | 70272000 | 101808000
2025-09-15 09:00 | -5006.2 | 6.108 | 49.4968 | 59.8258 | -1467.1724 |  | 2001 | 7203600 | 38739600 | 70275600 | 101811600
2025-09-16 10:00 | -4380.86 | 6.108 | 50.0431 | 59.8258 | -1283.9033 |  | 2002 | 7207200 | 38743200 | 70279200 | 101815200
2025-09-17 11:00 | -3613.84 | 6.108 | 50.7327 | 59.8258 | -1059.112 |  | 2003 | 7210800 | 38746800 | 70282800 | 101818800
2025-09-18 12:00 | -2193.3 | 6.108 | 51.9758 | 59.8258 | -642.7928 |  | 2004 | 7214400 | 38750400 | 70286400 | 101822400
2025-09-19 13:00 | -1846.84 | 5.8326 | 52.4518 | 59.8258 | -541.2554 |  | 2005 | 7218000 | 38754000 | 70290000 | 101826000
2025-09-20 14:00 | -1377.74 | 4.3411 | 52.6506 | 59.8258 | -403.7757 |  | 2006 | 7221600 | 38757600 | 70293600 | 101829600
2025-09-21 15:00 | -1319.36 | 4.3019 | 52.8962 | 59.8258 | -386.6662 |  | 2007 | 7225200 | 38761200 | 70297200 | 101833200
2025-09-22 16:00 | -1596.26 | 5.169 | 53.0428 | 59.8258 | -467.8176 |  | 2008 | 7228800 | 38764800 | 70300800 | 101836800
2025-09-23 17:00 | -554.717 | 1.8143 | 53.1282 | 59.8258 | -162.5715 |  | 2009 | 7232400 | 38768400 | 70304400 | 101840400
2025-09-24 18:00 | -1472.15 | 5.0034 | 53.3943 | 59.8258 | -431.4446 |  | 2010 | 7236000 | 38772000 | 70308000 | 101844000
2025-09-25 19:00 | -2699.13 | 6.108 | 52.7416 | 59.8258 | -791.0369 |  | 2011 | 7239600 | 38775600 | 70311600 | 101847600
2025-09-26 20:00 | -3644.81 | 6.108 | 51.8923 | 59.8258 | -1068.1884 |  | 2012 | 7243200 | 38779200 | 70315200 | 101851200
2025-09-27 21:00 | -4042.22 | 6.108 | 51.4292 | 59.8258 | -1184.6577 |  | 2013 | 7246800 | 38782800 | 70318800 | 101854800
2025-09-28 22:00 | -4716.35 | 6.108 | 50.8045 | 59.8258 | -1382.2257 |  | 2014 | 7250400 | 38786400 | 70322400 | 101858400
2025-09-29 23:00 | -5115.94 | 6.108 | 50.3228 | 59.8258 | -1499.334 |  | 2015 | 7254000 | 38790000 | 70326000 | 101862000
2025-10-01 | -6408.2 | 6.108 | 49.1833 | 59.8258 | -1878.058 |  | 2016 | 7257600 | 38793600 | 70329600 | 101865600
2025-10-02 01:00 | -6942.31 | 6.108 | 48.5075 | 59.8258 | -2034.5902 |  | 2017 | 7261200 | 38797200 | 70333200 | 101869200
2025-10-03 02:00 | -7385.32 | 6.108 | 47.9328 | 59.8258 | -2164.4236 |  | 2018 | 7264800 | 38800800 | 70336800 | 101872800
2025-10-04 03:00 | -7640.87 | 6.108 | 47.5242 | 59.8258 | -2239.3179 |  | 2019 | 7268400 | 38804400 | 70340400 | 101876400
2025-10-05 04:00 | -7716.28 | 6.108 | 47.2789 | 59.8258 | -2261.4184 |  | 2020 | 7272000 | 38808000 | 70344000 | 101880000
2025-10-06 05:00 | -8027.91 | 6.108 | 46.8722 | 59.8258 | -2352.7482 |  | 2021 | 7275600 | 38811600 | 70347600 | 101883600
2025-10-07 06:00 | -7566.58 | 6.108 | 47.0589 | 59.8258 | -2217.5457 |  | 2022 | 7279200 | 38815200 | 70351200 | 101887200
2025-10-08 07:00 | -6350.55 | 6.108 | 47.914 | 59.8258 | -1861.1625 |  | 2023 | 7282800 | 38818800 | 70354800 | 101890800
2025-10-09 08:00 | -4459.83 | 6.108 | 49.4385 | 59.8258 | -1307.0472 |  | 2024 | 7286400 | 38822400 | 70358400 | 101894400
2025-10-10 09:00 | -2977.02 | 6.108 | 50.8376 | 59.8258 | -872.4784 |  | 2025 | 7290000 | 38826000 | 70362000 | 101898000
2025-10-11 10:00 | -1128.15 | 3.5957 | 51.9705 | 59.8258 | -330.6281 |  | 2026 | 7293600 | 38829600 | 70365600 | 101901600
2025-10-12 11:00 | 1343.4 | 1 | 53.7414 | 59.8258 | 393.7117 |  | 2027 | 7297200 | 38833200 | 70369200 | 101905200
2025-10-13 12:00 | 3130.04 | 1 | 77.8094 | 59.8258 | 917.3242 |  | 2028 | 7300800 | 38836800 | 70372800 | 101908800
2025-10-14 13:00 | 3051.72 | 1 | 69.1983 | 59.8258 | 894.3708 |  | 2029 | 7304400 | 38840400 | 70376400 | 101912400
2025-10-15 14:00 | 3434.14 | 1.1006 | 69.7807 | 59.8258 | 1006.4471 |  | 2030 | 7308000 | 38844000 | 70380000 | 101916000
2025-10-16 15:00 | 3706.26 | 1.2087 | 69.8905 | 59.8258 | 1086.1976 |  | 2031 | 7311600 | 38847600 | 70383600 | 101919600
2025-10-17 16:00 | 4529.05 | 1.4342 | 70.6447 | 59.8258 | 1327.3335 |  | 2032 | 7315200 | 38851200 | 70387200 | 101923200
2025-10-18 17:00 | 3033.96 | 1 | 70.7042 | 59.8258 | 889.1659 |  | 2033 | 7318800 | 38854800 | 70390800 | 101926800
2025-10-19 18:00 | 3015.74 | 1 | 79.8854 | 59.8258 | 883.8261 |  | 2034 | 7322400 | 38858400 | 70394400 | 101930400
2025-10-20 19:00 | 0 | 0 | 56.7413 | 59.8258 | 0 |  | 2035 | 7326000 | 38862000 | 70398000 | 101934000
2025-10-21 20:00 | -1017.96 | 3.4829 | 55.1375 | 59.8258 | -298.3346 |  | 2036 | 7329600 | 38865600 | 70401600 | 101937600
2025-10-22 21:00 | -2516.36 | 6.108 | 54.3451 | 59.8258 | -737.4723 |  | 2037 | 7333200 | 38869200 | 70405200 | 101941200
2025-10-23 22:00 | -3446.04 | 6.108 | 53.3226 | 59.8258 | -1009.9346 |  | 2038 | 7336800 | 38872800 | 70408800 | 101944800
2025-10-24 23:00 | -4432.01 | 6.108 | 52.2619 | 59.8258 | -1298.8939 |  | 2039 | 7340400 | 38876400 | 70412400 | 101948400
2025-10-26 | -4711.57 | 6.108 | 51.6925 | 59.8258 | -1380.8249 |  | 2040 | 7344000 | 38880000 | 70416000 | 101952000
2025-10-27 01:00 | -5348.64 | 6.108 | 50.9801 | 59.8258 | -1567.5316 |  | 2041 | 7347600 | 38883600 | 70419600 | 101955600
2025-10-28 02:00 | -5532.23 | 6.108 | 50.5921 | 59.8258 | -1621.3366 |  | 2042 | 7351200 | 38887200 | 70423200 | 101959200
2025-10-29 03:00 | -6034.2 | 6.108 | 50.0199 | 59.8258 | -1768.4495 |  | 2043 | 7354800 | 38890800 | 70426800 | 101962800
2025-10-30 04:00 | -6052.04 | 6.108 | 49.7863 | 59.8258 | -1773.6778 |  | 2044 | 7358400 | 38894400 | 70430400 | 101966400
2025-10-31 05:00 | -5697.27 | 6.108 | 49.9068 | 59.8258 | -1669.705 |  | 2045 | 7362000 | 38898000 | 70434000 | 101970000
2025-11-01 06:00 | -4992.05 | 6.108 | 50.3614 | 59.8258 | -1463.0254 |  | 2046 | 7365600 | 38901600 | 70437600 | 101973600
2025-11-02 07:00 | -4375.78 | 6.108 | 50.8645 | 59.8258 | -1282.4145 |  | 2047 | 7369200 | 38905200 | 70441200 | 101977200
2025-11-03 08:00 | -2689.62 | 6.108 | 52.2025 | 59.8258 | -788.2498 |  | 2048 | 7372800 | 38908800 | 70444800 | 101980800
2025-11-04 09:00 | -1830.62 | 5.7627 | 53.0262 | 59.8258 | -536.5018 |  | 2049 | 7376400 | 38912400 | 70448400 | 101984400
2025-11-05 10:00 | -750.699 | 2.3554 | 53.2747 | 59.8258 | -220.0082 |  | 2050 | 7380000 | 38916000 | 70452000 | 101988000
2025-11-06 11:00 | 445.971 | 1 | 54.9831 | 59.8258 | 130.7012 |  | 2051 | 7383600 | 38919600 | 70455600 | 101991600
2025-11-07 12:00 | 2902.47 | 1 | 55.0915 | 59.8258 | 850.63 |  | 2052 | 7387200 | 38923200 | 70459200 | 101995200
2025-11-08 13:00 | -120.129 | 0.95389 | 55.314 | 59.8258 | -35.2063 |  | 2053 | 7390800 | 38926800 | 70462800 | 101998800
2025-11-09 14:00 | -440.796 | 1.8562 | 54.7141 | 59.8258 | -129.1846 |  | 2054 | 7394400 | 38930400 | 70466400 | 102002400
2025-11-10 15:00 | -504.004 | 1.9673 | 54.5671 | 59.8258 | -147.709 |  | 2055 | 7398000 | 38934000 | 70470000 | 102006000
2025-11-11 16:00 | 0 | 0 | 55.7661 | 59.8258 | 0 |  | 2056 | 7401600 | 38937600 | 70473600 | 102009600
2025-11-12 17:00 | 1979.89 | 1 | 55.6726 | 59.8258 | 580.2485 |  | 2057 | 7405200 | 38941200 | 70477200 | 102013200
2025-11-13 18:00 | 280.481 | 1 | 56.0851 | 59.8258 | 82.2009 |  | 2058 | 7408800 | 38944800 | 70480800 | 102016800
2025-11-14 19:00 | -442.79 | 1.9018 | 55.028 | 59.8258 | -129.7689 |  | 2059 | 7412400 | 38948400 | 70484400 | 102020400
2025-11-15 20:00 | -863.28 | 3.0492 | 54.7131 | 59.8258 | -253.0024 |  | 2060 | 7416000 | 38952000 | 70488000 | 102024000
2025-11-16 21:00 | -1580.75 | 5.1409 | 54.5654 | 59.8258 | -463.2721 |  | 2061 | 7419600 | 38955600 | 70491600 | 102027600
2025-11-17 22:00 | -1941.84 | 6.0558 | 54.4043 | 59.8258 | -569.0971 |  | 2062 | 7423200 | 38959200 | 70495200 | 102031200
2025-11-18 23:00 | -2630.08 | 6.108 | 53.7549 | 59.8258 | -770.8004 |  | 2063 | 7426800 | 38962800 | 70498800 | 102034800
2025-11-20 | -2789.64 | 6.108 | 53.457 | 59.8258 | -817.5628 |  | 2064 | 7430400 | 38966400 | 70502400 | 102038400
2025-11-21 01:00 | -2802.91 | 6.108 | 53.356 | 59.8258 | -821.4518 |  | 2065 | 7434000 | 38970000 | 70506000 | 102042000
2025-11-22 02:00 | -2778.7 | 6.108 | 53.3307 | 59.8258 | -814.3566 |  | 2066 | 7437600 | 38973600 | 70509600 | 102045600
2025-11-23 03:00 | -2699.54 | 6.108 | 53.3774 | 59.8258 | -791.1571 |  | 2067 | 7441200 | 38977200 | 70513200 | 102049200
2025-11-24 04:00 | -2375.18 | 6.108 | 53.6211 | 59.8258 | -696.0965 |  | 2068 | 7444800 | 38980800 | 70516800 | 102052800
2025-11-25 05:00 | -2056.66 | 6.108 | 53.8917 | 59.8258 | -602.7475 |  | 2069 | 7448400 | 38984400 | 70520400 | 102056400
2025-11-26 06:00 | -1575.54 | 4.8487 | 54.0157 | 59.8258 | -461.7452 |  | 2070 | 7452000 | 38988000 | 70524000 | 102060000
2025-11-27 07:00 | -1352.4 | 4.2767 | 54.1628 | 59.8258 | -396.3493 |  | 2071 | 7455600 | 38991600 | 70527600 | 102063600
2025-11-28 08:00 | -1019.59 | 3.3048 | 54.2826 | 59.8258 | -298.8123 |  | 2072 | 7459200 | 38995200 | 70531200 | 102067200
2025-11-29 09:00 | -1056.07 | 3.5107 | 54.4176 | 59.8258 | -309.5036 |  | 2073 | 7462800 | 38998800 | 70534800 | 102070800
2025-11-30 10:00 | -627.983 | 2.1779 | 54.5235 | 59.8258 | -184.0436 |  | 2074 | 7466400 | 39002400 | 70538400 | 102074400
2025-12-01 11:00 | -258.105 | 1.1854 | 54.9305 | 59.8258 | -75.6431 |  | 2075 | 7470000 | 39006000 | 70542000 | 102078000
2025-12-02 12:00 | 2325.89 | 1 | 55.8055 | 59.8258 | 681.6511 |  | 2076 | 7473600 | 39009600 | 70545600 | 102081600
2025-12-03 13:00 | 3001.92 | 1 | 56.152 | 59.8258 | 879.7759 |  | 2077 | 7477200 | 39013200 | 70549200 | 102085200
2025-12-04 14:00 | 3162.62 | 1 | 56.4701 | 59.8258 | 926.8724 |  | 2078 | 7480800 | 39016800 | 70552800 | 102088800
2025-12-05 15:00 | 3297.47 | 1 | 56.686 | 59.8258 | 966.3931 |  | 2079 | 7484400 | 39020400 | 70556400 | 102092400
2025-12-06 16:00 | 3184.87 | 1 | 72.6171 | 59.8258 | 933.3933 |  | 2080 | 7488000 | 39024000 | 70560000 | 102096000
2025-12-07 17:00 | 3329.06 | 1.0292 | 72.1117 | 59.8258 | 975.6512 |  | 2081 | 7491600 | 39027600 | 70563600 | 102099600
2025-12-08 18:00 | 3091.92 | 1 | 72.6629 | 59.8258 | 906.1523 |  | 2082 | 7495200 | 39031200 | 70567200 | 102103200
2025-12-09 19:00 | 3078.9 | 1 | 57.2325 | 59.8258 | 902.3365 |  | 2083 | 7498800 | 39034800 | 70570800 | 102106800
2025-12-10 20:00 | 3136.98 | 1 | 57.321 | 59.8258 | 919.3581 |  | 2084 | 7502400 | 39038400 | 70574400 | 102110400
2025-12-11 21:00 | -197.329 | 1.1591 | 56.9254 | 59.8258 | -57.8314 |  | 2085 | 7506000 | 39042000 | 70578000 | 102114000
2025-12-12 22:00 | -434.934 | 1.787 | 56.2444 | 59.8258 | -127.4666 |  | 2086 | 7509600 | 39045600 | 70581600 | 102117600
2025-12-13 23:00 | -1078.21 | 3.6589 | 55.822 | 59.8258 | -315.9922 |  | 2087 | 7513200 | 39049200 | 70585200 | 102121200
2025-12-15 | -1236.05 | 3.9654 | 55.5754 | 59.8258 | -362.2505 |  | 2088 | 7516800 | 39052800 | 70588800 | 102124800
2025-12-16 01:00 | -1274.83 | 4.0602 | 55.4146 | 59.8258 | -373.6158 |  | 2089 | 7520400 | 39056400 | 70592400 | 102128400
2025-12-17 02:00 | -1486.79 | 4.7028 | 55.2786 | 59.8258 | -435.7351 |  | 2090 | 7524000 | 39060000 | 70596000 | 102132000
2025-12-18 03:00 | -1563.04 | 4.8754 | 55.1861 | 59.8258 | -458.0818 |  | 2091 | 7527600 | 39063600 | 70599600 | 102135600
2025-12-19 04:00 | -1489.14 | 4.6363 | 55.1183 | 59.8258 | -436.4239 |  | 2092 | 7531200 | 39067200 | 70603200 | 102139200
2025-12-20 05:00 | -1425.53 | 4.4681 | 55.0949 | 59.8258 | -417.7816 |  | 2093 | 7534800 | 39070800 | 70606800 | 102142800
2025-12-21 06:00 | -1008.64 | 3.2165 | 55.0938 | 59.8258 | -295.6032 |  | 2094 | 7538400 | 39074400 | 70610400 | 102146400
2025-12-22 07:00 | -699.791 | 2.4051 | 55.2191 | 59.8258 | -205.0885 |  | 2095 | 7542000 | 39078000 | 70614000 | 102150000
2025-12-23 08:00 | -367.813 | 1.4839 | 55.4503 | 59.8258 | -107.7953 |  | 2096 | 7545600 | 39081600 | 70617600 | 102153600
2025-12-24 09:00 | -488.896 | 1.9341 | 55.513 | 59.8258 | -143.2813 |  | 2097 | 7549200 | 39085200 | 70621200 | 102157200
2025-12-25 10:00 | 0 | 1 | 56.7059 | 59.8258 | 0 |  | 2098 | 7552800 | 39088800 | 70624800 | 102160800
2025-12-26 11:00 | 2358.19 | 1 | 56.5917 | 59.8258 | 691.1173 |  | 2099 | 7556400 | 39092400 | 70628400 | 102164400
2025-12-27 12:00 | 2989.25 | 1 | 56.8963 | 59.8258 | 876.0627 |  | 2100 | 7560000 | 39096000 | 70632000 | 102168000
2025-12-28 13:00 | 3102.77 | 1 | 57.1801 | 59.8258 | 909.3321 |  | 2101 | 7563600 | 39099600 | 70635600 | 102171600
2025-12-29 14:00 | 3231.58 | 1 | 79.2747 | 59.8258 | 947.0826 |  | 2102 | 7567200 | 39103200 | 70639200 | 102175200
2025-12-30 15:00 | 3234.93 | 1 | 74.1449 | 59.8258 | 948.0644 |  | 2103 | 7570800 | 39106800 | 70642800 | 102178800
2025-12-31 16:00 | 4085.3 | 1.315 | 72.1722 | 59.8258 | 1197.2832 |  | 2104 | 7574400 | 39110400 | 70646400 | 102182400
2026-01-01 17:00 | 4826.24 | 1.535 | 72.5483 | 59.8258 | 1414.4313 |  | 2105 | 7578000 | 39114000 | 70650000 | 102186000
2026-01-02 18:00 | 3917.28 | 1.2471 | 72.7817 | 59.8258 | 1148.0414 |  | 2106 | 7581600 | 39117600 | 70653600 | 102189600
2026-01-03 19:00 | 3091.78 | 1 | 76.1133 | 59.8258 | 906.1113 |  | 2107 | 7585200 | 39121200 | 70657200 | 102193200
2026-01-04 20:00 | 3091.73 | 1 | 83.5181 | 59.8258 | 906.0966 |  | 2108 | 7588800 | 39124800 | 70660800 | 102196800
2026-01-05 21:00 | 0 | 0 | 58.4853 | 59.8258 | 0 |  | 2109 | 7592400 | 39128400 | 70664400 | 102200400
2026-01-06 22:00 | 0 | 0 | 58.1292 | 59.8258 | 0 |  | 2110 | 7596000 | 39132000 | 70668000 | 102204000
2026-01-07 23:00 | -793.805 | 2.8812 | 56.6487 | 59.8258 | -232.6413 |  | 2111 | 7599600 | 39135600 | 70671600 | 102207600
2026-01-09 | -1297.39 | 4.1889 | 56.2916 | 59.8258 | -380.2275 |  | 2112 | 7603200 | 39139200 | 70675200 | 102211200
2026-01-10 01:00 | -1436.55 | 4.4905 | 56.0385 | 59.8258 | -421.0112 |  | 2113 | 7606800 | 39142800 | 70678800 | 102214800
2026-01-11 02:00 | -1445.95 | 4.4988 | 55.8622 | 59.8258 | -423.7661 |  | 2114 | 7610400 | 39146400 | 70682400 | 102218400
2026-01-12 03:00 | -1459.58 | 4.5435 | 55.7885 | 59.8258 | -427.7607 |  | 2115 | 7614000 | 39150000 | 70686000 | 102222000
2026-01-13 04:00 | -1551.84 | 4.8235 | 55.7047 | 59.8258 | -454.7994 |  | 2116 | 7617600 | 39153600 | 70689600 | 102225600
2026-01-14 05:00 | -1360.07 | 4.2194 | 55.616 | 59.8258 | -398.5972 |  | 2117 | 7621200 | 39157200 | 70693200 | 102229200
2026-01-15 06:00 | -917.08 | 2.9438 | 55.6274 | 59.8258 | -268.7696 |  | 2118 | 7624800 | 39160800 | 70696800 | 102232800
2026-01-16 07:00 | -454.778 | 1.6822 | 55.8401 | 59.8258 | -133.2823 |  | 2119 | 7628400 | 39164400 | 70700400 | 102236400
2026-01-17 08:00 | 1772.09 | 1 | 56.9778 | 59.8258 | 519.3483 |  | 2120 | 7632000 | 39168000 | 70704000 | 102240000
2026-01-18 09:00 | 2265.29 | 1 | 57.2829 | 59.8258 | 663.891 |  | 2121 | 7635600 | 39171600 | 70707600 | 102243600
2026-01-19 10:00 | 3218.25 | 1 | 75.6482 | 59.8258 | 943.176 |  | 2122 | 7639200 | 39175200 | 70711200 | 102247200
2026-01-20 11:00 | 5202.58 | 1.601 | 72.8754 | 59.8258 | 1524.7257 |  | 2123 | 7642800 | 39178800 | 70714800 | 102250800
2026-01-21 12:00 | 5990.6 | 1.938 | 72.6148 | 59.8258 | 1755.6716 |  | 2124 | 7646400 | 39182400 | 70718400 | 102254400
2026-01-22 13:00 | 6462.19 | 2.066 | 73.1938 | 59.8258 | 1893.8809 |  | 2125 | 7650000 | 39186000 | 70722000 | 102258000
2026-01-23 14:00 | 7213.13 | 2.3949 | 72.9691 | 59.8258 | 2113.9597 |  | 2126 | 7653600 | 39189600 | 70725600 | 102261600
2026-01-24 15:00 | 7847.42 | 2.5547 | 73.588 | 59.8258 | 2299.8518 |  | 2127 | 7657200 | 39193200 | 70729200 | 102265200
2026-01-25 16:00 | 8437.75 | 2.8105 | 73.614 | 59.8258 | 2472.8604 |  | 2128 | 7660800 | 39196800 | 70732800 | 102268800
2026-01-26 17:00 | 8014.62 | 2.5531 | 74.5597 | 59.8258 | 2348.8533 |  | 2129 | 7664400 | 39200400 | 70736400 | 102272400
2026-01-27 18:00 | 6967.01 | 2.1643 | 75.115 | 59.8258 | 2041.8291 |  | 2130 | 7668000 | 39204000 | 70740000 | 102276000
2026-01-28 19:00 | 4857.21 | 1.4724 | 75.5302 | 59.8258 | 1423.5077 |  | 2131 | 7671600 | 39207600 | 70743600 | 102279600
2026-01-29 20:00 | 3134.94 | 1 | 74.5864 | 59.8258 | 918.7602 |  | 2132 | 7675200 | 39211200 | 70747200 | 102283200
2026-01-30 21:00 | 3097.55 | 1 | 59.679 | 59.8258 | 907.8023 |  | 2133 | 7678800 | 39214800 | 70750800 | 102286800
2026-01-31 22:00 | 119.208 | 1 | 59.8112 | 59.8258 | 34.9364 |  | 2134 | 7682400 | 39218400 | 70754400 | 102290400
2026-02-01 23:00 | -612.186 | 2.3385 | 58.1319 | 59.8258 | -179.414 |  | 2135 | 7686000 | 39222000 | 70758000 | 102294000
2026-02-03 | -1014.68 | 3.3424 | 57.5409 | 59.8258 | -297.3734 |  | 2136 | 7689600 | 39225600 | 70761600 | 102297600
2026-02-04 01:00 | -1348.02 | 4.2424 | 57.2111 | 59.8258 | -395.0657 |  | 2137 | 7693200 | 39229200 | 70765200 | 102301200
2026-02-05 02:00 | -1372.65 | 4.2409 | 56.9521 | 59.8258 | -402.284 |  | 2138 | 7696800 | 39232800 | 70768800 | 102304800
2026-02-06 03:00 | -1300.98 | 4.0389 | 56.7515 | 59.8258 | -381.2796 |  | 2139 | 7700400 | 39236400 | 70772400 | 102308400
2026-02-07 04:00 | -1488.73 | 4.6258 | 56.6304 | 59.8258 | -436.3037 |  | 2140 | 7704000 | 39240000 | 70776000 | 102312000
2026-02-08 05:00 | -1546.17 | 4.7481 | 56.4806 | 59.8258 | -453.1377 |  | 2141 | 7707600 | 39243600 | 70779600 | 102315600
2026-02-09 06:00 | -1417.91 | 4.3584 | 56.3651 | 59.8258 | -415.5484 |  | 2142 | 7711200 | 39247200 | 70783200 | 102319200
2026-02-10 07:00 | -607.332 | 1.981 | 56.3856 | 59.8258 | -177.9914 |  | 2143 | 7714800 | 39250800 | 70786800 | 102322800
2026-02-11 08:00 | 0 | 1 | 57.8401 | 59.8258 | 0 |  | 2144 | 7718400 | 39254400 | 70790400 | 102326400
2026-02-12 09:00 | -195.226 | 1.169 | 57.1474 | 59.8258 | -57.2151 |  | 2145 | 7722000 | 39258000 | 70794000 | 102330000
2026-02-13 10:00 | -139.371 | 0.90706 | 57.2223 | 59.8258 | -40.8456 |  | 2146 | 7725600 | 39261600 | 70797600 | 102333600
2026-02-14 11:00 | -992.867 | 3.4383 | 56.605 | 59.8258 | -290.9806 |  | 2147 | 7729200 | 39265200 | 70801200 | 102337200
2026-02-15 12:00 | -1381.53 | 4.3818 | 56.3622 | 59.8258 | -404.8865 |  | 2148 | 7732800 | 39268800 | 70804800 | 102340800
2026-02-16 13:00 | -1830.44 | 5.6494 | 56.1804 | 59.8258 | -536.449 |  | 2149 | 7736400 | 39272400 | 70808400 | 102344400
2026-02-17 14:00 | -1713.24 | 5.1806 | 55.977 | 59.8258 | -502.1011 |  | 2150 | 7740000 | 39276000 | 70812000 | 102348000
2026-02-18 15:00 | -1645.34 | 5.0302 | 55.8759 | 59.8258 | -482.2016 |  | 2151 | 7743600 | 39279600 | 70815600 | 102351600
2026-02-19 16:00 | -1227.23 | 3.7881 | 55.7828 | 59.8258 | -359.6656 |  | 2152 | 7747200 | 39283200 | 70819200 | 102355200
2026-02-20 17:00 | 314.347 | 1 | 57.202 | 59.8258 | 92.126 |  | 2153 | 7750800 | 39286800 | 70822800 | 102358800
2026-02-21 18:00 | -417.275 | 1.8285 | 56.3485 | 59.8258 | -122.2912 |  | 2154 | 7754400 | 39290400 | 70826400 | 102362400
2026-02-22 19:00 | -1120.91 | 3.774 | 56.0169 | 59.8258 | -328.5063 |  | 2155 | 7758000 | 39294000 | 70830000 | 102366000
2026-02-23 20:00 | -1792.15 | 5.6244 | 55.7961 | 59.8258 | -525.2273 |  | 2156 | 7761600 | 39297600 | 70833600 | 102369600
2026-02-24 21:00 | -2187.45 | 6.108 | 55.4775 | 59.8258 | -641.0783 |  | 2157 | 7765200 | 39301200 | 70837200 | 102373200
2026-02-25 22:00 | -2441.58 | 6.108 | 55.165 | 59.8258 | -715.5565 |  | 2158 | 7768800 | 39304800 | 70840800 | 102376800
2026-02-26 23:00 | -2504.94 | 6.108 | 54.9894 | 59.8258 | -734.1254 |  | 2159 | 7772400 | 39308400 | 70844400 | 102380400
2026-02-28 | -3865.56 | 6.108 | 53.8873 | 59.8258 | -1132.8838 |  | 2160 | 7776000 | 39312000 | 70848000 | 102384000
2026-03-01 01:00 | -4041.74 | 6.108 | 53.5212 | 59.8258 | -1184.5171 |  | 2161 | 7779600 | 39315600 | 70851600 | 102387600
2026-03-02 02:00 | -4113.06 | 6.108 | 53.3046 | 59.8258 | -1205.4189 |  | 2162 | 7783200 | 39319200 | 70855200 | 102391200
2026-03-03 03:00 | -4052.43 | 6.108 | 53.2423 | 59.8258 | -1187.65 |  | 2163 | 7786800 | 39322800 | 70858800 | 102394800
2026-03-04 04:00 | -4214.87 | 6.108 | 53.0332 | 59.8258 | -1235.2565 |  | 2164 | 7790400 | 39326400 | 70862400 | 102398400
2026-03-05 05:00 | -4513.39 | 6.108 | 52.6817 | 59.8258 | -1322.744 |  | 2165 | 7794000 | 39330000 | 70866000 | 102402000
2026-03-06 06:00 | -3494.42 | 6.108 | 53.321 | 59.8258 | -1024.1134 |  | 2166 | 7797600 | 39333600 | 70869600 | 102405600
2026-03-07 07:00 | -2555.82 | 6.108 | 54.0677 | 59.8258 | -749.0369 |  | 2167 | 7801200 | 39337200 | 70873200 | 102409200
2026-03-08 08:00 | -2338.06 | 6.108 | 54.3521 | 59.8258 | -685.2177 |  | 2168 | 7804800 | 39340800 | 70876800 | 102412800
2026-03-09 09:00 | -1065.51 | 3.2486 | 54.6634 | 59.8258 | -312.2702 |  | 2169 | 7808400 | 39344400 | 70880400 | 102416400
2026-03-10 10:00 | 2036.62 | 1 | 56.1867 | 59.8258 | 596.8744 |  | 2170 | 7812000 | 39348000 | 70884000 | 102420000
2026-03-11 11:00 | 2946.73 | 1 | 74.3349 | 59.8258 | 863.6013 |  | 2171 | 7815600 | 39351600 | 70887600 | 102423600
2026-03-12 12:00 | 3892.72 | 1.3141 | 70.8857 | 59.8258 | 1140.8436 |  | 2172 | 7819200 | 39355200 | 70891200 | 102427200
2026-03-13 13:00 | 4123.23 | 1.3617 | 71.5823 | 59.8258 | 1208.3994 |  | 2173 | 7822800 | 39358800 | 70894800 | 102430800
2026-03-14 14:00 | 5332.6 | 1.7665 | 71.8597 | 59.8258 | 1562.8308 |  | 2174 | 7826400 | 39362400 | 70898400 | 102434400
2026-03-15 15:00 | 4657.56 | 1.5353 | 72.3447 | 59.8258 | 1364.9961 |  | 2175 | 7830000 | 39366000 | 70902000 | 102438000
2026-03-16 16:00 | 6902.92 | 2.3213 | 72.2324 | 59.8258 | 2023.0462 |  | 2176 | 7833600 | 39369600 | 70905600 | 102441600
2026-03-17 17:00 | 5729.19 | 1.7746 | 73.8551 | 59.8258 | 1679.0598 |  | 2177 | 7837200 | 39373200 | 70909200 | 102445200
2026-03-18 18:00 | 3958.01 | 1.2283 | 73.994 | 59.8258 | 1159.9782 |  | 2178 | 7840800 | 39376800 | 70912800 | 102448800
2026-03-19 19:00 | 3168.79 | 1 | 83.4401 | 59.8258 | 928.6807 |  | 2179 | 7844400 | 39380400 | 70916400 | 102452400
2026-03-20 20:00 | 3136.76 | 1 | 58.7987 | 59.8258 | 919.2936 |  | 2180 | 7848000 | 39384000 | 70920000 | 102456000
2026-03-21 21:00 | 0 | 0 | 59.1164 | 59.8258 | 0 |  | 2181 | 7851600 | 39387600 | 70923600 | 102459600
2026-03-22 22:00 | -345.6 | 1.5555 | 57.649 | 59.8258 | -101.2854 |  | 2182 | 7855200 | 39391200 | 70927200 | 102463200
2026-03-23 23:00 | -1590.96 | 5.1414 | 56.9585 | 59.8258 | -466.2643 |  | 2183 | 7858800 | 39394800 | 70930800 | 102466800
2026-03-25 | -2184.16 | 6.108 | 56.4423 | 59.8258 | -640.1141 |  | 2184 | 7862400 | 39398400 | 70934400 | 102470400
2026-03-26 01:00 | -2642.08 | 6.108 | 55.8211 | 59.8258 | -774.3172 |  | 2185 | 7866000 | 39402000 | 70938000 | 102474000
2026-03-27 02:00 | -2817.33 | 6.108 | 55.4132 | 59.8258 | -825.6779 |  | 2186 | 7869600 | 39405600 | 70941600 | 102477600
2026-03-28 03:00 | -2679.84 | 6.108 | 55.3411 | 59.8258 | -785.3836 |  | 2187 | 7873200 | 39409200 | 70945200 | 102481200
2026-03-29 04:00 | -2985.92 | 6.108 | 54.9652 | 59.8258 | -875.0868 |  | 2188 | 7876800 | 39412800 | 70948800 | 102484800
2026-03-30 05:00 | -2467.85 | 6.108 | 55.2064 | 59.8258 | -723.2554 |  | 2189 | 7880400 | 39416400 | 70952400 | 102488400
2026-03-31 06:00 | -2399.49 | 6.108 | 55.2219 | 59.8258 | -703.2211 |  | 2190 | 7884000 | 39420000 | 70956000 | 102492000
2026-04-01 07:00 | -1758.15 | 5.3257 | 55.472 | 59.8258 | -515.2629 |  | 2191 | 7887600 | 39423600 | 70959600 | 102495600
2026-04-02 08:00 | -1486.31 | 4.5557 | 55.5191 | 59.8258 | -435.5945 |  | 2192 | 7891200 | 39427200 | 70963200 | 102499200
2026-04-03 09:00 | -345.045 | 1.1933 | 55.739 | 59.8258 | -101.1227 |  | 2193 | 7894800 | 39430800 | 70966800 | 102502800
2026-04-04 10:00 | 2407.59 | 1 | 57.0209 | 59.8258 | 705.595 |  | 2194 | 7898400 | 39434400 | 70970400 | 102506400
2026-04-05 11:00 | 3145.3 | 1 | 75.7341 | 59.8258 | 921.7964 |  | 2195 | 7902000 | 39438000 | 70974000 | 102510000
2026-04-06 12:00 | 2968.45 | 1 | 57.7891 | 59.8258 | 869.9668 |  | 2196 | 7905600 | 39441600 | 70977600 | 102513600
2026-04-07 13:00 | 3572.47 | 1.1542 | 72.4564 | 59.8258 | 1046.9876 |  | 2197 | 7909200 | 39445200 | 70981200 | 102517200
2026-04-08 14:00 | 4568.05 | 1.4876 | 72.5406 | 59.8258 | 1338.7633 |  | 2198 | 7912800 | 39448800 | 70984800 | 102520800
2026-04-09 15:00 | 5776.15 | 1.9813 | 72.1565 | 59.8258 | 1692.8225 |  | 2199 | 7916400 | 39452400 | 70988400 | 102524400
2026-04-10 16:00 | 5511.96 | 1.9725 | 71.9527 | 59.8258 | 1615.396 |  | 2200 | 7920000 | 39456000 | 70992000 | 102528000
2026-04-11 17:00 | 4808.09 | 1.6375 | 72.7919 | 59.8258 | 1409.1121 |  | 2201 | 7923600 | 39459600 | 70995600 | 102531600
2026-04-12 18:00 | 2876.65 | 1 | 74.9391 | 59.8258 | 843.0629 |  | 2202 | 7927200 | 39463200 | 70999200 | 102535200
2026-04-13 19:00 | 2785.09 | 1 | 59.0514 | 59.8258 | 816.2293 |  | 2203 | 7930800 | 39466800 | 71002800 | 102538800
2026-04-14 20:00 | -796.357 | 2.8598 | 57.9814 | 59.8258 | -233.3892 |  | 2204 | 7934400 | 39470400 | 71006400 | 102542400
2026-04-15 21:00 | -1763.25 | 5.5142 | 57.3132 | 59.8258 | -516.7576 |  | 2205 | 7938000 | 39474000 | 71010000 | 102546000
2026-04-16 22:00 | -3313.47 | 6.108 | 55.8657 | 59.8258 | -971.0822 |  | 2206 | 7941600 | 39477600 | 71013600 | 102549600
2026-04-17 23:00 | -3940.48 | 6.108 | 54.9478 | 59.8258 | -1154.8407 |  | 2207 | 7945200 | 39481200 | 71017200 | 102553200
2026-04-19 | -4586.3 | 6.108 | 54.1073 | 59.8258 | -1344.1118 |  | 2208 | 7948800 | 39484800 | 71020800 | 102556800
2026-04-20 01:00 | -4770.79 | 6.108 | 53.612 | 59.8258 | -1398.1805 |  | 2209 | 7952400 | 39488400 | 71024400 | 102560400
2026-04-21 02:00 | -5024.59 | 6.108 | 53.1703 | 59.8258 | -1472.562 |  | 2210 | 7956000 | 39492000 | 71028000 | 102564000
2026-04-22 03:00 | -4988.45 | 6.108 | 52.9514 | 59.8258 | -1461.9704 |  | 2211 | 7959600 | 39495600 | 71031600 | 102567600
2026-04-23 04:00 | -4952.55 | 6.108 | 52.7994 | 59.8258 | -1451.4491 |  | 2212 | 7963200 | 39499200 | 71035200 | 102571200
2026-04-24 05:00 | -4674.31 | 6.108 | 52.8609 | 59.8258 | -1369.905 |  | 2213 | 7966800 | 39502800 | 71038800 | 102574800
2026-04-25 06:00 | -4694.02 | 6.108 | 52.7667 | 59.8258 | -1375.6815 |  | 2214 | 7970400 | 39506400 | 71042400 | 102578400
2026-04-26 07:00 | -4712.37 | 6.108 | 52.6504 | 59.8258 | -1381.0593 |  | 2215 | 7974000 | 39510000 | 71046000 | 102582000
2026-04-27 08:00 | -5257.79 | 6.108 | 52.1672 | 59.8258 | -1540.9061 |  | 2216 | 7977600 | 39513600 | 71049600 | 102585600
2026-04-28 09:00 | -4626.33 | 6.108 | 52.4909 | 59.8258 | -1355.8435 |  | 2217 | 7981200 | 39517200 | 71053200 | 102589200
2026-04-29 10:00 | -3922.7 | 6.108 | 52.9772 | 59.8258 | -1149.6299 |  | 2218 | 7984800 | 39520800 | 71056800 | 102592800
2026-04-30 11:00 | -3631.4 | 6.108 | 53.2222 | 59.8258 | -1064.2583 |  | 2219 | 7988400 | 39524400 | 71060400 | 102596400
2026-05-01 12:00 | -3300.25 | 6.108 | 53.478 | 59.8258 | -967.2078 |  | 2220 | 7992000 | 39528000 | 71064000 | 102600000
2026-05-02 13:00 | -3121.71 | 6.108 | 53.6213 | 59.8258 | -914.8829 |  | 2221 | 7995600 | 39531600 | 71067600 | 102603600
2026-05-03 14:00 | -2725.33 | 6.108 | 53.928 | 59.8258 | -798.7154 |  | 2222 | 7999200 | 39535200 | 71071200 | 102607200
2026-05-04 15:00 | -1882.39 | 5.8046 | 54.5063 | 59.8258 | -551.6741 |  | 2223 | 8002800 | 39538800 | 71074800 | 102610800
2026-05-05 16:00 | -1662.42 | 5.1061 | 54.5843 | 59.8258 | -487.2072 |  | 2224 | 8006400 | 39542400 | 71078400 | 102614400
2026-05-06 17:00 | -1720.6 | 5.3543 | 54.6562 | 59.8258 | -504.2581 |  | 2225 | 8010000 | 39546000 | 71082000 | 102618000
2026-05-07 18:00 | -2412.66 | 6.108 | 54.3341 | 59.8258 | -707.0808 |  | 2226 | 8013600 | 39549600 | 71085600 | 102621600
2026-05-08 19:00 | -2768.59 | 6.108 | 53.987 | 59.8258 | -811.3936 |  | 2227 | 8017200 | 39553200 | 71089200 | 102625200
2026-05-09 20:00 | -4136.06 | 6.108 | 52.8958 | 59.8258 | -1212.1595 |  | 2228 | 8020800 | 39556800 | 71092800 | 102628800
2026-05-10 21:00 | -4740.38 | 6.108 | 52.2219 | 59.8258 | -1389.2682 |  | 2229 | 8024400 | 39560400 | 71096400 | 102632400
2026-05-11 22:00 | -5654.29 | 6.108 | 51.3255 | 59.8258 | -1657.1088 |  | 2230 | 8028000 | 39564000 | 71100000 | 102636000
2026-05-12 23:00 | -6056.7 | 6.108 | 50.7756 | 59.8258 | -1775.0435 |  | 2231 | 8031600 | 39567600 | 71103600 | 102639600
2026-05-14 | -6363.25 | 6.108 | 50.3348 | 59.8258 | -1864.8845 |  | 2232 | 8035200 | 39571200 | 71107200 | 102643200
2026-05-15 01:00 | -6477.2 | 6.108 | 50.0608 | 59.8258 | -1898.2799 |  | 2233 | 8038800 | 39574800 | 71110800 | 102646800
2026-05-16 02:00 | -6559.71 | 6.108 | 49.8554 | 59.8258 | -1922.4612 |  | 2234 | 8042400 | 39578400 | 71114400 | 102650400
2026-05-17 03:00 | -6383.91 | 6.108 | 49.8537 | 59.8258 | -1870.9393 |  | 2235 | 8046000 | 39582000 | 71118000 | 102654000
2026-05-18 04:00 | -6337.01 | 6.108 | 49.8077 | 59.8258 | -1857.1943 |  | 2236 | 8049600 | 39585600 | 71121600 | 102657600
2026-05-19 05:00 | -5983.62 | 6.108 | 49.9977 | 59.8258 | -1753.6259 |  | 2237 | 8053200 | 39589200 | 71125200 | 102661200
2026-05-20 06:00 | -6080.9 | 6.108 | 49.9033 | 59.8258 | -1782.1359 |  | 2238 | 8056800 | 39592800 | 71128800 | 102664800
2026-05-21 07:00 | -5557.18 | 6.108 | 50.2423 | 59.8258 | -1628.6487 |  | 2239 | 8060400 | 39596400 | 71132400 | 102668400
2026-05-22 08:00 | -4870.34 | 6.108 | 50.7863 | 59.8258 | -1427.3558 |  | 2240 | 8064000 | 39600000 | 71136000 | 102672000
2026-05-23 09:00 | -3393.15 | 6.108 | 51.9858 | 59.8258 | -994.4341 |  | 2241 | 8067600 | 39603600 | 71139600 | 102675600
2026-05-24 10:00 | -2306.87 | 6.108 | 53.0325 | 59.8258 | -676.0769 |  | 2242 | 8071200 | 39607200 | 71143200 | 102679200
2026-05-25 11:00 | -686.783 | 2.1204 | 53.5376 | 59.8258 | -201.2762 |  | 2243 | 8074800 | 39610800 | 71146800 | 102682800
2026-05-26 12:00 | 2406.02 | 1 | 55.1908 | 59.8258 | 705.1349 |  | 2244 | 8078400 | 39614400 | 71150400 | 102686400
2026-05-27 13:00 | 2927.35 | 1 | 55.8018 | 59.8258 | 857.9216 |  | 2245 | 8082000 | 39618000 | 71154000 | 102690000
2026-05-28 14:00 | 2953.94 | 1 | 78.5979 | 59.8258 | 865.7144 |  | 2246 | 8085600 | 39621600 | 71157600 | 102693600
2026-05-29 15:00 | 3401.05 | 1.1629 | 70.1972 | 59.8258 | 996.7494 |  | 2247 | 8089200 | 39625200 | 71161200 | 102697200
2026-05-30 16:00 | 3170.13 | 1.0716 | 70.6884 | 59.8258 | 929.0734 |  | 2248 | 8092800 | 39628800 | 71164800 | 102700800
2026-05-31 17:00 | 2933.66 | 1 | 75.3775 | 59.8258 | 859.7709 |  | 2249 | 8096400 | 39632400 | 71168400 | 102704400
2026-06-01 18:00 | 2783.7 | 1 | 57.2387 | 59.8258 | 815.8219 |  | 2250 | 8100000 | 39636000 | 71172000 | 102708000
2026-06-02 19:00 | -337.109 | 1.5798 | 56.6248 | 59.8258 | -98.7969 |  | 2251 | 8103600 | 39639600 | 71175600 | 102711600
2026-06-03 20:00 | -1564.21 | 5.1313 | 55.9226 | 59.8258 | -458.4247 |  | 2252 | 8107200 | 39643200 | 71179200 | 102715200
2026-06-04 21:00 | -2436.8 | 6.108 | 55.2018 | 59.8258 | -714.1556 |  | 2253 | 8110800 | 39646800 | 71182800 | 102718800
2026-06-05 22:00 | -3634.91 | 6.108 | 54.074 | 59.8258 | -1065.287 |  | 2254 | 8114400 | 39650400 | 71186400 | 102722400
2026-06-06 23:00 | -3995.88 | 6.108 | 53.4924 | 59.8258 | -1171.0768 |  | 2255 | 8118000 | 39654000 | 71190000 | 102726000
2026-06-08 | -4321.56 | 6.108 | 52.9607 | 59.8258 | -1266.5242 |  | 2256 | 8121600 | 39657600 | 71193600 | 102729600
2026-06-09 01:00 | -4368.29 | 6.108 | 52.7225 | 59.8258 | -1280.2194 |  | 2257 | 8125200 | 39661200 | 71197200 | 102733200
2026-06-10 02:00 | -4412.79 | 6.108 | 52.5399 | 59.8258 | -1293.2611 |  | 2258 | 8128800 | 39664800 | 71200800 | 102736800
2026-06-11 03:00 | -4409.33 | 6.108 | 52.4146 | 59.8258 | -1292.2471 |  | 2259 | 8132400 | 39668400 | 71204400 | 102740400
2026-06-12 04:00 | -4578.41 | 6.108 | 52.1944 | 59.8258 | -1341.7995 |  | 2260 | 8136000 | 39672000 | 71208000 | 102744000
2026-06-13 05:00 | -4230.3 | 6.108 | 52.3484 | 59.8258 | -1239.7785 |  | 2261 | 8139600 | 39675600 | 71211600 | 102747600
2026-06-14 06:00 | -4399.79 | 6.108 | 52.1796 | 59.8258 | -1289.4512 |  | 2262 | 8143200 | 39679200 | 71215200 | 102751200
2026-06-15 07:00 | -3499.06 | 6.108 | 52.8075 | 59.8258 | -1025.4733 |  | 2263 | 8146800 | 39682800 | 71218800 | 102754800
2026-06-16 08:00 | -2728.19 | 6.108 | 53.4708 | 59.8258 | -799.5536 |  | 2264 | 8150400 | 39686400 | 71222400 | 102758400
2026-06-17 09:00 | -1223.63 | 3.7744 | 54.1705 | 59.8258 | -358.6106 |  | 2265 | 8154000 | 39690000 | 71226000 | 102762000
2026-06-18 10:00 | 553.49 | 1 | 55.8862 | 59.8258 | 162.2119 |  | 2266 | 8157600 | 39693600 | 71229600 | 102765600
2026-06-19 11:00 | 3079.85 | 1 | 76.4833 | 59.8258 | 902.6149 |  | 2267 | 8161200 | 39697200 | 71233200 | 102769200
2026-06-20 12:00 | 4247.85 | 1.3289 | 71.4986 | 59.8258 | 1244.9219 |  | 2268 | 8164800 | 39700800 | 71236800 | 102772800
2026-06-21 13:00 | 4585.25 | 1.5539 | 70.8852 | 59.8258 | 1343.8041 |  | 2269 | 8168400 | 39704400 | 71240400 | 102776400
2026-06-22 14:00 | 5198.03 | 1.7234 | 71.5553 | 59.8258 | 1523.3922 |  | 2270 | 8172000 | 39708000 | 71244000 | 102780000
2026-06-23 15:00 | 6056.54 | 2.0128 | 71.8755 | 59.8258 | 1774.9967 |  | 2271 | 8175600 | 39711600 | 71247600 | 102783600
2026-06-24 16:00 | 5874.14 | 1.9749 | 72.1053 | 59.8258 | 1721.5405 |  | 2272 | 8179200 | 39715200 | 71251200 | 102787200
2026-06-25 17:00 | 5131.75 | 1.6902 | 72.6266 | 59.8258 | 1503.9675 |  | 2273 | 8182800 | 39718800 | 71254800 | 102790800
2026-06-26 18:00 | 3176.28 | 1 | 73.5831 | 59.8258 | 930.8758 |  | 2274 | 8186400 | 39722400 | 71258400 | 102794400
2026-06-27 19:00 | 2958.1 | 1 | 58.4539 | 59.8258 | 866.9335 |  | 2275 | 8190000 | 39726000 | 71262000 | 102798000
2026-06-28 20:00 | 0 | 0 | 58.6971 | 59.8258 | 0 |  | 2276 | 8193600 | 39729600 | 71265600 | 102801600
2026-06-29 21:00 | -519.126 | 1.9791 | 57.1203 | 59.8258 | -152.1408 |  | 2277 | 8197200 | 39733200 | 71269200 | 102805200
2026-06-30 22:00 | -1565.65 | 5.0529 | 56.6325 | 59.8258 | -458.8467 |  | 2278 | 8200800 | 39736800 | 71272800 | 102808800
2026-07-01 23:00 | -2018.6 | 6.108 | 56.2479 | 59.8258 | -591.5933 |  | 2279 | 8204400 | 39740400 | 71276400 | 102812400
2026-07-03 | -2278.52 | 6.108 | 55.8124 | 59.8258 | -667.7683 |  | 2280 | 8208000 | 39744000 | 71280000 | 102816000
2026-07-04 01:00 | -2755.76 | 6.108 | 55.243 | 59.8258 | -807.6335 |  | 2281 | 8211600 | 39747600 | 71283600 | 102819600
2026-07-05 02:00 | -2970.85 | 6.108 | 54.8962 | 59.8258 | -870.6702 |  | 2282 | 8215200 | 39751200 | 71287200 | 102823200
2026-07-06 03:00 | -3134.69 | 6.108 | 54.596 | 59.8258 | -918.687 |  | 2283 | 8218800 | 39754800 | 71290800 | 102826800
2026-07-07 04:00 | -3327.82 | 6.108 | 54.3073 | 59.8258 | -975.2878 |  | 2284 | 8222400 | 39758400 | 71294400 | 102830400
2026-07-08 05:00 | -3024.86 | 6.108 | 54.3955 | 59.8258 | -886.499 |  | 2285 | 8226000 | 39762000 | 71298000 | 102834000
2026-07-09 06:00 | -3307.74 | 6.108 | 54.1321 | 59.8258 | -969.4029 |  | 2286 | 8229600 | 39765600 | 71301600 | 102837600
2026-07-10 07:00 | -3307.41 | 6.108 | 54.0366 | 59.8258 | -969.3062 |  | 2287 | 8233200 | 39769200 | 71305200 | 102841200
2026-07-11 08:00 | -3982.42 | 6.108 | 53.4723 | 59.8258 | -1167.1321 |  | 2288 | 8236800 | 39772800 | 71308800 | 102844800
2026-07-12 09:00 | -3768.08 | 6.108 | 53.4863 | 59.8258 | -1104.3152 |  | 2289 | 8240400 | 39776400 | 71312400 | 102848400
2026-07-13 10:00 | -3320.91 | 6.108 | 53.7416 | 59.8258 | -973.2626 |  | 2290 | 8244000 | 39780000 | 71316000 | 102852000
2026-07-14 11:00 | -3025.52 | 6.108 | 53.9319 | 59.8258 | -886.6924 |  | 2291 | 8247600 | 39783600 | 71319600 | 102855600
2026-07-15 12:00 | -2868.2 | 6.108 | 54.0194 | 59.8258 | -840.5864 |  | 2292 | 8251200 | 39787200 | 71323200 | 102859200
2026-07-16 13:00 | -3162.63 | 6.108 | 53.7587 | 59.8258 | -926.8754 |  | 2293 | 8254800 | 39790800 | 71326800 | 102862800
2026-07-17 14:00 | -2776.35 | 6.108 | 53.9611 | 59.8258 | -813.6679 |  | 2294 | 8258400 | 39794400 | 71330400 | 102866400
2026-07-18 15:00 | -2156.74 | 6.108 | 54.3921 | 59.8258 | -632.0781 |  | 2295 | 8262000 | 39798000 | 71334000 | 102870000
2026-07-19 16:00 | -2070.27 | 6.108 | 54.4898 | 59.8258 | -606.7362 |  | 2296 | 8265600 | 39801600 | 71337600 | 102873600
2026-07-20 17:00 | -2318.59 | 6.108 | 54.295 | 59.8258 | -679.5117 |  | 2297 | 8269200 | 39805200 | 71341200 | 102877200
2026-07-21 18:00 | -3267.71 | 6.108 | 53.5298 | 59.8258 | -957.6713 |  | 2298 | 8272800 | 39808800 | 71344800 | 102880800
2026-07-22 19:00 | -3770.21 | 6.108 | 52.9977 | 59.8258 | -1104.9395 |  | 2299 | 8276400 | 39812400 | 71348400 | 102884400
2026-07-23 20:00 | -4957.58 | 6.108 | 51.9706 | 59.8258 | -1452.9233 |  | 2300 | 8280000 | 39816000 | 71352000 | 102888000
2026-07-24 21:00 | -5386.68 | 6.108 | 51.4026 | 59.8258 | -1578.6801 |  | 2301 | 8283600 | 39819600 | 71355600 | 102891600
2026-07-25 22:00 | -6228.66 | 6.108 | 50.5564 | 59.8258 | -1825.4401 |  | 2302 | 8287200 | 39823200 | 71359200 | 102895200
2026-07-26 23:00 | -7091.92 | 6.108 | 49.651 | 59.8258 | -2078.4366 |  | 2303 | 8290800 | 39826800 | 71362800 | 102898800
2026-07-28 | -7423.66 | 6.108 | 49.1124 | 59.8258 | -2175.66 |  | 2304 | 8294400 | 39830400 | 71366400 | 102902400
2026-07-29 01:00 | -7815.34 | 6.108 | 48.5806 | 59.8258 | -2290.4501 |  | 2305 | 8298000 | 39834000 | 71370000 | 102906000
2026-07-30 02:00 | -7708.6 | 6.108 | 48.4426 | 59.8258 | -2259.1677 |  | 2306 | 8301600 | 39837600 | 71373600 | 102909600
2026-07-31 03:00 | -8139.87 | 6.108 | 47.9533 | 59.8258 | -2385.5604 |  | 2307 | 8305200 | 39841200 | 71377200 | 102913200
2026-08-01 04:00 | -8173.1 | 6.108 | 47.7301 | 59.8258 | -2395.2992 |  | 2308 | 8308800 | 39844800 | 71380800 | 102916800
2026-08-02 05:00 | -8571.28 | 6.108 | 47.269 | 59.8258 | -2511.9942 |  | 2309 | 8312400 | 39848400 | 71384400 | 102920400
2026-08-03 06:00 | -7653.51 | 6.108 | 47.7787 | 59.8258 | -2243.0224 |  | 2310 | 8316000 | 39852000 | 71388000 | 102924000
2026-08-04 07:00 | -7193.63 | 6.108 | 48.1083 | 59.8258 | -2108.2448 |  | 2311 | 8319600 | 39855600 | 71391600 | 102927600
2026-08-05 08:00 | -6489.71 | 6.108 | 48.6563 | 59.8258 | -1901.9463 |  | 2312 | 8323200 | 39859200 | 71395200 | 102931200
2026-08-06 09:00 | -5135.94 | 6.108 | 49.7392 | 59.8258 | -1505.1954 |  | 2313 | 8326800 | 39862800 | 71398800 | 102934800
2026-08-07 10:00 | -3644.8 | 6.108 | 51.0551 | 59.8258 | -1068.1854 |  | 2314 | 8330400 | 39866400 | 71402400 | 102938400
2026-08-08 11:00 | -2248.82 | 6.108 | 52.4089 | 59.8258 | -659.0641 |  | 2315 | 8334000 | 39870000 | 71406000 | 102942000
2026-08-09 12:00 | -1285.73 | 4.0156 | 52.9685 | 59.8258 | -376.8103 |  | 2316 | 8337600 | 39873600 | 71409600 | 102945600
2026-08-10 13:00 | -800.521 | 2.6904 | 53.4079 | 59.8258 | -234.6095 |  | 2317 | 8341200 | 39877200 | 71413200 | 102949200
2026-08-11 14:00 | 0 | 0 | 55.0526 | 59.8258 | 0 |  | 2318 | 8344800 | 39880800 | 71416800 | 102952800
2026-08-12 15:00 | 2644.55 | 1 | 55.1146 | 59.8258 | 775.0411 |  | 2319 | 8348400 | 39884400 | 71420400 | 102956400
2026-08-13 16:00 | 2942.13 | 1 | 78.967 | 59.8258 | 862.2532 |  | 2320 | 8352000 | 39888000 | 71424000 | 102960000
2026-08-14 17:00 | 2727.68 | 1 | 56.0523 | 59.8258 | 799.4041 |  | 2321 | 8355600 | 39891600 | 71427600 | 102963600
2026-08-15 18:00 | -709.12 | 2.7026 | 55.3394 | 59.8258 | -207.8226 |  | 2322 | 8359200 | 39895200 | 71431200 | 102967200
2026-08-16 19:00 | -1987.63 | 6.108 | 54.817 | 59.8258 | -582.5169 |  | 2323 | 8362800 | 39898800 | 71434800 | 102970800
2026-08-17 20:00 | -2951.18 | 6.108 | 53.8774 | 59.8258 | -864.9055 |  | 2324 | 8366400 | 39902400 | 71438400 | 102974400
2026-08-18 21:00 | -3617.9 | 6.108 | 53.1483 | 59.8258 | -1060.3018 |  | 2325 | 8370000 | 39906000 | 71442000 | 102978000
2026-08-19 22:00 | -4260.59 | 6.108 | 52.4322 | 59.8258 | -1248.6557 |  | 2326 | 8373600 | 39909600 | 71445600 | 102981600
2026-08-20 23:00 | -6298.73 | 6.108 | 50.6492 | 59.8258 | -1845.9755 |  | 2327 | 8377200 | 39913200 | 71449200 | 102985200
2026-08-22 | -6908.92 | 6.108 | 49.7854 | 59.8258 | -2024.8046 |  | 2328 | 8380800 | 39916800 | 71452800 | 102988800
2026-08-23 01:00 | -7492.91 | 6.108 | 49.0254 | 59.8258 | -2195.9552 |  | 2329 | 8384400 | 39920400 | 71456400 | 102992400
2026-08-24 02:00 | -7899.09 | 6.108 | 48.4368 | 59.8258 | -2314.9948 |  | 2330 | 8388000 | 39924000 | 71460000 | 102996000
2026-08-25 03:00 | -8216.87 | 6.108 | 47.9011 | 59.8258 | -2408.1269 |  | 2331 | 8391600 | 39927600 | 71463600 | 102999600
2026-08-26 04:00 | -8459.84 | 6.108 | 47.4335 | 59.8258 | -2479.3344 |  | 2332 | 8395200 | 39931200 | 71467200 | 103003200
2026-08-27 05:00 | -8517.31 | 6.108 | 47.1542 | 59.8258 | -2496.1772 |  | 2333 | 8398800 | 39934800 | 71470800 | 103006800
2026-08-28 06:00 | -7693 | 6.108 | 47.6041 | 59.8258 | -2254.5957 |  | 2334 | 8402400 | 39938400 | 71474400 | 103010400
2026-08-29 07:00 | -6418.52 | 6.108 | 48.5426 | 59.8258 | -1881.0825 |  | 2335 | 8406000 | 39942000 | 71478000 | 103014000
2026-08-30 08:00 | -5717.09 | 6.108 | 49.1965 | 59.8258 | -1675.5137 |  | 2336 | 8409600 | 39945600 | 71481600 | 103017600
2026-08-31 09:00 | -4450.66 | 6.108 | 50.2728 | 59.8258 | -1304.3597 |  | 2337 | 8413200 | 39949200 | 71485200 | 103021200
2026-09-01 10:00 | -2759.19 | 6.108 | 51.7584 | 59.8258 | -808.6388 |  | 2338 | 8416800 | 39952800 | 71488800 | 103024800
2026-09-02 11:00 | -1496.71 | 4.7224 | 52.7386 | 59.8258 | -438.6424 |  | 2339 | 8420400 | 39956400 | 71492400 | 103028400
2026-09-03 12:00 | -638.978 | 2.1214 | 53.1815 | 59.8258 | -187.266 |  | 2340 | 8424000 | 39960000 | 71496000 | 103032000
2026-09-04 13:00 | 222.941 | 1 | 54.8827 | 59.8258 | 65.3376 |  | 2341 | 8427600 | 39963600 | 71499600 | 103035600
2026-09-05 14:00 | 2920.69 | 1 | 54.9911 | 59.8258 | 855.9697 |  | 2342 | 8431200 | 39967200 | 71503200 | 103039200
2026-09-06 15:00 | 2913.67 | 1 | 55.5841 | 59.8258 | 853.9124 |  | 2343 | 8434800 | 39970800 | 71506800 | 103042800
2026-09-07 16:00 | 3122.34 | 1.0648 | 69.6748 | 59.8258 | 915.0675 |  | 2344 | 8438400 | 39974400 | 71510400 | 103046400
2026-09-08 17:00 | 2856.55 | 1 | 56.2319 | 59.8258 | 837.1722 |  | 2345 | 8442000 | 39978000 | 71514000 | 103050000
2026-09-09 18:00 | 0 | 0 | 56.7159 | 59.8258 | 0 |  | 2346 | 8445600 | 39981600 | 71517600 | 103053600
2026-09-10 19:00 | -991.927 | 3.4123 | 55.2057 | 59.8258 | -290.7051 |  | 2347 | 8449200 | 39985200 | 71521200 | 103057200
2026-09-11 20:00 | -1657.68 | 5.3163 | 54.912 | 59.8258 | -485.8181 |  | 2348 | 8452800 | 39988800 | 71524800 | 103060800
2026-09-12 21:00 | -2226.45 | 6.108 | 54.529 | 59.8258 | -652.5081 |  | 2349 | 8456400 | 39992400 | 71528400 | 103064400
2026-09-13 22:00 | -3239.82 | 6.108 | 53.605 | 59.8258 | -949.4975 |  | 2350 | 8460000 | 39996000 | 71532000 | 103068000
2026-09-14 23:00 | -4627.87 | 6.108 | 52.3224 | 59.8258 | -1356.2948 |  | 2351 | 8463600 | 39999600 | 71535600 | 103071600
2026-09-16 | -5330.31 | 6.108 | 51.5013 | 59.8258 | -1562.1597 |  | 2352 | 8467200 | 40003200 | 71539200 | 103075200
2026-09-17 01:00 | -5851.19 | 6.108 | 50.8519 | 59.8258 | -1714.8145 |  | 2353 | 8470800 | 40006800 | 71542800 | 103078800
2026-09-18 02:00 | -5941.69 | 6.108 | 50.5288 | 59.8258 | -1741.3374 |  | 2354 | 8474400 | 40010400 | 71546400 | 103082400
2026-09-19 03:00 | -6128.55 | 6.108 | 50.1915 | 59.8258 | -1796.1007 |  | 2355 | 8478000 | 40014000 | 71550000 | 103086000
2026-09-20 04:00 | -6130.38 | 6.108 | 50.0131 | 59.8258 | -1796.637 |  | 2356 | 8481600 | 40017600 | 71553600 | 103089600
2026-09-21 05:00 | -5942.73 | 6.108 | 50.0267 | 59.8258 | -1741.6422 |  | 2357 | 8485200 | 40021200 | 71557200 | 103093200
2026-09-22 06:00 | -5876.31 | 6.108 | 50.0227 | 59.8258 | -1722.1765 |  | 2358 | 8488800 | 40024800 | 71560800 | 103096800
2026-09-23 07:00 | -5092.47 | 6.108 | 50.5678 | 59.8258 | -1492.4556 |  | 2359 | 8492400 | 40028400 | 71564400 | 103100400
2026-09-24 08:00 | -4389.97 | 6.108 | 51.1515 | 59.8258 | -1286.5732 |  | 2360 | 8496000 | 40032000 | 71568000 | 103104000
2026-09-25 09:00 | -2448.86 | 6.108 | 52.71 | 59.8258 | -717.69 |  | 2361 | 8499600 | 40035600 | 71571600 | 103107600
2026-09-26 10:00 | -819.861 | 2.5431 | 53.3584 | 59.8258 | -240.2775 |  | 2362 | 8503200 | 40039200 | 71575200 | 103111200
2026-09-27 11:00 | 2765.13 | 1 | 54.9751 | 59.8258 | 810.3796 |  | 2363 | 8506800 | 40042800 | 71578800 | 103114800
2026-09-28 12:00 | 3021.42 | 1 | 72.7142 | 59.8258 | 885.4908 |  | 2364 | 8510400 | 40046400 | 71582400 | 103118400
2026-09-29 13:00 | 4188.25 | 1.3398 | 70.6714 | 59.8258 | 1227.4549 |  | 2365 | 8514000 | 40050000 | 71586000 | 103122000
2026-09-30 14:00 | 5665.01 | 1.8003 | 71.2125 | 59.8258 | 1660.2505 |  | 2366 | 8517600 | 40053600 | 71589600 | 103125600
2026-10-01 15:00 | 7061.58 | 2.3062 | 71.3407 | 59.8258 | 2069.5448 |  | 2367 | 8521200 | 40057200 | 71593200 | 103129200
2026-10-02 16:00 | 6638.33 | 2.1974 | 71.7056 | 59.8258 | 1945.5025 |  | 2368 | 8524800 | 40060800 | 71596800 | 103132800
2026-10-03 17:00 | 5636.83 | 1.8858 | 71.8458 | 59.8258 | 1651.9918 |  | 2369 | 8528400 | 40064400 | 71600400 | 103136400
2026-10-04 18:00 | 3462.91 | 1.1642 | 71.9339 | 59.8258 | 1014.8787 |  | 2370 | 8532000 | 40068000 | 71604000 | 103140000
2026-10-05 19:00 | 3074.2 | 1 | 57.946 | 59.8258 | 900.9591 |  | 2371 | 8535600 | 40071600 | 71607600 | 103143600
2026-10-06 20:00 | 0 | 0 | 58.1934 | 59.8258 | 0 |  | 2372 | 8539200 | 40075200 | 71611200 | 103147200
2026-10-07 21:00 | -940.416 | 3.0653 | 56.3856 | 59.8258 | -275.6087 |  | 2373 | 8542800 | 40078800 | 71614800 | 103150800
2026-10-08 22:00 | -1886.71 | 5.9646 | 56.0052 | 59.8258 | -552.9401 |  | 2374 | 8546400 | 40082400 | 71618400 | 103154400
2026-10-09 23:00 | -2329.53 | 6.108 | 55.3942 | 59.8258 | -682.7178 |  | 2375 | 8550000 | 40086000 | 71622000 | 103158000
2026-10-11 | -2502.18 | 6.108 | 55.0306 | 59.8258 | -733.3166 |  | 2376 | 8553600 | 40089600 | 71625600 | 103161600
2026-10-12 01:00 | -2515.41 | 6.108 | 54.8219 | 59.8258 | -737.1939 |  | 2377 | 8557200 | 40093200 | 71629200 | 103165200
2026-10-13 02:00 | -2519.28 | 6.108 | 54.6991 | 59.8258 | -738.3281 |  | 2378 | 8560800 | 40096800 | 71632800 | 103168800
2026-10-14 03:00 | -2331.26 | 6.108 | 54.7339 | 59.8258 | -683.2249 |  | 2379 | 8564400 | 40100400 | 71636400 | 103172400
2026-10-15 04:00 | -2128.09 | 6.108 | 54.8342 | 59.8258 | -623.6816 |  | 2380 | 8568000 | 40104000 | 71640000 | 103176000
2026-10-16 05:00 | -1796.34 | 5.4707 | 54.9101 | 59.8258 | -526.4553 |  | 2381 | 8571600 | 40107600 | 71643600 | 103179600
2026-10-17 06:00 | -1769.1 | 5.4425 | 54.9642 | 59.8258 | -518.472 |  | 2382 | 8575200 | 40111200 | 71647200 | 103183200
2026-10-18 07:00 | -1277.41 | 3.9392 | 54.978 | 59.8258 | -374.3719 |  | 2383 | 8578800 | 40114800 | 71650800 | 103186800
2026-10-19 08:00 | -1152.58 | 3.7059 | 55.1351 | 59.8258 | -337.7879 |  | 2384 | 8582400 | 40118400 | 71654400 | 103190400
2026-10-20 09:00 | -565.392 | 1.9482 | 55.3033 | 59.8258 | -165.7 |  | 2385 | 8586000 | 40122000 | 71658000 | 103194000
2026-10-21 10:00 | 1722.56 | 1 | 56.6061 | 59.8258 | 504.8325 |  | 2386 | 8589600 | 40125600 | 71661600 | 103197600
2026-10-22 11:00 | 3164.36 | 1 | 56.8464 | 59.8258 | 927.3824 |  | 2387 | 8593200 | 40129200 | 71665200 | 103201200
2026-10-23 12:00 | 3177.36 | 1 | 75.0928 | 59.8258 | 931.1923 |  | 2388 | 8596800 | 40132800 | 71668800 | 103204800
2026-10-24 13:00 | 3263.66 | 1.0313 | 72.234 | 59.8258 | 956.4843 |  | 2389 | 8600400 | 40136400 | 71672400 | 103208400
2026-10-25 14:00 | 3116.85 | 1 | 80.4214 | 59.8258 | 913.4586 |  | 2390 | 8604000 | 40140000 | 71676000 | 103212000
2026-10-26 15:00 | 3350.42 | 1 | 78.3408 | 59.8258 | 981.9112 |  | 2391 | 8607600 | 40143600 | 71679600 | 103215600
2026-10-27 16:00 | 3084.31 | 1 | 57.8879 | 59.8258 | 903.922 |  | 2392 | 8611200 | 40147200 | 71683200 | 103219200
2026-10-28 17:00 | 3195.34 | 1 | 57.9209 | 59.8258 | 936.4617 |  | 2393 | 8614800 | 40150800 | 71686800 | 103222800
2026-10-29 18:00 | 2727.26 | 1 | 58.0402 | 59.8258 | 799.281 |  | 2394 | 8618400 | 40154400 | 71690400 | 103226400
2026-10-30 19:00 | -219.417 | 1.237 | 57.4823 | 59.8258 | -64.3048 |  | 2395 | 8622000 | 40158000 | 71694000 | 103230000
2026-10-31 20:00 | -1124.21 | 3.8028 | 56.6039 | 59.8258 | -329.4734 |  | 2396 | 8625600 | 40161600 | 71697600 | 103233600
2026-11-01 21:00 | -1491.68 | 4.6847 | 56.2185 | 59.8258 | -437.1683 |  | 2397 | 8629200 | 40165200 | 71701200 | 103237200
2026-11-02 22:00 | -2477.59 | 6.108 | 55.6333 | 59.8258 | -726.11 |  | 2398 | 8632800 | 40168800 | 71704800 | 103240800
2026-11-03 23:00 | -2689.41 | 6.108 | 55.1926 | 59.8258 | -788.1883 |  | 2399 | 8636400 | 40172400 | 71708400 | 103244400
2026-11-05 | -3031.55 | 6.108 | 54.7092 | 59.8258 | -888.4596 |  | 2400 | 8640000 | 40176000 | 71712000 | 103248000
2026-11-06 01:00 | -3365.56 | 6.108 | 54.2998 | 59.8258 | -986.3483 |  | 2401 | 8643600 | 40179600 | 71715600 | 103251600
2026-11-07 02:00 | -3617.1 | 6.108 | 53.9559 | 59.8258 | -1060.0674 |  | 2402 | 8647200 | 40183200 | 71719200 | 103255200
2026-11-08 03:00 | -3665.54 | 6.108 | 53.7665 | 59.8258 | -1074.2637 |  | 2403 | 8650800 | 40186800 | 71722800 | 103258800
2026-11-09 04:00 | -3735.98 | 6.108 | 53.6044 | 59.8258 | -1094.9077 |  | 2404 | 8654400 | 40190400 | 71726400 | 103262400
2026-11-10 05:00 | -3517.5 | 6.108 | 53.6622 | 59.8258 | -1030.8775 |  | 2405 | 8658000 | 40194000 | 71730000 | 103266000
2026-11-11 06:00 | -3559.19 | 6.108 | 53.5723 | 59.8258 | -1043.0956 |  | 2406 | 8661600 | 40197600 | 71733600 | 103269600
2026-11-12 07:00 | -3619.84 | 6.108 | 53.4871 | 59.8258 | -1060.8704 |  | 2407 | 8665200 | 40201200 | 71737200 | 103273200
2026-11-13 08:00 | -4132.69 | 6.108 | 53.0612 | 59.8258 | -1211.1719 |  | 2408 | 8668800 | 40204800 | 71740800 | 103276800
2026-11-14 09:00 | -3798.48 | 6.108 | 53.1978 | 59.8258 | -1113.2246 |  | 2409 | 8672400 | 40208400 | 71744400 | 103280400
2026-11-15 10:00 | -2988.15 | 6.108 | 53.7605 | 59.8258 | -875.7403 |  | 2410 | 8676000 | 40212000 | 71748000 | 103284000
2026-11-16 11:00 | -1988.29 | 6.108 | 54.5506 | 59.8258 | -582.7103 |  | 2411 | 8679600 | 40215600 | 71751600 | 103287600
2026-11-17 12:00 | -960.565 | 2.9177 | 54.6507 | 59.8258 | -281.5138 |  | 2412 | 8683200 | 40219200 | 71755200 | 103291200
2026-11-18 13:00 | 1719.98 | 1 | 56.1889 | 59.8258 | 504.0764 |  | 2413 | 8686800 | 40222800 | 71758800 | 103294800
2026-11-19 14:00 | 2904.24 | 1 | 56.5462 | 59.8258 | 851.1487 |  | 2414 | 8690400 | 40226400 | 71762400 | 103298400
2026-11-20 15:00 | 2933.15 | 1 | 56.9625 | 59.8258 | 859.6214 |  | 2415 | 8694000 | 40230000 | 71766000 | 103302000
2026-11-21 16:00 | 2906.43 | 1 | 57.2123 | 59.8258 | 851.7905 |  | 2416 | 8697600 | 40233600 | 71769600 | 103305600
2026-11-22 17:00 | 2889.17 | 1 | 57.3924 | 59.8258 | 846.7321 |  | 2417 | 8701200 | 40237200 | 71773200 | 103309200
2026-11-23 18:00 | -255.756 | 1.3246 | 56.9288 | 59.8258 | -74.9547 |  | 2418 | 8704800 | 40240800 | 71776800 | 103312800
2026-11-24 19:00 | -1131.13 | 3.8388 | 56.1662 | 59.8258 | -331.5015 |  | 2419 | 8708400 | 40244400 | 71780400 | 103316400
2026-11-25 20:00 | -2584.01 | 6.108 | 55.3379 | 59.8258 | -757.2986 |  | 2420 | 8712000 | 40248000 | 71784000 | 103320000
2026-11-26 21:00 | -3452.46 | 6.108 | 54.4044 | 59.8258 | -1011.8161 |  | 2421 | 8715600 | 40251600 | 71787600 | 103323600
2026-11-27 22:00 | -4719.73 | 6.108 | 53.167 | 59.8258 | -1383.2163 |  | 2422 | 8719200 | 40255200 | 71791200 | 103327200
2026-11-28 23:00 | -5217.12 | 6.108 | 52.4265 | 59.8258 | -1528.9869 |  | 2423 | 8722800 | 40258800 | 71794800 | 103330800
2026-11-30 | -5281.76 | 6.108 | 52.109 | 59.8258 | -1547.9311 |  | 2424 | 8726400 | 40262400 | 71798400 | 103334400
2026-12-01 01:00 | -5582.75 | 6.108 | 51.6704 | 59.8258 | -1636.1425 |  | 2425 | 8730000 | 40266000 | 71802000 | 103338000
2026-12-02 02:00 | -5782.21 | 6.108 | 51.309 | 59.8258 | -1694.5985 |  | 2426 | 8733600 | 40269600 | 71805600 | 103341600
2026-12-03 03:00 | -5761.2 | 6.108 | 51.125 | 59.8258 | -1688.441 |  | 2427 | 8737200 | 40273200 | 71809200 | 103345200
2026-12-04 04:00 | -6132.45 | 6.108 | 50.701 | 59.8258 | -1797.2437 |  | 2428 | 8740800 | 40276800 | 71812800 | 103348800
2026-12-05 05:00 | -5748.48 | 6.108 | 50.807 | 59.8258 | -1684.7132 |  | 2429 | 8744400 | 40280400 | 71816400 | 103352400
2026-12-06 06:00 | -5558.62 | 6.108 | 50.8777 | 59.8258 | -1629.0707 |  | 2430 | 8748000 | 40284000 | 71820000 | 103356000
2026-12-07 07:00 | -4983.05 | 6.108 | 51.2677 | 59.8258 | -1460.3878 |  | 2431 | 8751600 | 40287600 | 71823600 | 103359600
2026-12-08 08:00 | -4424.71 | 6.108 | 51.7215 | 59.8258 | -1296.7545 |  | 2432 | 8755200 | 40291200 | 71827200 | 103363200
2026-12-09 09:00 | -2891.35 | 6.108 | 52.9462 | 59.8258 | -847.371 |  | 2433 | 8758800 | 40294800 | 71830800 | 103366800
2026-12-10 10:00 | -1655.61 | 5.1519 | 53.8821 | 59.8258 | -485.2114 |  | 2434 | 8762400 | 40298400 | 71834400 | 103370400
2026-12-11 11:00 | -778.658 | 2.4769 | 54.1973 | 59.8258 | -228.2021 |  | 2435 | 8766000 | 40302000 | 71838000 | 103374000
2026-12-12 12:00 | -316.498 | 1.3328 | 54.8188 | 59.8258 | -92.7564 |  | 2436 | 8769600 | 40305600 | 71841600 | 103377600
2026-12-13 13:00 | 2644.79 | 1 | 55.8931 | 59.8258 | 775.1114 |  | 2437 | 8773200 | 40309200 | 71845200 | 103381200
2026-12-14 14:00 | 2933.95 | 1 | 56.4102 | 59.8258 | 859.8559 |  | 2438 | 8776800 | 40312800 | 71848800 | 103384800
2026-12-15 15:00 | 2934.61 | 1 | 70.9143 | 59.8258 | 860.0493 |  | 2439 | 8780400 | 40316400 | 71852400 | 103388400
2026-12-16 16:00 | 2959.54 | 1.016 | 70.5768 | 59.8258 | 867.3556 |  | 2440 | 8784000 | 40320000 | 71856000 | 103392000
2026-12-17 17:00 | 2901.85 | 1 | 71.7316 | 59.8258 | 850.4483 |  | 2441 | 8787600 | 40323600 | 71859600 | 103395600
2026-12-18 18:00 | 2781.36 | 1 | 57.3761 | 59.8258 | 815.1362 |  | 2442 | 8791200 | 40327200 | 71863200 | 103399200
2026-12-19 19:00 | -623.7 | 2.4083 | 56.5595 | 59.8258 | -182.7884 |  | 2443 | 8794800 | 40330800 | 71866800 | 103402800
2026-12-20 20:00 | -2178.56 | 6.108 | 55.7789 | 59.8258 | -638.4729 |  | 2444 | 8798400 | 40334400 | 71870400 | 103406400
2026-12-21 21:00 | -3161.61 | 6.108 | 54.6795 | 59.8258 | -926.5764 |  | 2445 | 8802000 | 40338000 | 71874000 | 103410000
2026-12-22 22:00 | -4705.31 | 6.108 | 53.2286 | 59.8258 | -1378.9902 |  | 2446 | 8805600 | 40341600 | 71877600 | 103413600
2026-12-23 23:00 | -5381.48 | 6.108 | 52.3216 | 59.8258 | -1577.1561 |  | 2447 | 8809200 | 40345200 | 71881200 | 103417200
2026-12-25 | -5715.39 | 6.108 | 51.7012 | 59.8258 | -1675.0155 |  | 2448 | 8812800 | 40348800 | 71884800 | 103420800
2026-12-26 01:00 | -6035.12 | 6.108 | 51.1852 | 59.8258 | -1768.7191 |  | 2449 | 8816400 | 40352400 | 71888400 | 103424400
2026-12-27 02:00 | -6536.19 | 6.108 | 50.5659 | 59.8258 | -1915.5682 |  | 2450 | 8820000 | 40356000 | 71892000 | 103428000
2026-12-28 03:00 | -6774.45 | 6.108 | 50.1271 | 59.8258 | -1985.3953 |  | 2451 | 8823600 | 40359600 | 71895600 | 103431600
2026-12-29 04:00 | -6761.93 | 6.108 | 49.9212 | 59.8258 | -1981.7261 |  | 2452 | 8827200 | 40363200 | 71899200 | 103435200
2026-12-30 05:00 | -6192.8 | 6.108 | 50.179 | 59.8258 | -1814.9305 |  | 2453 | 8830800 | 40366800 | 71902800 | 103438800
2026-12-31 06:00 | -5876.16 | 6.108 | 50.3414 | 59.8258 | -1722.1325 |  | 2454 | 8834400 | 40370400 | 71906400 | 103442400
2027-01-01 07:00 | -5326.23 | 6.108 | 50.7306 | 59.8258 | -1560.9639 |  | 2455 | 8838000 | 40374000 | 71910000 | 103446000
2027-01-02 08:00 | -4926.48 | 6.108 | 51.0705 | 59.8258 | -1443.8088 |  | 2456 | 8841600 | 40377600 | 71913600 | 103449600
2027-01-03 09:00 | -2984.2 | 6.108 | 52.5831 | 59.8258 | -874.5827 |  | 2457 | 8845200 | 40381200 | 71917200 | 103453200
2027-01-04 10:00 | -1381.16 | 4.3086 | 53.6341 | 59.8258 | -404.778 |  | 2458 | 8848800 | 40384800 | 71920800 | 103456800
2027-01-05 11:00 | -248.01 | 0.94359 | 54.2529 | 59.8258 | -72.6846 |  | 2459 | 8852400 | 40388400 | 71924400 | 103460400
2027-01-06 12:00 | 2732.28 | 1 | 55.5657 | 59.8258 | 800.7522 |  | 2460 | 8856000 | 40392000 | 71928000 | 103464000
2027-01-07 13:00 | 3020.66 | 1 | 73.5468 | 59.8258 | 885.2681 |  | 2461 | 8859600 | 40395600 | 71931600 | 103467600
2027-01-08 14:00 | 3222.48 | 1.0891 | 70.3449 | 59.8258 | 944.4157 |  | 2462 | 8863200 | 40399200 | 71935200 | 103471200
2027-01-09 15:00 | 4298.78 | 1.4437 | 70.714 | 59.8258 | 1259.8481 |  | 2463 | 8866800 | 40402800 | 71938800 | 103474800
2027-01-10 16:00 | 4333.21 | 1.4627 | 71.0133 | 59.8258 | 1269.9385 |  | 2464 | 8870400 | 40406400 | 71942400 | 103478400
2027-01-11 17:00 | 3291.5 | 1.1126 | 71.2747 | 59.8258 | 964.6434 |  | 2465 | 8874000 | 40410000 | 71946000 | 103482000
2027-01-12 18:00 | 3019.53 | 1 | 57.5072 | 59.8258 | 884.9369 |  | 2466 | 8877600 | 40413600 | 71949600 | 103485600
2027-01-13 19:00 | 0 | 0 | 57.8498 | 59.8258 | 0 |  | 2467 | 8881200 | 40417200 | 71953200 | 103489200
2027-01-14 20:00 | -1088.7 | 3.5535 | 56.1628 | 59.8258 | -319.0665 |  | 2468 | 8884800 | 40420800 | 71956800 | 103492800
2027-01-15 21:00 | -1772.43 | 5.5839 | 55.8291 | 59.8258 | -519.448 |  | 2469 | 8888400 | 40424400 | 71960400 | 103496400
2027-01-16 22:00 | -2971.05 | 6.108 | 54.8389 | 59.8258 | -870.7288 |  | 2470 | 8892000 | 40428000 | 71964000 | 103500000
2027-01-17 23:00 | -3845.21 | 6.108 | 53.8951 | 59.8258 | -1126.9198 |  | 2471 | 8895600 | 40431600 | 71967600 | 103503600
2027-01-19 | -4319.19 | 6.108 | 53.1978 | 59.8258 | -1265.8296 |  | 2472 | 8899200 | 40435200 | 71971200 | 103507200
2027-01-20 01:00 | -4548.59 | 6.108 | 52.7788 | 59.8258 | -1333.0601 |  | 2473 | 8902800 | 40438800 | 71974800 | 103510800
2027-01-21 02:00 | -4753.56 | 6.108 | 52.4303 | 59.8258 | -1393.1309 |  | 2474 | 8906400 | 40442400 | 71978400 | 103514400
2027-01-22 03:00 | -4759.42 | 6.108 | 52.2369 | 59.8258 | -1394.8483 |  | 2475 | 8910000 | 40446000 | 71982000 | 103518000
2027-01-23 04:00 | -5065.58 | 6.108 | 51.8651 | 59.8258 | -1484.575 |  | 2476 | 8913600 | 40449600 | 71985600 | 103521600
2027-01-24 05:00 | -5050.34 | 6.108 | 51.7262 | 59.8258 | -1480.1085 |  | 2477 | 8917200 | 40453200 | 71989200 | 103525200
2027-01-25 06:00 | -4232.8 | 6.108 | 52.2208 | 59.8258 | -1240.5112 |  | 2478 | 8920800 | 40456800 | 71992800 | 103528800
2027-01-26 07:00 | -3446.37 | 6.108 | 52.8484 | 59.8258 | -1010.0313 |  | 2479 | 8924400 | 40460400 | 71996400 | 103532400
2027-01-27 08:00 | -3350.99 | 6.108 | 53.0313 | 59.8258 | -982.0782 |  | 2480 | 8928000 | 40464000 | 72000000 | 103536000
2027-01-28 09:00 | -2269.49 | 6.108 | 53.8842 | 59.8258 | -665.1219 |  | 2481 | 8931600 | 40467600 | 72003600 | 103539600
2027-01-29 10:00 | -1088.28 | 3.3351 | 54.2492 | 59.8258 | -318.9434 |  | 2482 | 8935200 | 40471200 | 72007200 | 103543200
2027-01-30 11:00 | 0 | 1 | 56.0021 | 59.8258 | 0 |  | 2483 | 8938800 | 40474800 | 72010800 | 103546800
2027-01-31 12:00 | 147.109 | 1 | 56.2575 | 59.8258 | 43.1134 |  | 2484 | 8942400 | 40478400 | 72014400 | 103550400
2027-02-01 13:00 | 2939.15 | 1 | 56.1725 | 59.8258 | 861.3798 |  | 2485 | 8946000 | 40482000 | 72018000 | 103554000
2027-02-02 14:00 | 3009.78 | 1 | 56.6609 | 59.8258 | 882.0794 |  | 2486 | 8949600 | 40485600 | 72021600 | 103557600
2027-02-03 15:00 | 3097.87 | 1 | 56.9617 | 59.8258 | 907.8961 |  | 2487 | 8953200 | 40489200 | 72025200 | 103561200
2027-02-04 16:00 | 3153.81 | 1 | 77.5144 | 59.8258 | 924.2905 |  | 2488 | 8956800 | 40492800 | 72028800 | 103564800
2027-02-05 17:00 | 3189.12 | 1 | 57.3174 | 59.8258 | 934.6388 |  | 2489 | 8960400 | 40496400 | 72032400 | 103568400
2027-02-06 18:00 | -276.68 | 1.404 | 56.8714 | 59.8258 | -81.0869 |  | 2490 | 8964000 | 40500000 | 72036000 | 103572000
2027-02-07 19:00 | -735.011 | 2.6555 | 56.1552 | 59.8258 | -215.4105 |  | 2491 | 8967600 | 40503600 | 72039600 | 103575600
2027-02-08 20:00 | -1264.39 | 4.1373 | 55.8168 | 59.8258 | -370.5561 |  | 2492 | 8971200 | 40507200 | 72043200 | 103579200
2027-02-09 21:00 | -1640.78 | 5.141 | 55.6155 | 59.8258 | -480.8652 |  | 2493 | 8974800 | 40510800 | 72046800 | 103582800
2027-02-10 22:00 | -1713.53 | 5.272 | 55.4413 | 59.8258 | -502.1861 |  | 2494 | 8978400 | 40514400 | 72050400 | 103586400
2027-02-11 23:00 | -3257.19 | 6.108 | 54.3673 | 59.8258 | -954.5882 |  | 2495 | 8982000 | 40518000 | 72054000 | 103590000
2027-02-13 | -3715.09 | 6.108 | 53.7884 | 59.8258 | -1088.7854 |  | 2496 | 8985600 | 40521600 | 72057600 | 103593600
2027-02-14 01:00 | -3886.13 | 6.108 | 53.4342 | 59.8258 | -1138.9123 |  | 2497 | 8989200 | 40525200 | 72061200 | 103597200
2027-02-15 02:00 | -3791.09 | 6.108 | 53.3497 | 59.8258 | -1111.0588 |  | 2498 | 8992800 | 40528800 | 72064800 | 103600800
2027-02-16 03:00 | -3899.7 | 6.108 | 53.1599 | 59.8258 | -1142.8893 |  | 2499 | 8996400 | 40532400 | 72068400 | 103604400
2027-02-17 04:00 | -4047.69 | 6.108 | 52.9288 | 59.8258 | -1186.2608 |  | 2500 | 9000000 | 40536000 | 72072000 | 103608000
2027-02-18 05:00 | -4025.6 | 6.108 | 52.8408 | 59.8258 | -1179.7869 |  | 2501 | 9003600 | 40539600 | 72075600 | 103611600
2027-02-19 06:00 | -3136.43 | 6.108 | 53.462 | 59.8258 | -919.1969 |  | 2502 | 9007200 | 40543200 | 72079200 | 103615200
2027-02-20 07:00 | -2553.95 | 6.108 | 53.9819 | 59.8258 | -748.4889 |  | 2503 | 9010800 | 40546800 | 72082800 | 103618800
2027-02-21 08:00 | -2663.39 | 6.108 | 54.013 | 59.8258 | -780.5626 |  | 2504 | 9014400 | 40550400 | 72086400 | 103622400
2027-02-22 09:00 | -2063.32 | 6.108 | 54.4901 | 59.8258 | -604.6994 |  | 2505 | 9018000 | 40554000 | 72090000 | 103626000
2027-02-23 10:00 | -1461.92 | 4.4582 | 54.6191 | 59.8258 | -428.4465 |  | 2506 | 9021600 | 40557600 | 72093600 | 103629600
2027-02-24 11:00 | 0 | 0 | 56.2641 | 59.8258 | 0 |  | 2507 | 9025200 | 40561200 | 72097200 | 103633200
2027-02-25 12:00 | 2631.13 | 1 | 56.2939 | 59.8258 | 771.1081 |  | 2508 | 9028800 | 40564800 | 72100800 | 103636800
2027-02-26 13:00 | 3136.32 | 1 | 80.7353 | 59.8258 | 919.1647 |  | 2509 | 9032400 | 40568400 | 72104400 | 103640400
2027-02-27 14:00 | 3257.15 | 1.0527 | 71.4905 | 59.8258 | 954.5764 |  | 2510 | 9036000 | 40572000 | 72108000 | 103644000
2027-02-28 15:00 | 3851.97 | 1.2416 | 71.7784 | 59.8258 | 1128.901 |  | 2511 | 9039600 | 40575600 | 72111600 | 103647600
2027-03-01 16:00 | 6364.4 | 2.0482 | 72.0629 | 59.8258 | 1865.2215 |  | 2512 | 9043200 | 40579200 | 72115200 | 103651200
2027-03-02 17:00 | 4555.17 | 1.4791 | 72.4942 | 59.8258 | 1334.9885 |  | 2513 | 9046800 | 40582800 | 72118800 | 103654800
2027-03-03 18:00 | 3117.23 | 1 | 75.6839 | 59.8258 | 913.5699 |  | 2514 | 9050400 | 40586400 | 72122400 | 103658400
2027-03-04 19:00 | 3063.97 | 1 | 58.1458 | 59.8258 | 897.961 |  | 2515 | 9054000 | 40590000 | 72126000 | 103662000
2027-03-05 20:00 | 1403.95 | 1 | 58.3593 | 59.8258 | 411.4571 |  | 2516 | 9057600 | 40593600 | 72129600 | 103665600
2027-03-06 21:00 | -215.793 | 1.2241 | 57.542 | 59.8258 | -63.2427 |  | 2517 | 9061200 | 40597200 | 72133200 | 103669200
2027-03-07 22:00 | -630.825 | 2.3431 | 56.8024 | 59.8258 | -184.8766 |  | 2518 | 9064800 | 40600800 | 72136800 | 103672800
2027-03-08 23:00 | -1774.24 | 5.6607 | 56.4214 | 59.8258 | -519.9784 |  | 2519 | 9068400 | 40604400 | 72140400 | 103676400
2027-03-10 | -2267.04 | 6.108 | 55.9056 | 59.8258 | -664.4038 |  | 2520 | 9072000 | 40608000 | 72144000 | 103680000
2027-03-11 01:00 | -2560.17 | 6.108 | 55.4435 | 59.8258 | -750.3118 |  | 2521 | 9075600 | 40611600 | 72147600 | 103683600
2027-03-12 02:00 | -2800.02 | 6.108 | 55.0858 | 59.8258 | -820.6049 |  | 2522 | 9079200 | 40615200 | 72151200 | 103687200
2027-03-13 03:00 | -3001.92 | 6.108 | 54.7882 | 59.8258 | -879.7759 |  | 2523 | 9082800 | 40618800 | 72154800 | 103690800
2027-03-14 04:00 | -3083.53 | 6.108 | 54.5602 | 59.8258 | -903.6934 |  | 2524 | 9086400 | 40622400 | 72158400 | 103694400
2027-03-15 05:00 | -2948.78 | 6.108 | 54.549 | 59.8258 | -864.2021 |  | 2525 | 9090000 | 40626000 | 72162000 | 103698000
2027-03-16 06:00 | -2910.95 | 6.108 | 54.5148 | 59.8258 | -853.1152 |  | 2526 | 9093600 | 40629600 | 72165600 | 103701600
2027-03-17 07:00 | -2179.93 | 6.108 | 54.9996 | 59.8258 | -638.8744 |  | 2527 | 9097200 | 40633200 | 72169200 | 103705200
2027-03-18 08:00 | -1676.09 | 5.0844 | 55.1764 | 59.8258 | -491.2135 |  | 2528 | 9100800 | 40636800 | 72172800 | 103708800
2027-03-19 09:00 | -300.854 | 1.0112 | 55.4109 | 59.8258 | -88.1716 |  | 2529 | 9104400 | 40640400 | 72176400 | 103712400
2027-03-20 10:00 | 2694.35 | 1 | 78.0398 | 59.8258 | 789.636 |  | 2530 | 9108000 | 40644000 | 72180000 | 103716000
2027-03-21 11:00 | 4156.33 | 1.3172 | 71.9485 | 59.8258 | 1218.1001 |  | 2531 | 9111600 | 40647600 | 72183600 | 103719600
2027-03-22 12:00 | 5363.53 | 1.6955 | 72.5006 | 59.8258 | 1571.8955 |  | 2532 | 9115200 | 40651200 | 72187200 | 103723200
2027-03-23 13:00 | 5888.7 | 1.8981 | 72.6721 | 59.8258 | 1725.8076 |  | 2533 | 9118800 | 40654800 | 72190800 | 103726800
2027-03-24 14:00 | 6456.16 | 2.0672 | 73.1597 | 59.8258 | 1892.1137 |  | 2534 | 9122400 | 40658400 | 72194400 | 103730400
2027-03-25 15:00 | 7762.26 | 2.508 | 73.3929 | 59.8258 | 2274.8938 |  | 2535 | 9126000 | 40662000 | 72198000 | 103734000
2027-03-26 16:00 | 7801.19 | 2.4787 | 74.0464 | 59.8258 | 2286.3031 |  | 2536 | 9129600 | 40665600 | 72201600 | 103737600
2027-03-27 17:00 | 7223.51 | 2.2796 | 74.4481 | 59.8258 | 2117.0018 |  | 2537 | 9133200 | 40669200 | 72205200 | 103741200
2027-03-28 18:00 | 4787 | 1.5014 | 74.7172 | 59.8258 | 1402.9312 |  | 2538 | 9136800 | 40672800 | 72208800 | 103744800
2027-03-29 19:00 | 3456.7 | 1.0973 | 74.403 | 59.8258 | 1013.0588 |  | 2539 | 9140400 | 40676400 | 72212400 | 103748400
2027-03-30 20:00 | 3078.24 | 1 | 59.5476 | 59.8258 | 902.1431 |  | 2540 | 9144000 | 40680000 | 72216000 | 103752000
2027-03-31 21:00 | 0 | 0 | 59.7282 | 59.8258 | 0 |  | 2541 | 9147600 | 40683600 | 72219600 | 103755600
2027-04-01 22:00 | -929.057 | 2.9633 | 57.808 | 59.8258 | -272.2797 |  | 2542 | 9151200 | 40687200 | 72223200 | 103759200
2027-04-02 23:00 | -1269.58 | 4.0378 | 57.3929 | 59.8258 | -372.0772 |  | 2543 | 9154800 | 40690800 | 72226800 | 103762800
2027-04-04 | -1538.86 | 4.7463 | 57.0964 | 59.8258 | -450.9953 |  | 2544 | 9158400 | 40694400 | 72230400 | 103766400
2027-04-05 01:00 | -1856.73 | 5.6394 | 56.8641 | 59.8258 | -544.1538 |  | 2545 | 9162000 | 40698000 | 72234000 | 103770000
2027-04-06 02:00 | -2041.77 | 6.108 | 56.6189 | 59.8258 | -598.3837 |  | 2546 | 9165600 | 40701600 | 72237600 | 103773600
2027-04-07 03:00 | -2028.86 | 6.051 | 56.4506 | 59.8258 | -594.6002 |  | 2547 | 9169200 | 40705200 | 72241200 | 103777200
2027-04-08 04:00 | -1950.82 | 5.8304 | 56.3347 | 59.8258 | -571.7289 |  | 2548 | 9172800 | 40708800 | 72244800 | 103780800
2027-04-09 05:00 | -1679.21 | 5.0402 | 56.2504 | 59.8258 | -492.1279 |  | 2549 | 9176400 | 40712400 | 72248400 | 103784400
2027-04-10 06:00 | -1523.19 | 4.6516 | 56.2488 | 59.8258 | -446.4029 |  | 2550 | 9180000 | 40716000 | 72252000 | 103788000
2027-04-11 07:00 | -968.853 | 3.0299 | 56.2726 | 59.8258 | -283.9428 |  | 2551 | 9183600 | 40719600 | 72255600 | 103791600
2027-04-12 08:00 | -1107.32 | 3.6005 | 56.3828 | 59.8258 | -324.5235 |  | 2552 | 9187200 | 40723200 | 72259200 | 103795200
2027-04-13 09:00 | -676.692 | 2.2615 | 56.4369 | 59.8258 | -198.3188 |  | 2553 | 9190800 | 40726800 | 72262800 | 103798800
2027-04-14 10:00 | 2206.87 | 1 | 57.6675 | 59.8258 | 646.7698 |  | 2554 | 9194400 | 40730400 | 72266400 | 103802400
2027-04-15 11:00 | 3099.94 | 1 | 78.0453 | 59.8258 | 908.5027 |  | 2555 | 9198000 | 40734000 | 72270000 | 103806000
2027-04-16 12:00 | 3134.84 | 1 | 58.3106 | 59.8258 | 918.7309 |  | 2556 | 9201600 | 40737600 | 72273600 | 103809600
2027-04-17 13:00 | 3145.91 | 1 | 58.4894 | 59.8258 | 921.9752 |  | 2557 | 9205200 | 40741200 | 72277200 | 103813200
2027-04-18 14:00 | -285.788 | 1.3946 | 57.9649 | 59.8258 | -83.7562 |  | 2558 | 9208800 | 40744800 | 72280800 | 103816800
2027-04-19 15:00 | -335.235 | 1.4508 | 57.4897 | 59.8258 | -98.2477 |  | 2559 | 9212400 | 40748400 | 72284400 | 103820400
2027-04-20 16:00 | -408.053 | 1.6626 | 57.1819 | 59.8258 | -119.5885 |  | 2560 | 9216000 | 40752000 | 72288000 | 103824000
2027-04-21 17:00 | -654.015 | 2.3695 | 56.8993 | 59.8258 | -191.6729 |  | 2561 | 9219600 | 40755600 | 72291600 | 103827600
2027-04-22 18:00 | -1548.94 | 4.9709 | 56.587 | 59.8258 | -453.9495 |  | 2562 | 9223200 | 40759200 | 72295200 | 103831200
2027-04-23 19:00 | -2057.6 | 6.108 | 56.2206 | 59.8258 | -603.023 |  | 2563 | 9226800 | 40762800 | 72298800 | 103834800
2027-04-24 20:00 | -3407.84 | 6.108 | 55.0376 | 59.8258 | -998.7393 |  | 2564 | 9230400 | 40766400 | 72302400 | 103838400
2027-04-25 21:00 | -4020.23 | 6.108 | 54.3022 | 59.8258 | -1178.2131 |  | 2565 | 9234000 | 40770000 | 72306000 | 103842000
2027-04-26 22:00 | -5268.95 | 6.108 | 53.0784 | 59.8258 | -1544.1768 |  | 2566 | 9237600 | 40773600 | 72309600 | 103845600
2027-04-27 23:00 | -5700.75 | 6.108 | 52.3788 | 59.8258 | -1670.7249 |  | 2567 | 9241200 | 40777200 | 72313200 | 103849200
2027-04-29 | -5971.83 | 6.108 | 51.8576 | 59.8258 | -1750.1706 |  | 2568 | 9244800 | 40780800 | 72316800 | 103852800
2027-04-30 01:00 | -6329.62 | 6.108 | 51.3166 | 59.8258 | -1855.0285 |  | 2569 | 9248400 | 40784400 | 72320400 | 103856400
2027-05-01 02:00 | -6556.96 | 6.108 | 50.9267 | 59.8258 | -1921.6553 |  | 2570 | 9252000 | 40788000 | 72324000 | 103860000
2027-05-02 03:00 | -6518.58 | 6.108 | 50.7499 | 59.8258 | -1910.4072 |  | 2571 | 9255600 | 40791600 | 72327600 | 103863600
2027-05-03 04:00 | -6277.73 | 6.108 | 50.7856 | 59.8258 | -1839.821 |  | 2572 | 9259200 | 40795200 | 72331200 | 103867200
2027-05-04 05:00 | -6308.61 | 6.108 | 50.6668 | 59.8258 | -1848.8711 |  | 2573 | 9262800 | 40798800 | 72334800 | 103870800
2027-05-05 06:00 | -6009.22 | 6.108 | 50.7903 | 59.8258 | -1761.1285 |  | 2574 | 9266400 | 40802400 | 72338400 | 103874400
2027-05-06 07:00 | -5372.55 | 6.108 | 51.2088 | 59.8258 | -1574.539 |  | 2575 | 9270000 | 40806000 | 72342000 | 103878000
2027-05-07 08:00 | -5091.93 | 6.108 | 51.4511 | 59.8258 | -1492.2974 |  | 2576 | 9273600 | 40809600 | 72345600 | 103881600
2027-05-08 09:00 | -3950.21 | 6.108 | 52.3279 | 59.8258 | -1157.6923 |  | 2577 | 9277200 | 40813200 | 72349200 | 103885200
2027-05-09 10:00 | -2452.57 | 6.108 | 53.5694 | 59.8258 | -718.7773 |  | 2578 | 9280800 | 40816800 | 72352800 | 103888800
2027-05-10 11:00 | -1186.68 | 3.6501 | 54.1577 | 59.8258 | -347.7816 |  | 2579 | 9284400 | 40820400 | 72356400 | 103892400
2027-05-11 12:00 | -375.444 | 1.3928 | 54.6923 | 59.8258 | -110.0318 |  | 2580 | 9288000 | 40824000 | 72360000 | 103896000
2027-05-12 13:00 | 1179.25 | 1 | 56.0819 | 59.8258 | 345.6041 |  | 2581 | 9291600 | 40827600 | 72363600 | 103899600
2027-05-13 14:00 | 2927.85 | 1 | 56.3176 | 59.8258 | 858.0681 |  | 2582 | 9295200 | 40831200 | 72367200 | 103903200
2027-05-14 15:00 | 2931.11 | 1 | 72.012 | 59.8258 | 859.0235 |  | 2583 | 9298800 | 40834800 | 72370800 | 103906800
2027-05-15 16:00 | 2981.23 | 1.0123 | 70.8212 | 59.8258 | 873.7123 |  | 2584 | 9302400 | 40838400 | 72374400 | 103910400
2027-05-16 17:00 | 2930.27 | 1 | 73.8305 | 59.8258 | 858.7774 |  | 2585 | 9306000 | 40842000 | 72378000 | 103914000
2027-05-17 18:00 | 2811 | 1 | 57.5122 | 59.8258 | 823.8228 |  | 2586 | 9309600 | 40845600 | 72381600 | 103917600
2027-05-18 19:00 | -324.379 | 1.53 | 56.9478 | 59.8258 | -95.0661 |  | 2587 | 9313200 | 40849200 | 72385200 | 103921200
2027-05-19 20:00 | -1618.58 | 5.2775 | 56.2192 | 59.8258 | -474.359 |  | 2588 | 9316800 | 40852800 | 72388800 | 103924800
2027-05-20 21:00 | -2355.67 | 6.108 | 55.5659 | 59.8258 | -690.3787 |  | 2589 | 9320400 | 40856400 | 72392400 | 103928400
2027-05-21 22:00 | -3465.44 | 6.108 | 54.5152 | 59.8258 | -1015.6202 |  | 2590 | 9324000 | 40860000 | 72396000 | 103932000
2027-05-22 23:00 | -4155 | 6.108 | 53.7056 | 59.8258 | -1217.7103 |  | 2591 | 9327600 | 40863600 | 72399600 | 103935600
2027-05-24 | -4777.88 | 6.108 | 52.9372 | 59.8258 | -1400.2584 |  | 2592 | 9331200 | 40867200 | 72403200 | 103939200
2027-05-25 01:00 | -5003.55 | 6.108 | 52.516 | 59.8258 | -1466.3958 |  | 2593 | 9334800 | 40870800 | 72406800 | 103942800
2027-05-26 02:00 | -5542.04 | 6.108 | 51.9004 | 59.8258 | -1624.2116 |  | 2594 | 9338400 | 40874400 | 72410400 | 103946400
2027-05-27 03:00 | -5390.2 | 6.108 | 51.7794 | 59.8258 | -1579.7117 |  | 2595 | 9342000 | 40878000 | 72414000 | 103950000
2027-05-28 04:00 | -5413.75 | 6.108 | 51.6105 | 59.8258 | -1586.6135 |  | 2596 | 9345600 | 40881600 | 72417600 | 103953600
2027-05-29 05:00 | -5108.16 | 6.108 | 51.7104 | 59.8258 | -1497.0539 |  | 2597 | 9349200 | 40885200 | 72421200 | 103957200
2027-05-30 06:00 | -4717.55 | 6.108 | 51.9248 | 59.8258 | -1382.5774 |  | 2598 | 9352800 | 40888800 | 72424800 | 103960800
2027-05-31 07:00 | -3554.36 | 6.108 | 52.7903 | 59.8258 | -1041.6801 |  | 2599 | 9356400 | 40892400 | 72428400 | 103964400
2027-06-01 08:00 | -2854.45 | 6.108 | 53.4614 | 59.8258 | -836.5567 |  | 2600 | 9360000 | 40896000 | 72432000 | 103968000
2027-06-02 09:00 | -1338 | 4.1297 | 54.2723 | 59.8258 | -392.1291 |  | 2601 | 9363600 | 40899600 | 72435600 | 103971600
2027-06-03 10:00 | 163.595 | 1 | 56.0233 | 59.8258 | 47.945 |  | 2602 | 9367200 | 40903200 | 72439200 | 103975200
2027-06-04 11:00 | 2971.79 | 1 | 56.1392 | 59.8258 | 870.9457 |  | 2603 | 9370800 | 40906800 | 72442800 | 103978800
2027-06-05 12:00 | 2985.94 | 1 | 56.7357 | 59.8258 | 875.0926 |  | 2604 | 9374400 | 40910400 | 72446400 | 103982400
2027-06-06 13:00 | 3147.73 | 1 | 57.0742 | 59.8258 | 922.5086 |  | 2605 | 9378000 | 40914000 | 72450000 | 103986000
2027-06-07 14:00 | 3143.7 | 1 | 73.6598 | 59.8258 | 921.3275 |  | 2606 | 9381600 | 40917600 | 72453600 | 103989600
2027-06-08 15:00 | 5056.69 | 1.6045 | 72.2376 | 59.8258 | 1481.9695 |  | 2607 | 9385200 | 40921200 | 72457200 | 103993200
2027-06-09 16:00 | 5342.4 | 1.7336 | 72.3574 | 59.8258 | 1565.7029 |  | 2608 | 9388800 | 40924800 | 72460800 | 103996800
2027-06-10 17:00 | 5574.34 | 1.6877 | 73.6723 | 59.8258 | 1633.6778 |  | 2609 | 9392400 | 40928400 | 72464400 | 104000400
2027-06-11 18:00 | 3523.27 | 1.1679 | 72.6268 | 59.8258 | 1032.5685 |  | 2610 | 9396000 | 40932000 | 72468000 | 104004000
2027-06-12 19:00 | 2917.44 | 1 | 80.7666 | 59.8258 | 855.0173 |  | 2611 | 9399600 | 40935600 | 72471600 | 104007600
2027-06-13 20:00 | 0 | 0 | 58.7813 | 59.8258 | 0 |  | 2612 | 9403200 | 40939200 | 72475200 | 104011200
2027-06-14 21:00 | -615.775 | 2.1283 | 57.0973 | 59.8258 | -180.4658 |  | 2613 | 9406800 | 40942800 | 72478800 | 104014800
2027-06-15 22:00 | -1706.47 | 5.4531 | 56.7283 | 59.8258 | -500.117 |  | 2614 | 9410400 | 40946400 | 72482400 | 104018400
2027-06-16 23:00 | -2257.48 | 6.108 | 56.1608 | 59.8258 | -661.6021 |  | 2615 | 9414000 | 40950000 | 72486000 | 104022000
2027-06-18 | -2779.46 | 6.108 | 55.5205 | 59.8258 | -814.5793 |  | 2616 | 9417600 | 40953600 | 72489600 | 104025600
2027-06-19 01:00 | -3117.12 | 6.108 | 55.0306 | 59.8258 | -913.5377 |  | 2617 | 9421200 | 40957200 | 72493200 | 104029200
2027-06-20 02:00 | -3203.41 | 6.108 | 54.8023 | 59.8258 | -938.8268 |  | 2618 | 9424800 | 40960800 | 72496800 | 104032800
2027-06-21 03:00 | -3075.62 | 6.108 | 54.7515 | 59.8258 | -901.3752 |  | 2619 | 9428400 | 40964400 | 72500400 | 104036400
2027-06-22 04:00 | -2961.51 | 6.108 | 54.7461 | 59.8258 | -867.9329 |  | 2620 | 9432000 | 40968000 | 72504000 | 104040000
2027-06-23 05:00 | -2504.13 | 6.108 | 55.0168 | 59.8258 | -733.8881 |  | 2621 | 9435600 | 40971600 | 72507600 | 104043600
2027-06-24 06:00 | -2226.03 | 6.108 | 55.237 | 59.8258 | -652.385 |  | 2622 | 9439200 | 40975200 | 72511200 | 104047200
2027-06-25 07:00 | -1967.82 | 5.9624 | 55.4186 | 59.8258 | -576.7111 |  | 2623 | 9442800 | 40978800 | 72514800 | 104050800
2027-06-26 08:00 | -1964 | 5.9484 | 55.4748 | 59.8258 | -575.5916 |  | 2624 | 9446400 | 40982400 | 72518400 | 104054400
2027-06-27 09:00 | -1325.27 | 4.0049 | 55.4896 | 59.8258 | -388.3983 |  | 2625 | 9450000 | 40986000 | 72522000 | 104058000
2027-06-28 10:00 | -685.358 | 2.2671 | 55.7087 | 59.8258 | -200.8586 |  | 2626 | 9453600 | 40989600 | 72525600 | 104061600
2027-06-29 11:00 | 2449.51 | 1 | 56.9958 | 59.8258 | 717.8805 |  | 2627 | 9457200 | 40993200 | 72529200 | 104065200
2027-06-30 12:00 | 3120.44 | 1 | 57.414 | 59.8258 | 914.5107 |  | 2628 | 9460800 | 40996800 | 72532800 | 104068800
2027-07-01 13:00 | 3195.63 | 1 | 79.8602 | 59.8258 | 936.5467 |  | 2629 | 9464400 | 41000400 | 72536400 | 104072400
2027-07-02 14:00 | 3274.28 | 1 | 77.0264 | 59.8258 | 959.5967 |  | 2630 | 9468000 | 41004000 | 72540000 | 104076000
2027-07-03 15:00 | 4532.73 | 1.4037 | 73.1901 | 59.8258 | 1328.412 |  | 2631 | 9471600 | 41007600 | 72543600 | 104079600
2027-07-04 16:00 | 4793.24 | 1.5152 | 73.2177 | 59.8258 | 1404.76 |  | 2632 | 9475200 | 41011200 | 72547200 | 104083200
2027-07-05 17:00 | 4667.35 | 1.4607 | 73.5689 | 59.8258 | 1367.8653 |  | 2633 | 9478800 | 41014800 | 72550800 | 104086800
2027-07-06 18:00 | 3532.49 | 1.1309 | 73.373 | 59.8258 | 1035.2706 |  | 2634 | 9482400 | 41018400 | 72554400 | 104090400
2027-07-07 19:00 | 3057.62 | 1 | 81.1524 | 59.8258 | 896.1 |  | 2635 | 9486000 | 41022000 | 72558000 | 104094000
2027-07-08 20:00 | 0 | 0 | 59.0837 | 59.8258 | 0 |  | 2636 | 9489600 | 41025600 | 72561600 | 104097600
2027-07-09 21:00 | -334.167 | 1.3767 | 57.6001 | 59.8258 | -97.9347 |  | 2637 | 9493200 | 41029200 | 72565200 | 104101200
2027-07-10 22:00 | -1215.14 | 4.0339 | 57.1098 | 59.8258 | -356.1224 |  | 2638 | 9496800 | 41032800 | 72568800 | 104104800
2027-07-11 23:00 | -1821.92 | 5.6151 | 56.7575 | 59.8258 | -533.952 |  | 2639 | 9500400 | 41036400 | 72572400 | 104108400
2027-07-13 | -1957.38 | 5.8838 | 56.4747 | 59.8258 | -573.6515 |  | 2640 | 9504000 | 41040000 | 72576000 | 104112000
2027-07-14 01:00 | -2110.86 | 6.108 | 56.2299 | 59.8258 | -618.632 |  | 2641 | 9507600 | 41043600 | 72579600 | 104115600
2027-07-15 02:00 | -2104.75 | 6.108 | 56.1277 | 59.8258 | -616.8413 |  | 2642 | 9511200 | 41047200 | 72583200 | 104119200
2027-07-16 03:00 | -2085.75 | 6.108 | 56.0417 | 59.8258 | -611.273 |  | 2643 | 9514800 | 41050800 | 72586800 | 104122800
2027-07-17 04:00 | -2075.37 | 6.108 | 55.9734 | 59.8258 | -608.2309 |  | 2644 | 9518400 | 41054400 | 72590400 | 104126400
2027-07-18 05:00 | -2263.83 | 6.108 | 55.7672 | 59.8258 | -663.4631 |  | 2645 | 9522000 | 41058000 | 72594000 | 104130000
2027-07-19 06:00 | -1619.5 | 4.8686 | 55.8597 | 59.8258 | -474.6286 |  | 2646 | 9525600 | 41061600 | 72597600 | 104133600
2027-07-20 07:00 | -1309.6 | 4.0452 | 55.9211 | 59.8258 | -383.8059 |  | 2647 | 9529200 | 41065200 | 72601200 | 104137200
2027-07-21 08:00 | -2040.76 | 6.108 | 55.9427 | 59.8258 | -598.0877 |  | 2648 | 9532800 | 41068800 | 72604800 | 104140800
2027-07-22 09:00 | -1675.17 | 5.0294 | 55.8642 | 59.8258 | -490.9439 |  | 2649 | 9536400 | 41072400 | 72608400 | 104144400
2027-07-23 10:00 | -1116.44 | 3.4489 | 55.8997 | 59.8258 | -327.1963 |  | 2650 | 9540000 | 41076000 | 72612000 | 104148000
2027-07-24 11:00 | -674.068 | 2.2789 | 56.0839 | 59.8258 | -197.5498 |  | 2651 | 9543600 | 41079600 | 72615600 | 104151600
2027-07-25 12:00 | -353.538 | 1.4382 | 56.3663 | 59.8258 | -103.6118 |  | 2652 | 9547200 | 41083200 | 72619200 | 104155200
2027-07-26 13:00 | -164.33 | 0.9586 | 56.7544 | 59.8258 | -48.1604 |  | 2653 | 9550800 | 41086800 | 72622800 | 104158800
2027-07-27 14:00 | 1894.17 | 1 | 57.4356 | 59.8258 | 555.1264 |  | 2654 | 9554400 | 41090400 | 72626400 | 104162400
2027-07-28 15:00 | 2966.1 | 1 | 57.6382 | 59.8258 | 869.2781 |  | 2655 | 9558000 | 41094000 | 72630000 | 104166000
2027-07-29 16:00 | 3567.25 | 1.1389 | 72.5771 | 59.8258 | 1045.4578 |  | 2656 | 9561600 | 41097600 | 72633600 | 104169600
2027-07-30 17:00 | 3101.99 | 1 | 78.3152 | 59.8258 | 909.1035 |  | 2657 | 9565200 | 41101200 | 72637200 | 104173200
2027-07-31 18:00 | 3187.04 | 1 | 58.2784 | 59.8258 | 934.0292 |  | 2658 | 9568800 | 41104800 | 72640800 | 104176800
2027-08-01 19:00 | 674.531 | 1 | 58.6431 | 59.8258 | 197.6855 |  | 2659 | 9572400 | 41108400 | 72644400 | 104180400
2027-08-02 20:00 | -122.036 | 0.95164 | 57.9041 | 59.8258 | -35.7652 |  | 2660 | 9576000 | 41112000 | 72648000 | 104184000
2027-08-03 21:00 | -355.128 | 1.552 | 57.241 | 59.8258 | -104.0777 |  | 2661 | 9579600 | 41115600 | 72651600 | 104187600
2027-08-04 22:00 | -750.815 | 2.6641 | 56.8885 | 59.8258 | -220.0422 |  | 2662 | 9583200 | 41119200 | 72655200 | 104191200
2027-08-05 23:00 | -1981.3 | 6.108 | 56.5868 | 59.8258 | -580.6617 |  | 2663 | 9586800 | 41122800 | 72658800 | 104194800
2027-08-07 | -2392.82 | 6.108 | 56.0266 | 59.8258 | -701.2663 |  | 2664 | 9590400 | 41126400 | 72662400 | 104198400
2027-08-08 01:00 | -2611.61 | 6.108 | 55.6959 | 59.8258 | -765.3873 |  | 2665 | 9594000 | 41130000 | 72666000 | 104202000
2027-08-09 02:00 | -2793.47 | 6.108 | 55.4241 | 59.8258 | -818.6852 |  | 2666 | 9597600 | 41133600 | 72669600 | 104205600
2027-08-10 03:00 | -2691.76 | 6.108 | 55.3591 | 59.8258 | -788.877 |  | 2667 | 9601200 | 41137200 | 72673200 | 104209200
2027-08-11 04:00 | -2738.47 | 6.108 | 55.2165 | 59.8258 | -802.5663 |  | 2668 | 9604800 | 41140800 | 72676800 | 104212800
2027-08-12 05:00 | -2703.69 | 6.108 | 55.1621 | 59.8258 | -792.3733 |  | 2669 | 9608400 | 41144400 | 72680400 | 104216400
2027-08-13 06:00 | -1802.08 | 5.4669 | 55.6046 | 59.8258 | -528.1375 |  | 2670 | 9612000 | 41148000 | 72684000 | 104220000
2027-08-14 07:00 | -1285.73 | 3.9238 | 55.6906 | 59.8258 | -376.8103 |  | 2671 | 9615600 | 41151600 | 72687600 | 104223600
2027-08-15 08:00 | -1402.56 | 4.4253 | 55.8549 | 59.8258 | -411.0498 |  | 2672 | 9619200 | 41155200 | 72691200 | 104227200
2027-08-16 09:00 | -1010.81 | 3.194 | 55.8872 | 59.8258 | -296.2392 |  | 2673 | 9622800 | 41158800 | 72694800 | 104230800
2027-08-17 10:00 | 94.1302 | 1 | 57.4021 | 59.8258 | 27.5868 |  | 2674 | 9626400 | 41162400 | 72698400 | 104234400
2027-08-18 11:00 | 2220.16 | 1.0515 | 67.3067 | 59.8258 | 650.6647 |  | 2675 | 9630000 | 41166000 | 72702000 | 104238000
2027-08-19 12:00 | 4137.51 | 1.4951 | 70.6752 | 59.8258 | 1212.5845 |  | 2676 | 9633600 | 41169600 | 72705600 | 104241600
2027-08-20 13:00 | 4875.69 | 1.711 | 71.5254 | 59.8258 | 1428.9237 |  | 2677 | 9637200 | 41173200 | 72709200 | 104245200
2027-08-21 14:00 | 6211.83 | 2.106 | 72.3697 | 59.8258 | 1820.5077 |  | 2678 | 9640800 | 41176800 | 72712800 | 104248800
2027-08-22 15:00 | 6824.96 | 2.2115 | 73.439 | 59.8258 | 2000.1983 |  | 2679 | 9644400 | 41180400 | 72716400 | 104252400
2027-08-23 16:00 | 8764.22 | 2.9811 | 73.1614 | 59.8258 | 2568.5393 |  | 2680 | 9648000 | 41184000 | 72720000 | 104256000
2027-08-24 17:00 | 7716.57 | 2.4953 | 74.4067 | 59.8258 | 2261.5034 |  | 2681 | 9651600 | 41187600 | 72723600 | 104259600
2027-08-25 18:00 | 6022.74 | 1.9274 | 74.7792 | 59.8258 | 1765.0909 |  | 2682 | 9655200 | 41191200 | 72727200 | 104263200
2027-08-26 19:00 | 3841.74 | 1.1877 | 75.2695 | 59.8258 | 1125.9029 |  | 2683 | 9658800 | 41194800 | 72730800 | 104266800
2027-08-27 20:00 | 3142.14 | 1 | 80.6159 | 59.8258 | 920.8703 |  | 2684 | 9662400 | 41198400 | 72734400 | 104270400
2027-08-28 21:00 | 3090.2 | 1 | 59.8716 | 59.8258 | 905.6482 |  | 2685 | 9666000 | 41202000 | 72738000 | 104274000
2027-08-29 22:00 | 0 | 0 | 60.084 | 59.8258 | 0 |  | 2686 | 9669600 | 41205600 | 72741600 | 104277600
2027-08-30 23:00 | -1203.46 | 3.9411 | 58.2295 | 59.8258 | -352.6993 |  | 2687 | 9673200 | 41209200 | 72745200 | 104281200
2027-09-01 | -1807.07 | 5.5096 | 57.7053 | 59.8258 | -529.5999 |  | 2688 | 9676800 | 41212800 | 72748800 | 104284800
2027-09-02 01:00 | -2243.34 | 6.108 | 57.2398 | 59.8258 | -657.4581 |  | 2689 | 9680400 | 41216400 | 72752400 | 104288400
2027-09-03 02:00 | -2356.88 | 6.108 | 56.8865 | 59.8258 | -690.7333 |  | 2690 | 9684000 | 41220000 | 72756000 | 104292000
2027-09-04 03:00 | -2444.51 | 6.108 | 56.5761 | 59.8258 | -716.4152 |  | 2691 | 9687600 | 41223600 | 72759600 | 104295600
2027-09-05 04:00 | -2474.04 | 6.108 | 56.3676 | 59.8258 | -725.0696 |  | 2692 | 9691200 | 41227200 | 72763200 | 104299200
2027-09-06 05:00 | -2240.76 | 6.108 | 56.4001 | 59.8258 | -656.7019 |  | 2693 | 9694800 | 41230800 | 72766800 | 104302800
2027-09-07 06:00 | -1891.48 | 5.6462 | 56.4642 | 59.8258 | -554.3381 |  | 2694 | 9698400 | 41234400 | 72770400 | 104306400
2027-09-08 07:00 | -991.3 | 2.9884 | 56.4585 | 59.8258 | -290.5214 |  | 2695 | 9702000 | 41238000 | 72774000 | 104310000
2027-09-09 08:00 | -414.447 | 1.5393 | 56.834 | 59.8258 | -121.4624 |  | 2696 | 9705600 | 41241600 | 72777600 | 104313600
2027-09-10 09:00 | 2223.04 | 1 | 74.2511 | 59.8258 | 651.5087 |  | 2697 | 9709200 | 41245200 | 72781200 | 104317200
2027-09-11 10:00 | 4282.76 | 1.4424 | 72.1658 | 59.8258 | 1255.1531 |  | 2698 | 9712800 | 41248800 | 72784800 | 104320800
2027-09-12 11:00 | 5922.33 | 2.0965 | 72.0301 | 59.8258 | 1735.6636 |  | 2699 | 9716400 | 41252400 | 72788400 | 104324400
2027-09-13 12:00 | 6812.35 | 2.3947 | 72.6446 | 59.8258 | 1996.5027 |  | 2700 | 9720000 | 41256000 | 72792000 | 104328000
2027-09-14 13:00 | 7739.03 | 2.6283 | 73.5593 | 59.8258 | 2268.0858 |  | 2701 | 9723600 | 41259600 | 72795600 | 104331600
2027-09-15 14:00 | 8471.78 | 2.799 | 74.3878 | 59.8258 | 2482.8336 |  | 2702 | 9727200 | 41263200 | 72799200 | 104335200
2027-09-16 15:00 | 10095 | 3.25 | 75.1467 | 59.8258 | 2958.5525 |  | 2703 | 9730800 | 41266800 | 72802800 | 104338800
2027-09-17 16:00 | 10463.8 | 3.3216 | 75.8361 | 59.8258 | 3066.6371 |  | 2704 | 9734400 | 41270400 | 72806400 | 104342400
2027-09-18 17:00 | 10058.7 | 3.1708 | 76.3304 | 59.8258 | 2947.914 |  | 2705 | 9738000 | 41274000 | 72810000 | 104346000
2027-09-19 18:00 | 7949.84 | 2.4605 | 76.8588 | 59.8258 | 2329.8681 |  | 2706 | 9741600 | 41277600 | 72813600 | 104349600
2027-09-20 19:00 | 6005.18 | 1.8186 | 77.1549 | 59.8258 | 1759.9445 |  | 2707 | 9745200 | 41281200 | 72817200 | 104353200
2027-09-21 20:00 | 3286 | 1 | 78.5629 | 59.8258 | 963.0315 |  | 2708 | 9748800 | 41284800 | 72820800 | 104356800
2027-09-22 21:00 | 3145.64 | 1 | 61.1746 | 59.8258 | 921.8961 |  | 2709 | 9752400 | 41288400 | 72824400 | 104360400
2027-09-23 22:00 | 0 | 0 | 61.2198 | 59.8258 | 0 |  | 2710 | 9756000 | 41292000 | 72828000 | 104364000
2027-09-24 23:00 | -679.67 | 2.1618 | 59.2097 | 59.8258 | -199.1916 |  | 2711 | 9759600 | 41295600 | 72831600 | 104367600
2027-09-26 | -1017.85 | 3.3127 | 58.8104 | 59.8258 | -298.3024 |  | 2712 | 9763200 | 41299200 | 72835200 | 104371200
2027-09-27 01:00 | -1357.1 | 4.2037 | 58.4452 | 59.8258 | -397.7267 |  | 2713 | 9766800 | 41302800 | 72838800 | 104374800
2027-09-28 02:00 | -1511.59 | 4.5833 | 58.1702 | 59.8258 | -443.0033 |  | 2714 | 9770400 | 41306400 | 72842400 | 104378400
2027-09-29 03:00 | -1606.15 | 4.8391 | 57.9122 | 59.8258 | -470.7161 |  | 2715 | 9774000 | 41310000 | 72846000 | 104382000
2027-09-30 04:00 | -1731.46 | 5.1945 | 57.7328 | 59.8258 | -507.4408 |  | 2716 | 9777600 | 41313600 | 72849600 | 104385600
2027-10-01 05:00 | -1384.23 | 4.1457 | 57.5666 | 59.8258 | -405.6778 |  | 2717 | 9781200 | 41317200 | 72853200 | 104389200
2027-10-02 06:00 | -1082.38 | 3.3639 | 57.5434 | 59.8258 | -317.2143 |  | 2718 | 9784800 | 41320800 | 72856800 | 104392800
2027-10-03 07:00 | 0 | 0 | 58.9883 | 59.8258 | 0 |  | 2719 | 9788400 | 41324400 | 72860400 | 104396400
2027-10-04 08:00 | 1865.4 | 1 | 58.9441 | 59.8258 | 546.6948 |  | 2720 | 9792000 | 41328000 | 72864000 | 104400000
2027-10-05 09:00 | 2880.9 | 1 | 73.279 | 59.8258 | 844.3084 |  | 2721 | 9795600 | 41331600 | 72867600 | 104403600
2027-10-06 10:00 | 4922.41 | 1.6972 | 72.9557 | 59.8258 | 1442.616 |  | 2722 | 9799200 | 41335200 | 72871200 | 104407200
2027-10-07 11:00 | 6712 | 2.3334 | 73.2788 | 59.8258 | 1967.093 |  | 2723 | 9802800 | 41338800 | 72874800 | 104410800
2027-10-08 12:00 | 7983.72 | 2.6437 | 74.4462 | 59.8258 | 2339.7974 |  | 2724 | 9806400 | 41342400 | 72878400 | 104414400
2027-10-09 13:00 | 8857.57 | 2.9051 | 75.0635 | 59.8258 | 2595.8975 |  | 2725 | 9810000 | 41346000 | 72882000 | 104418000
2027-10-10 14:00 | 10009.6 | 3.2549 | 75.6037 | 59.8258 | 2933.5242 |  | 2726 | 9813600 | 41349600 | 72885600 | 104421600
2027-10-11 15:00 | 11638.8 | 3.7768 | 76.0793 | 59.8258 | 3410.9956 |  | 2727 | 9817200 | 41353200 | 72889200 | 104425200
2027-10-12 16:00 | 11751.6 | 3.806 | 76.6337 | 59.8258 | 3444.054 |  | 2728 | 9820800 | 41356800 | 72892800 | 104428800
2027-10-13 17:00 | 11452.5 | 3.6921 | 77.0731 | 59.8258 | 3356.3964 |  | 2729 | 9824400 | 41360400 | 72896400 | 104432400
2027-10-14 18:00 | 9347.6 | 2.9284 | 77.7529 | 59.8258 | 2739.5111 |  | 2730 | 9828000 | 41364000 | 72900000 | 104436000
2027-10-15 19:00 | 7324.44 | 2.2126 | 78.2732 | 59.8258 | 2146.5815 |  | 2731 | 9831600 | 41367600 | 72903600 | 104439600
2027-10-16 20:00 | 5092.8 | 1.4815 | 78.6637 | 59.8258 | 1492.5523 |  | 2732 | 9835200 | 41371200 | 72907200 | 104443200
2027-10-17 21:00 | 3656.57 | 1.1462 | 77.1746 | 59.8258 | 1071.6349 |  | 2733 | 9838800 | 41374800 | 72910800 | 104446800
2027-10-18 22:00 | 3068.49 | 1 | 61.9605 | 59.8258 | 899.2856 |  | 2734 | 9842400 | 41378400 | 72914400 | 104450400
2027-10-19 23:00 | 2753.66 | 1 | 61.7086 | 59.8258 | 807.0181 |  | 2735 | 9846000 | 41382000 | 72918000 | 104454000
2027-10-21 | -60.4041 | 0.75214 | 61.3755 | 59.8258 | -17.7027 |  | 2736 | 9849600 | 41385600 | 72921600 | 104457600
2027-10-22 01:00 | -405.714 | 1.6596 | 60.1063 | 59.8258 | -118.903 |  | 2737 | 9853200 | 41389200 | 72925200 | 104461200
2027-10-23 02:00 | -698.977 | 2.4212 | 59.5504 | 59.8258 | -204.8499 |  | 2738 | 9856800 | 41392800 | 72928800 | 104464800
2027-10-24 03:00 | -901.376 | 2.9394 | 59.2064 | 59.8258 | -264.1672 |  | 2739 | 9860400 | 41396400 | 72932400 | 104468400
2027-10-25 04:00 | -1097.34 | 3.4647 | 58.9123 | 59.8258 | -321.5986 |  | 2740 | 9864000 | 41400000 | 72936000 | 104472000
2027-10-26 05:00 | -759.519 | 2.4505 | 58.6959 | 59.8258 | -222.593 |  | 2741 | 9867600 | 41403600 | 72939600 | 104475600
2027-10-27 06:00 | -540.951 | 1.9196 | 58.7271 | 59.8258 | -158.5371 |  | 2742 | 9871200 | 41407200 | 72943200 | 104479200
2027-10-28 07:00 | 0 | 1 | 59.9614 | 59.8258 | 0 |  | 2743 | 9874800 | 41410800 | 72946800 | 104482800
2027-10-29 08:00 | 2766.86 | 1 | 59.7281 | 59.8258 | 810.8866 |  | 2744 | 9878400 | 41414400 | 72950400 | 104486400
2027-10-30 09:00 | 3155.05 | 1.0102 | 74.6556 | 59.8258 | 924.6539 |  | 2745 | 9882000 | 41418000 | 72954000 | 104490000
2027-10-31 10:00 | 5939.43 | 1.9142 | 74.7295 | 59.8258 | 1740.6751 |  | 2746 | 9885600 | 41421600 | 72957600 | 104493600
2027-11-01 11:00 | 7722.45 | 2.5711 | 74.7347 | 59.8258 | 2263.2267 |  | 2747 | 9889200 | 41425200 | 72961200 | 104497200
2027-11-02 12:00 | 8682.36 | 2.893 | 75.2757 | 59.8258 | 2544.5485 |  | 2748 | 9892800 | 41428800 | 72964800 | 104500800
2027-11-03 13:00 | 9521.46 | 3.097 | 76.0801 | 59.8258 | 2790.4645 |  | 2749 | 9896400 | 41432400 | 72968400 | 104504400
2027-11-04 14:00 | 10364.8 | 3.3623 | 76.5154 | 59.8258 | 3037.623 |  | 2750 | 9900000 | 41436000 | 72972000 | 104508000
2027-11-05 15:00 | 11938.1 | 3.8569 | 76.9804 | 59.8258 | 3498.7117 |  | 2751 | 9903600 | 41439600 | 72975600 | 104511600
2027-11-06 16:00 | 11986.3 | 3.8642 | 77.5002 | 59.8258 | 3512.8378 |  | 2752 | 9907200 | 41443200 | 72979200 | 104515200
2027-11-07 17:00 | 11679.8 | 3.685 | 78.1484 | 59.8258 | 3423.0115 |  | 2753 | 9910800 | 41446800 | 72982800 | 104518800
2027-11-08 18:00 | 9513.61 | 2.993 | 78.4334 | 59.8258 | 2788.1639 |  | 2754 | 9914400 | 41450400 | 72986400 | 104522400
2027-11-09 19:00 | 7417.61 | 2.2937 | 78.6456 | 59.8258 | 2173.8869 |  | 2755 | 9918000 | 41454000 | 72990000 | 104526000
2027-11-10 20:00 | 4717.11 | 1.443 | 78.5888 | 59.8258 | 1382.4485 |  | 2756 | 9921600 | 41457600 | 72993600 | 104529600
2027-11-11 21:00 | 3249.1 | 1 | 79.6435 | 59.8258 | 952.2172 |  | 2757 | 9925200 | 41461200 | 72997200 | 104533200
2027-11-12 22:00 | 3053.97 | 1 | 62.5134 | 59.8258 | 895.0303 |  | 2758 | 9928800 | 41464800 | 73000800 | 104536800
2027-11-13 23:00 | 0 | 0 | 62.5052 | 59.8258 | 0 |  | 2759 | 9932400 | 41468400 | 73004400 | 104540400
2027-11-15 | -454.968 | 1.663 | 60.6625 | 59.8258 | -133.338 |  | 2760 | 9936000 | 41472000 | 73008000 | 104544000
2027-11-16 01:00 | -811.913 | 2.7214 | 60.1222 | 59.8258 | -237.9482 |  | 2761 | 9939600 | 41475600 | 73011600 | 104547600
2027-11-17 02:00 | -1105.23 | 3.4715 | 59.74 | 59.8258 | -323.9109 |  | 2762 | 9943200 | 41479200 | 73015200 | 104551200
2027-11-18 03:00 | -1273.52 | 3.8962 | 59.4229 | 59.8258 | -373.2319 |  | 2763 | 9946800 | 41482800 | 73018800 | 104554800
2027-11-19 04:00 | -1231.67 | 3.7488 | 59.1473 | 59.8258 | -360.9668 |  | 2764 | 9950400 | 41486400 | 73022400 | 104558400
2027-11-20 05:00 | -910.697 | 2.8467 | 59.0133 | 59.8258 | -266.8989 |  | 2765 | 9954000 | 41490000 | 73026000 | 104562000
2027-11-21 06:00 | -610.818 | 2.0743 | 59.0357 | 59.8258 | -179.0131 |  | 2766 | 9957600 | 41493600 | 73029600 | 104565600
2027-11-22 07:00 | 1845.78 | 1 | 60.176 | 59.8258 | 540.9447 |  | 2767 | 9961200 | 41497200 | 73033200 | 104569200
2027-11-23 08:00 | 2917.28 | 1 | 60.3569 | 59.8258 | 854.9704 |  | 2768 | 9964800 | 41500800 | 73036800 | 104572800
2027-11-24 09:00 | 3934.17 | 1.2736 | 75.0645 | 59.8258 | 1152.9914 |  | 2769 | 9968400 | 41504400 | 73040400 | 104576400
2027-11-25 10:00 | 6489.96 | 2.2272 | 74.464 | 59.8258 | 1902.0195 |  | 2770 | 9972000 | 41508000 | 73044000 | 104580000
2027-11-26 11:00 | 8446.59 | 2.8763 | 75.0789 | 59.8258 | 2475.4512 |  | 2771 | 9975600 | 41511600 | 73047600 | 104583600
2027-11-27 12:00 | 9642.79 | 3.1531 | 76.22 | 59.8258 | 2826.0228 |  | 2772 | 9979200 | 41515200 | 73051200 | 104587200
2027-11-28 13:00 | 10282.1 | 3.3207 | 76.8841 | 59.8258 | 3013.386 |  | 2773 | 9982800 | 41518800 | 73054800 | 104590800
2027-11-29 14:00 | 10938.9 | 3.5135 | 77.3728 | 59.8258 | 3205.8751 |  | 2774 | 9986400 | 41522400 | 73058400 | 104594400
2027-11-30 15:00 | 12485.8 | 3.989 | 77.832 | 59.8258 | 3659.2268 |  | 2775 | 9990000 | 41526000 | 73062000 | 104598000
2027-12-01 16:00 | 12457.7 | 4.0009 | 78.2383 | 59.8258 | 3650.9915 |  | 2776 | 9993600 | 41529600 | 73065600 | 104601600
2027-12-02 17:00 | 12171.4 | 3.8678 | 78.7138 | 59.8258 | 3567.0852 |  | 2777 | 9997200 | 41533200 | 73069200 | 104605200
2027-12-03 18:00 | 10198.6 | 3.1948 | 79.1526 | 59.8258 | 2988.9146 |  | 2778 | 10000800 | 41536800 | 73072800 | 104608800
2027-12-04 19:00 | 8034.12 | 2.5226 | 79.0808 | 59.8258 | 2354.5681 |  | 2779 | 10004400 | 41540400 | 73076400 | 104612400
2027-12-05 20:00 | 5453.75 | 1.6056 | 79.8367 | 59.8258 | 1598.3363 |  | 2780 | 10008000 | 41544000 | 73080000 | 104616000
2027-12-06 21:00 | 3897.88 | 1.1735 | 79.0781 | 59.8258 | 1142.3559 |  | 2781 | 10011600 | 41547600 | 73083600 | 104619600
2027-12-07 22:00 | 3121.25 | 1 | 63.1891 | 59.8258 | 914.7481 |  | 2782 | 10015200 | 41551200 | 73087200 | 104623200
2027-12-08 23:00 | 0 | 0 | 63.118 | 59.8258 | 0 |  | 2783 | 10018800 | 41554800 | 73090800 | 104626800
2027-12-10 | -460.322 | 1.7118 | 61.242 | 59.8258 | -134.9071 |  | 2784 | 10022400 | 41558400 | 73094400 | 104630400
2027-12-11 01:00 | -702.222 | 2.3927 | 60.6744 | 59.8258 | -205.801 |  | 2785 | 10026000 | 41562000 | 73098000 | 104634000
2027-12-12 02:00 | -968.278 | 3.0914 | 60.2844 | 59.8258 | -283.7743 |  | 2786 | 10029600 | 41565600 | 73101600 | 104637600
2027-12-13 03:00 | -1103.43 | 3.4224 | 59.9549 | 59.8258 | -323.3834 |  | 2787 | 10033200 | 41569200 | 73105200 | 104641200
2027-12-14 04:00 | -1068.92 | 3.3044 | 59.6853 | 59.8258 | -313.2695 |  | 2788 | 10036800 | 41572800 | 73108800 | 104644800
2027-12-15 05:00 | -944.565 | 2.9672 | 59.5366 | 59.8258 | -276.8247 |  | 2789 | 10040400 | 41576400 | 73112400 | 104648400
2027-12-16 06:00 | -586.694 | 1.9825 | 59.5156 | 59.8258 | -171.943 |  | 2790 | 10044000 | 41580000 | 73116000 | 104652000
2027-12-17 07:00 | 2358.97 | 1 | 60.595 | 59.8258 | 691.3459 |  | 2791 | 10047600 | 41583600 | 73119600 | 104655600
2027-12-18 08:00 | 2190.44 | 1 | 60.9394 | 59.8258 | 641.9546 |  | 2792 | 10051200 | 41587200 | 73123200 | 104659200
2027-12-19 09:00 | 3701.34 | 1.3044 | 74.2763 | 59.8258 | 1084.7557 |  | 2793 | 10054800 | 41590800 | 73126800 | 104662800
2027-12-20 10:00 | 6187.6 | 2.1444 | 74.6779 | 59.8258 | 1813.4066 |  | 2794 | 10058400 | 41594400 | 73130400 | 104666400
2027-12-21 11:00 | 7842.12 | 2.7749 | 74.8994 | 59.8258 | 2298.2985 |  | 2795 | 10062000 | 41598000 | 73134000 | 104670000
2027-12-22 12:00 | 9048.03 | 2.9944 | 76.3089 | 59.8258 | 2651.7158 |  | 2796 | 10065600 | 41601600 | 73137600 | 104673600
2027-12-23 13:00 | 9833.29 | 3.1773 | 77.0709 | 59.8258 | 2881.8528 |  | 2797 | 10069200 | 41605200 | 73141200 | 104677200
2027-12-24 14:00 | 10576.3 | 3.457 | 77.3186 | 59.8258 | 3099.6076 |  | 2798 | 10072800 | 41608800 | 73144800 | 104680800
2027-12-25 15:00 | 12173 | 3.9206 | 77.8994 | 59.8258 | 3567.5541 |  | 2799 | 10076400 | 41612400 | 73148400 | 104684400
2027-12-26 16:00 | 12434.6 | 3.9935 | 78.4088 | 59.8258 | 3644.2215 |  | 2800 | 10080000 | 41616000 | 73152000 | 104688000
2027-12-27 17:00 | 11355.8 | 3.5861 | 79.0102 | 59.8258 | 3328.0565 |  | 2801 | 10083600 | 41619600 | 73155600 | 104691600
2027-12-28 18:00 | 9192.48 | 2.952 | 78.9079 | 59.8258 | 2694.0499 |  | 2802 | 10087200 | 41623200 | 73159200 | 104695200
2027-12-29 19:00 | 7004.37 | 2.2432 | 78.8144 | 59.8258 | 2052.7782 |  | 2803 | 10090800 | 41626800 | 73162800 | 104698800
2027-12-30 20:00 | 4387.91 | 1.3852 | 78.7647 | 59.8258 | 1285.9695 |  | 2804 | 10094400 | 41630400 | 73166400 | 104702400
2027-12-31 21:00 | 3377.78 | 1.0756 | 78.1775 | 59.8258 | 989.9296 |  | 2805 | 10098000 | 41634000 | 73170000 | 104706000
2028-01-01 22:00 | 3034.14 | 1 | 63.1487 | 59.8258 | 889.2187 |  | 2806 | 10101600 | 41637600 | 73173600 | 104709600
2028-01-02 23:00 | 3010.82 | 1 | 62.8871 | 59.8258 | 882.3842 |  | 2807 | 10105200 | 41641200 | 73177200 | 104713200
2028-01-04 | 0 | 0 | 62.9767 | 59.8258 | 0 |  | 2808 | 10108800 | 41644800 | 73180800 | 104716800
2028-01-05 01:00 | -254.938 | 1.1389 | 61.416 | 59.8258 | -74.715 |  | 2809 | 10112400 | 41648400 | 73184400 | 104720400
2028-01-06 02:00 | -334.553 | 1.4136 | 61.0149 | 59.8258 | -98.0478 |  | 2810 | 10116000 | 41652000 | 73188000 | 104724000
2028-01-07 03:00 | -557.431 | 2.0165 | 60.604 | 59.8258 | -163.3669 |  | 2811 | 10119600 | 41655600 | 73191600 | 104727600
2028-01-08 04:00 | -672.206 | 2.2928 | 60.2859 | 59.8258 | -197.0041 |  | 2812 | 10123200 | 41659200 | 73195200 | 104731200
2028-01-09 05:00 | -727.428 | 2.4303 | 60.0262 | 59.8258 | -213.1881 |  | 2813 | 10126800 | 41662800 | 73198800 | 104734800
2028-01-10 06:00 | -220.499 | 0.98935 | 60.2397 | 59.8258 | -64.6219 |  | 2814 | 10130400 | 41666400 | 73202400 | 104738400
2028-01-11 07:00 | 222.716 | 1 | 61.1892 | 59.8258 | 65.2716 |  | 2815 | 10134000 | 41670000 | 73206000 | 104742000
2028-01-12 08:00 | -621.678 | 2.2888 | 59.97 | 59.8258 | -182.1958 |  | 2816 | 10137600 | 41673600 | 73209600 | 104745600
2028-01-13 09:00 | -421.516 | 1.5734 | 59.8359 | 59.8258 | -123.5341 |  | 2817 | 10141200 | 41677200 | 73213200 | 104749200
2028-01-14 10:00 | 2602.34 | 1 | 78.3705 | 59.8258 | 762.6706 |  | 2818 | 10144800 | 41680800 | 73216800 | 104752800
2028-01-15 11:00 | 3000.93 | 1 | 75.8233 | 59.8258 | 879.4858 |  | 2819 | 10148400 | 41684400 | 73220400 | 104756400
2028-01-16 12:00 | 3044.63 | 1 | 77.5295 | 59.8258 | 892.293 |  | 2820 | 10152000 | 41688000 | 73224000 | 104760000
2028-01-17 13:00 | 751.427 | 1 | 61.4351 | 59.8258 | 220.2215 |  | 2821 | 10155600 | 41691600 | 73227600 | 104763600
2028-01-18 14:00 | -21.468 | 0.64693 | 61.0867 | 59.8258 | -6.2916 |  | 2822 | 10159200 | 41695200 | 73231200 | 104767200
2028-01-19 15:00 | 2641.14 | 1 | 60.7444 | 59.8258 | 774.0417 |  | 2823 | 10162800 | 41698800 | 73234800 | 104770800
2028-01-20 16:00 | 2972.55 | 1.1716 | 72.77 | 59.8258 | 871.1684 |  | 2824 | 10166400 | 41702400 | 73238400 | 104774400
2028-01-21 17:00 | 2969.63 | 1 | 84.4637 | 59.8258 | 870.3126 |  | 2825 | 10170000 | 41706000 | 73242000 | 104778000
2028-01-22 18:00 | 3044.22 | 1 | 60.9135 | 59.8258 | 892.1728 |  | 2826 | 10173600 | 41709600 | 73245600 | 104781600
2028-01-23 19:00 | 0 | 0 | 61.2453 | 59.8258 | 0 |  | 2827 | 10177200 | 41713200 | 73249200 | 104785200
2028-01-24 20:00 | -169.349 | 0.96736 | 60.1273 | 59.8258 | -49.6313 |  | 2828 | 10180800 | 41716800 | 73252800 | 104788800
2028-01-25 21:00 | -725.591 | 2.556 | 59.4128 | 59.8258 | -212.6497 |  | 2829 | 10184400 | 41720400 | 73256400 | 104792400
2028-01-26 22:00 | -1285.43 | 4.0362 | 59.0415 | 59.8258 | -376.7223 |  | 2830 | 10188000 | 41724000 | 73260000 | 104796000
2028-01-27 23:00 | -2834.42 | 6.108 | 58.1314 | 59.8258 | -830.6865 |  | 2831 | 10191600 | 41727600 | 73263600 | 104799600
2028-01-29 | -3283.05 | 6.108 | 57.4067 | 59.8258 | -962.167 |  | 2832 | 10195200 | 41731200 | 73267200 | 104803200
2028-01-30 01:00 | -3410.84 | 6.108 | 57.0667 | 59.8258 | -999.6185 |  | 2833 | 10198800 | 41734800 | 73270800 | 104806800
2028-01-31 02:00 | -3645.61 | 6.108 | 56.7226 | 59.8258 | -1068.4228 |  | 2834 | 10202400 | 41738400 | 73274400 | 104810400
2028-02-01 03:00 | -3751.48 | 6.108 | 56.4497 | 59.8258 | -1099.4503 |  | 2835 | 10206000 | 41742000 | 73278000 | 104814000
2028-02-02 04:00 | -3698.53 | 6.108 | 56.3089 | 59.8258 | -1083.9321 |  | 2836 | 10209600 | 41745600 | 73281600 | 104817600
2028-02-03 05:00 | -3796.67 | 6.108 | 56.1113 | 59.8258 | -1112.6941 |  | 2837 | 10213200 | 41749200 | 73285200 | 104821200
2028-02-04 06:00 | -2749.1 | 6.108 | 56.7631 | 59.8258 | -805.6817 |  | 2838 | 10216800 | 41752800 | 73288800 | 104824800
2028-02-05 07:00 | -2103.06 | 6.108 | 57.2874 | 59.8258 | -616.346 |  | 2839 | 10220400 | 41756400 | 73292400 | 104828400
2028-02-06 08:00 | -2233.14 | 6.108 | 57.2717 | 59.8258 | -654.4687 |  | 2840 | 10224000 | 41760000 | 73296000 | 104832000
2028-02-07 09:00 | -1582.59 | 4.6573 | 57.3799 | 59.8258 | -463.8113 |  | 2841 | 10227600 | 41763600 | 73299600 | 104835600
2028-02-08 10:00 | -610.847 | 1.9339 | 57.5281 | 59.8258 | -179.0216 |  | 2842 | 10231200 | 41767200 | 73303200 | 104839200
2028-02-09 11:00 | 1647.29 | 1 | 58.9854 | 59.8258 | 482.773 |  | 2843 | 10234800 | 41770800 | 73306800 | 104842800
2028-02-10 12:00 | 3172.09 | 1 | 59.2082 | 59.8258 | 929.6478 |  | 2844 | 10238400 | 41774400 | 73310400 | 104846400
2028-02-11 13:00 | 3257.3 | 1 | 80.4608 | 59.8258 | 954.6204 |  | 2845 | 10242000 | 41778000 | 73314000 | 104850000
2028-02-12 14:00 | 4330.37 | 1.3295 | 75.0147 | 59.8258 | 1269.1062 |  | 2846 | 10245600 | 41781600 | 73317600 | 104853600
2028-02-13 15:00 | 4677.64 | 1.5515 | 74.2254 | 59.8258 | 1370.881 |  | 2847 | 10249200 | 41785200 | 73321200 | 104857200
2028-02-14 16:00 | 7488.41 | 2.4769 | 74.5167 | 59.8258 | 2194.6363 |  | 2848 | 10252800 | 41788800 | 73324800 | 104860800
2028-02-15 17:00 | 6583.86 | 2.1399 | 75.31 | 59.8258 | 1929.5389 |  | 2849 | 10256400 | 41792400 | 73328400 | 104864400
2028-02-16 18:00 | 5066.57 | 1.5503 | 76.403 | 59.8258 | 1484.8651 |  | 2850 | 10260000 | 41796000 | 73332000 | 104868000
2028-02-17 19:00 | 3429.05 | 1.051 | 76.3635 | 59.8258 | 1004.9554 |  | 2851 | 10263600 | 41799600 | 73335600 | 104871600
2028-02-18 20:00 | 3125.3 | 1 | 61.0314 | 59.8258 | 915.935 |  | 2852 | 10267200 | 41803200 | 73339200 | 104875200
2028-02-19 21:00 | 3130.49 | 1 | 60.9993 | 59.8258 | 917.4561 |  | 2853 | 10270800 | 41806800 | 73342800 | 104878800
2028-02-20 22:00 | 3081.82 | 1 | 60.9689 | 59.8258 | 903.1923 |  | 2854 | 10274400 | 41810400 | 73346400 | 104882400
2028-02-21 23:00 | -844.567 | 2.9405 | 59.9053 | 59.8258 | -247.5182 |  | 2855 | 10278000 | 41814000 | 73350000 | 104886000
2028-02-23 | -1111.39 | 3.4919 | 59.2361 | 59.8258 | -325.7163 |  | 2856 | 10281600 | 41817600 | 73353600 | 104889600
2028-02-24 01:00 | -1441.92 | 4.4072 | 58.8965 | 59.8258 | -422.585 |  | 2857 | 10285200 | 41821200 | 73357200 | 104893200
2028-02-25 02:00 | -1585.72 | 4.7491 | 58.668 | 59.8258 | -464.7287 |  | 2858 | 10288800 | 41824800 | 73360800 | 104896800
2028-02-26 03:00 | -1457.41 | 4.354 | 58.4711 | 59.8258 | -427.1247 |  | 2859 | 10292400 | 41828400 | 73364400 | 104900400
2028-02-27 04:00 | -1233.55 | 3.7499 | 58.3104 | 59.8258 | -361.5178 |  | 2860 | 10296000 | 41832000 | 73368000 | 104904000
2028-02-28 05:00 | -461.428 | 1.5722 | 58.4121 | 59.8258 | -135.2312 |  | 2861 | 10299600 | 41835600 | 73371600 | 104907600
2028-02-29 06:00 | -308.071 | 1.336 | 58.7462 | 59.8258 | -90.2867 |  | 2862 | 10303200 | 41839200 | 73375200 | 104911200
2028-03-01 07:00 | 512.706 | 1 | 59.7916 | 59.8258 | 150.2593 |  | 2863 | 10306800 | 41842800 | 73378800 | 104914800
2028-03-02 08:00 | 1704.22 | 1 | 59.8033 | 59.8258 | 499.4576 |  | 2864 | 10310400 | 41846400 | 73382400 | 104918400
2028-03-03 09:00 | 2777.14 | 1 | 59.9269 | 59.8258 | 813.8994 |  | 2865 | 10314000 | 41850000 | 73386000 | 104922000
2028-03-04 10:00 | 3091.07 | 1 | 78.7391 | 59.8258 | 905.9032 |  | 2866 | 10317600 | 41853600 | 73389600 | 104925600
2028-03-05 11:00 | 3896.77 | 1.2027 | 75.4125 | 59.8258 | 1142.0306 |  | 2867 | 10321200 | 41857200 | 73393200 | 104929200
2028-03-06 12:00 | 4486.27 | 1.3812 | 75.6937 | 59.8258 | 1314.7959 |  | 2868 | 10324800 | 41860800 | 73396800 | 104932800
2028-03-07 13:00 | 5620.39 | 1.7141 | 76.079 | 59.8258 | 1647.1737 |  | 2869 | 10328400 | 41864400 | 73400400 | 104936400
2028-03-08 14:00 | 5908.94 | 1.8995 | 75.6217 | 59.8258 | 1731.7394 |  | 2870 | 10332000 | 41868000 | 73404000 | 104940000
2028-03-09 15:00 | 8201.37 | 2.803 | 74.9967 | 59.8258 | 2403.5843 |  | 2871 | 10335600 | 41871600 | 73407600 | 104943600
2028-03-10 16:00 | 8970.94 | 2.9977 | 75.7596 | 59.8258 | 2629.123 |  | 2872 | 10339200 | 41875200 | 73411200 | 104947200
2028-03-11 17:00 | 9192.51 | 2.9851 | 76.5583 | 59.8258 | 2694.0587 |  | 2873 | 10342800 | 41878800 | 73414800 | 104950800
2028-03-12 18:00 | 7804.96 | 2.4545 | 77.3327 | 59.8258 | 2287.408 |  | 2874 | 10346400 | 41882400 | 73418400 | 104954400
2028-03-13 19:00 | 6422.75 | 1.8911 | 78.3966 | 59.8258 | 1882.3222 |  | 2875 | 10350000 | 41886000 | 73422000 | 104958000
2028-03-14 20:00 | 3768.28 | 1.0952 | 78.5474 | 59.8258 | 1104.3739 |  | 2876 | 10353600 | 41889600 | 73425600 | 104961600
2028-03-15 21:00 | 3255.88 | 1 | 84.8015 | 59.8258 | 954.2042 |  | 2877 | 10357200 | 41893200 | 73429200 | 104965200
2028-03-16 22:00 | 0 | 0 | 62.2232 | 59.8258 | 0 |  | 2878 | 10360800 | 41896800 | 73432800 | 104968800
2028-03-17 23:00 | -293.687 | 1.3207 | 60.6495 | 59.8258 | -86.0712 |  | 2879 | 10364400 | 41900400 | 73436400 | 104972400
2028-03-19 | -341.205 | 1.4295 | 60.2127 | 59.8258 | -99.9973 |  | 2880 | 10368000 | 41904000 | 73440000 | 104976000
2028-03-20 01:00 | -571.24 | 2.0727 | 59.8262 | 59.8258 | -167.4139 |  | 2881 | 10371600 | 41907600 | 73443600 | 104979600
2028-03-21 02:00 | -730.615 | 2.4735 | 59.5586 | 59.8258 | -214.1221 |  | 2882 | 10375200 | 41911200 | 73447200 | 104983200
2028-03-22 03:00 | -808.298 | 2.6648 | 59.3232 | 59.8258 | -236.8888 |  | 2883 | 10378800 | 41914800 | 73450800 | 104986800
2028-03-23 04:00 | -789.294 | 2.5969 | 59.1917 | 59.8258 | -231.3192 |  | 2884 | 10382400 | 41918400 | 73454400 | 104990400
2028-03-24 05:00 | -579.71 | 2.0068 | 59.1434 | 59.8258 | -169.8962 |  | 2885 | 10386000 | 41922000 | 73458000 | 104994000
2028-03-25 06:00 | 0 | 1 | 60.3943 | 59.8258 | 0 |  | 2886 | 10389600 | 41925600 | 73461600 | 104997600
2028-03-26 07:00 | 1914.94 | 1 | 60.2267 | 59.8258 | 561.2135 |  | 2887 | 10393200 | 41929200 | 73465200 | 105001200
2028-03-27 08:00 | 2757.57 | 1 | 60.4024 | 59.8258 | 808.164 |  | 2888 | 10396800 | 41932800 | 73468800 | 105004800
2028-03-28 09:00 | 3896.23 | 1.2436 | 75.2428 | 59.8258 | 1141.8723 |  | 2889 | 10400400 | 41936400 | 73472400 | 105008400
2028-03-29 10:00 | 5650.01 | 1.817 | 75.3829 | 59.8258 | 1655.8545 |  | 2890 | 10404000 | 41940000 | 73476000 | 105012000
2028-03-30 11:00 | 6045.07 | 1.8445 | 76.5781 | 59.8258 | 1771.6351 |  | 2891 | 10407600 | 41943600 | 73479600 | 105015600
2028-03-31 12:00 | 4968.9 | 1.4737 | 77.3336 | 59.8258 | 1456.2408 |  | 2892 | 10411200 | 41947200 | 73483200 | 105019200
2028-04-01 13:00 | 3730.77 | 1.1432 | 76.8845 | 59.8258 | 1093.3808 |  | 2893 | 10414800 | 41950800 | 73486800 | 105022800
2028-04-02 14:00 | 4211.6 | 1.2583 | 77.1628 | 59.8258 | 1234.2981 |  | 2894 | 10418400 | 41954400 | 73490400 | 105026400
2028-04-03 15:00 | 5478.17 | 1.7586 | 76.1213 | 59.8258 | 1605.4931 |  | 2895 | 10422000 | 41958000 | 73494000 | 105030000
2028-04-04 16:00 | 6563.02 | 2.2134 | 75.5932 | 59.8258 | 1923.4313 |  | 2896 | 10425600 | 41961600 | 73497600 | 105033600
2028-04-05 17:00 | 6692.69 | 2.1168 | 76.7056 | 59.8258 | 1961.4338 |  | 2897 | 10429200 | 41965200 | 73501200 | 105037200
2028-04-06 18:00 | 5748 | 1.7583 | 77.3592 | 59.8258 | 1684.5725 |  | 2898 | 10432800 | 41968800 | 73504800 | 105040800
2028-04-07 19:00 | 4628.74 | 1.424 | 77.2895 | 59.8258 | 1356.5498 |  | 2899 | 10436400 | 41972400 | 73508400 | 105044400
2028-04-08 20:00 | 3129 | 1 | 84.2329 | 59.8258 | 917.0194 |  | 2900 | 10440000 | 41976000 | 73512000 | 105048000
2028-04-09 21:00 | 3175.34 | 1 | 61.8223 | 59.8258 | 930.6003 |  | 2901 | 10443600 | 41979600 | 73515600 | 105051600
2028-04-10 22:00 | 163.573 | 1 | 61.9714 | 59.8258 | 47.9385 |  | 2902 | 10447200 | 41983200 | 73519200 | 105055200
2028-04-11 23:00 | 494.422 | 1 | 61.4562 | 59.8258 | 144.9008 |  | 2903 | 10450800 | 41986800 | 73522800 | 105058800
2028-04-13 | 1018.74 | 1 | 61.1783 | 59.8258 | 298.5632 |  | 2904 | 10454400 | 41990400 | 73526400 | 105062400
2028-04-14 01:00 | 0 | 0 | 61.2365 | 59.8258 | 0 |  | 2905 | 10458000 | 41994000 | 73530000 | 105066000
2028-04-15 02:00 | 3525.21 | 1 | 60.7411 | 59.8258 | 1033.1371 |  | 2906 | 10461600 | 41997600 | 73533600 | 105069600
2028-04-16 03:00 | 3585.4 | 1 | 61.0606 | 59.8258 | 1050.777 |  | 2907 | 10465200 | 42001200 | 73537200 | 105073200
2028-04-17 04:00 | 3468.52 | 1 | 61.2951 | 59.8258 | 1016.5229 |  | 2908 | 10468800 | 42004800 | 73540800 | 105076800
2028-04-18 05:00 | 3279.54 | 1 | 61.3826 | 59.8258 | 961.1383 |  | 2909 | 10472400 | 42008400 | 73544400 | 105080400
2028-04-19 06:00 | 3253.49 | 1 | 84.9274 | 59.8258 | 953.5038 |  | 2910 | 10476000 | 42012000 | 73548000 | 105084000
2028-04-20 07:00 | 3393.6 | 1 | 80.0465 | 59.8258 | 994.566 |  | 2911 | 10479600 | 42015600 | 73551600 | 105087600
2028-04-21 08:00 | 3221.92 | 1 | 78.0366 | 59.8258 | 944.2515 |  | 2912 | 10483200 | 42019200 | 73555200 | 105091200
2028-04-22 09:00 | 3198.34 | 1 | 77.1904 | 59.8258 | 937.3409 |  | 2913 | 10486800 | 42022800 | 73558800 | 105094800
2028-04-23 10:00 | 3247.7 | 1.0386 | 76.1078 | 59.8258 | 951.8069 |  | 2914 | 10490400 | 42026400 | 73562400 | 105098400
2028-04-24 11:00 | 4003.5 | 1.2516 | 76.4513 | 59.8258 | 1173.31 |  | 2915 | 10494000 | 42030000 | 73566000 | 105102000
2028-04-25 12:00 | 4741.88 | 1.4572 | 76.8152 | 59.8258 | 1389.7078 |  | 2916 | 10497600 | 42033600 | 73569600 | 105105600
2028-04-26 13:00 | 6611.09 | 2.1816 | 75.968 | 59.8258 | 1937.5192 |  | 2917 | 10501200 | 42037200 | 73573200 | 105109200
2028-04-27 14:00 | 6803.77 | 2.3239 | 75.8338 | 59.8258 | 1993.9882 |  | 2918 | 10504800 | 42040800 | 73576800 | 105112800
2028-04-28 15:00 | 7478.19 | 2.4446 | 76.6411 | 59.8258 | 2191.6411 |  | 2919 | 10508400 | 42044400 | 73580400 | 105116400
2028-04-29 16:00 | 7735.91 | 2.5028 | 77.0007 | 59.8258 | 2267.1714 |  | 2920 | 10512000 | 42048000 | 73584000 | 105120000
2028-04-30 17:00 | 7648.8 | 2.4188 | 77.5179 | 59.8258 | 2241.642 |  | 2921 | 10515600 | 42051600 | 73587600 | 105123600
2028-05-01 18:00 | 5920.5 | 1.7233 | 78.9114 | 59.8258 | 1735.1273 |  | 2922 | 10519200 | 42055200 | 73591200 | 105127200
2028-05-02 19:00 | 3962.21 | 1.2517 | 77.5522 | 59.8258 | 1161.2091 |  | 2923 | 10522800 | 42058800 | 73594800 | 105130800
2028-05-03 20:00 | 3088.44 | 1 | 62.5307 | 59.8258 | 905.1324 |  | 2924 | 10526400 | 42062400 | 73598400 | 105134400
2028-05-04 21:00 | 3153.35 | 1 | 62.2905 | 59.8258 | 924.1557 |  | 2925 | 10530000 | 42066000 | 73602000 | 105138000
2028-05-05 22:00 | -507.145 | 1.957 | 61.2899 | 59.8258 | -148.6295 |  | 2926 | 10533600 | 42069600 | 73605600 | 105141600
2028-05-06 23:00 | -840.988 | 2.7652 | 60.5107 | 59.8258 | -246.4693 |  | 2927 | 10537200 | 42073200 | 73609200 | 105145200
2028-05-08 | -1314.37 | 4.048 | 60.036 | 59.8258 | -385.2038 |  | 2928 | 10540800 | 42076800 | 73612800 | 105148800
2028-05-09 01:00 | -1518.88 | 4.5281 | 59.7159 | 59.8258 | -445.1398 |  | 2929 | 10544400 | 42080400 | 73616400 | 105152400
2028-05-10 02:00 | -1870.26 | 5.51 | 59.4367 | 59.8258 | -548.1191 |  | 2930 | 10548000 | 42084000 | 73620000 | 105156000
2028-05-11 03:00 | -1744.36 | 5.0719 | 59.1237 | 59.8258 | -511.2215 |  | 2931 | 10551600 | 42087600 | 73623600 | 105159600
2028-05-12 04:00 | -1776.13 | 5.217 | 58.9737 | 59.8258 | -520.5323 |  | 2932 | 10555200 | 42091200 | 73627200 | 105163200
2028-05-13 05:00 | -1532.47 | 4.5059 | 58.8176 | 59.8258 | -449.1226 |  | 2933 | 10558800 | 42094800 | 73630800 | 105166800
2028-05-14 06:00 | -1547.59 | 4.6238 | 58.744 | 59.8258 | -453.5539 |  | 2934 | 10562400 | 42098400 | 73634400 | 105170400
2028-05-15 07:00 | -1480.15 | 4.4221 | 58.6492 | 59.8258 | -433.7891 |  | 2935 | 10566000 | 42102000 | 73638000 | 105174000
2028-05-16 08:00 | -2100.71 | 6.108 | 58.5317 | 59.8258 | -615.6573 |  | 2936 | 10569600 | 42105600 | 73641600 | 105177600
2028-05-17 09:00 | -1792.51 | 5.2072 | 58.3541 | 59.8258 | -525.3328 |  | 2937 | 10573200 | 42109200 | 73645200 | 105181200
2028-05-18 10:00 | -1732.83 | 5.1221 | 58.3137 | 59.8258 | -507.8423 |  | 2938 | 10576800 | 42112800 | 73648800 | 105184800
2028-05-19 11:00 | -1394.36 | 4.1453 | 58.2533 | 59.8258 | -408.6466 |  | 2939 | 10580400 | 42116400 | 73652400 | 105188400
2028-05-20 12:00 | -1451.06 | 4.407 | 58.2522 | 59.8258 | -425.2637 |  | 2940 | 10584000 | 42120000 | 73656000 | 105192000
2028-05-21 13:00 | -1387.09 | 4.1989 | 58.1765 | 59.8258 | -406.516 |  | 2941 | 10587600 | 42123600 | 73659600 | 105195600
2028-05-22 14:00 | -1212.35 | 3.7116 | 58.1374 | 59.8258 | -355.3047 |  | 2942 | 10591200 | 42127200 | 73663200 | 105199200
2028-05-23 15:00 | -574.148 | 1.9052 | 58.2001 | 59.8258 | -168.2662 |  | 2943 | 10594800 | 42130800 | 73666800 | 105202800
2028-05-24 16:00 | 483.346 | 1 | 59.5553 | 59.8258 | 141.6547 |  | 2944 | 10598400 | 42134400 | 73670400 | 105206400
2028-05-25 17:00 | 1849.88 | 1 | 59.5429 | 59.8258 | 542.1463 |  | 2945 | 10602000 | 42138000 | 73674000 | 105210000
2028-05-26 18:00 | -358.824 | 1.6043 | 58.9123 | 59.8258 | -105.1609 |  | 2946 | 10605600 | 42141600 | 73677600 | 105213600
2028-05-27 19:00 | -755.576 | 2.622 | 58.4494 | 59.8258 | -221.4375 |  | 2947 | 10609200 | 42145200 | 73681200 | 105217200
2028-05-28 20:00 | -1582.85 | 4.9431 | 58.1774 | 59.8258 | -463.8875 |  | 2948 | 10612800 | 42148800 | 73684800 | 105220800
2028-05-29 21:00 | -1674.84 | 5.0028 | 57.9511 | 59.8258 | -490.8472 |  | 2949 | 10616400 | 42152400 | 73688400 | 105224400
2028-05-30 22:00 | -2656.01 | 6.108 | 57.3893 | 59.8258 | -778.3997 |  | 2950 | 10620000 | 42156000 | 73692000 | 105228000
2028-05-31 23:00 | -3136.15 | 6.108 | 56.797 | 59.8258 | -919.1148 |  | 2951 | 10623600 | 42159600 | 73695600 | 105231600
2028-06-02 | -3149.01 | 6.108 | 56.6008 | 59.8258 | -922.8837 |  | 2952 | 10627200 | 42163200 | 73699200 | 105235200
2028-06-03 01:00 | -3305.45 | 6.108 | 56.3701 | 59.8258 | -968.7318 |  | 2953 | 10630800 | 42166800 | 73702800 | 105238800
2028-06-04 02:00 | -3193.08 | 6.108 | 56.3459 | 59.8258 | -935.7994 |  | 2954 | 10634400 | 42170400 | 73706400 | 105242400
2028-06-05 03:00 | -3007.38 | 6.108 | 56.3952 | 59.8258 | -881.3761 |  | 2955 | 10638000 | 42174000 | 73710000 | 105246000
2028-06-06 04:00 | -2819.24 | 6.108 | 56.4813 | 59.8258 | -826.2377 |  | 2956 | 10641600 | 42177600 | 73713600 | 105249600
2028-06-07 05:00 | -2563.67 | 6.108 | 56.6224 | 59.8258 | -751.3375 |  | 2957 | 10645200 | 42181200 | 73717200 | 105253200
2028-06-08 06:00 | -2431.26 | 6.108 | 56.7142 | 59.8258 | -712.532 |  | 2958 | 10648800 | 42184800 | 73720800 | 105256800
2028-06-09 07:00 | -2410.89 | 6.108 | 56.7231 | 59.8258 | -706.5621 |  | 2959 | 10652400 | 42188400 | 73724400 | 105260400
2028-06-10 08:00 | -2792.14 | 6.108 | 56.4262 | 59.8258 | -818.2955 |  | 2960 | 10656000 | 42192000 | 73728000 | 105264000
2028-06-11 09:00 | -2671.26 | 6.108 | 56.4392 | 59.8258 | -782.869 |  | 2961 | 10659600 | 42195600 | 73731600 | 105267600
2028-06-12 10:00 | -2200.2 | 6.108 | 56.7552 | 59.8258 | -644.815 |  | 2962 | 10663200 | 42199200 | 73735200 | 105271200
2028-06-13 11:00 | -1673.68 | 4.9594 | 56.884 | 59.8258 | -490.5072 |  | 2963 | 10666800 | 42202800 | 73738800 | 105274800
2028-06-14 12:00 | -1110.36 | 3.3892 | 56.9878 | 59.8258 | -325.4144 |  | 2964 | 10670400 | 42206400 | 73742400 | 105278400
2028-06-15 13:00 | -788.516 | 2.5897 | 57.1776 | 59.8258 | -231.0912 |  | 2965 | 10674000 | 42210000 | 73746000 | 105282000
2028-06-16 14:00 | -162.542 | 0.83192 | 57.7593 | 59.8258 | -47.6364 |  | 2966 | 10677600 | 42213600 | 73749600 | 105285600
2028-06-17 15:00 | 2194.92 | 1 | 58.5797 | 59.8258 | 643.2676 |  | 2967 | 10681200 | 42217200 | 73753200 | 105289200
2028-06-18 16:00 | 2896.19 | 1 | 58.8881 | 59.8258 | 848.7895 |  | 2968 | 10684800 | 42220800 | 73756800 | 105292800
2028-06-19 17:00 | 3098.44 | 1 | 83.7148 | 59.8258 | 908.0631 |  | 2969 | 10688400 | 42224400 | 73760400 | 105296400
2028-06-20 18:00 | 3106.06 | 1 | 59.3497 | 59.8258 | 910.2963 |  | 2970 | 10692000 | 42228000 | 73764000 | 105300000
2028-06-21 19:00 | 2424.65 | 1 | 59.5947 | 59.8258 | 710.5948 |  | 2971 | 10695600 | 42231600 | 73767600 | 105303600
2028-06-22 20:00 | -579.76 | 2.2363 | 58.6968 | 59.8258 | -169.9109 |  | 2972 | 10699200 | 42235200 | 73771200 | 105307200
2028-06-23 21:00 | -867.363 | 2.8977 | 58.1645 | 59.8258 | -254.199 |  | 2973 | 10702800 | 42238800 | 73774800 | 105310800
2028-06-24 22:00 | -1629.85 | 5.0751 | 57.8741 | 59.8258 | -477.6619 |  | 2974 | 10706400 | 42242400 | 73778400 | 105314400
2028-06-25 23:00 | -2190.86 | 6.108 | 57.5221 | 59.8258 | -642.0777 |  | 2975 | 10710000 | 42246000 | 73782000 | 105318000
2028-06-27 | -2488.41 | 6.108 | 57.0894 | 59.8258 | -729.281 |  | 2976 | 10713600 | 42249600 | 73785600 | 105321600
2028-06-28 01:00 | -2619.38 | 6.108 | 56.8128 | 59.8258 | -767.6645 |  | 2977 | 10717200 | 42253200 | 73789200 | 105325200
2028-06-29 02:00 | -2653.04 | 6.108 | 56.6898 | 59.8258 | -777.5293 |  | 2978 | 10720800 | 42256800 | 73792800 | 105328800
2028-06-30 03:00 | -2627.68 | 6.108 | 56.6025 | 59.8258 | -770.097 |  | 2979 | 10724400 | 42260400 | 73796400 | 105332400
2028-07-01 04:00 | -2850.62 | 6.108 | 56.3476 | 59.8258 | -835.4343 |  | 2980 | 10728000 | 42264000 | 73800000 | 105336000
2028-07-02 05:00 | -2867.31 | 6.108 | 56.2239 | 59.8258 | -840.3256 |  | 2981 | 10731600 | 42267600 | 73803600 | 105339600
2028-07-03 06:00 | -1857.18 | 5.556 | 56.7444 | 59.8258 | -544.2857 |  | 2982 | 10735200 | 42271200 | 73807200 | 105343200
2028-07-04 07:00 | -1050.93 | 3.1604 | 56.8043 | 59.8258 | -307.9972 |  | 2983 | 10738800 | 42274800 | 73810800 | 105346800
2028-07-05 08:00 | -1044.94 | 3.3719 | 57.0551 | 59.8258 | -306.2417 |  | 2984 | 10742400 | 42278400 | 73814400 | 105350400
2028-07-06 09:00 | -531.041 | 1.8356 | 57.212 | 59.8258 | -155.6328 |  | 2985 | 10746000 | 42282000 | 73818000 | 105354000
2028-07-07 10:00 | 2194.15 | 1 | 58.46 | 59.8258 | 643.0419 |  | 2986 | 10749600 | 42285600 | 73821600 | 105357600
2028-07-08 11:00 | 2931.06 | 1 | 75.6994 | 59.8258 | 859.0089 |  | 2987 | 10753200 | 42289200 | 73825200 | 105361200
2028-07-09 12:00 | 4376.6 | 1.4371 | 73.3855 | 59.8258 | 1282.6548 |  | 2988 | 10756800 | 42292800 | 73828800 | 105364800
2028-07-10 13:00 | 5424.62 | 1.7698 | 73.8836 | 59.8258 | 1589.7992 |  | 2989 | 10760400 | 42296400 | 73832400 | 105368400
2028-07-11 14:00 | 6076 | 2.0219 | 74.0421 | 59.8258 | 1780.6998 |  | 2990 | 10764000 | 42300000 | 73836000 | 105372000
2028-07-12 15:00 | 6612.18 | 2.1921 | 74.4765 | 59.8258 | 1937.8387 |  | 2991 | 10767600 | 42303600 | 73839600 | 105375600
2028-07-13 16:00 | 9111.17 | 2.9484 | 75.1197 | 59.8258 | 2670.2203 |  | 2992 | 10771200 | 42307200 | 73843200 | 105379200
2028-07-14 17:00 | 7954.36 | 2.5101 | 76.069 | 59.8258 | 2331.1928 |  | 2993 | 10774800 | 42310800 | 73846800 | 105382800
2028-07-15 18:00 | 6647.94 | 2.041 | 76.7097 | 59.8258 | 1948.3189 |  | 2994 | 10778400 | 42314400 | 73850400 | 105386400
2028-07-16 19:00 | 4594.46 | 1.4158 | 76.6718 | 59.8258 | 1346.5033 |  | 2995 | 10782000 | 42318000 | 73854000 | 105390000
2028-07-17 20:00 | 3359.4 | 1.051 | 76.3072 | 59.8258 | 984.543 |  | 2996 | 10785600 | 42321600 | 73857600 | 105393600
2028-07-18 21:00 | 3183.7 | 1 | 61.239 | 59.8258 | 933.0504 |  | 2997 | 10789200 | 42325200 | 73861200 | 105397200
2028-07-19 22:00 | 3070.14 | 1 | 61.1273 | 59.8258 | 899.7692 |  | 2998 | 10792800 | 42328800 | 73864800 | 105400800
2028-07-20 23:00 | -901.564 | 3.079 | 59.9891 | 59.8258 | -264.2223 |  | 2999 | 10796400 | 42332400 | 73868400 | 105404400
2028-07-22 | -1277.49 | 3.9539 | 59.2665 | 59.8258 | -374.3954 |  | 3000 | 10800000 | 42336000 | 73872000 | 105408000
2028-07-23 01:00 | -1666.8 | 5.0167 | 58.8576 | 59.8258 | -488.4909 |  | 3001 | 10803600 | 42339600 | 73875600 | 105411600
2028-07-24 02:00 | -1999.02 | 5.9007 | 58.5813 | 59.8258 | -585.8549 |  | 3002 | 10807200 | 42343200 | 73879200 | 105415200
2028-07-25 03:00 | -2326.24 | 6.108 | 58.1283 | 59.8258 | -681.7536 |  | 3003 | 10810800 | 42346800 | 73882800 | 105418800
2028-07-26 04:00 | -2598.37 | 6.108 | 57.626 | 59.8258 | -761.5071 |  | 3004 | 10814400 | 42350400 | 73886400 | 105422400
2028-07-27 05:00 | -2675.51 | 6.108 | 57.3656 | 59.8258 | -784.1146 |  | 3005 | 10818000 | 42354000 | 73890000 | 105426000
2028-07-28 06:00 | -1682.49 | 4.9573 | 57.6453 | 59.8258 | -493.0891 |  | 3006 | 10821600 | 42357600 | 73893600 | 105429600
2028-07-29 07:00 | -742.285 | 2.2823 | 57.7136 | 59.8258 | -217.5423 |  | 3007 | 10825200 | 42361200 | 73897200 | 105433200
2028-07-30 08:00 | -143.89 | 0.80227 | 58.4874 | 59.8258 | -42.17 |  | 3008 | 10828800 | 42364800 | 73900800 | 105436800
2028-07-31 09:00 | 1854.05 | 1 | 59.2533 | 59.8258 | 543.3684 |  | 3009 | 10832400 | 42368400 | 73904400 | 105440400
2028-08-01 10:00 | 2716.99 | 1 | 73.8028 | 59.8258 | 796.2712 |  | 3010 | 10836000 | 42372000 | 73908000 | 105444000
2028-08-02 11:00 | 4359.99 | 1.421 | 74.0626 | 59.8258 | 1277.7869 |  | 3011 | 10839600 | 42375600 | 73911600 | 105447600
2028-08-03 12:00 | 5313.11 | 1.7511 | 74.3012 | 59.8258 | 1557.1188 |  | 3012 | 10843200 | 42379200 | 73915200 | 105451200
2028-08-04 13:00 | 6071.79 | 1.9065 | 75.367 | 59.8258 | 1779.466 |  | 3013 | 10846800 | 42382800 | 73918800 | 105454800
2028-08-05 14:00 | 5351.27 | 1.6913 | 75.6323 | 59.8258 | 1568.3024 |  | 3014 | 10850400 | 42386400 | 73922400 | 105458400
2028-08-06 15:00 | 5636.15 | 1.6867 | 76.5723 | 59.8258 | 1651.7925 |  | 3015 | 10854000 | 42390000 | 73926000 | 105462000
2028-08-07 16:00 | 7915.61 | 2.4173 | 76.4035 | 59.8258 | 2319.8363 |  | 3016 | 10857600 | 42393600 | 73929600 | 105465600
2028-08-08 17:00 | 6719.02 | 2.0915 | 76.5654 | 59.8258 | 1969.1504 |  | 3017 | 10861200 | 42397200 | 73933200 | 105469200
2028-08-09 18:00 | 5469.07 | 1.6692 | 76.9787 | 59.8258 | 1602.8262 |  | 3018 | 10864800 | 42400800 | 73936800 | 105472800
2028-08-10 19:00 | 4297.47 | 1.3097 | 76.9301 | 59.8258 | 1259.4641 |  | 3019 | 10868400 | 42404400 | 73940400 | 105476400
2028-08-11 20:00 | 3231.17 | 1.0108 | 76.4534 | 59.8258 | 946.9624 |  | 3020 | 10872000 | 42408000 | 73944000 | 105480000
2028-08-12 21:00 | 3160.35 | 1 | 80.5385 | 59.8258 | 926.2072 |  | 3021 | 10875600 | 42411600 | 73947600 | 105483600
2028-08-13 22:00 | 3094.94 | 1 | 61.2814 | 59.8258 | 907.0374 |  | 3022 | 10879200 | 42415200 | 73951200 | 105487200
2028-08-14 23:00 | -561.363 | 2.1051 | 60.2892 | 59.8258 | -164.5193 |  | 3023 | 10882800 | 42418800 | 73954800 | 105490800
2028-08-16 | -685.729 | 2.3414 | 59.6426 | 59.8258 | -200.9673 |  | 3024 | 10886400 | 42422400 | 73958400 | 105494400
2028-08-17 01:00 | -760.411 | 2.5413 | 59.3015 | 59.8258 | -222.8545 |  | 3025 | 10890000 | 42426000 | 73962000 | 105498000
2028-08-18 02:00 | -717.363 | 2.4044 | 59.1511 | 59.8258 | -210.2383 |  | 3026 | 10893600 | 42429600 | 73965600 | 105501600
2028-08-19 03:00 | -513.372 | 1.837 | 59.0972 | 59.8258 | -150.4545 |  | 3027 | 10897200 | 42433200 | 73969200 | 105505200
2028-08-20 04:00 | -332.188 | 1.3742 | 59.1359 | 59.8258 | -97.3547 |  | 3028 | 10900800 | 42436800 | 73972800 | 105508800
2028-08-21 05:00 | 292.724 | 1 | 60.1948 | 59.8258 | 85.7889 |  | 3029 | 10904400 | 42440400 | 73976400 | 105512400
2028-08-22 06:00 | 3355.22 | 1 | 59.9737 | 59.8258 | 983.3179 |  | 3030 | 10908000 | 42444000 | 73980000 | 105516000
2028-08-23 07:00 | 2083.88 | 1 | 60.5219 | 59.8258 | 610.7249 |  | 3031 | 10911600 | 42447600 | 73983600 | 105519600
2028-08-24 08:00 | 2865.25 | 1 | 60.5263 | 59.8258 | 839.7219 |  | 3032 | 10915200 | 42451200 | 73987200 | 105523200
2028-08-25 09:00 | 3227.42 | 1 | 82.402 | 59.8258 | 945.8634 |  | 3033 | 10918800 | 42454800 | 73990800 | 105526800
2028-08-26 10:00 | 4975.04 | 1.5336 | 75.8754 | 59.8258 | 1458.0403 |  | 3034 | 10922400 | 42458400 | 73994400 | 105530400
2028-08-27 11:00 | 6834.43 | 2.2578 | 75.2554 | 59.8258 | 2002.9737 |  | 3035 | 10926000 | 42462000 | 73998000 | 105534000
2028-08-28 12:00 | 7627.47 | 2.5644 | 75.4415 | 59.8258 | 2235.3908 |  | 3036 | 10929600 | 42465600 | 74001600 | 105537600
2028-08-29 13:00 | 8731.86 | 2.8701 | 76.141 | 59.8258 | 2559.0556 |  | 3037 | 10933200 | 42469200 | 74005200 | 105541200
2028-08-30 14:00 | 8988.34 | 2.9807 | 76.4339 | 59.8258 | 2634.2224 |  | 3038 | 10936800 | 42472800 | 74008800 | 105544800
2028-08-31 15:00 | 10545.3 | 3.5185 | 76.6898 | 59.8258 | 3090.5224 |  | 3039 | 10940400 | 42476400 | 74012400 | 105548400
2028-09-01 16:00 | 11477.7 | 3.7056 | 77.586 | 59.8258 | 3363.7818 |  | 3040 | 10944000 | 42480000 | 74016000 | 105552000
2028-09-02 17:00 | 11609.2 | 3.6976 | 78.209 | 59.8258 | 3402.3207 |  | 3041 | 10947600 | 42483600 | 74019600 | 105555600
2028-09-03 18:00 | 9563.01 | 3.046 | 78.5235 | 59.8258 | 2802.6416 |  | 3042 | 10951200 | 42487200 | 74023200 | 105559200
2028-09-04 19:00 | 7876.48 | 2.4058 | 79.137 | 59.8258 | 2308.3684 |  | 3043 | 10954800 | 42490800 | 74026800 | 105562800
2028-09-05 20:00 | 5517.92 | 1.5876 | 79.9384 | 59.8258 | 1617.1427 |  | 3044 | 10958400 | 42494400 | 74030400 | 105566400
2028-09-06 21:00 | 4124.01 | 1.2354 | 78.9886 | 59.8258 | 1208.628 |  | 3045 | 10962000 | 42498000 | 74034000 | 105570000
2028-09-07 22:00 | 3167.63 | 1 | 63.0919 | 59.8258 | 928.3407 |  | 3046 | 10965600 | 42501600 | 74037600 | 105573600
2028-09-08 23:00 | 3088.63 | 1 | 62.7852 | 59.8258 | 905.1881 |  | 3047 | 10969200 | 42505200 | 74041200 | 105577200
2028-09-10 | 1546.75 | 1 | 62.7334 | 59.8258 | 453.3077 |  | 3048 | 10972800 | 42508800 | 74044800 | 105580800
2028-09-11 01:00 | -17.3434 | 0.62836 | 62.4088 | 59.8258 | -5.0828 |  | 3049 | 10976400 | 42512400 | 74048400 | 105584400
2028-09-12 02:00 | -97.8928 | 0.80115 | 61.5672 | 59.8258 | -28.6895 |  | 3050 | 10980000 | 42516000 | 74052000 | 105588000
2028-09-13 03:00 | -37.9772 | 0.62355 | 61.5852 | 59.8258 | -11.13 |  | 3051 | 10983600 | 42519600 | 74055600 | 105591600
2028-09-14 04:00 | 79.614 | 1 | 61.672 | 59.8258 | 23.3326 |  | 3052 | 10987200 | 42523200 | 74059200 | 105595200
2028-09-15 05:00 | 1734.87 | 1 | 61.3508 | 59.8258 | 508.4402 |  | 3053 | 10990800 | 42526800 | 74062800 | 105598800
2028-09-16 06:00 | 2605.11 | 1 | 61.3543 | 59.8258 | 763.4824 |  | 3054 | 10994400 | 42530400 | 74066400 | 105602400
2028-09-17 07:00 | 2964.04 | 1 | 80.6434 | 59.8258 | 868.6744 |  | 3055 | 10998000 | 42534000 | 74070000 | 105606000
2028-09-18 08:00 | 3214.22 | 1 | 76.8118 | 59.8258 | 941.9949 |  | 3056 | 11001600 | 42537600 | 74073600 | 105609600
2028-09-19 09:00 | 4522.58 | 1.3729 | 77.0355 | 59.8258 | 1325.4374 |  | 3057 | 11005200 | 42541200 | 74077200 | 105613200
2028-09-20 10:00 | 6071.74 | 1.9105 | 76.7587 | 59.8258 | 1779.4513 |  | 3058 | 11008800 | 42544800 | 74080800 | 105616800
2028-09-21 11:00 | 7587.72 | 2.5105 | 76.3774 | 59.8258 | 2223.7412 |  | 3059 | 11012400 | 42548400 | 74084400 | 105620400
2028-09-22 12:00 | 8682.64 | 2.8416 | 76.9244 | 59.8258 | 2544.6306 |  | 3060 | 11016000 | 42552000 | 74088000 | 105624000
2028-09-23 13:00 | 9223.04 | 2.978 | 77.5196 | 59.8258 | 2703.0062 |  | 3061 | 11019600 | 42555600 | 74091600 | 105627600
2028-09-24 14:00 | 9648.06 | 3.1867 | 77.5625 | 59.8258 | 2827.5673 |  | 3062 | 11023200 | 42559200 | 74095200 | 105631200
2028-09-25 15:00 | 11680 | 3.7826 | 78.1358 | 59.8258 | 3423.0701 |  | 3063 | 11026800 | 42562800 | 74098800 | 105634800
2028-09-26 16:00 | 12097.2 | 3.9173 | 78.6259 | 59.8258 | 3545.3393 |  | 3064 | 11030400 | 42566400 | 74102400 | 105638400
2028-09-27 17:00 | 11881.8 | 3.8245 | 79.0794 | 59.8258 | 3482.2118 |  | 3065 | 11034000 | 42570000 | 74106000 | 105642000
2028-09-28 18:00 | 9892.12 | 3.1865 | 79.3047 | 59.8258 | 2899.0942 |  | 3066 | 11037600 | 42573600 | 74109600 | 105645600
2028-09-29 19:00 | 8094.96 | 2.5443 | 79.6185 | 59.8258 | 2372.3986 |  | 3067 | 11041200 | 42577200 | 74113200 | 105649200
2028-09-30 20:00 | 5534.42 | 1.6699 | 80.0738 | 59.8258 | 1621.9784 |  | 3068 | 11044800 | 42580800 | 74116800 | 105652800
2028-10-01 21:00 | 4450.18 | 1.316 | 79.9914 | 59.8258 | 1304.219 |  | 3069 | 11048400 | 42584400 | 74120400 | 105656400
2028-10-02 22:00 | 3193.41 | 1 | 86.0493 | 59.8258 | 935.8961 |  | 3070 | 11052000 | 42588000 | 74124000 | 105660000
2028-10-03 23:00 | 3244.11 | 1 | 63.5245 | 59.8258 | 950.7548 |  | 3071 | 11055600 | 42591600 | 74127600 | 105663600
2028-10-05 | 3147.39 | 1 | 63.3275 | 59.8258 | 922.409 |  | 3072 | 11059200 | 42595200 | 74131200 | 105667200
2028-10-06 01:00 | 3069.03 | 1 | 63.1907 | 59.8258 | 899.4439 |  | 3073 | 11062800 | 42598800 | 74134800 | 105670800
2028-10-07 02:00 | 3179.15 | 1 | 63.0841 | 59.8258 | 931.7169 |  | 3074 | 11066400 | 42602400 | 74138400 | 105674400
2028-10-08 03:00 | 2502.54 | 1 | 63.0717 | 59.8258 | 733.4221 |  | 3075 | 11070000 | 42606000 | 74142000 | 105678000
2028-10-09 04:00 | 3321.09 | 1 | 62.8522 | 59.8258 | 973.3154 |  | 3076 | 11073600 | 42609600 | 74145600 | 105681600
2028-10-10 05:00 | 3299.18 | 1 | 62.8446 | 59.8258 | 966.8942 |  | 3077 | 11077200 | 42613200 | 74149200 | 105685200
2028-10-11 06:00 | 3321.07 | 1 | 80.8481 | 59.8258 | 973.3095 |  | 3078 | 11080800 | 42616800 | 74152800 | 105688800
2028-10-12 07:00 | 4395.44 | 1.288 | 78.6623 | 59.8258 | 1288.1763 |  | 3079 | 11084400 | 42620400 | 74156400 | 105692400
2028-10-13 08:00 | 4501.26 | 1.3443 | 78.5132 | 59.8258 | 1319.1891 |  | 3080 | 11088000 | 42624000 | 74160000 | 105696000
2028-10-14 09:00 | 5743.85 | 1.8298 | 77.6588 | 59.8258 | 1683.3563 |  | 3081 | 11091600 | 42627600 | 74163600 | 105699600
2028-10-15 10:00 | 6281.45 | 2.0653 | 77.4222 | 59.8258 | 1840.9113 |  | 3082 | 11095200 | 42631200 | 74167200 | 105703200
2028-10-16 11:00 | 7405.75 | 2.4674 | 77.4282 | 59.8258 | 2170.4111 |  | 3083 | 11098800 | 42634800 | 74170800 | 105706800
2028-10-17 12:00 | 7400.61 | 2.3246 | 78.5254 | 59.8258 | 2168.9047 |  | 3084 | 11102400 | 42638400 | 74174400 | 105710400
2028-10-18 13:00 | 6771.66 | 2.2403 | 77.9405 | 59.8258 | 1984.5776 |  | 3085 | 11106000 | 42642000 | 74178000 | 105714000
2028-10-19 14:00 | 5833.49 | 1.7631 | 79.2714 | 59.8258 | 1709.6272 |  | 3086 | 11109600 | 42645600 | 74181600 | 105717600
2028-10-20 15:00 | 6990.98 | 2.2127 | 78.4664 | 59.8258 | 2048.854 |  | 3087 | 11113200 | 42649200 | 74185200 | 105721200
2028-10-21 16:00 | 7198.79 | 2.3398 | 78.176 | 59.8258 | 2109.7571 |  | 3088 | 11116800 | 42652800 | 74188800 | 105724800
2028-10-22 17:00 | 7548.76 | 2.4404 | 78.3107 | 59.8258 | 2212.3232 |  | 3089 | 11120400 | 42656400 | 74192400 | 105728400
2028-10-23 18:00 | 6742.33 | 2.0752 | 79.1029 | 59.8258 | 1975.9819 |  | 3090 | 11124000 | 42660000 | 74196000 | 105732000
2028-10-24 19:00 | 5558.83 | 1.6459 | 79.6554 | 59.8258 | 1629.1323 |  | 3091 | 11127600 | 42663600 | 74199600 | 105735600
2028-10-25 20:00 | 3328.97 | 1 | 79.78 | 59.8258 | 975.6248 |  | 3092 | 11131200 | 42667200 | 74203200 | 105739200
2028-10-26 21:00 | 3239.25 | 1 | 85.1134 | 59.8258 | 949.3305 |  | 3093 | 11134800 | 42670800 | 74206800 | 105742800
2028-10-27 22:00 | 2904.29 | 1 | 63.2834 | 59.8258 | 851.1634 |  | 3094 | 11138400 | 42674400 | 74210400 | 105746400
2028-10-28 23:00 | 80.094 | 1 | 63.3624 | 59.8258 | 23.4732 |  | 3095 | 11142000 | 42678000 | 74214000 | 105750000
2028-10-30 | -213.662 | 1.1199 | 61.9718 | 59.8258 | -62.6182 |  | 3096 | 11145600 | 42681600 | 74217600 | 105753600
2028-10-31 01:00 | -405.999 | 1.6066 | 61.3377 | 59.8258 | -118.9866 |  | 3097 | 11149200 | 42685200 | 74221200 | 105757200
2028-11-01 02:00 | -381.892 | 1.5021 | 61.1271 | 59.8258 | -111.9215 |  | 3098 | 11152800 | 42688800 | 74224800 | 105760800
2028-11-02 03:00 | -166.076 | 0.91418 | 61.2737 | 59.8258 | -48.6721 |  | 3099 | 11156400 | 42692400 | 74228400 | 105764400
2028-11-03 04:00 | -116.951 | 0.83136 | 61.3116 | 59.8258 | -34.275 |  | 3100 | 11160000 | 42696000 | 74232000 | 105768000
2028-11-04 05:00 | 1551.47 | 1 | 61.7193 | 59.8258 | 454.691 |  | 3101 | 11163600 | 42699600 | 74235600 | 105771600
2028-11-05 06:00 | 2475.04 | 1 | 61.766 | 59.8258 | 725.3626 |  | 3102 | 11167200 | 42703200 | 74239200 | 105775200
2028-11-06 07:00 | 2879.54 | 1 | 61.8975 | 59.8258 | 843.9099 |  | 3103 | 11170800 | 42706800 | 74242800 | 105778800
2028-11-07 08:00 | -49.1351 | 0.70203 | 61.9675 | 59.8258 | -14.4001 |  | 3104 | 11174400 | 42710400 | 74246400 | 105782400
2028-11-08 09:00 | 0 | 1 | 61.9498 | 59.8258 | 0 |  | 3105 | 11178000 | 42714000 | 74250000 | 105786000
2028-11-09 10:00 | 3105.22 | 1 | 61.4865 | 59.8258 | 910.0501 |  | 3106 | 11181600 | 42717600 | 74253600 | 105789600
2028-11-10 11:00 | 3399.42 | 1.0573 | 76.8168 | 59.8258 | 996.2717 |  | 3107 | 11185200 | 42721200 | 74257200 | 105793200
2028-11-11 12:00 | 4336.39 | 1.3519 | 76.8864 | 59.8258 | 1270.8705 |  | 3108 | 11188800 | 42724800 | 74260800 | 105796800
2028-11-12 13:00 | 3316.86 | 1 | 86.228 | 59.8258 | 972.0757 |  | 3109 | 11192400 | 42728400 | 74264400 | 105800400
2028-11-13 14:00 | 3117.92 | 1 | 82.7637 | 59.8258 | 913.7722 |  | 3110 | 11196000 | 42732000 | 74268000 | 105804000
2028-11-14 15:00 | 4135.58 | 1.3222 | 76.6774 | 59.8258 | 1212.0189 |  | 3111 | 11199600 | 42735600 | 74271600 | 105807600
2028-11-15 16:00 | 4237.3 | 1.3445 | 76.9079 | 59.8258 | 1241.83 |  | 3112 | 11203200 | 42739200 | 74275200 | 105811200
2028-11-16 17:00 | 5313.46 | 1.6814 | 76.9864 | 59.8258 | 1557.2214 |  | 3113 | 11206800 | 42742800 | 74278800 | 105814800
2028-11-17 18:00 | 4076.59 | 1.2691 | 77.3652 | 59.8258 | 1194.7306 |  | 3114 | 11210400 | 42746400 | 74282400 | 105818400
2028-11-18 19:00 | 3028.32 | 1 | 81.7135 | 59.8258 | 887.513 |  | 3115 | 11214000 | 42750000 | 74286000 | 105822000
2028-11-19 20:00 | 2934.25 | 1 | 62.2429 | 59.8258 | 859.9438 |  | 3116 | 11217600 | 42753600 | 74289600 | 105825600
2028-11-20 21:00 | -22.8367 | 0.64112 | 62.3057 | 59.8258 | -6.6928 |  | 3117 | 11221200 | 42757200 | 74293200 | 105829200
2028-11-21 22:00 | -828.72 | 2.8224 | 60.6884 | 59.8258 | -242.8739 |  | 3118 | 11224800 | 42760800 | 74296800 | 105832800
2028-11-22 23:00 | -1229.62 | 3.7963 | 60.1695 | 59.8258 | -360.366 |  | 3119 | 11228400 | 42764400 | 74300400 | 105836400
2028-11-24 | -1497.75 | 4.4833 | 59.8568 | 59.8258 | -438.9472 |  | 3120 | 11232000 | 42768000 | 74304000 | 105840000
2028-11-25 01:00 | -1667.96 | 4.9193 | 59.6187 | 59.8258 | -488.8308 |  | 3121 | 11235600 | 42771600 | 74307600 | 105843600
2028-11-26 02:00 | -1613.05 | 4.7326 | 59.4043 | 59.8258 | -472.7383 |  | 3122 | 11239200 | 42775200 | 74311200 | 105847200
2028-11-27 03:00 | -1456.53 | 4.3067 | 59.2926 | 59.8258 | -426.8668 |  | 3123 | 11242800 | 42778800 | 74314800 | 105850800
2028-11-28 04:00 | -1260.18 | 3.7867 | 59.232 | 59.8258 | -369.3223 |  | 3124 | 11246400 | 42782400 | 74318400 | 105854400
2028-11-29 05:00 | -842.772 | 2.6417 | 59.2111 | 59.8258 | -246.9921 |  | 3125 | 11250000 | 42786000 | 74322000 | 105858000
2028-11-30 06:00 | -460.044 | 1.6571 | 59.3685 | 59.8258 | -134.8256 |  | 3126 | 11253600 | 42789600 | 74325600 | 105861600
2028-12-01 07:00 | 198.212 | 1 | 60.6276 | 59.8258 | 58.0902 |  | 3127 | 11257200 | 42793200 | 74329200 | 105865200
2028-12-02 08:00 | 2417.33 | 1 | 60.5017 | 59.8258 | 708.4495 |  | 3128 | 11260800 | 42796800 | 74332800 | 105868800
2028-12-03 09:00 | 3165.23 | 1 | 80.3054 | 59.8258 | 927.6373 |  | 3129 | 11264400 | 42800400 | 74336400 | 105872400
2028-12-04 10:00 | 5187.2 | 1.6572 | 75.6366 | 59.8258 | 1520.2183 |  | 3130 | 11268000 | 42804000 | 74340000 | 105876000
2028-12-05 11:00 | 7110.55 | 2.3535 | 75.5681 | 59.8258 | 2083.8965 |  | 3131 | 11271600 | 42807600 | 74343600 | 105879600
2028-12-06 12:00 | 8609.4 | 2.7255 | 76.728 | 59.8258 | 2523.1661 |  | 3132 | 11275200 | 42811200 | 74347200 | 105883200
2028-12-07 13:00 | 9738.3 | 3.2303 | 76.6175 | 59.8258 | 2854.014 |  | 3133 | 11278800 | 42814800 | 74350800 | 105886800
2028-12-08 14:00 | 11008.9 | 3.5063 | 77.6954 | 59.8258 | 3226.3901 |  | 3134 | 11282400 | 42818400 | 74354400 | 105890400
2028-12-09 15:00 | 11980.5 | 3.7923 | 78.3151 | 59.8258 | 3511.138 |  | 3135 | 11286000 | 42822000 | 74358000 | 105894000
2028-12-10 16:00 | 12220.6 | 3.795 | 79.0999 | 59.8258 | 3581.5043 |  | 3136 | 11289600 | 42825600 | 74361600 | 105897600
2028-12-11 17:00 | 11188.3 | 3.4971 | 79.3929 | 59.8258 | 3278.9671 |  | 3137 | 11293200 | 42829200 | 74365200 | 105901200
2028-12-12 18:00 | 9600.54 | 2.9936 | 79.6091 | 59.8258 | 2813.6405 |  | 3138 | 11296800 | 42832800 | 74368800 | 105904800
2028-12-13 19:00 | 8021.72 | 2.4561 | 79.8727 | 59.8258 | 2350.9341 |  | 3139 | 11300400 | 42836400 | 74372400 | 105908400
2028-12-14 20:00 | 5684.34 | 1.7076 | 80.0245 | 59.8258 | 1665.9156 |  | 3140 | 11304000 | 42840000 | 74376000 | 105912000
2028-12-15 21:00 | 4470.63 | 1.327 | 79.8817 | 59.8258 | 1310.2123 |  | 3141 | 11307600 | 42843600 | 74379600 | 105915600
2028-12-16 22:00 | 3198.46 | 1 | 63.873 | 59.8258 | 937.3761 |  | 3142 | 11311200 | 42847200 | 74383200 | 105919200
2028-12-17 23:00 | 2852.87 | 1 | 63.5687 | 59.8258 | 836.0937 |  | 3143 | 11314800 | 42850800 | 74386800 | 105922800
2028-12-19 | 120.924 | 1 | 63.5606 | 59.8258 | 35.4393 |  | 3144 | 11318400 | 42854400 | 74390400 | 105926400
2028-12-20 01:00 | -140.05 | 0.92227 | 62.3393 | 59.8258 | -41.0446 |  | 3145 | 11322000 | 42858000 | 74394000 | 105930000
2028-12-21 02:00 | -301.353 | 1.3318 | 61.6325 | 59.8258 | -88.3178 |  | 3146 | 11325600 | 42861600 | 74397600 | 105933600
2028-12-22 03:00 | -512.224 | 1.8851 | 61.1609 | 59.8258 | -150.118 |  | 3147 | 11329200 | 42865200 | 74401200 | 105937200
2028-12-23 04:00 | -714.318 | 2.4077 | 60.7973 | 59.8258 | -209.3459 |  | 3148 | 11332800 | 42868800 | 74404800 | 105940800
2028-12-24 05:00 | -775.68 | 2.5408 | 60.5079 | 59.8258 | -227.3294 |  | 3149 | 11336400 | 42872400 | 74408400 | 105944400
2028-12-25 06:00 | 0 | 1 | 61.7415 | 59.8258 | 0 |  | 3150 | 11340000 | 42876000 | 74412000 | 105948000
2028-12-26 07:00 | 1848.01 | 1 | 61.5462 | 59.8258 | 541.5983 |  | 3151 | 11343600 | 42879600 | 74415600 | 105951600
2028-12-27 08:00 | 0 | 0 | 61.9153 | 59.8258 | 0 |  | 3152 | 11347200 | 42883200 | 74419200 | 105955200
2028-12-28 09:00 | 3868.15 | 1 | 61.4032 | 59.8258 | 1133.6429 |  | 3153 | 11350800 | 42886800 | 74422800 | 105958800
2028-12-29 10:00 | 3733.41 | 1 | 79.7368 | 59.8258 | 1094.1545 |  | 3154 | 11354400 | 42890400 | 74426400 | 105962400
2028-12-30 11:00 | 5283.02 | 1.5111 | 78.3193 | 59.8258 | 1548.3003 |  | 3155 | 11358000 | 42894000 | 74430000 | 105966000
2028-12-31 12:00 | 6077.35 | 1.8551 | 77.612 | 59.8258 | 1781.0955 |  | 3156 | 11361600 | 42897600 | 74433600 | 105969600
2029-01-01 13:00 | 6362.14 | 2.0494 | 77.1083 | 59.8258 | 1864.5592 |  | 3157 | 11365200 | 42901200 | 74437200 | 105973200
2029-01-02 14:00 | 7328.42 | 2.428 | 76.9686 | 59.8258 | 2147.7479 |  | 3158 | 11368800 | 42904800 | 74440800 | 105976800
2029-01-03 15:00 | 7704.8 | 2.4867 | 77.5798 | 59.8258 | 2258.054 |  | 3159 | 11372400 | 42908400 | 74444400 | 105980400
2029-01-04 16:00 | 10588.6 | 3.5646 | 77.2158 | 59.8258 | 3103.2123 |  | 3160 | 11376000 | 42912000 | 74448000 | 105984000
2029-01-05 17:00 | 9562.05 | 3.0659 | 78.4436 | 59.8258 | 2802.3602 |  | 3161 | 11379600 | 42915600 | 74451600 | 105987600
2029-01-06 18:00 | 8330.16 | 2.6183 | 78.9501 | 59.8258 | 2441.3289 |  | 3162 | 11383200 | 42919200 | 74455200 | 105991200
2029-01-07 19:00 | 6559.06 | 2.0159 | 79.2832 | 59.8258 | 1922.2707 |  | 3163 | 11386800 | 42922800 | 74458800 | 105994800
2029-01-08 20:00 | 5635.49 | 1.6686 | 79.7306 | 59.8258 | 1651.5991 |  | 3164 | 11390400 | 42926400 | 74462400 | 105998400
2029-01-09 21:00 | 4762.59 | 1.4186 | 79.5022 | 59.8258 | 1395.7773 |  | 3165 | 11394000 | 42930000 | 74466000 | 106002000
2029-01-10 22:00 | 3776.01 | 1.1802 | 78.588 | 59.8258 | 1106.6393 |  | 3166 | 11397600 | 42933600 | 74469600 | 106005600
2029-01-11 23:00 | 3059.85 | 1 | 63.4545 | 59.8258 | 896.7535 |  | 3167 | 11401200 | 42937200 | 74473200 | 106009200
2029-01-13 | 1366.61 | 1 | 63.3963 | 59.8258 | 400.5139 |  | 3168 | 11404800 | 42940800 | 74476800 | 106012800
2029-01-14 01:00 | 2084.51 | 1 | 62.9979 | 59.8258 | 610.9096 |  | 3169 | 11408400 | 42944400 | 74480400 | 106016400
2029-01-15 02:00 | 83.794 | 1 | 63.0718 | 59.8258 | 24.5576 |  | 3170 | 11412000 | 42948000 | 74484000 | 106020000
2029-01-16 03:00 | -31.1082 | 0.62634 | 62.508 | 59.8258 | -9.1169 |  | 3171 | 11415600 | 42951600 | 74487600 | 106023600
2029-01-17 04:00 | -39.1343 | 0.63794 | 62.1735 | 59.8258 | -11.4691 |  | 3172 | 11419200 | 42955200 | 74491200 | 106027200
2029-01-18 05:00 | -51.3074 | 0.67144 | 61.925 | 59.8258 | -15.0367 |  | 3173 | 11422800 | 42958800 | 74494800 | 106030800
2029-01-19 06:00 | 2091.1 | 1 | 75.8309 | 59.8258 | 612.8409 |  | 3174 | 11426400 | 42962400 | 74498400 | 106034400
2029-01-20 07:00 | 3077.25 | 1.0803 | 75.3168 | 59.8258 | 901.853 |  | 3175 | 11430000 | 42966000 | 74502000 | 106038000
2029-01-21 08:00 | 2423.8 | 1 | 62.303 | 59.8258 | 710.3457 |  | 3176 | 11433600 | 42969600 | 74505600 | 106041600
2029-01-22 09:00 | 0 | 0 | 62.5161 | 59.8258 | 0 |  | 3177 | 11437200 | 42973200 | 74509200 | 106045200
2029-01-23 10:00 | -127.733 | 0.91404 | 61.5411 | 59.8258 | -37.4348 |  | 3178 | 11440800 | 42976800 | 74512800 | 106048800
2029-01-24 11:00 | 2246.91 | 1 | 61.7832 | 59.8258 | 658.5043 |  | 3179 | 11444400 | 42980400 | 74516400 | 106052400
2029-01-25 12:00 | 2921.7 | 1 | 61.8985 | 59.8258 | 856.2657 |  | 3180 | 11448000 | 42984000 | 74520000 | 106056000
2029-01-26 13:00 | 2999.92 | 1 | 61.993 | 59.8258 | 879.1898 |  | 3181 | 11451600 | 42987600 | 74523600 | 106059600
2029-01-27 14:00 | 3362.74 | 1 | 61.9818 | 59.8258 | 985.5218 |  | 3182 | 11455200 | 42991200 | 74527200 | 106063200
2029-01-28 15:00 | 2735.51 | 1 | 62.1302 | 59.8258 | 801.6988 |  | 3183 | 11458800 | 42994800 | 74530800 | 106066800
2029-01-29 16:00 | 3117.2 | 1.1208 | 75.0886 | 59.8258 | 913.5611 |  | 3184 | 11462400 | 42998400 | 74534400 | 106070400
2029-01-30 17:00 | 2966.81 | 1 | 85.2788 | 59.8258 | 869.4862 |  | 3185 | 11466000 | 43002000 | 74538000 | 106074000
2029-01-31 18:00 | 3093.92 | 1 | 62.0038 | 59.8258 | 906.7384 |  | 3186 | 11469600 | 43005600 | 74541600 | 106077600
2029-02-01 19:00 | 0 | 0 | 62.26 | 59.8258 | 0 |  | 3187 | 11473200 | 43009200 | 74545200 | 106081200
2029-02-02 20:00 | -702.631 | 2.4633 | 60.5142 | 59.8258 | -205.9208 |  | 3188 | 11476800 | 43012800 | 74548800 | 106084800
2029-02-03 21:00 | -1116.04 | 3.5124 | 60.0542 | 59.8258 | -327.079 |  | 3189 | 11480400 | 43016400 | 74552400 | 106088400
2029-02-04 22:00 | -1507.57 | 4.5433 | 59.7719 | 59.8258 | -441.8252 |  | 3190 | 11484000 | 43020000 | 74556000 | 106092000
2029-02-05 23:00 | -2790.72 | 6.108 | 58.966 | 59.8258 | -817.8793 |  | 3191 | 11487600 | 43023600 | 74559600 | 106095600
2029-02-07 | -3075.38 | 6.108 | 58.3852 | 59.8258 | -901.3049 |  | 3192 | 11491200 | 43027200 | 74563200 | 106099200
2029-02-08 01:00 | -3394.88 | 6.108 | 57.8932 | 59.8258 | -994.9411 |  | 3193 | 11494800 | 43030800 | 74566800 | 106102800
2029-02-09 02:00 | -3660.94 | 6.108 | 57.4817 | 59.8258 | -1072.9156 |  | 3194 | 11498400 | 43034400 | 74570400 | 106106400
2029-02-10 03:00 | -3547.16 | 6.108 | 57.3639 | 59.8258 | -1039.57 |  | 3195 | 11502000 | 43038000 | 74574000 | 106110000
2029-02-11 04:00 | -3797.08 | 6.108 | 57.0213 | 59.8258 | -1112.8143 |  | 3196 | 11505600 | 43041600 | 74577600 | 106113600
2029-02-12 05:00 | -3637.36 | 6.108 | 56.9825 | 59.8258 | -1066.005 |  | 3197 | 11509200 | 43045200 | 74581200 | 106117200
2029-02-13 06:00 | -2999.7 | 6.108 | 57.3222 | 59.8258 | -879.1253 |  | 3198 | 11512800 | 43048800 | 74584800 | 106120800
2029-02-14 07:00 | -2252.76 | 6.108 | 57.861 | 59.8258 | -660.2188 |  | 3199 | 11516400 | 43052400 | 74588400 | 106124400
2029-02-15 08:00 | -1936.31 | 5.6575 | 58.0489 | 59.8258 | -567.4764 |  | 3200 | 11520000 | 43056000 | 74592000 | 106128000
2029-02-16 09:00 | -1025.18 | 3.0233 | 58.1081 | 59.8258 | -300.4506 |  | 3201 | 11523600 | 43059600 | 74595600 | 106131600
2029-02-17 10:00 | 0 | 1 | 59.7973 | 59.8258 | 0 |  | 3202 | 11527200 | 43063200 | 74599200 | 106135200
2029-02-18 11:00 | 3245.14 | 1 | 59.7131 | 59.8258 | 951.0567 |  | 3203 | 11530800 | 43066800 | 74602800 | 106138800
2029-02-19 12:00 | 3132.93 | 1 | 76.7656 | 59.8258 | 918.1711 |  | 3204 | 11534400 | 43070400 | 74606400 | 106142400
2029-02-20 13:00 | 3492.62 | 1.1468 | 74.7446 | 59.8258 | 1023.5859 |  | 3205 | 11538000 | 43074000 | 74610000 | 106146000
2029-02-21 14:00 | 4732 | 1.4787 | 75.6773 | 59.8258 | 1386.8123 |  | 3206 | 11541600 | 43077600 | 74613600 | 106149600
2029-02-22 15:00 | 6374.42 | 2.0805 | 75.4002 | 59.8258 | 1868.1581 |  | 3207 | 11545200 | 43081200 | 74617200 | 106153200
2029-02-23 16:00 | 7165.54 | 2.3175 | 75.9909 | 59.8258 | 2100.0125 |  | 3208 | 11548800 | 43084800 | 74620800 | 106156800
2029-02-24 17:00 | 6615.65 | 2.1377 | 76.3705 | 59.8258 | 1938.8556 |  | 3209 | 11552400 | 43088400 | 74624400 | 106160400
2029-02-25 18:00 | 5192.45 | 1.6365 | 76.9222 | 59.8258 | 1521.7569 |  | 3210 | 11556000 | 43092000 | 74628000 | 106164000
2029-02-26 19:00 | 3061.48 | 1 | 76.8239 | 59.8258 | 897.2312 |  | 3211 | 11559600 | 43095600 | 74631600 | 106167600
2029-02-27 20:00 | 2918.12 | 1 | 61.9653 | 59.8258 | 855.2166 |  | 3212 | 11563200 | 43099200 | 74635200 | 106171200
2029-02-28 21:00 | -158.784 | 1.0058 | 61.4117 | 59.8258 | -46.535 |  | 3213 | 11566800 | 43102800 | 74638800 | 106174800
2029-03-01 22:00 | -1118.22 | 3.6254 | 60.266 | 59.8258 | -327.7179 |  | 3214 | 11570400 | 43106400 | 74642400 | 106178400
2029-03-02 23:00 | -2064.71 | 6.108 | 59.713 | 59.8258 | -605.1068 |  | 3215 | 11574000 | 43110000 | 74646000 | 106182000
2029-03-04 | -2510.48 | 6.108 | 59.0304 | 59.8258 | -735.7491 |  | 3216 | 11577600 | 43113600 | 74649600 | 106185600
2029-03-05 01:00 | -2879.13 | 6.108 | 58.4759 | 59.8258 | -843.7897 |  | 3217 | 11581200 | 43117200 | 74653200 | 106189200
2029-03-06 02:00 | -3037.1 | 6.108 | 58.0828 | 59.8258 | -890.0861 |  | 3218 | 11584800 | 43120800 | 74656800 | 106192800
2029-03-07 03:00 | -3070.65 | 6.108 | 57.8484 | 59.8258 | -899.9187 |  | 3219 | 11588400 | 43124400 | 74660400 | 106196400
2029-03-08 04:00 | -3157.34 | 6.108 | 57.6054 | 59.8258 | -925.325 |  | 3220 | 11592000 | 43128000 | 74664000 | 106200000
2029-03-09 05:00 | -2785.74 | 6.108 | 57.7268 | 59.8258 | -816.4198 |  | 3221 | 11595600 | 43131600 | 74667600 | 106203600
2029-03-10 06:00 | -2072.05 | 6.0804 | 58.1678 | 59.8258 | -607.2579 |  | 3222 | 11599200 | 43135200 | 74671200 | 106207200
2029-03-11 07:00 | -1207.81 | 3.51 | 58.1675 | 59.8258 | -353.9742 |  | 3223 | 11602800 | 43138800 | 74674800 | 106210800
2029-03-12 08:00 | -362.149 | 1.3079 | 58.5579 | 59.8258 | -106.1354 |  | 3224 | 11606400 | 43142400 | 74678400 | 106214400
2029-03-13 09:00 | 2113.66 | 1 | 59.8058 | 59.8258 | 619.4526 |  | 3225 | 11610000 | 43146000 | 74682000 | 106218000
2029-03-14 10:00 | 2932.51 | 1 | 73.9571 | 59.8258 | 859.4338 |  | 3226 | 11613600 | 43149600 | 74685600 | 106221600
2029-03-15 11:00 | 5148.72 | 1.6759 | 74.7972 | 59.8258 | 1508.9409 |  | 3227 | 11617200 | 43153200 | 74689200 | 106225200
2029-03-16 12:00 | 6197.27 | 1.9924 | 75.46 | 59.8258 | 1816.2405 |  | 3228 | 11620800 | 43156800 | 74692800 | 106228800
2029-03-17 13:00 | 7216.08 | 2.344 | 75.7724 | 59.8258 | 2114.8243 |  | 3229 | 11624400 | 43160400 | 74696400 | 106232400
2029-03-18 14:00 | 7934.87 | 2.594 | 76.1193 | 59.8258 | 2325.4808 |  | 3230 | 11628000 | 43164000 | 74700000 | 106236000
2029-03-19 15:00 | 9462.21 | 3.0753 | 76.5718 | 59.8258 | 2773.1 |  | 3231 | 11631600 | 43167600 | 74703600 | 106239600
2029-03-20 16:00 | 9581.82 | 3.1175 | 77.0409 | 59.8258 | 2808.1542 |  | 3232 | 11635200 | 43171200 | 74707200 | 106243200
2029-03-21 17:00 | 8677.66 | 2.7496 | 77.7626 | 59.8258 | 2543.1711 |  | 3233 | 11638800 | 43174800 | 74710800 | 106246800
2029-03-22 18:00 | 7431.61 | 2.3082 | 78.197 | 59.8258 | 2177.9899 |  | 3234 | 11642400 | 43178400 | 74714400 | 106250400
2029-03-23 19:00 | 5389.54 | 1.6428 | 78.4926 | 59.8258 | 1579.5183 |  | 3235 | 11646000 | 43182000 | 74718000 | 106254000
2029-03-24 20:00 | 3182.81 | 1 | 82.7884 | 59.8258 | 932.7895 |  | 3236 | 11649600 | 43185600 | 74721600 | 106257600
2029-03-25 21:00 | 3068.1 | 1 | 62.6722 | 59.8258 | 899.1713 |  | 3237 | 11653200 | 43189200 | 74725200 | 106261200
2029-03-26 22:00 | -623.168 | 2.2558 | 61.4943 | 59.8258 | -182.6325 |  | 3238 | 11656800 | 43192800 | 74728800 | 106264800
2029-03-27 23:00 | -1110.34 | 3.4876 | 60.6916 | 59.8258 | -325.4085 |  | 3239 | 11660400 | 43196400 | 74732400 | 106268400
2029-03-29 | -1538.47 | 4.6098 | 60.184 | 59.8258 | -450.881 |  | 3240 | 11664000 | 43200000 | 74736000 | 106272000
2029-03-30 01:00 | -1943.29 | 5.6826 | 59.8451 | 59.8258 | -569.5221 |  | 3241 | 11667600 | 43203600 | 74739600 | 106275600
2029-03-31 02:00 | -2054.87 | 5.922 | 59.5495 | 59.8258 | -602.2229 |  | 3242 | 11671200 | 43207200 | 74743200 | 106279200
2029-04-01 03:00 | -1929.93 | 5.5573 | 59.2822 | 59.8258 | -565.6067 |  | 3243 | 11674800 | 43210800 | 74746800 | 106282800
2029-04-02 04:00 | -2069.39 | 6.0074 | 59.1522 | 59.8258 | -606.4783 |  | 3244 | 11678400 | 43214400 | 74750400 | 106286400
2029-04-03 05:00 | -1464.58 | 4.2217 | 58.9896 | 59.8258 | -429.226 |  | 3245 | 11682000 | 43218000 | 74754000 | 106290000
2029-04-04 06:00 | -1445.71 | 4.341 | 59.0075 | 59.8258 | -423.6958 |  | 3246 | 11685600 | 43221600 | 74757600 | 106293600
2029-04-05 07:00 | -967.592 | 2.9537 | 58.9796 | 59.8258 | -283.5732 |  | 3247 | 11689200 | 43225200 | 74761200 | 106297200
2029-04-06 08:00 | -503.201 | 1.7538 | 59.181 | 59.8258 | -147.4737 |  | 3248 | 11692800 | 43228800 | 74764800 | 106300800
2029-04-07 09:00 | 2086.15 | 1 | 60.3403 | 59.8258 | 611.3902 |  | 3249 | 11696400 | 43232400 | 74768400 | 106304400
2029-04-08 10:00 | 3019.51 | 1 | 77.0084 | 59.8258 | 884.931 |  | 3250 | 11700000 | 43236000 | 74772000 | 106308000
2029-04-09 11:00 | 4449.14 | 1.4234 | 75.4832 | 59.8258 | 1303.9142 |  | 3251 | 11703600 | 43239600 | 74775600 | 106311600
2029-04-10 12:00 | 5664.93 | 1.7941 | 75.9819 | 59.8258 | 1660.2271 |  | 3252 | 11707200 | 43243200 | 74779200 | 106315200
2029-04-11 13:00 | 6382.69 | 2.0806 | 75.9599 | 59.8258 | 1870.5818 |  | 3253 | 11710800 | 43246800 | 74782800 | 106318800
2029-04-12 14:00 | 7237.01 | 2.3477 | 76.3793 | 59.8258 | 2120.9583 |  | 3254 | 11714400 | 43250400 | 74786400 | 106322400
2029-04-13 15:00 | 8937.13 | 2.9186 | 76.589 | 59.8258 | 2619.2143 |  | 3255 | 11718000 | 43254000 | 74790000 | 106326000
2029-04-14 16:00 | 9337.32 | 3.0417 | 77.0655 | 59.8258 | 2736.4984 |  | 3256 | 11721600 | 43257600 | 74793600 | 106329600
2029-04-15 17:00 | 9415.69 | 2.967 | 77.8805 | 59.8258 | 2759.4663 |  | 3257 | 11725200 | 43261200 | 74797200 | 106333200
2029-04-16 18:00 | 7863.4 | 2.4569 | 78.2684 | 59.8258 | 2304.5351 |  | 3258 | 11728800 | 43264800 | 74800800 | 106336800
2029-04-17 19:00 | 5821.17 | 1.762 | 78.778 | 59.8258 | 1706.0165 |  | 3259 | 11732400 | 43268400 | 74804400 | 106340400
2029-04-18 20:00 | 3273.76 | 1.0041 | 78.4178 | 59.8258 | 959.4443 |  | 3260 | 11736000 | 43272000 | 74808000 | 106344000
2029-04-19 21:00 | 3167.18 | 1 | 62.8245 | 59.8258 | 928.2088 |  | 3261 | 11739600 | 43275600 | 74811600 | 106347600
2029-04-20 22:00 | 0 | 0 | 62.9137 | 59.8258 | 0 |  | 3262 | 11743200 | 43279200 | 74815200 | 106351200
2029-04-21 23:00 | -454.826 | 1.6275 | 61.0804 | 59.8258 | -133.2963 |  | 3263 | 11746800 | 43282800 | 74818800 | 106354800
2029-04-23 | -639.829 | 2.2267 | 60.6427 | 59.8258 | -187.5154 |  | 3264 | 11750400 | 43286400 | 74822400 | 106358400
2029-04-24 01:00 | -909.909 | 2.9417 | 60.2912 | 59.8258 | -266.668 |  | 3265 | 11754000 | 43290000 | 74826000 | 106362000
2029-04-25 02:00 | -1156.34 | 3.5836 | 60.0205 | 59.8258 | -338.8898 |  | 3266 | 11757600 | 43293600 | 74829600 | 106365600
2029-04-26 03:00 | -1099.59 | 3.373 | 59.7658 | 59.8258 | -322.258 |  | 3267 | 11761200 | 43297200 | 74833200 | 106369200
2029-04-27 04:00 | -1318.77 | 4.0249 | 59.6193 | 59.8258 | -386.4933 |  | 3268 | 11764800 | 43300800 | 74836800 | 106372800
2029-04-28 05:00 | -751.894 | 2.351 | 59.4928 | 59.8258 | -220.3584 |  | 3269 | 11768400 | 43304400 | 74840400 | 106376400
2029-04-29 06:00 | -217.925 | 0.9931 | 59.8965 | 59.8258 | -63.8675 |  | 3270 | 11772000 | 43308000 | 74844000 | 106380000
2029-04-30 07:00 | 2089.07 | 1 | 60.7337 | 59.8258 | 612.246 |  | 3271 | 11775600 | 43311600 | 74847600 | 106383600
2029-05-01 08:00 | 2922.54 | 1 | 60.9696 | 59.8258 | 856.5119 |  | 3272 | 11779200 | 43315200 | 74851200 | 106387200
2029-05-02 09:00 | 3084.7 | 1 | 85.0109 | 59.8258 | 904.0363 |  | 3273 | 11782800 | 43318800 | 74854800 | 106390800
2029-05-03 10:00 | 4722.19 | 1.378 | 77.3018 | 59.8258 | 1383.9373 |  | 3274 | 11786400 | 43322400 | 74858400 | 106394400
2029-05-04 11:00 | 6142.4 | 1.9685 | 76.2545 | 59.8258 | 1800.1597 |  | 3275 | 11790000 | 43326000 | 74862000 | 106398000
2029-05-05 12:00 | 7193.53 | 2.3035 | 76.6809 | 59.8258 | 2108.2155 |  | 3276 | 11793600 | 43329600 | 74865600 | 106401600
2029-05-06 13:00 | 8372.73 | 2.6386 | 77.2728 | 59.8258 | 2453.8049 |  | 3277 | 11797200 | 43333200 | 74869200 | 106405200
2029-05-07 14:00 | 8902.05 | 2.9394 | 77.0054 | 59.8258 | 2608.9333 |  | 3278 | 11800800 | 43336800 | 74872800 | 106408800
2029-05-08 15:00 | 10200.3 | 3.4152 | 77.1572 | 59.8258 | 2989.4128 |  | 3279 | 11804400 | 43340400 | 74876400 | 106412400
2029-05-09 16:00 | 10723.8 | 3.4892 | 77.9667 | 59.8258 | 3142.8355 |  | 3280 | 11808000 | 43344000 | 74880000 | 106416000
2029-05-10 17:00 | 10609.5 | 3.3758 | 78.6418 | 59.8258 | 3109.3375 |  | 3281 | 11811600 | 43347600 | 74883600 | 106419600
2029-05-11 18:00 | 8677.63 | 2.6971 | 79.2432 | 59.8258 | 2543.1623 |  | 3282 | 11815200 | 43351200 | 74887200 | 106423200
2029-05-12 19:00 | 7286.7 | 2.15 | 79.9803 | 59.8258 | 2135.521 |  | 3283 | 11818800 | 43354800 | 74890800 | 106426800
2029-05-13 20:00 | 4729.4 | 1.3027 | 80.9663 | 59.8258 | 1386.0503 |  | 3284 | 11822400 | 43358400 | 74894400 | 106430400
2029-05-14 21:00 | 3451.65 | 1 | 80.1024 | 59.8258 | 1011.5788 |  | 3285 | 11826000 | 43362000 | 74898000 | 106434000
2029-05-15 22:00 | 3210.76 | 1 | 63.3905 | 59.8258 | 940.9809 |  | 3286 | 11829600 | 43365600 | 74901600 | 106437600
2029-05-16 23:00 | 0 | 0 | 63.4641 | 59.8258 | 0 |  | 3287 | 11833200 | 43369200 | 74905200 | 106441200
2029-05-18 | -163.452 | 0.88899 | 62.0525 | 59.8258 | -47.9031 |  | 3288 | 11836800 | 43372800 | 74908800 | 106444800
2029-05-19 01:00 | -656.285 | 2.3165 | 61.2206 | 59.8258 | -192.3381 |  | 3289 | 11840400 | 43376400 | 74912400 | 106448400
2029-05-20 02:00 | -1412 | 4.3266 | 60.7542 | 59.8258 | -413.8164 |  | 3290 | 11844000 | 43380000 | 74916000 | 106452000
2029-05-21 03:00 | -1676.3 | 4.9117 | 60.3582 | 59.8258 | -491.275 |  | 3291 | 11847600 | 43383600 | 74919600 | 106455600
2029-05-22 04:00 | -2003.59 | 5.8119 | 60.0408 | 59.8258 | -587.1943 |  | 3292 | 11851200 | 43387200 | 74923200 | 106459200
2029-05-23 05:00 | -2045.48 | 5.8642 | 59.7837 | 59.8258 | -599.471 |  | 3293 | 11854800 | 43390800 | 74926800 | 106462800
2029-05-24 06:00 | -2283.63 | 6.108 | 59.474 | 59.8258 | -669.2659 |  | 3294 | 11858400 | 43394400 | 74930400 | 106466400
2029-05-25 07:00 | -2182.71 | 6.108 | 59.346 | 59.8258 | -639.6892 |  | 3295 | 11862000 | 43398000 | 74934000 | 106470000
2029-05-26 08:00 | -2871.6 | 6.108 | 58.6978 | 59.8258 | -841.5829 |  | 3296 | 11865600 | 43401600 | 74937600 | 106473600
2029-05-27 09:00 | -2453.45 | 6.108 | 58.7961 | 59.8258 | -719.0352 |  | 3297 | 11869200 | 43405200 | 74941200 | 106477200
2029-05-28 10:00 | -2122.63 | 6.108 | 58.9163 | 59.8258 | -622.0814 |  | 3298 | 11872800 | 43408800 | 74944800 | 106480800
2029-05-29 11:00 | -2287.8 | 6.108 | 58.7305 | 59.8258 | -670.488 |  | 3299 | 11876400 | 43412400 | 74948400 | 106484400
2029-05-30 12:00 | -1901.85 | 5.5058 | 58.7412 | 59.8258 | -557.3772 |  | 3300 | 11880000 | 43416000 | 74952000 | 106488000
2029-05-31 13:00 | -1741.42 | 5.0929 | 58.6797 | 59.8258 | -510.3598 |  | 3301 | 11883600 | 43419600 | 74955600 | 106491600
2029-06-01 14:00 | -1187.98 | 3.5291 | 58.6475 | 59.8258 | -348.1626 |  | 3302 | 11887200 | 43423200 | 74959200 | 106495200
2029-06-02 15:00 | -205.041 | 0.85136 | 59.0604 | 59.8258 | -60.0916 |  | 3303 | 11890800 | 43426800 | 74962800 | 106498800
2029-06-03 16:00 | 2788.95 | 1 | 59.9851 | 59.8258 | 817.3606 |  | 3304 | 11894400 | 43430400 | 74966400 | 106502400
2029-06-04 17:00 | 3120.33 | 1 | 60.3603 | 59.8258 | 914.4785 |  | 3305 | 11898000 | 43434000 | 74970000 | 106506000
2029-06-05 18:00 | 1255.43 | 1 | 60.7863 | 59.8258 | 367.9302 |  | 3306 | 11901600 | 43437600 | 74973600 | 106509600
2029-06-06 19:00 | -621.676 | 2.3267 | 59.5693 | 59.8258 | -182.1953 |  | 3307 | 11905200 | 43441200 | 74977200 | 106513200
2029-06-07 20:00 | -1706.48 | 5.2711 | 59.066 | 59.8258 | -500.1199 |  | 3308 | 11908800 | 43444800 | 74980800 | 106516800
2029-06-08 21:00 | -2491.1 | 6.108 | 58.4448 | 59.8258 | -730.0693 |  | 3309 | 11912400 | 43448400 | 74984400 | 106520400
2029-06-09 22:00 | -3719.56 | 6.108 | 57.248 | 59.8258 | -1090.0954 |  | 3310 | 11916000 | 43452000 | 74988000 | 106524000
2029-06-10 23:00 | -4381.94 | 6.108 | 56.4034 | 59.8258 | -1284.2198 |  | 3311 | 11919600 | 43455600 | 74991600 | 106527600
2029-06-12 | -4827.61 | 6.108 | 55.768 | 59.8258 | -1414.8328 |  | 3312 | 11923200 | 43459200 | 74995200 | 106531200
2029-06-13 01:00 | -5072.28 | 6.108 | 55.3476 | 59.8258 | -1486.5385 |  | 3313 | 11926800 | 43462800 | 74998800 | 106534800
2029-06-14 02:00 | -5341.23 | 6.108 | 54.9477 | 59.8258 | -1565.36 |  | 3314 | 11930400 | 43466400 | 75002400 | 106538400
2029-06-15 03:00 | -5578.15 | 6.108 | 54.5721 | 59.8258 | -1634.7944 |  | 3315 | 11934000 | 43470000 | 75006000 | 106542000
2029-06-16 04:00 | -5595.97 | 6.108 | 54.3482 | 59.8258 | -1640.0169 |  | 3316 | 11937600 | 43473600 | 75009600 | 106545600
2029-06-17 05:00 | -5549.72 | 6.108 | 54.2019 | 59.8258 | -1626.4624 |  | 3317 | 11941200 | 43477200 | 75013200 | 106549200
2029-06-18 06:00 | -4489.13 | 6.108 | 54.8614 | 59.8258 | -1315.6341 |  | 3318 | 11944800 | 43480800 | 75016800 | 106552800
2029-06-19 07:00 | -3400.57 | 6.108 | 55.7039 | 59.8258 | -996.6087 |  | 3319 | 11948400 | 43484400 | 75020400 | 106556400
2029-06-20 08:00 | -3247.15 | 6.108 | 55.9501 | 59.8258 | -951.6457 |  | 3320 | 11952000 | 43488000 | 75024000 | 106560000
2029-06-21 09:00 | -2373.86 | 6.108 | 56.6644 | 59.8258 | -695.7097 |  | 3321 | 11955600 | 43491600 | 75027600 | 106563600
2029-06-22 10:00 | -1625.22 | 4.813 | 57.0341 | 59.8258 | -476.305 |  | 3322 | 11959200 | 43495200 | 75031200 | 106567200
2029-06-23 11:00 | -685.896 | 2.1434 | 57.2955 | 59.8258 | -201.0163 |  | 3323 | 11962800 | 43498800 | 75034800 | 106570800
2029-06-24 12:00 | 2260.85 | 1 | 58.7778 | 59.8258 | 662.5897 |  | 3324 | 11966400 | 43502400 | 75038400 | 106574400
2029-06-25 13:00 | 2939.67 | 1 | 59.2261 | 59.8258 | 861.5322 |  | 3325 | 11970000 | 43506000 | 75042000 | 106578000
2029-06-26 14:00 | 2972.54 | 1 | 59.6182 | 59.8258 | 871.1655 |  | 3326 | 11973600 | 43509600 | 75045600 | 106581600
2029-06-27 15:00 | 2920.41 | 1 | 59.8528 | 59.8258 | 855.8877 |  | 3327 | 11977200 | 43513200 | 75049200 | 106585200
2029-06-28 16:00 | 3839.72 | 1.2956 | 73.862 | 59.8258 | 1125.3108 |  | 3328 | 11980800 | 43516800 | 75052800 | 106588800
2029-06-29 17:00 | 2948.92 | 1.008 | 73.917 | 59.8258 | 864.2431 |  | 3329 | 11984400 | 43520400 | 75056400 | 106592400
2029-06-30 18:00 | 2889.33 | 1 | 60.3132 | 59.8258 | 846.779 |  | 3330 | 11988000 | 43524000 | 75060000 | 106596000
2029-07-01 19:00 | 0 | 0 | 60.6135 | 59.8258 | 0 |  | 3331 | 11991600 | 43527600 | 75063600 | 106599600
2029-07-02 20:00 | -660.562 | 2.3918 | 59.0399 | 59.8258 | -193.5916 |  | 3332 | 11995200 | 43531200 | 75067200 | 106603200
2029-07-03 21:00 | -1354.42 | 4.2728 | 58.6244 | 59.8258 | -396.9413 |  | 3333 | 11998800 | 43534800 | 75070800 | 106606800
2029-07-04 22:00 | -1887.95 | 5.6666 | 58.3485 | 59.8258 | -553.3035 |  | 3334 | 12002400 | 43538400 | 75074400 | 106610400
2029-07-05 23:00 | -3761.66 | 6.108 | 56.8662 | 59.8258 | -1102.4337 |  | 3335 | 12006000 | 43542000 | 75078000 | 106614000
2029-07-07 | -4546.31 | 6.108 | 55.8575 | 59.8258 | -1332.3919 |  | 3336 | 12009600 | 43545600 | 75081600 | 106617600
2029-07-08 01:00 | -5013.97 | 6.108 | 55.1657 | 59.8258 | -1469.4496 |  | 3337 | 12013200 | 43549200 | 75085200 | 106621200
2029-07-09 02:00 | -5529.09 | 6.108 | 54.5024 | 59.8258 | -1620.4163 |  | 3338 | 12016800 | 43552800 | 75088800 | 106624800
2029-07-10 03:00 | -5225.77 | 6.108 | 54.4536 | 59.8258 | -1531.522 |  | 3339 | 12020400 | 43556400 | 75092400 | 106628400
2029-07-11 04:00 | -5523.73 | 6.108 | 54.0452 | 59.8258 | -1618.8455 |  | 3340 | 12024000 | 43560000 | 75096000 | 106632000
2029-07-12 05:00 | -5480.77 | 6.108 | 53.9032 | 59.8258 | -1606.2551 |  | 3341 | 12027600 | 43563600 | 75099600 | 106635600
2029-07-13 06:00 | -4068.42 | 6.108 | 54.813 | 59.8258 | -1192.3362 |  | 3342 | 12031200 | 43567200 | 75103200 | 106639200
2029-07-14 07:00 | -2710.56 | 6.108 | 55.9188 | 59.8258 | -794.3867 |  | 3343 | 12034800 | 43570800 | 75106800 | 106642800
2029-07-15 08:00 | -2122.89 | 6.108 | 56.5722 | 59.8258 | -622.1576 |  | 3344 | 12038400 | 43574400 | 75110400 | 106646400
2029-07-16 09:00 | -1346.09 | 3.9857 | 56.7693 | 59.8258 | -394.5 |  | 3345 | 12042000 | 43578000 | 75114000 | 106650000
2029-07-17 10:00 | 0.042022 | 1 | 58.504 | 59.8258 | 0.012315 |  | 3346 | 12045600 | 43581600 | 75117600 | 106653600
2029-07-18 11:00 | 2860.53 | 1 | 58.5702 | 59.8258 | 838.3386 |  | 3347 | 12049200 | 43585200 | 75121200 | 106657200
2029-07-19 12:00 | 3021.11 | 1 | 59.1193 | 59.8258 | 885.3999 |  | 3348 | 12052800 | 43588800 | 75124800 | 106660800
2029-07-20 13:00 | 2995.11 | 1 | 59.4664 | 59.8258 | 877.7801 |  | 3349 | 12056400 | 43592400 | 75128400 | 106664400
2029-07-21 14:00 | 3034.75 | 1 | 59.6845 | 59.8258 | 889.3974 |  | 3350 | 12060000 | 43596000 | 75132000 | 106668000
2029-07-22 15:00 | 2916.45 | 1 | 59.8908 | 59.8258 | 854.7271 |  | 3351 | 12063600 | 43599600 | 75135600 | 106671600
2029-07-23 16:00 | 3055.93 | 1 | 76.9501 | 59.8258 | 895.6047 |  | 3352 | 12067200 | 43603200 | 75139200 | 106675200
2029-07-24 17:00 | 2996.69 | 1 | 80.3099 | 59.8258 | 878.2431 |  | 3353 | 12070800 | 43606800 | 75142800 | 106678800
2029-07-25 18:00 | 2851.69 | 1 | 60.1951 | 59.8258 | 835.7478 |  | 3354 | 12074400 | 43610400 | 75146400 | 106682400
2029-07-26 19:00 | -91.0011 | 0.82922 | 60.0187 | 59.8258 | -26.6698 |  | 3355 | 12078000 | 43614000 | 75150000 | 106686000
2029-07-27 20:00 | -568.459 | 2.1362 | 58.9803 | 59.8258 | -166.5989 |  | 3356 | 12081600 | 43617600 | 75153600 | 106689600
2029-07-28 21:00 | -1097.7 | 3.5559 | 58.5728 | 59.8258 | -321.7041 |  | 3357 | 12085200 | 43621200 | 75157200 | 106693200
2029-07-29 22:00 | -1536.65 | 4.7098 | 58.3299 | 59.8258 | -450.3477 |  | 3358 | 12088800 | 43624800 | 75160800 | 106696800
2029-07-30 23:00 | -2801.58 | 6.108 | 57.532 | 59.8258 | -821.062 |  | 3359 | 12092400 | 43628400 | 75164400 | 106700400
2029-08-01 | -3505.59 | 6.108 | 56.6887 | 59.8258 | -1027.387 |  | 3360 | 12096000 | 43632000 | 75168000 | 106704000
2029-08-02 01:00 | -3897.21 | 6.108 | 56.1405 | 59.8258 | -1142.1595 |  | 3361 | 12099600 | 43635600 | 75171600 | 106707600
2029-08-03 02:00 | -4170.73 | 6.108 | 55.7269 | 59.8258 | -1222.3203 |  | 3362 | 12103200 | 43639200 | 75175200 | 106711200
2029-08-04 03:00 | -4167.76 | 6.108 | 55.5419 | 59.8258 | -1221.4499 |  | 3363 | 12106800 | 43642800 | 75178800 | 106714800
2029-08-05 04:00 | -4044.64 | 6.108 | 55.4871 | 59.8258 | -1185.367 |  | 3364 | 12110400 | 43646400 | 75182400 | 106718400
2029-08-06 05:00 | -3829.86 | 6.108 | 55.5556 | 59.8258 | -1122.4212 |  | 3365 | 12114000 | 43650000 | 75186000 | 106722000
2029-08-07 06:00 | -3284.11 | 6.108 | 55.8983 | 59.8258 | -962.4776 |  | 3366 | 12117600 | 43653600 | 75189600 | 106725600
2029-08-08 07:00 | -2579.76 | 6.108 | 56.4453 | 59.8258 | -756.053 |  | 3367 | 12121200 | 43657200 | 75193200 | 106729200
2029-08-09 08:00 | -2310.68 | 6.108 | 56.7313 | 59.8258 | -677.1935 |  | 3368 | 12124800 | 43660800 | 75196800 | 106732800
2029-08-10 09:00 | -1303.74 | 3.8559 | 56.9738 | 59.8258 | -382.0885 |  | 3369 | 12128400 | 43664400 | 75200400 | 106736400
2029-08-11 10:00 | -1279.57 | 3.9891 | 57.2029 | 59.8258 | -375.0049 |  | 3370 | 12132000 | 43668000 | 75204000 | 106740000
2029-08-12 11:00 | -602.594 | 1.9805 | 57.3477 | 59.8258 | -176.6029 |  | 3371 | 12135600 | 43671600 | 75207600 | 106743600
2029-08-13 12:00 | -755.581 | 2.6173 | 57.5325 | 59.8258 | -221.4389 |  | 3372 | 12139200 | 43675200 | 75211200 | 106747200
2029-08-14 13:00 | -150.964 | 0.79368 | 58.0191 | 59.8258 | -44.2432 |  | 3373 | 12142800 | 43678800 | 75214800 | 106750800
2029-08-15 14:00 | 0 | 1 | 58.9931 | 59.8258 | 0 |  | 3374 | 12146400 | 43682400 | 75218400 | 106754400
2029-08-16 15:00 | 2863.59 | 1 | 58.8074 | 59.8258 | 839.2354 |  | 3375 | 12150000 | 43686000 | 75222000 | 106758000
2029-08-17 16:00 | 3097.02 | 1 | 77.6232 | 59.8258 | 907.647 |  | 3376 | 12153600 | 43689600 | 75225600 | 106761600
2029-08-18 17:00 | 3047.23 | 1 | 82.0378 | 59.8258 | 893.055 |  | 3377 | 12157200 | 43693200 | 75229200 | 106765200
2029-08-19 18:00 | 2998.03 | 1 | 59.6353 | 59.8258 | 878.6359 |  | 3378 | 12160800 | 43696800 | 75232800 | 106768800
2029-08-20 19:00 | -232.905 | 1.2258 | 59.1908 | 59.8258 | -68.2577 |  | 3379 | 12164400 | 43700400 | 75236400 | 106772400
2029-08-21 20:00 | -1519.98 | 4.8633 | 58.3506 | 59.8258 | -445.4622 |  | 3380 | 12168000 | 43704000 | 75240000 | 106776000
2029-08-22 21:00 | -2267.87 | 6.108 | 57.7405 | 59.8258 | -664.6471 |  | 3381 | 12171600 | 43707600 | 75243600 | 106779600
2029-08-23 22:00 | -3651.14 | 6.108 | 56.4434 | 59.8258 | -1070.0435 |  | 3382 | 12175200 | 43711200 | 75247200 | 106783200
2029-08-24 23:00 | -4186.63 | 6.108 | 55.69 | 59.8258 | -1226.9801 |  | 3383 | 12178800 | 43714800 | 75250800 | 106786800
2029-08-26 | -4614.81 | 6.108 | 55.0584 | 59.8258 | -1352.4673 |  | 3384 | 12182400 | 43718400 | 75254400 | 106790400
2029-08-27 01:00 | -4887.18 | 6.108 | 54.6346 | 59.8258 | -1432.2911 |  | 3385 | 12186000 | 43722000 | 75258000 | 106794000
2029-08-28 02:00 | -5097.82 | 6.108 | 54.2948 | 59.8258 | -1494.0236 |  | 3386 | 12189600 | 43725600 | 75261600 | 106797600
2029-08-29 03:00 | -5127.3 | 6.108 | 54.076 | 59.8258 | -1502.6633 |  | 3387 | 12193200 | 43729200 | 75265200 | 106801200
2029-08-30 04:00 | -5148.29 | 6.108 | 53.9109 | 59.8258 | -1508.8149 |  | 3388 | 12196800 | 43732800 | 75268800 | 106804800
2029-08-31 05:00 | -4755.53 | 6.108 | 54.0734 | 59.8258 | -1393.7083 |  | 3389 | 12200400 | 43736400 | 75272400 | 106808400
2029-09-01 06:00 | -4104.78 | 6.108 | 54.4883 | 59.8258 | -1202.9923 |  | 3390 | 12204000 | 43740000 | 75276000 | 106812000
2029-09-02 07:00 | -3281.17 | 6.108 | 55.1344 | 59.8258 | -961.616 |  | 3391 | 12207600 | 43743600 | 75279600 | 106815600
2029-09-03 08:00 | -2718.8 | 6.108 | 55.6635 | 59.8258 | -796.8016 |  | 3392 | 12211200 | 43747200 | 75283200 | 106819200
2029-09-04 09:00 | -1460.91 | 4.3821 | 56.2864 | 59.8258 | -428.1505 |  | 3393 | 12214800 | 43750800 | 75286800 | 106822800
2029-09-05 10:00 | 0 | 0 | 58.0501 | 59.8258 | 0 |  | 3394 | 12218400 | 43754400 | 75290400 | 106826400
2029-09-06 11:00 | 2844.73 | 1 | 58.1269 | 59.8258 | 833.7081 |  | 3395 | 12222000 | 43758000 | 75294000 | 106830000
2029-09-07 12:00 | 3252.12 | 1 | 74.6244 | 59.8258 | 953.1023 |  | 3396 | 12225600 | 43761600 | 75297600 | 106833600
2029-09-08 13:00 | 3848.37 | 1.2208 | 73.7692 | 59.8258 | 1127.8459 |  | 3397 | 12229200 | 43765200 | 75301200 | 106837200
2029-09-09 14:00 | 5110.84 | 1.5795 | 74.4973 | 59.8258 | 1497.8393 |  | 3398 | 12232800 | 43768800 | 75304800 | 106840800
2029-09-10 15:00 | 6980.16 | 2.2624 | 74.2279 | 59.8258 | 2045.683 |  | 3399 | 12236400 | 43772400 | 75308400 | 106844400
2029-09-11 16:00 | 7789.8 | 2.4937 | 74.9524 | 59.8258 | 2282.965 |  | 3400 | 12240000 | 43776000 | 75312000 | 106848000
2029-09-12 17:00 | 7874.35 | 2.5204 | 75.3967 | 59.8258 | 2307.7442 |  | 3401 | 12243600 | 43779600 | 75315600 | 106851600
2029-09-13 18:00 | 6306.83 | 1.9721 | 76.0746 | 59.8258 | 1848.3494 |  | 3402 | 12247200 | 43783200 | 75319200 | 106855200
2029-09-14 19:00 | 3982.35 | 1.2893 | 75.6801 | 59.8258 | 1167.1116 |  | 3403 | 12250800 | 43786800 | 75322800 | 106858800
2029-09-15 20:00 | 3074.42 | 1 | 61.1266 | 59.8258 | 901.0236 |  | 3404 | 12254400 | 43790400 | 75326400 | 106862400
2029-09-16 21:00 | 0 | 0 | 61.2607 | 59.8258 | 0 |  | 3405 | 12258000 | 43794000 | 75330000 | 106866000
2029-09-17 22:00 | -1296.82 | 4.0685 | 59.3431 | 59.8258 | -380.0604 |  | 3406 | 12261600 | 43797600 | 75333600 | 106869600
2029-09-18 23:00 | -1811.67 | 5.4293 | 58.8218 | 59.8258 | -530.9481 |  | 3407 | 12265200 | 43801200 | 75337200 | 106873200
2029-09-20 | -2501.5 | 6.108 | 58.1669 | 59.8258 | -733.1173 |  | 3408 | 12268800 | 43804800 | 75340800 | 106876800
2029-09-21 01:00 | -2619.21 | 6.108 | 57.7986 | 59.8258 | -767.6147 |  | 3409 | 12272400 | 43808400 | 75344400 | 106880400
2029-09-22 02:00 | -3138.18 | 6.108 | 57.1797 | 59.8258 | -919.7098 |  | 3410 | 12276000 | 43812000 | 75348000 | 106884000
2029-09-23 03:00 | -3392.69 | 6.108 | 56.7671 | 59.8258 | -994.2993 |  | 3411 | 12279600 | 43815600 | 75351600 | 106887600
2029-09-24 04:00 | -3491.92 | 6.108 | 56.4897 | 59.8258 | -1023.3807 |  | 3412 | 12283200 | 43819200 | 75355200 | 106891200
2029-09-25 05:00 | -3179.66 | 6.108 | 56.5468 | 59.8258 | -931.8664 |  | 3413 | 12286800 | 43822800 | 75358800 | 106894800
2029-09-26 06:00 | -2492.79 | 6.108 | 56.9668 | 59.8258 | -730.5646 |  | 3414 | 12290400 | 43826400 | 75362400 | 106898400
2029-09-27 07:00 | -1344.62 | 3.9679 | 57.2863 | 59.8258 | -394.0692 |  | 3415 | 12294000 | 43830000 | 75366000 | 106902000
2029-09-28 08:00 | -679.505 | 2.2019 | 57.5531 | 59.8258 | -199.1433 |  | 3416 | 12297600 | 43833600 | 75369600 | 106905600
2029-09-29 09:00 | 2189.11 | 1 | 58.9365 | 59.8258 | 641.5648 |  | 3417 | 12301200 | 43837200 | 75373200 | 106909200
2029-09-30 10:00 | 3022.62 | 1 | 73.9916 | 59.8258 | 885.8425 |  | 3418 | 12304800 | 43840800 | 75376800 | 106912800
2029-10-01 11:00 | 4804.3 | 1.5337 | 74.3113 | 59.8258 | 1408.0013 |  | 3419 | 12308400 | 43844400 | 75380400 | 106916400
2029-10-02 12:00 | 6280.16 | 2.0301 | 74.5938 | 59.8258 | 1840.5332 |  | 3420 | 12312000 | 43848000 | 75384000 | 106920000
2029-10-03 13:00 | 6674.18 | 2.157 | 75.1036 | 59.8258 | 1956.0091 |  | 3421 | 12315600 | 43851600 | 75387600 | 106923600
2029-10-04 14:00 | 7376.53 | 2.3767 | 75.542 | 59.8258 | 2161.8475 |  | 3422 | 12319200 | 43855200 | 75391200 | 106927200
2029-10-05 15:00 | 9289.36 | 2.9934 | 75.8697 | 59.8258 | 2722.4427 |  | 3423 | 12322800 | 43858800 | 75394800 | 106930800
2029-10-06 16:00 | 9863.69 | 3.1981 | 76.3015 | 59.8258 | 2890.7622 |  | 3424 | 12326400 | 43862400 | 75398400 | 106934400
2029-10-07 17:00 | 9668.39 | 3.1123 | 76.8293 | 59.8258 | 2833.5254 |  | 3425 | 12330000 | 43866000 | 75402000 | 106938000
2029-10-08 18:00 | 7918.33 | 2.5132 | 77.3089 | 59.8258 | 2320.6334 |  | 3426 | 12333600 | 43869600 | 75405600 | 106941600
2029-10-09 19:00 | 5801.56 | 1.804 | 77.645 | 59.8258 | 1700.2694 |  | 3427 | 12337200 | 43873200 | 75409200 | 106945200
2029-10-10 20:00 | 3258.23 | 1 | 79.466 | 59.8258 | 954.893 |  | 3428 | 12340800 | 43876800 | 75412800 | 106948800
2029-10-11 21:00 | 3139.18 | 1 | 62.1204 | 59.8258 | 920.0028 |  | 3429 | 12344400 | 43880400 | 75416400 | 106952400
2029-10-12 22:00 | -458.456 | 1.8105 | 61.0527 | 59.8258 | -134.3602 |  | 3430 | 12348000 | 43884000 | 75420000 | 106956000
2029-10-13 23:00 | -1103.86 | 3.5304 | 60.1813 | 59.8258 | -323.5094 |  | 3431 | 12351600 | 43887600 | 75423600 | 106959600
2029-10-15 | -1409.96 | 4.2696 | 59.6516 | 59.8258 | -413.2185 |  | 3432 | 12355200 | 43891200 | 75427200 | 106963200
2029-10-16 01:00 | -1894.39 | 5.6121 | 59.3354 | 59.8258 | -555.1909 |  | 3433 | 12358800 | 43894800 | 75430800 | 106966800
2029-10-17 02:00 | -2049.23 | 5.9518 | 59.0481 | 59.8258 | -600.57 |  | 3434 | 12362400 | 43898400 | 75434400 | 106970400
2029-10-18 03:00 | -2124.08 | 6.108 | 58.7744 | 59.8258 | -622.5064 |  | 3435 | 12366000 | 43902000 | 75438000 | 106974000
2029-10-19 04:00 | -2389.7 | 6.108 | 58.4094 | 59.8258 | -700.3519 |  | 3436 | 12369600 | 43905600 | 75441600 | 106977600
2029-10-20 05:00 | -2085.91 | 6.0743 | 58.4477 | 59.8258 | -611.3199 |  | 3437 | 12373200 | 43909200 | 75445200 | 106981200
2029-10-21 06:00 | -1206.31 | 3.499 | 58.3352 | 59.8258 | -353.5346 |  | 3438 | 12376800 | 43912800 | 75448800 | 106984800
2029-10-22 07:00 | -224.762 | 0.91265 | 58.8175 | 59.8258 | -65.8712 |  | 3439 | 12380400 | 43916400 | 75452400 | 106988400
2029-10-23 08:00 | 2064 | 1 | 59.8999 | 59.8258 | 604.8987 |  | 3440 | 12384000 | 43920000 | 75456000 | 106992000
2029-10-24 09:00 | 2997.24 | 1 | 81.2937 | 59.8258 | 878.4043 |  | 3441 | 12387600 | 43923600 | 75459600 | 106995600
2029-10-25 10:00 | 4270.47 | 1.3794 | 74.8942 | 59.8258 | 1251.5512 |  | 3442 | 12391200 | 43927200 | 75463200 | 106999200
2029-10-26 11:00 | 5867.46 | 1.8892 | 75.3048 | 59.8258 | 1719.5828 |  | 3443 | 12394800 | 43930800 | 75466800 | 107002800
2029-10-27 12:00 | 6963.11 | 2.2749 | 75.5365 | 59.8258 | 2040.6861 |  | 3444 | 12398400 | 43934400 | 75470400 | 107006400
2029-10-28 13:00 | 8158.32 | 2.6134 | 76.2467 | 59.8258 | 2390.9676 |  | 3445 | 12402000 | 43938000 | 75474000 | 107010000
2029-10-29 14:00 | 8747.66 | 2.7955 | 76.7014 | 59.8258 | 2563.6861 |  | 3446 | 12405600 | 43941600 | 75477600 | 107013600
2029-10-30 15:00 | 10046 | 3.2827 | 76.7406 | 59.8258 | 2944.192 |  | 3447 | 12409200 | 43945200 | 75481200 | 107017200
2029-10-31 16:00 | 9996.7 | 3.2657 | 77.1759 | 59.8258 | 2929.7436 |  | 3448 | 12412800 | 43948800 | 75484800 | 107020800
2029-11-01 17:00 | 10123.6 | 3.2464 | 77.7288 | 59.8258 | 2966.9343 |  | 3449 | 12416400 | 43952400 | 75488400 | 107024400
2029-11-02 18:00 | 8717.23 | 2.6739 | 78.6312 | 59.8258 | 2554.7679 |  | 3450 | 12420000 | 43956000 | 75492000 | 107028000
2029-11-03 19:00 | 6634.14 | 2.0452 | 78.6031 | 59.8258 | 1944.2745 |  | 3451 | 12423600 | 43959600 | 75495600 | 107031600
2029-11-04 20:00 | 4117.96 | 1.2724 | 78.3908 | 59.8258 | 1206.8549 |  | 3452 | 12427200 | 43963200 | 75499200 | 107035200
2029-11-05 21:00 | 3216.91 | 1 | 81.6452 | 59.8258 | 942.7833 |  | 3453 | 12430800 | 43966800 | 75502800 | 107038800
2029-11-06 22:00 | 1245.8 | 1 | 62.8067 | 59.8258 | 365.1079 |  | 3454 | 12434400 | 43970400 | 75506400 | 107042400
2029-11-07 23:00 | -198.308 | 1.1223 | 61.6737 | 59.8258 | -58.1183 |  | 3455 | 12438000 | 43974000 | 75510000 | 107046000
2029-11-09 | -715.242 | 2.4766 | 60.6942 | 59.8258 | -209.6167 |  | 3456 | 12441600 | 43977600 | 75513600 | 107049600
2029-11-10 01:00 | -1074.7 | 3.3872 | 60.215 | 59.8258 | -314.9635 |  | 3457 | 12445200 | 43981200 | 75517200 | 107053200
2029-11-11 02:00 | -1239.98 | 3.785 | 59.9021 | 59.8258 | -363.4023 |  | 3458 | 12448800 | 43984800 | 75520800 | 107056800
2029-11-12 03:00 | -1253.25 | 3.7972 | 59.6474 | 59.8258 | -367.2913 |  | 3459 | 12452400 | 43988400 | 75524400 | 107060400
2029-11-13 04:00 | -1560.24 | 4.6857 | 59.4589 | 59.8258 | -457.2612 |  | 3460 | 12456000 | 43992000 | 75528000 | 107064000
2029-11-14 05:00 | -1059.14 | 3.1717 | 59.2682 | 59.8258 | -310.4033 |  | 3461 | 12459600 | 43995600 | 75531600 | 107067600
2029-11-15 06:00 | -450.359 | 1.5782 | 59.4108 | 59.8258 | -131.9872 |  | 3462 | 12463200 | 43999200 | 75535200 | 107071200
2029-11-16 07:00 | 2088.3 | 1 | 60.5433 | 59.8258 | 612.0203 |  | 3463 | 12466800 | 44002800 | 75538800 | 107074800
2029-11-17 08:00 | 3026.64 | 1 | 82.3143 | 59.8258 | 887.0206 |  | 3464 | 12470400 | 44006400 | 75542400 | 107078400
2029-11-18 09:00 | 4565.49 | 1.4404 | 75.7908 | 59.8258 | 1338.013 |  | 3465 | 12474000 | 44010000 | 75546000 | 107082000
2029-11-19 10:00 | 6279.53 | 2.1591 | 74.9685 | 59.8258 | 1840.3486 |  | 3466 | 12477600 | 44013600 | 75549600 | 107085600
2029-11-20 11:00 | 7746.54 | 2.6132 | 75.687 | 59.8258 | 2270.2868 |  | 3467 | 12481200 | 44017200 | 75553200 | 107089200
2029-11-21 12:00 | 8937.92 | 2.8419 | 77.0055 | 59.8258 | 2619.4458 |  | 3468 | 12484800 | 44020800 | 75556800 | 107092800
2029-11-22 13:00 | 9150.73 | 2.9131 | 77.4404 | 59.8258 | 2681.8142 |  | 3469 | 12488400 | 44024400 | 75560400 | 107096400
2029-11-23 14:00 | 9736.46 | 3.1207 | 77.6821 | 59.8258 | 2853.4748 |  | 3470 | 12492000 | 44028000 | 75564000 | 107100000
2029-11-24 15:00 | 11270.4 | 3.6446 | 77.8639 | 59.8258 | 3303.0282 |  | 3471 | 12495600 | 44031600 | 75567600 | 107103600
2029-11-25 16:00 | 11813.1 | 3.7694 | 78.4981 | 59.8258 | 3462.0779 |  | 3472 | 12499200 | 44035200 | 75571200 | 107107200
2029-11-26 17:00 | 11706 | 3.6596 | 79.1687 | 59.8258 | 3430.6899 |  | 3473 | 12502800 | 44038800 | 75574800 | 107110800
2029-11-27 18:00 | 9395.44 | 2.8917 | 79.6659 | 59.8258 | 2753.5317 |  | 3474 | 12506400 | 44042400 | 75578400 | 107114400
2029-11-28 19:00 | 7572.67 | 2.3255 | 79.6265 | 59.8258 | 2219.3305 |  | 3475 | 12510000 | 44046000 | 75582000 | 107118000
2029-11-29 20:00 | 5003.02 | 1.4867 | 79.9441 | 59.8258 | 1466.2404 |  | 3476 | 12513600 | 44049600 | 75585600 | 107121600
2029-11-30 21:00 | 3550.83 | 1.0985 | 78.9371 | 59.8258 | 1040.6455 |  | 3477 | 12517200 | 44053200 | 75589200 | 107125200
2029-12-01 22:00 | 3075.98 | 1 | 63.4881 | 59.8258 | 901.4807 |  | 3478 | 12520800 | 44056800 | 75592800 | 107128800
2029-12-02 23:00 | 0 | 0 | 63.472 | 59.8258 | 0 |  | 3479 | 12524400 | 44060400 | 75596400 | 107132400
2029-12-04 | -463.97 | 1.4957 | 61.4514 | 59.8258 | -135.9762 |  | 3480 | 12528000 | 44064000 | 75600000 | 107136000
2029-12-05 01:00 | -721.806 | 2.4529 | 61.0989 | 59.8258 | -211.5405 |  | 3481 | 12531600 | 44067600 | 75603600 | 107139600
2029-12-06 02:00 | -930.332 | 2.9626 | 60.7333 | 59.8258 | -272.6534 |  | 3482 | 12535200 | 44071200 | 75607200 | 107143200
2029-12-07 03:00 | -1200.81 | 3.689 | 60.4243 | 59.8258 | -351.9227 |  | 3483 | 12538800 | 44074800 | 75610800 | 107146800
2029-12-08 04:00 | -1342.2 | 4.0358 | 60.1261 | 59.8258 | -393.36 |  | 3484 | 12542400 | 44078400 | 75614400 | 107150400
2029-12-09 05:00 | -1409 | 4.2037 | 59.9177 | 59.8258 | -412.9371 |  | 3485 | 12546000 | 44082000 | 75618000 | 107154000
2029-12-10 06:00 | -280.074 | 0.98972 | 59.9937 | 59.8258 | -82.0816 |  | 3486 | 12549600 | 44085600 | 75621600 | 107157600
2029-12-11 07:00 | 2209 | 1 | 79.1251 | 59.8258 | 647.394 |  | 3487 | 12553200 | 44089200 | 75625200 | 107161200
2029-12-12 08:00 | 2877.81 | 1 | 84.3033 | 59.8258 | 843.4029 |  | 3488 | 12556800 | 44092800 | 75628800 | 107164800
2029-12-13 09:00 | 3939.08 | 1.2552 | 76.1744 | 59.8258 | 1154.4304 |  | 3489 | 12560400 | 44096400 | 75632400 | 107168400
2029-12-14 10:00 | 5812.42 | 1.9373 | 75.8002 | 59.8258 | 1703.4521 |  | 3490 | 12564000 | 44100000 | 75636000 | 107172000
2029-12-15 11:00 | 7396.96 | 2.5179 | 75.9466 | 59.8258 | 2167.835 |  | 3491 | 12567600 | 44103600 | 75639600 | 107175600
2029-12-16 12:00 | 8794.11 | 2.8155 | 77.2701 | 59.8258 | 2577.2992 |  | 3492 | 12571200 | 44107200 | 75643200 | 107179200
2029-12-17 13:00 | 9116.3 | 3.0848 | 76.9551 | 59.8258 | 2671.7238 |  | 3493 | 12574800 | 44110800 | 75646800 | 107182800
2029-12-18 14:00 | 9990.75 | 3.1915 | 78.1018 | 59.8258 | 2927.9998 |  | 3494 | 12578400 | 44114400 | 75650400 | 107186400
2029-12-19 15:00 | 9333.37 | 2.8636 | 79.0561 | 59.8258 | 2735.3407 |  | 3495 | 12582000 | 44118000 | 75654000 | 107190000
2029-12-20 16:00 | 10550 | 3.3759 | 78.601 | 59.8258 | 3091.8998 |  | 3496 | 12585600 | 44121600 | 75657600 | 107193600
2029-12-21 17:00 | 9003.61 | 2.9658 | 78.5053 | 59.8258 | 2638.6976 |  | 3497 | 12589200 | 44125200 | 75661200 | 107197200
2029-12-22 18:00 | 7843.29 | 2.42 | 79.4724 | 59.8258 | 2298.6414 |  | 3498 | 12592800 | 44128800 | 75664800 | 107200800
2029-12-23 19:00 | 5944.75 | 1.8139 | 79.5406 | 59.8258 | 1742.2342 |  | 3499 | 12596400 | 44132400 | 75668400 | 107204400
2029-12-24 20:00 | 4896.37 | 1.489 | 79.3484 | 59.8258 | 1434.9844 |  | 3500 | 12600000 | 44136000 | 75672000 | 107208000
2029-12-25 21:00 | 3719.82 | 1.1449 | 78.9504 | 59.8258 | 1090.1716 |  | 3501 | 12603600 | 44139600 | 75675600 | 107211600
2029-12-26 22:00 | 3166.16 | 1 | 81.4433 | 59.8258 | 927.9099 |  | 3502 | 12607200 | 44143200 | 75679200 | 107215200
2029-12-27 23:00 | 0 | 0 | 63.5837 | 59.8258 | 0 |  | 3503 | 12610800 | 44146800 | 75682800 | 107218800
2029-12-29 | -655.949 | 2.2546 | 61.6759 | 59.8258 | -192.2397 |  | 3504 | 12614400 | 44150400 | 75686400 | 107222400
2029-12-30 01:00 | -983.025 | 3.1124 | 61.1399 | 59.8258 | -288.0962 |  | 3505 | 12618000 | 44154000 | 75690000 | 107226000
2029-12-31 02:00 | -1377.48 | 4.1564 | 60.7654 | 59.8258 | -403.6995 |  | 3506 | 12621600 | 44157600 | 75693600 | 107229600
2030-01-01 03:00 | -1526.97 | 4.4983 | 60.448 | 59.8258 | -447.5107 |  | 3507 | 12625200 | 44161200 | 75697200 | 107233200
2030-01-02 04:00 | -1626.37 | 4.7644 | 60.1723 | 59.8258 | -476.642 |  | 3508 | 12628800 | 44164800 | 75700800 | 107236800
2030-01-03 05:00 | -1697.53 | 4.9528 | 59.9956 | 59.8258 | -497.4969 |  | 3509 | 12632400 | 44168400 | 75704400 | 107240400
2030-01-04 06:00 | -494.916 | 1.5236 | 59.9208 | 59.8258 | -145.0456 |  | 3510 | 12636000 | 44172000 | 75708000 | 107244000
2030-01-05 07:00 | 1934.14 | 1 | 61.2658 | 59.8258 | 566.8405 |  | 3511 | 12639600 | 44175600 | 75711600 | 107247600
2030-01-06 08:00 | 2853.86 | 1 | 82.6745 | 59.8258 | 836.3838 |  | 3512 | 12643200 | 44179200 | 75715200 | 107251200
2030-01-07 09:00 | 3884.79 | 1.2709 | 75.9457 | 59.8258 | 1138.5196 |  | 3513 | 12646800 | 44182800 | 75718800 | 107254800
2030-01-08 10:00 | 5961.12 | 1.9864 | 75.9432 | 59.8258 | 1747.0318 |  | 3514 | 12650400 | 44186400 | 75722400 | 107258400
2030-01-09 11:00 | 7726.99 | 2.5748 | 76.3963 | 59.8258 | 2264.5572 |  | 3515 | 12654000 | 44190000 | 75726000 | 107262000
2030-01-10 12:00 | 7065.51 | 2.2756 | 77.3861 | 59.8258 | 2070.6966 |  | 3516 | 12657600 | 44193600 | 75729600 | 107265600
2030-01-11 13:00 | 6502.96 | 2.0539 | 77.8626 | 59.8258 | 1905.8294 |  | 3517 | 12661200 | 44197200 | 75733200 | 107269200
2030-01-12 14:00 | 5908.91 | 1.6962 | 79.386 | 59.8258 | 1731.7306 |  | 3518 | 12664800 | 44200800 | 75736800 | 107272800
2030-01-13 15:00 | 5850.75 | 1.7876 | 78.4376 | 59.8258 | 1714.6856 |  | 3519 | 12668400 | 44204400 | 75740400 | 107276400
2030-01-14 16:00 | 9019.35 | 3.0897 | 76.8147 | 59.8258 | 2643.3106 |  | 3520 | 12672000 | 44208000 | 75744000 | 107280000
2030-01-15 17:00 | 7907.09 | 2.6341 | 77.6356 | 59.8258 | 2317.3393 |  | 3521 | 12675600 | 44211600 | 75747600 | 107283600
2030-01-16 18:00 | 7111.12 | 2.293 | 78.2158 | 59.8258 | 2084.0635 |  | 3522 | 12679200 | 44215200 | 75751200 | 107287200
2030-01-17 19:00 | 5888.57 | 1.7881 | 79.0732 | 59.8258 | 1725.7695 |  | 3523 | 12682800 | 44218800 | 75754800 | 107290800
2030-01-18 20:00 | 4971.77 | 1.5316 | 78.774 | 59.8258 | 1457.082 |  | 3524 | 12686400 | 44222400 | 75758400 | 107294400
2030-01-19 21:00 | 3873.82 | 1.1773 | 78.869 | 59.8258 | 1135.3046 |  | 3525 | 12690000 | 44226000 | 75762000 | 107298000
2030-01-20 22:00 | 3177.51 | 1 | 78.5166 | 59.8258 | 931.2363 |  | 3526 | 12693600 | 44229600 | 75765600 | 107301600
2030-01-21 23:00 | 0 | 0 | 63.3637 | 59.8258 | 0 |  | 3527 | 12697200 | 44233200 | 75769200 | 107305200
2030-01-23 | -546.487 | 1.8918 | 61.4935 | 59.8258 | -160.1595 |  | 3528 | 12700800 | 44236800 | 75772800 | 107308800
2030-01-24 01:00 | -789.843 | 2.6095 | 61.053 | 59.8258 | -231.4801 |  | 3529 | 12704400 | 44240400 | 75776400 | 107312400
2030-01-25 02:00 | -974.375 | 3.071 | 60.7471 | 59.8258 | -285.5611 |  | 3530 | 12708000 | 44244000 | 75780000 | 107316000
2030-01-26 03:00 | -1103.35 | 3.4003 | 60.5096 | 59.8258 | -323.36 |  | 3531 | 12711600 | 44247600 | 75783600 | 107319600
2030-01-27 04:00 | -1268.86 | 3.8481 | 60.264 | 59.8258 | -371.8662 |  | 3532 | 12715200 | 44251200 | 75787200 | 107323200
2030-01-28 05:00 | -1426.68 | 4.2623 | 60.0958 | 59.8258 | -418.1186 |  | 3533 | 12718800 | 44254800 | 75790800 | 107326800
2030-01-29 06:00 | -244.391 | 0.88182 | 60.21 | 59.8258 | -71.6239 |  | 3534 | 12722400 | 44258400 | 75794400 | 107330400
2030-01-30 07:00 | 1961.89 | 1 | 74.0919 | 59.8258 | 574.9732 |  | 3535 | 12726000 | 44262000 | 75798000 | 107334000
2030-01-31 08:00 | 2708.32 | 1 | 81.6457 | 59.8258 | 793.7302 |  | 3536 | 12729600 | 44265600 | 75801600 | 107337600
2030-02-01 09:00 | 3524.08 | 1.1664 | 75.7851 | 59.8258 | 1032.8059 |  | 3537 | 12733200 | 44269200 | 75805200 | 107341200
2030-02-02 10:00 | 5017.56 | 1.6088 | 76.4328 | 59.8258 | 1470.5017 |  | 3538 | 12736800 | 44272800 | 75808800 | 107344800
2030-02-03 11:00 | 6283.42 | 2.0897 | 76.2597 | 59.8258 | 1841.4886 |  | 3539 | 12740400 | 44276400 | 75812400 | 107348400
2030-02-04 12:00 | 6960.8 | 2.3152 | 76.6398 | 59.8258 | 2040.0091 |  | 3540 | 12744000 | 44280000 | 75816000 | 107352000
2030-02-05 13:00 | 6670.15 | 2.0961 | 77.7498 | 59.8258 | 1954.828 |  | 3541 | 12747600 | 44283600 | 75819600 | 107355600
2030-02-06 14:00 | 6539.58 | 2.0703 | 77.8103 | 59.8258 | 1916.5617 |  | 3542 | 12751200 | 44287200 | 75823200 | 107359200
2030-02-07 15:00 | 7399.66 | 2.3441 | 77.9241 | 59.8258 | 2168.6263 |  | 3543 | 12754800 | 44290800 | 75826800 | 107362800
2030-02-08 16:00 | 10214.9 | 3.454 | 77.2071 | 59.8258 | 2993.6917 |  | 3544 | 12758400 | 44294400 | 75830400 | 107366400
2030-02-09 17:00 | 9840.6 | 3.1119 | 78.6793 | 59.8258 | 2883.9952 |  | 3545 | 12762000 | 44298000 | 75834000 | 107370000
2030-02-10 18:00 | 8648.69 | 2.7049 | 79.116 | 59.8258 | 2534.6808 |  | 3546 | 12765600 | 44301600 | 75837600 | 107373600
2030-02-11 19:00 | 7152.59 | 2.1879 | 79.4853 | 59.8258 | 2096.2172 |  | 3547 | 12769200 | 44305200 | 75841200 | 107377200
2030-02-12 20:00 | 5950.13 | 1.8198 | 79.4106 | 59.8258 | 1743.811 |  | 3548 | 12772800 | 44308800 | 75844800 | 107380800
2030-02-13 21:00 | 4769.05 | 1.3914 | 80.0007 | 59.8258 | 1397.6706 |  | 3549 | 12776400 | 44312400 | 75848400 | 107384400
2030-02-14 22:00 | 3475.91 | 1.0918 | 78.64 | 59.8258 | 1018.6887 |  | 3550 | 12780000 | 44316000 | 75852000 | 107388000
2030-02-15 23:00 | 2951.08 | 1 | 63.5348 | 59.8258 | 864.8762 |  | 3551 | 12783600 | 44319600 | 75855600 | 107391600
2030-02-17 | 0 | 0 | 63.579 | 59.8258 | 0 |  | 3552 | 12787200 | 44323200 | 75859200 | 107395200
2030-02-18 01:00 | -358.299 | 1.3996 | 61.8899 | 59.8258 | -105.0071 |  | 3553 | 12790800 | 44326800 | 75862800 | 107398800
2030-02-19 02:00 | -429.595 | 1.6444 | 61.5201 | 59.8258 | -125.9019 |  | 3554 | 12794400 | 44330400 | 75866400 | 107402400
2030-02-20 03:00 | -537.239 | 1.9262 | 61.224 | 59.8258 | -157.4492 |  | 3555 | 12798000 | 44334000 | 75870000 | 107406000
2030-02-21 04:00 | -622.268 | 2.1434 | 60.9572 | 59.8258 | -182.3687 |  | 3556 | 12801600 | 44337600 | 75873600 | 107409600
2030-02-22 05:00 | -304.882 | 1.2426 | 60.961 | 59.8258 | -89.3521 |  | 3557 | 12805200 | 44341200 | 75877200 | 107413200
2030-02-23 06:00 | 2206.76 | 1 | 61.8105 | 59.8258 | 646.7375 |  | 3558 | 12808800 | 44344800 | 75880800 | 107416800
2030-02-24 07:00 | 3030.98 | 1 | 83.1492 | 59.8258 | 888.2926 |  | 3559 | 12812400 | 44348400 | 75884400 | 107420400
2030-02-25 08:00 | 3044.32 | 1 | 77.1928 | 59.8258 | 892.2021 |  | 3560 | 12816000 | 44352000 | 75888000 | 107424000
2030-02-26 09:00 | 5272.38 | 1.7018 | 76.7066 | 59.8258 | 1545.182 |  | 3561 | 12819600 | 44355600 | 75891600 | 107427600
2030-02-27 10:00 | 7220.99 | 2.4722 | 76.252 | 59.8258 | 2116.2633 |  | 3562 | 12823200 | 44359200 | 75895200 | 107431200
2030-02-28 11:00 | 9032.09 | 3.0493 | 76.9195 | 59.8258 | 2647.0443 |  | 3563 | 12826800 | 44362800 | 75898800 | 107434800
2030-03-01 12:00 | 9287.19 | 3.0195 | 77.9559 | 59.8258 | 2721.8067 |  | 3564 | 12830400 | 44366400 | 75902400 | 107438400
2030-03-02 13:00 | 8954.1 | 2.9183 | 78.2929 | 59.8258 | 2624.1877 |  | 3565 | 12834000 | 44370000 | 75906000 | 107442000
2030-03-03 14:00 | 10045.8 | 3.1823 | 78.9429 | 59.8258 | 2944.1334 |  | 3566 | 12837600 | 44373600 | 75909600 | 107445600
2030-03-04 15:00 | 11796.6 | 3.7675 | 79.1676 | 59.8258 | 3457.2422 |  | 3567 | 12841200 | 44377200 | 75913200 | 107449200
2030-03-05 16:00 | 12459.1 | 3.9931 | 79.5848 | 59.8258 | 3651.4018 |  | 3568 | 12844800 | 44380800 | 75916800 | 107452800
2030-03-06 17:00 | 12433 | 3.9778 | 79.9952 | 59.8258 | 3643.7526 |  | 3569 | 12848400 | 44384400 | 75920400 | 107456400
2030-03-07 18:00 | 10966 | 3.4188 | 80.6384 | 59.8258 | 3213.8174 |  | 3570 | 12852000 | 44388000 | 75924000 | 107460000
2030-03-08 19:00 | 9474.85 | 2.8894 | 81.0291 | 59.8258 | 2776.8044 |  | 3571 | 12855600 | 44391600 | 75927600 | 107463600
2030-03-09 20:00 | 6899.31 | 2.0627 | 81.2677 | 59.8258 | 2021.9882 |  | 3572 | 12859200 | 44395200 | 75931200 | 107467200
2030-03-10 21:00 | 5924.95 | 1.7317 | 81.2803 | 59.8258 | 1736.4314 |  | 3573 | 12862800 | 44398800 | 75934800 | 107470800
2030-03-11 22:00 | 3250.64 | 1.007 | 80.1048 | 59.8258 | 952.6685 |  | 3574 | 12866400 | 44402400 | 75938400 | 107474400
2030-03-12 23:00 | 3226.79 | 1 | 88.009 | 59.8258 | 945.6788 |  | 3575 | 12870000 | 44406000 | 75942000 | 107478000
2030-03-14 | 3189.33 | 1 | 64.2425 | 59.8258 | 934.7004 |  | 3576 | 12873600 | 44409600 | 75945600 | 107481600
2030-03-15 01:00 | 3116.97 | 1 | 64.0928 | 59.8258 | 913.4937 |  | 3577 | 12877200 | 44413200 | 75949200 | 107485200
2030-03-16 02:00 | 0 | 0 | 64.2461 | 59.8258 | 0 |  | 3578 | 12880800 | 44416800 | 75952800 | 107488800
2030-03-17 03:00 | 338.334 | 1 | 63.6731 | 59.8258 | 99.1559 |  | 3579 | 12884400 | 44420400 | 75956400 | 107492400
2030-03-18 04:00 | -69.7687 | 0.74759 | 63.0126 | 59.8258 | -20.4472 |  | 3580 | 12888000 | 44424000 | 75960000 | 107496000
2030-03-19 05:00 | 1868.65 | 1 | 63.0437 | 59.8258 | 547.6473 |  | 3581 | 12891600 | 44427600 | 75963600 | 107499600
2030-03-20 06:00 | 2875.41 | 1 | 62.9969 | 59.8258 | 842.6995 |  | 3582 | 12895200 | 44431200 | 75967200 | 107503200
2030-03-21 07:00 | 3180.53 | 1 | 79.8111 | 59.8258 | 932.1213 |  | 3583 | 12898800 | 44434800 | 75970800 | 107506800
2030-03-22 08:00 | 3760.22 | 1.1801 | 77.9969 | 59.8258 | 1102.0117 |  | 3584 | 12902400 | 44438400 | 75974400 | 107510400
2030-03-23 09:00 | 5575.97 | 1.8141 | 77.5928 | 59.8258 | 1634.1555 |  | 3585 | 12906000 | 44442000 | 75978000 | 107514000
2030-03-24 10:00 | 7465.26 | 2.5279 | 77.3741 | 59.8258 | 2187.8517 |  | 3586 | 12909600 | 44445600 | 75981600 | 107517600
2030-03-25 11:00 | 9315.68 | 3.1362 | 77.8568 | 59.8258 | 2730.1563 |  | 3587 | 12913200 | 44449200 | 75985200 | 107521200
2030-03-26 12:00 | 10115.9 | 3.2967 | 78.7679 | 59.8258 | 2964.6776 |  | 3588 | 12916800 | 44452800 | 75988800 | 107524800
2030-03-27 13:00 | 10479.8 | 3.3966 | 79.2446 | 59.8258 | 3071.3262 |  | 3589 | 12920400 | 44456400 | 75992400 | 107528400
2030-03-28 14:00 | 11313.8 | 3.6007 | 79.8563 | 59.8258 | 3315.7475 |  | 3590 | 12924000 | 44460000 | 75996000 | 107532000
2030-03-29 15:00 | 12563.8 | 4.1528 | 79.6802 | 59.8258 | 3682.0863 |  | 3591 | 12927600 | 44463600 | 75999600 | 107535600
2030-03-30 16:00 | 13542.9 | 4.3016 | 80.6605 | 59.8258 | 3969.0322 |  | 3592 | 12931200 | 44467200 | 76003200 | 107539200
2030-03-31 17:00 | 13434.5 | 4.2737 | 81.0328 | 59.8258 | 3937.2633 |  | 3593 | 12934800 | 44470800 | 76006800 | 107542800
2030-04-01 18:00 | 11836.5 | 3.6922 | 81.5923 | 59.8258 | 3468.9357 |  | 3594 | 12938400 | 44474400 | 76010400 | 107546400
2030-04-02 19:00 | 9807.75 | 3.0693 | 81.582 | 59.8258 | 2874.3678 |  | 3595 | 12942000 | 44478000 | 76014000 | 107550000
2030-04-03 20:00 | 7399.32 | 2.2505 | 81.856 | 59.8258 | 2168.5266 |  | 3596 | 12945600 | 44481600 | 76017600 | 107553600
2030-04-04 21:00 | 6333.94 | 1.8759 | 81.9115 | 59.8258 | 1856.2946 |  | 3597 | 12949200 | 44485200 | 76021200 | 107557200
2030-04-05 22:00 | 4049.03 | 1.2051 | 81.5295 | 59.8258 | 1186.6536 |  | 3598 | 12952800 | 44488800 | 76024800 | 107560800
2030-04-06 23:00 | 3346.3 | 1 | 84.327 | 59.8258 | 980.7037 |  | 3599 | 12956400 | 44492400 | 76028400 | 107564400
2030-04-08 | 3243.36 | 1 | 89.5359 | 59.8258 | 950.535 |  | 3600 | 12960000 | 44496000 | 76032000 | 107568000
2030-04-09 01:00 | 3181.08 | 1 | 64.7686 | 59.8258 | 932.2825 |  | 3601 | 12963600 | 44499600 | 76035600 | 107571600
2030-04-10 02:00 | 3151.55 | 1 | 64.6272 | 59.8258 | 923.6281 |  | 3602 | 12967200 | 44503200 | 76039200 | 107575200
2030-04-11 03:00 | 3217.75 | 1 | 64.4788 | 59.8258 | 943.0294 |  | 3603 | 12970800 | 44506800 | 76042800 | 107578800
2030-04-12 04:00 | 3121.56 | 1 | 64.4017 | 59.8258 | 914.8389 |  | 3604 | 12974400 | 44510400 | 76046400 | 107582400
2030-04-13 05:00 | 3203.54 | 1 | 64.2977 | 59.8258 | 938.8649 |  | 3605 | 12978000 | 44514000 | 76050000 | 107586000
2030-04-14 06:00 | 3322.66 | 1 | 83.9583 | 59.8258 | 973.7755 |  | 3606 | 12981600 | 44517600 | 76053600 | 107589600
2030-04-15 07:00 | 4319.92 | 1.3131 | 79.474 | 59.8258 | 1266.0436 |  | 3607 | 12985200 | 44521200 | 76057200 | 107593200
2030-04-16 08:00 | 4988.42 | 1.5376 | 79.3745 | 59.8258 | 1461.9616 |  | 3608 | 12988800 | 44524800 | 76060800 | 107596800
2030-04-17 09:00 | 6719.98 | 2.2924 | 78.0602 | 59.8258 | 1969.4317 |  | 3609 | 12992400 | 44528400 | 76064400 | 107600400
2030-04-18 10:00 | 8759.88 | 3.0121 | 78.2431 | 59.8258 | 2567.2674 |  | 3610 | 12996000 | 44532000 | 76068000 | 107604000
2030-04-19 11:00 | 10507.7 | 3.4256 | 79.4008 | 59.8258 | 3079.5029 |  | 3611 | 12999600 | 44535600 | 76071600 | 107607600
2030-04-20 12:00 | 11317.2 | 3.7453 | 79.6801 | 59.8258 | 3316.7439 |  | 3612 | 13003200 | 44539200 | 76075200 | 107611200
2030-04-21 13:00 | 12025 | 3.8292 | 80.6315 | 59.8258 | 3524.1796 |  | 3613 | 13006800 | 44542800 | 76078800 | 107614800
2030-04-22 14:00 | 12501.2 | 4.0691 | 80.6969 | 59.8258 | 3663.7401 |  | 3614 | 13010400 | 44546400 | 76082400 | 107618400
2030-04-23 15:00 | 13894.3 | 4.3958 | 81.4187 | 59.8258 | 4072.0174 |  | 3615 | 13014000 | 44550000 | 76086000 | 107622000
2030-04-24 16:00 | 14462.3 | 4.5549 | 81.8842 | 59.8258 | 4238.4817 |  | 3616 | 13017600 | 44553600 | 76089600 | 107625600
2030-04-25 17:00 | 14236.7 | 4.4903 | 82.2121 | 59.8258 | 4172.3649 |  | 3617 | 13021200 | 44557200 | 76093200 | 107629200
2030-04-26 18:00 | 12718.6 | 3.9726 | 82.5947 | 59.8258 | 3727.4537 |  | 3618 | 13024800 | 44560800 | 76096800 | 107632800
2030-04-27 19:00 | 10734.3 | 3.2807 | 82.937 | 59.8258 | 3145.9128 |  | 3619 | 13028400 | 44564400 | 76100400 | 107636400
2030-04-28 20:00 | 7808.71 | 2.3617 | 82.9492 | 59.8258 | 2288.507 |  | 3620 | 13032000 | 44568000 | 76104000 | 107640000
2030-04-29 21:00 | 6359.12 | 1.9088 | 82.6361 | 59.8258 | 1863.6741 |  | 3621 | 13035600 | 44571600 | 76107600 | 107643600
2030-04-30 22:00 | 3944.67 | 1.1791 | 82.3025 | 59.8258 | 1156.0687 |  | 3622 | 13039200 | 44575200 | 76111200 | 107647200
2030-05-01 23:00 | 3180.92 | 1 | 83.6485 | 59.8258 | 932.2356 |  | 3623 | 13042800 | 44578800 | 76114800 | 107650800
2030-05-03 | 3151.63 | 1 | 86.2696 | 59.8258 | 923.6516 |  | 3624 | 13046400 | 44582400 | 76118400 | 107654400
2030-05-04 01:00 | 3114.54 | 1 | 65.4382 | 59.8258 | 912.7816 |  | 3625 | 13050000 | 44586000 | 76122000 | 107658000
2030-05-05 02:00 | 3101.69 | 1 | 65.2511 | 59.8258 | 909.0156 |  | 3626 | 13053600 | 44589600 | 76125600 | 107661600
2030-05-06 03:00 | 3123.67 | 1 | 65.0697 | 59.8258 | 915.4573 |  | 3627 | 13057200 | 44593200 | 76129200 | 107665200
2030-05-07 04:00 | 3194.45 | 1 | 64.9397 | 59.8258 | 936.2009 |  | 3628 | 13060800 | 44596800 | 76132800 | 107668800
2030-05-08 05:00 | 3238.53 | 1 | 64.8346 | 59.8258 | 949.1195 |  | 3629 | 13064400 | 44600400 | 76136400 | 107672400
2030-05-09 06:00 | 3244.94 | 1 | 64.7462 | 59.8258 | 950.998 |  | 3630 | 13068000 | 44604000 | 76140000 | 107676000
2030-05-10 07:00 | 3205.94 | 1 | 64.6705 | 59.8258 | 939.5683 |  | 3631 | 13071600 | 44607600 | 76143600 | 107679600
2030-05-11 08:00 | 3087.88 | 1 | 64.6197 | 59.8258 | 904.9683 |  | 3632 | 13075200 | 44611200 | 76147200 | 107683200
2030-05-12 09:00 | 3293.64 | 1 | 64.5238 | 59.8258 | 965.2706 |  | 3633 | 13078800 | 44614800 | 76150800 | 107686800
2030-05-13 10:00 | 3242.17 | 1 | 64.4926 | 59.8258 | 950.1862 |  | 3634 | 13082400 | 44618400 | 76154400 | 107690400
2030-05-14 11:00 | 3267.96 | 1 | 88.5699 | 59.8258 | 957.7445 |  | 3635 | 13086000 | 44622000 | 76158000 | 107694000
2030-05-15 12:00 | 3342.75 | 1.034 | 79.3974 | 59.8258 | 979.6633 |  | 3636 | 13089600 | 44625600 | 76161600 | 107697600
2030-05-16 13:00 | 4086.97 | 1.2748 | 79.2252 | 59.8258 | 1197.7727 |  | 3637 | 13093200 | 44629200 | 76165200 | 107701200
2030-05-17 14:00 | 4960.89 | 1.5925 | 78.8339 | 59.8258 | 1453.8933 |  | 3638 | 13096800 | 44632800 | 76168800 | 107704800
2030-05-18 15:00 | 6316.19 | 2.0675 | 78.6365 | 59.8258 | 1851.0926 |  | 3639 | 13100400 | 44636400 | 76172400 | 107708400
2030-05-19 16:00 | 6421.37 | 2.0701 | 79.0345 | 59.8258 | 1881.9178 |  | 3640 | 13104000 | 44640000 | 76176000 | 107712000
2030-05-20 17:00 | 6536.07 | 2.1336 | 78.9482 | 59.8258 | 1915.533 |  | 3641 | 13107600 | 44643600 | 76179600 | 107715600
2030-05-21 18:00 | 4885.92 | 1.5363 | 79.5604 | 59.8258 | 1431.9218 |  | 3642 | 13111200 | 44647200 | 76183200 | 107719200
2030-05-22 19:00 | 3587.67 | 1.1421 | 79.2261 | 59.8258 | 1051.4423 |  | 3643 | 13114800 | 44650800 | 76186800 | 107722800
2030-05-23 20:00 | 3146.16 | 1 | 64.3513 | 59.8258 | 922.0485 |  | 3644 | 13118400 | 44654400 | 76190400 | 107726400
2030-05-24 21:00 | 0 | 0 | 64.4514 | 59.8258 | 0 |  | 3645 | 13122000 | 44658000 | 76194000 | 107730000
2030-05-25 22:00 | -780.978 | 2.6522 | 62.5777 | 59.8258 | -228.8821 |  | 3646 | 13125600 | 44661600 | 76197600 | 107733600
2030-05-26 23:00 | -1346.56 | 4.0511 | 61.9725 | 59.8258 | -394.6378 |  | 3647 | 13129200 | 44665200 | 76201200 | 107737200
2030-05-28 | -1534.72 | 4.4643 | 61.6052 | 59.8258 | -449.782 |  | 3648 | 13132800 | 44668800 | 76204800 | 107740800
2030-05-29 01:00 | -1646.65 | 4.7543 | 61.3338 | 59.8258 | -482.5855 |  | 3649 | 13136400 | 44672400 | 76208400 | 107744400
2030-05-30 02:00 | -1674.2 | 4.8194 | 61.0846 | 59.8258 | -490.6596 |  | 3650 | 13140000 | 44676000 | 76212000 | 107748000
2030-05-31 03:00 | -1847.3 | 5.3133 | 60.9047 | 59.8258 | -541.3902 |  | 3651 | 13143600 | 44679600 | 76215600 | 107751600
2030-06-01 04:00 | -1793.91 | 5.1276 | 60.7138 | 59.8258 | -525.7431 |  | 3652 | 13147200 | 44683200 | 76219200 | 107755200
2030-06-02 05:00 | -1847.92 | 5.3084 | 60.5695 | 59.8258 | -541.5719 |  | 3653 | 13150800 | 44686800 | 76222800 | 107758800
2030-06-03 06:00 | -816.064 | 2.3812 | 60.4509 | 59.8258 | -239.1647 |  | 3654 | 13154400 | 44690400 | 76226400 | 107762400
2030-06-04 07:00 | -143.853 | 0.77234 | 61.1813 | 59.8258 | -42.1592 |  | 3655 | 13158000 | 44694000 | 76230000 | 107766000
2030-06-05 08:00 | -343.666 | 1.4696 | 61.0166 | 59.8258 | -100.7186 |  | 3656 | 13161600 | 44697600 | 76233600 | 107769600
2030-06-06 09:00 | -127.929 | 0.81158 | 61.3464 | 59.8258 | -37.4923 |  | 3657 | 13165200 | 44701200 | 76237200 | 107773200
2030-06-07 10:00 | 2171.11 | 1 | 61.8731 | 59.8258 | 636.2895 |  | 3658 | 13168800 | 44704800 | 76240800 | 107776800
2030-06-08 11:00 | 3090.48 | 1.0641 | 75.6822 | 59.8258 | 905.7303 |  | 3659 | 13172400 | 44708400 | 76244400 | 107780400
2030-06-09 12:00 | 4135.7 | 1.2893 | 77.2917 | 59.8258 | 1212.054 |  | 3660 | 13176000 | 44712000 | 76248000 | 107784000
2030-06-10 13:00 | 5522.5 | 1.8192 | 76.7516 | 59.8258 | 1618.485 |  | 3661 | 13179600 | 44715600 | 76251600 | 107787600
2030-06-11 14:00 | 7146.38 | 2.408 | 76.7861 | 59.8258 | 2094.3972 |  | 3662 | 13183200 | 44719200 | 76255200 | 107791200
2030-06-12 15:00 | 8252.22 | 2.7195 | 77.5258 | 59.8258 | 2418.4869 |  | 3663 | 13186800 | 44722800 | 76258800 | 107794800
2030-06-13 16:00 | 10709.1 | 3.54 | 77.8644 | 59.8258 | 3138.5274 |  | 3664 | 13190400 | 44726400 | 76262400 | 107798400
2030-06-14 17:00 | 9792.51 | 3.0161 | 79.4723 | 59.8258 | 2869.9014 |  | 3665 | 13194000 | 44730000 | 76266000 | 107802000
2030-06-15 18:00 | 8113.53 | 2.5002 | 79.7414 | 59.8258 | 2377.8409 |  | 3666 | 13197600 | 44733600 | 76269600 | 107805600
2030-06-16 19:00 | 6861.58 | 2.0966 | 79.86 | 59.8258 | 2010.9306 |  | 3667 | 13201200 | 44737200 | 76273200 | 107809200
2030-06-17 20:00 | 5947.97 | 1.7466 | 80.3969 | 59.8258 | 1743.1779 |  | 3668 | 13204800 | 44740800 | 76276800 | 107812800
2030-06-18 21:00 | 4856.12 | 1.4185 | 80.4101 | 59.8258 | 1423.1883 |  | 3669 | 13208400 | 44744400 | 76280400 | 107816400
2030-06-19 22:00 | 3813.16 | 1.1927 | 79.1874 | 59.8258 | 1117.5269 |  | 3670 | 13212000 | 44748000 | 76284000 | 107820000
2030-06-20 23:00 | 2749.16 | 1 | 64.1126 | 59.8258 | 805.6993 |  | 3671 | 13215600 | 44751600 | 76287600 | 107823600
2030-06-22 | -69.3656 | 0.75537 | 63.6989 | 59.8258 | -20.3291 |  | 3672 | 13219200 | 44755200 | 76291200 | 107827200
2030-06-23 01:00 | -338.27 | 1.4326 | 62.518 | 59.8258 | -99.1372 |  | 3673 | 13222800 | 44758800 | 76294800 | 107830800
2030-06-24 02:00 | -525.169 | 1.8945 | 61.9772 | 59.8258 | -153.9118 |  | 3674 | 13226400 | 44762400 | 76298400 | 107834400
2030-06-25 03:00 | -644.896 | 2.1912 | 61.646 | 59.8258 | -189.0004 |  | 3675 | 13230000 | 44766000 | 76302000 | 107838000
2030-06-26 04:00 | -687.9 | 2.291 | 61.3653 | 59.8258 | -201.6036 |  | 3676 | 13233600 | 44769600 | 76305600 | 107841600
2030-06-27 05:00 | -858.101 | 2.7623 | 61.1046 | 59.8258 | -251.4846 |  | 3677 | 13237200 | 44773200 | 76309200 | 107845200
2030-06-28 06:00 | 0 | 0 | 62.3725 | 59.8258 | 0 |  | 3678 | 13240800 | 44776800 | 76312800 | 107848800
2030-06-29 07:00 | 2016.92 | 1 | 62.1813 | 59.8258 | 591.1009 |  | 3679 | 13244400 | 44780400 | 76316400 | 107852400
2030-06-30 08:00 | 0 | 0 | 62.5964 | 59.8258 | 0 |  | 3680 | 13248000 | 44784000 | 76320000 | 107856000
2030-07-01 09:00 | 3469.02 | 1 | 62.1135 | 59.8258 | 1016.6694 |  | 3681 | 13251600 | 44787600 | 76323600 | 107859600
2030-07-02 10:00 | 3510.05 | 1 | 62.4505 | 59.8258 | 1028.6941 |  | 3682 | 13255200 | 44791200 | 76327200 | 107863200
2030-07-03 11:00 | 3312.55 | 1 | 84.3425 | 59.8258 | 970.8126 |  | 3683 | 13258800 | 44794800 | 76330800 | 107866800
2030-07-04 12:00 | 3698.33 | 1.1213 | 78.1248 | 59.8258 | 1083.8735 |  | 3684 | 13262400 | 44798400 | 76334400 | 107870400
2030-07-05 13:00 | 5061.34 | 1.5366 | 78.2027 | 59.8258 | 1483.3323 |  | 3685 | 13266000 | 44802000 | 76338000 | 107874000
2030-07-06 14:00 | 4710.07 | 1.3991 | 78.8312 | 59.8258 | 1380.3853 |  | 3686 | 13269600 | 44805600 | 76341600 | 107877600
2030-07-07 15:00 | 5534.65 | 1.7425 | 78.0241 | 59.8258 | 1622.0458 |  | 3687 | 13273200 | 44809200 | 76345200 | 107881200
2030-07-08 16:00 | 8863.09 | 3.0749 | 76.8016 | 59.8258 | 2597.5153 |  | 3688 | 13276800 | 44812800 | 76348800 | 107884800
2030-07-09 17:00 | 8498.55 | 2.8447 | 77.8536 | 59.8258 | 2490.6791 |  | 3689 | 13280400 | 44816400 | 76352400 | 107888400
2030-07-10 18:00 | 7471.45 | 2.3688 | 78.9189 | 59.8258 | 2189.6658 |  | 3690 | 13284000 | 44820000 | 76356000 | 107892000
2030-07-11 19:00 | 6244.99 | 1.9336 | 79.2963 | 59.8258 | 1830.2259 |  | 3691 | 13287600 | 44823600 | 76359600 | 107895600
2030-07-12 20:00 | 5607.31 | 1.6051 | 80.4769 | 59.8258 | 1643.3403 |  | 3692 | 13291200 | 44827200 | 76363200 | 107899200
2030-07-13 21:00 | 4895.22 | 1.4241 | 80.1723 | 59.8258 | 1434.6474 |  | 3693 | 13294800 | 44830800 | 76366800 | 107902800
2030-07-14 22:00 | 4053.17 | 1.2569 | 79.0743 | 59.8258 | 1187.8669 |  | 3694 | 13298400 | 44834400 | 76370400 | 107906400
2030-07-15 23:00 | 3139.71 | 1 | 63.8982 | 59.8258 | 920.1582 |  | 3695 | 13302000 | 44838000 | 76374000 | 107910000
2030-07-17 | 2954.53 | 1 | 63.7431 | 59.8258 | 865.8873 |  | 3696 | 13305600 | 44841600 | 76377600 | 107913600
2030-07-18 01:00 | 36.1268 | 1 | 63.8954 | 59.8258 | 10.5877 |  | 3697 | 13309200 | 44845200 | 76381200 | 107917200
2030-07-19 02:00 | 489.717 | 1 | 63.4093 | 59.8258 | 143.5219 |  | 3698 | 13312800 | 44848800 | 76384800 | 107920800
2030-07-20 03:00 | 3329.97 | 1 | 62.9521 | 59.8258 | 975.9179 |  | 3699 | 13316400 | 44852400 | 76388400 | 107924400
2030-07-21 04:00 | 1172.11 | 1 | 63.3871 | 59.8258 | 343.5115 |  | 3700 | 13320000 | 44856000 | 76392000 | 107928000
2030-07-22 05:00 | 1910.99 | 1 | 63.1166 | 59.8258 | 560.0559 |  | 3701 | 13323600 | 44859600 | 76395600 | 107931600
2030-07-23 06:00 | 2770.44 | 1 | 82.1801 | 59.8258 | 811.9358 |  | 3702 | 13327200 | 44863200 | 76399200 | 107935200
2030-07-24 07:00 | 3628.1 | 1.1905 | 77.2685 | 59.8258 | 1063.2911 |  | 3703 | 13330800 | 44866800 | 76402800 | 107938800
2030-07-25 08:00 | 4214.45 | 1.3362 | 77.9563 | 59.8258 | 1235.1334 |  | 3704 | 13334400 | 44870400 | 76406400 | 107942400
2030-07-26 09:00 | 5684.16 | 1.8832 | 77.44 | 59.8258 | 1665.8629 |  | 3705 | 13338000 | 44874000 | 76410000 | 107946000
2030-07-27 10:00 | 7380.08 | 2.495 | 77.4555 | 59.8258 | 2162.8879 |  | 3706 | 13341600 | 44877600 | 76413600 | 107949600
2030-07-28 11:00 | 8960.44 | 2.9631 | 78.1649 | 59.8258 | 2626.0457 |  | 3707 | 13345200 | 44881200 | 76417200 | 107953200
2030-07-29 12:00 | 9791.9 | 3.0895 | 79.2834 | 59.8258 | 2869.7226 |  | 3708 | 13348800 | 44884800 | 76420800 | 107956800
2030-07-30 13:00 | 9814.35 | 3.1991 | 79.2431 | 59.8258 | 2876.3021 |  | 3709 | 13352400 | 44888400 | 76424400 | 107960400
2030-07-31 14:00 | 10722.6 | 3.4451 | 79.7486 | 59.8258 | 3142.4839 |  | 3710 | 13356000 | 44892000 | 76428000 | 107964000
2030-08-01 15:00 | 12555.9 | 4.118 | 79.7742 | 59.8258 | 3679.771 |  | 3711 | 13359600 | 44895600 | 76431600 | 107967600
2030-08-02 16:00 | 13275.1 | 4.3192 | 80.3619 | 59.8258 | 3890.5478 |  | 3712 | 13363200 | 44899200 | 76435200 | 107971200
2030-08-03 17:00 | 13490 | 4.2791 | 81.1251 | 59.8258 | 3953.5287 |  | 3713 | 13366800 | 44902800 | 76438800 | 107974800
2030-08-04 18:00 | 11999.7 | 3.7445 | 81.6834 | 59.8258 | 3516.7649 |  | 3714 | 13370400 | 44906400 | 76442400 | 107978400
2030-08-05 19:00 | 10086.3 | 3.139 | 81.8096 | 59.8258 | 2956.0027 |  | 3715 | 13374000 | 44910000 | 76446000 | 107982000
2030-08-06 20:00 | 7397.7 | 2.2406 | 82.1048 | 59.8258 | 2168.0519 |  | 3716 | 13377600 | 44913600 | 76449600 | 107985600
2030-08-07 21:00 | 6353.42 | 1.8416 | 82.4091 | 59.8258 | 1862.0036 |  | 3717 | 13381200 | 44917200 | 76453200 | 107989200
2030-08-08 22:00 | 3804.76 | 1.0982 | 82.1613 | 59.8258 | 1115.0651 |  | 3718 | 13384800 | 44920800 | 76456800 | 107992800
2030-08-09 23:00 | 3232.53 | 1 | 85.1402 | 59.8258 | 947.361 |  | 3719 | 13388400 | 44924400 | 76460400 | 107996400
2030-08-11 | 3235.42 | 1 | 90.1491 | 59.8258 | 948.208 |  | 3720 | 13392000 | 44928000 | 76464000 | 108000000
2030-08-12 01:00 | 3155.05 | 1 | 64.908 | 59.8258 | 924.6539 |  | 3721 | 13395600 | 44931600 | 76467600 | 108003600
2030-08-13 02:00 | 3027.09 | 1 | 64.7734 | 59.8258 | 887.1525 |  | 3722 | 13399200 | 44935200 | 76471200 | 108007200
2030-08-14 03:00 | 3131.99 | 1 | 64.5816 | 59.8258 | 917.8957 |  | 3723 | 13402800 | 44938800 | 76474800 | 108010800
2030-08-15 04:00 | 3226.94 | 1 | 64.4776 | 59.8258 | 945.7228 |  | 3724 | 13406400 | 44942400 | 76478400 | 108014400
2030-08-16 05:00 | 3233.53 | 1 | 90.0011 | 59.8258 | 947.6541 |  | 3725 | 13410000 | 44946000 | 76482000 | 108018000
2030-08-17 06:00 | 3360.76 | 1 | 80.6757 | 59.8258 | 984.9415 |  | 3726 | 13413600 | 44949600 | 76485600 | 108021600
2030-08-18 07:00 | 4712.46 | 1.4455 | 79.4417 | 59.8258 | 1381.0857 |  | 3727 | 13417200 | 44953200 | 76489200 | 108025200
2030-08-19 08:00 | 5591.9 | 1.8317 | 78.6537 | 59.8258 | 1638.8241 |  | 3728 | 13420800 | 44956800 | 76492800 | 108028800
2030-08-20 09:00 | 7269.76 | 2.3408 | 79.0787 | 59.8258 | 2130.5563 |  | 3729 | 13424400 | 44960400 | 76496400 | 108032400
2030-08-21 10:00 | 9327.54 | 2.9759 | 79.5369 | 59.8258 | 2733.6321 |  | 3730 | 13428000 | 44964000 | 76500000 | 108036000
2030-08-22 11:00 | 10619.1 | 3.5785 | 79.257 | 59.8258 | 3112.151 |  | 3731 | 13431600 | 44967600 | 76503600 | 108039600
2030-08-23 12:00 | 12102.6 | 3.8802 | 80.4259 | 59.8258 | 3546.9219 |  | 3732 | 13435200 | 44971200 | 76507200 | 108043200
2030-08-24 13:00 | 12685.7 | 4.0521 | 80.9799 | 59.8258 | 3717.8117 |  | 3733 | 13438800 | 44974800 | 76510800 | 108046800
2030-08-25 14:00 | 12886.8 | 4.2827 | 80.8554 | 59.8258 | 3776.7483 |  | 3734 | 13442400 | 44978400 | 76514400 | 108050400
2030-08-26 15:00 | 15040.9 | 4.8026 | 81.7282 | 59.8258 | 4408.0527 |  | 3735 | 13446000 | 44982000 | 76518000 | 108054000
2030-08-27 16:00 | 15320.1 | 4.8827 | 82.2717 | 59.8258 | 4489.8781 |  | 3736 | 13449600 | 44985600 | 76521600 | 108057600
2030-08-28 17:00 | 15203 | 4.8689 | 82.6025 | 59.8258 | 4455.5595 |  | 3737 | 13453200 | 44989200 | 76525200 | 108061200
2030-08-29 18:00 | 13590.9 | 4.2845 | 83.1099 | 59.8258 | 3983.0996 |  | 3738 | 13456800 | 44992800 | 76528800 | 108064800
2030-08-30 19:00 | 11890.3 | 3.6542 | 83.5302 | 59.8258 | 3484.7029 |  | 3739 | 13460400 | 44996400 | 76532400 | 108068400
2030-08-31 20:00 | 9126.46 | 2.7648 | 83.6651 | 59.8258 | 2674.7014 |  | 3740 | 13464000 | 45000000 | 76536000 | 108072000
2030-09-01 21:00 | 7478.36 | 2.2653 | 83.3015 | 59.8258 | 2191.691 |  | 3741 | 13467600 | 45003600 | 76539600 | 108075600
2030-09-02 22:00 | 5465.5 | 1.5599 | 83.8432 | 59.8258 | 1601.7799 |  | 3742 | 13471200 | 45007200 | 76543200 | 108079200
2030-09-03 23:00 | 4478.98 | 1.2814 | 83.3229 | 59.8258 | 1312.6595 |  | 3743 | 13474800 | 45010800 | 76546800 | 108082800
2030-09-05 | 3708.23 | 1.1227 | 82.0232 | 59.8258 | 1086.7749 |  | 3744 | 13478400 | 45014400 | 76550400 | 108086400
2030-09-06 01:00 | 3217.5 | 1 | 82.2318 | 59.8258 | 942.9562 |  | 3745 | 13482000 | 45018000 | 76554000 | 108090000
2030-09-07 02:00 | 3101.7 | 1 | 83.7153 | 59.8258 | 909.0185 |  | 3746 | 13485600 | 45021600 | 76557600 | 108093600
2030-09-08 03:00 | 3144.01 | 1 | 83.4878 | 59.8258 | 921.4184 |  | 3747 | 13489200 | 45025200 | 76561200 | 108097200
2030-09-09 04:00 | 3164.29 | 1 | 83.836 | 59.8258 | 927.3619 |  | 3748 | 13492800 | 45028800 | 76564800 | 108100800
2030-09-10 05:00 | 3817.12 | 1.1957 | 80.2912 | 59.8258 | 1118.6874 |  | 3749 | 13496400 | 45032400 | 76568400 | 108104400
2030-09-11 06:00 | 5096.8 | 1.5965 | 80.2622 | 59.8258 | 1493.7246 |  | 3750 | 13500000 | 45036000 | 76572000 | 108108000
2030-09-12 07:00 | 6392.67 | 2.0872 | 79.7887 | 59.8258 | 1873.5066 |  | 3751 | 13503600 | 45039600 | 76575600 | 108111600
2030-09-13 08:00 | 7107.04 | 2.2179 | 80.6683 | 59.8258 | 2082.8678 |  | 3752 | 13507200 | 45043200 | 76579200 | 108115200
2030-09-14 09:00 | 8523.74 | 2.9172 | 79.586 | 59.8258 | 2498.0616 |  | 3753 | 13510800 | 45046800 | 76582800 | 108118800
2030-09-15 10:00 | 10722.9 | 3.6088 | 80.1299 | 59.8258 | 3142.5718 |  | 3754 | 13514400 | 45050400 | 76586400 | 108122400
2030-09-16 11:00 | 12550.7 | 4.0699 | 81.1374 | 59.8258 | 3678.2471 |  | 3755 | 13518000 | 45054000 | 76590000 | 108126000
2030-09-17 12:00 | 13283.2 | 4.3575 | 81.5165 | 59.8258 | 3892.9216 |  | 3756 | 13521600 | 45057600 | 76593600 | 108129600
2030-09-18 13:00 | 13829.5 | 4.5361 | 81.9535 | 59.8258 | 4053.0264 |  | 3757 | 13525200 | 45061200 | 76597200 | 108133200
2030-09-19 14:00 | 14868.8 | 4.8643 | 82.3704 | 59.8258 | 4357.6151 |  | 3758 | 13528800 | 45064800 | 76600800 | 108136800
2030-09-20 15:00 | 15293.7 | 4.8325 | 83.2789 | 59.8258 | 4482.141 |  | 3759 | 13532400 | 45068400 | 76604400 | 108140400
2030-09-21 16:00 | 15290.6 | 4.5715 | 84.439 | 59.8258 | 4481.2325 |  | 3760 | 13536000 | 45072000 | 76608000 | 108144000
2030-09-22 17:00 | 13255.9 | 4.1423 | 84.0175 | 59.8258 | 3884.9208 |  | 3761 | 13539600 | 45075600 | 76611600 | 108147600
2030-09-23 18:00 | 11036.6 | 3.3246 | 84.5002 | 59.8258 | 3234.5082 |  | 3762 | 13543200 | 45079200 | 76615200 | 108151200
2030-09-24 19:00 | 9185.32 | 2.8736 | 83.6741 | 59.8258 | 2691.9516 |  | 3763 | 13546800 | 45082800 | 76618800 | 108154800
2030-09-25 20:00 | 6752.45 | 2.0539 | 83.7715 | 59.8258 | 1978.9477 |  | 3764 | 13550400 | 45086400 | 76622400 | 108158400
2030-09-26 21:00 | 5734.34 | 1.6935 | 83.7304 | 59.8258 | 1680.5692 |  | 3765 | 13554000 | 45090000 | 76626000 | 108162000
2030-09-27 22:00 | 3277.56 | 1.0189 | 82.5344 | 59.8258 | 960.558 |  | 3766 | 13557600 | 45093600 | 76629600 | 108165600
2030-09-28 23:00 | 3253.03 | 1 | 89.8904 | 59.8258 | 953.369 |  | 3767 | 13561200 | 45097200 | 76633200 | 108169200
2030-09-30 | 3310.3 | 1 | 66.576 | 59.8258 | 970.1532 |  | 3768 | 13564800 | 45100800 | 76636800 | 108172800
2030-10-01 01:00 | 3204.64 | 1 | 66.3571 | 59.8258 | 939.1873 |  | 3769 | 13568400 | 45104400 | 76640400 | 108176400
2030-10-02 02:00 | 3187.08 | 1 | 66.1509 | 59.8258 | 934.0409 |  | 3770 | 13572000 | 45108000 | 76644000 | 108180000
2030-10-03 03:00 | 3144.48 | 1 | 65.9666 | 59.8258 | 921.5561 |  | 3771 | 13575600 | 45111600 | 76647600 | 108183600
2030-10-04 04:00 | 3213.21 | 1 | 65.827 | 59.8258 | 941.6989 |  | 3772 | 13579200 | 45115200 | 76651200 | 108187200
2030-10-05 05:00 | 3288.52 | 1 | 89.7238 | 59.8258 | 963.7701 |  | 3773 | 13582800 | 45118800 | 76654800 | 108190800
2030-10-06 06:00 | 3303.95 | 1 | 87.4951 | 59.8258 | 968.2922 |  | 3774 | 13586400 | 45122400 | 76658400 | 108194400
2030-10-07 07:00 | 4483.89 | 1.4362 | 80.0946 | 59.8258 | 1314.0984 |  | 3775 | 13590000 | 45126000 | 76662000 | 108198000
2030-10-08 08:00 | 5387.2 | 1.739 | 80.1011 | 59.8258 | 1578.8325 |  | 3776 | 13593600 | 45129600 | 76665600 | 108201600
2030-10-09 09:00 | 6865.27 | 2.3991 | 79.1679 | 59.8258 | 2012.012 |  | 3777 | 13597200 | 45133200 | 76669200 | 108205200
2030-10-10 10:00 | 8505.53 | 2.9274 | 79.6331 | 59.8258 | 2492.7248 |  | 3778 | 13600800 | 45136800 | 76672800 | 108208800
2030-10-11 11:00 | 9789.82 | 3.12 | 81.0489 | 59.8258 | 2869.113 |  | 3779 | 13604400 | 45140400 | 76676400 | 108212400
2030-10-12 12:00 | 9689.45 | 3.0864 | 81.436 | 59.8258 | 2839.6975 |  | 3780 | 13608000 | 45144000 | 76680000 | 108216000
2030-10-13 13:00 | 10741.4 | 3.3961 | 81.7439 | 59.8258 | 3147.9936 |  | 3781 | 13611600 | 45147600 | 76683600 | 108219600
2030-10-14 14:00 | 11707 | 3.7177 | 81.9593 | 59.8258 | 3430.983 |  | 3782 | 13615200 | 45151200 | 76687200 | 108223200
2030-10-15 15:00 | 13492.2 | 4.3825 | 81.9443 | 59.8258 | 3954.1735 |  | 3783 | 13618800 | 45154800 | 76690800 | 108226800
2030-10-16 16:00 | 13992.9 | 4.5679 | 82.2951 | 59.8258 | 4100.9142 |  | 3784 | 13622400 | 45158400 | 76694400 | 108230400
2030-10-17 17:00 | 14329.2 | 4.5422 | 83.0504 | 59.8258 | 4199.474 |  | 3785 | 13626000 | 45162000 | 76698000 | 108234000
2030-10-18 18:00 | 12720.2 | 4.0038 | 83.4771 | 59.8258 | 3727.9226 |  | 3786 | 13629600 | 45165600 | 76701600 | 108237600
2030-10-19 19:00 | 10945.5 | 3.369 | 83.858 | 59.8258 | 3207.8094 |  | 3787 | 13633200 | 45169200 | 76705200 | 108241200
2030-10-20 20:00 | 8268.27 | 2.489 | 84.0779 | 59.8258 | 2423.1907 |  | 3788 | 13636800 | 45172800 | 76708800 | 108244800
2030-10-21 21:00 | 7055.28 | 2.162 | 83.4354 | 59.8258 | 2067.6985 |  | 3789 | 13640400 | 45176400 | 76712400 | 108248400
2030-10-22 22:00 | 5403.65 | 1.4891 | 84.7743 | 59.8258 | 1583.6535 |  | 3790 | 13644000 | 45180000 | 76716000 | 108252000
2030-10-23 23:00 | 4531.68 | 1.2865 | 83.8684 | 59.8258 | 1328.1043 |  | 3791 | 13647600 | 45183600 | 76719600 | 108255600
2030-10-25 | 3705.51 | 1.1265 | 82.4449 | 59.8258 | 1085.9778 |  | 3792 | 13651200 | 45187200 | 76723200 | 108259200
2030-10-26 01:00 | 3229.45 | 1 | 82.309 | 59.8258 | 946.4584 |  | 3793 | 13654800 | 45190800 | 76726800 | 108262800
2030-10-27 02:00 | 3204.13 | 1 | 84.1468 | 59.8258 | 939.0378 |  | 3794 | 13658400 | 45194400 | 76730400 | 108266400
2030-10-28 03:00 | 3118.97 | 1 | 83.5987 | 59.8258 | 914.0799 |  | 3795 | 13662000 | 45198000 | 76734000 | 108270000
2030-10-29 04:00 | 3075.11 | 1 | 82.2567 | 59.8258 | 901.2258 |  | 3796 | 13665600 | 45201600 | 76737600 | 108273600
2030-10-30 05:00 | 3840.67 | 1.2061 | 80.7906 | 59.8258 | 1125.5893 |  | 3797 | 13669200 | 45205200 | 76741200 | 108277200
2030-10-31 06:00 | 4896.17 | 1.5425 | 80.7173 | 59.8258 | 1434.9258 |  | 3798 | 13672800 | 45208800 | 76744800 | 108280800
2030-11-01 07:00 | 5897.89 | 1.9641 | 80.0254 | 59.8258 | 1728.5009 |  | 3799 | 13676400 | 45212400 | 76748400 | 108284400
2030-11-02 08:00 | 6255.35 | 1.9781 | 80.9228 | 59.8258 | 1833.2621 |  | 3800 | 13680000 | 45216000 | 76752000 | 108288000
2030-11-03 09:00 | 7517.5 | 2.5479 | 80.0703 | 59.8258 | 2203.1618 |  | 3801 | 13683600 | 45219600 | 76755600 | 108291600
2030-11-04 10:00 | 8477.26 | 2.8321 | 80.5039 | 59.8258 | 2484.4397 |  | 3802 | 13687200 | 45223200 | 76759200 | 108295200
2030-11-05 11:00 | 9947.31 | 3.1765 | 81.3917 | 59.8258 | 2915.2688 |  | 3803 | 13690800 | 45226800 | 76762800 | 108298800
2030-11-06 12:00 | 11058.2 | 3.6146 | 81.402 | 59.8258 | 3240.8385 |  | 3804 | 13694400 | 45230400 | 76766400 | 108302400
2030-11-07 13:00 | 10282 | 3.2975 | 82.0318 | 59.8258 | 3013.3567 |  | 3805 | 13698000 | 45234000 | 76770000 | 108306000
2030-11-08 14:00 | 11871.1 | 3.6959 | 82.5715 | 59.8258 | 3479.076 |  | 3806 | 13701600 | 45237600 | 76773600 | 108309600
2030-11-09 15:00 | 13440.5 | 4.2734 | 82.5564 | 59.8258 | 3939.0217 |  | 3807 | 13705200 | 45241200 | 76777200 | 108313200
2030-11-10 16:00 | 14265.2 | 4.543 | 82.9529 | 59.8258 | 4180.7174 |  | 3808 | 13708800 | 45244800 | 76780800 | 108316800
2030-11-11 17:00 | 14059.5 | 4.4688 | 83.3356 | 59.8258 | 4120.4327 |  | 3809 | 13712400 | 45248400 | 76784400 | 108320400
2030-11-12 18:00 | 11353.5 | 3.452 | 84.2082 | 59.8258 | 3327.3824 |  | 3810 | 13716000 | 45252000 | 76788000 | 108324000
2030-11-13 19:00 | 9230.39 | 2.9556 | 83.3068 | 59.8258 | 2705.1603 |  | 3811 | 13719600 | 45255600 | 76791600 | 108327600
2030-11-14 20:00 | 6894.72 | 2.0296 | 84.2795 | 59.8258 | 2020.643 |  | 3812 | 13723200 | 45259200 | 76795200 | 108331200
2030-11-15 21:00 | 5826.76 | 1.7356 | 83.6643 | 59.8258 | 1707.6548 |  | 3813 | 13726800 | 45262800 | 76798800 | 108334800
2030-11-16 22:00 | 3332.45 | 1 | 83.5861 | 59.8258 | 976.6447 |  | 3814 | 13730400 | 45266400 | 76802400 | 108338400
2030-11-17 23:00 | 3162.41 | 1 | 67.0883 | 59.8258 | 926.8109 |  | 3815 | 13734000 | 45270000 | 76806000 | 108342000
2030-11-19 | 3231.79 | 1 | 66.7099 | 59.8258 | 947.1442 |  | 3816 | 13737600 | 45273600 | 76809600 | 108345600
2030-11-20 01:00 | 3072.7 | 1 | 66.5113 | 59.8258 | 900.5195 |  | 3817 | 13741200 | 45277200 | 76813200 | 108349200
2030-11-21 02:00 | 3169.38 | 1 | 66.3054 | 59.8258 | 928.8536 |  | 3818 | 13744800 | 45280800 | 76816800 | 108352800
2030-11-22 03:00 | 2474.54 | 1 | 66.1976 | 59.8258 | 725.2161 |  | 3819 | 13748400 | 45284400 | 76820400 | 108356400
2030-11-23 04:00 | 1263.49 | 1 | 66.0884 | 59.8258 | 370.2924 |  | 3820 | 13752000 | 45288000 | 76824000 | 108360000
2030-11-24 05:00 | 883.662 | 1 | 65.7758 | 59.8258 | 258.9758 |  | 3821 | 13755600 | 45291600 | 76827600 | 108363600
2030-11-25 06:00 | 2223.07 | 1.2354 | 73.8138 | 59.8258 | 651.5175 |  | 3822 | 13759200 | 45295200 | 76831200 | 108367200
2030-11-26 07:00 | 4382.06 | 1.7042 | 77.3021 | 59.8258 | 1284.255 |  | 3823 | 13762800 | 45298800 | 76834800 | 108370800
2030-11-27 08:00 | 4573.79 | 1.5953 | 78.8749 | 59.8258 | 1340.4455 |  | 3824 | 13766400 | 45302400 | 76838400 | 108374400
2030-11-28 09:00 | 6014.33 | 2.0472 | 79.2901 | 59.8258 | 1762.6261 |  | 3825 | 13770000 | 45306000 | 76842000 | 108378000
2030-11-29 10:00 | 7731.62 | 2.7252 | 79.0752 | 59.8258 | 2265.9141 |  | 3826 | 13773600 | 45309600 | 76845600 | 108381600
2030-11-30 11:00 | 9787.68 | 3.2109 | 80.4287 | 59.8258 | 2868.4859 |  | 3827 | 13777200 | 45313200 | 76849200 | 108385200
2030-12-01 12:00 | 10459.1 | 3.406 | 81.0171 | 59.8258 | 3065.2596 |  | 3828 | 13780800 | 45316800 | 76852800 | 108388800
2030-12-02 13:00 | 10296.7 | 3.2903 | 81.6446 | 59.8258 | 3017.6649 |  | 3829 | 13784400 | 45320400 | 76856400 | 108392400
2030-12-03 14:00 | 9586.24 | 3.018 | 82.0714 | 59.8258 | 2809.4496 |  | 3830 | 13788000 | 45324000 | 76860000 | 108396000
2030-12-04 15:00 | 8226.88 | 2.6288 | 81.9183 | 59.8258 | 2411.0605 |  | 3831 | 13791600 | 45327600 | 76863600 | 108399600
2030-12-05 16:00 | 11659.6 | 3.7806 | 81.5783 | 59.8258 | 3417.0914 |  | 3832 | 13795200 | 45331200 | 76867200 | 108403200
2030-12-06 17:00 | 11479.1 | 3.57 | 82.5912 | 59.8258 | 3364.1921 |  | 3833 | 13798800 | 45334800 | 76870800 | 108406800
2030-12-07 18:00 | 10280.8 | 3.2384 | 82.6418 | 59.8258 | 3013.0051 |  | 3834 | 13802400 | 45338400 | 76874400 | 108410400
2030-12-08 19:00 | 8632.08 | 2.7412 | 82.4948 | 59.8258 | 2529.8129 |  | 3835 | 13806000 | 45342000 | 76878000 | 108414000
2030-12-09 20:00 | 7748.52 | 2.3851 | 82.8058 | 59.8258 | 2270.867 |  | 3836 | 13809600 | 45345600 | 76881600 | 108417600
2030-12-10 21:00 | 7173.74 | 2.09 | 83.5415 | 59.8258 | 2102.4157 |  | 3837 | 13813200 | 45349200 | 76885200 | 108421200
2030-12-11 22:00 | 6361.66 | 1.9546 | 82.5798 | 59.8258 | 1864.4185 |  | 3838 | 13816800 | 45352800 | 76888800 | 108424800
2030-12-12 23:00 | 3416.59 | 1 | 84.7195 | 59.8258 | 1001.3037 |  | 3839 | 13820400 | 45356400 | 76892400 | 108428400
2030-12-14 | 3225.15 | 1 | 88.9913 | 59.8258 | 945.1982 |  | 3840 | 13824000 | 45360000 | 76896000 | 108432000
2030-12-15 01:00 | 3221.74 | 1 | 66.3813 | 59.8258 | 944.1988 |  | 3841 | 13827600 | 45363600 | 76899600 | 108435600
2030-12-16 02:00 | 3156.92 | 1 | 66.2206 | 59.8258 | 925.2019 |  | 3842 | 13831200 | 45367200 | 76903200 | 108439200
2030-12-17 03:00 | 3192.8 | 1 | 66.0726 | 59.8258 | 935.7173 |  | 3843 | 13834800 | 45370800 | 76906800 | 108442800
2030-12-18 04:00 | 3157.02 | 1 | 65.9261 | 59.8258 | 925.2312 |  | 3844 | 13838400 | 45374400 | 76910400 | 108446400
2030-12-19 05:00 | 3320.34 | 1 | 65.8251 | 59.8258 | 973.0956 |  | 3845 | 13842000 | 45378000 | 76914000 | 108450000
2030-12-20 06:00 | 3335.72 | 1 | 87.4621 | 59.8258 | 977.603 |  | 3846 | 13845600 | 45381600 | 76917600 | 108453600
2030-12-21 07:00 | 5013.64 | 1.5554 | 80.6997 | 59.8258 | 1469.3528 |  | 3847 | 13849200 | 45385200 | 76921200 | 108457200
2030-12-22 08:00 | 5094.95 | 1.5315 | 81.3517 | 59.8258 | 1493.1824 |  | 3848 | 13852800 | 45388800 | 76924800 | 108460800
2030-12-23 09:00 | 6261.21 | 2.06 | 80.1056 | 59.8258 | 1834.9795 |  | 3849 | 13856400 | 45392400 | 76928400 | 108464400
2030-12-24 10:00 | 8017.12 | 2.8415 | 79.2659 | 59.8258 | 2349.5859 |  | 3850 | 13860000 | 45396000 | 76932000 | 108468000
2030-12-25 11:00 | 9760.57 | 3.2814 | 80.3025 | 59.8258 | 2860.5407 |  | 3851 | 13863600 | 45399600 | 76935600 | 108471600
2030-12-26 12:00 | 10524.7 | 3.4343 | 81.1426 | 59.8258 | 3084.4851 |  | 3852 | 13867200 | 45403200 | 76939200 | 108475200
2030-12-27 13:00 | 9066.49 | 2.7289 | 82.6684 | 59.8258 | 2657.1259 |  | 3853 | 13870800 | 45406800 | 76942800 | 108478800
2030-12-28 14:00 | 9416.49 | 3.0202 | 81.7648 | 59.8258 | 2759.7008 |  | 3854 | 13874400 | 45410400 | 76946400 | 108482400
2030-12-29 15:00 | 10568.4 | 3.2688 | 82.4019 | 59.8258 | 3097.2923 |  | 3855 | 13878000 | 45414000 | 76950000 | 108486000
2030-12-30 16:00 | 12595 | 3.9941 | 82.2647 | 59.8258 | 3691.2301 |  | 3856 | 13881600 | 45417600 | 76953600 | 108489600
2030-12-31 17:00 | 10223.3 | 3.2873 | 82.4786 | 59.8258 | 2996.1535 |  | 3857 | 13885200 | 45421200 | 76957200 | 108493200
2031-01-01 18:00 | 8700.9 | 2.7721 | 82.5425 | 59.8258 | 2549.9821 |  | 3858 | 13888800 | 45424800 | 76960800 | 108496800
2031-01-02 19:00 | 7614.08 | 2.2754 | 83.3109 | 59.8258 | 2231.4666 |  | 3859 | 13892400 | 45428400 | 76964400 | 108500400
2031-01-03 20:00 | 6682.9 | 2.0082 | 83.0724 | 59.8258 | 1958.5647 |  | 3860 | 13896000 | 45432000 | 76968000 | 108504000
2031-01-04 21:00 | 5766.66 | 1.7382 | 82.8293 | 59.8258 | 1690.0412 |  | 3861 | 13899600 | 45435600 | 76971600 | 108507600
2031-01-05 22:00 | 5191.49 | 1.5628 | 82.5665 | 59.8258 | 1521.4755 |  | 3862 | 13903200 | 45439200 | 76975200 | 108511200
2031-01-06 23:00 | 3240.05 | 1 | 88.0424 | 59.8258 | 949.5649 |  | 3863 | 13906800 | 45442800 | 76978800 | 108514800
2031-01-08 | 3303.34 | 1 | 66.4763 | 59.8258 | 968.1134 |  | 3864 | 13910400 | 45446400 | 76982400 | 108518400
2031-01-09 01:00 | 3131.85 | 1 | 66.2827 | 59.8258 | 917.8546 |  | 3865 | 13914000 | 45450000 | 76986000 | 108522000
2031-01-10 02:00 | 3250.76 | 1 | 66.1115 | 59.8258 | 952.7037 |  | 3866 | 13917600 | 45453600 | 76989600 | 108525600
2031-01-11 03:00 | 3276.25 | 1 | 65.9823 | 59.8258 | 960.1741 |  | 3867 | 13921200 | 45457200 | 76993200 | 108529200
2031-01-12 04:00 | 3190.48 | 1 | 89.1016 | 59.8258 | 935.0374 |  | 3868 | 13924800 | 45460800 | 76996800 | 108532800
2031-01-13 05:00 | 3460.22 | 1 | 81.9057 | 59.8258 | 1014.0904 |  | 3869 | 13928400 | 45464400 | 77000400 | 108536400
2031-01-14 06:00 | 3702.18 | 1.1378 | 80.9006 | 59.8258 | 1085.0019 |  | 3870 | 13932000 | 45468000 | 77004000 | 108540000
2031-01-15 07:00 | 4342.74 | 1.3386 | 80.8482 | 59.8258 | 1272.7315 |  | 3871 | 13935600 | 45471600 | 77007600 | 108543600
2031-01-16 08:00 | 4110.22 | 1.302 | 80.5146 | 59.8258 | 1204.5866 |  | 3872 | 13939200 | 45475200 | 77011200 | 108547200
2031-01-17 09:00 | 5389.63 | 1.7113 | 80.4573 | 59.8258 | 1579.5446 |  | 3873 | 13942800 | 45478800 | 77014800 | 108550800
2031-01-18 10:00 | 6441.02 | 2.2091 | 79.5217 | 59.8258 | 1887.6766 |  | 3874 | 13946400 | 45482400 | 77018400 | 108554400
2031-01-19 11:00 | 7703.55 | 2.5534 | 80.1959 | 59.8258 | 2257.6876 |  | 3875 | 13950000 | 45486000 | 77022000 | 108558000
2031-01-20 12:00 | 8990.04 | 2.9545 | 80.5769 | 59.8258 | 2634.7206 |  | 3876 | 13953600 | 45489600 | 77025600 | 108561600
2031-01-21 13:00 | 9329.1 | 2.9819 | 81.2984 | 59.8258 | 2734.0893 |  | 3877 | 13957200 | 45493200 | 77029200 | 108565200
2031-01-22 14:00 | 8619.6 | 2.8425 | 81.1255 | 59.8258 | 2526.1554 |  | 3878 | 13960800 | 45496800 | 77032800 | 108568800
2031-01-23 15:00 | 10943.8 | 3.7267 | 80.7462 | 59.8258 | 3207.3112 |  | 3879 | 13964400 | 45500400 | 77036400 | 108572400
2031-01-24 16:00 | 10969.7 | 3.67 | 81.3536 | 59.8258 | 3214.9017 |  | 3880 | 13968000 | 45504000 | 77040000 | 108576000
2031-01-25 17:00 | 10984.9 | 3.4978 | 82.2903 | 59.8258 | 3219.3564 |  | 3881 | 13971600 | 45507600 | 77043600 | 108579600
2031-01-26 18:00 | 10207.8 | 3.1649 | 82.8297 | 59.8258 | 2991.6109 |  | 3882 | 13975200 | 45511200 | 77047200 | 108583200
2031-01-27 19:00 | 8587.47 | 2.6211 | 83.1118 | 59.8258 | 2516.739 |  | 3883 | 13978800 | 45514800 | 77050800 | 108586800
2031-01-28 20:00 | 6559.61 | 1.8795 | 83.9932 | 59.8258 | 1922.4319 |  | 3884 | 13982400 | 45518400 | 77054400 | 108590400
2031-01-29 21:00 | 5454.2 | 1.614 | 83.1702 | 59.8258 | 1598.4682 |  | 3885 | 13986000 | 45522000 | 77058000 | 108594000
2031-01-30 22:00 | 3339.48 | 1 | 84.3084 | 59.8258 | 978.705 |  | 3886 | 13989600 | 45525600 | 77061600 | 108597600
2031-01-31 23:00 | 3086.41 | 1 | 86.3284 | 59.8258 | 904.5375 |  | 3887 | 13993200 | 45529200 | 77065200 | 108601200
2031-02-02 | 3143.21 | 1 | 91.7035 | 59.8258 | 921.1839 |  | 3888 | 13996800 | 45532800 | 77068800 | 108604800
2031-02-03 01:00 | 3194.8 | 1 | 66.1811 | 59.8258 | 936.3035 |  | 3889 | 14000400 | 45536400 | 77072400 | 108608400
2031-02-04 02:00 | 3168.51 | 1 | 66.0671 | 59.8258 | 928.5986 |  | 3890 | 14004000 | 45540000 | 77076000 | 108612000
2031-02-05 03:00 | 3226.84 | 1 | 65.9235 | 59.8258 | 945.6935 |  | 3891 | 14007600 | 45543600 | 77079600 | 108615600
2031-02-06 04:00 | 3154.93 | 1 | 65.8495 | 59.8258 | 924.6187 |  | 3892 | 14011200 | 45547200 | 77083200 | 108619200
2031-02-07 05:00 | 3318.19 | 1 | 85.187 | 59.8258 | 972.4655 |  | 3893 | 14014800 | 45550800 | 77086800 | 108622800
2031-02-08 06:00 | 3624.06 | 1.0941 | 81.0956 | 59.8258 | 1062.1071 |  | 3894 | 14018400 | 45554400 | 77090400 | 108626400
2031-02-09 07:00 | 4993.89 | 1.5481 | 80.6799 | 59.8258 | 1463.5647 |  | 3895 | 14022000 | 45558000 | 77094000 | 108630000
2031-02-10 08:00 | 4422.19 | 1.3513 | 81.0626 | 59.8258 | 1296.016 |  | 3896 | 14025600 | 45561600 | 77097600 | 108633600
2031-02-11 09:00 | 5238.47 | 1.5451 | 81.5925 | 59.8258 | 1535.244 |  | 3897 | 14029200 | 45565200 | 77101200 | 108637200
2031-02-12 10:00 | 5398.76 | 1.7077 | 80.6482 | 59.8258 | 1582.2204 |  | 3898 | 14032800 | 45568800 | 77104800 | 108640800
2031-02-13 11:00 | 6204.05 | 1.9473 | 80.8401 | 59.8258 | 1818.2276 |  | 3899 | 14036400 | 45572400 | 77108400 | 108644400
2031-02-14 12:00 | 6703 | 2.2698 | 79.9084 | 59.8258 | 1964.4554 |  | 3900 | 14040000 | 45576000 | 77112000 | 108648000
2031-02-15 13:00 | 7908.3 | 2.6701 | 80.0684 | 59.8258 | 2317.6939 |  | 3901 | 14043600 | 45579600 | 77115600 | 108651600
2031-02-16 14:00 | 10094.9 | 3.2761 | 80.8498 | 59.8258 | 2958.5231 |  | 3902 | 14047200 | 45583200 | 77119200 | 108655200
2031-02-17 15:00 | 12831.9 | 4.1277 | 81.3799 | 59.8258 | 3760.6587 |  | 3903 | 14050800 | 45586800 | 77122800 | 108658800
2031-02-18 16:00 | 13643 | 4.5071 | 81.6184 | 59.8258 | 3998.3686 |  | 3904 | 14054400 | 45590400 | 77126400 | 108662400
2031-02-19 17:00 | 13273 | 4.321 | 82.3088 | 59.8258 | 3889.9323 |  | 3905 | 14058000 | 45594000 | 77130000 | 108666000
2031-02-20 18:00 | 11951.5 | 3.7795 | 83.0202 | 59.8258 | 3502.6389 |  | 3906 | 14061600 | 45597600 | 77133600 | 108669600
2031-02-21 19:00 | 10421.6 | 3.2078 | 83.5023 | 59.8258 | 3054.2695 |  | 3907 | 14065200 | 45601200 | 77137200 | 108673200
2031-02-22 20:00 | 8063.28 | 2.4096 | 83.893 | 59.8258 | 2363.1141 |  | 3908 | 14068800 | 45604800 | 77140800 | 108676800
2031-02-23 21:00 | 6923.19 | 2.1041 | 83.327 | 59.8258 | 2028.9867 |  | 3909 | 14072400 | 45608400 | 77144400 | 108680400
2031-02-24 22:00 | 5537.31 | 1.5027 | 84.8522 | 59.8258 | 1622.8254 |  | 3910 | 14076000 | 45612000 | 77148000 | 108684000
2031-02-25 23:00 | 4569.28 | 1.3135 | 83.5913 | 59.8258 | 1339.1238 |  | 3911 | 14079600 | 45615600 | 77151600 | 108687600
2031-02-27 | 3477.8 | 1.0639 | 82.3307 | 59.8258 | 1019.2426 |  | 3912 | 14083200 | 45619200 | 77155200 | 108691200
2031-02-28 01:00 | 3054.98 | 1 | 82.7979 | 59.8258 | 895.3263 |  | 3913 | 14086800 | 45622800 | 77158800 | 108694800
2031-03-01 02:00 | 3149.64 | 1 | 85.2615 | 59.8258 | 923.0684 |  | 3914 | 14090400 | 45626400 | 77162400 | 108698400
2031-03-02 03:00 | 3154 | 1 | 83.8814 | 59.8258 | 924.3462 |  | 3915 | 14094000 | 45630000 | 77166000 | 108702000
2031-03-03 04:00 | 3229.62 | 1 | 84.0271 | 59.8258 | 946.5082 |  | 3916 | 14097600 | 45633600 | 77169600 | 108705600
2031-03-04 05:00 | 3764.26 | 1.1885 | 80.762 | 59.8258 | 1103.1957 |  | 3917 | 14101200 | 45637200 | 77173200 | 108709200
2031-03-05 06:00 | 4515.01 | 1.383 | 81.1818 | 59.8258 | 1323.2188 |  | 3918 | 14104800 | 45640800 | 77176800 | 108712800
2031-03-06 07:00 | 5069.46 | 1.6716 | 80.1713 | 59.8258 | 1485.7121 |  | 3919 | 14108400 | 45644400 | 77180400 | 108716400
2031-03-07 08:00 | 4908.37 | 1.4956 | 81.4081 | 59.8258 | 1438.5012 |  | 3920 | 14112000 | 45648000 | 77184000 | 108720000
2031-03-08 09:00 | 5816.86 | 1.9122 | 80.3216 | 59.8258 | 1704.7534 |  | 3921 | 14115600 | 45651600 | 77187600 | 108723600
2031-03-09 10:00 | 6460.72 | 2.1354 | 80.3823 | 59.8258 | 1893.4501 |  | 3922 | 14119200 | 45655200 | 77191200 | 108727200
2031-03-10 11:00 | 6932.11 | 2.2983 | 80.5019 | 59.8258 | 2031.6009 |  | 3923 | 14122800 | 45658800 | 77194800 | 108730800
2031-03-11 12:00 | 8254.01 | 2.7032 | 80.8138 | 59.8258 | 2419.0115 |  | 3924 | 14126400 | 45662400 | 77198400 | 108734400
2031-03-12 13:00 | 9180.16 | 3.1193 | 80.5677 | 59.8258 | 2690.4393 |  | 3925 | 14130000 | 45666000 | 77202000 | 108738000
2031-03-13 14:00 | 9740.15 | 3.1241 | 81.6561 | 59.8258 | 2854.5562 |  | 3926 | 14133600 | 45669600 | 77205600 | 108741600
2031-03-14 15:00 | 11909.1 | 3.8625 | 81.7141 | 59.8258 | 3490.2127 |  | 3927 | 14137200 | 45673200 | 77209200 | 108745200
2031-03-15 16:00 | 12886.1 | 4.1579 | 82.2158 | 59.8258 | 3776.5431 |  | 3928 | 14140800 | 45676800 | 77212800 | 108748800
2031-03-16 17:00 | 13262.3 | 4.2566 | 82.6994 | 59.8258 | 3886.7965 |  | 3929 | 14144400 | 45680400 | 77216400 | 108752400
2031-03-17 18:00 | 11994.9 | 3.7781 | 83.2818 | 59.8258 | 3515.3582 |  | 3930 | 14148000 | 45684000 | 77220000 | 108756000
2031-03-18 19:00 | 10333.2 | 3.2555 | 83.3546 | 59.8258 | 3028.362 |  | 3931 | 14151600 | 45687600 | 77223600 | 108759600
2031-03-19 20:00 | 7751.22 | 2.3603 | 83.7819 | 59.8258 | 2271.6583 |  | 3932 | 14155200 | 45691200 | 77227200 | 108763200
2031-03-20 21:00 | 6740.84 | 1.9225 | 84.4508 | 59.8258 | 1975.5452 |  | 3933 | 14158800 | 45694800 | 77230800 | 108766800
2031-03-21 22:00 | 4379.49 | 1.2914 | 83.6386 | 59.8258 | 1283.5018 |  | 3934 | 14162400 | 45698400 | 77234400 | 108770400
2031-03-22 23:00 | 3409.61 | 1.033 | 82.7547 | 59.8258 | 999.2581 |  | 3935 | 14166000 | 45702000 | 77238000 | 108774000
2031-03-24 | 3190.44 | 1 | 85.1878 | 59.8258 | 935.0257 |  | 3936 | 14169600 | 45705600 | 77241600 | 108777600
2031-03-25 01:00 | 3252.76 | 1 | 88.3778 | 59.8258 | 953.2899 |  | 3937 | 14173200 | 45709200 | 77245200 | 108781200
2031-03-26 02:00 | 3099.48 | 1 | 66.5263 | 59.8258 | 908.3679 |  | 3938 | 14176800 | 45712800 | 77248800 | 108784800
2031-03-27 03:00 | 3198.91 | 1 | 66.3327 | 59.8258 | 937.508 |  | 3939 | 14180400 | 45716400 | 77252400 | 108788400
2031-03-28 04:00 | 3118.22 | 1 | 91.2723 | 59.8258 | 913.8601 |  | 3940 | 14184000 | 45720000 | 77256000 | 108792000
2031-03-29 05:00 | 3330.79 | 1.0239 | 81.1956 | 59.8258 | 976.1582 |  | 3941 | 14187600 | 45723600 | 77259600 | 108795600
2031-03-30 06:00 | 4678.42 | 1.3955 | 81.5786 | 59.8258 | 1371.1096 |  | 3942 | 14191200 | 45727200 | 77263200 | 108799200
2031-03-31 07:00 | 6002.57 | 2.0209 | 79.9206 | 59.8258 | 1759.1796 |  | 3943 | 14194800 | 45730800 | 77266800 | 108802800
2031-04-01 08:00 | 6960.64 | 2.2055 | 80.9967 | 59.8258 | 2039.9622 |  | 3944 | 14198400 | 45734400 | 77270400 | 108806400
2031-04-02 09:00 | 9021.87 | 2.8994 | 81.0178 | 59.8258 | 2644.0491 |  | 3945 | 14202000 | 45738000 | 77274000 | 108810000
2031-04-03 10:00 | 10810.7 | 3.5277 | 81.2317 | 59.8258 | 3168.3034 |  | 3946 | 14205600 | 45741600 | 77277600 | 108813600
2031-04-04 11:00 | 11827.1 | 3.9596 | 81.401 | 59.8258 | 3466.1809 |  | 3947 | 14209200 | 45745200 | 77281200 | 108817200
2031-04-05 12:00 | 12568.4 | 3.9871 | 82.6094 | 59.8258 | 3683.4344 |  | 3948 | 14212800 | 45748800 | 77284800 | 108820800
2031-04-06 13:00 | 12606.1 | 4.1139 | 82.6049 | 59.8258 | 3694.4832 |  | 3949 | 14216400 | 45752400 | 77288400 | 108824400
2031-04-07 14:00 | 13400.3 | 4.2706 | 83.2348 | 59.8258 | 3927.2403 |  | 3950 | 14220000 | 45756000 | 77292000 | 108828000
2031-04-08 15:00 | 15214.1 | 4.7811 | 83.735 | 59.8258 | 4458.8126 |  | 3951 | 14223600 | 45759600 | 77295600 | 108831600
2031-04-09 16:00 | 15097.7 | 4.8786 | 83.793 | 59.8258 | 4424.6991 |  | 3952 | 14227200 | 45763200 | 77299200 | 108835200
2031-04-10 17:00 | 15172 | 4.799 | 84.3882 | 59.8258 | 4446.4743 |  | 3953 | 14230800 | 45766800 | 77302800 | 108838800
2031-04-11 18:00 | 13627.5 | 4.1965 | 85.0143 | 59.8258 | 3993.826 |  | 3954 | 14234400 | 45770400 | 77306400 | 108842400
2031-04-12 19:00 | 11620 | 3.5831 | 85.0206 | 59.8258 | 3405.4858 |  | 3955 | 14238000 | 45774000 | 77310000 | 108846000
2031-04-13 20:00 | 9262.38 | 2.7731 | 85.3009 | 59.8258 | 2714.5356 |  | 3956 | 14241600 | 45777600 | 77313600 | 108849600
2031-04-14 21:00 | 7344.62 | 2.3302 | 84.0665 | 59.8258 | 2152.4956 |  | 3957 | 14245200 | 45781200 | 77317200 | 108853200
2031-04-15 22:00 | 5281.53 | 1.5502 | 84.804 | 59.8258 | 1547.8636 |  | 3958 | 14248800 | 45784800 | 77320800 | 108856800
2031-04-16 23:00 | 4181.82 | 1.2212 | 84.3535 | 59.8258 | 1225.5705 |  | 3959 | 14252400 | 45788400 | 77324400 | 108860400
2031-04-18 | 3341.34 | 1.0182 | 83.2361 | 59.8258 | 979.2501 |  | 3960 | 14256000 | 45792000 | 77328000 | 108864000
2031-04-19 01:00 | 3263.97 | 1 | 86.8436 | 59.8258 | 956.5752 |  | 3961 | 14259600 | 45795600 | 77331600 | 108867600
2031-04-20 02:00 | 3110.42 | 1 | 90.9158 | 59.8258 | 911.5741 |  | 3962 | 14263200 | 45799200 | 77335200 | 108871200
2031-04-21 03:00 | 3147.73 | 1 | 90.2998 | 59.8258 | 922.5086 |  | 3963 | 14266800 | 45802800 | 77338800 | 108874800
2031-04-22 04:00 | 3102.47 | 1 | 87.0461 | 59.8258 | 909.2442 |  | 3964 | 14270400 | 45806400 | 77342400 | 108878400
2031-04-23 05:00 | 3221.24 | 1.0364 | 81.1517 | 59.8258 | 944.0523 |  | 3965 | 14274000 | 45810000 | 77346000 | 108882000
2031-04-24 06:00 | 4594.42 | 1.4132 | 81.6886 | 59.8258 | 1346.4916 |  | 3966 | 14277600 | 45813600 | 77349600 | 108885600
2031-04-25 07:00 | 5842.49 | 1.9256 | 80.7636 | 59.8258 | 1712.2648 |  | 3967 | 14281200 | 45817200 | 77353200 | 108889200
2031-04-26 08:00 | 6238.96 | 2.0659 | 80.8858 | 59.8258 | 1828.4587 |  | 3968 | 14284800 | 45820800 | 77356800 | 108892800
2031-04-27 09:00 | 7800.68 | 2.6084 | 80.8705 | 59.8258 | 2286.1536 |  | 3969 | 14288400 | 45824400 | 77360400 | 108896400
2031-04-28 10:00 | 8756.63 | 3.0459 | 80.6204 | 59.8258 | 2566.3149 |  | 3970 | 14292000 | 45828000 | 77364000 | 108900000
2031-04-29 11:00 | 9819.86 | 3.2699 | 81.5123 | 59.8258 | 2877.9169 |  | 3971 | 14295600 | 45831600 | 77367600 | 108903600
2031-04-30 12:00 | 10318.5 | 3.3359 | 82.2353 | 59.8258 | 3024.0538 |  | 3972 | 14299200 | 45835200 | 77371200 | 108907200
2031-05-01 13:00 | 11050 | 3.5038 | 82.766 | 59.8258 | 3238.4353 |  | 3973 | 14302800 | 45838800 | 77374800 | 108910800
2031-05-02 14:00 | 11496.1 | 3.7007 | 82.8273 | 59.8258 | 3369.1743 |  | 3974 | 14306400 | 45842400 | 77378400 | 108914400
2031-05-03 15:00 | 13130.1 | 4.3018 | 82.7967 | 59.8258 | 3848.0525 |  | 3975 | 14310000 | 45846000 | 77382000 | 108918000
2031-05-04 16:00 | 13588.5 | 4.4272 | 83.2458 | 59.8258 | 3982.3962 |  | 3976 | 14313600 | 45849600 | 77385600 | 108921600
2031-05-05 17:00 | 13421.7 | 4.2955 | 83.7991 | 59.8258 | 3933.512 |  | 3977 | 14317200 | 45853200 | 77389200 | 108925200
2031-05-06 18:00 | 12128.1 | 3.7617 | 84.4431 | 59.8258 | 3554.3952 |  | 3978 | 14320800 | 45856800 | 77392800 | 108928800
2031-05-07 19:00 | 10157.7 | 3.1676 | 84.3632 | 59.8258 | 2976.928 |  | 3979 | 14324400 | 45860400 | 77396400 | 108932400
2031-05-08 20:00 | 7761.07 | 2.3482 | 84.6366 | 59.8258 | 2274.5451 |  | 3980 | 14328000 | 45864000 | 77400000 | 108936000
2031-05-09 21:00 | 6568.57 | 1.9431 | 84.5895 | 59.8258 | 1925.0578 |  | 3981 | 14331600 | 45867600 | 77403600 | 108939600
2031-05-10 22:00 | 4270.43 | 1.2671 | 84.2003 | 59.8258 | 1251.5395 |  | 3982 | 14335200 | 45871200 | 77407200 | 108943200
2031-05-11 23:00 | 3240.44 | 1 | 88.8603 | 59.8258 | 949.6792 |  | 3983 | 14338800 | 45874800 | 77410800 | 108946800
2031-05-13 | 3093.49 | 1 | 67.5635 | 59.8258 | 906.6124 |  | 3984 | 14342400 | 45878400 | 77414400 | 108950400
2031-05-14 01:00 | 3117.95 | 1 | 67.2694 | 59.8258 | 913.7809 |  | 3985 | 14346000 | 45882000 | 77418000 | 108954000
2031-05-15 02:00 | 1559.72 | 1 | 67.208 | 59.8258 | 457.1088 |  | 3986 | 14349600 | 45885600 | 77421600 | 108957600
2031-05-16 03:00 | -34.9932 | 0.64986 | 66.6974 | 59.8258 | -10.2555 |  | 3987 | 14353200 | 45889200 | 77425200 | 108961200
2031-05-17 04:00 | -234.097 | 1.1233 | 65.5029 | 59.8258 | -68.6071 |  | 3988 | 14356800 | 45892800 | 77428800 | 108964800
2031-05-18 05:00 | -243.615 | 1.1148 | 65.1102 | 59.8258 | -71.3965 |  | 3989 | 14360400 | 45896400 | 77432400 | 108968400
2031-05-19 06:00 | 2098.93 | 1 | 65.6482 | 59.8258 | 615.1357 |  | 3990 | 14364000 | 45900000 | 77436000 | 108972000
2031-05-20 07:00 | 3429.63 | 1.2084 | 78.8925 | 59.8258 | 1005.1253 |  | 3991 | 14367600 | 45903600 | 77439600 | 108975600
2031-05-21 08:00 | 4125.43 | 1.3074 | 80.4739 | 59.8258 | 1209.0442 |  | 3992 | 14371200 | 45907200 | 77443200 | 108979200
2031-05-22 09:00 | 5156.7 | 1.7415 | 79.7148 | 59.8258 | 1511.2796 |  | 3993 | 14374800 | 45910800 | 77446800 | 108982800
2031-05-23 10:00 | 6902.59 | 2.3084 | 80.0532 | 59.8258 | 2022.9494 |  | 3994 | 14378400 | 45914400 | 77450400 | 108986400
2031-05-24 11:00 | 7456.49 | 2.5365 | 80.1867 | 59.8258 | 2185.2815 |  | 3995 | 14382000 | 45918000 | 77454000 | 108990000
2031-05-25 12:00 | 7294.38 | 2.4118 | 80.8252 | 59.8258 | 2137.7718 |  | 3996 | 14385600 | 45921600 | 77457600 | 108993600
2031-05-26 13:00 | 7656.52 | 2.4799 | 81.2103 | 59.8258 | 2243.9045 |  | 3997 | 14389200 | 45925200 | 77461200 | 108997200
2031-05-27 14:00 | 8642.94 | 2.8054 | 81.3066 | 59.8258 | 2532.9957 |  | 3998 | 14392800 | 45928800 | 77464800 | 109000800
2031-05-28 15:00 | 9935.95 | 3.1827 | 81.714 | 59.8258 | 2911.9395 |  | 3999 | 14396400 | 45932400 | 77468400 | 109004400
2031-05-29 16:00 | 12259.2 | 3.9505 | 81.9103 | 59.8258 | 3592.8169 |  | 4000 | 14400000 | 45936000 | 77472000 | 109008000
2031-05-30 17:00 | 11045.3 | 3.5105 | 82.6054 | 59.8258 | 3237.0579 |  | 4001 | 14403600 | 45939600 | 77475600 | 109011600
2031-05-31 18:00 | 9739.36 | 3.0516 | 82.9608 | 59.8258 | 2854.3247 |  | 4002 | 14407200 | 45943200 | 77479200 | 109015200
2031-06-01 19:00 | 7796.98 | 2.4573 | 82.8372 | 59.8258 | 2285.0693 |  | 4003 | 14410800 | 45946800 | 77482800 | 109018800
2031-06-02 20:00 | 6288.56 | 1.9866 | 82.6097 | 59.8258 | 1842.995 |  | 4004 | 14414400 | 45950400 | 77486400 | 109022400
2031-06-03 21:00 | 5415.59 | 1.6868 | 82.5416 | 59.8258 | 1587.1528 |  | 4005 | 14418000 | 45954000 | 77490000 | 109026000
2031-06-04 22:00 | 4761.87 | 1.4805 | 82.2783 | 59.8258 | 1395.5663 |  | 4006 | 14421600 | 45957600 | 77493600 | 109029600
2031-06-05 23:00 | 3073.59 | 1 | 67.0678 | 59.8258 | 900.7803 |  | 4007 | 14425200 | 45961200 | 77497200 | 109033200
2031-06-07 | 3140.86 | 1 | 66.6917 | 59.8258 | 920.4952 |  | 4008 | 14428800 | 45964800 | 77500800 | 109036800
2031-06-08 01:00 | 0 | 0 | 66.7663 | 59.8258 | 0 |  | 4009 | 14432400 | 45968400 | 77504400 | 109040400
2031-06-09 02:00 | -384.875 | 1.5499 | 65.0777 | 59.8258 | -112.7957 |  | 4010 | 14436000 | 45972000 | 77508000 | 109044000
2031-06-10 03:00 | -651.396 | 2.1675 | 64.426 | 59.8258 | -190.9053 |  | 4011 | 14439600 | 45975600 | 77511600 | 109047600
2031-06-11 04:00 | -959.444 | 2.9508 | 63.9854 | 59.8258 | -281.1853 |  | 4012 | 14443200 | 45979200 | 77515200 | 109051200
2031-06-12 05:00 | -1163.78 | 3.4462 | 63.6373 | 59.8258 | -341.0702 |  | 4013 | 14446800 | 45982800 | 77518800 | 109054800
2031-06-13 06:00 | 0 | 1 | 64.8837 | 59.8258 | 0 |  | 4014 | 14450400 | 45986400 | 77522400 | 109058400
2031-06-14 07:00 | 2392.81 | 1 | 81.4961 | 59.8258 | 701.2634 |  | 4015 | 14454000 | 45990000 | 77526000 | 109062000
2031-06-15 08:00 | 2868.25 | 1 | 87.2088 | 59.8258 | 840.6011 |  | 4016 | 14457600 | 45993600 | 77529600 | 109065600
2031-06-16 09:00 | 3292.01 | 1.0892 | 79.034 | 59.8258 | 964.7929 |  | 4017 | 14461200 | 45997200 | 77533200 | 109069200
2031-06-17 10:00 | 4918.1 | 1.5779 | 79.5672 | 59.8258 | 1441.3528 |  | 4018 | 14464800 | 46000800 | 77536800 | 109072800
2031-06-18 11:00 | 6187.24 | 2.05 | 79.398 | 59.8258 | 1813.301 |  | 4019 | 14468400 | 46004400 | 77540400 | 109076400
2031-06-19 12:00 | 7154.35 | 2.3138 | 80.0571 | 59.8258 | 2096.733 |  | 4020 | 14472000 | 46008000 | 77544000 | 109080000
2031-06-20 13:00 | 7627.77 | 2.5005 | 80.1689 | 59.8258 | 2235.4787 |  | 4021 | 14475600 | 46011600 | 77547600 | 109083600
2031-06-21 14:00 | 8693.7 | 2.8457 | 80.4422 | 59.8258 | 2547.872 |  | 4022 | 14479200 | 46015200 | 77551200 | 109087200
2031-06-22 15:00 | 9298.25 | 3.0047 | 80.9411 | 59.8258 | 2725.0481 |  | 4023 | 14482800 | 46018800 | 77554800 | 109090800
2031-06-23 16:00 | 11747.7 | 3.8253 | 81.0964 | 59.8258 | 3442.911 |  | 4024 | 14486400 | 46022400 | 77558400 | 109094400
2031-06-24 17:00 | 10871.4 | 3.4681 | 81.9103 | 59.8258 | 3186.0928 |  | 4025 | 14490000 | 46026000 | 77562000 | 109098000
2031-06-25 18:00 | 9313.48 | 2.9618 | 82.1813 | 59.8258 | 2729.5115 |  | 4026 | 14493600 | 46029600 | 77565600 | 109101600
2031-06-26 19:00 | 7629.74 | 2.3556 | 82.5754 | 59.8258 | 2236.0561 |  | 4027 | 14497200 | 46033200 | 77569200 | 109105200
2031-06-27 20:00 | 6177.37 | 1.9157 | 82.3495 | 59.8258 | 1810.4084 |  | 4028 | 14500800 | 46036800 | 77572800 | 109108800
2031-06-28 21:00 | 4582.74 | 1.3408 | 83.0174 | 59.8258 | 1343.0685 |  | 4029 | 14504400 | 46040400 | 77576400 | 109112400
2031-06-29 22:00 | 3348.61 | 1.0265 | 81.9507 | 59.8258 | 981.3807 |  | 4030 | 14508000 | 46044000 | 77580000 | 109116000
2031-06-30 23:00 | 3080.67 | 1 | 66.4078 | 59.8258 | 902.8553 |  | 4031 | 14511600 | 46047600 | 77583600 | 109119600
2031-07-02 | -67.6068 | 0.72207 | 66.0088 | 59.8258 | -19.8136 |  | 4032 | 14515200 | 46051200 | 77587200 | 109123200
2031-07-03 01:00 | -328.881 | 1.3756 | 64.7672 | 59.8258 | -96.3855 |  | 4033 | 14518800 | 46054800 | 77590800 | 109126800
2031-07-04 02:00 | -477.069 | 1.7237 | 64.1998 | 59.8258 | -139.8151 |  | 4034 | 14522400 | 46058400 | 77594400 | 109130400
2031-07-05 03:00 | -619.189 | 2.081 | 63.8485 | 59.8258 | -181.4664 |  | 4035 | 14526000 | 46062000 | 77598000 | 109134000
2031-07-06 04:00 | -797.053 | 2.5369 | 63.517 | 59.8258 | -233.5932 |  | 4036 | 14529600 | 46065600 | 77601600 | 109137600
2031-07-07 05:00 | -260.694 | 1.0541 | 63.5714 | 59.8258 | -76.4019 |  | 4037 | 14533200 | 46069200 | 77605200 | 109141200
2031-07-08 06:00 | 2195.29 | 1 | 64.4218 | 59.8258 | 643.376 |  | 4038 | 14536800 | 46072800 | 77608800 | 109144800
2031-07-09 07:00 | 2991.98 | 1 | 83.0722 | 59.8258 | 876.8628 |  | 4039 | 14540400 | 46076400 | 77612400 | 109148400
2031-07-10 08:00 | 3281.33 | 1.0518 | 79.2803 | 59.8258 | 961.6629 |  | 4040 | 14544000 | 46080000 | 77616000 | 109152000
2031-07-11 09:00 | 5386.89 | 1.7504 | 79.2009 | 59.8258 | 1578.7416 |  | 4041 | 14547600 | 46083600 | 77619600 | 109155600
2031-07-12 10:00 | 7101.16 | 2.3647 | 79.2091 | 59.8258 | 2081.1446 |  | 4042 | 14551200 | 46087200 | 77623200 | 109159200
2031-07-13 11:00 | 8462.02 | 2.8058 | 79.703 | 59.8258 | 2479.9733 |  | 4043 | 14554800 | 46090800 | 77626800 | 109162800
2031-07-14 12:00 | 8992.21 | 2.9754 | 80.1581 | 59.8258 | 2635.3566 |  | 4044 | 14558400 | 46094400 | 77630400 | 109166400
2031-07-15 13:00 | 9700.73 | 3.1503 | 80.7626 | 59.8258 | 2843.0033 |  | 4045 | 14562000 | 46098000 | 77634000 | 109170000
2031-07-16 14:00 | 10389.2 | 3.2877 | 81.4783 | 59.8258 | 3044.774 |  | 4046 | 14565600 | 46101600 | 77637600 | 109173600
2031-07-17 15:00 | 11406.9 | 3.6536 | 81.6288 | 59.8258 | 3343.0324 |  | 4047 | 14569200 | 46105200 | 77641200 | 109177200
2031-07-18 16:00 | 12098.3 | 3.8166 | 82.1888 | 59.8258 | 3545.6617 |  | 4048 | 14572800 | 46108800 | 77644800 | 109180800
2031-07-19 17:00 | 11781 | 3.725 | 82.488 | 59.8258 | 3452.6703 |  | 4049 | 14576400 | 46112400 | 77648400 | 109184400
2031-07-20 18:00 | 10284.5 | 3.2228 | 82.8156 | 59.8258 | 3014.0894 |  | 4050 | 14580000 | 46116000 | 77652000 | 109188000
2031-07-21 19:00 | 8503.93 | 2.634 | 82.9689 | 59.8258 | 2492.2559 |  | 4051 | 14583600 | 46119600 | 77655600 | 109191600
2031-07-22 20:00 | 6042.63 | 1.8364 | 83.0886 | 59.8258 | 1770.92 |  | 4052 | 14587200 | 46123200 | 77659200 | 109195200
2031-07-23 21:00 | 4972.24 | 1.4555 | 83.2782 | 59.8258 | 1457.2197 |  | 4053 | 14590800 | 46126800 | 77662800 | 109198800
2031-07-24 22:00 | 3206.25 | 1 | 88.1938 | 59.8258 | 939.6591 |  | 4054 | 14594400 | 46130400 | 77666400 | 109202400
2031-07-25 23:00 | 3160.56 | 1 | 66.5854 | 59.8258 | 926.2687 |  | 4055 | 14598000 | 46134000 | 77670000 | 109206000
2031-07-27 | 3124.08 | 1 | 66.3242 | 59.8258 | 915.5775 |  | 4056 | 14601600 | 46137600 | 77673600 | 109209600
2031-07-28 01:00 | 3152.48 | 1 | 66.1503 | 59.8258 | 923.9007 |  | 4057 | 14605200 | 46141200 | 77677200 | 109213200
2031-07-29 02:00 | 794.024 | 1 | 66.2492 | 59.8258 | 232.7055 |  | 4058 | 14608800 | 46144800 | 77680800 | 109216800
2031-07-30 03:00 | 2108.26 | 1 | 65.7093 | 59.8258 | 617.87 |  | 4059 | 14612400 | 46148400 | 77684400 | 109220400
2031-07-31 04:00 | 3164.06 | 1 | 65.5397 | 59.8258 | 927.2944 |  | 4060 | 14616000 | 46152000 | 77688000 | 109224000
2031-08-01 05:00 | 3266.94 | 1 | 65.6089 | 59.8258 | 957.4456 |  | 4061 | 14619600 | 46155600 | 77691600 | 109227600
2031-08-02 06:00 | 3253.64 | 1 | 65.5955 | 59.8258 | 953.5478 |  | 4062 | 14623200 | 46159200 | 77695200 | 109231200
2031-08-03 07:00 | 3258.13 | 1 | 80.9698 | 59.8258 | 954.8636 |  | 4063 | 14626800 | 46162800 | 77698800 | 109234800
2031-08-04 08:00 | 4313.86 | 1.3506 | 80.4397 | 59.8258 | 1264.2676 |  | 4064 | 14630400 | 46166400 | 77702400 | 109238400
2031-08-05 09:00 | 6296.15 | 2.0633 | 79.9128 | 59.8258 | 1845.2194 |  | 4065 | 14634000 | 46170000 | 77706000 | 109242000
2031-08-06 10:00 | 7680.03 | 2.5549 | 80.0221 | 59.8258 | 2250.7946 |  | 4066 | 14637600 | 46173600 | 77709600 | 109245600
2031-08-07 11:00 | 9098.87 | 3.0337 | 80.3323 | 59.8258 | 2666.6156 |  | 4067 | 14641200 | 46177200 | 77713200 | 109249200
2031-08-08 12:00 | 10112.6 | 3.3486 | 80.8093 | 59.8258 | 2963.7105 |  | 4068 | 14644800 | 46180800 | 77716800 | 109252800
2031-08-09 13:00 | 10579 | 3.4276 | 81.5011 | 59.8258 | 3100.3988 |  | 4069 | 14648400 | 46184400 | 77720400 | 109256400
2031-08-10 14:00 | 11264.3 | 3.5879 | 82.083 | 59.8258 | 3301.2405 |  | 4070 | 14652000 | 46188000 | 77724000 | 109260000
2031-08-11 15:00 | 12914.5 | 4.2078 | 82.0566 | 59.8258 | 3784.8663 |  | 4071 | 14655600 | 46191600 | 77727600 | 109263600
2031-08-12 16:00 | 13292.5 | 4.2466 | 82.7514 | 59.8258 | 3895.6472 |  | 4072 | 14659200 | 46195200 | 77731200 | 109267200
2031-08-13 17:00 | 13124 | 4.1983 | 83.0558 | 59.8258 | 3846.2647 |  | 4073 | 14662800 | 46198800 | 77734800 | 109270800
2031-08-14 18:00 | 11875.9 | 3.688 | 83.7065 | 59.8258 | 3480.4827 |  | 4074 | 14666400 | 46202400 | 77738400 | 109274400
2031-08-15 19:00 | 10010.6 | 3.103 | 83.792 | 59.8258 | 2933.8173 |  | 4075 | 14670000 | 46206000 | 77742000 | 109278000
2031-08-16 20:00 | 7281.6 | 2.2239 | 83.8925 | 59.8258 | 2134.0263 |  | 4076 | 14673600 | 46209600 | 77745600 | 109281600
2031-08-17 21:00 | 6330.27 | 1.8674 | 84.0221 | 59.8258 | 1855.219 |  | 4077 | 14677200 | 46213200 | 77749200 | 109285200
2031-08-18 22:00 | 3848.84 | 1.1509 | 83.5045 | 59.8258 | 1127.9837 |  | 4078 | 14680800 | 46216800 | 77752800 | 109288800
2031-08-19 23:00 | 3247.14 | 1 | 88.1954 | 59.8258 | 951.6428 |  | 4079 | 14684400 | 46220400 | 77756400 | 109292400
2031-08-21 | 3130.51 | 1 | 67.0277 | 59.8258 | 917.4619 |  | 4080 | 14688000 | 46224000 | 77760000 | 109296000
2031-08-22 01:00 | 3134.22 | 1 | 66.7757 | 59.8258 | 918.5492 |  | 4081 | 14691600 | 46227600 | 77763600 | 109299600
2031-08-23 02:00 | 3164 | 1 | 66.6112 | 59.8258 | 927.2769 |  | 4082 | 14695200 | 46231200 | 77767200 | 109303200
2031-08-24 03:00 | 3187.19 | 1 | 66.4523 | 59.8258 | 934.0732 |  | 4083 | 14698800 | 46234800 | 77770800 | 109306800
2031-08-25 04:00 | 3177.94 | 1 | 66.3455 | 59.8258 | 931.3623 |  | 4084 | 14702400 | 46238400 | 77774400 | 109310400
2031-08-26 05:00 | 3262.61 | 1 | 66.2397 | 59.8258 | 956.1766 |  | 4085 | 14706000 | 46242000 | 77778000 | 109314000
2031-08-27 06:00 | 3180.68 | 1 | 85.9482 | 59.8258 | 932.1653 |  | 4086 | 14709600 | 46245600 | 77781600 | 109317600
2031-08-28 07:00 | 3862.66 | 1.1854 | 81.239 | 59.8258 | 1132.0339 |  | 4087 | 14713200 | 46249200 | 77785200 | 109321200
2031-08-29 08:00 | 4480.99 | 1.3804 | 81.2261 | 59.8258 | 1313.2485 |  | 4088 | 14716800 | 46252800 | 77788800 | 109324800
2031-08-30 09:00 | 5857.9 | 1.8944 | 80.5916 | 59.8258 | 1716.781 |  | 4089 | 14720400 | 46256400 | 77792400 | 109328400
2031-08-31 10:00 | 7619.72 | 2.5033 | 80.5809 | 59.8258 | 2233.1195 |  | 4090 | 14724000 | 46260000 | 77796000 | 109332000
2031-09-01 11:00 | 7953.59 | 2.6199 | 80.8926 | 59.8258 | 2330.9671 |  | 4091 | 14727600 | 46263600 | 77799600 | 109335600
2031-09-02 12:00 | 8627.51 | 2.8333 | 81.1744 | 59.8258 | 2528.4736 |  | 4092 | 14731200 | 46267200 | 77803200 | 109339200
2031-09-03 13:00 | 8622.62 | 2.6663 | 82.271 | 59.8258 | 2527.0405 |  | 4093 | 14734800 | 46270800 | 77806800 | 109342800
2031-09-04 14:00 | 6164.7 | 1.807 | 83.2514 | 59.8258 | 1806.6952 |  | 4094 | 14738400 | 46274400 | 77810400 | 109346400
2031-09-05 15:00 | 6884.18 | 2.1382 | 82.1227 | 59.8258 | 2017.554 |  | 4095 | 14742000 | 46278000 | 77814000 | 109350000
2031-09-06 16:00 | 6779.68 | 2.1513 | 81.7562 | 59.8258 | 1986.9281 |  | 4096 | 14745600 | 46281600 | 77817600 | 109353600
2031-09-07 17:00 | 7102 | 2.3551 | 81.1019 | 59.8258 | 2081.3907 |  | 4097 | 14749200 | 46285200 | 77821200 | 109357200
2031-09-08 18:00 | 5875.75 | 1.8227 | 82.0522 | 59.8258 | 1722.0123 |  | 4098 | 14752800 | 46288800 | 77824800 | 109360800
2031-09-09 19:00 | 4844.28 | 1.4762 | 82.143 | 59.8258 | 1419.7183 |  | 4099 | 14756400 | 46292400 | 77828400 | 109364400
2031-09-10 20:00 | 3168.29 | 1 | 85.9264 | 59.8258 | 928.5341 |  | 4100 | 14760000 | 46296000 | 77832000 | 109368000
2031-09-11 21:00 | 3196.93 | 1 | 66.3556 | 59.8258 | 936.9277 |  | 4101 | 14763600 | 46299600 | 77835600 | 109371600
2031-09-12 22:00 | 0 | 0 | 66.4578 | 59.8258 | 0 |  | 4102 | 14767200 | 46303200 | 77839200 | 109375200
2031-09-13 23:00 | -380.863 | 1.4466 | 64.6726 | 59.8258 | -111.6199 |  | 4103 | 14770800 | 46306800 | 77842800 | 109378800
2031-09-15 | -581.137 | 1.996 | 64.1174 | 59.8258 | -170.3144 |  | 4104 | 14774400 | 46310400 | 77846400 | 109382400
2031-09-16 01:00 | -718.03 | 2.3253 | 63.7415 | 59.8258 | -210.4338 |  | 4105 | 14778000 | 46314000 | 77850000 | 109386000
2031-09-17 02:00 | -640.163 | 2.0925 | 63.538 | 59.8258 | -187.6133 |  | 4106 | 14781600 | 46317600 | 77853600 | 109389600
2031-09-18 03:00 | -666.649 | 2.1892 | 63.3413 | 59.8258 | -195.3755 |  | 4107 | 14785200 | 46321200 | 77857200 | 109393200
2031-09-19 04:00 | -659.899 | 2.166 | 63.2054 | 59.8258 | -193.3973 |  | 4108 | 14788800 | 46324800 | 77860800 | 109396800
2031-09-20 05:00 | -164.325 | 0.82939 | 63.5611 | 59.8258 | -48.1589 |  | 4109 | 14792400 | 46328400 | 77864400 | 109400400
2031-09-21 06:00 | 1992.97 | 1 | 64.2461 | 59.8258 | 584.0819 |  | 4110 | 14796000 | 46332000 | 77868000 | 109404000
2031-09-22 07:00 | 2824.14 | 1 | 64.3983 | 59.8258 | 827.6737 |  | 4111 | 14799600 | 46335600 | 77871600 | 109407600
2031-09-23 08:00 | 3076.39 | 1 | 83.4434 | 59.8258 | 901.6009 |  | 4112 | 14803200 | 46339200 | 77875200 | 109411200
2031-09-24 09:00 | 4339.26 | 1.3615 | 79.515 | 59.8258 | 1271.7116 |  | 4113 | 14806800 | 46342800 | 77878800 | 109414800
2031-09-25 10:00 | 5956.76 | 1.9743 | 78.9962 | 59.8258 | 1745.754 |  | 4114 | 14810400 | 46346400 | 77882400 | 109418400
2031-09-26 11:00 | 7226.86 | 2.3694 | 79.5232 | 59.8258 | 2117.9836 |  | 4115 | 14814000 | 46350000 | 77886000 | 109422000
2031-09-27 12:00 | 7922.93 | 2.4886 | 80.493 | 59.8258 | 2321.9816 |  | 4116 | 14817600 | 46353600 | 77889600 | 109425600
2031-09-28 13:00 | 8816.72 | 2.8004 | 80.6361 | 59.8258 | 2583.9256 |  | 4117 | 14821200 | 46357200 | 77893200 | 109429200
2031-09-29 14:00 | 9428.76 | 3.0773 | 80.6005 | 59.8258 | 2763.2968 |  | 4118 | 14824800 | 46360800 | 77896800 | 109432800
2031-09-30 15:00 | 11230.1 | 3.7441 | 80.6187 | 59.8258 | 3291.2174 |  | 4119 | 14828400 | 46364400 | 77900400 | 109436400
2031-10-01 16:00 | 12000.1 | 3.8948 | 81.4488 | 59.8258 | 3516.8821 |  | 4120 | 14832000 | 46368000 | 77904000 | 109440000
2031-10-02 17:00 | 12140.2 | 3.8461 | 82.1988 | 59.8258 | 3557.9414 |  | 4121 | 14835600 | 46371600 | 77907600 | 109443600
2031-10-03 18:00 | 10562.7 | 3.3006 | 82.6998 | 59.8258 | 3095.6218 |  | 4122 | 14839200 | 46375200 | 77911200 | 109447200
2031-10-04 19:00 | 9114.86 | 2.8125 | 82.9226 | 59.8258 | 2671.3018 |  | 4123 | 14842800 | 46378800 | 77914800 | 109450800
2031-10-05 20:00 | 6670.91 | 1.9592 | 83.606 | 59.8258 | 1955.0507 |  | 4124 | 14846400 | 46382400 | 77918400 | 109454400
2031-10-06 21:00 | 5523.91 | 1.6423 | 83.0969 | 59.8258 | 1618.8982 |  | 4125 | 14850000 | 46386000 | 77922000 | 109458000
2031-10-07 22:00 | 3272.44 | 1 | 85.4583 | 59.8258 | 959.0575 |  | 4126 | 14853600 | 46389600 | 77925600 | 109461600
2031-10-08 23:00 | 3176.43 | 1 | 92.1318 | 59.8258 | 930.9197 |  | 4127 | 14857200 | 46393200 | 77929200 | 109465200
2031-10-10 | 3205.1 | 1 | 66.4054 | 59.8258 | 939.3221 |  | 4128 | 14860800 | 46396800 | 77932800 | 109468800
2031-10-11 01:00 | 3099.9 | 1 | 66.2556 | 59.8258 | 908.491 |  | 4129 | 14864400 | 46400400 | 77936400 | 109472400
2031-10-12 02:00 | 1601 | 1 | 66.257 | 59.8258 | 469.2068 |  | 4130 | 14868000 | 46404000 | 77940000 | 109476000
2031-10-13 03:00 | 2224.06 | 1 | 65.8731 | 59.8258 | 651.8076 |  | 4131 | 14871600 | 46407600 | 77943600 | 109479600
2031-10-14 04:00 | 3199.41 | 1 | 65.6743 | 59.8258 | 937.6545 |  | 4132 | 14875200 | 46411200 | 77947200 | 109483200
2031-10-15 05:00 | 3254.3 | 1 | 65.7044 | 59.8258 | 953.7412 |  | 4133 | 14878800 | 46414800 | 77950800 | 109486800
2031-10-16 06:00 | 3238.89 | 1 | 89.3171 | 59.8258 | 949.225 |  | 4134 | 14882400 | 46418400 | 77954400 | 109490400
2031-10-17 07:00 | 3997.97 | 1.1784 | 81.3721 | 59.8258 | 1171.6893 |  | 4135 | 14886000 | 46422000 | 77958000 | 109494000
2031-10-18 08:00 | 4592.73 | 1.3815 | 81.1711 | 59.8258 | 1345.9963 |  | 4136 | 14889600 | 46425600 | 77961600 | 109497600
2031-10-19 09:00 | 6067.01 | 2.0596 | 79.5523 | 59.8258 | 1778.0651 |  | 4137 | 14893200 | 46429200 | 77965200 | 109501200
2031-10-20 10:00 | 7710.96 | 2.6984 | 79.3893 | 59.8258 | 2259.8593 |  | 4138 | 14896800 | 46432800 | 77968800 | 109504800
2031-10-21 11:00 | 8847.72 | 3.0612 | 79.8867 | 59.8258 | 2593.0108 |  | 4139 | 14900400 | 46436400 | 77972400 | 109508400
2031-10-22 12:00 | 9841.06 | 3.2232 | 80.9827 | 59.8258 | 2884.13 |  | 4140 | 14904000 | 46440000 | 77976000 | 109512000
2031-10-23 13:00 | 10639.3 | 3.4571 | 81.4375 | 59.8258 | 3118.071 |  | 4141 | 14907600 | 46443600 | 77979600 | 109515600
2031-10-24 14:00 | 11600.7 | 3.6942 | 82.0865 | 59.8258 | 3399.8296 |  | 4142 | 14911200 | 46447200 | 77983200 | 109519200
2031-10-25 15:00 | 13361.6 | 4.2997 | 82.2914 | 59.8258 | 3915.8984 |  | 4143 | 14914800 | 46450800 | 77986800 | 109522800
2031-10-26 16:00 | 14007.6 | 4.4218 | 83.032 | 59.8258 | 4105.2223 |  | 4144 | 14918400 | 46454400 | 77990400 | 109526400
2031-10-27 17:00 | 14013.8 | 4.4164 | 83.4516 | 59.8258 | 4107.0394 |  | 4145 | 14922000 | 46458000 | 77994000 | 109530000
2031-10-28 18:00 | 12524.8 | 3.8836 | 83.9898 | 59.8258 | 3670.6565 |  | 4146 | 14925600 | 46461600 | 77997600 | 109533600
2031-10-29 19:00 | 10402.4 | 3.2047 | 84.1525 | 59.8258 | 3048.6425 |  | 4147 | 14929200 | 46465200 | 78001200 | 109537200
2031-10-30 20:00 | 7814.08 | 2.3312 | 84.4972 | 59.8258 | 2290.0808 |  | 4148 | 14932800 | 46468800 | 78004800 | 109540800
2031-10-31 21:00 | 6475.93 | 1.9359 | 84.0903 | 59.8258 | 1897.9077 |  | 4149 | 14936400 | 46472400 | 78008400 | 109544400
2031-11-01 22:00 | 4230.04 | 1.2321 | 84.1538 | 59.8258 | 1239.7023 |  | 4150 | 14940000 | 46476000 | 78012000 | 109548000
2031-11-02 23:00 | 3225.07 | 1 | 87.2762 | 59.8258 | 945.1747 |  | 4151 | 14943600 | 46479600 | 78015600 | 109551600
2031-11-04 | 3159.9 | 1 | 67.2462 | 59.8258 | 926.0753 |  | 4152 | 14947200 | 46483200 | 78019200 | 109555200
2031-11-05 01:00 | 3089.46 | 1 | 66.9833 | 59.8258 | 905.4313 |  | 4153 | 14950800 | 46486800 | 78022800 | 109558800
2031-11-06 02:00 | 3153.16 | 1 | 66.7889 | 59.8258 | 924.1 |  | 4154 | 14954400 | 46490400 | 78026400 | 109562400
2031-11-07 03:00 | 2905.35 | 1 | 66.6426 | 59.8258 | 851.474 |  | 4155 | 14958000 | 46494000 | 78030000 | 109566000
2031-11-08 04:00 | 74.0119 | 1 | 66.7299 | 59.8258 | 21.6907 |  | 4156 | 14961600 | 46497600 | 78033600 | 109569600
2031-11-09 05:00 | 50.3337 | 1 | 66.21 | 59.8258 | 14.7514 |  | 4157 | 14965200 | 46501200 | 78037200 | 109573200
2031-11-10 06:00 | 2197.99 | 1.2197 | 74.1239 | 59.8258 | 644.1673 |  | 4158 | 14968800 | 46504800 | 78040800 | 109576800
2031-11-11 07:00 | 4468.85 | 1.8164 | 77.1769 | 59.8258 | 1309.6907 |  | 4159 | 14972400 | 46508400 | 78044400 | 109580400
2031-11-12 08:00 | 4855.7 | 1.6802 | 79.4106 | 59.8258 | 1423.0652 |  | 4160 | 14976000 | 46512000 | 78048000 | 109584000
2031-11-13 09:00 | 6204.59 | 2.1596 | 79.4534 | 59.8258 | 1818.3858 |  | 4161 | 14979600 | 46515600 | 78051600 | 109587600
2031-11-14 10:00 | 8367.65 | 2.8268 | 80.1299 | 59.8258 | 2452.3161 |  | 4162 | 14983200 | 46519200 | 78055200 | 109591200
2031-11-15 11:00 | 9576.89 | 3.2974 | 80.3603 | 59.8258 | 2806.7094 |  | 4163 | 14986800 | 46522800 | 78058800 | 109594800
2031-11-16 12:00 | 9976.49 | 3.4073 | 80.8968 | 59.8258 | 2923.8206 |  | 4164 | 14990400 | 46526400 | 78062400 | 109598400
2031-11-17 13:00 | 10880.2 | 3.4886 | 82.0464 | 59.8258 | 3188.6719 |  | 4165 | 14994000 | 46530000 | 78066000 | 109602000
2031-11-18 14:00 | 11581.9 | 3.7264 | 82.3149 | 59.8258 | 3394.3198 |  | 4166 | 14997600 | 46533600 | 78069600 | 109605600
2031-11-19 15:00 | 11891.8 | 3.9068 | 82.326 | 59.8258 | 3485.1426 |  | 4167 | 15001200 | 46537200 | 78073200 | 109609200
2031-11-20 16:00 | 14296.3 | 4.7188 | 82.5039 | 59.8258 | 4189.8319 |  | 4168 | 15004800 | 46540800 | 78076800 | 109612800
2031-11-21 17:00 | 13539.8 | 4.3957 | 83.2513 | 59.8258 | 3968.1237 |  | 4169 | 15008400 | 46544400 | 78080400 | 109616400
2031-11-22 18:00 | 12326.6 | 3.8793 | 83.9464 | 59.8258 | 3612.5699 |  | 4170 | 15012000 | 46548000 | 78084000 | 109620000
2031-11-23 19:00 | 10525.1 | 3.2121 | 84.4219 | 59.8258 | 3084.6023 |  | 4171 | 15015600 | 46551600 | 78087600 | 109623600
2031-11-24 20:00 | 8869.71 | 2.7291 | 84.1785 | 59.8258 | 2599.4554 |  | 4172 | 15019200 | 46555200 | 78091200 | 109627200
2031-11-25 21:00 | 7423.88 | 2.2898 | 83.931 | 59.8258 | 2175.7245 |  | 4173 | 15022800 | 46558800 | 78094800 | 109630800
2031-11-26 22:00 | 6373.56 | 1.9916 | 83.4296 | 59.8258 | 1867.906 |  | 4174 | 15026400 | 46562400 | 78098400 | 109634400
2031-11-27 23:00 | 3330.5 | 1 | 85.8742 | 59.8258 | 976.0732 |  | 4175 | 15030000 | 46566000 | 78102000 | 109638000
2031-11-29 | 3244.39 | 1 | 67.6358 | 59.8258 | 950.8368 |  | 4176 | 15033600 | 46569600 | 78105600 | 109641600
2031-11-30 01:00 | 3172.15 | 1 | 67.2877 | 59.8258 | 929.6654 |  | 4177 | 15037200 | 46573200 | 78109200 | 109645200
2031-12-01 02:00 | 2698.78 | 1 | 67.1029 | 59.8258 | 790.9343 |  | 4178 | 15040800 | 46576800 | 78112800 | 109648800
2031-12-02 03:00 | 616.59 | 1 | 67.0351 | 59.8258 | 180.7047 |  | 4179 | 15044400 | 46580400 | 78116400 | 109652400
2031-12-03 04:00 | -24.9023 | 0.61165 | 66.4029 | 59.8258 | -7.2981 |  | 4180 | 15048000 | 46584000 | 78120000 | 109656000
2031-12-04 05:00 | -249.278 | 1.1677 | 65.2349 | 59.8258 | -73.0562 |  | 4181 | 15051600 | 46587600 | 78123600 | 109659600
2031-12-05 06:00 | 2055.16 | 1 | 77.4306 | 59.8258 | 602.3079 |  | 4182 | 15055200 | 46591200 | 78127200 | 109663200
2031-12-06 07:00 | 4262.04 | 1.4722 | 79.1962 | 59.8258 | 1249.0806 |  | 4183 | 15058800 | 46594800 | 78130800 | 109666800
2031-12-07 08:00 | 4675.17 | 1.5246 | 80.2346 | 59.8258 | 1370.1571 |  | 4184 | 15062400 | 46598400 | 78134400 | 109670400
2031-12-08 09:00 | 6098.63 | 2.0433 | 80.0133 | 59.8258 | 1787.332 |  | 4185 | 15066000 | 46602000 | 78138000 | 109674000
2031-12-09 10:00 | 7859.15 | 2.6966 | 79.9457 | 59.8258 | 2303.2895 |  | 4186 | 15069600 | 46605600 | 78141600 | 109677600
2031-12-10 11:00 | 9163.34 | 3.155 | 80.3285 | 59.8258 | 2685.5099 |  | 4187 | 15073200 | 46609200 | 78145200 | 109681200
2031-12-11 12:00 | 10429.1 | 3.3877 | 81.5241 | 59.8258 | 3056.4675 |  | 4188 | 15076800 | 46612800 | 78148800 | 109684800
2031-12-12 13:00 | 11404.7 | 3.6526 | 82.105 | 59.8258 | 3342.3876 |  | 4189 | 15080400 | 46616400 | 78152400 | 109688400
2031-12-13 14:00 | 11343.9 | 3.8033 | 81.8616 | 59.8258 | 3324.5689 |  | 4190 | 15084000 | 46620000 | 78156000 | 109692000
2031-12-14 15:00 | 12003.5 | 3.9077 | 82.5367 | 59.8258 | 3517.8786 |  | 4191 | 15087600 | 46623600 | 78159600 | 109695600
2031-12-15 16:00 | 14863 | 4.8406 | 82.7959 | 59.8258 | 4355.9153 |  | 4192 | 15091200 | 46627200 | 78163200 | 109699200
2031-12-16 17:00 | 14156.3 | 4.4752 | 83.8354 | 59.8258 | 4148.802 |  | 4193 | 15094800 | 46630800 | 78166800 | 109702800
2031-12-17 18:00 | 12929 | 4.02 | 84.3727 | 59.8258 | 3789.1159 |  | 4194 | 15098400 | 46634400 | 78170400 | 109706400
2031-12-18 19:00 | 10939.4 | 3.4094 | 84.3851 | 59.8258 | 3206.0217 |  | 4195 | 15102000 | 46638000 | 78174000 | 109710000
2031-12-19 20:00 | 9623.97 | 2.9342 | 84.5959 | 59.8258 | 2820.5072 |  | 4196 | 15105600 | 46641600 | 78177600 | 109713600
2031-12-20 21:00 | 8527.8 | 2.5433 | 84.7697 | 59.8258 | 2499.2515 |  | 4197 | 15109200 | 46645200 | 78181200 | 109717200
2031-12-21 22:00 | 7748.5 | 2.4137 | 83.8836 | 59.8258 | 2270.8612 |  | 4198 | 15112800 | 46648800 | 78184800 | 109720800
2031-12-22 23:00 | 5455.38 | 1.5471 | 85.1256 | 59.8258 | 1598.8141 |  | 4199 | 15116400 | 46652400 | 78188400 | 109724400
2031-12-24 | 4344.27 | 1.318 | 83.6469 | 59.8258 | 1273.1799 |  | 4200 | 15120000 | 46656000 | 78192000 | 109728000
2031-12-25 01:00 | 3725.93 | 1.1238 | 83.3531 | 59.8258 | 1091.9623 |  | 4201 | 15123600 | 46659600 | 78195600 | 109731600
2031-12-26 02:00 | 3288.03 | 1 | 83.0684 | 59.8258 | 963.6265 |  | 4202 | 15127200 | 46663200 | 78199200 | 109735200
2031-12-27 03:00 | 3273.93 | 1 | 83.6675 | 59.8258 | 959.4942 |  | 4203 | 15130800 | 46666800 | 78202800 | 109738800
2031-12-28 04:00 | 3260.75 | 1 | 83.4876 | 59.8258 | 955.6315 |  | 4204 | 15134400 | 46670400 | 78206400 | 109742400
2031-12-29 05:00 | 3824.42 | 1.2235 | 81.5893 | 59.8258 | 1120.8269 |  | 4205 | 15138000 | 46674000 | 78210000 | 109746000
2031-12-30 06:00 | 4311.33 | 1.3415 | 81.9513 | 59.8258 | 1263.5261 |  | 4206 | 15141600 | 46677600 | 78213600 | 109749600
2031-12-31 07:00 | 4801.03 | 1.5002 | 81.8928 | 59.8258 | 1407.043 |  | 4207 | 15145200 | 46681200 | 78217200 | 109753200
2032-01-01 08:00 | 5556.28 | 1.8881 | 80.7598 | 59.8258 | 1628.3849 |  | 4208 | 15148800 | 46684800 | 78220800 | 109756800
2032-01-02 09:00 | 7528.44 | 2.5434 | 80.935 | 59.8258 | 2206.368 |  | 4209 | 15152400 | 46688400 | 78224400 | 109760400
2032-01-03 10:00 | 9090.91 | 3.0672 | 81.2477 | 59.8258 | 2664.2827 |  | 4210 | 15156000 | 46692000 | 78228000 | 109764000
2032-01-04 11:00 | 10460.4 | 3.4738 | 81.8334 | 59.8258 | 3065.6406 |  | 4211 | 15159600 | 46695600 | 78231600 | 109767600
2032-01-05 12:00 | 11496.5 | 3.6816 | 82.7348 | 59.8258 | 3369.2916 |  | 4212 | 15163200 | 46699200 | 78235200 | 109771200
2032-01-06 13:00 | 12253.4 | 3.9209 | 83.1351 | 59.8258 | 3591.117 |  | 4213 | 15166800 | 46702800 | 78238800 | 109774800
2032-01-07 14:00 | 12687.6 | 4.1108 | 83.3322 | 59.8258 | 3718.3685 |  | 4214 | 15170400 | 46706400 | 78242400 | 109778400
2032-01-08 15:00 | 14466.8 | 4.6232 | 83.824 | 59.8258 | 4239.8006 |  | 4215 | 15174000 | 46710000 | 78246000 | 109782000
2032-01-09 16:00 | 14802 | 4.8087 | 84.0234 | 59.8258 | 4338.038 |  | 4216 | 15177600 | 46713600 | 78249600 | 109785600
2032-01-10 17:00 | 14616.1 | 4.6907 | 84.5308 | 59.8258 | 4283.5561 |  | 4217 | 15181200 | 46717200 | 78253200 | 109789200
2032-01-11 18:00 | 13189.8 | 4.0658 | 85.3351 | 59.8258 | 3865.5488 |  | 4218 | 15184800 | 46720800 | 78256800 | 109792800
2032-01-12 19:00 | 11242.7 | 3.4972 | 85.2248 | 59.8258 | 3294.9101 |  | 4219 | 15188400 | 46724400 | 78260400 | 109796400
2032-01-13 20:00 | 8881.04 | 2.7286 | 85.2548 | 59.8258 | 2602.7759 |  | 4220 | 15192000 | 46728000 | 78264000 | 109800000
2032-01-14 21:00 | 7585.26 | 2.3395 | 84.8263 | 59.8258 | 2223.0203 |  | 4221 | 15195600 | 46731600 | 78267600 | 109803600
2032-01-15 22:00 | 5731.4 | 1.6593 | 85.4365 | 59.8258 | 1679.7075 |  | 4222 | 15199200 | 46735200 | 78271200 | 109807200
2032-01-16 23:00 | 4781.39 | 1.3606 | 85.2609 | 59.8258 | 1401.2871 |  | 4223 | 15202800 | 46738800 | 78274800 | 109810800
2032-01-18 | 4006.79 | 1.2533 | 83.4124 | 59.8258 | 1174.2742 |  | 4224 | 15206400 | 46742400 | 78278400 | 109814400
2032-01-19 01:00 | 3448.18 | 1.0845 | 82.9871 | 59.8258 | 1010.5618 |  | 4225 | 15210000 | 46746000 | 78282000 | 109818000
2032-01-20 02:00 | 3365.09 | 1 | 83.8509 | 59.8258 | 986.2105 |  | 4226 | 15213600 | 46749600 | 78285600 | 109821600
2032-01-21 03:00 | 3305.51 | 1.0074 | 82.9193 | 59.8258 | 968.7494 |  | 4227 | 15217200 | 46753200 | 78289200 | 109825200
2032-01-22 04:00 | 3447.52 | 1.0356 | 82.9597 | 59.8258 | 1010.3684 |  | 4228 | 15220800 | 46756800 | 78292800 | 109828800
2032-01-23 05:00 | 4529.94 | 1.4465 | 81.9188 | 59.8258 | 1327.5944 |  | 4229 | 15224400 | 46760400 | 78296400 | 109832400
2032-01-24 06:00 | 5004.41 | 1.5869 | 82.0498 | 59.8258 | 1466.6478 |  | 4230 | 15228000 | 46764000 | 78300000 | 109836000
2032-01-25 07:00 | 5717 | 1.8334 | 81.9369 | 59.8258 | 1675.4873 |  | 4231 | 15231600 | 46767600 | 78303600 | 109839600
2032-01-26 08:00 | 5806.21 | 1.8676 | 82.0024 | 59.8258 | 1701.6322 |  | 4232 | 15235200 | 46771200 | 78307200 | 109843200
2032-01-27 09:00 | 7198.45 | 2.5387 | 80.8063 | 59.8258 | 2109.6574 |  | 4233 | 15238800 | 46774800 | 78310800 | 109846800
2032-01-28 10:00 | 9396.42 | 3.2155 | 81.4141 | 59.8258 | 2753.8189 |  | 4234 | 15242400 | 46778400 | 78314400 | 109850400
2032-01-29 11:00 | 10502.9 | 3.3937 | 82.6055 | 59.8258 | 3078.0961 |  | 4235 | 15246000 | 46782000 | 78318000 | 109854000
2032-01-30 12:00 | 10089.3 | 3.1464 | 83.4903 | 59.8258 | 2956.8819 |  | 4236 | 15249600 | 46785600 | 78321600 | 109857600
2032-01-31 13:00 | 10401.1 | 3.2799 | 83.4864 | 59.8258 | 3048.2615 |  | 4237 | 15253200 | 46789200 | 78325200 | 109861200
2032-02-01 14:00 | 9541.05 | 3.0562 | 83.4484 | 59.8258 | 2796.2057 |  | 4238 | 15256800 | 46792800 | 78328800 | 109864800
2032-02-02 15:00 | 10257.5 | 3.0966 | 84.3316 | 59.8258 | 3006.1765 |  | 4239 | 15260400 | 46796400 | 78332400 | 109868400
2032-02-03 16:00 | 11566.6 | 3.7845 | 83.2405 | 59.8258 | 3389.8358 |  | 4240 | 15264000 | 46800000 | 78336000 | 109872000
2032-02-04 17:00 | 12001.9 | 3.7932 | 83.9546 | 59.8258 | 3517.4097 |  | 4241 | 15267600 | 46803600 | 78339600 | 109875600
2032-02-05 18:00 | 10734.3 | 3.437 | 83.9747 | 59.8258 | 3145.9128 |  | 4242 | 15271200 | 46807200 | 78343200 | 109879200
2032-02-06 19:00 | 9470.16 | 2.9517 | 84.3364 | 59.8258 | 2775.4299 |  | 4243 | 15274800 | 46810800 | 78346800 | 109882800
2032-02-07 20:00 | 7384.87 | 2.259 | 84.5145 | 59.8258 | 2164.2918 |  | 4244 | 15278400 | 46814400 | 78350400 | 109886400
2032-02-08 21:00 | 6554.66 | 1.9918 | 84.3214 | 59.8258 | 1920.9812 |  | 4245 | 15282000 | 46818000 | 78354000 | 109890000
2032-02-09 22:00 | 4895.94 | 1.4268 | 84.6867 | 59.8258 | 1434.8584 |  | 4246 | 15285600 | 46821600 | 78357600 | 109893600
2032-02-10 23:00 | 4148.85 | 1.2408 | 83.8885 | 59.8258 | 1215.9079 |  | 4247 | 15289200 | 46825200 | 78361200 | 109897200
2032-02-12 | 3759.99 | 1.1208 | 83.6034 | 59.8258 | 1101.9443 |  | 4248 | 15292800 | 46828800 | 78364800 | 109900800
2032-02-13 01:00 | 3373.75 | 1.0453 | 82.7633 | 59.8258 | 988.7485 |  | 4249 | 15296400 | 46832400 | 78368400 | 109904400
2032-02-14 02:00 | 3256.87 | 1 | 83.2812 | 59.8258 | 954.4944 |  | 4250 | 15300000 | 46836000 | 78372000 | 109908000
2032-02-15 03:00 | 3416.89 | 1.0257 | 82.8534 | 59.8258 | 1001.3916 |  | 4251 | 15303600 | 46839600 | 78375600 | 109911600
2032-02-16 04:00 | 3513.42 | 1.0904 | 82.2458 | 59.8258 | 1029.6818 |  | 4252 | 15307200 | 46843200 | 78379200 | 109915200
2032-02-17 05:00 | 4447.01 | 1.3657 | 82.3025 | 59.8258 | 1303.29 |  | 4253 | 15310800 | 46846800 | 78382800 | 109918800
2032-02-18 06:00 | 5222.48 | 1.7213 | 81.3188 | 59.8258 | 1530.5578 |  | 4254 | 15314400 | 46850400 | 78386400 | 109922400
2032-02-19 07:00 | 6230.77 | 1.9998 | 81.7886 | 59.8258 | 1826.0584 |  | 4255 | 15318000 | 46854000 | 78390000 | 109926000
2032-02-20 08:00 | 6452.64 | 2.0883 | 81.8521 | 59.8258 | 1891.0821 |  | 4256 | 15321600 | 46857600 | 78393600 | 109929600
2032-02-21 09:00 | 8154.55 | 2.7543 | 81.3717 | 59.8258 | 2389.8627 |  | 4257 | 15325200 | 46861200 | 78397200 | 109933200
2032-02-22 10:00 | 9833.94 | 3.3839 | 81.4136 | 59.8258 | 2882.0433 |  | 4258 | 15328800 | 46864800 | 78400800 | 109936800
2032-02-23 11:00 | 11858.8 | 3.8537 | 82.583 | 59.8258 | 3475.4712 |  | 4259 | 15332400 | 46868400 | 78404400 | 109940400
2032-02-24 12:00 | 12855 | 4.1767 | 83.0827 | 59.8258 | 3767.4286 |  | 4260 | 15336000 | 46872000 | 78408000 | 109944000
2032-02-25 13:00 | 11876.4 | 3.6867 | 84.1859 | 59.8258 | 3480.6293 |  | 4261 | 15339600 | 46875600 | 78411600 | 109947600
2032-02-26 14:00 | 12123.5 | 3.932 | 83.734 | 59.8258 | 3553.0471 |  | 4262 | 15343200 | 46879200 | 78415200 | 109951200
2032-02-27 15:00 | 14727.4 | 4.7668 | 83.9359 | 59.8258 | 4316.1749 |  | 4263 | 15346800 | 46882800 | 78418800 | 109954800
2032-02-28 16:00 | 15590.4 | 4.9816 | 84.6223 | 59.8258 | 4569.0952 |  | 4264 | 15350400 | 46886400 | 78422400 | 109958400
2032-02-29 17:00 | 15581 | 5.0749 | 84.7632 | 59.8258 | 4566.3403 |  | 4265 | 15354000 | 46890000 | 78426000 | 109962000
2032-03-01 18:00 | 13999.3 | 4.3362 | 85.7497 | 59.8258 | 4102.7898 |  | 4266 | 15357600 | 46893600 | 78429600 | 109965600
2032-03-02 19:00 | 11876.5 | 3.6961 | 85.7276 | 59.8258 | 3480.6586 |  | 4267 | 15361200 | 46897200 | 78433200 | 109969200
2032-03-03 20:00 | 9027.93 | 2.7692 | 85.8096 | 59.8258 | 2645.8251 |  | 4268 | 15364800 | 46900800 | 78436800 | 109972800
2032-03-04 21:00 | 7887.52 | 2.3721 | 85.6852 | 59.8258 | 2311.6039 |  | 4269 | 15368400 | 46904400 | 78440400 | 109976400
2032-03-05 22:00 | 5945.81 | 1.6658 | 86.4413 | 59.8258 | 1742.5449 |  | 4270 | 15372000 | 46908000 | 78444000 | 109980000
2032-03-06 23:00 | 4956.91 | 1.3737 | 86.1414 | 59.8258 | 1452.7269 |  | 4271 | 15375600 | 46911600 | 78447600 | 109983600
2032-03-08 | 3915.54 | 1.1809 | 84.3727 | 59.8258 | 1147.5315 |  | 4272 | 15379200 | 46915200 | 78451200 | 109987200
2032-03-09 01:00 | 3240.09 | 1 | 83.6762 | 59.8258 | 949.5766 |  | 4273 | 15382800 | 46918800 | 78454800 | 109990800
2032-03-10 02:00 | 3068.47 | 1 | 84.2815 | 59.8258 | 899.2798 |  | 4274 | 15386400 | 46922400 | 78458400 | 109994400
2032-03-11 03:00 | 3138.05 | 1 | 83.8564 | 59.8258 | 919.6717 |  | 4275 | 15390000 | 46926000 | 78462000 | 109998000
2032-03-12 04:00 | 3223.29 | 1 | 83.3249 | 59.8258 | 944.653 |  | 4276 | 15393600 | 46929600 | 78465600 | 110001600
2032-03-13 05:00 | 4265.69 | 1.3433 | 82.3561 | 59.8258 | 1250.1503 |  | 4277 | 15397200 | 46933200 | 78469200 | 110005200
2032-03-14 06:00 | 5459.31 | 1.6606 | 82.8575 | 59.8258 | 1599.9658 |  | 4278 | 15400800 | 46936800 | 78472800 | 110008800
2032-03-15 07:00 | 6293.99 | 2.1578 | 81.2806 | 59.8258 | 1844.5864 |  | 4279 | 15404400 | 46940400 | 78476400 | 110012400
2032-03-16 08:00 | 6887.93 | 2.2372 | 82.1873 | 59.8258 | 2018.653 |  | 4280 | 15408000 | 46944000 | 78480000 | 110016000
2032-03-17 09:00 | 8141.96 | 2.7475 | 81.8049 | 59.8258 | 2386.1729 |  | 4281 | 15411600 | 46947600 | 78483600 | 110019600
2032-03-18 10:00 | 9651.39 | 3.199 | 82.3054 | 59.8258 | 2828.5432 |  | 4282 | 15415200 | 46951200 | 78487200 | 110023200
2032-03-19 11:00 | 11214.7 | 3.6054 | 83.0709 | 59.8258 | 3286.7041 |  | 4283 | 15418800 | 46954800 | 78490800 | 110026800
2032-03-20 12:00 | 11873.7 | 3.8058 | 83.5186 | 59.8258 | 3479.838 |  | 4284 | 15422400 | 46958400 | 78494400 | 110030400
2032-03-21 13:00 | 12552 | 3.9662 | 84.0701 | 59.8258 | 3678.6281 |  | 4285 | 15426000 | 46962000 | 78498000 | 110034000
2032-03-22 14:00 | 12955.2 | 4.2117 | 84.0045 | 59.8258 | 3796.7943 |  | 4286 | 15429600 | 46965600 | 78501600 | 110037600
2032-03-23 15:00 | 14266.1 | 4.5514 | 84.5535 | 59.8258 | 4180.9812 |  | 4287 | 15433200 | 46969200 | 78505200 | 110041200
2032-03-24 16:00 | 14280 | 4.5313 | 85.0018 | 59.8258 | 4185.0549 |  | 4288 | 15436800 | 46972800 | 78508800 | 110044800
2032-03-25 17:00 | 14304.2 | 4.5687 | 85.1451 | 59.8258 | 4192.1472 |  | 4289 | 15440400 | 46976400 | 78512400 | 110048400
2032-03-26 18:00 | 12942 | 4.1358 | 85.3267 | 59.8258 | 3792.9258 |  | 4290 | 15444000 | 46980000 | 78516000 | 110052000
2032-03-27 19:00 | 11606.1 | 3.6011 | 85.75 | 59.8258 | 3401.4121 |  | 4291 | 15447600 | 46983600 | 78519600 | 110055600
2032-03-28 20:00 | 9166.97 | 2.7158 | 86.3508 | 59.8258 | 2686.5737 |  | 4292 | 15451200 | 46987200 | 78523200 | 110059200
2032-03-29 21:00 | 7888.14 | 2.3558 | 85.8827 | 59.8258 | 2311.7856 |  | 4293 | 15454800 | 46990800 | 78526800 | 110062800
2032-03-30 22:00 | 5805.21 | 1.6432 | 86.397 | 59.8258 | 1701.3391 |  | 4294 | 15458400 | 46994400 | 78530400 | 110066400
2032-03-31 23:00 | 4711.88 | 1.3969 | 85.1988 | 59.8258 | 1380.9157 |  | 4295 | 15462000 | 46998000 | 78534000 | 110070000
2032-04-02 | 3883.14 | 1.1808 | 84.3923 | 59.8258 | 1138.036 |  | 4296 | 15465600 | 47001600 | 78537600 | 110073600
2032-04-03 01:00 | 3416.29 | 1.0635 | 83.6706 | 59.8258 | 1001.2158 |  | 4297 | 15469200 | 47005200 | 78541200 | 110077200
2032-04-04 02:00 | 3151.61 | 1 | 83.4608 | 59.8258 | 923.6457 |  | 4298 | 15472800 | 47008800 | 78544800 | 110080800
2032-04-05 03:00 | 3204.05 | 1 | 83.6129 | 59.8258 | 939.0144 |  | 4299 | 15476400 | 47012400 | 78548400 | 110084400
2032-04-06 04:00 | 3163.55 | 1 | 83.0875 | 59.8258 | 927.145 |  | 4300 | 15480000 | 47016000 | 78552000 | 110088000
2032-04-07 05:00 | 4319.3 | 1.3419 | 82.7636 | 59.8258 | 1265.8619 |  | 4301 | 15483600 | 47019600 | 78555600 | 110091600
2032-04-08 06:00 | 5172.16 | 1.6686 | 82.2258 | 59.8258 | 1515.8105 |  | 4302 | 15487200 | 47023200 | 78559200 | 110095200
2032-04-09 07:00 | 6343.64 | 2.1059 | 81.9008 | 59.8258 | 1859.1374 |  | 4303 | 15490800 | 47026800 | 78562800 | 110098800
2032-04-10 08:00 | 6856.1 | 2.2836 | 82.0324 | 59.8258 | 2009.3246 |  | 4304 | 15494400 | 47030400 | 78566400 | 110102400
2032-04-11 09:00 | 8516.42 | 2.7767 | 82.4704 | 59.8258 | 2495.9163 |  | 4305 | 15498000 | 47034000 | 78570000 | 110106000
2032-04-12 10:00 | 10055.4 | 3.3577 | 82.4466 | 59.8258 | 2946.9468 |  | 4306 | 15501600 | 47037600 | 78573600 | 110109600
2032-04-13 11:00 | 11139.4 | 3.684 | 82.9559 | 59.8258 | 3264.6359 |  | 4307 | 15505200 | 47041200 | 78577200 | 110113200
2032-04-14 12:00 | 12333.5 | 3.8648 | 84.0807 | 59.8258 | 3614.592 |  | 4308 | 15508800 | 47044800 | 78580800 | 110116800
2032-04-15 13:00 | 13266.3 | 4.151 | 84.4861 | 59.8258 | 3887.9687 |  | 4309 | 15512400 | 47048400 | 78584400 | 110120400
2032-04-16 14:00 | 13542.7 | 4.382 | 84.4029 | 59.8258 | 3968.9736 |  | 4310 | 15516000 | 47052000 | 78588000 | 110124000
2032-04-17 15:00 | 15196 | 4.9605 | 84.5574 | 59.8258 | 4453.508 |  | 4311 | 15519600 | 47055600 | 78591600 | 110127600
2032-04-18 16:00 | 15923.8 | 5.1224 | 85.185 | 59.8258 | 4666.8051 |  | 4312 | 15523200 | 47059200 | 78595200 | 110131200
2032-04-19 17:00 | 15768.9 | 5.037 | 85.6682 | 59.8258 | 4621.4084 |  | 4313 | 15526800 | 47062800 | 78598800 | 110134800
2032-04-20 18:00 | 14615 | 4.5105 | 86.4167 | 59.8258 | 4283.2337 |  | 4314 | 15530400 | 47066400 | 78602400 | 110138400
2032-04-21 19:00 | 12836.7 | 3.9528 | 86.5099 | 59.8258 | 3762.0654 |  | 4315 | 15534000 | 47070000 | 78606000 | 110142000
2032-04-22 20:00 | 10229.7 | 3.0602 | 86.8541 | 59.8258 | 2998.0291 |  | 4316 | 15537600 | 47073600 | 78609600 | 110145600
2032-04-23 21:00 | 8736.97 | 2.63 | 86.4036 | 59.8258 | 2560.5531 |  | 4317 | 15541200 | 47077200 | 78613200 | 110149200
2032-04-24 22:00 | 6752.53 | 1.924 | 86.9024 | 59.8258 | 1978.9712 |  | 4318 | 15544800 | 47080800 | 78616800 | 110152800
2032-04-25 23:00 | 5377.52 | 1.5415 | 86.3477 | 59.8258 | 1575.9955 |  | 4319 | 15548400 | 47084400 | 78620400 | 110156400
2032-04-27 | 4140.2 | 1.2967 | 84.5403 | 59.8258 | 1213.3728 |  | 4320 | 15552000 | 47088000 | 78624000 | 110160000
2032-04-28 01:00 | 3392.49 | 1.05 | 84.2684 | 59.8258 | 994.2407 |  | 4321 | 15555600 | 47091600 | 78627600 | 110163600
2032-04-29 02:00 | 3074.49 | 1 | 86.6539 | 59.8258 | 901.0441 |  | 4322 | 15559200 | 47095200 | 78631200 | 110167200
2032-04-30 03:00 | 3243.37 | 1 | 92.7165 | 59.8258 | 950.5379 |  | 4323 | 15562800 | 47098800 | 78634800 | 110170800
2032-05-01 04:00 | 3112.82 | 1 | 68.3141 | 59.8258 | 912.2775 |  | 4324 | 15566400 | 47102400 | 78638400 | 110174400
2032-05-02 05:00 | 3183.79 | 1 | 68.1036 | 59.8258 | 933.0767 |  | 4325 | 15570000 | 47106000 | 78642000 | 110178000
2032-05-03 06:00 | 4288.04 | 1.3425 | 82.8368 | 59.8258 | 1256.7005 |  | 4326 | 15573600 | 47109600 | 78645600 | 110181600
2032-05-04 07:00 | 6290.27 | 2.0576 | 82.17 | 59.8258 | 1843.4962 |  | 4327 | 15577200 | 47113200 | 78649200 | 110185200
2032-05-05 08:00 | 6531.19 | 2.0256 | 83.1811 | 59.8258 | 1914.1028 |  | 4328 | 15580800 | 47116800 | 78652800 | 110188800
2032-05-06 09:00 | 7652.26 | 2.5063 | 82.5164 | 59.8258 | 2242.656 |  | 4329 | 15584400 | 47120400 | 78656400 | 110192400
2032-05-07 10:00 | 9271.56 | 3.1789 | 82.0885 | 59.8258 | 2717.226 |  | 4330 | 15588000 | 47124000 | 78660000 | 110196000
2032-05-08 11:00 | 11555.6 | 3.7885 | 83.0409 | 59.8258 | 3386.6121 |  | 4331 | 15591600 | 47127600 | 78663600 | 110199600
2032-05-09 12:00 | 12130 | 3.9335 | 83.7037 | 59.8258 | 3554.9521 |  | 4332 | 15595200 | 47131200 | 78667200 | 110203200
2032-05-10 13:00 | 12681.5 | 4.1474 | 83.9425 | 59.8258 | 3716.5808 |  | 4333 | 15598800 | 47134800 | 78670800 | 110206800
2032-05-11 14:00 | 12665.3 | 3.8286 | 85.4069 | 59.8258 | 3711.833 |  | 4334 | 15602400 | 47138400 | 78674400 | 110210400
2032-05-12 15:00 | 12931.4 | 4.0924 | 84.9498 | 59.8258 | 3789.8192 |  | 4335 | 15606000 | 47142000 | 78678000 | 110214000
2032-05-13 16:00 | 15270.5 | 5.035 | 84.5603 | 59.8258 | 4475.3418 |  | 4336 | 15609600 | 47145600 | 78681600 | 110217600
2032-05-14 17:00 | 13675.1 | 4.3304 | 85.592 | 59.8258 | 4007.7762 |  | 4337 | 15613200 | 47149200 | 78685200 | 110221200
2032-05-15 18:00 | 12969.3 | 4.0727 | 85.7966 | 59.8258 | 3800.9266 |  | 4338 | 15616800 | 47152800 | 78688800 | 110224800
2032-05-16 19:00 | 11749.5 | 3.5387 | 86.3998 | 59.8258 | 3443.4385 |  | 4339 | 15620400 | 47156400 | 78692400 | 110228400
2032-05-17 20:00 | 10089.7 | 3.1181 | 85.9527 | 59.8258 | 2956.9992 |  | 4340 | 15624000 | 47160000 | 78696000 | 110232000
2032-05-18 21:00 | 8657.39 | 2.707 | 85.5826 | 59.8258 | 2537.2306 |  | 4341 | 15627600 | 47163600 | 78699600 | 110235600
2032-05-19 22:00 | 7687.28 | 2.3642 | 85.5176 | 59.8258 | 2252.9194 |  | 4342 | 15631200 | 47167200 | 78703200 | 110239200
2032-05-20 23:00 | 4178.18 | 1.2028 | 86.2627 | 59.8258 | 1224.5037 |  | 4343 | 15634800 | 47170800 | 78706800 | 110242800
2032-05-22 | 3282.05 | 1.0118 | 84.5753 | 59.8258 | 961.8739 |  | 4344 | 15638400 | 47174400 | 78710400 | 110246400
2032-05-23 01:00 | 3115.14 | 1 | 90.9988 | 59.8258 | 912.9574 |  | 4345 | 15642000 | 47178000 | 78714000 | 110250000
2032-05-24 02:00 | 3023.37 | 1 | 68.6745 | 59.8258 | 886.0623 |  | 4346 | 15645600 | 47181600 | 78717600 | 110253600
2032-05-25 03:00 | 2895.44 | 1 | 68.4375 | 59.8258 | 848.5697 |  | 4347 | 15649200 | 47185200 | 78721200 | 110257200
2032-05-26 04:00 | 0 | 0 | 68.4333 | 59.8258 | 0 |  | 4348 | 15652800 | 47188800 | 78724800 | 110260800
2032-05-27 05:00 | -120.092 | 0.83251 | 67.2143 | 59.8258 | -35.1955 |  | 4349 | 15656400 | 47192400 | 78728400 | 110264400
2032-05-28 06:00 | 2237.96 | 1 | 67.2853 | 59.8258 | 655.8813 |  | 4350 | 15660000 | 47196000 | 78732000 | 110268000
2032-05-29 07:00 | 2858.05 | 1 | 82.0959 | 59.8258 | 837.6118 |  | 4351 | 15663600 | 47199600 | 78735600 | 110271600
2032-05-30 08:00 | 2955.82 | 1 | 84.5276 | 59.8258 | 866.2653 |  | 4352 | 15667200 | 47203200 | 78739200 | 110275200
2032-05-31 09:00 | 3510.3 | 1.1588 | 81.2755 | 59.8258 | 1028.7674 |  | 4353 | 15670800 | 47206800 | 78742800 | 110278800
2032-06-01 10:00 | 4362.77 | 1.5046 | 80.7061 | 59.8258 | 1278.6017 |  | 4354 | 15674400 | 47210400 | 78746400 | 110282400
2032-06-02 11:00 | 5458.97 | 1.8738 | 80.8883 | 59.8258 | 1599.8662 |  | 4355 | 15678000 | 47214000 | 78750000 | 110286000
2032-06-03 12:00 | 6006.3 | 2.0065 | 81.406 | 59.8258 | 1760.2728 |  | 4356 | 15681600 | 47217600 | 78753600 | 110289600
2032-06-04 13:00 | 6492.39 | 2.083 | 82.0864 | 59.8258 | 1902.7317 |  | 4357 | 15685200 | 47221200 | 78757200 | 110293200
2032-06-05 14:00 | 6581.32 | 2.1811 | 81.7455 | 59.8258 | 1928.7945 |  | 4358 | 15688800 | 47224800 | 78760800 | 110296800
2032-06-06 15:00 | 6819.77 | 2.2527 | 81.849 | 59.8258 | 1998.6773 |  | 4359 | 15692400 | 47228400 | 78764400 | 110300400
2032-06-07 16:00 | 9825.28 | 3.2084 | 82.0581 | 59.8258 | 2879.5053 |  | 4360 | 15696000 | 47232000 | 78768000 | 110304000
2032-06-08 17:00 | 8737.92 | 2.9085 | 82.2418 | 59.8258 | 2560.8316 |  | 4361 | 15699600 | 47235600 | 78771600 | 110307600
2032-06-09 18:00 | 7781.57 | 2.5225 | 82.7041 | 59.8258 | 2280.553 |  | 4362 | 15703200 | 47239200 | 78775200 | 110311200
2032-06-10 19:00 | 6405.63 | 1.9909 | 83.2315 | 59.8258 | 1877.3048 |  | 4363 | 15706800 | 47242800 | 78778800 | 110314800
2032-06-11 20:00 | 4995.47 | 1.5887 | 82.7435 | 59.8258 | 1464.0277 |  | 4364 | 15710400 | 47246400 | 78782400 | 110318400
2032-06-12 21:00 | 3532.43 | 1.0772 | 83.1299 | 59.8258 | 1035.253 |  | 4365 | 15714000 | 47250000 | 78786000 | 110322000
2032-06-13 22:00 | 3081.73 | 1 | 87.7002 | 59.8258 | 903.1659 |  | 4366 | 15717600 | 47253600 | 78789600 | 110325600
2032-06-14 23:00 | 0 | 0 | 67.5228 | 59.8258 | 0 |  | 4367 | 15721200 | 47257200 | 78793200 | 110329200
2032-06-16 | -855.521 | 2.6831 | 65.4813 | 59.8258 | -250.7285 |  | 4368 | 15724800 | 47260800 | 78796800 | 110332800
2032-06-17 01:00 | -1251.94 | 3.6526 | 64.8942 | 59.8258 | -366.9074 |  | 4369 | 15728400 | 47264400 | 78800400 | 110336400
2032-06-18 02:00 | -1443.62 | 4.0975 | 64.5063 | 59.8258 | -423.0833 |  | 4370 | 15732000 | 47268000 | 78804000 | 110340000
2032-06-19 03:00 | -1588.49 | 4.463 | 64.2042 | 59.8258 | -465.5405 |  | 4371 | 15735600 | 47271600 | 78807600 | 110343600
2032-06-20 04:00 | -1675.39 | 4.6816 | 63.9075 | 59.8258 | -491.0083 |  | 4372 | 15739200 | 47275200 | 78811200 | 110347200
2032-06-21 05:00 | -1294.32 | 3.639 | 63.7125 | 59.8258 | -379.3277 |  | 4373 | 15742800 | 47278800 | 78814800 | 110350800
2032-06-22 06:00 | -750.388 | 2.267 | 63.6915 | 59.8258 | -219.917 |  | 4374 | 15746400 | 47282400 | 78818400 | 110354400
2032-06-23 07:00 | 2245.92 | 1 | 64.943 | 59.8258 | 658.2142 |  | 4375 | 15750000 | 47286000 | 78822000 | 110358000
2032-06-24 08:00 | 2528.72 | 1 | 65.2375 | 59.8258 | 741.0947 |  | 4376 | 15753600 | 47289600 | 78825600 | 110361600
2032-06-25 09:00 | 3239.43 | 1.0575 | 79.6739 | 59.8258 | 949.3832 |  | 4377 | 15757200 | 47293200 | 78829200 | 110365200
2032-06-26 10:00 | 6000.95 | 1.923 | 80.0356 | 59.8258 | 1758.7048 |  | 4378 | 15760800 | 47296800 | 78832800 | 110368800
2032-06-27 11:00 | 7710.04 | 2.4831 | 80.4432 | 59.8258 | 2259.5897 |  | 4379 | 15764400 | 47300400 | 78836400 | 110372400
2032-06-28 12:00 | 8127.48 | 2.5609 | 81.286 | 59.8258 | 2381.9293 |  | 4380 | 15768000 | 47304000 | 78840000 | 110376000
2032-06-29 13:00 | 8206.38 | 2.5871 | 81.6033 | 59.8258 | 2405.0526 |  | 4381 | 15771600 | 47307600 | 78843600 | 110379600
2032-06-30 14:00 | 7967.89 | 2.4202 | 82.4016 | 59.8258 | 2335.158 |  | 4382 | 15775200 | 47311200 | 78847200 | 110383200
2032-07-01 15:00 | 8877.17 | 2.755 | 82.2533 | 59.8258 | 2601.6417 |  | 4383 | 15778800 | 47314800 | 78850800 | 110386800
2032-07-02 16:00 | 9235.42 | 2.8958 | 82.3253 | 59.8258 | 2706.6344 |  | 4384 | 15782400 | 47318400 | 78854400 | 110390400
2032-07-03 17:00 | 9262.56 | 2.7412 | 83.3898 | 59.8258 | 2714.5884 |  | 4385 | 15786000 | 47322000 | 78858000 | 110394000
2032-07-04 18:00 | 7438.88 | 2.3555 | 82.5323 | 59.8258 | 2180.1205 |  | 4386 | 15789600 | 47325600 | 78861600 | 110397600
2032-07-05 19:00 | 6413.08 | 1.9642 | 82.8898 | 59.8258 | 1879.4882 |  | 4387 | 15793200 | 47329200 | 78865200 | 110401200
2032-07-06 20:00 | 4237.34 | 1.2157 | 83.7509 | 59.8258 | 1241.8418 |  | 4388 | 15796800 | 47332800 | 78868800 | 110404800
2032-07-07 21:00 | 3183.61 | 1 | 82.1179 | 59.8258 | 933.024 |  | 4389 | 15800400 | 47336400 | 78872400 | 110408400
2032-07-08 22:00 | 3200.93 | 1 | 66.8413 | 59.8258 | 938.1 |  | 4390 | 15804000 | 47340000 | 78876000 | 110412000
2032-07-09 23:00 | 3033.77 | 1 | 66.6513 | 59.8258 | 889.1102 |  | 4391 | 15807600 | 47343600 | 78879600 | 110415600
2032-07-11 | 0 | 0 | 66.7708 | 59.8258 | 0 |  | 4392 | 15811200 | 47347200 | 78883200 | 110419200
2032-07-12 01:00 | 68.362 | 1 | 66.2327 | 59.8258 | 20.0349 |  | 4393 | 15814800 | 47350800 | 78886800 | 110422800
2032-07-13 02:00 | 3361.71 | 1 | 65.6471 | 59.8258 | 985.2199 |  | 4394 | 15818400 | 47354400 | 78890400 | 110426400
2032-07-14 03:00 | 590.961 | 1 | 66.1727 | 59.8258 | 173.1936 |  | 4395 | 15822000 | 47358000 | 78894000 | 110430000
2032-07-15 04:00 | 2585.41 | 1 | 65.7058 | 59.8258 | 757.7089 |  | 4396 | 15825600 | 47361600 | 78897600 | 110433600
2032-07-16 05:00 | 2968.5 | 1 | 65.7001 | 59.8258 | 869.9815 |  | 4397 | 15829200 | 47365200 | 78901200 | 110437200
2032-07-17 06:00 | 3138.34 | 1 | 65.8262 | 59.8258 | 919.7567 |  | 4398 | 15832800 | 47368800 | 78904800 | 110440800
2032-07-18 07:00 | 3192.26 | 1 | 90.43 | 59.8258 | 935.5591 |  | 4399 | 15836400 | 47372400 | 78908400 | 110444400
2032-07-19 08:00 | 3191.81 | 1 | 65.8676 | 59.8258 | 935.4272 |  | 4400 | 15840000 | 47376000 | 78912000 | 110448000
2032-07-20 09:00 | 3167.76 | 1 | 65.9296 | 59.8258 | 928.3788 |  | 4401 | 15843600 | 47379600 | 78915600 | 110451600
2032-07-21 10:00 | 3256.47 | 1 | 84.2591 | 59.8258 | 954.3771 |  | 4402 | 15847200 | 47383200 | 78919200 | 110455200
2032-07-22 11:00 | 3928 | 1.1847 | 81.2909 | 59.8258 | 1151.1832 |  | 4403 | 15850800 | 47386800 | 78922800 | 110458800
2032-07-23 12:00 | 5536.31 | 1.8143 | 80.1617 | 59.8258 | 1622.5323 |  | 4404 | 15854400 | 47390400 | 78926400 | 110462400
2032-07-24 13:00 | 6615.66 | 2.1506 | 80.5244 | 59.8258 | 1938.8586 |  | 4405 | 15858000 | 47394000 | 78930000 | 110466000
2032-07-25 14:00 | 7351.54 | 2.4301 | 80.5351 | 59.8258 | 2154.5237 |  | 4406 | 15861600 | 47397600 | 78933600 | 110469600
2032-07-26 15:00 | 9310.6 | 3.1 | 80.6802 | 59.8258 | 2728.6675 |  | 4407 | 15865200 | 47401200 | 78937200 | 110473200
2032-07-27 16:00 | 9942.26 | 3.2363 | 81.3955 | 59.8258 | 2913.7888 |  | 4408 | 15868800 | 47404800 | 78940800 | 110476800
2032-07-28 17:00 | 9990.94 | 3.2061 | 81.9347 | 59.8258 | 2928.0555 |  | 4409 | 15872400 | 47408400 | 78944400 | 110480400
2032-07-29 18:00 | 8749.51 | 2.7904 | 82.2484 | 59.8258 | 2564.2283 |  | 4410 | 15876000 | 47412000 | 78948000 | 110484000
2032-07-30 19:00 | 8109.58 | 2.4104 | 83.3117 | 59.8258 | 2376.6833 |  | 4411 | 15879600 | 47415600 | 78951600 | 110487600
2032-07-31 20:00 | 6043.14 | 1.6852 | 84.3335 | 59.8258 | 1771.0695 |  | 4412 | 15883200 | 47419200 | 78955200 | 110491200
2032-08-01 21:00 | 5101.47 | 1.4608 | 83.6774 | 59.8258 | 1495.0933 |  | 4413 | 15886800 | 47422800 | 78958800 | 110494800
2032-08-02 22:00 | 3093.38 | 1 | 87.4031 | 59.8258 | 906.5802 |  | 4414 | 15890400 | 47426400 | 78962400 | 110498400
2032-08-03 23:00 | 2866.21 | 1 | 66.8729 | 59.8258 | 840.0032 |  | 4415 | 15894000 | 47430000 | 78966000 | 110502000
2032-08-05 | 0 | 0 | 66.9105 | 59.8258 | 0 |  | 4416 | 15897600 | 47433600 | 78969600 | 110505600
2032-08-06 01:00 | 0 | 0 | 66.3773 | 59.8258 | 0 |  | 4417 | 15901200 | 47437200 | 78973200 | 110509200
2032-08-07 02:00 | -202.249 | 1.048 | 65.1514 | 59.8258 | -59.2733 |  | 4418 | 15904800 | 47440800 | 78976800 | 110512800
2032-08-08 03:00 | -254.672 | 1.154 | 64.7691 | 59.8258 | -74.637 |  | 4419 | 15908400 | 47444400 | 78980400 | 110516400
2032-08-09 04:00 | -341.928 | 1.3797 | 64.4217 | 59.8258 | -100.2092 |  | 4420 | 15912000 | 47448000 | 78984000 | 110520000
2032-08-10 05:00 | -343.105 | 1.3679 | 64.1829 | 59.8258 | -100.5541 |  | 4421 | 15915600 | 47451600 | 78987600 | 110523600
2032-08-11 06:00 | 1869.76 | 1 | 65.0214 | 59.8258 | 547.9726 |  | 4422 | 15919200 | 47455200 | 78991200 | 110527200
2032-08-12 07:00 | 2554.68 | 1 | 77.7204 | 59.8258 | 748.7028 |  | 4423 | 15922800 | 47458800 | 78994800 | 110530800
2032-08-13 08:00 | 3286.19 | 1.0477 | 79.8274 | 59.8258 | 963.0872 |  | 4424 | 15926400 | 47462400 | 78998400 | 110534400
2032-08-14 09:00 | 4903.29 | 1.6551 | 79.1609 | 59.8258 | 1437.0124 |  | 4425 | 15930000 | 47466000 | 79002000 | 110538000
2032-08-15 10:00 | 6615.4 | 2.2936 | 79.107 | 59.8258 | 1938.7824 |  | 4426 | 15933600 | 47469600 | 79005600 | 110541600
2032-08-16 11:00 | 8456.74 | 2.7433 | 80.422 | 59.8258 | 2478.4258 |  | 4427 | 15937200 | 47473200 | 79009200 | 110545200
2032-08-17 12:00 | 8981.57 | 2.8693 | 81.1205 | 59.8258 | 2632.2383 |  | 4428 | 15940800 | 47476800 | 79012800 | 110548800
2032-08-18 13:00 | 9052.34 | 2.8358 | 81.773 | 59.8258 | 2652.979 |  | 4429 | 15944400 | 47480400 | 79016400 | 110552400
2032-08-19 14:00 | 10213.2 | 3.1869 | 82.0943 | 59.8258 | 2993.1935 |  | 4430 | 15948000 | 47484000 | 79020000 | 110556000
2032-08-20 15:00 | 10920.8 | 3.4906 | 82.0979 | 59.8258 | 3200.5705 |  | 4431 | 15951600 | 47487600 | 79023600 | 110559600
2032-08-21 16:00 | 13574.2 | 4.4436 | 82.0842 | 59.8258 | 3978.2053 |  | 4432 | 15955200 | 47491200 | 79027200 | 110563200
2032-08-22 17:00 | 12260.7 | 3.908 | 83.0458 | 59.8258 | 3593.2565 |  | 4433 | 15958800 | 47494800 | 79030800 | 110566800
2032-08-23 18:00 | 11271 | 3.4792 | 83.718 | 59.8258 | 3303.204 |  | 4434 | 15962400 | 47498400 | 79034400 | 110570400
2032-08-24 19:00 | 9757.25 | 3.0179 | 83.745 | 59.8258 | 2859.5677 |  | 4435 | 15966000 | 47502000 | 79038000 | 110574000
2032-08-25 20:00 | 8077.14 | 2.5393 | 83.4475 | 59.8258 | 2367.1761 |  | 4436 | 15969600 | 47505600 | 79041600 | 110577600
2032-08-26 21:00 | 7306.85 | 2.1789 | 84.0402 | 59.8258 | 2141.4263 |  | 4437 | 15973200 | 47509200 | 79045200 | 110581200
2032-08-27 22:00 | 6559.72 | 2.0034 | 83.4589 | 59.8258 | 1922.4642 |  | 4438 | 15976800 | 47512800 | 79048800 | 110584800
2032-08-28 23:00 | 3777.29 | 1.1006 | 83.9866 | 59.8258 | 1107.0144 |  | 4439 | 15980400 | 47516400 | 79052400 | 110588400
2032-08-30 | 3297.33 | 1 | 86.2272 | 59.8258 | 966.352 |  | 4440 | 15984000 | 47520000 | 79056000 | 110592000
2032-08-31 01:00 | 3179.94 | 1 | 91.7288 | 59.8258 | 931.9484 |  | 4441 | 15987600 | 47523600 | 79059600 | 110595600
2032-09-01 02:00 | 3172.8 | 1 | 67.0294 | 59.8258 | 929.8559 |  | 4442 | 15991200 | 47527200 | 79063200 | 110599200
2032-09-02 03:00 | 3198.27 | 1 | 66.8782 | 59.8258 | 937.3204 |  | 4443 | 15994800 | 47530800 | 79066800 | 110602800
2032-09-03 04:00 | 3066.55 | 1 | 66.7248 | 59.8258 | 898.7171 |  | 4444 | 15998400 | 47534400 | 79070400 | 110606400
2032-09-04 05:00 | 3207.01 | 1 | 86.9135 | 59.8258 | 939.8819 |  | 4445 | 16002000 | 47538000 | 79074000 | 110610000
2032-09-05 06:00 | 3953.57 | 1.1748 | 82.1682 | 59.8258 | 1158.677 |  | 4446 | 16005600 | 47541600 | 79077600 | 110613600
2032-09-06 07:00 | 4983.19 | 1.5493 | 81.5303 | 59.8258 | 1460.4288 |  | 4447 | 16009200 | 47545200 | 79081200 | 110617200
2032-09-07 08:00 | 4736.41 | 1.5192 | 81.2254 | 59.8258 | 1388.1047 |  | 4448 | 16012800 | 47548800 | 79084800 | 110620800
2032-09-08 09:00 | 6317.24 | 2.0853 | 80.8373 | 59.8258 | 1851.4003 |  | 4449 | 16016400 | 47552400 | 79088400 | 110624400
2032-09-09 10:00 | 8420.13 | 2.8358 | 80.7685 | 59.8258 | 2467.6965 |  | 4450 | 16020000 | 47556000 | 79092000 | 110628000
2032-09-10 11:00 | 9657.96 | 3.2806 | 81.0818 | 59.8258 | 2830.4687 |  | 4451 | 16023600 | 47559600 | 79095600 | 110631600
2032-09-11 12:00 | 10705.7 | 3.5194 | 81.9325 | 59.8258 | 3137.531 |  | 4452 | 16027200 | 47563200 | 79099200 | 110635200
2032-09-12 13:00 | 11538.5 | 3.7555 | 82.4496 | 59.8258 | 3381.6005 |  | 4453 | 16030800 | 47566800 | 79102800 | 110638800
2032-09-13 14:00 | 12251.9 | 4.0396 | 82.6564 | 59.8258 | 3590.6774 |  | 4454 | 16034400 | 47570400 | 79106400 | 110642400
2032-09-14 15:00 | 14554 | 4.4854 | 83.9698 | 59.8258 | 4265.3564 |  | 4455 | 16038000 | 47574000 | 79110000 | 110646000
2032-09-15 16:00 | 15353 | 4.7121 | 84.5581 | 59.8258 | 4499.5201 |  | 4456 | 16041600 | 47577600 | 79113600 | 110649600
2032-09-16 17:00 | 14590.6 | 4.5739 | 84.7157 | 59.8258 | 4276.0828 |  | 4457 | 16045200 | 47581200 | 79117200 | 110653200
2032-09-17 18:00 | 12801.3 | 3.9883 | 85.0325 | 59.8258 | 3751.6907 |  | 4458 | 16048800 | 47584800 | 79120800 | 110656800
2032-09-18 19:00 | 11041.1 | 3.3864 | 85.2451 | 59.8258 | 3235.827 |  | 4459 | 16052400 | 47588400 | 79124400 | 110660400
2032-09-19 20:00 | 8446.76 | 2.5306 | 85.4781 | 59.8258 | 2475.501 |  | 4460 | 16056000 | 47592000 | 79128000 | 110664000
2032-09-20 21:00 | 7055.23 | 2.1437 | 84.8856 | 59.8258 | 2067.6838 |  | 4461 | 16059600 | 47595600 | 79131600 | 110667600
2032-09-21 22:00 | 4590.8 | 1.3244 | 85.3002 | 59.8258 | 1345.4307 |  | 4462 | 16063200 | 47599200 | 79135200 | 110671200
2032-09-22 23:00 | 3577.79 | 1.0858 | 83.9813 | 59.8258 | 1048.5467 |  | 4463 | 16066800 | 47602800 | 79138800 | 110674800
2032-09-24 | 3200.25 | 1 | 88.3691 | 59.8258 | 937.9007 |  | 4464 | 16070400 | 47606400 | 79142400 | 110678400
2032-09-25 01:00 | 3147.93 | 1 | 67.876 | 59.8258 | 922.5672 |  | 4465 | 16074000 | 47610000 | 79146000 | 110682000
2032-09-26 02:00 | 3219.49 | 1 | 67.6526 | 59.8258 | 943.5394 |  | 4466 | 16077600 | 47613600 | 79149600 | 110685600
2032-09-27 03:00 | 3116.53 | 1 | 67.468 | 59.8258 | 913.3648 |  | 4467 | 16081200 | 47617200 | 79153200 | 110689200
2032-09-28 04:00 | 3155.87 | 1 | 67.3026 | 59.8258 | 924.8942 |  | 4468 | 16084800 | 47620800 | 79156800 | 110692800
2032-09-29 05:00 | 3252.49 | 1 | 87.5151 | 59.8258 | 953.2107 |  | 4469 | 16088400 | 47624400 | 79160400 | 110696400
2032-09-30 06:00 | 3881.4 | 1.1437 | 82.8523 | 59.8258 | 1137.5261 |  | 4470 | 16092000 | 47628000 | 79164000 | 110700000
2032-10-01 07:00 | 5045.13 | 1.6738 | 81.1182 | 59.8258 | 1478.5816 |  | 4471 | 16095600 | 47631600 | 79167600 | 110703600
2032-10-02 08:00 | 5601.86 | 1.8212 | 81.5427 | 59.8258 | 1641.7431 |  | 4472 | 16099200 | 47635200 | 79171200 | 110707200
2032-10-03 09:00 | 7092.53 | 2.4187 | 81.0109 | 59.8258 | 2078.6154 |  | 4473 | 16102800 | 47638800 | 79174800 | 110710800
2032-10-04 10:00 | 8638.14 | 2.9425 | 81.2881 | 59.8258 | 2531.5889 |  | 4474 | 16106400 | 47642400 | 79178400 | 110714400
2032-10-05 11:00 | 9627.15 | 3.3238 | 81.4727 | 59.8258 | 2821.4392 |  | 4475 | 16110000 | 47646000 | 79182000 | 110718000
2032-10-06 12:00 | 10348.8 | 3.5099 | 82.0532 | 59.8258 | 3032.9339 |  | 4476 | 16113600 | 47649600 | 79185600 | 110721600
2032-10-07 13:00 | 10861.6 | 3.7268 | 82.199 | 59.8258 | 3183.2207 |  | 4477 | 16117200 | 47653200 | 79189200 | 110725200
2032-10-08 14:00 | 11974.1 | 3.8225 | 83.4692 | 59.8258 | 3509.2623 |  | 4478 | 16120800 | 47656800 | 79192800 | 110728800
2032-10-09 15:00 | 14253.9 | 4.5344 | 83.8327 | 59.8258 | 4177.4057 |  | 4479 | 16124400 | 47660400 | 79196400 | 110732400
2032-10-10 16:00 | 14998.3 | 4.8657 | 84.0587 | 59.8258 | 4395.5678 |  | 4480 | 16128000 | 47664000 | 79200000 | 110736000
2032-10-11 17:00 | 14956.5 | 4.8376 | 84.5286 | 59.8258 | 4383.3175 |  | 4481 | 16131600 | 47667600 | 79203600 | 110739600
2032-10-12 18:00 | 13907.4 | 4.3786 | 85.2138 | 59.8258 | 4075.8566 |  | 4482 | 16135200 | 47671200 | 79207200 | 110743200
2032-10-13 19:00 | 11830.2 | 3.6491 | 85.6431 | 59.8258 | 3467.0894 |  | 4483 | 16138800 | 47674800 | 79210800 | 110746800
2032-10-14 20:00 | 8873.56 | 2.709 | 85.7015 | 59.8258 | 2600.5837 |  | 4484 | 16142400 | 47678400 | 79214400 | 110750400
2032-10-15 21:00 | 7481.36 | 2.2866 | 85.2758 | 59.8258 | 2192.5702 |  | 4485 | 16146000 | 47682000 | 79218000 | 110754000
2032-10-16 22:00 | 5311.27 | 1.5461 | 85.6507 | 59.8258 | 1556.5796 |  | 4486 | 16149600 | 47685600 | 79221600 | 110757600
2032-10-17 23:00 | 3255.83 | 1 | 84.5712 | 59.8258 | 954.1896 |  | 4487 | 16153200 | 47689200 | 79225200 | 110761200
2032-10-19 | 3174.73 | 1 | 90.0742 | 59.8258 | 930.4215 |  | 4488 | 16156800 | 47692800 | 79228800 | 110764800
2032-10-20 01:00 | 3156.53 | 1 | 68.2596 | 59.8258 | 925.0876 |  | 4489 | 16160400 | 47696400 | 79232400 | 110768400
2032-10-21 02:00 | 3043.36 | 1 | 68.0449 | 59.8258 | 891.9208 |  | 4490 | 16164000 | 47700000 | 79236000 | 110772000
2032-10-22 03:00 | 0 | 0 | 68.084 | 59.8258 | 0 |  | 4491 | 16167600 | 47703600 | 79239600 | 110775600
2032-10-23 04:00 | -215.64 | 1.0669 | 66.5519 | 59.8258 | -63.1978 |  | 4492 | 16171200 | 47707200 | 79243200 | 110779200
2032-10-24 05:00 | -341.467 | 1.3634 | 65.9163 | 59.8258 | -100.0741 |  | 4493 | 16174800 | 47710800 | 79246800 | 110782800
2032-10-25 06:00 | 2163.84 | 1 | 66.5624 | 59.8258 | 634.1589 |  | 4494 | 16178400 | 47714400 | 79250400 | 110786400
2032-10-26 07:00 | 3403.23 | 1.1752 | 80.0773 | 59.8258 | 997.3883 |  | 4495 | 16182000 | 47718000 | 79254000 | 110790000
2032-10-27 08:00 | 4521.39 | 1.4563 | 81.1213 | 59.8258 | 1325.0886 |  | 4496 | 16185600 | 47721600 | 79257600 | 110793600
2032-10-28 09:00 | 6130.59 | 2.0825 | 80.5706 | 59.8258 | 1796.6986 |  | 4497 | 16189200 | 47725200 | 79261200 | 110797200
2032-10-29 10:00 | 8131.96 | 2.7208 | 81.0885 | 59.8258 | 2383.2422 |  | 4498 | 16192800 | 47728800 | 79264800 | 110800800
2032-10-30 11:00 | 9732.51 | 3.2522 | 81.5764 | 59.8258 | 2852.3171 |  | 4499 | 16196400 | 47732400 | 79268400 | 110804400
2032-10-31 12:00 | 10895.5 | 3.5463 | 82.3971 | 59.8258 | 3193.1558 |  | 4500 | 16200000 | 47736000 | 79272000 | 110808000
2032-11-01 13:00 | 11837.8 | 3.8469 | 82.8392 | 59.8258 | 3469.3167 |  | 4501 | 16203600 | 47739600 | 79275600 | 110811600
2032-11-02 14:00 | 12780.2 | 4.1396 | 83.2791 | 59.8258 | 3745.5069 |  | 4502 | 16207200 | 47743200 | 79279200 | 110815200
2032-11-03 15:00 | 13723.6 | 4.4231 | 83.7522 | 59.8258 | 4021.9901 |  | 4503 | 16210800 | 47746800 | 79282800 | 110818800
2032-11-04 16:00 | 16290.1 | 5.2291 | 84.1962 | 59.8258 | 4774.157 |  | 4504 | 16214400 | 47750400 | 79286400 | 110822400
2032-11-05 17:00 | 15149.9 | 4.8079 | 84.996 | 59.8258 | 4439.9974 |  | 4505 | 16218000 | 47754000 | 79290000 | 110826000
2032-11-06 18:00 | 13688.6 | 4.3575 | 85.2151 | 59.8258 | 4011.7326 |  | 4506 | 16221600 | 47757600 | 79293600 | 110829600
2032-11-07 19:00 | 11838.6 | 3.6512 | 85.7028 | 59.8258 | 3469.5512 |  | 4507 | 16225200 | 47761200 | 79297200 | 110833200
2032-11-08 20:00 | 10015.1 | 3.1353 | 85.3748 | 59.8258 | 2935.1361 |  | 4508 | 16228800 | 47764800 | 79300800 | 110836800
2032-11-09 21:00 | 8910.77 | 2.7235 | 85.499 | 59.8258 | 2611.4889 |  | 4509 | 16232400 | 47768400 | 79304400 | 110840400
2032-11-10 22:00 | 7838.94 | 2.3845 | 85.2995 | 59.8258 | 2297.3665 |  | 4510 | 16236000 | 47772000 | 79308000 | 110844000
2032-11-11 23:00 | 4635.58 | 1.3081 | 86.2125 | 59.8258 | 1358.5544 |  | 4511 | 16239600 | 47775600 | 79311600 | 110847600
2032-11-13 | 3333.78 | 1 | 85.8177 | 59.8258 | 977.0345 |  | 4512 | 16243200 | 47779200 | 79315200 | 110851200
2032-11-14 01:00 | 3192.37 | 1 | 92.7806 | 59.8258 | 935.5913 |  | 4513 | 16246800 | 47782800 | 79318800 | 110854800
2032-11-15 02:00 | 3182.96 | 1 | 68.3347 | 59.8258 | 932.8335 |  | 4514 | 16250400 | 47786400 | 79322400 | 110858400
2032-11-16 03:00 | 3142.31 | 1 | 68.1159 | 59.8258 | 920.9202 |  | 4515 | 16254000 | 47790000 | 79326000 | 110862000
2032-11-17 04:00 | 3147.09 | 1 | 67.8797 | 59.8258 | 922.321 |  | 4516 | 16257600 | 47793600 | 79329600 | 110865600
2032-11-18 05:00 | 3120.99 | 1 | 67.736 | 59.8258 | 914.6719 |  | 4517 | 16261200 | 47797200 | 79333200 | 110869200
2032-11-19 06:00 | 3304.43 | 1 | 83.6951 | 59.8258 | 968.4328 |  | 4518 | 16264800 | 47800800 | 79336800 | 110872800
2032-11-20 07:00 | 5574.95 | 1.7665 | 82.2056 | 59.8258 | 1633.8566 |  | 4519 | 16268400 | 47804400 | 79340400 | 110876400
2032-11-21 08:00 | 6230.42 | 2.0456 | 81.9288 | 59.8258 | 1825.9559 |  | 4520 | 16272000 | 47808000 | 79344000 | 110880000
2032-11-22 09:00 | 7637.48 | 2.6158 | 81.5253 | 59.8258 | 2238.3244 |  | 4521 | 16275600 | 47811600 | 79347600 | 110883600
2032-11-23 10:00 | 9613.98 | 3.252 | 81.9306 | 59.8258 | 2817.5794 |  | 4522 | 16279200 | 47815200 | 79351200 | 110887200
2032-11-24 11:00 | 11514.7 | 3.8414 | 82.5433 | 59.8258 | 3374.6254 |  | 4523 | 16282800 | 47818800 | 79354800 | 110890800
2032-11-25 12:00 | 12394.1 | 4.0575 | 83.333 | 59.8258 | 3632.3521 |  | 4524 | 16286400 | 47822400 | 79358400 | 110894400
2032-11-26 13:00 | 13531.4 | 4.314 | 84.1213 | 59.8258 | 3965.6619 |  | 4525 | 16290000 | 47826000 | 79362000 | 110898000
2032-11-27 14:00 | 14496.5 | 4.6846 | 84.3583 | 59.8258 | 4248.5048 |  | 4526 | 16293600 | 47829600 | 79365600 | 110901600
2032-11-28 15:00 | 14796.6 | 4.8576 | 84.5623 | 59.8258 | 4336.4554 |  | 4527 | 16297200 | 47833200 | 79369200 | 110905200
2032-11-29 16:00 | 17387.4 | 5.4978 | 85.3883 | 59.8258 | 5095.7439 |  | 4528 | 16300800 | 47836800 | 79372800 | 110908800
2032-11-30 17:00 | 17023.8 | 5.4249 | 85.8537 | 59.8258 | 4989.1833 |  | 4529 | 16304400 | 47840400 | 79376400 | 110912400
2032-12-01 18:00 | 15778.5 | 5.024 | 86.233 | 59.8258 | 4624.2219 |  | 4530 | 16308000 | 47844000 | 79380000 | 110916000
2032-12-02 19:00 | 13751.6 | 4.3061 | 86.5761 | 59.8258 | 4030.1961 |  | 4531 | 16311600 | 47847600 | 79383600 | 110919600
2032-12-03 20:00 | 11770.6 | 3.6526 | 86.6101 | 59.8258 | 3449.6223 |  | 4532 | 16315200 | 47851200 | 79387200 | 110923200
2032-12-04 21:00 | 10230.8 | 3.2082 | 86.2339 | 59.8258 | 2998.3515 |  | 4533 | 16318800 | 47854800 | 79390800 | 110926800
2032-12-05 22:00 | 8966.35 | 2.7689 | 86.1406 | 59.8258 | 2627.7778 |  | 4534 | 16322400 | 47858400 | 79394400 | 110930400
2032-12-06 23:00 | 6228.22 | 1.8134 | 86.726 | 59.8258 | 1825.3111 |  | 4535 | 16326000 | 47862000 | 79398000 | 110934000
2032-12-08 | 5258.49 | 1.4929 | 86.5833 | 59.8258 | 1541.1113 |  | 4536 | 16329600 | 47865600 | 79401600 | 110937600
2032-12-09 01:00 | 4343.78 | 1.301 | 85.3036 | 59.8258 | 1273.0363 |  | 4537 | 16333200 | 47869200 | 79405200 | 110941200
2032-12-10 02:00 | 3613.1 | 1.1275 | 84.3095 | 59.8258 | 1058.8951 |  | 4538 | 16336800 | 47872800 | 79408800 | 110944800
2032-12-11 03:00 | 3433.69 | 1.0517 | 84.2265 | 59.8258 | 1006.3152 |  | 4539 | 16340400 | 47876400 | 79412400 | 110948400
2032-12-12 04:00 | 3473.94 | 1.0809 | 83.6842 | 59.8258 | 1018.1113 |  | 4540 | 16344000 | 47880000 | 79416000 | 110952000
2032-12-13 05:00 | 4191.29 | 1.321 | 83.292 | 59.8258 | 1228.3458 |  | 4541 | 16347600 | 47883600 | 79419600 | 110955600
2032-12-14 06:00 | 5273.67 | 1.6549 | 83.2761 | 59.8258 | 1545.5601 |  | 4542 | 16351200 | 47887200 | 79423200 | 110959200
2032-12-15 07:00 | 6538.31 | 2.1735 | 82.5105 | 59.8258 | 1916.1895 |  | 4543 | 16354800 | 47890800 | 79426800 | 110962800
2032-12-16 08:00 | 7398.39 | 2.4432 | 82.7735 | 59.8258 | 2168.2541 |  | 4544 | 16358400 | 47894400 | 79430400 | 110966400
2032-12-17 09:00 | 9117.36 | 3.0517 | 82.7688 | 59.8258 | 2672.0345 |  | 4545 | 16362000 | 47898000 | 79434000 | 110970000
2032-12-18 10:00 | 11009.8 | 3.6642 | 83.1609 | 59.8258 | 3226.6539 |  | 4546 | 16365600 | 47901600 | 79437600 | 110973600
2032-12-19 11:00 | 12740.2 | 4.2145 | 83.6862 | 59.8258 | 3733.784 |  | 4547 | 16369200 | 47905200 | 79441200 | 110977200
2032-12-20 12:00 | 14226.4 | 4.5904 | 84.5235 | 59.8258 | 4169.3463 |  | 4548 | 16372800 | 47908800 | 79444800 | 110980800
2032-12-21 13:00 | 15118.1 | 4.858 | 85.0837 | 59.8258 | 4430.6777 |  | 4549 | 16376400 | 47912400 | 79448400 | 110984400
2032-12-22 14:00 | 15603.1 | 5.15 | 85.1692 | 59.8258 | 4572.8172 |  | 4550 | 16380000 | 47916000 | 79452000 | 110988000
2032-12-23 15:00 | 17631.7 | 5.4925 | 86.3672 | 59.8258 | 5167.3412 |  | 4551 | 16383600 | 47919600 | 79455600 | 110991600
2032-12-24 16:00 | 17866.4 | 5.5432 | 86.9553 | 59.8258 | 5236.125 |  | 4552 | 16387200 | 47923200 | 79459200 | 110995200
2032-12-25 17:00 | 17048.9 | 5.3946 | 87.0646 | 59.8258 | 4996.5394 |  | 4553 | 16390800 | 47926800 | 79462800 | 110998800
2032-12-26 18:00 | 15177.6 | 4.7627 | 87.3609 | 59.8258 | 4448.1155 |  | 4554 | 16394400 | 47930400 | 79466400 | 111002400
2032-12-27 19:00 | 13343.8 | 4.1834 | 87.3185 | 59.8258 | 3910.6817 |  | 4555 | 16398000 | 47934000 | 79470000 | 111006000
2032-12-28 20:00 | 10895 | 3.3839 | 87.2877 | 59.8258 | 3193.0093 |  | 4556 | 16401600 | 47937600 | 79473600 | 111009600
2032-12-29 21:00 | 9219.18 | 2.9015 | 86.707 | 59.8258 | 2701.8749 |  | 4557 | 16405200 | 47941200 | 79477200 | 111013200
2032-12-30 22:00 | 6877.34 | 2.0756 | 86.9053 | 59.8258 | 2015.5494 |  | 4558 | 16408800 | 47944800 | 79480800 | 111016800
2032-12-31 23:00 | 6213.9 | 1.8653 | 86.4424 | 59.8258 | 1821.1143 |  | 4559 | 16412400 | 47948400 | 79484400 | 111020400
2033-01-02 | 5307.22 | 1.5798 | 86.1641 | 59.8258 | 1555.3926 |  | 4560 | 16416000 | 47952000 | 79488000 | 111024000
2033-01-03 01:00 | 4584.98 | 1.3876 | 85.5374 | 59.8258 | 1343.725 |  | 4561 | 16419600 | 47955600 | 79491600 | 111027600
2033-01-04 02:00 | 4049.81 | 1.2317 | 85.1184 | 59.8258 | 1186.8821 |  | 4562 | 16423200 | 47959200 | 79495200 | 111031200
2033-01-05 03:00 | 3870 | 1.2106 | 84.3701 | 59.8258 | 1134.185 |  | 4563 | 16426800 | 47962800 | 79498800 | 111034800
2033-01-06 04:00 | 4224.7 | 1.3248 | 84.0839 | 59.8258 | 1238.1373 |  | 4564 | 16430400 | 47966400 | 79502400 | 111038400
2033-01-07 05:00 | 4970.57 | 1.5527 | 83.9823 | 59.8258 | 1456.7303 |  | 4565 | 16434000 | 47970000 | 79506000 | 111042000
2033-01-08 06:00 | 5473.1 | 1.7103 | 83.9411 | 59.8258 | 1604.0073 |  | 4566 | 16437600 | 47973600 | 79509600 | 111045600
2033-01-09 07:00 | 6637.28 | 2.1832 | 83.2056 | 59.8258 | 1945.1948 |  | 4567 | 16441200 | 47977200 | 79513200 | 111049200
2033-01-10 08:00 | 7039.37 | 2.2363 | 83.834 | 59.8258 | 2063.0357 |  | 4568 | 16444800 | 47980800 | 79516800 | 111052800
2033-01-11 09:00 | 9191.75 | 2.9402 | 83.8389 | 59.8258 | 2693.836 |  | 4569 | 16448400 | 47984400 | 79520400 | 111056400
2033-01-12 10:00 | 10877 | 3.5484 | 83.8958 | 59.8258 | 3187.734 |  | 4570 | 16452000 | 47988000 | 79524000 | 111060000
2033-01-13 11:00 | 12642.6 | 4.1309 | 84.2751 | 59.8258 | 3705.1803 |  | 4571 | 16455600 | 47991600 | 79527600 | 111063600
2033-01-14 12:00 | 13928.1 | 4.4284 | 85.1225 | 59.8258 | 4081.9232 |  | 4572 | 16459200 | 47995200 | 79531200 | 111067200
2033-01-15 13:00 | 14293.6 | 4.6932 | 85.1215 | 59.8258 | 4189.0406 |  | 4573 | 16462800 | 47998800 | 79534800 | 111070800
2033-01-16 14:00 | 15657.1 | 5.0599 | 85.7012 | 59.8258 | 4588.6431 |  | 4574 | 16466400 | 48002400 | 79538400 | 111074400
2033-01-17 15:00 | 17244.8 | 5.5094 | 86.2762 | 59.8258 | 5053.952 |  | 4575 | 16470000 | 48006000 | 79542000 | 111078000
2033-01-18 16:00 | 17400.3 | 5.4438 | 87.071 | 59.8258 | 5099.5245 |  | 4576 | 16473600 | 48009600 | 79545600 | 111081600
2033-01-19 17:00 | 17652.9 | 5.4726 | 87.538 | 59.8258 | 5173.5543 |  | 4577 | 16477200 | 48013200 | 79549200 | 111085200
2033-01-20 18:00 | 15716 | 4.8713 | 87.8385 | 59.8258 | 4605.9049 |  | 4578 | 16480800 | 48016800 | 79552800 | 111088800
2033-01-21 19:00 | 12970.9 | 4.1294 | 87.4672 | 59.8258 | 3801.3955 |  | 4579 | 16484400 | 48020400 | 79556400 | 111092400
2033-01-22 20:00 | 10066.2 | 3.1614 | 87.399 | 59.8258 | 2950.112 |  | 4580 | 16488000 | 48024000 | 79560000 | 111096000
2033-01-23 21:00 | 9065.64 | 2.7791 | 87.2628 | 59.8258 | 2656.8768 |  | 4581 | 16491600 | 48027600 | 79563600 | 111099600
2033-01-24 22:00 | 7261.22 | 2.2062 | 87.0281 | 59.8258 | 2128.0535 |  | 4582 | 16495200 | 48031200 | 79567200 | 111103200
2033-01-25 23:00 | 6723.29 | 2.0388 | 86.5828 | 59.8258 | 1970.4018 |  | 4583 | 16498800 | 48034800 | 79570800 | 111106800
2033-01-27 | 5941.35 | 1.801 | 86.2194 | 59.8258 | 1741.2378 |  | 4584 | 16502400 | 48038400 | 79574400 | 111110400
2033-01-28 01:00 | 5549.48 | 1.6377 | 86.3091 | 59.8258 | 1626.392 |  | 4585 | 16506000 | 48042000 | 79578000 | 111114000
2033-01-29 02:00 | 5145.68 | 1.517 | 86.0668 | 59.8258 | 1508.0499 |  | 4586 | 16509600 | 48045600 | 79581600 | 111117600
2033-01-30 03:00 | 4871.39 | 1.5237 | 84.9265 | 59.8258 | 1427.6635 |  | 4587 | 16513200 | 48049200 | 79585200 | 111121200
2033-01-31 04:00 | 5062.43 | 1.5684 | 84.8504 | 59.8258 | 1483.6518 |  | 4588 | 16516800 | 48052800 | 79588800 | 111124800
2033-02-01 05:00 | 5751.22 | 1.8067 | 84.4852 | 59.8258 | 1685.5162 |  | 4589 | 16520400 | 48056400 | 79592400 | 111128400
2033-02-02 06:00 | 6205.88 | 1.9823 | 84.2063 | 59.8258 | 1818.7639 |  | 4590 | 16524000 | 48060000 | 79596000 | 111132000
2033-02-03 07:00 | 7226.3 | 2.3492 | 83.9609 | 59.8258 | 2117.8195 |  | 4591 | 16527600 | 48063600 | 79599600 | 111135600
2033-02-04 08:00 | 7389.94 | 2.3221 | 84.5798 | 59.8258 | 2165.7776 |  | 4592 | 16531200 | 48067200 | 79603200 | 111139200
2033-02-05 09:00 | 8738.08 | 2.9154 | 83.8059 | 59.8258 | 2560.8785 |  | 4593 | 16534800 | 48070800 | 79606800 | 111142800
2033-02-06 10:00 | 9978.05 | 3.2482 | 84.3593 | 59.8258 | 2924.2778 |  | 4594 | 16538400 | 48074400 | 79610400 | 111146400
2033-02-07 11:00 | 11865.4 | 3.9223 | 84.4116 | 59.8258 | 3477.4055 |  | 4595 | 16542000 | 48078000 | 79614000 | 111150000
2033-02-08 12:00 | 12650.9 | 4.1015 | 85.0796 | 59.8258 | 3707.6128 |  | 4596 | 16545600 | 48081600 | 79617600 | 111153600
2033-02-09 13:00 | 12439.1 | 3.9388 | 85.7485 | 59.8258 | 3645.5403 |  | 4597 | 16549200 | 48085200 | 79621200 | 111157200
2033-02-10 14:00 | 12752.5 | 3.9227 | 86.3535 | 59.8258 | 3737.3888 |  | 4598 | 16552800 | 48088800 | 79624800 | 111160800
2033-02-11 15:00 | 13918.2 | 4.5416 | 85.6618 | 59.8258 | 4079.0218 |  | 4599 | 16556400 | 48092400 | 79628400 | 111164400
2033-02-12 16:00 | 14693.5 | 4.7566 | 86.0492 | 59.8258 | 4306.2398 |  | 4600 | 16560000 | 48096000 | 79632000 | 111168000
2033-02-13 17:00 | 14469.9 | 4.5585 | 86.6974 | 59.8258 | 4240.7091 |  | 4601 | 16563600 | 48099600 | 79635600 | 111171600
2033-02-14 18:00 | 13381.2 | 4.0627 | 87.3878 | 59.8258 | 3921.6426 |  | 4602 | 16567200 | 48103200 | 79639200 | 111175200
2033-02-15 19:00 | 12028.6 | 3.6791 | 87.2787 | 59.8258 | 3525.2347 |  | 4603 | 16570800 | 48106800 | 79642800 | 111178800
2033-02-16 20:00 | 9748.4 | 2.9567 | 87.3171 | 59.8258 | 2856.974 |  | 4604 | 16574400 | 48110400 | 79646400 | 111182400
2033-02-17 21:00 | 9012.55 | 2.7499 | 86.9057 | 59.8258 | 2641.3177 |  | 4605 | 16578000 | 48114000 | 79650000 | 111186000
2033-02-18 22:00 | 7046.15 | 2.0392 | 87.4666 | 59.8258 | 2065.0227 |  | 4606 | 16581600 | 48117600 | 79653600 | 111189600
2033-02-19 23:00 | 6067.6 | 1.8085 | 86.5971 | 59.8258 | 1778.238 |  | 4607 | 16585200 | 48121200 | 79657200 | 111193200
2033-02-21 | 4764.78 | 1.4174 | 86.2495 | 59.8258 | 1396.4192 |  | 4608 | 16588800 | 48124800 | 79660800 | 111196800
2033-02-22 01:00 | 4058.8 | 1.253 | 85.2918 | 59.8258 | 1189.5169 |  | 4609 | 16592400 | 48128400 | 79664400 | 111200400
2033-02-23 02:00 | 3595.09 | 1.12 | 84.8232 | 59.8258 | 1053.6169 |  | 4610 | 16596000 | 48132000 | 79668000 | 111204000
2033-02-24 03:00 | 3776.68 | 1.1783 | 84.4898 | 59.8258 | 1106.8356 |  | 4611 | 16599600 | 48135600 | 79671600 | 111207600
2033-02-25 04:00 | 4003.47 | 1.251 | 84.2652 | 59.8258 | 1173.3012 |  | 4612 | 16603200 | 48139200 | 79675200 | 111211200
2033-02-26 05:00 | 5181.72 | 1.6144 | 84.1556 | 59.8258 | 1518.6122 |  | 4613 | 16606800 | 48142800 | 79678800 | 111214800
2033-02-27 06:00 | 5474.67 | 1.7128 | 84.1238 | 59.8258 | 1604.4674 |  | 4614 | 16610400 | 48146400 | 79682400 | 111218400
2033-02-28 07:00 | 6168.71 | 1.9206 | 84.2063 | 59.8258 | 1807.8704 |  | 4615 | 16614000 | 48150000 | 79686000 | 111222000
2033-03-01 08:00 | 5584.14 | 1.6695 | 84.9013 | 59.8258 | 1636.5499 |  | 4616 | 16617600 | 48153600 | 79689600 | 111225600
2033-03-02 09:00 | 5692.94 | 1.7976 | 84.0293 | 59.8258 | 1668.436 |  | 4617 | 16621200 | 48157200 | 79693200 | 111229200
2033-03-03 10:00 | 6551.31 | 2.214 | 83.0437 | 59.8258 | 1919.9994 |  | 4618 | 16624800 | 48160800 | 79696800 | 111232800
2033-03-04 11:00 | 8463.82 | 2.8453 | 83.1695 | 59.8258 | 2480.5008 |  | 4619 | 16628400 | 48164400 | 79700400 | 111236400
2033-03-05 12:00 | 9320.38 | 3.1111 | 83.5311 | 59.8258 | 2731.5337 |  | 4620 | 16632000 | 48168000 | 79704000 | 111240000
2033-03-06 13:00 | 10054.4 | 3.3849 | 83.6496 | 59.8258 | 2946.6538 |  | 4621 | 16635600 | 48171600 | 79707600 | 111243600
2033-03-07 14:00 | 10838.8 | 3.5201 | 84.3782 | 59.8258 | 3176.5387 |  | 4622 | 16639200 | 48175200 | 79711200 | 111247200
2033-03-08 15:00 | 12601.6 | 4.1616 | 84.3905 | 59.8258 | 3693.1644 |  | 4623 | 16642800 | 48178800 | 79714800 | 111250800
2033-03-09 16:00 | 13279 | 4.3815 | 84.7922 | 59.8258 | 3891.6907 |  | 4624 | 16646400 | 48182400 | 79718400 | 111254400
2033-03-10 17:00 | 12685.1 | 4.0621 | 85.5184 | 59.8258 | 3717.6358 |  | 4625 | 16650000 | 48186000 | 79722000 | 111258000
2033-03-11 18:00 | 11425.9 | 3.5856 | 85.9301 | 59.8258 | 3348.6007 |  | 4626 | 16653600 | 48189600 | 79725600 | 111261600
2033-03-12 19:00 | 10561.4 | 3.2326 | 86.2504 | 59.8258 | 3095.2408 |  | 4627 | 16657200 | 48193200 | 79729200 | 111265200
2033-03-13 20:00 | 8207.33 | 2.5462 | 85.9986 | 59.8258 | 2405.331 |  | 4628 | 16660800 | 48196800 | 79732800 | 111268800
2033-03-14 21:00 | 7625.26 | 2.2463 | 86.4611 | 59.8258 | 2234.7431 |  | 4629 | 16664400 | 48200400 | 79736400 | 111272400
2033-03-15 22:00 | 5956.91 | 1.6854 | 86.8616 | 59.8258 | 1745.798 |  | 4630 | 16668000 | 48204000 | 79740000 | 111276000
2033-03-16 23:00 | 5227.57 | 1.4927 | 86.3637 | 59.8258 | 1532.0495 |  | 4631 | 16671600 | 48207600 | 79743600 | 111279600
2033-03-18 | 4599.37 | 1.3584 | 85.5283 | 59.8258 | 1347.9423 |  | 4632 | 16675200 | 48211200 | 79747200 | 111283200
2033-03-19 01:00 | 4023.71 | 1.2835 | 84.1103 | 59.8258 | 1179.233 |  | 4633 | 16678800 | 48214800 | 79750800 | 111286800
2033-03-20 02:00 | 3800.39 | 1.1954 | 84.0705 | 59.8258 | 1113.7844 |  | 4634 | 16682400 | 48218400 | 79754400 | 111290400
2033-03-21 03:00 | 4069.84 | 1.2658 | 84.0052 | 59.8258 | 1192.7524 |  | 4635 | 16686000 | 48222000 | 79758000 | 111294000
2033-03-22 04:00 | 4306.57 | 1.3337 | 83.9369 | 59.8258 | 1262.1311 |  | 4636 | 16689600 | 48225600 | 79761600 | 111297600
2033-03-23 05:00 | 5257.74 | 1.7037 | 83.1871 | 59.8258 | 1540.8915 |  | 4637 | 16693200 | 48229200 | 79765200 | 111301200
2033-03-24 06:00 | 5560.25 | 1.8065 | 83.1872 | 59.8258 | 1629.5484 |  | 4638 | 16696800 | 48232800 | 79768800 | 111304800
2033-03-25 07:00 | 5827.04 | 1.7709 | 84.1875 | 59.8258 | 1707.7368 |  | 4639 | 16700400 | 48236400 | 79772400 | 111308400
2033-03-26 08:00 | 4759.72 | 1.4593 | 84.1093 | 59.8258 | 1394.9362 |  | 4640 | 16704000 | 48240000 | 79776000 | 111312000
2033-03-27 09:00 | 5965.26 | 1.9573 | 82.9977 | 59.8258 | 1748.2451 |  | 4641 | 16707600 | 48243600 | 79779600 | 111315600
2033-03-28 10:00 | 6368.85 | 2.0567 | 83.3084 | 59.8258 | 1866.5257 |  | 4642 | 16711200 | 48247200 | 79783200 | 111319200
2033-03-29 11:00 | 6871.5 | 2.1936 | 83.5458 | 59.8258 | 2013.8379 |  | 4643 | 16714800 | 48250800 | 79786800 | 111322800
2033-03-30 12:00 | 6794.46 | 2.1792 | 83.549 | 59.8258 | 1991.2597 |  | 4644 | 16718400 | 48254400 | 79790400 | 111326400
2033-03-31 13:00 | 6950.24 | 2.1723 | 83.9338 | 59.8258 | 2036.9143 |  | 4645 | 16722000 | 48258000 | 79794000 | 111330000
2033-04-01 14:00 | 8050.13 | 2.6314 | 83.3289 | 59.8258 | 2359.2602 |  | 4646 | 16725600 | 48261600 | 79797600 | 111333600
2033-04-02 15:00 | 9434.25 | 3.116 | 83.3152 | 59.8258 | 2764.9057 |  | 4647 | 16729200 | 48265200 | 79801200 | 111337200
2033-04-03 16:00 | 9906.03 | 3.2071 | 83.8301 | 59.8258 | 2903.1708 |  | 4648 | 16732800 | 48268800 | 79804800 | 111340800
2033-04-04 17:00 | 10134.6 | 3.1665 | 84.508 | 59.8258 | 2970.1581 |  | 4649 | 16736400 | 48272400 | 79808400 | 111344400
2033-04-05 18:00 | 9112.12 | 2.8572 | 84.5995 | 59.8258 | 2670.4988 |  | 4650 | 16740000 | 48276000 | 79812000 | 111348000
2033-04-06 19:00 | 8475.16 | 2.5994 | 84.9058 | 59.8258 | 2483.8242 |  | 4651 | 16743600 | 48279600 | 79815600 | 111351600
2033-04-07 20:00 | 6703.56 | 1.9069 | 86.0331 | 59.8258 | 1964.6195 |  | 4652 | 16747200 | 48283200 | 79819200 | 111355200
2033-04-08 21:00 | 5888.18 | 1.7676 | 84.9409 | 59.8258 | 1725.6552 |  | 4653 | 16750800 | 48286800 | 79822800 | 111358800
2033-04-09 22:00 | 4133.86 | 1.1998 | 85.2389 | 59.8258 | 1211.5148 |  | 4654 | 16754400 | 48290400 | 79826400 | 111362400
2033-04-10 23:00 | 3213.98 | 1 | 85.916 | 59.8258 | 941.9246 |  | 4655 | 16758000 | 48294000 | 79830000 | 111366000
2033-04-12 | 3193.46 | 1 | 88.0367 | 59.8258 | 935.9107 |  | 4656 | 16761600 | 48297600 | 79833600 | 111369600
2033-04-13 01:00 | 3183.6 | 1 | 89.4875 | 59.8258 | 933.0211 |  | 4657 | 16765200 | 48301200 | 79837200 | 111373200
2033-04-14 02:00 | 3132.39 | 1 | 90.0446 | 59.8258 | 918.0129 |  | 4658 | 16768800 | 48304800 | 79840800 | 111376800
2033-04-15 03:00 | 3178.64 | 1 | 92.3366 | 59.8258 | 931.5674 |  | 4659 | 16772400 | 48308400 | 79844400 | 111380400
2033-04-16 04:00 | 3168.92 | 1 | 93.5391 | 59.8258 | 928.7188 |  | 4660 | 16776000 | 48312000 | 79848000 | 111384000
2033-04-17 05:00 | 3204.8 | 1 | 92.4329 | 59.8258 | 939.2342 |  | 4661 | 16779600 | 48315600 | 79851600 | 111387600
2033-04-18 06:00 | 4409.61 | 1.3993 | 82.3893 | 59.8258 | 1292.3291 |  | 4662 | 16783200 | 48319200 | 79855200 | 111391200
2033-04-19 07:00 | 5539.61 | 1.9243 | 81.2348 | 59.8258 | 1623.4994 |  | 4663 | 16786800 | 48322800 | 79858800 | 111394800
2033-04-20 08:00 | 5150.35 | 1.5351 | 83.6036 | 59.8258 | 1509.4186 |  | 4664 | 16790400 | 48326400 | 79862400 | 111398400
2033-04-21 09:00 | 5992.83 | 1.9027 | 82.6831 | 59.8258 | 1756.3251 |  | 4665 | 16794000 | 48330000 | 79866000 | 111402000
2033-04-22 10:00 | 7168.35 | 2.3801 | 82.1855 | 59.8258 | 2100.836 |  | 4666 | 16797600 | 48333600 | 79869600 | 111405600
2033-04-23 11:00 | 9060.95 | 3.0973 | 82.0427 | 59.8258 | 2655.5023 |  | 4667 | 16801200 | 48337200 | 79873200 | 111409200
2033-04-24 12:00 | 10313.6 | 3.4677 | 82.6509 | 59.8258 | 3022.6178 |  | 4668 | 16804800 | 48340800 | 79876800 | 111412800
2033-04-25 13:00 | 11305.7 | 3.6267 | 83.6836 | 59.8258 | 3313.3736 |  | 4669 | 16808400 | 48344400 | 79880400 | 111416400
2033-04-26 14:00 | 12182.8 | 3.9243 | 83.9994 | 59.8258 | 3570.4262 |  | 4670 | 16812000 | 48348000 | 79884000 | 111420000
2033-04-27 15:00 | 12720.7 | 4.2445 | 83.8698 | 59.8258 | 3728.0692 |  | 4671 | 16815600 | 48351600 | 79887600 | 111423600
2033-04-28 16:00 | 15692.9 | 5.177 | 84.3346 | 59.8258 | 4599.135 |  | 4672 | 16819200 | 48355200 | 79891200 | 111427200
2033-04-29 17:00 | 15384 | 4.8809 | 85.5098 | 59.8258 | 4508.6053 |  | 4673 | 16822800 | 48358800 | 79894800 | 111430800
2033-04-30 18:00 | 14248.3 | 4.3517 | 86.4379 | 59.8258 | 4175.7645 |  | 4674 | 16826400 | 48362400 | 79898400 | 111434400
2033-05-01 19:00 | 12097.8 | 3.759 | 86.2945 | 59.8258 | 3545.5152 |  | 4675 | 16830000 | 48366000 | 79902000 | 111438000
2033-05-02 20:00 | 10568.7 | 3.2315 | 86.4332 | 59.8258 | 3097.3802 |  | 4676 | 16833600 | 48369600 | 79905600 | 111441600
2033-05-03 21:00 | 8962.07 | 2.8525 | 85.685 | 59.8258 | 2626.5234 |  | 4677 | 16837200 | 48373200 | 79909200 | 111445200
2033-05-04 22:00 | 8372.12 | 2.5183 | 86.2359 | 59.8258 | 2453.6262 |  | 4678 | 16840800 | 48376800 | 79912800 | 111448800
2033-05-05 23:00 | 5449.66 | 1.4933 | 87.5028 | 59.8258 | 1597.1377 |  | 4679 | 16844400 | 48380400 | 79916400 | 111452400
2033-05-07 | 4023.55 | 1.2691 | 84.7953 | 59.8258 | 1179.1861 |  | 4680 | 16848000 | 48384000 | 79920000 | 111456000
2033-05-08 01:00 | 3464.82 | 1.0361 | 85.1028 | 59.8258 | 1015.4385 |  | 4681 | 16851600 | 48387600 | 79923600 | 111459600
2033-05-09 02:00 | 3324.43 | 1 | 86.365 | 59.8258 | 974.2943 |  | 4682 | 16855200 | 48391200 | 79927200 | 111463200
2033-05-10 03:00 | 3277.34 | 1 | 87.1985 | 59.8258 | 960.4935 |  | 4683 | 16858800 | 48394800 | 79930800 | 111466800
2033-05-11 04:00 | 3025.59 | 1 | 87.2943 | 59.8258 | 886.7129 |  | 4684 | 16862400 | 48398400 | 79934400 | 111470400
2033-05-12 05:00 | 3219.55 | 1 | 90.9458 | 59.8258 | 943.557 |  | 4685 | 16866000 | 48402000 | 79938000 | 111474000
2033-05-13 06:00 | 5163.09 | 1.5844 | 83.412 | 59.8258 | 1513.1523 |  | 4686 | 16869600 | 48405600 | 79941600 | 111477600
2033-05-14 07:00 | 6757.81 | 2.3175 | 81.993 | 59.8258 | 1980.5186 |  | 4687 | 16873200 | 48409200 | 79945200 | 111481200
2033-05-15 08:00 | 7336.62 | 2.3119 | 83.4338 | 59.8258 | 2150.1511 |  | 4688 | 16876800 | 48412800 | 79948800 | 111484800
2033-05-16 09:00 | 8561.01 | 2.88 | 82.7006 | 59.8258 | 2508.9844 |  | 4689 | 16880400 | 48416400 | 79952400 | 111488400
2033-05-17 10:00 | 10434.1 | 3.5039 | 82.9912 | 59.8258 | 3057.9329 |  | 4690 | 16884000 | 48420000 | 79956000 | 111492000
2033-05-18 11:00 | 12232.8 | 4.0499 | 83.6298 | 59.8258 | 3585.0798 |  | 4691 | 16887600 | 48423600 | 79959600 | 111495600
2033-05-19 12:00 | 13596.5 | 4.3891 | 84.4875 | 59.8258 | 3984.7408 |  | 4692 | 16891200 | 48427200 | 79963200 | 111499200
2033-05-20 13:00 | 14456.6 | 4.5422 | 85.3657 | 59.8258 | 4236.8112 |  | 4693 | 16894800 | 48430800 | 79966800 | 111502800
2033-05-21 14:00 | 14639.4 | 4.8083 | 85.1851 | 59.8258 | 4290.3846 |  | 4694 | 16898400 | 48434400 | 79970400 | 111506400
2033-05-22 15:00 | 15607.4 | 5.0063 | 85.8586 | 59.8258 | 4574.0774 |  | 4695 | 16902000 | 48438000 | 79974000 | 111510000
2033-05-23 16:00 | 18346.5 | 5.7519 | 86.5485 | 59.8258 | 5376.8284 |  | 4696 | 16905600 | 48441600 | 79977600 | 111513600
2033-05-24 17:00 | 17434.3 | 5.3936 | 87.3939 | 59.8258 | 5109.489 |  | 4697 | 16909200 | 48445200 | 79981200 | 111517200
2033-05-25 18:00 | 16139.8 | 5.0621 | 87.4911 | 59.8258 | 4730.1085 |  | 4698 | 16912800 | 48448800 | 79984800 | 111520800
2033-05-26 19:00 | 14277.7 | 4.3578 | 87.9561 | 59.8258 | 4184.3808 |  | 4699 | 16916400 | 48452400 | 79988400 | 111524400
2033-05-27 20:00 | 12929.7 | 3.8757 | 88.1481 | 59.8258 | 3789.321 |  | 4700 | 16920000 | 48456000 | 79992000 | 111528000
2033-05-28 21:00 | 11608.7 | 3.525 | 87.8155 | 59.8258 | 3402.1741 |  | 4701 | 16923600 | 48459600 | 79995600 | 111531600
2033-05-29 22:00 | 10558.1 | 3.2418 | 87.4019 | 59.8258 | 3094.2737 |  | 4702 | 16927200 | 48463200 | 79999200 | 111535200
2033-05-30 23:00 | 8033.23 | 2.2954 | 88.2714 | 59.8258 | 2354.3073 |  | 4703 | 16930800 | 48466800 | 80002800 | 111538800
2033-06-01 | 7042.81 | 2.0947 | 87.1808 | 59.8258 | 2064.0439 |  | 4704 | 16934400 | 48470400 | 80006400 | 111542400
2033-06-02 01:00 | 6516.48 | 2.0029 | 86.3039 | 59.8258 | 1909.7918 |  | 4705 | 16938000 | 48474000 | 80010000 | 111546000
2033-06-03 02:00 | 5918.68 | 1.8683 | 85.6341 | 59.8258 | 1734.5939 |  | 4706 | 16941600 | 48477600 | 80013600 | 111549600
2033-06-04 03:00 | 5858.52 | 1.863 | 85.2465 | 59.8258 | 1716.9627 |  | 4707 | 16945200 | 48481200 | 80017200 | 111553200
2033-06-05 04:00 | 6118.9 | 1.8893 | 85.4314 | 59.8258 | 1793.2726 |  | 4708 | 16948800 | 48484800 | 80020800 | 111556800
2033-06-06 05:00 | 6789.27 | 2.2088 | 84.5547 | 59.8258 | 1989.7386 |  | 4709 | 16952400 | 48488400 | 80024400 | 111560400
2033-06-07 06:00 | 7620.74 | 2.5418 | 84.1875 | 59.8258 | 2233.4184 |  | 4710 | 16956000 | 48492000 | 80028000 | 111564000
2033-06-08 07:00 | 9149.62 | 3.0324 | 84.333 | 59.8258 | 2681.4889 |  | 4711 | 16959600 | 48495600 | 80031600 | 111567600
2033-06-09 08:00 | 10051 | 3.2396 | 84.9483 | 59.8258 | 2945.6573 |  | 4712 | 16963200 | 48499200 | 80035200 | 111571200
2033-06-10 09:00 | 12033.6 | 3.9231 | 85.0211 | 59.8258 | 3526.7 |  | 4713 | 16966800 | 48502800 | 80038800 | 111574800
2033-06-11 10:00 | 14316.5 | 4.4539 | 86.0812 | 59.8258 | 4195.752 |  | 4714 | 16970400 | 48506400 | 80042400 | 111578400
2033-06-12 11:00 | 14975.9 | 4.9343 | 85.8177 | 59.8258 | 4389.003 |  | 4715 | 16974000 | 48510000 | 80046000 | 111582000
2033-06-13 12:00 | 16735.2 | 5.2857 | 86.8406 | 59.8258 | 4904.603 |  | 4716 | 16977600 | 48513600 | 80049600 | 111585600
2033-06-14 13:00 | 16820.3 | 5.3726 | 87.1947 | 59.8258 | 4929.5433 |  | 4717 | 16981200 | 48517200 | 80053200 | 111589200
2033-06-15 14:00 | 18307.6 | 5.5228 | 88.4157 | 59.8258 | 5365.4279 |  | 4718 | 16984800 | 48520800 | 80056800 | 111592800
2033-06-16 15:00 | 18880.5 | 5.8172 | 88.5655 | 59.8258 | 5533.3283 |  | 4719 | 16988400 | 48524400 | 80060400 | 111596400
2033-06-17 16:00 | 15968.4 | 5.1254 | 88.3645 | 59.8258 | 4679.8761 |  | 4720 | 16992000 | 48528000 | 80064000 | 111600000
2033-06-18 17:00 | 14489.3 | 4.7016 | 88.1006 | 59.8258 | 4246.3947 |  | 4721 | 16995600 | 48531600 | 80067600 | 111603600
2033-06-19 18:00 | 12883 | 4.083 | 88.2337 | 59.8258 | 3775.6346 |  | 4722 | 16999200 | 48535200 | 80071200 | 111607200
2033-06-20 19:00 | 11821.6 | 3.5919 | 88.614 | 59.8258 | 3464.569 |  | 4723 | 17002800 | 48538800 | 80074800 | 111610800
2033-06-21 20:00 | 9191.72 | 2.8314 | 88.1467 | 59.8258 | 2693.8272 |  | 4724 | 17006400 | 48542400 | 80078400 | 111614400
2033-06-22 21:00 | 8301.14 | 2.5262 | 87.794 | 59.8258 | 2432.824 |  | 4725 | 17010000 | 48546000 | 80082000 | 111618000
2033-06-23 22:00 | 6384 | 1.8424 | 88.1981 | 59.8258 | 1870.9657 |  | 4726 | 17013600 | 48549600 | 80085600 | 111621600
2033-06-24 23:00 | 5491.5 | 1.6617 | 86.9788 | 59.8258 | 1609.3998 |  | 4727 | 17017200 | 48553200 | 80089200 | 111625200
2033-06-26 | 4962.85 | 1.4391 | 87.1952 | 59.8258 | 1454.4678 |  | 4728 | 17020800 | 48556800 | 80092800 | 111628800
2033-06-27 01:00 | 4253.41 | 1.3011 | 86.0072 | 59.8258 | 1246.5514 |  | 4729 | 17024400 | 48560400 | 80096400 | 111632400
2033-06-28 02:00 | 3850.44 | 1.2178 | 85.1621 | 59.8258 | 1128.4526 |  | 4730 | 17028000 | 48564000 | 80100000 | 111636000
2033-06-29 03:00 | 4106.04 | 1.2784 | 85.0487 | 59.8258 | 1203.3615 |  | 4731 | 17031600 | 48567600 | 80103600 | 111639600
2033-06-30 04:00 | 4213.79 | 1.3143 | 84.8381 | 59.8258 | 1234.9399 |  | 4732 | 17035200 | 48571200 | 80107200 | 111643200
2033-07-01 05:00 | 5039.82 | 1.6129 | 84.3256 | 59.8258 | 1477.0254 |  | 4733 | 17038800 | 48574800 | 80110800 | 111646800
2033-07-02 06:00 | 5451.27 | 1.7167 | 84.5337 | 59.8258 | 1597.6095 |  | 4734 | 17042400 | 48578400 | 80114400 | 111650400
2033-07-03 07:00 | 6431.82 | 2.149 | 83.6922 | 59.8258 | 1884.9804 |  | 4735 | 17046000 | 48582000 | 80118000 | 111654000
2033-07-04 08:00 | 7272.39 | 2.3514 | 84.258 | 59.8258 | 2131.3271 |  | 4736 | 17049600 | 48585600 | 80121600 | 111657600
2033-07-05 09:00 | 9172.81 | 3.0621 | 83.9476 | 59.8258 | 2688.2852 |  | 4737 | 17053200 | 48589200 | 80125200 | 111661200
2033-07-06 10:00 | 11097.7 | 3.6415 | 84.4968 | 59.8258 | 3252.4148 |  | 4738 | 17056800 | 48592800 | 80128800 | 111664800
2033-07-07 11:00 | 13126.8 | 4.2626 | 85.0586 | 59.8258 | 3847.0853 |  | 4739 | 17060400 | 48596400 | 80132400 | 111668400
2033-07-08 12:00 | 14239.6 | 4.6464 | 85.4955 | 59.8258 | 4173.2148 |  | 4740 | 17064000 | 48600000 | 80136000 | 111672000
2033-07-09 13:00 | 14867 | 4.8886 | 85.8481 | 59.8258 | 4357.0876 |  | 4741 | 17067600 | 48603600 | 80139600 | 111675600
2033-07-10 14:00 | 15816 | 5.0669 | 86.6003 | 59.8258 | 4635.212 |  | 4742 | 17071200 | 48607200 | 80143200 | 111679200
2033-07-11 15:00 | 17738.7 | 5.5215 | 87.3969 | 59.8258 | 5198.6998 |  | 4743 | 17074800 | 48610800 | 80146800 | 111682800
2033-07-12 16:00 | 17980.6 | 5.6423 | 87.8152 | 59.8258 | 5269.5937 |  | 4744 | 17078400 | 48614400 | 80150400 | 111686400
2033-07-13 17:00 | 18148.5 | 5.585 | 88.4875 | 59.8258 | 5318.8003 |  | 4745 | 17082000 | 48618000 | 80154000 | 111690000
2033-07-14 18:00 | 16642 | 5.1422 | 88.7494 | 59.8258 | 4877.2887 |  | 4746 | 17085600 | 48621600 | 80157600 | 111693600
2033-07-15 19:00 | 14201 | 4.4348 | 88.686 | 59.8258 | 4161.9023 |  | 4747 | 17089200 | 48625200 | 80161200 | 111697200
2033-07-16 20:00 | 11560.3 | 3.5145 | 88.9167 | 59.8258 | 3387.9895 |  | 4748 | 17092800 | 48628800 | 80164800 | 111700800
2033-07-17 21:00 | 9900.68 | 3.0501 | 88.3219 | 59.8258 | 2901.6029 |  | 4749 | 17096400 | 48632400 | 80168400 | 111704400
2033-07-18 22:00 | 7966.89 | 2.3519 | 88.5716 | 59.8258 | 2334.865 |  | 4750 | 17100000 | 48636000 | 80172000 | 111708000
2033-07-19 23:00 | 7508.78 | 2.2276 | 88.0005 | 59.8258 | 2200.6062 |  | 4751 | 17103600 | 48639600 | 80175600 | 111711600
2033-07-21 | 7220.96 | 2.1661 | 87.4686 | 59.8258 | 2116.2545 |  | 4752 | 17107200 | 48643200 | 80179200 | 111715200
2033-07-22 01:00 | 6014.38 | 1.9168 | 86.3241 | 59.8258 | 1762.6408 |  | 4753 | 17110800 | 48646800 | 80182800 | 111718800
2033-07-23 02:00 | 6003.52 | 1.6753 | 88.0277 | 59.8258 | 1759.458 |  | 4754 | 17114400 | 48650400 | 80186400 | 111722400
2033-07-24 03:00 | 5365.44 | 1.6971 | 85.8567 | 59.8258 | 1572.4552 |  | 4755 | 17118000 | 48654000 | 80190000 | 111726000
2033-07-25 04:00 | 5451.31 | 1.7056 | 85.7706 | 59.8258 | 1597.6213 |  | 4756 | 17121600 | 48657600 | 80193600 | 111729600
2033-07-26 05:00 | 6082.7 | 1.963 | 85.1235 | 59.8258 | 1782.6634 |  | 4757 | 17125200 | 48661200 | 80197200 | 111733200
2033-07-27 06:00 | 6238.92 | 2.0207 | 84.9945 | 59.8258 | 1828.447 |  | 4758 | 17128800 | 48664800 | 80200800 | 111736800
2033-07-28 07:00 | 7226.18 | 2.3825 | 84.6861 | 59.8258 | 2117.7843 |  | 4759 | 17132400 | 48668400 | 80204400 | 111740400
2033-07-29 08:00 | 8175.44 | 2.5292 | 85.6651 | 59.8258 | 2395.9849 |  | 4760 | 17136000 | 48672000 | 80208000 | 111744000
2033-07-30 09:00 | 9827.29 | 3.1698 | 85.207 | 59.8258 | 2880.0944 |  | 4761 | 17139600 | 48675600 | 80211600 | 111747600
2033-07-31 10:00 | 11880.6 | 3.8108 | 85.5683 | 59.8258 | 3481.8602 |  | 4762 | 17143200 | 48679200 | 80215200 | 111751200
2033-08-01 11:00 | 13104.7 | 4.2226 | 85.9149 | 59.8258 | 3840.6085 |  | 4763 | 17146800 | 48682800 | 80218800 | 111754800
2033-08-02 12:00 | 14391.7 | 4.5077 | 86.7132 | 59.8258 | 4217.7909 |  | 4764 | 17150400 | 48686400 | 80222400 | 111758400
2033-08-03 13:00 | 14975 | 4.7483 | 86.9504 | 59.8258 | 4388.7393 |  | 4765 | 17154000 | 48690000 | 80226000 | 111762000
2033-08-04 14:00 | 14703.8 | 4.9695 | 86.4111 | 59.8258 | 4309.2584 |  | 4766 | 17157600 | 48693600 | 80229600 | 111765600
2033-08-05 15:00 | 15596.7 | 5.2458 | 86.6636 | 59.8258 | 4570.9416 |  | 4767 | 17161200 | 48697200 | 80233200 | 111769200
2033-08-06 16:00 | 16364.6 | 5.2224 | 87.6534 | 59.8258 | 4795.9908 |  | 4768 | 17164800 | 48700800 | 80236800 | 111772800
2033-08-07 17:00 | 16538 | 5.2724 | 87.959 | 59.8258 | 4846.8094 |  | 4769 | 17168400 | 48704400 | 80240400 | 111776400
2033-08-08 18:00 | 14637.2 | 4.6083 | 88.3773 | 59.8258 | 4289.7399 |  | 4770 | 17172000 | 48708000 | 80244000 | 111780000
2033-08-09 19:00 | 13702.1 | 4.1107 | 89.0295 | 59.8258 | 4015.6891 |  | 4771 | 17175600 | 48711600 | 80247600 | 111783600
2033-08-10 20:00 | 10590.3 | 3.2568 | 88.5991 | 59.8258 | 3103.7106 |  | 4772 | 17179200 | 48715200 | 80251200 | 111787200
2033-08-11 21:00 | 9042.97 | 2.7737 | 88.2445 | 59.8258 | 2650.2329 |  | 4773 | 17182800 | 48718800 | 80254800 | 111790800
2033-08-12 22:00 | 6797.34 | 2.0104 | 88.3802 | 59.8258 | 1992.1037 |  | 4774 | 17186400 | 48722400 | 80258400 | 111794400
2033-08-13 23:00 | 5895.25 | 1.756 | 87.7286 | 59.8258 | 1727.7272 |  | 4775 | 17190000 | 48726000 | 80262000 | 111798000
2033-08-15 | 5450.96 | 1.6361 | 87.1614 | 59.8258 | 1597.5187 |  | 4776 | 17193600 | 48729600 | 80265600 | 111801600
2033-08-16 01:00 | 5205.86 | 1.5203 | 87.2248 | 59.8258 | 1525.687 |  | 4777 | 17197200 | 48733200 | 80269200 | 111805200
2033-08-17 02:00 | 4672.41 | 1.444 | 86.1022 | 59.8258 | 1369.3482 |  | 4778 | 17200800 | 48736800 | 80272800 | 111808800
2033-08-18 03:00 | 4690.02 | 1.4377 | 85.9469 | 59.8258 | 1374.5092 |  | 4779 | 17204400 | 48740400 | 80276400 | 111812400
2033-08-19 04:00 | 4866.61 | 1.5478 | 85.2121 | 59.8258 | 1426.2626 |  | 4780 | 17208000 | 48744000 | 80280000 | 111816000
2033-08-20 05:00 | 5512.67 | 1.8734 | 84.1478 | 59.8258 | 1615.6041 |  | 4781 | 17211600 | 48747600 | 80283600 | 111819600
2033-08-21 06:00 | 6609.26 | 2.1711 | 84.5701 | 59.8258 | 1936.9829 |  | 4782 | 17215200 | 48751200 | 80287200 | 111823200
2033-08-22 07:00 | 7848.5 | 2.5078 | 85.0271 | 59.8258 | 2300.1683 |  | 4783 | 17218800 | 48754800 | 80290800 | 111826800
2033-08-23 08:00 | 8028.95 | 2.5606 | 85.2495 | 59.8258 | 2353.053 |  | 4784 | 17222400 | 48758400 | 80294400 | 111830400
2033-08-24 09:00 | 9835.95 | 3.1625 | 85.2376 | 59.8258 | 2882.6324 |  | 4785 | 17226000 | 48762000 | 80298000 | 111834000
2033-08-25 10:00 | 11237.5 | 3.755 | 85.0023 | 59.8258 | 3293.3861 |  | 4786 | 17229600 | 48765600 | 80301600 | 111837600
2033-08-26 11:00 | 12408.6 | 3.9836 | 85.9242 | 59.8258 | 3636.6017 |  | 4787 | 17233200 | 48769200 | 80305200 | 111841200
2033-08-27 12:00 | 13063.4 | 4.2823 | 85.9793 | 59.8258 | 3828.5046 |  | 4788 | 17236800 | 48772800 | 80308800 | 111844800
2033-08-28 13:00 | 13470.6 | 4.3382 | 86.5228 | 59.8258 | 3947.8432 |  | 4789 | 17240400 | 48776400 | 80312400 | 111848400
2033-08-29 14:00 | 13787.4 | 4.4715 | 86.6953 | 59.8258 | 4040.6881 |  | 4790 | 17244000 | 48780000 | 80316000 | 111852000
2033-08-30 15:00 | 15480 | 5.0551 | 86.8074 | 59.8258 | 4536.7402 |  | 4791 | 17247600 | 48783600 | 80319600 | 111855600
2033-08-31 16:00 | 16200.2 | 5.1801 | 87.4731 | 59.8258 | 4747.8099 |  | 4792 | 17251200 | 48787200 | 80323200 | 111859200
2033-09-01 17:00 | 16185.4 | 5.1681 | 87.8218 | 59.8258 | 4743.4725 |  | 4793 | 17254800 | 48790800 | 80326800 | 111862800
2033-09-02 18:00 | 14780.7 | 4.6893 | 88.1399 | 59.8258 | 4331.7956 |  | 4794 | 17258400 | 48794400 | 80330400 | 111866400
2033-09-03 19:00 | 12406.1 | 3.9218 | 88.1995 | 59.8258 | 3635.869 |  | 4795 | 17262000 | 48798000 | 80334000 | 111870000
2033-09-04 20:00 | 9622.92 | 2.942 | 88.4761 | 59.8258 | 2820.1995 |  | 4796 | 17265600 | 48801600 | 80337600 | 111873600
2033-09-05 21:00 | 8352.56 | 2.519 | 88.22 | 59.8258 | 2447.8937 |  | 4797 | 17269200 | 48805200 | 80341200 | 111877200
2033-09-06 22:00 | 6307.67 | 1.8554 | 88.201 | 59.8258 | 1848.5956 |  | 4798 | 17272800 | 48808800 | 80344800 | 111880800
2033-09-07 23:00 | 5395.13 | 1.5765 | 87.7834 | 59.8258 | 1581.1565 |  | 4799 | 17276400 | 48812400 | 80348400 | 111884400
2033-09-09 | 5039.44 | 1.4978 | 87.0642 | 59.8258 | 1476.9141 |  | 4800 | 17280000 | 48816000 | 80352000 | 111888000
2033-09-10 01:00 | 4375.31 | 1.3322 | 86.3726 | 59.8258 | 1282.2768 |  | 4801 | 17283600 | 48819600 | 80355600 | 111891600
2033-09-11 02:00 | 4107.11 | 1.2798 | 85.7278 | 59.8258 | 1203.6751 |  | 4802 | 17287200 | 48823200 | 80359200 | 111895200
2033-09-12 03:00 | 4043.57 | 1.2878 | 85.1334 | 59.8258 | 1185.0534 |  | 4803 | 17290800 | 48826800 | 80362800 | 111898800
2033-09-13 04:00 | 4289.2 | 1.3581 | 85.0036 | 59.8258 | 1257.0404 |  | 4804 | 17294400 | 48830400 | 80366400 | 111902400
2033-09-14 05:00 | 5283.77 | 1.6601 | 84.9587 | 59.8258 | 1548.5201 |  | 4805 | 17298000 | 48834000 | 80370000 | 111906000
2033-09-15 06:00 | 6095.62 | 1.9959 | 84.3526 | 59.8258 | 1786.4499 |  | 4806 | 17301600 | 48837600 | 80373600 | 111909600
2033-09-16 07:00 | 7614.47 | 2.4327 | 84.7546 | 59.8258 | 2231.5809 |  | 4807 | 17305200 | 48841200 | 80377200 | 111913200
2033-09-17 08:00 | 7999.67 | 2.4426 | 85.6349 | 59.8258 | 2344.4718 |  | 4808 | 17308800 | 48844800 | 80380800 | 111916800
2033-09-18 09:00 | 9266.42 | 2.9537 | 85.155 | 59.8258 | 2715.7196 |  | 4809 | 17312400 | 48848400 | 80384400 | 111920400
2033-09-19 10:00 | 10736.5 | 3.552 | 84.881 | 59.8258 | 3146.5575 |  | 4810 | 17316000 | 48852000 | 80388000 | 111924000
2033-09-20 11:00 | 11973.4 | 3.9471 | 85.2699 | 59.8258 | 3509.0571 |  | 4811 | 17319600 | 48855600 | 80391600 | 111927600
2033-09-21 12:00 | 12466 | 3.9753 | 86.0964 | 59.8258 | 3653.424 |  | 4812 | 17323200 | 48859200 | 80395200 | 111931200
2033-09-22 13:00 | 11680.2 | 3.7427 | 86.3063 | 59.8258 | 3423.1287 |  | 4813 | 17326800 | 48862800 | 80398800 | 111934800
2033-09-23 14:00 | 12735.7 | 4.0026 | 86.6683 | 59.8258 | 3732.4652 |  | 4814 | 17330400 | 48866400 | 80402400 | 111938400
2033-09-24 15:00 | 14432.4 | 4.697 | 86.3783 | 59.8258 | 4229.7189 |  | 4815 | 17334000 | 48870000 | 80406000 | 111942000
2033-09-25 16:00 | 15726 | 5.0391 | 86.9689 | 59.8258 | 4608.8356 |  | 4816 | 17337600 | 48873600 | 80409600 | 111945600
2033-09-26 17:00 | 15388.9 | 5.0603 | 86.9895 | 59.8258 | 4510.0414 |  | 4817 | 17341200 | 48877200 | 80413200 | 111949200
2033-09-27 18:00 | 13802.4 | 4.4097 | 87.6063 | 59.8258 | 4045.0841 |  | 4818 | 17344800 | 48880800 | 80416800 | 111952800
2033-09-28 19:00 | 11991.3 | 3.7414 | 87.9366 | 59.8258 | 3514.3031 |  | 4819 | 17348400 | 48884400 | 80420400 | 111956400
2033-09-29 20:00 | 9509.01 | 2.9051 | 88.0963 | 59.8258 | 2786.8157 |  | 4820 | 17352000 | 48888000 | 80424000 | 111960000
2033-09-30 21:00 | 8220.47 | 2.5181 | 87.6784 | 59.8258 | 2409.1819 |  | 4821 | 17355600 | 48891600 | 80427600 | 111963600
2033-10-01 22:00 | 6423.71 | 1.899 | 87.8462 | 59.8258 | 1882.6036 |  | 4822 | 17359200 | 48895200 | 80431200 | 111967200
2033-10-02 23:00 | 5563.42 | 1.6954 | 86.9237 | 59.8258 | 1630.4775 |  | 4823 | 17362800 | 48898800 | 80434800 | 111970800
2033-10-04 | 5155.15 | 1.5752 | 86.4884 | 59.8258 | 1510.8253 |  | 4824 | 17366400 | 48902400 | 80438400 | 111974400
2033-10-05 01:00 | 4921.36 | 1.5242 | 86.0006 | 59.8258 | 1442.3082 |  | 4825 | 17370000 | 48906000 | 80442000 | 111978000
2033-10-06 02:00 | 4564.28 | 1.4033 | 85.893 | 59.8258 | 1337.6584 |  | 4826 | 17373600 | 48909600 | 80445600 | 111981600
2033-10-07 03:00 | 4134.67 | 1.2086 | 86.4331 | 59.8258 | 1211.7522 |  | 4827 | 17377200 | 48913200 | 80449200 | 111985200
2033-10-08 04:00 | 3689.67 | 1.108 | 85.7822 | 59.8258 | 1081.3355 |  | 4828 | 17380800 | 48916800 | 80452800 | 111988800
2033-10-09 05:00 | 3487.22 | 1.0719 | 85.1865 | 59.8258 | 1022.0033 |  | 4829 | 17384400 | 48920400 | 80456400 | 111992400
2033-10-10 06:00 | 5224.07 | 1.6706 | 84.3855 | 59.8258 | 1531.0238 |  | 4830 | 17388000 | 48924000 | 80460000 | 111996000
2033-10-11 07:00 | 6181.22 | 2.0689 | 83.8056 | 59.8258 | 1811.5368 |  | 4831 | 17391600 | 48927600 | 80463600 | 111999600
2033-10-12 08:00 | 5505.42 | 1.6373 | 85.6548 | 59.8258 | 1613.4793 |  | 4832 | 17395200 | 48931200 | 80467200 | 112003200
2033-10-13 09:00 | 5663.13 | 1.8079 | 84.5324 | 59.8258 | 1659.6996 |  | 4833 | 17398800 | 48934800 | 80470800 | 112006800
2033-10-14 10:00 | 5102.67 | 1.6348 | 84.4611 | 59.8258 | 1495.445 |  | 4834 | 17402400 | 48938400 | 80474400 | 112010400
2033-10-15 11:00 | 5229.85 | 1.6887 | 84.2617 | 59.8258 | 1532.7177 |  | 4835 | 17406000 | 48942000 | 80478000 | 112014000
2033-10-16 12:00 | 5494.03 | 1.712 | 84.6874 | 59.8258 | 1610.1413 |  | 4836 | 17409600 | 48945600 | 80481600 | 112017600
2033-10-17 13:00 | 5366.51 | 1.7072 | 84.3327 | 59.8258 | 1572.7688 |  | 4837 | 17413200 | 48949200 | 80485200 | 112021200
2033-10-18 14:00 | 5544.44 | 1.821 | 83.7995 | 59.8258 | 1624.915 |  | 4838 | 17416800 | 48952800 | 80488800 | 112024800
2033-10-19 15:00 | 5766.79 | 1.9326 | 83.4448 | 59.8258 | 1690.0793 |  | 4839 | 17420400 | 48956400 | 80492400 | 112028400
2033-10-20 16:00 | 9043.97 | 3.1648 | 82.8077 | 59.8258 | 2650.526 |  | 4840 | 17424000 | 48960000 | 80496000 | 112032000
2033-10-21 17:00 | 8876.08 | 2.8079 | 84.5808 | 59.8258 | 2601.3223 |  | 4841 | 17427600 | 48963600 | 80499600 | 112035600
2033-10-22 18:00 | 8082.61 | 2.5133 | 84.9916 | 59.8258 | 2368.7792 |  | 4842 | 17431200 | 48967200 | 80503200 | 112039200
2033-10-23 19:00 | 6997.55 | 2.1551 | 85.0995 | 59.8258 | 2050.7795 |  | 4843 | 17434800 | 48970800 | 80506800 | 112042800
2033-10-24 20:00 | 6065.75 | 1.8465 | 85.1743 | 59.8258 | 1777.6958 |  | 4844 | 17438400 | 48974400 | 80510400 | 112046400
2033-10-25 21:00 | 5358.78 | 1.625 | 85.1017 | 59.8258 | 1570.5034 |  | 4845 | 17442000 | 48978000 | 80514000 | 112050000
2033-10-26 22:00 | 4905.99 | 1.5216 | 84.5808 | 59.8258 | 1437.8037 |  | 4846 | 17445600 | 48981600 | 80517600 | 112053600
2033-10-27 23:00 | 3123.95 | 1 | 69.4195 | 59.8258 | 915.5394 |  | 4847 | 17449200 | 48985200 | 80521200 | 112057200
2033-10-29 | 3070.96 | 1 | 69.0904 | 59.8258 | 900.0095 |  | 4848 | 17452800 | 48988800 | 80524800 | 112060800
2033-10-30 01:00 | 2597.78 | 1 | 68.934 | 59.8258 | 761.3342 |  | 4849 | 17456400 | 48992400 | 80528400 | 112064400
2033-10-31 02:00 | 3206 | 1 | 68.7014 | 59.8258 | 939.5859 |  | 4850 | 17460000 | 48996000 | 80532000 | 112068000
2033-11-01 03:00 | 3179.89 | 1 | 68.6553 | 59.8258 | 931.9338 |  | 4851 | 17463600 | 48999600 | 80535600 | 112071600
2033-11-02 04:00 | 280.377 | 1 | 68.8213 | 59.8258 | 82.1704 |  | 4852 | 17467200 | 49003200 | 80539200 | 112075200
2033-11-03 05:00 | 1434.23 | 1 | 68.2454 | 59.8258 | 420.3313 |  | 4853 | 17470800 | 49006800 | 80542800 | 112078800
2033-11-04 06:00 | 1740.12 | 1 | 76.5752 | 59.8258 | 509.9788 |  | 4854 | 17474400 | 49010400 | 80546400 | 112082400
2033-11-05 07:00 | 3195.87 | 1.2002 | 80.3255 | 59.8258 | 936.617 |  | 4855 | 17478000 | 49014000 | 80550000 | 112086000
2033-11-06 08:00 | 2786.01 | 1 | 84.3222 | 59.8258 | 816.4989 |  | 4856 | 17481600 | 49017600 | 80553600 | 112089600
2033-11-07 09:00 | 3963.29 | 1.2992 | 82.0792 | 59.8258 | 1161.5256 |  | 4857 | 17485200 | 49021200 | 80557200 | 112093200
2033-11-08 10:00 | 5704.71 | 1.9504 | 81.627 | 59.8258 | 1671.8855 |  | 4858 | 17488800 | 49024800 | 80560800 | 112096800
2033-11-09 11:00 | 6791.25 | 2.3204 | 81.929 | 59.8258 | 1990.3189 |  | 4859 | 17492400 | 49028400 | 80564400 | 112100400
2033-11-10 12:00 | 7955.49 | 2.656 | 82.5299 | 59.8258 | 2331.524 |  | 4860 | 17496000 | 49032000 | 80568000 | 112104000
2033-11-11 13:00 | 8921.85 | 2.9115 | 83.1451 | 59.8258 | 2614.7361 |  | 4861 | 17499600 | 49035600 | 80571600 | 112107600
2033-11-12 14:00 | 10146.9 | 3.3164 | 83.4484 | 59.8258 | 2973.7628 |  | 4862 | 17503200 | 49039200 | 80575200 | 112111200
2033-11-13 15:00 | 11200 | 3.6119 | 84.0006 | 59.8258 | 3282.396 |  | 4863 | 17506800 | 49042800 | 80578800 | 112114800
2033-11-14 16:00 | 13604.5 | 4.5626 | 83.8219 | 59.8258 | 3987.0854 |  | 4864 | 17510400 | 49046400 | 80582400 | 112118400
2033-11-15 17:00 | 12888.1 | 4.0684 | 85.2445 | 59.8258 | 3777.1293 |  | 4865 | 17514000 | 49050000 | 80586000 | 112122000
2033-11-16 18:00 | 11410 | 3.5642 | 85.6833 | 59.8258 | 3343.9409 |  | 4866 | 17517600 | 49053600 | 80589600 | 112125600
2033-11-17 19:00 | 9705.14 | 3.0645 | 85.5477 | 59.8258 | 2844.2958 |  | 4867 | 17521200 | 49057200 | 80593200 | 112129200
2033-11-18 20:00 | 8889.67 | 2.6437 | 86.3308 | 59.8258 | 2605.3051 |  | 4868 | 17524800 | 49060800 | 80596800 | 112132800
2033-11-19 21:00 | 8009.09 | 2.4017 | 86.1015 | 59.8258 | 2347.2326 |  | 4869 | 17528400 | 49064400 | 80600400 | 112136400
2033-11-20 22:00 | 7475.7 | 2.2564 | 85.8238 | 59.8258 | 2190.9114 |  | 4870 | 17532000 | 49068000 | 80604000 | 112140000
2033-11-21 23:00 | 4622.12 | 1.2744 | 87.1149 | 59.8258 | 1354.6097 |  | 4871 | 17535600 | 49071600 | 80607600 | 112143600
2033-11-23 | 3613.96 | 1.1088 | 84.9768 | 59.8258 | 1059.1471 |  | 4872 | 17539200 | 49075200 | 80611200 | 112147200
2033-11-24 01:00 | 3258.07 | 1 | 86.3282 | 59.8258 | 954.8461 |  | 4873 | 17542800 | 49078800 | 80614800 | 112150800
2033-11-25 02:00 | 3197.83 | 1 | 88.4644 | 59.8258 | 937.1915 |  | 4874 | 17546400 | 49082400 | 80618400 | 112154400
2033-11-26 03:00 | 3124.67 | 1 | 87.423 | 59.8258 | 915.7504 |  | 4875 | 17550000 | 49086000 | 80622000 | 112158000
2033-11-27 04:00 | 3187.86 | 1 | 88.7422 | 59.8258 | 934.2695 |  | 4876 | 17553600 | 49089600 | 80625600 | 112161600
2033-11-28 05:00 | 3265.68 | 1.0459 | 83.12 | 59.8258 | 957.0763 |  | 4877 | 17557200 | 49093200 | 80629200 | 112165200
2033-11-29 06:00 | 3740.65 | 1.1852 | 83.1907 | 59.8258 | 1096.2763 |  | 4878 | 17560800 | 49096800 | 80632800 | 112168800
2033-11-30 07:00 | 4864.83 | 1.5455 | 83.1249 | 59.8258 | 1425.7409 |  | 4879 | 17564400 | 49100400 | 80636400 | 112172400
2033-12-01 08:00 | 5203.49 | 1.6635 | 83.1505 | 59.8258 | 1524.9924 |  | 4880 | 17568000 | 49104000 | 80640000 | 112176000
2033-12-02 09:00 | 6737.47 | 2.3243 | 82.1779 | 59.8258 | 1974.5575 |  | 4881 | 17571600 | 49107600 | 80643600 | 112179600
2033-12-03 10:00 | 8238.33 | 2.775 | 82.7196 | 59.8258 | 2414.4162 |  | 4882 | 17575200 | 49111200 | 80647200 | 112183200
2033-12-04 11:00 | 9499.87 | 3.1385 | 83.3309 | 59.8258 | 2784.1371 |  | 4883 | 17578800 | 49114800 | 80650800 | 112186800
2033-12-05 12:00 | 10436.4 | 3.3409 | 84.1473 | 59.8258 | 3058.6069 |  | 4884 | 17582400 | 49118400 | 80654400 | 112190400
2033-12-06 13:00 | 11116.7 | 3.6046 | 84.3155 | 59.8258 | 3257.9832 |  | 4885 | 17586000 | 49122000 | 80658000 | 112194000
2033-12-07 14:00 | 12333.9 | 3.9852 | 84.6955 | 59.8258 | 3614.7093 |  | 4886 | 17589600 | 49125600 | 80661600 | 112197600
2033-12-08 15:00 | 13807.2 | 4.3614 | 85.3983 | 59.8258 | 4046.4909 |  | 4887 | 17593200 | 49129200 | 80665200 | 112201200
2033-12-09 16:00 | 14357.9 | 4.6182 | 85.569 | 59.8258 | 4207.8851 |  | 4888 | 17596800 | 49132800 | 80668800 | 112204800
2033-12-10 17:00 | 14113.8 | 4.55 | 85.8975 | 59.8258 | 4136.3465 |  | 4889 | 17600400 | 49136400 | 80672400 | 112208400
2033-12-11 18:00 | 12711.8 | 3.9602 | 86.6288 | 59.8258 | 3725.4608 |  | 4890 | 17604000 | 49140000 | 80676000 | 112212000
2033-12-12 19:00 | 10838.6 | 3.3243 | 86.8928 | 59.8258 | 3176.4801 |  | 4891 | 17607600 | 49143600 | 80679600 | 112215600
2033-12-13 20:00 | 8093.17 | 2.422 | 87.1147 | 59.8258 | 2371.874 |  | 4892 | 17611200 | 49147200 | 80683200 | 112219200
2033-12-14 21:00 | 6810.38 | 1.9968 | 87.0135 | 59.8258 | 1995.9254 |  | 4893 | 17614800 | 49150800 | 80686800 | 112222800
2033-12-15 22:00 | 4457.86 | 1.248 | 87.363 | 59.8258 | 1306.4698 |  | 4894 | 17618400 | 49154400 | 80690400 | 112226400
2033-12-16 23:00 | 3441.77 | 1.0575 | 85.3813 | 59.8258 | 1008.6832 |  | 4895 | 17622000 | 49158000 | 80694000 | 112230000
2033-12-18 | 3210.11 | 1 | 88.9593 | 59.8258 | 940.7904 |  | 4896 | 17625600 | 49161600 | 80697600 | 112233600
2033-12-19 01:00 | 3139.87 | 1 | 93.9305 | 59.8258 | 920.2051 |  | 4897 | 17629200 | 49165200 | 80701200 | 112237200
2033-12-20 02:00 | 3072.87 | 1 | 69.2204 | 59.8258 | 900.5693 |  | 4898 | 17632800 | 49168800 | 80704800 | 112240800
2033-12-21 03:00 | 3157.42 | 1 | 69.0027 | 59.8258 | 925.3485 |  | 4899 | 17636400 | 49172400 | 80708400 | 112244400
2033-12-22 04:00 | 3154.27 | 1 | 68.8565 | 59.8258 | 924.4253 |  | 4900 | 17640000 | 49176000 | 80712000 | 112248000
2033-12-23 05:00 | 3117.84 | 1 | 87.3408 | 59.8258 | 913.7487 |  | 4901 | 17643600 | 49179600 | 80715600 | 112251600
2033-12-24 06:00 | 3377.58 | 1.0048 | 84.2283 | 59.8258 | 989.871 |  | 4902 | 17647200 | 49183200 | 80719200 | 112255200
2033-12-25 07:00 | 4921.52 | 1.4858 | 83.9275 | 59.8258 | 1442.3551 |  | 4903 | 17650800 | 49186800 | 80722800 | 112258800
2033-12-26 08:00 | 5643.53 | 1.8572 | 82.8281 | 59.8258 | 1653.9554 |  | 4904 | 17654400 | 49190400 | 80726400 | 112262400
2033-12-27 09:00 | 7296.63 | 2.527 | 82.2831 | 59.8258 | 2138.4312 |  | 4905 | 17658000 | 49194000 | 80730000 | 112266000
2033-12-28 10:00 | 9315.02 | 3.2127 | 82.6218 | 59.8258 | 2729.9629 |  | 4906 | 17661600 | 49197600 | 80733600 | 112269600
2033-12-29 11:00 | 10605.2 | 3.549 | 83.4689 | 59.8258 | 3108.0773 |  | 4907 | 17665200 | 49201200 | 80737200 | 112273200
2033-12-30 12:00 | 10971.9 | 3.6153 | 84.1177 | 59.8258 | 3215.5465 |  | 4908 | 17668800 | 49204800 | 80740800 | 112276800
2033-12-31 13:00 | 11018.7 | 3.645 | 84.3682 | 59.8258 | 3229.2622 |  | 4909 | 17672400 | 49208400 | 80744400 | 112280400
2034-01-01 14:00 | 11706.3 | 3.8002 | 84.8453 | 59.8258 | 3430.7779 |  | 4910 | 17676000 | 49212000 | 80748000 | 112284000
2034-01-02 15:00 | 13701.9 | 4.4028 | 85.2224 | 59.8258 | 4015.6305 |  | 4911 | 17679600 | 49215600 | 80751600 | 112287600
2034-01-03 16:00 | 14643.4 | 4.6094 | 85.9314 | 59.8258 | 4291.5569 |  | 4912 | 17683200 | 49219200 | 80755200 | 112291200
2034-01-04 17:00 | 14380.7 | 4.5936 | 86.1067 | 59.8258 | 4214.5671 |  | 4913 | 17686800 | 49222800 | 80758800 | 112294800
2034-01-05 18:00 | 12757 | 4.0388 | 86.4758 | 59.8258 | 3738.7076 |  | 4914 | 17690400 | 49226400 | 80762400 | 112298400
2034-01-06 19:00 | 10979.1 | 3.4021 | 86.7921 | 59.8258 | 3217.6566 |  | 4915 | 17694000 | 49230000 | 80766000 | 112302000
2034-01-07 20:00 | 8134.86 | 2.4325 | 87.1939 | 59.8258 | 2384.0921 |  | 4916 | 17697600 | 49233600 | 80769600 | 112305600
2034-01-08 21:00 | 6745.31 | 1.9986 | 86.9108 | 59.8258 | 1976.8552 |  | 4917 | 17701200 | 49237200 | 80773200 | 112309200
2034-01-09 22:00 | 4328.92 | 1.2417 | 87.0093 | 59.8258 | 1268.6812 |  | 4918 | 17704800 | 49240800 | 80776800 | 112312800
2034-01-10 23:00 | 3295.18 | 1 | 86.0235 | 59.8258 | 965.7219 |  | 4919 | 17708400 | 49244400 | 80780400 | 112316400
2034-01-12 | 3162.18 | 1 | 91.1017 | 59.8258 | 926.7435 |  | 4920 | 17712000 | 49248000 | 80784000 | 112320000
2034-01-13 01:00 | 3231.03 | 1 | 69.435 | 59.8258 | 946.9214 |  | 4921 | 17715600 | 49251600 | 80787600 | 112323600
2034-01-14 02:00 | 3056.39 | 1 | 69.252 | 59.8258 | 895.7395 |  | 4922 | 17719200 | 49255200 | 80791200 | 112327200
2034-01-15 03:00 | 3145.05 | 1 | 69.0229 | 59.8258 | 921.7232 |  | 4923 | 17722800 | 49258800 | 80794800 | 112330800
2034-01-16 04:00 | 3158.27 | 1 | 68.8655 | 59.8258 | 925.5976 |  | 4924 | 17726400 | 49262400 | 80798400 | 112334400
2034-01-17 05:00 | 3148.07 | 1 | 68.739 | 59.8258 | 922.6082 |  | 4925 | 17730000 | 49266000 | 80802000 | 112338000
2034-01-18 06:00 | 3307.03 | 1 | 86.4292 | 59.8258 | 969.1948 |  | 4926 | 17733600 | 49269600 | 80805600 | 112341600
2034-01-19 07:00 | 3769.64 | 1.1071 | 84.349 | 59.8258 | 1104.7724 |  | 4927 | 17737200 | 49273200 | 80809200 | 112345200
2034-01-20 08:00 | 4346.48 | 1.3738 | 83.2437 | 59.8258 | 1273.8275 |  | 4928 | 17740800 | 49276800 | 80812800 | 112348800
2034-01-21 09:00 | 6747.99 | 2.2368 | 82.6013 | 59.8258 | 1977.6406 |  | 4929 | 17744400 | 49280400 | 80816400 | 112352400
2034-01-22 10:00 | 8248.07 | 2.8755 | 82.2454 | 59.8258 | 2417.2707 |  | 4930 | 17748000 | 49284000 | 80820000 | 112356000
2034-01-23 11:00 | 9817.62 | 3.2694 | 83.2284 | 59.8258 | 2877.2604 |  | 4931 | 17751600 | 49287600 | 80823600 | 112359600
2034-01-24 12:00 | 10512.2 | 3.4688 | 83.7631 | 59.8258 | 3080.8217 |  | 4932 | 17755200 | 49291200 | 80827200 | 112363200
2034-01-25 13:00 | 11171.9 | 3.6292 | 84.3309 | 59.8258 | 3274.1607 |  | 4933 | 17758800 | 49294800 | 80830800 | 112366800
2034-01-26 14:00 | 12338.3 | 3.9266 | 84.9465 | 59.8258 | 3615.9988 |  | 4934 | 17762400 | 49298400 | 80834400 | 112370400
2034-01-27 15:00 | 13530.5 | 4.3052 | 85.2973 | 59.8258 | 3965.3981 |  | 4935 | 17766000 | 49302000 | 80838000 | 112374000
2034-01-28 16:00 | 13191.3 | 4.1373 | 85.8879 | 59.8258 | 3865.9884 |  | 4936 | 17769600 | 49305600 | 80841600 | 112377600
2034-01-29 17:00 | 13558.3 | 4.271 | 86.0167 | 59.8258 | 3973.5455 |  | 4937 | 17773200 | 49309200 | 80845200 | 112381200
2034-01-30 18:00 | 12012.9 | 3.7151 | 86.5153 | 59.8258 | 3520.6335 |  | 4938 | 17776800 | 49312800 | 80848800 | 112384800
2034-01-31 19:00 | 10283.1 | 3.1889 | 86.4835 | 59.8258 | 3013.6791 |  | 4939 | 17780400 | 49316400 | 80852400 | 112388400
2034-02-01 20:00 | 8057.93 | 2.4433 | 86.6636 | 59.8258 | 2361.5462 |  | 4940 | 17784000 | 49320000 | 80856000 | 112392000
2034-02-02 21:00 | 6982.22 | 2.0424 | 86.8619 | 59.8258 | 2046.2867 |  | 4941 | 17787600 | 49323600 | 80859600 | 112395600
2034-02-03 22:00 | 4697.84 | 1.3653 | 86.6693 | 59.8258 | 1376.801 |  | 4942 | 17791200 | 49327200 | 80863200 | 112399200
2034-02-04 23:00 | 3707.21 | 1.1351 | 85.3815 | 59.8258 | 1086.476 |  | 4943 | 17794800 | 49330800 | 80866800 | 112402800
2034-02-06 | 3156.47 | 1 | 87.3253 | 59.8258 | 925.07 |  | 4944 | 17798400 | 49334400 | 80870400 | 112406400
2034-02-07 01:00 | 3206.46 | 1 | 93.9309 | 59.8258 | 939.7207 |  | 4945 | 17802000 | 49338000 | 80874000 | 112410000
2034-02-08 02:00 | 3202.57 | 1 | 69.1803 | 59.8258 | 938.5806 |  | 4946 | 17805600 | 49341600 | 80877600 | 112413600
2034-02-09 03:00 | 3129.49 | 1 | 94.7214 | 59.8258 | 917.163 |  | 4947 | 17809200 | 49345200 | 80881200 | 112417200
2034-02-10 04:00 | 3153.56 | 1 | 92.2365 | 59.8258 | 924.2172 |  | 4948 | 17812800 | 49348800 | 80884800 | 112420800
2034-02-11 05:00 | 3201.54 | 1 | 85.1616 | 59.8258 | 938.2788 |  | 4949 | 17816400 | 49352400 | 80888400 | 112424400
2034-02-12 06:00 | 4103.01 | 1.2656 | 83.6896 | 59.8258 | 1202.4735 |  | 4950 | 17820000 | 49356000 | 80892000 | 112428000
2034-02-13 07:00 | 5582.16 | 1.8239 | 82.8888 | 59.8258 | 1635.9696 |  | 4951 | 17823600 | 49359600 | 80895600 | 112431600
2034-02-14 08:00 | 6228.78 | 2.0282 | 83.1373 | 59.8258 | 1825.4752 |  | 4952 | 17827200 | 49363200 | 80899200 | 112435200
2034-02-15 09:00 | 8034.43 | 2.651 | 83.1103 | 59.8258 | 2354.659 |  | 4953 | 17830800 | 49366800 | 80902800 | 112438800
2034-02-16 10:00 | 9728.84 | 3.2663 | 83.1965 | 59.8258 | 2851.2415 |  | 4954 | 17834400 | 49370400 | 80906400 | 112442400
2034-02-17 11:00 | 11163.6 | 3.7662 | 83.5567 | 59.8258 | 3271.7282 |  | 4955 | 17838000 | 49374000 | 80910000 | 112446000
2034-02-18 12:00 | 12593 | 3.947 | 85.0321 | 59.8258 | 3690.644 |  | 4956 | 17841600 | 49377600 | 80913600 | 112449600
2034-02-19 13:00 | 12939 | 4.1089 | 85.3017 | 59.8258 | 3792.0466 |  | 4957 | 17845200 | 49381200 | 80917200 | 112453200
2034-02-20 14:00 | 13418 | 4.2998 | 85.5249 | 59.8258 | 3932.4276 |  | 4958 | 17848800 | 49384800 | 80920800 | 112456800
2034-02-21 15:00 | 12712 | 3.9231 | 86.3705 | 59.8258 | 3725.5194 |  | 4959 | 17852400 | 49388400 | 80924400 | 112460400
2034-02-22 16:00 | 11745.8 | 3.7777 | 85.8913 | 59.8258 | 3442.3542 |  | 4960 | 17856000 | 49392000 | 80928000 | 112464000
2034-02-23 17:00 | 12079.7 | 3.7113 | 86.5295 | 59.8258 | 3540.2106 |  | 4961 | 17859600 | 49395600 | 80931600 | 112467600
2034-02-24 18:00 | 10321.8 | 3.1631 | 86.6484 | 59.8258 | 3025.021 |  | 4962 | 17863200 | 49399200 | 80935200 | 112471200
2034-02-25 19:00 | 9108.06 | 2.7672 | 86.6253 | 59.8258 | 2669.3089 |  | 4963 | 17866800 | 49402800 | 80938800 | 112474800
2034-02-26 20:00 | 6974.37 | 2.0191 | 87.1507 | 59.8258 | 2043.9861 |  | 4964 | 17870400 | 49406400 | 80942400 | 112478400
2034-02-27 21:00 | 6028.59 | 1.8019 | 86.2766 | 59.8258 | 1766.8053 |  | 4965 | 17874000 | 49410000 | 80946000 | 112482000
2034-02-28 22:00 | 3571.26 | 1.0521 | 86.1903 | 59.8258 | 1046.633 |  | 4966 | 17877600 | 49413600 | 80949600 | 112485600
2034-03-01 23:00 | 3244.54 | 1 | 89.011 | 59.8258 | 950.8808 |  | 4967 | 17881200 | 49417200 | 80953200 | 112489200
2034-03-03 | 3159.93 | 1 | 69.4825 | 59.8258 | 926.0841 |  | 4968 | 17884800 | 49420800 | 80956800 | 112492800
2034-03-04 01:00 | 3141.15 | 1 | 69.2233 | 59.8258 | 920.5802 |  | 4969 | 17888400 | 49424400 | 80960400 | 112496400
2034-03-05 02:00 | 3187.04 | 1 | 69.0087 | 59.8258 | 934.0292 |  | 4970 | 17892000 | 49428000 | 80964000 | 112500000
2034-03-06 03:00 | 3185.38 | 1 | 68.8387 | 59.8258 | 933.5427 |  | 4971 | 17895600 | 49431600 | 80967600 | 112503600
2034-03-07 04:00 | 3229.56 | 1 | 93.0911 | 59.8258 | 946.4906 |  | 4972 | 17899200 | 49435200 | 80971200 | 112507200
2034-03-08 05:00 | 3509.6 | 1.0934 | 83.5552 | 59.8258 | 1028.5622 |  | 4973 | 17902800 | 49438800 | 80974800 | 112510800
2034-03-09 06:00 | 3494.32 | 1.0753 | 83.7071 | 59.8258 | 1024.0841 |  | 4974 | 17906400 | 49442400 | 80978400 | 112514400
2034-03-10 07:00 | 4359.53 | 1.3535 | 83.5053 | 59.8258 | 1277.6521 |  | 4975 | 17910000 | 49446000 | 80982000 | 112518000
2034-03-11 08:00 | 3765.78 | 1.1567 | 83.7271 | 59.8258 | 1103.6412 |  | 4976 | 17913600 | 49449600 | 80985600 | 112521600
2034-03-12 09:00 | 5381.58 | 1.7386 | 82.9068 | 59.8258 | 1577.1854 |  | 4977 | 17917200 | 49453200 | 80989200 | 112525200
2034-03-13 10:00 | 7153.56 | 2.4746 | 82.1188 | 59.8258 | 2096.5015 |  | 4978 | 17920800 | 49456800 | 80992800 | 112528800
2034-03-14 11:00 | 9599.33 | 3.2444 | 82.725 | 59.8258 | 2813.2859 |  | 4979 | 17924400 | 49460400 | 80996400 | 112532400
2034-03-15 12:00 | 10969 | 3.637 | 83.4517 | 59.8258 | 3214.6966 |  | 4980 | 17928000 | 49464000 | 81000000 | 112536000
2034-03-16 13:00 | 12010.6 | 3.9166 | 84.1124 | 59.8258 | 3519.9594 |  | 4981 | 17931600 | 49467600 | 81003600 | 112539600
2034-03-17 14:00 | 11819.5 | 3.669 | 85.2403 | 59.8258 | 3463.9535 |  | 4982 | 17935200 | 49471200 | 81007200 | 112543200
2034-03-18 15:00 | 12855 | 4.2057 | 84.7285 | 59.8258 | 3767.4286 |  | 4983 | 17938800 | 49474800 | 81010800 | 112546800
2034-03-19 16:00 | 12170 | 3.7196 | 86.0448 | 59.8258 | 3566.6749 |  | 4984 | 17942400 | 49478400 | 81014400 | 112550400
2034-03-20 17:00 | 10150.4 | 3.2861 | 85.3375 | 59.8258 | 2974.7886 |  | 4985 | 17946000 | 49482000 | 81018000 | 112554000
2034-03-21 18:00 | 9202.58 | 2.8105 | 86.0262 | 59.8258 | 2697.01 |  | 4986 | 17949600 | 49485600 | 81021600 | 112557600
2034-03-22 19:00 | 8149.16 | 2.4384 | 86.1662 | 59.8258 | 2388.283 |  | 4987 | 17953200 | 49489200 | 81025200 | 112561200
2034-03-23 20:00 | 6011.54 | 1.7131 | 86.7823 | 59.8258 | 1761.8085 |  | 4988 | 17956800 | 49492800 | 81028800 | 112564800
2034-03-24 21:00 | 4965.33 | 1.4828 | 85.6673 | 59.8258 | 1455.1946 |  | 4989 | 17960400 | 49496400 | 81032400 | 112568400
2034-03-25 22:00 | 3205.37 | 1 | 89.543 | 59.8258 | 939.4012 |  | 4990 | 17964000 | 49500000 | 81036000 | 112572000
2034-03-26 23:00 | 3115.58 | 1 | 69.3234 | 59.8258 | 913.0864 |  | 4991 | 17967600 | 49503600 | 81039600 | 112575600
2034-03-28 | 3018.97 | 1 | 69.0407 | 59.8258 | 884.7728 |  | 4992 | 17971200 | 49507200 | 81043200 | 112579200
2034-03-29 01:00 | 0 | 0 | 69.0795 | 59.8258 | 0 |  | 4993 | 17974800 | 49510800 | 81046800 | 112582800
2034-03-30 02:00 | 131.023 | 1 | 68.4807 | 59.8258 | 38.3991 |  | 4994 | 17978400 | 49514400 | 81050400 | 112586400
2034-03-31 03:00 | 0 | 0 | 68.1103 | 59.8258 | 0 |  | 4995 | 17982000 | 49518000 | 81054000 | 112590000
2034-04-01 04:00 | -219.265 | 1.0726 | 66.9178 | 59.8258 | -64.2602 |  | 4996 | 17985600 | 49521600 | 81057600 | 112593600
2034-04-02 05:00 | -268.188 | 1.1656 | 66.5389 | 59.8258 | -78.5981 |  | 4997 | 17989200 | 49525200 | 81061200 | 112597200
2034-04-03 06:00 | 1867.89 | 1 | 67.1842 | 59.8258 | 547.4245 |  | 4998 | 17992800 | 49528800 | 81064800 | 112600800
2034-04-04 07:00 | 3008.45 | 1.0587 | 80.4906 | 59.8258 | 881.6897 |  | 4999 | 17996400 | 49532400 | 81068400 | 112604400
2034-04-05 08:00 | 3367.72 | 1.0748 | 81.9782 | 59.8258 | 986.9813 |  | 5000 | 18000000 | 49536000 | 81072000 | 112608000
2034-04-06 09:00 | 5095.97 | 1.7231 | 81.2574 | 59.8258 | 1493.4814 |  | 5001 | 18003600 | 49539600 | 81075600 | 112611600
2034-04-07 10:00 | 7261.85 | 2.4722 | 81.4344 | 59.8258 | 2128.2381 |  | 5002 | 18007200 | 49543200 | 81079200 | 112615200
2034-04-08 11:00 | 8931.69 | 3.0475 | 81.839 | 59.8258 | 2617.6199 |  | 5003 | 18010800 | 49546800 | 81082800 | 112618800
2034-04-09 12:00 | 10488.8 | 3.4752 | 82.6591 | 59.8258 | 3073.9638 |  | 5004 | 18014400 | 49550400 | 81086400 | 112622400
2034-04-10 13:00 | 11102.6 | 3.6176 | 83.3605 | 59.8258 | 3253.8509 |  | 5005 | 18018000 | 49554000 | 81090000 | 112626000
2034-04-11 14:00 | 11991.9 | 3.8912 | 83.8137 | 59.8258 | 3514.479 |  | 5006 | 18021600 | 49557600 | 81093600 | 112629600
2034-04-12 15:00 | 12883.6 | 4.1516 | 84.2935 | 59.8258 | 3775.8104 |  | 5007 | 18025200 | 49561200 | 81097200 | 112633200
2034-04-13 16:00 | 15489.5 | 5.0639 | 84.4713 | 59.8258 | 4539.5243 |  | 5008 | 18028800 | 49564800 | 81100800 | 112636800
2034-04-14 17:00 | 14605.3 | 4.6254 | 85.569 | 59.8258 | 4280.3909 |  | 5009 | 18032400 | 49568400 | 81104400 | 112640400
2034-04-15 18:00 | 13205.5 | 4.0662 | 86.2831 | 59.8258 | 3870.15 |  | 5010 | 18036000 | 49572000 | 81108000 | 112644000
2034-04-16 19:00 | 10934.7 | 3.4569 | 85.9613 | 59.8258 | 3204.6442 |  | 5011 | 18039600 | 49575600 | 81111600 | 112647600
2034-04-17 20:00 | 9657.66 | 2.9219 | 86.4717 | 59.8258 | 2830.3807 |  | 5012 | 18043200 | 49579200 | 81115200 | 112651200
2034-04-18 21:00 | 8465.59 | 2.5559 | 86.3368 | 59.8258 | 2481.0195 |  | 5013 | 18046800 | 49582800 | 81118800 | 112654800
2034-04-19 22:00 | 7415.08 | 2.2635 | 85.9315 | 59.8258 | 2173.1454 |  | 5014 | 18050400 | 49586400 | 81122400 | 112658400
2034-04-20 23:00 | 4372.62 | 1.2316 | 86.9287 | 59.8258 | 1281.4884 |  | 5015 | 18054000 | 49590000 | 81126000 | 112662000
2034-04-22 | 3376.87 | 1 | 85.7965 | 59.8258 | 989.6629 |  | 5016 | 18057600 | 49593600 | 81129600 | 112665600
2034-04-23 01:00 | 3164.14 | 1 | 88.3978 | 59.8258 | 927.3179 |  | 5017 | 18061200 | 49597200 | 81133200 | 112669200
2034-04-24 02:00 | 3165.79 | 1 | 92.5207 | 59.8258 | 927.8015 |  | 5018 | 18064800 | 49600800 | 81136800 | 112672800
2034-04-25 03:00 | 3271.65 | 1 | 68.9111 | 59.8258 | 958.826 |  | 5019 | 18068400 | 49604400 | 81140400 | 112676400
2034-04-26 04:00 | 3193.38 | 1 | 68.7237 | 59.8258 | 935.8873 |  | 5020 | 18072000 | 49608000 | 81144000 | 112680000
2034-04-27 05:00 | 3220.85 | 1 | 68.5795 | 59.8258 | 943.938 |  | 5021 | 18075600 | 49611600 | 81147600 | 112683600
2034-04-28 06:00 | 3382 | 1.0319 | 83.7587 | 59.8258 | 991.1664 |  | 5022 | 18079200 | 49615200 | 81151200 | 112687200
2034-04-29 07:00 | 5394 | 1.7446 | 82.7923 | 59.8258 | 1580.8254 |  | 5023 | 18082800 | 49618800 | 81154800 | 112690800
2034-04-30 08:00 | 5996.07 | 1.8665 | 83.5519 | 59.8258 | 1757.2747 |  | 5024 | 18086400 | 49622400 | 81158400 | 112694400
2034-05-01 09:00 | 7320.74 | 2.4351 | 82.7671 | 59.8258 | 2145.4971 |  | 5025 | 18090000 | 49626000 | 81162000 | 112698000
2034-05-02 10:00 | 9340.52 | 3.1559 | 82.7829 | 59.8258 | 2737.4362 |  | 5026 | 18093600 | 49629600 | 81165600 | 112701600
2034-05-03 11:00 | 11151.2 | 3.6452 | 83.6599 | 59.8258 | 3268.0941 |  | 5027 | 18097200 | 49633200 | 81169200 | 112705200
2034-05-04 12:00 | 12220.3 | 4.0213 | 84.0731 | 59.8258 | 3581.4164 |  | 5028 | 18100800 | 49636800 | 81172800 | 112708800
2034-05-05 13:00 | 13251.3 | 4.2445 | 84.8827 | 59.8258 | 3883.5727 |  | 5029 | 18104400 | 49640400 | 81176400 | 112712400
2034-05-06 14:00 | 14120.9 | 4.5441 | 85.2442 | 59.8258 | 4138.4273 |  | 5030 | 18108000 | 49644000 | 81180000 | 112716000
2034-05-07 15:00 | 14436.4 | 4.6565 | 85.6234 | 59.8258 | 4230.8912 |  | 5031 | 18111600 | 49647600 | 81183600 | 112719600
2034-05-08 16:00 | 15902.5 | 5.1409 | 85.8968 | 59.8258 | 4660.5627 |  | 5032 | 18115200 | 49651200 | 81187200 | 112723200
2034-05-09 17:00 | 14340 | 4.4953 | 86.7787 | 59.8258 | 4202.6391 |  | 5033 | 18118800 | 49654800 | 81190800 | 112726800
2034-05-10 18:00 | 12053.2 | 3.7351 | 87.0712 | 59.8258 | 3532.4442 |  | 5034 | 18122400 | 49658400 | 81194400 | 112730400
2034-05-11 19:00 | 10390.2 | 3.1156 | 87.3842 | 59.8258 | 3045.067 |  | 5035 | 18126000 | 49662000 | 81198000 | 112734000
2034-05-12 20:00 | 8656.74 | 2.7099 | 86.5114 | 59.8258 | 2537.0401 |  | 5036 | 18129600 | 49665600 | 81201600 | 112737600
2034-05-13 21:00 | 7982.28 | 2.378 | 86.9437 | 59.8258 | 2339.3753 |  | 5037 | 18133200 | 49669200 | 81205200 | 112741200
2034-05-14 22:00 | 6931.4 | 2.1936 | 85.7578 | 59.8258 | 2031.3928 |  | 5038 | 18136800 | 49672800 | 81208800 | 112744800
2034-05-15 23:00 | 4575.45 | 1.2516 | 87.7356 | 59.8258 | 1340.932 |  | 5039 | 18140400 | 49676400 | 81212400 | 112748400
2034-05-17 | 3552.96 | 1.0728 | 85.6736 | 59.8258 | 1041.2698 |  | 5040 | 18144000 | 49680000 | 81216000 | 112752000
2034-05-18 01:00 | 3197.41 | 1 | 87.1835 | 59.8258 | 937.0684 |  | 5041 | 18147600 | 49683600 | 81219600 | 112755600
2034-05-19 02:00 | 3185.95 | 1 | 88.4995 | 59.8258 | 933.7098 |  | 5042 | 18151200 | 49687200 | 81223200 | 112759200
2034-05-20 03:00 | 3217.79 | 1 | 87.7829 | 59.8258 | 943.0412 |  | 5043 | 18154800 | 49690800 | 81226800 | 112762800
2034-05-21 04:00 | 3091.45 | 1 | 84.7378 | 59.8258 | 906.0146 |  | 5044 | 18158400 | 49694400 | 81230400 | 112766400
2034-05-22 05:00 | 3692.67 | 1.1421 | 83.9685 | 59.8258 | 1082.2147 |  | 5045 | 18162000 | 49698000 | 81234000 | 112770000
2034-05-23 06:00 | 4705.92 | 1.4495 | 83.9922 | 59.8258 | 1379.169 |  | 5046 | 18165600 | 49701600 | 81237600 | 112773600
2034-05-24 07:00 | 5778.75 | 1.8736 | 83.33 | 59.8258 | 1693.5844 |  | 5047 | 18169200 | 49705200 | 81241200 | 112777200
2034-05-25 08:00 | 6510.98 | 2.1222 | 83.4202 | 59.8258 | 1908.1799 |  | 5048 | 18172800 | 49708800 | 81244800 | 112780800
2034-05-26 09:00 | 8437.93 | 2.8214 | 83.2199 | 59.8258 | 2472.9132 |  | 5049 | 18176400 | 49712400 | 81248400 | 112784400
2034-05-27 10:00 | 10289.6 | 3.3536 | 83.9054 | 59.8258 | 3015.5841 |  | 5050 | 18180000 | 49716000 | 81252000 | 112788000
2034-05-28 11:00 | 11615.2 | 3.8175 | 84.2335 | 59.8258 | 3404.0791 |  | 5051 | 18183600 | 49719600 | 81255600 | 112791600
2034-05-29 12:00 | 13096 | 4.0939 | 85.3771 | 59.8258 | 3838.0587 |  | 5052 | 18187200 | 49723200 | 81259200 | 112795200
2034-05-30 13:00 | 13047.2 | 4.2693 | 85.1936 | 59.8258 | 3823.7569 |  | 5053 | 18190800 | 49726800 | 81262800 | 112798800
2034-05-31 14:00 | 13624.4 | 4.485 | 85.4167 | 59.8258 | 3992.9175 |  | 5054 | 18194400 | 49730400 | 81266400 | 112802400
2034-06-01 15:00 | 14736.8 | 4.7483 | 86.0023 | 59.8258 | 4318.9297 |  | 5055 | 18198000 | 49734000 | 81270000 | 112806000
2034-06-02 16:00 | 14710.8 | 4.6555 | 86.6114 | 59.8258 | 4311.3099 |  | 5056 | 18201600 | 49737600 | 81273600 | 112809600
2034-06-03 17:00 | 14704.8 | 4.623 | 86.9474 | 59.8258 | 4309.5515 |  | 5057 | 18205200 | 49741200 | 81277200 | 112813200
2034-06-04 18:00 | 12956 | 4.0587 | 87.1865 | 59.8258 | 3797.0288 |  | 5058 | 18208800 | 49744800 | 81280800 | 112816800
2034-06-05 19:00 | 11118 | 3.4064 | 87.4728 | 59.8258 | 3258.3642 |  | 5059 | 18212400 | 49748400 | 81284400 | 112820400
2034-06-06 20:00 | 8660.12 | 2.5479 | 87.8962 | 59.8258 | 2538.0306 |  | 5060 | 18216000 | 49752000 | 81288000 | 112824000
2034-06-07 21:00 | 7391.36 | 2.1993 | 87.3138 | 59.8258 | 2166.1938 |  | 5061 | 18219600 | 49755600 | 81291600 | 112827600
2034-06-08 22:00 | 5441.98 | 1.4888 | 88.2765 | 59.8258 | 1594.8869 |  | 5062 | 18223200 | 49759200 | 81295200 | 112831200
2034-06-09 23:00 | 4210.67 | 1.3131 | 85.7419 | 59.8258 | 1234.0256 |  | 5063 | 18226800 | 49762800 | 81298800 | 112834800
2034-06-11 | 3455.8 | 1.0793 | 85.2587 | 59.8258 | 1012.795 |  | 5064 | 18230400 | 49766400 | 81302400 | 112838400
2034-06-12 01:00 | 3271.4 | 1 | 85.1857 | 59.8258 | 958.7527 |  | 5065 | 18234000 | 49770000 | 81306000 | 112842000
2034-06-13 02:00 | 3225.97 | 1 | 85.0799 | 59.8258 | 945.4385 |  | 5066 | 18237600 | 49773600 | 81309600 | 112845600
2034-06-14 03:00 | 3304.09 | 1.0481 | 84.1242 | 59.8258 | 968.3332 |  | 5067 | 18241200 | 49777200 | 81313200 | 112849200
2034-06-15 04:00 | 3453.89 | 1.0773 | 84.1993 | 59.8258 | 1012.2352 |  | 5068 | 18244800 | 49780800 | 81316800 | 112852800
2034-06-16 05:00 | 4058.36 | 1.3089 | 83.5859 | 59.8258 | 1189.3879 |  | 5069 | 18248400 | 49784400 | 81320400 | 112856400
2034-06-17 06:00 | 4684.42 | 1.4306 | 84.3505 | 59.8258 | 1372.868 |  | 5070 | 18252000 | 49788000 | 81324000 | 112860000
2034-06-18 07:00 | 5972.62 | 2.0031 | 83.0339 | 59.8258 | 1750.4021 |  | 5071 | 18255600 | 49791600 | 81327600 | 112863600
2034-06-19 08:00 | 6595.62 | 2.1024 | 83.9154 | 59.8258 | 1932.9854 |  | 5072 | 18259200 | 49795200 | 81331200 | 112867200
2034-06-20 09:00 | 8150.78 | 2.8048 | 83.0069 | 59.8258 | 2388.7578 |  | 5073 | 18262800 | 49798800 | 81334800 | 112870800
2034-06-21 10:00 | 10327.7 | 3.3571 | 84.0637 | 59.8258 | 3026.7501 |  | 5074 | 18266400 | 49802400 | 81338400 | 112874400
2034-06-22 11:00 | 12028.7 | 3.9144 | 84.4947 | 59.8258 | 3525.264 |  | 5075 | 18270000 | 49806000 | 81342000 | 112878000
2034-06-23 12:00 | 12581.8 | 4.1751 | 84.7123 | 59.8258 | 3687.3616 |  | 5076 | 18273600 | 49809600 | 81345600 | 112881600
2034-06-24 13:00 | 13444.7 | 4.3 | 85.589 | 59.8258 | 3940.2526 |  | 5077 | 18277200 | 49813200 | 81349200 | 112885200
2034-06-25 14:00 | 14050.6 | 4.5774 | 85.6959 | 59.8258 | 4117.8244 |  | 5078 | 18280800 | 49816800 | 81352800 | 112888800
2034-06-26 15:00 | 16119.7 | 5.2326 | 86.0765 | 59.8258 | 4724.2177 |  | 5079 | 18284400 | 49820400 | 81356400 | 112892400
2034-06-27 16:00 | 17071.9 | 5.3667 | 87.0328 | 59.8258 | 5003.28 |  | 5080 | 18288000 | 49824000 | 81360000 | 112896000
2034-06-28 17:00 | 16883.6 | 5.3046 | 87.4969 | 59.8258 | 4948.0947 |  | 5081 | 18291600 | 49827600 | 81363600 | 112899600
2034-06-29 18:00 | 15227.6 | 4.6707 | 88.1634 | 59.8258 | 4462.769 |  | 5082 | 18295200 | 49831200 | 81367200 | 112903200
2034-06-30 19:00 | 13023.5 | 4.0789 | 87.9072 | 59.8258 | 3816.8111 |  | 5083 | 18298800 | 49834800 | 81370800 | 112906800
2034-07-01 20:00 | 10356.2 | 3.1123 | 88.38 | 59.8258 | 3035.1026 |  | 5084 | 18302400 | 49838400 | 81374400 | 112910400
2034-07-02 21:00 | 8995.66 | 2.7224 | 87.8894 | 59.8258 | 2636.3677 |  | 5085 | 18306000 | 49842000 | 81378000 | 112914000
2034-07-03 22:00 | 6915.7 | 2.0002 | 88.2228 | 59.8258 | 2026.7916 |  | 5086 | 18309600 | 49845600 | 81381600 | 112917600
2034-07-04 23:00 | 5842.45 | 1.7489 | 87.2023 | 59.8258 | 1712.2531 |  | 5087 | 18313200 | 49849200 | 81385200 | 112921200
2034-07-06 | 5476.21 | 1.6759 | 86.4396 | 59.8258 | 1604.9187 |  | 5088 | 18316800 | 49852800 | 81388800 | 112924800
2034-07-07 01:00 | 5088.2 | 1.5426 | 86.2796 | 59.8258 | 1491.2042 |  | 5089 | 18320400 | 49856400 | 81392400 | 112928400
2034-07-08 02:00 | 4958.53 | 1.4987 | 86.0823 | 59.8258 | 1453.2017 |  | 5090 | 18324000 | 49860000 | 81396000 | 112932000
2034-07-09 03:00 | 5070.39 | 1.582 | 85.3885 | 59.8258 | 1485.9846 |  | 5091 | 18327600 | 49863600 | 81399600 | 112935600
2034-07-10 04:00 | 5142.76 | 1.6601 | 84.7511 | 59.8258 | 1507.1942 |  | 5092 | 18331200 | 49867200 | 81403200 | 112939200
2034-07-11 05:00 | 5868.24 | 1.94 | 84.2963 | 59.8258 | 1719.8114 |  | 5093 | 18334800 | 49870800 | 81406800 | 112942800
2034-07-12 06:00 | 6563.05 | 2.1241 | 84.5795 | 59.8258 | 1923.4401 |  | 5094 | 18338400 | 49874400 | 81410400 | 112946400
2034-07-13 07:00 | 7599.1 | 2.487 | 84.4775 | 59.8258 | 2227.0764 |  | 5095 | 18342000 | 49878000 | 81414000 | 112950000
2034-07-14 08:00 | 8347.36 | 2.6415 | 85.1158 | 59.8258 | 2446.3697 |  | 5096 | 18345600 | 49881600 | 81417600 | 112953600
2034-07-15 09:00 | 10039 | 3.2216 | 85.0835 | 59.8258 | 2942.1405 |  | 5097 | 18349200 | 49885200 | 81421200 | 112957200
2034-07-16 10:00 | 11156.9 | 3.6345 | 85.1952 | 59.8258 | 3269.7646 |  | 5098 | 18352800 | 49888800 | 81424800 | 112960800
2034-07-17 11:00 | 12685 | 4.1489 | 85.4702 | 59.8258 | 3717.6065 |  | 5099 | 18356400 | 49892400 | 81428400 | 112964400
2034-07-18 12:00 | 13478.1 | 4.3697 | 85.9931 | 59.8258 | 3950.0412 |  | 5100 | 18360000 | 49896000 | 81432000 | 112968000
2034-07-19 13:00 | 13669.3 | 4.4158 | 86.4038 | 59.8258 | 4006.0764 |  | 5101 | 18363600 | 49899600 | 81435600 | 112971600
2034-07-20 14:00 | 14456.3 | 4.6111 | 86.8476 | 59.8258 | 4236.7233 |  | 5102 | 18367200 | 49903200 | 81439200 | 112975200
2034-07-21 15:00 | 16313.6 | 5.2205 | 87.0704 | 59.8258 | 4781.0442 |  | 5103 | 18370800 | 49906800 | 81442800 | 112978800
2034-07-22 16:00 | 16556.2 | 5.2348 | 87.6873 | 59.8258 | 4852.1432 |  | 5104 | 18374400 | 49910400 | 81446400 | 112982400
2034-07-23 17:00 | 16100.7 | 5.1433 | 87.8483 | 59.8258 | 4718.6494 |  | 5105 | 18378000 | 49914000 | 81450000 | 112986000
2034-07-24 18:00 | 13816.9 | 4.2847 | 88.4489 | 59.8258 | 4049.3337 |  | 5106 | 18381600 | 49917600 | 81453600 | 112989600
2034-07-25 19:00 | 12111.2 | 3.7592 | 88.314 | 59.8258 | 3549.4423 |  | 5107 | 18385200 | 49921200 | 81457200 | 112993200
2034-07-26 20:00 | 9660.27 | 2.9296 | 88.4556 | 59.8258 | 2831.1457 |  | 5108 | 18388800 | 49924800 | 81460800 | 112996800
2034-07-27 21:00 | 8459.31 | 2.5338 | 88.2263 | 59.8258 | 2479.179 |  | 5109 | 18392400 | 49928400 | 81464400 | 113000400
2034-07-28 22:00 | 6414.11 | 1.883 | 88.1607 | 59.8258 | 1879.7901 |  | 5110 | 18396000 | 49932000 | 81468000 | 113004000
2034-07-29 23:00 | 5685.87 | 1.6934 | 87.4379 | 59.8258 | 1666.364 |  | 5111 | 18399600 | 49935600 | 81471600 | 113007600
2034-07-31 | 5260.4 | 1.5811 | 86.9044 | 59.8258 | 1541.6711 |  | 5112 | 18403200 | 49939200 | 81475200 | 113011200
2034-08-01 01:00 | 4832.02 | 1.4552 | 86.574 | 59.8258 | 1416.1253 |  | 5113 | 18406800 | 49942800 | 81478800 | 113014800
2034-08-02 02:00 | 4368.81 | 1.3817 | 85.5885 | 59.8258 | 1280.3718 |  | 5114 | 18410400 | 49946400 | 81482400 | 113018400
2034-08-03 03:00 | 4366.61 | 1.3694 | 85.4288 | 59.8258 | 1279.7271 |  | 5115 | 18414000 | 49950000 | 81486000 | 113022000
2034-08-04 04:00 | 4433.65 | 1.3843 | 85.2938 | 59.8258 | 1299.3745 |  | 5116 | 18417600 | 49953600 | 81489600 | 113025600
2034-08-05 05:00 | 5174.08 | 1.6736 | 84.6239 | 59.8258 | 1516.3732 |  | 5117 | 18421200 | 49957200 | 81493200 | 113029200
2034-08-06 06:00 | 5504.99 | 1.7625 | 84.7365 | 59.8258 | 1613.3533 |  | 5118 | 18424800 | 49960800 | 81496800 | 113032800
2034-08-07 07:00 | 6415.33 | 2.1375 | 84.1596 | 59.8258 | 1880.1476 |  | 5119 | 18428400 | 49964400 | 81500400 | 113036400
2034-08-08 08:00 | 6772.02 | 2.238 | 84.3672 | 59.8258 | 1984.6831 |  | 5120 | 18432000 | 49968000 | 81504000 | 113040000
2034-08-09 09:00 | 8389.69 | 2.8143 | 84.2316 | 59.8258 | 2458.7754 |  | 5121 | 18435600 | 49971600 | 81507600 | 113043600
2034-08-10 10:00 | 10002.2 | 3.3012 | 84.6978 | 59.8258 | 2931.3555 |  | 5122 | 18439200 | 49975200 | 81511200 | 113047200
2034-08-11 11:00 | 11394.9 | 3.7024 | 85.2493 | 59.8258 | 3339.5155 |  | 5123 | 18442800 | 49978800 | 81514800 | 113050800
2034-08-12 12:00 | 12349.8 | 3.9329 | 85.9009 | 59.8258 | 3619.3691 |  | 5124 | 18446400 | 49982400 | 81518400 | 113054400
2034-08-13 13:00 | 12935.4 | 4.1865 | 86.014 | 59.8258 | 3790.9915 |  | 5125 | 18450000 | 49986000 | 81522000 | 113058000
2034-08-14 14:00 | 13647.5 | 4.4451 | 86.2346 | 59.8258 | 3999.6874 |  | 5126 | 18453600 | 49989600 | 81525600 | 113061600
2034-08-15 15:00 | 15209.2 | 4.9914 | 86.4103 | 59.8258 | 4457.3765 |  | 5127 | 18457200 | 49993200 | 81529200 | 113065200
2034-08-16 16:00 | 15788.8 | 5.0977 | 87.034 | 59.8258 | 4627.2405 |  | 5128 | 18460800 | 49996800 | 81532800 | 113068800
2034-08-17 17:00 | 15608.3 | 4.9679 | 87.5664 | 59.8258 | 4574.3412 |  | 5129 | 18464400 | 50000400 | 81536400 | 113072400
2034-08-18 18:00 | 14064.6 | 4.3691 | 88.1406 | 59.8258 | 4121.9274 |  | 5130 | 18468000 | 50004000 | 81540000 | 113076000
2034-08-19 19:00 | 12140.7 | 3.7739 | 88.1304 | 59.8258 | 3558.0879 |  | 5131 | 18471600 | 50007600 | 81543600 | 113079600
2034-08-20 20:00 | 9647.45 | 2.9059 | 88.4408 | 59.8258 | 2827.3885 |  | 5132 | 18475200 | 50011200 | 81547200 | 113083200
2034-08-21 21:00 | 8461.62 | 2.5175 | 88.243 | 59.8258 | 2479.856 |  | 5133 | 18478800 | 50014800 | 81550800 | 113086800
2034-08-22 22:00 | 6346.38 | 1.8261 | 88.4193 | 59.8258 | 1859.9404 |  | 5134 | 18482400 | 50018400 | 81554400 | 113090400
2034-08-23 23:00 | 5333.95 | 1.5635 | 87.6417 | 59.8258 | 1563.2264 |  | 5135 | 18486000 | 50022000 | 81558000 | 113094000
2034-08-25 | 4402.35 | 1.3432 | 86.5962 | 59.8258 | 1290.2014 |  | 5136 | 18489600 | 50025600 | 81561600 | 113097600
2034-08-26 01:00 | 3769.06 | 1.1631 | 86.0376 | 59.8258 | 1104.6024 |  | 5137 | 18493200 | 50029200 | 81565200 | 113101200
2034-08-27 02:00 | 3325.64 | 1.0571 | 85.2688 | 59.8258 | 974.6489 |  | 5138 | 18496800 | 50032800 | 81568800 | 113104800
2034-08-28 03:00 | 3369.23 | 1.0586 | 85.1122 | 59.8258 | 987.4238 |  | 5139 | 18500400 | 50036400 | 81572400 | 113108400
2034-08-29 04:00 | 3570.26 | 1.1243 | 84.8476 | 59.8258 | 1046.3399 |  | 5140 | 18504000 | 50040000 | 81576000 | 113112000
2034-08-30 05:00 | 4376.57 | 1.4045 | 84.4011 | 59.8258 | 1282.6461 |  | 5141 | 18507600 | 50043600 | 81579600 | 113115600
2034-08-31 06:00 | 4856.86 | 1.5203 | 84.7154 | 59.8258 | 1423.4052 |  | 5142 | 18511200 | 50047200 | 81583200 | 113119200
2034-09-01 07:00 | 5856.79 | 1.9517 | 83.8205 | 59.8258 | 1716.4557 |  | 5143 | 18514800 | 50050800 | 81586800 | 113122800
2034-09-02 08:00 | 6544.83 | 2.2194 | 83.6906 | 59.8258 | 1918.1003 |  | 5144 | 18518400 | 50054400 | 81590400 | 113126400
2034-09-03 09:00 | 8404.49 | 2.8681 | 83.721 | 59.8258 | 2463.1129 |  | 5145 | 18522000 | 50058000 | 81594000 | 113130000
2034-09-04 10:00 | 10351.2 | 3.4339 | 84.4024 | 59.8258 | 3033.6373 |  | 5146 | 18525600 | 50061600 | 81597600 | 113133600
2034-09-05 11:00 | 11885.2 | 3.8391 | 85.1866 | 59.8258 | 3483.2083 |  | 5147 | 18529200 | 50065200 | 81601200 | 113137200
2034-09-06 12:00 | 12277.1 | 3.8516 | 86.0466 | 59.8258 | 3598.0628 |  | 5148 | 18532800 | 50068800 | 81604800 | 113140800
2034-09-07 13:00 | 12414.1 | 3.9725 | 86.0828 | 59.8258 | 3638.2136 |  | 5149 | 18536400 | 50072400 | 81608400 | 113144400
2034-09-08 14:00 | 12960.8 | 4.1508 | 86.3187 | 59.8258 | 3798.4355 |  | 5150 | 18540000 | 50076000 | 81612000 | 113148000
2034-09-09 15:00 | 14870.8 | 4.7404 | 86.6201 | 59.8258 | 4358.2013 |  | 5151 | 18543600 | 50079600 | 81615600 | 113151600
2034-09-10 16:00 | 15374.4 | 4.9531 | 86.8854 | 59.8258 | 4505.7919 |  | 5152 | 18547200 | 50083200 | 81619200 | 113155200
2034-09-11 17:00 | 15307 | 4.8748 | 87.3689 | 59.8258 | 4486.0389 |  | 5153 | 18550800 | 50086800 | 81622800 | 113158800
2034-09-12 18:00 | 13478.3 | 4.2256 | 87.8245 | 59.8258 | 3950.0998 |  | 5154 | 18554400 | 50090400 | 81626400 | 113162400
2034-09-13 19:00 | 11959.7 | 3.683 | 88.057 | 59.8258 | 3505.0421 |  | 5155 | 18558000 | 50094000 | 81630000 | 113166000
2034-09-14 20:00 | 9488 | 2.8376 | 88.3775 | 59.8258 | 2780.6583 |  | 5156 | 18561600 | 50097600 | 81633600 | 113169600
2034-09-15 21:00 | 8336.75 | 2.4577 | 88.2324 | 59.8258 | 2443.2602 |  | 5157 | 18565200 | 50101200 | 81637200 | 113173200
2034-09-16 22:00 | 6121.49 | 1.7698 | 88.2008 | 59.8258 | 1794.0316 |  | 5158 | 18568800 | 50104800 | 81640800 | 113176800
2034-09-17 23:00 | 4564.72 | 1.3354 | 87.518 | 59.8258 | 1337.7874 |  | 5159 | 18572400 | 50108400 | 81644400 | 113180400
2034-09-19 | 3716.09 | 1.1271 | 86.464 | 59.8258 | 1089.0785 |  | 5160 | 18576000 | 50112000 | 81648000 | 113184000
2034-09-20 01:00 | 3098.12 | 1 | 86.33 | 59.8258 | 907.9693 |  | 5161 | 18579600 | 50115600 | 81651600 | 113187600
2034-09-21 02:00 | 3111.73 | 1 | 92.2647 | 59.8258 | 911.958 |  | 5162 | 18583200 | 50119200 | 81655200 | 113191200
2034-09-22 03:00 | 3094.2 | 1 | 70.087 | 59.8258 | 906.8205 |  | 5163 | 18586800 | 50122800 | 81658800 | 113194800
2034-09-23 04:00 | 3110.85 | 1 | 69.8763 | 59.8258 | 911.7001 |  | 5164 | 18590400 | 50126400 | 81662400 | 113198400
2034-09-24 05:00 | 3169.36 | 1 | 69.6847 | 59.8258 | 928.8477 |  | 5165 | 18594000 | 50130000 | 81666000 | 113202000
2034-09-25 06:00 | 3228.02 | 1 | 86.0217 | 59.8258 | 946.0393 |  | 5166 | 18597600 | 50133600 | 81669600 | 113205600
2034-09-26 07:00 | 4645.94 | 1.4035 | 84.8089 | 59.8258 | 1361.5906 |  | 5167 | 18601200 | 50137200 | 81673200 | 113209200
2034-09-27 08:00 | 4465.44 | 1.3338 | 85.0751 | 59.8258 | 1308.6913 |  | 5168 | 18604800 | 50140800 | 81676800 | 113212800
2034-09-28 09:00 | 5839.97 | 1.9119 | 83.7085 | 59.8258 | 1711.5263 |  | 5169 | 18608400 | 50144400 | 81680400 | 113216400
2034-09-29 10:00 | 7670.65 | 2.6551 | 83.0788 | 59.8258 | 2248.0456 |  | 5170 | 18612000 | 50148000 | 81684000 | 113220000
2034-09-30 11:00 | 9243.64 | 3.1272 | 83.6883 | 59.8258 | 2709.0435 |  | 5171 | 18615600 | 50151600 | 81687600 | 113223600
2034-10-01 12:00 | 10339.5 | 3.4407 | 84.282 | 59.8258 | 3030.2083 |  | 5172 | 18619200 | 50155200 | 81691200 | 113227200
2034-10-02 13:00 | 10963.2 | 3.6358 | 84.6682 | 59.8258 | 3212.9968 |  | 5173 | 18622800 | 50158800 | 81694800 | 113230800
2034-10-03 14:00 | 11905.3 | 3.8787 | 85.2194 | 59.8258 | 3489.099 |  | 5174 | 18626400 | 50162400 | 81698400 | 113234400
2034-10-04 15:00 | 12603.2 | 4.07 | 85.6535 | 59.8258 | 3693.6333 |  | 5175 | 18630000 | 50166000 | 81702000 | 113238000
2034-10-05 16:00 | 14961.1 | 4.8461 | 85.8859 | 59.8258 | 4384.6656 |  | 5176 | 18633600 | 50169600 | 81705600 | 113241600
2034-10-06 17:00 | 14168.6 | 4.3936 | 87.0205 | 59.8258 | 4152.4068 |  | 5177 | 18637200 | 50173200 | 81709200 | 113245200
2034-10-07 18:00 | 12910.3 | 3.9414 | 87.4864 | 59.8258 | 3783.6354 |  | 5178 | 18640800 | 50176800 | 81712800 | 113248800
2034-10-08 19:00 | 11085.8 | 3.4089 | 87.3972 | 59.8258 | 3248.9273 |  | 5179 | 18644400 | 50180400 | 81716400 | 113252400
2034-10-09 20:00 | 9651.71 | 2.9808 | 87.2083 | 59.8258 | 2828.637 |  | 5180 | 18648000 | 50184000 | 81720000 | 113256000
2034-10-10 21:00 | 8511.87 | 2.6081 | 87.1325 | 59.8258 | 2494.5828 |  | 5181 | 18651600 | 50187600 | 81723600 | 113259600
2034-10-11 22:00 | 7712.99 | 2.3368 | 87.0435 | 59.8258 | 2260.4542 |  | 5182 | 18655200 | 50191200 | 81727200 | 113263200
2034-10-12 23:00 | 4442.1 | 1.2644 | 87.7862 | 59.8258 | 1301.851 |  | 5183 | 18658800 | 50194800 | 81730800 | 113266800
2034-10-14 | 3409.36 | 1.015 | 86.5049 | 59.8258 | 999.1848 |  | 5184 | 18662400 | 50198400 | 81734400 | 113270400
2034-10-15 01:00 | 3157.11 | 1 | 88.0429 | 59.8258 | 925.2576 |  | 5185 | 18666000 | 50202000 | 81738000 | 113274000
2034-10-16 02:00 | 3168.85 | 1 | 92.5725 | 59.8258 | 928.6983 |  | 5186 | 18669600 | 50205600 | 81741600 | 113277600
2034-10-17 03:00 | 3152.6 | 1 | 94.8811 | 59.8258 | 923.9359 |  | 5187 | 18673200 | 50209200 | 81745200 | 113281200
2034-10-18 04:00 | 3126.69 | 1 | 69.64 | 59.8258 | 916.3424 |  | 5188 | 18676800 | 50212800 | 81748800 | 113284800
2034-10-19 05:00 | 3066.19 | 1 | 69.4914 | 59.8258 | 898.6116 |  | 5189 | 18680400 | 50216400 | 81752400 | 113288400
2034-10-20 06:00 | 3215.74 | 1 | 85.267 | 59.8258 | 942.4404 |  | 5190 | 18684000 | 50220000 | 81756000 | 113292000
2034-10-21 07:00 | 5151.81 | 1.5868 | 84.3413 | 59.8258 | 1509.8465 |  | 5191 | 18687600 | 50223600 | 81759600 | 113295600
2034-10-22 08:00 | 5113.46 | 1.5731 | 84.5334 | 59.8258 | 1498.6072 |  | 5192 | 18691200 | 50227200 | 81763200 | 113299200
2034-10-23 09:00 | 6447.33 | 2.1199 | 83.6198 | 59.8258 | 1889.5259 |  | 5193 | 18694800 | 50230800 | 81766800 | 113302800
2034-10-24 10:00 | 8168.95 | 2.7771 | 83.3137 | 59.8258 | 2394.0829 |  | 5194 | 18698400 | 50234400 | 81770400 | 113306400
2034-10-25 11:00 | 9597.98 | 3.216 | 83.8412 | 59.8258 | 2812.8903 |  | 5195 | 18702000 | 50238000 | 81774000 | 113310000
2034-10-26 12:00 | 10840.6 | 3.525 | 84.638 | 59.8258 | 3177.0662 |  | 5196 | 18705600 | 50241600 | 81777600 | 113313600
2034-10-27 13:00 | 11642.5 | 3.75 | 85.1385 | 59.8258 | 3412.0799 |  | 5197 | 18709200 | 50245200 | 81781200 | 113317200
2034-10-28 14:00 | 12482.3 | 4.0105 | 85.5223 | 59.8258 | 3658.201 |  | 5198 | 18712800 | 50248800 | 81784800 | 113320800
2034-10-29 15:00 | 13362.8 | 4.2079 | 86.1426 | 59.8258 | 3916.2501 |  | 5199 | 18716400 | 50252400 | 81788400 | 113324400
2034-10-30 16:00 | 15646.2 | 5.0959 | 85.9738 | 59.8258 | 4585.4486 |  | 5200 | 18720000 | 50256000 | 81792000 | 113328000
2034-10-31 17:00 | 14300.8 | 4.6097 | 86.6583 | 59.8258 | 4191.1508 |  | 5201 | 18723600 | 50259600 | 81795600 | 113331600
2034-11-01 18:00 | 12907.4 | 4.0777 | 87.1277 | 59.8258 | 3782.7855 |  | 5202 | 18727200 | 50263200 | 81799200 | 113335200
2034-11-02 19:00 | 11235.1 | 3.4736 | 87.4122 | 59.8258 | 3292.6828 |  | 5203 | 18730800 | 50266800 | 81802800 | 113338800
2034-11-03 20:00 | 9904.84 | 3.0263 | 87.4545 | 59.8258 | 2902.8221 |  | 5204 | 18734400 | 50270400 | 81806400 | 113342400
2034-11-04 21:00 | 8844.91 | 2.6731 | 87.4234 | 59.8258 | 2592.1872 |  | 5205 | 18738000 | 50274000 | 81810000 | 113346000
2034-11-05 22:00 | 7872.14 | 2.418 | 86.9163 | 59.8258 | 2307.0965 |  | 5206 | 18741600 | 50277600 | 81813600 | 113349600
2034-11-06 23:00 | 5543.62 | 1.5117 | 88.553 | 59.8258 | 1624.6746 |  | 5207 | 18745200 | 50281200 | 81817200 | 113353200
2034-11-08 | 4472.3 | 1.3309 | 86.701 | 59.8258 | 1310.7017 |  | 5208 | 18748800 | 50284800 | 81820800 | 113356800
2034-11-09 01:00 | 3681.1 | 1.1512 | 85.5639 | 59.8258 | 1078.8239 |  | 5209 | 18752400 | 50288400 | 81824400 | 113360400
2034-11-10 02:00 | 3305.36 | 1.068 | 84.7523 | 59.8258 | 968.7054 |  | 5210 | 18756000 | 50292000 | 81828000 | 113364000
2034-11-11 03:00 | 3360.22 | 1.0617 | 84.7712 | 59.8258 | 984.7833 |  | 5211 | 18759600 | 50295600 | 81831600 | 113367600
2034-11-12 04:00 | 3581.69 | 1.1255 | 84.6003 | 59.8258 | 1049.6897 |  | 5212 | 18763200 | 50299200 | 81835200 | 113371200
2034-11-13 05:00 | 4521.52 | 1.4125 | 84.5392 | 59.8258 | 1325.1267 |  | 5213 | 18766800 | 50302800 | 81838800 | 113374800
2034-11-14 06:00 | 4778.54 | 1.4927 | 84.5487 | 59.8258 | 1400.4518 |  | 5214 | 18770400 | 50306400 | 81842400 | 113378400
2034-11-15 07:00 | 5788.29 | 1.8952 | 83.8756 | 59.8258 | 1696.3803 |  | 5215 | 18774000 | 50310000 | 81846000 | 113382000
2034-11-16 08:00 | 6408.72 | 2.0854 | 84.0782 | 59.8258 | 1878.2104 |  | 5216 | 18777600 | 50313600 | 81849600 | 113385600
2034-11-17 09:00 | 8457.63 | 2.7853 | 84.0333 | 59.8258 | 2478.6867 |  | 5217 | 18781200 | 50317200 | 81853200 | 113389200
2034-11-18 10:00 | 10299.9 | 3.3931 | 84.3499 | 59.8258 | 3018.6027 |  | 5218 | 18784800 | 50320800 | 81856800 | 113392800
2034-11-19 11:00 | 11785.8 | 3.8897 | 84.75 | 59.8258 | 3454.077 |  | 5219 | 18788400 | 50324400 | 81860400 | 113396400
2034-11-20 12:00 | 13201.2 | 4.2562 | 85.5246 | 59.8258 | 3868.8898 |  | 5220 | 18792000 | 50328000 | 81864000 | 113400000
2034-11-21 13:00 | 13889.6 | 4.4993 | 85.9319 | 59.8258 | 4070.6399 |  | 5221 | 18795600 | 50331600 | 81867600 | 113403600
2034-11-22 14:00 | 14482.1 | 4.7079 | 86.3006 | 59.8258 | 4244.2845 |  | 5222 | 18799200 | 50335200 | 81871200 | 113407200
2034-11-23 15:00 | 16265.5 | 5.2442 | 86.766 | 59.8258 | 4766.9475 |  | 5223 | 18802800 | 50338800 | 81874800 | 113410800
2034-11-24 16:00 | 16642 | 5.2954 | 87.4279 | 59.8258 | 4877.2887 |  | 5224 | 18806400 | 50342400 | 81878400 | 113414400
2034-11-25 17:00 | 16335.8 | 5.1206 | 88.0183 | 59.8258 | 4787.5504 |  | 5225 | 18810000 | 50346000 | 81882000 | 113418000
2034-11-26 18:00 | 14678.5 | 4.5142 | 88.5354 | 59.8258 | 4301.8437 |  | 5226 | 18813600 | 50349600 | 81885600 | 113421600
2034-11-27 19:00 | 12943.4 | 3.9638 | 88.6052 | 59.8258 | 3793.3361 |  | 5227 | 18817200 | 50353200 | 81889200 | 113425200
2034-11-28 20:00 | 10389.4 | 3.1544 | 88.6098 | 59.8258 | 3044.8326 |  | 5228 | 18820800 | 50356800 | 81892800 | 113428800
2034-11-29 21:00 | 9312.69 | 2.7777 | 88.5024 | 59.8258 | 2729.28 |  | 5229 | 18824400 | 50360400 | 81896400 | 113432400
2034-11-30 22:00 | 7056.74 | 2.1094 | 88.1377 | 59.8258 | 2068.1263 |  | 5230 | 18828000 | 50364000 | 81900000 | 113436000
2034-12-01 23:00 | 6042.38 | 1.8112 | 87.6159 | 59.8258 | 1770.8468 |  | 5231 | 18831600 | 50367600 | 81903600 | 113439600
2034-12-03 | 5295.11 | 1.5975 | 87.0967 | 59.8258 | 1551.8436 |  | 5232 | 18835200 | 50371200 | 81907200 | 113443200
2034-12-04 01:00 | 4802.53 | 1.4335 | 86.9076 | 59.8258 | 1407.4826 |  | 5233 | 18838800 | 50374800 | 81910800 | 113446800
2034-12-05 02:00 | 4480.12 | 1.3569 | 86.3975 | 59.8258 | 1312.9936 |  | 5234 | 18842400 | 50378400 | 81914400 | 113450400
2034-12-06 03:00 | 4587.01 | 1.3877 | 86.1387 | 59.8258 | 1344.3199 |  | 5235 | 18846000 | 50382000 | 81918000 | 113454000
2034-12-07 04:00 | 4648.27 | 1.4744 | 85.2602 | 59.8258 | 1362.2735 |  | 5236 | 18849600 | 50385600 | 81921600 | 113457600
2034-12-08 05:00 | 5325.24 | 1.7451 | 84.6498 | 59.8258 | 1560.6738 |  | 5237 | 18853200 | 50389200 | 81925200 | 113461200
2034-12-09 06:00 | 5682.5 | 1.853 | 84.6888 | 59.8258 | 1665.3764 |  | 5238 | 18856800 | 50392800 | 81928800 | 113464800
2034-12-10 07:00 | 6685.01 | 2.1919 | 84.6031 | 59.8258 | 1959.183 |  | 5239 | 18860400 | 50396400 | 81932400 | 113468400
2034-12-11 08:00 | 7495.26 | 2.4006 | 85.0503 | 59.8258 | 2196.6439 |  | 5240 | 18864000 | 50400000 | 81936000 | 113472000
2034-12-12 09:00 | 9223.32 | 3.0362 | 84.8074 | 59.8258 | 2703.0883 |  | 5241 | 18867600 | 50403600 | 81939600 | 113475600
2034-12-13 10:00 | 10825.4 | 3.5998 | 84.9721 | 59.8258 | 3172.6116 |  | 5242 | 18871200 | 50407200 | 81943200 | 113479200
2034-12-14 11:00 | 12529.8 | 4.1436 | 85.4245 | 59.8258 | 3672.1219 |  | 5243 | 18874800 | 50410800 | 81946800 | 113482800
2034-12-15 12:00 | 13643 | 4.458 | 86.0386 | 59.8258 | 3998.3686 |  | 5244 | 18878400 | 50414400 | 81950400 | 113486400
2034-12-16 13:00 | 14315 | 4.613 | 86.6597 | 59.8258 | 4195.3124 |  | 5245 | 18882000 | 50418000 | 81954000 | 113490000
2034-12-17 14:00 | 15356.6 | 4.8383 | 87.3545 | 59.8258 | 4500.5752 |  | 5246 | 18885600 | 50421600 | 81957600 | 113493600
2034-12-18 15:00 | 17083.2 | 5.4027 | 87.676 | 59.8258 | 5006.5917 |  | 5247 | 18889200 | 50425200 | 81961200 | 113497200
2034-12-19 16:00 | 17484.8 | 5.4984 | 88.2478 | 59.8258 | 5124.289 |  | 5248 | 18892800 | 50428800 | 81964800 | 113500800
2034-12-20 17:00 | 17164.2 | 5.4065 | 88.5969 | 59.8258 | 5030.3305 |  | 5249 | 18896400 | 50432400 | 81968400 | 113504400
2034-12-21 18:00 | 15547 | 4.9037 | 88.8197 | 59.8258 | 4556.3759 |  | 5250 | 18900000 | 50436000 | 81972000 | 113508000
2034-12-22 19:00 | 13793.5 | 4.288 | 89.0497 | 59.8258 | 4042.4758 |  | 5251 | 18903600 | 50439600 | 81975600 | 113511600
2034-12-23 20:00 | 11256.5 | 3.4125 | 89.3002 | 59.8258 | 3298.9545 |  | 5252 | 18907200 | 50443200 | 81979200 | 113515200
2034-12-24 21:00 | 10095.7 | 3.0261 | 89.1037 | 59.8258 | 2958.7576 |  | 5253 | 18910800 | 50446800 | 81982800 | 113518800
2034-12-25 22:00 | 7932.16 | 2.35 | 88.959 | 59.8258 | 2324.6866 |  | 5254 | 18914400 | 50450400 | 81986400 | 113522400
2034-12-26 23:00 | 6977.93 | 2.1107 | 88.1747 | 59.8258 | 2045.0294 |  | 5255 | 18918000 | 50454000 | 81990000 | 113526000
2034-12-28 | 6263.91 | 1.9241 | 87.5429 | 59.8258 | 1835.7708 |  | 5256 | 18921600 | 50457600 | 81993600 | 113529600
2034-12-29 01:00 | 5882.43 | 1.7779 | 87.4514 | 59.8258 | 1723.9701 |  | 5257 | 18925200 | 50461200 | 81997200 | 113533200
2034-12-30 02:00 | 5591.81 | 1.6861 | 87.2223 | 59.8258 | 1638.7977 |  | 5258 | 18928800 | 50464800 | 82000800 | 113536800
2034-12-31 03:00 | 5691.01 | 1.7289 | 86.8556 | 59.8258 | 1667.8704 |  | 5259 | 18932400 | 50468400 | 82004400 | 113540400
2035-01-01 04:00 | 5610.09 | 1.8016 | 85.8786 | 59.8258 | 1644.1551 |  | 5260 | 18936000 | 50472000 | 82008000 | 113544000
2035-01-02 05:00 | 6215.49 | 2.0262 | 85.5106 | 59.8258 | 1821.5803 |  | 5261 | 18939600 | 50475600 | 82011600 | 113547600
2035-01-03 06:00 | 6766.39 | 2.2227 | 85.3622 | 59.8258 | 1983.0332 |  | 5262 | 18943200 | 50479200 | 82015200 | 113551200
2035-01-04 07:00 | 7781.72 | 2.594 | 85.1753 | 59.8258 | 2280.597 |  | 5263 | 18946800 | 50482800 | 82018800 | 113554800
2035-01-05 08:00 | 8785.33 | 2.7851 | 86.0121 | 59.8258 | 2574.7261 |  | 5264 | 18950400 | 50486400 | 82022400 | 113558400
2035-01-06 09:00 | 10705 | 3.4037 | 86.1463 | 59.8258 | 3137.3258 |  | 5265 | 18954000 | 50490000 | 82026000 | 113562000
2035-01-07 10:00 | 12211 | 3.9765 | 86.1642 | 59.8258 | 3578.6908 |  | 5266 | 18957600 | 50493600 | 82029600 | 113565600
2035-01-08 11:00 | 13563.2 | 4.4554 | 86.4429 | 59.8258 | 3974.9815 |  | 5267 | 18961200 | 50497200 | 82033200 | 113569200
2035-01-09 12:00 | 14592.7 | 4.7425 | 87.0097 | 59.8258 | 4276.6982 |  | 5268 | 18964800 | 50500800 | 82036800 | 113572800
2035-01-10 13:00 | 15011 | 4.8549 | 87.4829 | 59.8258 | 4399.2898 |  | 5269 | 18968400 | 50504400 | 82040400 | 113576400
2035-01-11 14:00 | 15986.9 | 5.1209 | 87.945 | 59.8258 | 4685.2979 |  | 5270 | 18972000 | 50508000 | 82044000 | 113580000
2035-01-12 15:00 | 17823.8 | 5.5896 | 88.5824 | 59.8258 | 5223.6401 |  | 5271 | 18975600 | 50511600 | 82047600 | 113583600
2035-01-13 16:00 | 18113.3 | 5.6816 | 89.0586 | 59.8258 | 5308.4842 |  | 5272 | 18979200 | 50515200 | 82051200 | 113587200
2035-01-14 17:00 | 17847.6 | 5.5446 | 89.5498 | 59.8258 | 5230.6152 |  | 5273 | 18982800 | 50518800 | 82054800 | 113590800
2035-01-15 18:00 | 16490.8 | 5.1135 | 89.8051 | 59.8258 | 4832.9764 |  | 5274 | 18986400 | 50522400 | 82058400 | 113594400
2035-01-16 19:00 | 14710.5 | 4.5259 | 89.9696 | 59.8258 | 4311.222 |  | 5275 | 18990000 | 50526000 | 82062000 | 113598000
2035-01-17 20:00 | 11971.8 | 3.6203 | 90.1174 | 59.8258 | 3508.5882 |  | 5276 | 18993600 | 50529600 | 82065600 | 113601600
2035-01-18 21:00 | 10603.6 | 3.215 | 89.6833 | 59.8258 | 3107.6084 |  | 5277 | 18997200 | 50533200 | 82069200 | 113605200
2035-01-19 22:00 | 8222.04 | 2.4644 | 89.4969 | 59.8258 | 2409.6421 |  | 5278 | 19000800 | 50536800 | 82072800 | 113608800
2035-01-20 23:00 | 7092.96 | 2.1735 | 88.6491 | 59.8258 | 2078.7414 |  | 5279 | 19004400 | 50540400 | 82076400 | 113612400
2035-01-22 | 6204.91 | 1.917 | 88.0679 | 59.8258 | 1818.4796 |  | 5280 | 19008000 | 50544000 | 82080000 | 113616000
2035-01-23 01:00 | 5652.45 | 1.7415 | 87.7115 | 59.8258 | 1656.5696 |  | 5281 | 19011600 | 50547600 | 82083600 | 113619600
2035-01-24 02:00 | 5432.73 | 1.6458 | 87.6326 | 59.8258 | 1592.176 |  | 5282 | 19015200 | 50551200 | 82087200 | 113623200
2035-01-25 03:00 | 5368.32 | 1.6801 | 86.858 | 59.8258 | 1573.2993 |  | 5283 | 19018800 | 50554800 | 82090800 | 113626800
2035-01-26 04:00 | 5508.41 | 1.7277 | 86.6099 | 59.8258 | 1614.3556 |  | 5284 | 19022400 | 50558400 | 82094400 | 113630400
2035-01-27 05:00 | 6170.14 | 1.9878 | 86.0573 | 59.8258 | 1808.2895 |  | 5285 | 19026000 | 50562000 | 82098000 | 113634000
2035-01-28 06:00 | 6549.22 | 2.0937 | 86.1177 | 59.8258 | 1919.3869 |  | 5286 | 19029600 | 50565600 | 82101600 | 113637600
2035-01-29 07:00 | 7589.78 | 2.4647 | 85.8701 | 59.8258 | 2224.3449 |  | 5287 | 19033200 | 50569200 | 82105200 | 113641200
2035-01-30 08:00 | 8344.57 | 2.6865 | 86.0945 | 59.8258 | 2445.5521 |  | 5288 | 19036800 | 50572800 | 82108800 | 113644800
2035-01-31 09:00 | 10203.3 | 3.35 | 85.944 | 59.8258 | 2990.292 |  | 5289 | 19040400 | 50576400 | 82112400 | 113648400
2035-02-01 10:00 | 12066.5 | 3.9199 | 86.3992 | 59.8258 | 3536.3421 |  | 5290 | 19044000 | 50580000 | 82116000 | 113652000
2035-02-02 11:00 | 13651.3 | 4.3887 | 86.9585 | 59.8258 | 4000.8011 |  | 5291 | 19047600 | 50583600 | 82119600 | 113655600
2035-02-03 12:00 | 14979.9 | 4.7364 | 87.6465 | 59.8258 | 4390.1753 |  | 5292 | 19051200 | 50587200 | 82123200 | 113659200
2035-02-04 13:00 | 15267.1 | 4.9069 | 87.8709 | 59.8258 | 4474.3453 |  | 5293 | 19054800 | 50590800 | 82126800 | 113662800
2035-02-05 14:00 | 16087.9 | 5.1455 | 88.2814 | 59.8258 | 4714.8981 |  | 5294 | 19058400 | 50594400 | 82130400 | 113666400
2035-02-06 15:00 | 17927.9 | 5.6342 | 88.86 | 59.8258 | 5254.1488 |  | 5295 | 19062000 | 50598000 | 82134000 | 113670000
2035-02-07 16:00 | 18218.6 | 5.7122 | 89.3705 | 59.8258 | 5339.3446 |  | 5296 | 19065600 | 50601600 | 82137600 | 113673600
2035-02-08 17:00 | 18003.6 | 5.5899 | 89.8609 | 59.8258 | 5276.3343 |  | 5297 | 19069200 | 50605200 | 82141200 | 113677200
2035-02-09 18:00 | 16289.3 | 5.0955 | 89.9797 | 59.8258 | 4773.9226 |  | 5298 | 19072800 | 50608800 | 82144800 | 113680800
2035-02-10 19:00 | 14137.8 | 4.4382 | 89.9279 | 59.8258 | 4143.3802 |  | 5299 | 19076400 | 50612400 | 82148400 | 113684400
2035-02-11 20:00 | 11467.1 | 3.5105 | 90.1114 | 59.8258 | 3360.6753 |  | 5300 | 19080000 | 50616000 | 82152000 | 113688000
2035-02-12 21:00 | 10051.7 | 3.0825 | 89.6598 | 59.8258 | 2945.8625 |  | 5301 | 19083600 | 50619600 | 82155600 | 113691600
2035-02-13 22:00 | 7986.34 | 2.3679 | 89.7763 | 59.8258 | 2340.5652 |  | 5302 | 19087200 | 50623200 | 82159200 | 113695200
2035-02-14 23:00 | 7014.62 | 2.1259 | 88.9335 | 59.8258 | 2055.7822 |  | 5303 | 19090800 | 50626800 | 82162800 | 113698800
2035-02-16 | 6407.98 | 1.9399 | 88.5071 | 59.8258 | 1877.9936 |  | 5304 | 19094400 | 50630400 | 82166400 | 113702400
2035-02-17 01:00 | 5997.25 | 1.8176 | 88.1399 | 59.8258 | 1757.6205 |  | 5305 | 19098000 | 50634000 | 82170000 | 113706000
2035-02-18 02:00 | 5716.3 | 1.7815 | 87.4408 | 59.8258 | 1675.2822 |  | 5306 | 19101600 | 50637600 | 82173600 | 113709600
2035-02-19 03:00 | 5783.89 | 1.8049 | 87.153 | 59.8258 | 1695.0908 |  | 5307 | 19105200 | 50641200 | 82177200 | 113713200
2035-02-20 04:00 | 6060.14 | 1.8904 | 86.9711 | 59.8258 | 1776.0517 |  | 5308 | 19108800 | 50644800 | 82180800 | 113716800
2035-02-21 05:00 | 6777.9 | 2.1776 | 86.4161 | 59.8258 | 1986.4064 |  | 5309 | 19112400 | 50648400 | 82184400 | 113720400
2035-02-22 06:00 | 6987.58 | 2.1929 | 86.7364 | 59.8258 | 2047.8575 |  | 5310 | 19116000 | 50652000 | 82188000 | 113724000
2035-02-23 07:00 | 7902.75 | 2.5221 | 86.4728 | 59.8258 | 2316.0674 |  | 5311 | 19119600 | 50655600 | 82191600 | 113727600
2035-02-24 08:00 | 8494.51 | 2.7022 | 86.6168 | 59.8258 | 2489.4951 |  | 5312 | 19123200 | 50659200 | 82195200 | 113731200
2035-02-25 09:00 | 10188.9 | 3.2948 | 86.4904 | 59.8258 | 2986.0718 |  | 5313 | 19126800 | 50662800 | 82198800 | 113734800
2035-02-26 10:00 | 11502.4 | 3.7756 | 86.5543 | 59.8258 | 3371.0207 |  | 5314 | 19130400 | 50666400 | 82202400 | 113738400
2035-02-27 11:00 | 13030.6 | 4.2858 | 86.8394 | 59.8258 | 3818.8919 |  | 5315 | 19134000 | 50670000 | 82206000 | 113742000
2035-02-28 12:00 | 14125.8 | 4.5158 | 87.6186 | 59.8258 | 4139.8633 |  | 5316 | 19137600 | 50673600 | 82209600 | 113745600
2035-03-01 13:00 | 14516.2 | 4.684 | 87.8648 | 59.8258 | 4254.2783 |  | 5317 | 19141200 | 50677200 | 82213200 | 113749200
2035-03-02 14:00 | 15382.5 | 4.9413 | 88.2248 | 59.8258 | 4508.1657 |  | 5318 | 19144800 | 50680800 | 82216800 | 113752800
2035-03-03 15:00 | 17142.2 | 5.4417 | 88.6847 | 59.8258 | 5023.8829 |  | 5319 | 19148400 | 50684400 | 82220400 | 113756400
2035-03-04 16:00 | 17403.7 | 5.5266 | 89.1187 | 59.8258 | 5100.521 |  | 5320 | 19152000 | 50688000 | 82224000 | 113760000
2035-03-05 17:00 | 16886.7 | 5.3298 | 89.5153 | 59.8258 | 4949.0032 |  | 5321 | 19155600 | 50691600 | 82227600 | 113763600
2035-03-06 18:00 | 14919.9 | 4.6732 | 89.7863 | 59.8258 | 4372.5911 |  | 5322 | 19159200 | 50695200 | 82231200 | 113767200
2035-03-07 19:00 | 13173.7 | 4.0975 | 89.8019 | 59.8258 | 3860.8304 |  | 5323 | 19162800 | 50698800 | 82234800 | 113770800
2035-03-08 20:00 | 10382.2 | 3.2155 | 89.6775 | 59.8258 | 3042.7225 |  | 5324 | 19166400 | 50702400 | 82238400 | 113774400
2035-03-09 21:00 | 8930.69 | 2.7432 | 89.3467 | 59.8258 | 2617.3269 |  | 5325 | 19170000 | 50706000 | 82242000 | 113778000
2035-03-10 22:00 | 6874.43 | 2.0098 | 89.6733 | 59.8258 | 2014.6966 |  | 5326 | 19173600 | 50709600 | 82245600 | 113781600
2035-03-11 23:00 | 5344.53 | 1.6058 | 88.7264 | 59.8258 | 1566.3271 |  | 5327 | 19177200 | 50713200 | 82249200 | 113785200
2035-03-13 | 4570.5 | 1.3734 | 88.1948 | 59.8258 | 1339.4813 |  | 5328 | 19180800 | 50716800 | 82252800 | 113788800
2035-03-14 01:00 | 3876.88 | 1.1949 | 87.3759 | 59.8258 | 1136.2014 |  | 5329 | 19184400 | 50720400 | 82256400 | 113792400
2035-03-15 02:00 | 3402.65 | 1.0642 | 86.7793 | 59.8258 | 997.2183 |  | 5330 | 19188000 | 50724000 | 82260000 | 113796000
2035-03-16 03:00 | 3189.97 | 1 | 87.3664 | 59.8258 | 934.8879 |  | 5331 | 19191600 | 50727600 | 82263600 | 113799600
2035-03-17 04:00 | 3161.6 | 1 | 88.6239 | 59.8258 | 926.5735 |  | 5332 | 19195200 | 50731200 | 82267200 | 113803200
2035-03-18 05:00 | 3131.8 | 1 | 88.6067 | 59.8258 | 917.84 |  | 5333 | 19198800 | 50734800 | 82270800 | 113806800
2035-03-19 06:00 | 4619.09 | 1.4631 | 85.4529 | 59.8258 | 1353.7216 |  | 5334 | 19202400 | 50738400 | 82274400 | 113810400
2035-03-20 07:00 | 6018.71 | 1.9887 | 84.8788 | 59.8258 | 1763.9098 |  | 5335 | 19206000 | 50742000 | 82278000 | 113814000
2035-03-21 08:00 | 6138.86 | 1.8581 | 86.312 | 59.8258 | 1799.1223 |  | 5336 | 19209600 | 50745600 | 82281600 | 113817600
2035-03-22 09:00 | 6807.41 | 2.0883 | 86.1581 | 59.8258 | 1995.0549 |  | 5337 | 19213200 | 50749200 | 82285200 | 113821200
2035-03-23 10:00 | 6909.63 | 2.2176 | 85.5967 | 59.8258 | 2025.0127 |  | 5338 | 19216800 | 50752800 | 82288800 | 113824800
2035-03-24 11:00 | 7857.65 | 2.6032 | 85.2172 | 59.8258 | 2302.8499 |  | 5339 | 19220400 | 50756400 | 82292400 | 113828400
2035-03-25 12:00 | 7567.25 | 2.4816 | 85.4922 | 59.8258 | 2217.7421 |  | 5340 | 19224000 | 50760000 | 82296000 | 113832000
2035-03-26 13:00 | 8361.24 | 2.6756 | 85.8399 | 59.8258 | 2450.4376 |  | 5341 | 19227600 | 50763600 | 82299600 | 113835600
2035-03-27 14:00 | 8995.58 | 2.8742 | 85.949 | 59.8258 | 2636.3443 |  | 5342 | 19231200 | 50767200 | 82303200 | 113839200
2035-03-28 15:00 | 9694.57 | 3.0809 | 86.1342 | 59.8258 | 2841.198 |  | 5343 | 19234800 | 50770800 | 82306800 | 113842800
2035-03-29 16:00 | 12047.1 | 4.0071 | 85.6209 | 59.8258 | 3530.6565 |  | 5344 | 19238400 | 50774400 | 82310400 | 113846400
2035-03-30 17:00 | 10759.2 | 3.4357 | 86.5803 | 59.8258 | 3153.2103 |  | 5345 | 19242000 | 50778000 | 82314000 | 113850000
2035-03-31 18:00 | 9463.57 | 2.8918 | 87.2871 | 59.8258 | 2773.4986 |  | 5346 | 19245600 | 50781600 | 82317600 | 113853600
2035-04-01 19:00 | 8095.18 | 2.4754 | 87.1415 | 59.8258 | 2372.4631 |  | 5347 | 19249200 | 50785200 | 82321200 | 113857200
2035-04-02 20:00 | 6930.04 | 2.1922 | 86.4549 | 59.8258 | 2030.9942 |  | 5348 | 19252800 | 50788800 | 82324800 | 113860800
2035-04-03 21:00 | 6038.61 | 1.8782 | 86.4663 | 59.8258 | 1769.7419 |  | 5349 | 19256400 | 50792400 | 82328400 | 113864400
2035-04-04 22:00 | 5376.63 | 1.6984 | 85.9632 | 59.8258 | 1575.7347 |  | 5350 | 19260000 | 50796000 | 82332000 | 113868000
2035-04-05 23:00 | 3207.21 | 1 | 95.2349 | 59.8258 | 939.9405 |  | 5351 | 19263600 | 50799600 | 82335600 | 113871600
2035-04-07 | 3088.8 | 1 | 70.5573 | 59.8258 | 905.2379 |  | 5352 | 19267200 | 50803200 | 82339200 | 113875200
2035-04-08 01:00 | 3116.93 | 1 | 70.2868 | 59.8258 | 913.482 |  | 5353 | 19270800 | 50806800 | 82342800 | 113878800
2035-04-09 02:00 | 3055.75 | 1 | 70.1244 | 59.8258 | 895.5519 |  | 5354 | 19274400 | 50810400 | 82346400 | 113882400
2035-04-10 03:00 | 3115.29 | 1 | 69.9585 | 59.8258 | 913.0014 |  | 5355 | 19278000 | 50814000 | 82350000 | 113886000
2035-04-11 04:00 | 0 | 0 | 70.0779 | 59.8258 | 0 |  | 5356 | 19281600 | 50817600 | 82353600 | 113889600
2035-04-12 05:00 | 2423.74 | 1 | 69.3307 | 59.8258 | 710.3281 |  | 5357 | 19285200 | 50821200 | 82357200 | 113893200
2035-04-13 06:00 | 1946.43 | 1 | 81.6161 | 59.8258 | 570.4423 |  | 5358 | 19288800 | 50824800 | 82360800 | 113896800
2035-04-14 07:00 | 2744.78 | 1.0389 | 81.4913 | 59.8258 | 804.4156 |  | 5359 | 19292400 | 50828400 | 82364400 | 113900400
2035-04-15 08:00 | 2967.22 | 1 | 91.3482 | 59.8258 | 869.6063 |  | 5360 | 19296000 | 50832000 | 82368000 | 113904000
2035-04-16 09:00 | 3041.57 | 1 | 85.3001 | 59.8258 | 891.3962 |  | 5361 | 19299600 | 50835600 | 82371600 | 113907600
2035-04-17 10:00 | 3834.04 | 1.2396 | 83.4382 | 59.8258 | 1123.6462 |  | 5362 | 19303200 | 50839200 | 82375200 | 113911200
2035-04-18 11:00 | 4928.46 | 1.5863 | 83.5443 | 59.8258 | 1444.389 |  | 5363 | 19306800 | 50842800 | 82378800 | 113914800
2035-04-19 12:00 | 5360.88 | 1.7422 | 83.559 | 59.8258 | 1571.1188 |  | 5364 | 19310400 | 50846400 | 82382400 | 113918400
2035-04-20 13:00 | 5794.11 | 1.8925 | 83.5844 | 59.8258 | 1698.086 |  | 5365 | 19314000 | 50850000 | 82386000 | 113922000
2035-04-21 14:00 | 6516.61 | 2.1547 | 83.4938 | 59.8258 | 1909.8299 |  | 5366 | 19317600 | 50853600 | 82389600 | 113925600
2035-04-22 15:00 | 7114.87 | 2.293 | 83.9763 | 59.8258 | 2085.1626 |  | 5367 | 19321200 | 50857200 | 82393200 | 113929200
2035-04-23 16:00 | 9858.55 | 3.3304 | 83.4648 | 59.8258 | 2889.2558 |  | 5368 | 19324800 | 50860800 | 82396800 | 113932800
2035-04-24 17:00 | 9316.43 | 3.0128 | 84.5001 | 59.8258 | 2730.3761 |  | 5369 | 19328400 | 50864400 | 82400400 | 113936400
2035-04-25 18:00 | 8579.61 | 2.6809 | 85.1848 | 59.8258 | 2514.4355 |  | 5370 | 19332000 | 50868000 | 82404000 | 113940000
2035-04-26 19:00 | 7276.34 | 2.2475 | 85.3836 | 59.8258 | 2132.4847 |  | 5371 | 19335600 | 50871600 | 82407600 | 113943600
2035-04-27 20:00 | 6221.02 | 1.8944 | 85.5079 | 59.8258 | 1823.201 |  | 5372 | 19339200 | 50875200 | 82411200 | 113947200
2035-04-28 21:00 | 5359.17 | 1.6002 | 85.6704 | 59.8258 | 1570.6177 |  | 5373 | 19342800 | 50878800 | 82414800 | 113950800
2035-04-29 22:00 | 4493.46 | 1.3916 | 84.916 | 59.8258 | 1316.9031 |  | 5374 | 19346400 | 50882400 | 82418400 | 113954400
2035-04-30 23:00 | 3199.59 | 1 | 69.6691 | 59.8258 | 937.7073 |  | 5375 | 19350000 | 50886000 | 82422000 | 113958000
2035-05-02 | 3168.07 | 1 | 69.3756 | 59.8258 | 928.4697 |  | 5376 | 19353600 | 50889600 | 82425600 | 113961600
2035-05-03 01:00 | 3075.37 | 1 | 69.2093 | 59.8258 | 901.302 |  | 5377 | 19357200 | 50893200 | 82429200 | 113965200
2035-05-04 02:00 | 1024.35 | 1 | 69.2715 | 59.8258 | 300.2074 |  | 5378 | 19360800 | 50896800 | 82432800 | 113968800
2035-05-05 03:00 | 1380.22 | 1 | 68.8551 | 59.8258 | 404.5026 |  | 5379 | 19364400 | 50900400 | 82436400 | 113972400
2035-05-06 04:00 | 2726.71 | 1 | 68.5237 | 59.8258 | 799.1198 |  | 5380 | 19368000 | 50904000 | 82440000 | 113976000
2035-05-07 05:00 | 3194.46 | 1 | 68.5272 | 59.8258 | 936.2038 |  | 5381 | 19371600 | 50907600 | 82443600 | 113979600
2035-05-08 06:00 | 3208.54 | 1 | 68.5531 | 59.8258 | 940.3303 |  | 5382 | 19375200 | 50911200 | 82447200 | 113983200
2035-05-09 07:00 | 3252.41 | 1 | 89.4998 | 59.8258 | 953.1873 |  | 5383 | 19378800 | 50914800 | 82450800 | 113986800
2035-05-10 08:00 | 3273.41 | 1 | 84.0063 | 59.8258 | 959.3418 |  | 5384 | 19382400 | 50918400 | 82454400 | 113990400
2035-05-11 09:00 | 5360.91 | 1.6942 | 83.2456 | 59.8258 | 1571.1276 |  | 5385 | 19386000 | 50922000 | 82458000 | 113994000
2035-05-12 10:00 | 7193 | 2.3833 | 82.8238 | 59.8258 | 2108.0602 |  | 5386 | 19389600 | 50925600 | 82461600 | 113997600
2035-05-13 11:00 | 8771.6 | 2.9019 | 83.2136 | 59.8258 | 2570.7022 |  | 5387 | 19393200 | 50929200 | 82465200 | 114001200
2035-05-14 12:00 | 10115.6 | 3.2731 | 83.9268 | 59.8258 | 2964.5897 |  | 5388 | 19396800 | 50932800 | 82468800 | 114004800
2035-05-15 13:00 | 10496.3 | 3.3707 | 84.4667 | 59.8258 | 3076.1619 |  | 5389 | 19400400 | 50936400 | 82472400 | 114008400
2035-05-16 14:00 | 11181.2 | 3.6008 | 84.7944 | 59.8258 | 3276.8862 |  | 5390 | 19404000 | 50940000 | 82476000 | 114012000
2035-05-17 15:00 | 12952.4 | 4.2017 | 85.0197 | 59.8258 | 3795.9737 |  | 5391 | 19407600 | 50943600 | 82479600 | 114015600
2035-05-18 16:00 | 13281.8 | 4.3071 | 85.4664 | 59.8258 | 3892.5113 |  | 5392 | 19411200 | 50947200 | 82483200 | 114019200
2035-05-19 17:00 | 13271.5 | 4.2351 | 86.0267 | 59.8258 | 3889.4927 |  | 5393 | 19414800 | 50950800 | 82486800 | 114022800
2035-05-20 18:00 | 11758.8 | 3.7001 | 86.4679 | 59.8258 | 3446.1641 |  | 5394 | 19418400 | 50954400 | 82490400 | 114026400
2035-05-21 19:00 | 10106.8 | 3.1265 | 86.7472 | 59.8258 | 2962.0107 |  | 5395 | 19422000 | 50958000 | 82494000 | 114030000
2035-05-22 20:00 | 7657.22 | 2.312 | 87.0023 | 59.8258 | 2244.1097 |  | 5396 | 19425600 | 50961600 | 82497600 | 114033600
2035-05-23 21:00 | 6641.01 | 1.9486 | 87.0856 | 59.8258 | 1946.2879 |  | 5397 | 19429200 | 50965200 | 82501200 | 114037200
2035-05-24 22:00 | 4508.57 | 1.3374 | 86.6049 | 59.8258 | 1321.3314 |  | 5398 | 19432800 | 50968800 | 82504800 | 114040800
2035-05-25 23:00 | 3699.39 | 1.1038 | 86.0494 | 59.8258 | 1084.1842 |  | 5399 | 19436400 | 50972400 | 82508400 | 114044400
2035-05-27 | 3247.82 | 1 | 85.4446 | 59.8258 | 951.8421 |  | 5400 | 19440000 | 50976000 | 82512000 | 114048000
2035-05-28 01:00 | 3194.92 | 1 | 86.7956 | 59.8258 | 936.3386 |  | 5401 | 19443600 | 50979600 | 82515600 | 114051600
2035-05-29 02:00 | 3207.43 | 1 | 88.274 | 59.8258 | 940.0049 |  | 5402 | 19447200 | 50983200 | 82519200 | 114055200
2035-05-30 03:00 | 3187.44 | 1 | 86.4636 | 59.8258 | 934.1465 |  | 5403 | 19450800 | 50986800 | 82522800 | 114058800
2035-05-31 04:00 | 3143.61 | 1 | 85.3213 | 59.8258 | 921.3011 |  | 5404 | 19454400 | 50990400 | 82526400 | 114062400
2035-06-01 05:00 | 3722.2 | 1.1635 | 83.9799 | 59.8258 | 1090.8691 |  | 5405 | 19458000 | 50994000 | 82530000 | 114066000
2035-06-02 06:00 | 3836.04 | 1.1917 | 84.0469 | 59.8258 | 1124.2323 |  | 5406 | 19461600 | 50997600 | 82533600 | 114069600
2035-06-03 07:00 | 4882.03 | 1.5168 | 84.012 | 59.8258 | 1430.7818 |  | 5407 | 19465200 | 51001200 | 82537200 | 114073200
2035-06-04 08:00 | 5120.29 | 1.6624 | 83.4923 | 59.8258 | 1500.6089 |  | 5408 | 19468800 | 51004800 | 82540800 | 114076800
2035-06-05 09:00 | 6681.21 | 2.2586 | 83.0087 | 59.8258 | 1958.0694 |  | 5409 | 19472400 | 51008400 | 82544400 | 114080400
2035-06-06 10:00 | 8355.13 | 2.8437 | 83.162 | 59.8258 | 2448.6469 |  | 5410 | 19476000 | 51012000 | 82548000 | 114084000
2035-06-07 11:00 | 9715.57 | 3.2439 | 83.7788 | 59.8258 | 2847.3525 |  | 5411 | 19479600 | 51015600 | 82551600 | 114087600
2035-06-08 12:00 | 10647.9 | 3.4911 | 84.4159 | 59.8258 | 3120.5914 |  | 5412 | 19483200 | 51019200 | 82555200 | 114091200
2035-06-09 13:00 | 11361.9 | 3.6882 | 84.9071 | 59.8258 | 3329.8442 |  | 5413 | 19486800 | 51022800 | 82558800 | 114094800
2035-06-10 14:00 | 12085.7 | 3.8883 | 85.3695 | 59.8258 | 3541.969 |  | 5414 | 19490400 | 51026400 | 82562400 | 114098400
2035-06-11 15:00 | 13842.1 | 4.4201 | 85.7823 | 59.8258 | 4056.7191 |  | 5415 | 19494000 | 51030000 | 82566000 | 114102000
2035-06-12 16:00 | 13993.2 | 4.4857 | 86.1667 | 59.8258 | 4101.0021 |  | 5416 | 19497600 | 51033600 | 82569600 | 114105600
2035-06-13 17:00 | 13522.6 | 4.3207 | 86.5178 | 59.8258 | 3963.0829 |  | 5417 | 19501200 | 51037200 | 82573200 | 114109200
2035-06-14 18:00 | 11549.3 | 3.5986 | 87.0529 | 59.8258 | 3384.7657 |  | 5418 | 19504800 | 51040800 | 82576800 | 114112800
2035-06-15 19:00 | 9885.19 | 3.0961 | 86.8876 | 59.8258 | 2897.0632 |  | 5419 | 19508400 | 51044400 | 82580400 | 114116400
2035-06-16 20:00 | 7610.1 | 2.3099 | 87.172 | 59.8258 | 2230.3001 |  | 5420 | 19512000 | 51048000 | 82584000 | 114120000
2035-06-17 21:00 | 6494.34 | 1.9754 | 86.7593 | 59.8258 | 1903.3032 |  | 5421 | 19515600 | 51051600 | 82587600 | 114123600
2035-06-18 22:00 | 4377.56 | 1.2797 | 87.0229 | 59.8258 | 1282.9362 |  | 5422 | 19519200 | 51055200 | 82591200 | 114127200
2035-06-19 23:00 | 3308.21 | 1.0243 | 85.6592 | 59.8258 | 969.5406 |  | 5423 | 19522800 | 51058800 | 82594800 | 114130800
2035-06-21 | 3235.3 | 1 | 90.2689 | 59.8258 | 948.1728 |  | 5424 | 19526400 | 51062400 | 82598400 | 114134400
2035-06-22 01:00 | 3201.42 | 1 | 93.245 | 59.8258 | 938.2436 |  | 5425 | 19530000 | 51066000 | 82602000 | 114138000
2035-06-23 02:00 | 3194.07 | 1 | 93.966 | 59.8258 | 936.0895 |  | 5426 | 19533600 | 51069600 | 82605600 | 114141600
2035-06-24 03:00 | 3184.1 | 1 | 90.0102 | 59.8258 | 933.1676 |  | 5427 | 19537200 | 51073200 | 82609200 | 114145200
2035-06-25 04:00 | 3173.36 | 1 | 87.0478 | 59.8258 | 930.02 |  | 5428 | 19540800 | 51076800 | 82612800 | 114148800
2035-06-26 05:00 | 3675.16 | 1.154 | 84.0455 | 59.8258 | 1077.0831 |  | 5429 | 19544400 | 51080400 | 82616400 | 114152400
2035-06-27 06:00 | 3826.95 | 1.2021 | 84.0087 | 59.8258 | 1121.5683 |  | 5430 | 19548000 | 51084000 | 82620000 | 114156000
2035-06-28 07:00 | 4371.19 | 1.3545 | 84.1725 | 59.8258 | 1281.0693 |  | 5431 | 19551600 | 51087600 | 82623600 | 114159600
2035-06-29 08:00 | 3847.34 | 1.1864 | 84.285 | 59.8258 | 1127.5441 |  | 5432 | 19555200 | 51091200 | 82627200 | 114163200
2035-06-30 09:00 | 5166.55 | 1.6081 | 84.0671 | 59.8258 | 1514.1663 |  | 5433 | 19558800 | 51094800 | 82630800 | 114166800
2035-07-01 10:00 | 6043.1 | 1.9905 | 83.3796 | 59.8258 | 1771.0578 |  | 5434 | 19562400 | 51098400 | 82634400 | 114170400
2035-07-02 11:00 | 7033.65 | 2.3564 | 83.3161 | 59.8258 | 2061.3593 |  | 5435 | 19566000 | 51102000 | 82638000 | 114174000
2035-07-03 12:00 | 8004.83 | 2.6617 | 83.6146 | 59.8258 | 2345.9841 |  | 5436 | 19569600 | 51105600 | 82641600 | 114177600
2035-07-04 13:00 | 8322.16 | 2.6847 | 84.2621 | 59.8258 | 2438.9843 |  | 5437 | 19573200 | 51109200 | 82645200 | 114181200
2035-07-05 14:00 | 8884.86 | 2.8888 | 84.3329 | 59.8258 | 2603.8954 |  | 5438 | 19576800 | 51112800 | 82648800 | 114184800
2035-07-06 15:00 | 10381.4 | 3.3839 | 84.4533 | 59.8258 | 3042.488 |  | 5439 | 19580400 | 51116400 | 82652400 | 114188400
2035-07-07 16:00 | 10952.1 | 3.5823 | 84.7004 | 59.8258 | 3209.7437 |  | 5440 | 19584000 | 51120000 | 82656000 | 114192000
2035-07-08 17:00 | 10387.9 | 3.3133 | 85.3078 | 59.8258 | 3044.393 |  | 5441 | 19587600 | 51123600 | 82659600 | 114195600
2035-07-09 18:00 | 9199.16 | 2.9255 | 85.4385 | 59.8258 | 2696.0077 |  | 5442 | 19591200 | 51127200 | 82663200 | 114199200
2035-07-10 19:00 | 7906.94 | 2.4684 | 85.6509 | 59.8258 | 2317.2954 |  | 5443 | 19594800 | 51130800 | 82666800 | 114202800
2035-07-11 20:00 | 5775.89 | 1.6975 | 86.4378 | 59.8258 | 1692.7463 |  | 5444 | 19598400 | 51134400 | 82670400 | 114206400
2035-07-12 21:00 | 4480.29 | 1.3518 | 85.6917 | 59.8258 | 1313.0434 |  | 5445 | 19602000 | 51138000 | 82674000 | 114210000
2035-07-13 22:00 | 3116.5 | 1 | 93.5631 | 59.8258 | 913.356 |  | 5446 | 19605600 | 51141600 | 82677600 | 114213600
2035-07-14 23:00 | 3006.9 | 1 | 69.546 | 59.8258 | 881.2354 |  | 5447 | 19609200 | 51145200 | 82681200 | 114217200
2035-07-16 | 2541.19 | 1 | 69.3372 | 59.8258 | 744.7493 |  | 5448 | 19612800 | 51148800 | 82684800 | 114220800
2035-07-17 01:00 | 93.194 | 1 | 69.3146 | 59.8258 | 27.3125 |  | 5449 | 19616400 | 51152400 | 82688400 | 114224400
2035-07-18 02:00 | -215.375 | 1.0592 | 67.8858 | 59.8258 | -63.1202 |  | 5450 | 19620000 | 51156000 | 82692000 | 114228000
2035-07-19 03:00 | -270.136 | 1.1616 | 67.3713 | 59.8258 | -79.169 |  | 5451 | 19623600 | 51159600 | 82695600 | 114231600
2035-07-20 04:00 | -246.65 | 1.0961 | 67.1488 | 59.8258 | -72.286 |  | 5452 | 19627200 | 51163200 | 82699200 | 114235200
2035-07-21 05:00 | 15.2221 | 1 | 67.9388 | 59.8258 | 4.4612 |  | 5453 | 19630800 | 51166800 | 82702800 | 114238800
2035-07-22 06:00 | 284.641 | 1 | 67.734 | 59.8258 | 83.42 |  | 5454 | 19634400 | 51170400 | 82706400 | 114242400
2035-07-23 07:00 | 2656.11 | 1 | 67.423 | 59.8258 | 778.429 |  | 5455 | 19638000 | 51174000 | 82710000 | 114246000
2035-07-24 08:00 | 3082.89 | 1 | 67.6194 | 59.8258 | 903.5059 |  | 5456 | 19641600 | 51177600 | 82713600 | 114249600
2035-07-25 09:00 | 3209.2 | 1 | 84.5726 | 59.8258 | 940.5237 |  | 5457 | 19645200 | 51181200 | 82717200 | 114253200
2035-07-26 10:00 | 5041.08 | 1.5679 | 82.7796 | 59.8258 | 1477.3947 |  | 5458 | 19648800 | 51184800 | 82720800 | 114256800
2035-07-27 11:00 | 6923.01 | 2.2763 | 82.2545 | 59.8258 | 2028.9339 |  | 5459 | 19652400 | 51188400 | 82724400 | 114260400
2035-07-28 12:00 | 8277.76 | 2.7016 | 82.7664 | 59.8258 | 2425.972 |  | 5460 | 19656000 | 51192000 | 82728000 | 114264000
2035-07-29 13:00 | 8831.98 | 2.9019 | 83.0662 | 59.8258 | 2588.3978 |  | 5461 | 19659600 | 51195600 | 82731600 | 114267600
2035-07-30 14:00 | 9698.51 | 3.1712 | 83.4474 | 59.8258 | 2842.3527 |  | 5462 | 19663200 | 51199200 | 82735200 | 114271200
2035-07-31 15:00 | 11668.4 | 3.774 | 83.9295 | 59.8258 | 3419.6705 |  | 5463 | 19666800 | 51202800 | 82738800 | 114274800
2035-08-01 16:00 | 12203.1 | 3.9417 | 84.4343 | 59.8258 | 3576.3756 |  | 5464 | 19670400 | 51206400 | 82742400 | 114278400
2035-08-02 17:00 | 11828.1 | 3.7946 | 84.913 | 59.8258 | 3466.4739 |  | 5465 | 19674000 | 51210000 | 82746000 | 114282000
2035-08-03 18:00 | 10120.3 | 3.1971 | 85.3543 | 59.8258 | 2965.9671 |  | 5466 | 19677600 | 51213600 | 82749600 | 114285600
2035-08-04 19:00 | 8425.49 | 2.642 | 85.4285 | 59.8258 | 2469.2674 |  | 5467 | 19681200 | 51217200 | 82753200 | 114289200
2035-08-05 20:00 | 6052.38 | 1.8211 | 85.8894 | 59.8258 | 1773.7775 |  | 5468 | 19684800 | 51220800 | 82756800 | 114292800
2035-08-06 21:00 | 4720.34 | 1.4055 | 85.6884 | 59.8258 | 1383.3951 |  | 5469 | 19688400 | 51224400 | 82760400 | 114296400
2035-08-07 22:00 | 3147.83 | 1 | 91.7085 | 59.8258 | 922.5379 |  | 5470 | 19692000 | 51228000 | 82764000 | 114300000
2035-08-08 23:00 | 3168.7 | 1 | 69.2677 | 59.8258 | 928.6543 |  | 5471 | 19695600 | 51231600 | 82767600 | 114303600
2035-08-10 | 3100.51 | 1 | 69.0136 | 59.8258 | 908.6698 |  | 5472 | 19699200 | 51235200 | 82771200 | 114307200
2035-08-11 01:00 | 0 | 0 | 69.1153 | 59.8258 | 0 |  | 5473 | 19702800 | 51238800 | 82774800 | 114310800
2035-08-12 02:00 | 68.4488 | 1 | 68.5591 | 59.8258 | 20.0604 |  | 5474 | 19706400 | 51242400 | 82778400 | 114314400
2035-08-13 03:00 | 76.8184 | 1 | 68.2039 | 59.8258 | 22.5133 |  | 5475 | 19710000 | 51246000 | 82782000 | 114318000
2035-08-14 04:00 | 524.568 | 1 | 67.9411 | 59.8258 | 153.7357 |  | 5476 | 19713600 | 51249600 | 82785600 | 114321600
2035-08-15 05:00 | 2187.06 | 1 | 67.6266 | 59.8258 | 640.964 |  | 5477 | 19717200 | 51253200 | 82789200 | 114325200
2035-08-16 06:00 | 2858.67 | 1 | 67.6213 | 59.8258 | 837.7935 |  | 5478 | 19720800 | 51256800 | 82792800 | 114328800
2035-08-17 07:00 | 3163.62 | 1 | 67.7044 | 59.8258 | 927.1655 |  | 5479 | 19724400 | 51260400 | 82796400 | 114332400
2035-08-18 08:00 | 3190.82 | 1 | 84.89 | 59.8258 | 935.137 |  | 5480 | 19728000 | 51264000 | 82800000 | 114336000
2035-08-19 09:00 | 5364.04 | 1.6337 | 83.0949 | 59.8258 | 1572.0449 |  | 5481 | 19731600 | 51267600 | 82803600 | 114339600
2035-08-20 10:00 | 7239.7 | 2.4003 | 82.1929 | 59.8258 | 2121.7466 |  | 5482 | 19735200 | 51271200 | 82807200 | 114343200
2035-08-21 11:00 | 9066.06 | 2.9918 | 82.6513 | 59.8258 | 2656.9999 |  | 5483 | 19738800 | 51274800 | 82810800 | 114346800
2035-08-22 12:00 | 10445 | 3.3994 | 83.2776 | 59.8258 | 3061.1273 |  | 5484 | 19742400 | 51278400 | 82814400 | 114350400
2035-08-23 13:00 | 11098.2 | 3.5728 | 83.9116 | 59.8258 | 3252.5613 |  | 5485 | 19746000 | 51282000 | 82818000 | 114354000
2035-08-24 14:00 | 11824.1 | 3.8155 | 84.2959 | 59.8258 | 3465.3016 |  | 5486 | 19749600 | 51285600 | 82821600 | 114357600
2035-08-25 15:00 | 13540.1 | 4.3258 | 84.7964 | 59.8258 | 3968.2116 |  | 5487 | 19753200 | 51289200 | 82825200 | 114361200
2035-08-26 16:00 | 13998 | 4.4521 | 85.3427 | 59.8258 | 4102.4088 |  | 5488 | 19756800 | 51292800 | 82828800 | 114364800
2035-08-27 17:00 | 13821.5 | 4.3783 | 85.7703 | 59.8258 | 4050.6818 |  | 5489 | 19760400 | 51296400 | 82832400 | 114368400
2035-08-28 18:00 | 12163.1 | 3.7906 | 86.2531 | 59.8258 | 3564.6527 |  | 5490 | 19764000 | 51300000 | 82836000 | 114372000
2035-08-29 19:00 | 10266.7 | 3.2108 | 86.2164 | 59.8258 | 3008.8728 |  | 5491 | 19767600 | 51303600 | 82839600 | 114375600
2035-08-30 20:00 | 7900.53 | 2.3668 | 86.7259 | 59.8258 | 2315.4168 |  | 5492 | 19771200 | 51307200 | 82843200 | 114379200
2035-08-31 21:00 | 6662.31 | 1.9927 | 86.4026 | 59.8258 | 1952.5303 |  | 5493 | 19774800 | 51310800 | 82846800 | 114382800
2035-09-01 22:00 | 4452.56 | 1.3025 | 86.4214 | 59.8258 | 1304.9165 |  | 5494 | 19778400 | 51314400 | 82850400 | 114386400
2035-09-02 23:00 | 3250.12 | 1 | 87.8328 | 59.8258 | 952.5161 |  | 5495 | 19782000 | 51318000 | 82854000 | 114390000
2035-09-04 | 3245.96 | 1 | 94.8709 | 59.8258 | 951.297 |  | 5496 | 19785600 | 51321600 | 82857600 | 114393600
2035-09-05 01:00 | 3142.56 | 1 | 69.2972 | 59.8258 | 920.9934 |  | 5497 | 19789200 | 51325200 | 82861200 | 114397200
2035-09-06 02:00 | 3108.82 | 1 | 69.1177 | 59.8258 | 911.1052 |  | 5498 | 19792800 | 51328800 | 82864800 | 114400800
2035-09-07 03:00 | 3098.35 | 1 | 68.937 | 59.8258 | 908.0367 |  | 5499 | 19796400 | 51332400 | 82868400 | 114404400
2035-09-08 04:00 | 3131.85 | 1 | 68.7987 | 59.8258 | 917.8546 |  | 5500 | 19800000 | 51336000 | 82872000 | 114408000
2035-09-09 05:00 | 1611.76 | 1 | 68.8248 | 59.8258 | 472.3602 |  | 5501 | 19803600 | 51339600 | 82875600 | 114411600
2035-09-10 06:00 | 3215.54 | 1 | 68.3724 | 59.8258 | 942.3817 |  | 5502 | 19807200 | 51343200 | 82879200 | 114415200
2035-09-11 07:00 | 3544.17 | 1.0772 | 83.7312 | 59.8258 | 1038.6937 |  | 5503 | 19810800 | 51346800 | 82882800 | 114418800
2035-09-12 08:00 | 3908.42 | 1.2098 | 83.4593 | 59.8258 | 1145.4448 |  | 5504 | 19814400 | 51350400 | 82886400 | 114422400
2035-09-13 09:00 | 5422.06 | 1.6843 | 83.4144 | 59.8258 | 1589.0489 |  | 5505 | 19818000 | 51354000 | 82890000 | 114426000
2035-09-14 10:00 | 7210.61 | 2.376 | 82.7575 | 59.8258 | 2113.2212 |  | 5506 | 19821600 | 51357600 | 82893600 | 114429600
2035-09-15 11:00 | 8857.1 | 2.912 | 83.151 | 59.8258 | 2595.7598 |  | 5507 | 19825200 | 51361200 | 82897200 | 114433200
2035-09-16 12:00 | 10220.2 | 3.3078 | 83.7531 | 59.8258 | 2995.2449 |  | 5508 | 19828800 | 51364800 | 82900800 | 114436800
2035-09-17 13:00 | 10817.9 | 3.4847 | 84.2234 | 59.8258 | 3170.4135 |  | 5509 | 19832400 | 51368400 | 82904400 | 114440400
2035-09-18 14:00 | 11481 | 3.6848 | 84.6098 | 59.8258 | 3364.749 |  | 5510 | 19836000 | 51372000 | 82908000 | 114444000
2035-09-19 15:00 | 12154.5 | 3.8397 | 85.1269 | 59.8258 | 3562.1323 |  | 5511 | 19839600 | 51375600 | 82911600 | 114447600
2035-09-20 16:00 | 14281.7 | 4.6746 | 84.8938 | 59.8258 | 4185.5531 |  | 5512 | 19843200 | 51379200 | 82915200 | 114451200
2035-09-21 17:00 | 13219.8 | 4.1969 | 85.8263 | 59.8258 | 3874.3409 |  | 5513 | 19846800 | 51382800 | 82918800 | 114454800
2035-09-22 18:00 | 11925.4 | 3.7379 | 86.1915 | 59.8258 | 3494.9897 |  | 5514 | 19850400 | 51386400 | 82922400 | 114458400
2035-09-23 19:00 | 10125.3 | 3.1789 | 86.164 | 59.8258 | 2967.4325 |  | 5515 | 19854000 | 51390000 | 82926000 | 114462000
2035-09-24 20:00 | 9000.35 | 2.7891 | 86.2204 | 59.8258 | 2637.7422 |  | 5516 | 19857600 | 51393600 | 82929600 | 114465600
2035-09-25 21:00 | 7840.05 | 2.4478 | 85.9504 | 59.8258 | 2297.6918 |  | 5517 | 19861200 | 51397200 | 82933200 | 114469200
2035-09-26 22:00 | 7167.04 | 2.1868 | 86.0502 | 59.8258 | 2100.4521 |  | 5518 | 19864800 | 51400800 | 82936800 | 114472800
2035-09-27 23:00 | 4052.51 | 1.1646 | 86.7718 | 59.8258 | 1187.6734 |  | 5519 | 19868400 | 51404400 | 82940400 | 114476400
2035-09-29 | 3277.21 | 1 | 86.8937 | 59.8258 | 960.4554 |  | 5520 | 19872000 | 51408000 | 82944000 | 114480000
2035-09-30 01:00 | 3236.72 | 1 | 91.6599 | 59.8258 | 948.589 |  | 5521 | 19875600 | 51411600 | 82947600 | 114483600
2035-10-01 02:00 | 3211.24 | 1 | 69.3912 | 59.8258 | 941.1215 |  | 5522 | 19879200 | 51415200 | 82951200 | 114487200
2035-10-02 03:00 | 3116.35 | 1 | 69.2071 | 59.8258 | 913.312 |  | 5523 | 19882800 | 51418800 | 82954800 | 114490800
2035-10-03 04:00 | 3119.67 | 1 | 68.9852 | 59.8258 | 914.285 |  | 5524 | 19886400 | 51422400 | 82958400 | 114494400
2035-10-04 05:00 | 3155.88 | 1 | 68.8529 | 59.8258 | 924.8971 |  | 5525 | 19890000 | 51426000 | 82962000 | 114498000
2035-10-05 06:00 | 3224.31 | 1 | 84.6137 | 59.8258 | 944.952 |  | 5526 | 19893600 | 51429600 | 82965600 | 114501600
2035-10-06 07:00 | 5264.35 | 1.617 | 83.8098 | 59.8258 | 1542.8287 |  | 5527 | 19897200 | 51433200 | 82969200 | 114505200
2035-10-07 08:00 | 5800.26 | 1.787 | 83.9707 | 59.8258 | 1699.8884 |  | 5528 | 19900800 | 51436800 | 82972800 | 114508800
2035-10-08 09:00 | 7220.24 | 2.3406 | 83.3884 | 59.8258 | 2116.0435 |  | 5529 | 19904400 | 51440400 | 82976400 | 114512400
2035-10-09 10:00 | 9201.67 | 3.0237 | 83.4332 | 59.8258 | 2696.7433 |  | 5530 | 19908000 | 51444000 | 82980000 | 114516000
2035-10-10 11:00 | 10864.2 | 3.5897 | 83.7808 | 59.8258 | 3183.9827 |  | 5531 | 19911600 | 51447600 | 82983600 | 114519600
2035-10-11 12:00 | 11875.6 | 3.8657 | 84.4758 | 59.8258 | 3480.3948 |  | 5532 | 19915200 | 51451200 | 82987200 | 114523200
2035-10-12 13:00 | 12474.9 | 4.059 | 84.8933 | 59.8258 | 3656.0323 |  | 5533 | 19918800 | 51454800 | 82990800 | 114526800
2035-10-13 14:00 | 13106.2 | 4.2576 | 85.2759 | 59.8258 | 3841.0481 |  | 5534 | 19922400 | 51458400 | 82994400 | 114530400
2035-10-14 15:00 | 13873 | 4.4527 | 85.7796 | 59.8258 | 4065.775 |  | 5535 | 19926000 | 51462000 | 82998000 | 114534000
2035-10-15 16:00 | 16381.2 | 5.299 | 85.9801 | 59.8258 | 4800.8558 |  | 5536 | 19929600 | 51465600 | 83001600 | 114537600
2035-10-16 17:00 | 15558.8 | 4.9126 | 86.9014 | 59.8258 | 4559.8342 |  | 5537 | 19933200 | 51469200 | 83005200 | 114541200
2035-10-17 18:00 | 14131.9 | 4.386 | 87.4404 | 59.8258 | 4141.6511 |  | 5538 | 19936800 | 51472800 | 83008800 | 114544800
2035-10-18 19:00 | 12130.3 | 3.7658 | 87.4756 | 59.8258 | 3555.04 |  | 5539 | 19940400 | 51476400 | 83012400 | 114548400
2035-10-19 20:00 | 10833.6 | 3.3286 | 87.4986 | 59.8258 | 3175.0147 |  | 5540 | 19944000 | 51480000 | 83016000 | 114552000
2035-10-20 21:00 | 9693.86 | 2.9646 | 87.4019 | 59.8258 | 2840.9899 |  | 5541 | 19947600 | 51483600 | 83019600 | 114555600
2035-10-21 22:00 | 8688.12 | 2.6643 | 87.1161 | 59.8258 | 2546.2366 |  | 5542 | 19951200 | 51487200 | 83023200 | 114559200
2035-10-22 23:00 | 6165.12 | 1.7864 | 87.7411 | 59.8258 | 1806.8183 |  | 5543 | 19954800 | 51490800 | 83026800 | 114562800
2035-10-24 | 5381.13 | 1.5544 | 87.3155 | 59.8258 | 1577.0535 |  | 5544 | 19958400 | 51494400 | 83030400 | 114566400
2035-10-25 01:00 | 4745.06 | 1.4217 | 86.3888 | 59.8258 | 1390.6398 |  | 5545 | 19962000 | 51498000 | 83034000 | 114570000
2035-10-26 02:00 | 4495.4 | 1.3676 | 85.8645 | 59.8258 | 1317.4717 |  | 5546 | 19965600 | 51501600 | 83037600 | 114573600
2035-10-27 03:00 | 4464.38 | 1.3905 | 85.2679 | 59.8258 | 1308.3806 |  | 5547 | 19969200 | 51505200 | 83041200 | 114577200
2035-10-28 04:00 | 4495.36 | 1.4441 | 84.6016 | 59.8258 | 1317.46 |  | 5548 | 19972800 | 51508800 | 83044800 | 114580800
2035-10-29 05:00 | 5116.2 | 1.6567 | 84.3502 | 59.8258 | 1499.4102 |  | 5549 | 19976400 | 51512400 | 83048400 | 114584400
2035-10-30 06:00 | 5346.41 | 1.7248 | 84.3775 | 59.8258 | 1566.8781 |  | 5550 | 19980000 | 51516000 | 83052000 | 114588000
2035-10-31 07:00 | 6377.89 | 2.0968 | 84.0986 | 59.8258 | 1869.175 |  | 5551 | 19983600 | 51519600 | 83055600 | 114591600
2035-11-01 08:00 | 7203.08 | 2.29 | 84.6822 | 59.8258 | 2111.0144 |  | 5552 | 19987200 | 51523200 | 83059200 | 114595200
2035-11-02 09:00 | 9060.78 | 2.9782 | 84.3612 | 59.8258 | 2655.4525 |  | 5553 | 19990800 | 51526800 | 83062800 | 114598800
2035-11-03 10:00 | 11003.3 | 3.6002 | 84.7377 | 59.8258 | 3224.7489 |  | 5554 | 19994400 | 51530400 | 83066400 | 114602400
2035-11-04 11:00 | 12916.4 | 4.2729 | 85.025 | 59.8258 | 3785.4232 |  | 5555 | 19998000 | 51534000 | 83070000 | 114606000
2035-11-05 12:00 | 14199.3 | 4.5464 | 86.0052 | 59.8258 | 4161.404 |  | 5556 | 20001600 | 51537600 | 83073600 | 114609600
2035-11-06 13:00 | 14599.7 | 4.7642 | 86.2388 | 59.8258 | 4278.7497 |  | 5557 | 20005200 | 51541200 | 83077200 | 114613200
2035-11-07 14:00 | 15177.5 | 4.9192 | 86.7293 | 59.8258 | 4448.0862 |  | 5558 | 20008800 | 51544800 | 83080800 | 114616800
2035-11-08 15:00 | 16943.9 | 5.4423 | 87.2061 | 59.8258 | 4965.7669 |  | 5559 | 20012400 | 51548400 | 83084400 | 114620400
2035-11-09 16:00 | 17503.1 | 5.5443 | 87.8856 | 59.8258 | 5129.6522 |  | 5560 | 20016000 | 51552000 | 83088000 | 114624000
2035-11-10 17:00 | 17436.2 | 5.4364 | 88.5131 | 59.8258 | 5110.0458 |  | 5561 | 20019600 | 51555600 | 83091600 | 114627600
2035-11-11 18:00 | 15974.6 | 4.9155 | 88.994 | 59.8258 | 4681.6931 |  | 5562 | 20023200 | 51559200 | 83095200 | 114631200
2035-11-12 19:00 | 13827.8 | 4.279 | 88.9853 | 59.8258 | 4052.5281 |  | 5563 | 20026800 | 51562800 | 83098800 | 114634800
2035-11-13 20:00 | 11292.5 | 3.4345 | 89.1056 | 59.8258 | 3309.5051 |  | 5564 | 20030400 | 51566400 | 83102400 | 114638400
2035-11-14 21:00 | 9936.88 | 3.0136 | 88.7819 | 59.8258 | 2912.2121 |  | 5565 | 20034000 | 51570000 | 83106000 | 114642000
2035-11-15 22:00 | 7821.37 | 2.318 | 88.7791 | 59.8258 | 2292.2173 |  | 5566 | 20037600 | 51573600 | 83109600 | 114645600
2035-11-16 23:00 | 6754 | 2.0574 | 87.8832 | 59.8258 | 1979.402 |  | 5567 | 20041200 | 51577200 | 83113200 | 114649200
2035-11-18 | 6054.29 | 1.8431 | 87.4602 | 59.8258 | 1774.3372 |  | 5568 | 20044800 | 51580800 | 83116800 | 114652800
2035-11-19 01:00 | 5685.1 | 1.6978 | 87.4069 | 59.8258 | 1666.1383 |  | 5569 | 20048400 | 51584400 | 83120400 | 114656400
2035-11-20 02:00 | 5596.59 | 1.6789 | 87.0726 | 59.8258 | 1640.1986 |  | 5570 | 20052000 | 51588000 | 83124000 | 114660000
2035-11-21 03:00 | 5550.45 | 1.7292 | 86.2862 | 59.8258 | 1626.6763 |  | 5571 | 20055600 | 51591600 | 83127600 | 114663600
2035-11-22 04:00 | 5671.64 | 1.7892 | 85.9344 | 59.8258 | 1662.1936 |  | 5572 | 20059200 | 51595200 | 83131200 | 114667200
2035-11-23 05:00 | 6354.99 | 2.0547 | 85.4497 | 59.8258 | 1862.4637 |  | 5573 | 20062800 | 51598800 | 83134800 | 114670800
2035-11-24 06:00 | 6427.35 | 2.0426 | 85.684 | 59.8258 | 1883.6703 |  | 5574 | 20066400 | 51602400 | 83138400 | 114674400
2035-11-25 07:00 | 7193.23 | 2.3343 | 85.3568 | 59.8258 | 2108.1276 |  | 5575 | 20070000 | 51606000 | 83142000 | 114678000
2035-11-26 08:00 | 7666.03 | 2.4318 | 85.7554 | 59.8258 | 2246.6916 |  | 5576 | 20073600 | 51609600 | 83145600 | 114681600
2035-11-27 09:00 | 9389.71 | 3.08 | 85.3635 | 59.8258 | 2751.8524 |  | 5577 | 20077200 | 51613200 | 83149200 | 114685200
2035-11-28 10:00 | 11359.7 | 3.7292 | 85.6176 | 59.8258 | 3329.1994 |  | 5578 | 20080800 | 51616800 | 83152800 | 114688800
2035-11-29 11:00 | 13064.4 | 4.2881 | 86.0167 | 59.8258 | 3828.7977 |  | 5579 | 20084400 | 51620400 | 83156400 | 114692400
2035-11-30 12:00 | 14364.3 | 4.6052 | 86.8006 | 59.8258 | 4209.7608 |  | 5580 | 20088000 | 51624000 | 83160000 | 114696000
2035-12-01 13:00 | 14163.8 | 4.5897 | 87.1034 | 59.8258 | 4151 |  | 5581 | 20091600 | 51627600 | 83163600 | 114699600
2035-12-02 14:00 | 14170.7 | 4.4947 | 87.6855 | 59.8258 | 4153.0222 |  | 5582 | 20095200 | 51631200 | 83167200 | 114703200
2035-12-03 15:00 | 14458.2 | 4.6191 | 87.7691 | 59.8258 | 4237.2801 |  | 5583 | 20098800 | 51634800 | 83170800 | 114706800
2035-12-04 16:00 | 13906.4 | 4.4833 | 87.8194 | 59.8258 | 4075.5635 |  | 5584 | 20102400 | 51638400 | 83174400 | 114710400
2035-12-05 17:00 | 13264.1 | 4.2361 | 87.9983 | 59.8258 | 3887.324 |  | 5585 | 20106000 | 51642000 | 83178000 | 114714000
2035-12-06 18:00 | 11687.6 | 3.6839 | 88.1559 | 59.8258 | 3425.2974 |  | 5586 | 20109600 | 51645600 | 83181600 | 114717600
2035-12-07 19:00 | 10525 | 3.2913 | 88.0963 | 59.8258 | 3084.573 |  | 5587 | 20113200 | 51649200 | 83185200 | 114721200
2035-12-08 20:00 | 8623.88 | 2.5712 | 88.6098 | 59.8258 | 2527.4097 |  | 5588 | 20116800 | 51652800 | 83188800 | 114724800
2035-12-09 21:00 | 7797.9 | 2.3426 | 88.1369 | 59.8258 | 2285.3389 |  | 5589 | 20120400 | 51656400 | 83192400 | 114728400
2035-12-10 22:00 | 5918.15 | 1.6944 | 88.5809 | 59.8258 | 1734.4386 |  | 5590 | 20124000 | 51660000 | 83196000 | 114732000
2035-12-11 23:00 | 5166.63 | 1.5229 | 87.6779 | 59.8258 | 1514.1898 |  | 5591 | 20127600 | 51663600 | 83199600 | 114735600
2035-12-13 | 4554.21 | 1.3776 | 86.8999 | 59.8258 | 1334.7072 |  | 5592 | 20131200 | 51667200 | 83203200 | 114739200
2035-12-14 01:00 | 4103.86 | 1.2894 | 86.0101 | 59.8258 | 1202.7226 |  | 5593 | 20134800 | 51670800 | 83206800 | 114742800
2035-12-15 02:00 | 3940.56 | 1.214 | 86.0143 | 59.8258 | 1154.8641 |  | 5594 | 20138400 | 51674400 | 83210400 | 114746400
2035-12-16 03:00 | 4298.3 | 1.3261 | 85.7454 | 59.8258 | 1259.7074 |  | 5595 | 20142000 | 51678000 | 83214000 | 114750000
2035-12-17 04:00 | 4527.81 | 1.4451 | 85.1265 | 59.8258 | 1326.9701 |  | 5596 | 20145600 | 51681600 | 83217600 | 114753600
2035-12-18 05:00 | 5286.3 | 1.7103 | 84.8441 | 59.8258 | 1549.2616 |  | 5597 | 20149200 | 51685200 | 83221200 | 114757200
2035-12-19 06:00 | 5399.78 | 1.7193 | 85.0901 | 59.8258 | 1582.5193 |  | 5598 | 20152800 | 51688800 | 83224800 | 114760800
2035-12-20 07:00 | 5967.24 | 1.9505 | 84.7138 | 59.8258 | 1748.8254 |  | 5599 | 20156400 | 51692400 | 83228400 | 114764400
2035-12-21 08:00 | 5846.85 | 1.8592 | 85.1683 | 59.8258 | 1713.5426 |  | 5600 | 20160000 | 51696000 | 83232000 | 114768000
2035-12-22 09:00 | 6928.17 | 2.3196 | 84.4328 | 59.8258 | 2030.4462 |  | 5601 | 20163600 | 51699600 | 83235600 | 114771600
2035-12-23 10:00 | 8252.9 | 2.7207 | 84.763 | 59.8258 | 2418.6862 |  | 5602 | 20167200 | 51703200 | 83239200 | 114775200
2035-12-24 11:00 | 9582.25 | 3.0831 | 85.3148 | 59.8258 | 2808.2803 |  | 5603 | 20170800 | 51706800 | 83242800 | 114778800
2035-12-25 12:00 | 11007.8 | 3.5218 | 85.665 | 59.8258 | 3226.0677 |  | 5604 | 20174400 | 51710400 | 83246400 | 114782400
2035-12-26 13:00 | 11304.3 | 3.6254 | 85.9706 | 59.8258 | 3312.9633 |  | 5605 | 20178000 | 51714000 | 83250000 | 114786000
2035-12-27 14:00 | 10900.7 | 3.4426 | 86.4499 | 59.8258 | 3194.6798 |  | 5606 | 20181600 | 51717600 | 83253600 | 114789600
2035-12-28 15:00 | 11798.5 | 3.8131 | 86.2128 | 59.8258 | 3457.799 |  | 5607 | 20185200 | 51721200 | 83257200 | 114793200
2035-12-29 16:00 | 12148.4 | 3.9272 | 86.4057 | 59.8258 | 3560.3446 |  | 5608 | 20188800 | 51724800 | 83260800 | 114796800
2035-12-30 17:00 | 12093.8 | 3.8703 | 86.7243 | 59.8258 | 3544.3429 |  | 5609 | 20192400 | 51728400 | 83264400 | 114800400
2035-12-31 18:00 | 10857.1 | 3.4211 | 87.0531 | 59.8258 | 3181.9019 |  | 5610 | 20196000 | 51732000 | 83268000 | 114804000
2036-01-01 19:00 | 10064.3 | 3.0924 | 87.3534 | 59.8258 | 2949.5552 |  | 5611 | 20199600 | 51735600 | 83271600 | 114807600
2036-01-02 20:00 | 8102.37 | 2.4352 | 87.6171 | 59.8258 | 2374.5702 |  | 5612 | 20203200 | 51739200 | 83275200 | 114811200
2036-01-03 21:00 | 7398.46 | 2.1995 | 87.5085 | 59.8258 | 2168.2746 |  | 5613 | 20206800 | 51742800 | 83278800 | 114814800
2036-01-04 22:00 | 5453.65 | 1.5778 | 87.7031 | 59.8258 | 1598.307 |  | 5614 | 20210400 | 51746400 | 83282400 | 114818400
2036-01-05 23:00 | 4522.79 | 1.3248 | 87.1156 | 59.8258 | 1325.4989 |  | 5615 | 20214000 | 51750000 | 83286000 | 114822000
2036-01-07 | 3658.24 | 1.1428 | 85.777 | 59.8258 | 1072.1243 |  | 5616 | 20217600 | 51753600 | 83289600 | 114825600
2036-01-08 01:00 | 3102.01 | 1.0059 | 84.8948 | 59.8258 | 909.1094 |  | 5617 | 20221200 | 51757200 | 83293200 | 114829200
2036-01-09 02:00 | 3163.72 | 1 | 86.8539 | 59.8258 | 927.1948 |  | 5618 | 20224800 | 51760800 | 83296800 | 114832800
2036-01-10 03:00 | 3167.34 | 1 | 85.0054 | 59.8258 | 928.2557 |  | 5619 | 20228400 | 51764400 | 83300400 | 114836400
2036-01-11 04:00 | 3429.34 | 1.0793 | 84.6378 | 59.8258 | 1005.0403 |  | 5620 | 20232000 | 51768000 | 83304000 | 114840000
2036-01-12 05:00 | 4286.94 | 1.3637 | 84.3622 | 59.8258 | 1256.3781 |  | 5621 | 20235600 | 51771600 | 83307600 | 114843600
2036-01-13 06:00 | 4529.19 | 1.3936 | 84.8644 | 59.8258 | 1327.3746 |  | 5622 | 20239200 | 51775200 | 83311200 | 114847200
2036-01-14 07:00 | 5222.68 | 1.6589 | 84.4 | 59.8258 | 1530.6164 |  | 5623 | 20242800 | 51778800 | 83314800 | 114850800
2036-01-15 08:00 | 4870.73 | 1.4794 | 85.1361 | 59.8258 | 1427.4701 |  | 5624 | 20246400 | 51782400 | 83318400 | 114854400
2036-01-16 09:00 | 5938.74 | 1.9686 | 83.8438 | 59.8258 | 1740.4729 |  | 5625 | 20250000 | 51786000 | 83322000 | 114858000
2036-01-17 10:00 | 7657.64 | 2.587 | 83.6924 | 59.8258 | 2244.2327 |  | 5626 | 20253600 | 51789600 | 83325600 | 114861600
2036-01-18 11:00 | 8915.46 | 2.9765 | 84.1224 | 59.8258 | 2612.8634 |  | 5627 | 20257200 | 51793200 | 83329200 | 114865200
2036-01-19 12:00 | 9241.83 | 2.9305 | 85.1454 | 59.8258 | 2708.513 |  | 5628 | 20260800 | 51796800 | 83332800 | 114868800
2036-01-20 13:00 | 9564.83 | 3.042 | 85.3029 | 59.8258 | 2803.175 |  | 5629 | 20264400 | 51800400 | 83336400 | 114872400
2036-01-21 14:00 | 10197.8 | 3.3388 | 85.0833 | 59.8258 | 2988.6802 |  | 5630 | 20268000 | 51804000 | 83340000 | 114876000
2036-01-22 15:00 | 12039.5 | 3.9138 | 85.3928 | 59.8258 | 3528.4291 |  | 5631 | 20271600 | 51807600 | 83343600 | 114879600
2036-01-23 16:00 | 12844.7 | 4.1956 | 85.6967 | 59.8258 | 3764.41 |  | 5632 | 20275200 | 51811200 | 83347200 | 114883200
2036-01-24 17:00 | 12789.5 | 4.091 | 86.3175 | 59.8258 | 3748.2324 |  | 5633 | 20278800 | 51814800 | 83350800 | 114886800
2036-01-25 18:00 | 11401.6 | 3.546 | 86.9427 | 59.8258 | 3341.4791 |  | 5634 | 20282400 | 51818400 | 83354400 | 114890400
2036-01-26 19:00 | 9988.11 | 3.1162 | 86.8988 | 59.8258 | 2927.2261 |  | 5635 | 20286000 | 51822000 | 83358000 | 114894000
2036-01-27 20:00 | 7971.18 | 2.3844 | 87.4324 | 59.8258 | 2336.1223 |  | 5636 | 20289600 | 51825600 | 83361600 | 114897600
2036-01-28 21:00 | 6871.68 | 2.072 | 87.0166 | 59.8258 | 2013.8906 |  | 5637 | 20293200 | 51829200 | 83365200 | 114901200
2036-01-29 22:00 | 4935.36 | 1.4116 | 87.5451 | 59.8258 | 1446.4112 |  | 5638 | 20296800 | 51832800 | 83368800 | 114904800
2036-01-30 23:00 | 3973.1 | 1.2397 | 85.7798 | 59.8258 | 1164.4007 |  | 5639 | 20300400 | 51836400 | 83372400 | 114908400
2036-02-01 | 3370.66 | 1.0585 | 85.3079 | 59.8258 | 987.8429 |  | 5640 | 20304000 | 51840000 | 83376000 | 114912000
2036-02-02 01:00 | 3178.26 | 1 | 85.3287 | 59.8258 | 931.4561 |  | 5641 | 20307600 | 51843600 | 83379600 | 114915600
2036-02-03 02:00 | 3224.25 | 1 | 85.8953 | 59.8258 | 944.9344 |  | 5642 | 20311200 | 51847200 | 83383200 | 114919200
2036-02-04 03:00 | 3505.59 | 1.0912 | 84.7086 | 59.8258 | 1027.387 |  | 5643 | 20314800 | 51850800 | 83386800 | 114922800
2036-02-05 04:00 | 3900.03 | 1.2209 | 84.5124 | 59.8258 | 1142.986 |  | 5644 | 20318400 | 51854400 | 83390400 | 114926400
2036-02-06 05:00 | 4926.78 | 1.5554 | 84.3233 | 59.8258 | 1443.8967 |  | 5645 | 20322000 | 51858000 | 83394000 | 114930000
2036-02-07 06:00 | 5006.18 | 1.5801 | 84.3989 | 59.8258 | 1467.1665 |  | 5646 | 20325600 | 51861600 | 83397600 | 114933600
2036-02-08 07:00 | 5557.72 | 1.7855 | 84.1653 | 59.8258 | 1628.8069 |  | 5647 | 20329200 | 51865200 | 83401200 | 114937200
2036-02-09 08:00 | 5483.41 | 1.7132 | 84.6489 | 59.8258 | 1607.0288 |  | 5648 | 20332800 | 51868800 | 83404800 | 114940800
2036-02-10 09:00 | 6781.39 | 2.2155 | 84.0334 | 59.8258 | 1987.4292 |  | 5649 | 20336400 | 51872400 | 83408400 | 114944400
2036-02-11 10:00 | 8447.4 | 2.7758 | 84.133 | 59.8258 | 2475.6886 |  | 5650 | 20340000 | 51876000 | 83412000 | 114948000
2036-02-12 11:00 | 9464.92 | 3.0324 | 84.7996 | 59.8258 | 2773.8942 |  | 5651 | 20343600 | 51879600 | 83415600 | 114951600
2036-02-13 12:00 | 10035.7 | 3.1985 | 85.1815 | 59.8258 | 2941.1733 |  | 5652 | 20347200 | 51883200 | 83419200 | 114955200
2036-02-14 13:00 | 10593.4 | 3.3996 | 85.3396 | 59.8258 | 3104.6191 |  | 5653 | 20350800 | 51886800 | 83422800 | 114958800
2036-02-15 14:00 | 11455 | 3.7608 | 85.2799 | 59.8258 | 3357.1291 |  | 5654 | 20354400 | 51890400 | 83426400 | 114962400
2036-02-16 15:00 | 13001.2 | 4.2651 | 85.5647 | 59.8258 | 3810.2756 |  | 5655 | 20358000 | 51894000 | 83430000 | 114966000
2036-02-17 16:00 | 13654.3 | 4.4733 | 85.9546 | 59.8258 | 4001.6803 |  | 5656 | 20361600 | 51897600 | 83433600 | 114969600
2036-02-18 17:00 | 13420.5 | 4.2979 | 86.5882 | 59.8258 | 3933.1603 |  | 5657 | 20365200 | 51901200 | 83437200 | 114973200
2036-02-19 18:00 | 11797.2 | 3.7306 | 86.9681 | 59.8258 | 3457.418 |  | 5658 | 20368800 | 51904800 | 83440800 | 114976800
2036-02-20 19:00 | 10420 | 3.269 | 87.047 | 59.8258 | 3053.8005 |  | 5659 | 20372400 | 51908400 | 83444400 | 114980400
2036-02-21 20:00 | 8315.86 | 2.5109 | 87.4991 | 59.8258 | 2437.138 |  | 5660 | 20376000 | 51912000 | 83448000 | 114984000
2036-02-22 21:00 | 7275.52 | 2.2095 | 87.0989 | 59.8258 | 2132.2444 |  | 5661 | 20379600 | 51915600 | 83451600 | 114987600
2036-02-23 22:00 | 5540.75 | 1.6087 | 87.495 | 59.8258 | 1623.8335 |  | 5662 | 20383200 | 51919200 | 83455200 | 114991200
2036-02-24 23:00 | 4247.99 | 1.2835 | 86.4795 | 59.8258 | 1244.963 |  | 5663 | 20386800 | 51922800 | 83458800 | 114994800
2036-02-26 | 3718.04 | 1.1516 | 85.7029 | 59.8258 | 1089.65 |  | 5664 | 20390400 | 51926400 | 83462400 | 114998400
2036-02-27 01:00 | 3271.17 | 1.0174 | 85.3262 | 59.8258 | 958.6853 |  | 5665 | 20394000 | 51930000 | 83466000 | 115002000
2036-02-28 02:00 | 3174.78 | 1 | 86.0305 | 59.8258 | 930.4362 |  | 5666 | 20397600 | 51933600 | 83469600 | 115005600
2036-02-29 03:00 | 3260.58 | 1 | 87.9797 | 59.8258 | 955.5817 |  | 5667 | 20401200 | 51937200 | 83473200 | 115009200
2036-03-01 04:00 | 3198.08 | 1 | 88.5745 | 59.8258 | 937.2647 |  | 5668 | 20404800 | 51940800 | 83476800 | 115012800
2036-03-02 05:00 | 3096.58 | 1 | 87.8804 | 59.8258 | 907.518 |  | 5669 | 20408400 | 51944400 | 83480400 | 115016400
2036-03-03 06:00 | 4410.8 | 1.3757 | 84.2949 | 59.8258 | 1292.6779 |  | 5670 | 20412000 | 51948000 | 83484000 | 115020000
2036-03-04 07:00 | 5648.53 | 1.8509 | 83.6522 | 59.8258 | 1655.4207 |  | 5671 | 20415600 | 51951600 | 83487600 | 115023600
2036-03-05 08:00 | 5254.14 | 1.6388 | 84.5462 | 59.8258 | 1539.8364 |  | 5672 | 20419200 | 51955200 | 83491200 | 115027200
2036-03-06 09:00 | 6284.33 | 2.0245 | 84.0843 | 59.8258 | 1841.7553 |  | 5673 | 20422800 | 51958800 | 83494800 | 115030800
2036-03-07 10:00 | 7493.05 | 2.4357 | 84.0857 | 59.8258 | 2195.9962 |  | 5674 | 20426400 | 51962400 | 83498400 | 115034400
2036-03-08 11:00 | 8813.86 | 2.9505 | 83.9285 | 59.8258 | 2583.0874 |  | 5675 | 20430000 | 51966000 | 83502000 | 115038000
2036-03-09 12:00 | 9518.13 | 3.122 | 84.5081 | 59.8258 | 2789.4885 |  | 5676 | 20433600 | 51969600 | 83505600 | 115041600
2036-03-10 13:00 | 9705.62 | 3.0967 | 85.1497 | 59.8258 | 2844.4364 |  | 5677 | 20437200 | 51973200 | 83509200 | 115045200
2036-03-11 14:00 | 10370.5 | 3.3258 | 85.2683 | 59.8258 | 3039.2935 |  | 5678 | 20440800 | 51976800 | 83512800 | 115048800
2036-03-12 15:00 | 10704.2 | 3.3884 | 85.6642 | 59.8258 | 3137.0913 |  | 5679 | 20444400 | 51980400 | 83516400 | 115052400
2036-03-13 16:00 | 13058.6 | 4.2622 | 85.3969 | 59.8258 | 3827.0979 |  | 5680 | 20448000 | 51984000 | 83520000 | 115056000
2036-03-14 17:00 | 11794 | 3.7274 | 86.2945 | 59.8258 | 3456.4802 |  | 5681 | 20451600 | 51987600 | 83523600 | 115059600
2036-03-15 18:00 | 10537.6 | 3.2589 | 86.7175 | 59.8258 | 3088.2657 |  | 5682 | 20455200 | 51991200 | 83527200 | 115063200
2036-03-16 19:00 | 9466.06 | 2.8966 | 86.7981 | 59.8258 | 2774.2283 |  | 5683 | 20458800 | 51994800 | 83530800 | 115066800
2036-03-17 20:00 | 8688.13 | 2.6336 | 86.8429 | 59.8258 | 2546.2396 |  | 5684 | 20462400 | 51998400 | 83534400 | 115070400
2036-03-18 21:00 | 8028.76 | 2.4456 | 86.6631 | 59.8258 | 2352.9973 |  | 5685 | 20466000 | 52002000 | 83538000 | 115074000
2036-03-19 22:00 | 7393.42 | 2.2789 | 86.3249 | 59.8258 | 2166.7975 |  | 5686 | 20469600 | 52005600 | 83541600 | 115077600
2036-03-20 23:00 | 4513.5 | 1.3137 | 87.0514 | 59.8258 | 1322.7763 |  | 5687 | 20473200 | 52009200 | 83545200 | 115081200
2036-03-22 | 3756.34 | 1.1302 | 86.0709 | 59.8258 | 1100.8746 |  | 5688 | 20476800 | 52012800 | 83548800 | 115084800
2036-03-23 01:00 | 3251.74 | 1.0259 | 85.0103 | 59.8258 | 952.9909 |  | 5689 | 20480400 | 52016400 | 83552400 | 115088400
2036-03-24 02:00 | 3217.76 | 1 | 87.0723 | 59.8258 | 943.0324 |  | 5690 | 20484000 | 52020000 | 83556000 | 115092000
2036-03-25 03:00 | 3202.19 | 1 | 87.8514 | 59.8258 | 938.4692 |  | 5691 | 20487600 | 52023600 | 83559600 | 115095600
2036-03-26 04:00 | 3189.71 | 1 | 89.0747 | 59.8258 | 934.8117 |  | 5692 | 20491200 | 52027200 | 83563200 | 115099200
2036-03-27 05:00 | 3142.69 | 1 | 90.0392 | 59.8258 | 921.0315 |  | 5693 | 20494800 | 52030800 | 83566800 | 115102800
2036-03-28 06:00 | 4284.46 | 1.3118 | 84.4693 | 59.8258 | 1255.6513 |  | 5694 | 20498400 | 52034400 | 83570400 | 115106400
2036-03-29 07:00 | 5186.67 | 1.692 | 83.6127 | 59.8258 | 1520.0629 |  | 5695 | 20502000 | 52038000 | 83574000 | 115110000
2036-03-30 08:00 | 4843.9 | 1.5214 | 84.2813 | 59.8258 | 1419.607 |  | 5696 | 20505600 | 52041600 | 83577600 | 115113600
2036-03-31 09:00 | 5518.17 | 1.8408 | 83.4094 | 59.8258 | 1617.216 |  | 5697 | 20509200 | 52045200 | 83581200 | 115117200
2036-04-01 10:00 | 7478.37 | 2.4839 | 83.5155 | 59.8258 | 2191.6939 |  | 5698 | 20512800 | 52048800 | 83584800 | 115120800
2036-04-02 11:00 | 9040.31 | 2.9418 | 84.1078 | 59.8258 | 2649.4533 |  | 5699 | 20516400 | 52052400 | 83588400 | 115124400
2036-04-03 12:00 | 10617.8 | 3.3321 | 84.9853 | 59.8258 | 3111.77 |  | 5700 | 20520000 | 52056000 | 83592000 | 115128000
2036-04-04 13:00 | 10418.2 | 3.2912 | 85.2972 | 59.8258 | 3053.273 |  | 5701 | 20523600 | 52059600 | 83595600 | 115131600
2036-04-05 14:00 | 10338.1 | 3.2804 | 85.4735 | 59.8258 | 3029.798 |  | 5702 | 20527200 | 52063200 | 83599200 | 115135200
2036-04-06 15:00 | 10024.9 | 3.1714 | 85.6805 | 59.8258 | 2938.0082 |  | 5703 | 20530800 | 52066800 | 83602800 | 115138800
2036-04-07 16:00 | 11952.4 | 3.9325 | 85.1839 | 59.8258 | 3502.9027 |  | 5704 | 20534400 | 52070400 | 83606400 | 115142400
2036-04-08 17:00 | 10719.9 | 3.4053 | 86.0125 | 59.8258 | 3141.6926 |  | 5705 | 20538000 | 52074000 | 83610000 | 115146000
2036-04-09 18:00 | 9665.57 | 3.014 | 86.3107 | 59.8258 | 2832.6989 |  | 5706 | 20541600 | 52077600 | 83613600 | 115149600
2036-04-10 19:00 | 8825.47 | 2.6887 | 86.5521 | 59.8258 | 2586.4899 |  | 5707 | 20545200 | 52081200 | 83617200 | 115153200
2036-04-11 20:00 | 8379.16 | 2.5593 | 86.4164 | 59.8258 | 2455.6894 |  | 5708 | 20548800 | 52084800 | 83620800 | 115156800
2036-04-12 21:00 | 7972.5 | 2.4312 | 86.3759 | 59.8258 | 2336.5091 |  | 5709 | 20552400 | 52088400 | 83624400 | 115160400
2036-04-13 22:00 | 7365.75 | 2.3131 | 85.8244 | 59.8258 | 2158.6882 |  | 5710 | 20556000 | 52092000 | 83628000 | 115164000
2036-04-14 23:00 | 5110.17 | 1.454 | 87.2125 | 59.8258 | 1497.643 |  | 5711 | 20559600 | 52095600 | 83631600 | 115167600
2036-04-16 | 4393.44 | 1.3145 | 86.0497 | 59.8258 | 1287.5902 |  | 5712 | 20563200 | 52099200 | 83635200 | 115171200
2036-04-17 01:00 | 4020.47 | 1.2343 | 85.3665 | 59.8258 | 1178.2834 |  | 5713 | 20566800 | 52102800 | 83638800 | 115174800
2036-04-18 02:00 | 3875.16 | 1.1842 | 85.216 | 59.8258 | 1135.6973 |  | 5714 | 20570400 | 52106400 | 83642400 | 115178400
2036-04-19 03:00 | 4173.41 | 1.2886 | 84.8803 | 59.8258 | 1223.1057 |  | 5715 | 20574000 | 52110000 | 83646000 | 115182000
2036-04-20 04:00 | 4412.74 | 1.4075 | 84.2791 | 59.8258 | 1293.2464 |  | 5716 | 20577600 | 52113600 | 83649600 | 115185600
2036-04-21 05:00 | 5224.21 | 1.6798 | 84.1194 | 59.8258 | 1531.0648 |  | 5717 | 20581200 | 52117200 | 83653200 | 115189200
2036-04-22 06:00 | 5331.34 | 1.6903 | 84.3821 | 59.8258 | 1562.4615 |  | 5718 | 20584800 | 52120800 | 83656800 | 115192800
2036-04-23 07:00 | 5771.61 | 1.9084 | 83.815 | 59.8258 | 1691.4919 |  | 5719 | 20588400 | 52124400 | 83660400 | 115196400
2036-04-24 08:00 | 5687.19 | 1.8111 | 84.4122 | 59.8258 | 1666.7509 |  | 5720 | 20592000 | 52128000 | 83664000 | 115200000
2036-04-25 09:00 | 7001.09 | 2.3223 | 83.845 | 59.8258 | 2051.8169 |  | 5721 | 20595600 | 52131600 | 83667600 | 115203600
2036-04-26 10:00 | 9107.85 | 3.0733 | 83.7675 | 59.8258 | 2669.2473 |  | 5722 | 20599200 | 52135200 | 83671200 | 115207200
2036-04-27 11:00 | 10588.6 | 3.5236 | 84.3224 | 59.8258 | 3103.2123 |  | 5723 | 20602800 | 52138800 | 83674800 | 115210800
2036-04-28 12:00 | 11694 | 3.7769 | 85.1361 | 59.8258 | 3427.1731 |  | 5724 | 20606400 | 52142400 | 83678400 | 115214400
2036-04-29 13:00 | 12390.9 | 3.9875 | 85.5744 | 59.8258 | 3631.4143 |  | 5725 | 20610000 | 52146000 | 83682000 | 115218000
2036-04-30 14:00 | 13278.6 | 4.3523 | 85.6857 | 59.8258 | 3891.5735 |  | 5726 | 20613600 | 52149600 | 83685600 | 115221600
2036-05-01 15:00 | 15315 | 4.9435 | 86.2727 | 59.8258 | 4488.3834 |  | 5727 | 20617200 | 52153200 | 83689200 | 115225200
2036-05-02 16:00 | 15667.1 | 5.0572 | 86.7833 | 59.8258 | 4591.5738 |  | 5728 | 20620800 | 52156800 | 83692800 | 115228800
2036-05-03 17:00 | 15353.3 | 4.8702 | 87.417 | 59.8258 | 4499.6081 |  | 5729 | 20624400 | 52160400 | 83696400 | 115232400
2036-05-04 18:00 | 13737.6 | 4.2828 | 87.9137 | 59.8258 | 4026.0931 |  | 5730 | 20628000 | 52164000 | 83700000 | 115236000
2036-05-05 19:00 | 11844.2 | 3.7004 | 87.9051 | 59.8258 | 3471.1924 |  | 5731 | 20631600 | 52167600 | 83703600 | 115239600
2036-05-06 20:00 | 9456.42 | 2.8726 | 88.1803 | 59.8258 | 2771.4031 |  | 5732 | 20635200 | 52171200 | 83707200 | 115243200
2036-05-07 21:00 | 8170.94 | 2.4896 | 87.7709 | 59.8258 | 2394.6661 |  | 5733 | 20638800 | 52174800 | 83710800 | 115246800
2036-05-08 22:00 | 6187.78 | 1.8158 | 87.9874 | 59.8258 | 1813.4593 |  | 5734 | 20642400 | 52178400 | 83714400 | 115250400
2036-05-09 23:00 | 5480.23 | 1.6038 | 87.5645 | 59.8258 | 1606.0969 |  | 5735 | 20646000 | 52182000 | 83718000 | 115254000
2036-05-11 | 4870.91 | 1.4675 | 86.7453 | 59.8258 | 1427.5228 |  | 5736 | 20649600 | 52185600 | 83721600 | 115257600
2036-05-12 01:00 | 4469.97 | 1.3779 | 86.0942 | 59.8258 | 1310.0189 |  | 5737 | 20653200 | 52189200 | 83725200 | 115261200
2036-05-13 02:00 | 4277.08 | 1.3165 | 85.8568 | 59.8258 | 1253.4884 |  | 5738 | 20656800 | 52192800 | 83728800 | 115264800
2036-05-14 03:00 | 4544.28 | 1.4096 | 85.5013 | 59.8258 | 1331.797 |  | 5739 | 20660400 | 52196400 | 83732400 | 115268400
2036-05-15 04:00 | 4714.63 | 1.4917 | 85.0743 | 59.8258 | 1381.7217 |  | 5740 | 20664000 | 52200000 | 83736000 | 115272000
2036-05-16 05:00 | 5435.14 | 1.7644 | 84.5942 | 59.8258 | 1592.8823 |  | 5741 | 20667600 | 52203600 | 83739600 | 115275600
2036-05-17 06:00 | 5643.7 | 1.7974 | 84.8623 | 59.8258 | 1654.0052 |  | 5742 | 20671200 | 52207200 | 83743200 | 115279200
2036-05-18 07:00 | 6412.75 | 2.0639 | 84.7096 | 59.8258 | 1879.3915 |  | 5743 | 20674800 | 52210800 | 83746800 | 115282800
2036-05-19 08:00 | 6840.21 | 2.1969 | 84.8404 | 59.8258 | 2004.6677 |  | 5744 | 20678400 | 52214400 | 83750400 | 115286400
2036-05-20 09:00 | 8505.82 | 2.815 | 84.5188 | 59.8258 | 2492.8098 |  | 5745 | 20682000 | 52218000 | 83754000 | 115290000
2036-05-21 10:00 | 9925.98 | 3.2555 | 84.9177 | 59.8258 | 2909.0176 |  | 5746 | 20685600 | 52221600 | 83757600 | 115293600
2036-05-22 11:00 | 11786.4 | 3.9168 | 85.0661 | 59.8258 | 3454.2529 |  | 5747 | 20689200 | 52225200 | 83761200 | 115297200
2036-05-23 12:00 | 13222.6 | 4.2806 | 85.869 | 59.8258 | 3875.1615 |  | 5748 | 20692800 | 52228800 | 83764800 | 115300800
2036-05-24 13:00 | 12966.8 | 4.195 | 86.3476 | 59.8258 | 3800.194 |  | 5749 | 20696400 | 52232400 | 83768400 | 115304400
2036-05-25 14:00 | 12774 | 4.1528 | 86.5541 | 59.8258 | 3743.6898 |  | 5750 | 20700000 | 52236000 | 83772000 | 115308000
2036-05-26 15:00 | 12957.7 | 4.1927 | 86.7771 | 59.8258 | 3797.527 |  | 5751 | 20703600 | 52239600 | 83775600 | 115311600
2036-05-27 16:00 | 12899.4 | 4.1159 | 87.1343 | 59.8258 | 3780.441 |  | 5752 | 20707200 | 52243200 | 83779200 | 115315200
2036-05-28 17:00 | 12577.4 | 3.9304 | 87.5387 | 59.8258 | 3686.0721 |  | 5753 | 20710800 | 52246800 | 83782800 | 115318800
2036-05-29 18:00 | 11201.6 | 3.4069 | 87.9816 | 59.8258 | 3282.8649 |  | 5754 | 20714400 | 52250400 | 83786400 | 115322400
2036-05-30 19:00 | 9824.87 | 3.0432 | 87.5991 | 59.8258 | 2879.3852 |  | 5755 | 20718000 | 52254000 | 83790000 | 115326000
2036-05-31 20:00 | 7805.79 | 2.3487 | 87.8467 | 59.8258 | 2287.6512 |  | 5756 | 20721600 | 52257600 | 83793600 | 115329600
2036-06-01 21:00 | 6841.96 | 2.0759 | 87.3668 | 59.8258 | 2005.1805 |  | 5757 | 20725200 | 52261200 | 83797200 | 115333200
2036-06-02 22:00 | 5032.36 | 1.4358 | 88.0057 | 59.8258 | 1474.8391 |  | 5758 | 20728800 | 52264800 | 83800800 | 115336800
2036-06-03 23:00 | 4183.36 | 1.2853 | 86.4167 | 59.8258 | 1226.0218 |  | 5759 | 20732400 | 52268400 | 83804400 | 115340400
2036-06-05 | 3635.63 | 1.1234 | 85.9309 | 59.8258 | 1065.498 |  | 5760 | 20736000 | 52272000 | 83808000 | 115344000
2036-06-06 01:00 | 3350.64 | 1.04 | 85.5352 | 59.8258 | 981.9756 |  | 5761 | 20739600 | 52275600 | 83811600 | 115347600
2036-06-07 02:00 | 3273.42 | 1 | 85.9143 | 59.8258 | 959.3447 |  | 5762 | 20743200 | 52279200 | 83815200 | 115351200
2036-06-08 03:00 | 3511.92 | 1.08 | 85.1916 | 59.8258 | 1029.2422 |  | 5763 | 20746800 | 52282800 | 83818800 | 115354800
2036-06-09 04:00 | 3757.35 | 1.2016 | 84.4903 | 59.8258 | 1101.1706 |  | 5764 | 20750400 | 52286400 | 83822400 | 115358400
2036-06-10 05:00 | 4736.83 | 1.5146 | 84.3971 | 59.8258 | 1388.2278 |  | 5765 | 20754000 | 52290000 | 83826000 | 115362000
2036-06-11 06:00 | 4899.55 | 1.5276 | 84.8042 | 59.8258 | 1435.9164 |  | 5766 | 20757600 | 52293600 | 83829600 | 115365600
2036-06-12 07:00 | 5301.54 | 1.6869 | 84.5217 | 59.8258 | 1553.728 |  | 5767 | 20761200 | 52297200 | 83833200 | 115369200
2036-06-13 08:00 | 5454.04 | 1.6962 | 84.9035 | 59.8258 | 1598.4213 |  | 5768 | 20764800 | 52300800 | 83836800 | 115372800
2036-06-14 09:00 | 6762.53 | 2.3031 | 83.6527 | 59.8258 | 1981.9019 |  | 5769 | 20768400 | 52304400 | 83840400 | 115376400
2036-06-15 10:00 | 8373.21 | 2.7689 | 84.2319 | 59.8258 | 2453.9456 |  | 5770 | 20772000 | 52308000 | 83844000 | 115380000
2036-06-16 11:00 | 10263.8 | 3.4244 | 84.3928 | 59.8258 | 3008.0228 |  | 5771 | 20775600 | 52311600 | 83847600 | 115383600
2036-06-17 12:00 | 11710.2 | 3.799 | 85.1783 | 59.8258 | 3431.9208 |  | 5772 | 20779200 | 52315200 | 83851200 | 115387200
2036-06-18 13:00 | 12459.7 | 4.0149 | 85.7007 | 59.8258 | 3651.5776 |  | 5773 | 20782800 | 52318800 | 83854800 | 115390800
2036-06-19 14:00 | 13593.6 | 4.3371 | 86.2177 | 59.8258 | 3983.8909 |  | 5774 | 20786400 | 52322400 | 83858400 | 115394400
2036-06-20 15:00 | 15406.4 | 4.979 | 86.4295 | 59.8258 | 4515.1701 |  | 5775 | 20790000 | 52326000 | 83862000 | 115398000
2036-06-21 16:00 | 15295.3 | 4.9212 | 87.0102 | 59.8258 | 4482.6099 |  | 5776 | 20793600 | 52329600 | 83865600 | 115401600
2036-06-22 17:00 | 14857.2 | 4.713 | 87.5254 | 59.8258 | 4354.2155 |  | 5777 | 20797200 | 52333200 | 83869200 | 115405200
2036-06-23 18:00 | 13271.5 | 4.1128 | 88.049 | 59.8258 | 3889.4927 |  | 5778 | 20800800 | 52336800 | 83872800 | 115408800
2036-06-24 19:00 | 11608.1 | 3.5919 | 88.0618 | 59.8258 | 3401.9983 |  | 5779 | 20804400 | 52340400 | 83876400 | 115412400
2036-06-25 20:00 | 9185.46 | 2.8054 | 88.1226 | 59.8258 | 2691.9926 |  | 5780 | 20808000 | 52344000 | 83880000 | 115416000
2036-06-26 21:00 | 8052.41 | 2.4764 | 87.6537 | 59.8258 | 2359.9284 |  | 5781 | 20811600 | 52347600 | 83883600 | 115419600
2036-06-27 22:00 | 6225.79 | 1.8139 | 88.1593 | 59.8258 | 1824.5989 |  | 5782 | 20815200 | 52351200 | 83887200 | 115423200
2036-06-28 23:00 | 5514.99 | 1.6648 | 87.1866 | 59.8258 | 1616.284 |  | 5783 | 20818800 | 52354800 | 83890800 | 115426800
2036-06-30 | 5086.6 | 1.5249 | 86.937 | 59.8258 | 1490.7353 |  | 5784 | 20822400 | 52358400 | 83894400 | 115430400
2036-07-01 01:00 | 4555.96 | 1.3954 | 86.3374 | 59.8258 | 1335.2201 |  | 5785 | 20826000 | 52362000 | 83898000 | 115434000
2036-07-02 02:00 | 4293.25 | 1.3244 | 85.973 | 59.8258 | 1258.2274 |  | 5786 | 20829600 | 52365600 | 83901600 | 115437600
2036-07-03 03:00 | 4101.13 | 1.3048 | 85.2761 | 59.8258 | 1201.9226 |  | 5787 | 20833200 | 52369200 | 83905200 | 115441200
2036-07-04 04:00 | 4258.37 | 1.3575 | 85.0481 | 59.8258 | 1248.0051 |  | 5788 | 20836800 | 52372800 | 83908800 | 115444800
2036-07-05 05:00 | 4911.27 | 1.5735 | 84.8277 | 59.8258 | 1439.3512 |  | 5789 | 20840400 | 52376400 | 83912400 | 115448400
2036-07-06 06:00 | 4952.11 | 1.5917 | 84.747 | 59.8258 | 1451.3202 |  | 5790 | 20844000 | 52380000 | 83916000 | 115452000
2036-07-07 07:00 | 5741.59 | 1.901 | 84.2813 | 59.8258 | 1682.6939 |  | 5791 | 20847600 | 52383600 | 83919600 | 115455600
2036-07-08 08:00 | 6440.59 | 2.1393 | 84.3018 | 59.8258 | 1887.5506 |  | 5792 | 20851200 | 52387200 | 83923200 | 115459200
2036-07-09 09:00 | 8269.42 | 2.7201 | 84.5471 | 59.8258 | 2423.5278 |  | 5793 | 20854800 | 52390800 | 83926800 | 115462800
2036-07-10 10:00 | 10317.8 | 3.3931 | 84.8422 | 59.8258 | 3023.8487 |  | 5794 | 20858400 | 52394400 | 83930400 | 115466400
2036-07-11 11:00 | 12048.5 | 3.9215 | 85.4046 | 59.8258 | 3531.0668 |  | 5795 | 20862000 | 52398000 | 83934000 | 115470000
2036-07-12 12:00 | 13590.2 | 4.2827 | 86.3292 | 59.8258 | 3982.8945 |  | 5796 | 20865600 | 52401600 | 83937600 | 115473600
2036-07-13 13:00 | 13414.5 | 4.3684 | 86.3591 | 59.8258 | 3931.4019 |  | 5797 | 20869200 | 52405200 | 83941200 | 115477200
2036-07-14 14:00 | 12501.7 | 4.0392 | 86.7831 | 59.8258 | 3663.8866 |  | 5798 | 20872800 | 52408800 | 83944800 | 115480800
2036-07-15 15:00 | 12554.5 | 4.0499 | 86.8939 | 59.8258 | 3679.3607 |  | 5799 | 20876400 | 52412400 | 83948400 | 115484400
2036-07-16 16:00 | 12299.1 | 3.912 | 87.1988 | 59.8258 | 3604.5104 |  | 5800 | 20880000 | 52416000 | 83952000 | 115488000
2036-07-17 17:00 | 11898.6 | 3.7065 | 87.5576 | 59.8258 | 3487.1354 |  | 5801 | 20883600 | 52419600 | 83955600 | 115491600
2036-07-18 18:00 | 10577.2 | 3.2133 | 87.9295 | 59.8258 | 3099.8713 |  | 5802 | 20887200 | 52423200 | 83959200 | 115495200
2036-07-19 19:00 | 9308 | 2.854 | 87.6525 | 59.8258 | 2727.9055 |  | 5803 | 20890800 | 52426800 | 83962800 | 115498800
2036-07-20 20:00 | 7228.87 | 2.0905 | 88.3671 | 59.8258 | 2118.5727 |  | 5804 | 20894400 | 52430400 | 83966400 | 115502400
2036-07-21 21:00 | 6061 | 1.8032 | 87.5592 | 59.8258 | 1776.3038 |  | 5805 | 20898000 | 52434000 | 83970000 | 115506000
2036-07-22 22:00 | 3807.76 | 1.155 | 86.9095 | 59.8258 | 1115.9443 |  | 5806 | 20901600 | 52437600 | 83973600 | 115509600
2036-07-23 23:00 | 3237.76 | 1 | 88.033 | 59.8258 | 948.8938 |  | 5807 | 20905200 | 52441200 | 83977200 | 115513200
2036-07-25 | 3195.88 | 1 | 90.9561 | 59.8258 | 936.62 |  | 5808 | 20908800 | 52444800 | 83980800 | 115516800
2036-07-26 01:00 | 3130.32 | 1 | 94.6571 | 59.8258 | 917.4062 |  | 5809 | 20912400 | 52448400 | 83984400 | 115520400
2036-07-27 02:00 | 3146.52 | 1 | 95.4983 | 59.8258 | 922.154 |  | 5810 | 20916000 | 52452000 | 83988000 | 115524000
2036-07-28 03:00 | 3106.45 | 1 | 92.988 | 59.8258 | 910.4106 |  | 5811 | 20919600 | 52455600 | 83991600 | 115527600
2036-07-29 04:00 | 3081.53 | 1 | 91.5066 | 59.8258 | 903.1073 |  | 5812 | 20923200 | 52459200 | 83995200 | 115531200
2036-07-30 05:00 | 3145.19 | 1 | 85.0186 | 59.8258 | 921.7642 |  | 5813 | 20926800 | 52462800 | 83998800 | 115534800
2036-07-31 06:00 | 3180.52 | 1 | 85.1282 | 59.8258 | 932.1184 |  | 5814 | 20930400 | 52466400 | 84002400 | 115538400
2036-08-01 07:00 | 4024.7 | 1.247 | 84.4925 | 59.8258 | 1179.5231 |  | 5815 | 20934000 | 52470000 | 84006000 | 115542000
2036-08-02 08:00 | 4277.75 | 1.298 | 84.8443 | 59.8258 | 1253.6848 |  | 5816 | 20937600 | 52473600 | 84009600 | 115545600
2036-08-03 09:00 | 5864.88 | 1.8409 | 84.3573 | 59.8258 | 1718.8267 |  | 5817 | 20941200 | 52477200 | 84013200 | 115549200
2036-08-04 10:00 | 7047.35 | 2.3628 | 83.626 | 59.8258 | 2065.3744 |  | 5818 | 20944800 | 52480800 | 84016800 | 115552800
2036-08-05 11:00 | 9008.42 | 3.0303 | 83.8235 | 59.8258 | 2640.1073 |  | 5819 | 20948400 | 52484400 | 84020400 | 115556400
2036-08-06 12:00 | 10577.1 | 3.5017 | 84.4153 | 59.8258 | 3099.842 |  | 5820 | 20952000 | 52488000 | 84024000 | 115560000
2036-08-07 13:00 | 11793.8 | 3.8249 | 85.1182 | 59.8258 | 3456.4216 |  | 5821 | 20955600 | 52491600 | 84027600 | 115563600
2036-08-08 14:00 | 12743.6 | 4.0086 | 85.9759 | 59.8258 | 3734.7805 |  | 5822 | 20959200 | 52495200 | 84031200 | 115567200
2036-08-09 15:00 | 13682.8 | 4.3315 | 86.2649 | 59.8258 | 4010.0328 |  | 5823 | 20962800 | 52498800 | 84034800 | 115570800
2036-08-10 16:00 | 13606.1 | 4.3929 | 86.377 | 59.8258 | 3987.5543 |  | 5824 | 20966400 | 52502400 | 84038400 | 115574400
2036-08-11 17:00 | 12347.9 | 4.0372 | 86.4615 | 59.8258 | 3618.8123 |  | 5825 | 20970000 | 52506000 | 84042000 | 115578000
2036-08-12 18:00 | 10636.3 | 3.4002 | 86.8237 | 59.8258 | 3117.1918 |  | 5826 | 20973600 | 52509600 | 84045600 | 115581600
2036-08-13 19:00 | 9524.72 | 2.9584 | 87.1004 | 59.8258 | 2791.4199 |  | 5827 | 20977200 | 52513200 | 84049200 | 115585200
2036-08-14 20:00 | 7503.01 | 2.2643 | 87.3828 | 59.8258 | 2198.9152 |  | 5828 | 20980800 | 52516800 | 84052800 | 115588800
2036-08-15 21:00 | 6694.46 | 2.0323 | 86.9594 | 59.8258 | 1961.9526 |  | 5829 | 20984400 | 52520400 | 84056400 | 115592400
2036-08-16 22:00 | 4946.73 | 1.4127 | 87.6337 | 59.8258 | 1449.7435 |  | 5830 | 20988000 | 52524000 | 84060000 | 115596000
2036-08-17 23:00 | 3617.77 | 1.1115 | 86.1193 | 59.8258 | 1060.2637 |  | 5831 | 20991600 | 52527600 | 84063600 | 115599600
2036-08-19 | 3245.71 | 1 | 87.7111 | 59.8258 | 951.2237 |  | 5832 | 20995200 | 52531200 | 84067200 | 115603200
2036-08-20 01:00 | 3129.64 | 1 | 89.8176 | 59.8258 | 917.2069 |  | 5833 | 20998800 | 52534800 | 84070800 | 115606800
2036-08-21 02:00 | 3184.26 | 1 | 95.5748 | 59.8258 | 933.2145 |  | 5834 | 21002400 | 52538400 | 84074400 | 115610400
2036-08-22 03:00 | 3172.68 | 1 | 69.7887 | 59.8258 | 929.8207 |  | 5835 | 21006000 | 52542000 | 84078000 | 115614000
2036-08-23 04:00 | 3114.25 | 1 | 69.6411 | 59.8258 | 912.6966 |  | 5836 | 21009600 | 52545600 | 84081600 | 115617600
2036-08-24 05:00 | 3192.96 | 1 | 69.503 | 59.8258 | 935.7642 |  | 5837 | 21013200 | 52549200 | 84085200 | 115621200
2036-08-25 06:00 | 3227.56 | 1 | 87.7144 | 59.8258 | 945.9045 |  | 5838 | 21016800 | 52552800 | 84088800 | 115624800
2036-08-26 07:00 | 4629.91 | 1.4196 | 84.4938 | 59.8258 | 1356.8927 |  | 5839 | 21020400 | 52556400 | 84092400 | 115628400
2036-08-27 08:00 | 4668.77 | 1.4618 | 84.3149 | 59.8258 | 1368.2814 |  | 5840 | 21024000 | 52560000 | 84096000 | 115632000
2036-08-28 09:00 | 6233.35 | 2.1183 | 83.1992 | 59.8258 | 1826.8146 |  | 5841 | 21027600 | 52563600 | 84099600 | 115635600
2036-08-29 10:00 | 8625.99 | 2.9177 | 83.4598 | 59.8258 | 2528.0281 |  | 5842 | 21031200 | 52567200 | 84103200 | 115639200
2036-08-30 11:00 | 10534.1 | 3.5961 | 83.7632 | 59.8258 | 3087.24 |  | 5843 | 21034800 | 52570800 | 84106800 | 115642800
2036-08-31 12:00 | 12183.1 | 3.961 | 84.9186 | 59.8258 | 3570.5142 |  | 5844 | 21038400 | 52574400 | 84110400 | 115646400
2036-09-01 13:00 | 12878.5 | 4.1108 | 85.6661 | 59.8258 | 3774.3158 |  | 5845 | 21042000 | 52578000 | 84114000 | 115650000
2036-09-02 14:00 | 13490.1 | 4.3026 | 86.0963 | 59.8258 | 3953.558 |  | 5846 | 21045600 | 52581600 | 84117600 | 115653600
2036-09-03 15:00 | 13727.3 | 4.4533 | 86.2199 | 59.8258 | 4023.0745 |  | 5847 | 21049200 | 52585200 | 84121200 | 115657200
2036-09-04 16:00 | 16154.8 | 5.1755 | 86.6729 | 59.8258 | 4734.5045 |  | 5848 | 21052800 | 52588800 | 84124800 | 115660800
2036-09-05 17:00 | 14703.6 | 4.6966 | 87.2702 | 59.8258 | 4309.1998 |  | 5849 | 21056400 | 52592400 | 84128400 | 115664400
2036-09-06 18:00 | 12855.1 | 4.0568 | 87.6365 | 59.8258 | 3767.4579 |  | 5850 | 21060000 | 52596000 | 84132000 | 115668000
2036-09-07 19:00 | 11626.2 | 3.4878 | 88.3058 | 59.8258 | 3407.3029 |  | 5851 | 21063600 | 52599600 | 84135600 | 115671600
2036-09-08 20:00 | 10366.7 | 3.1435 | 88.0562 | 59.8258 | 3038.1799 |  | 5852 | 21067200 | 52603200 | 84139200 | 115675200
2036-09-09 21:00 | 9075.46 | 2.8064 | 87.6279 | 59.8258 | 2659.7548 |  | 5853 | 21070800 | 52606800 | 84142800 | 115678800
2036-09-10 22:00 | 8222.42 | 2.5763 | 87.1724 | 59.8258 | 2409.7534 |  | 5854 | 21074400 | 52610400 | 84146400 | 115682400
2036-09-11 23:00 | 5725.78 | 1.625 | 88.4567 | 59.8258 | 1678.0605 |  | 5855 | 21078000 | 52614000 | 84150000 | 115686000
2036-09-13 | 4642.04 | 1.3887 | 87.1673 | 59.8258 | 1360.4476 |  | 5856 | 21081600 | 52617600 | 84153600 | 115689600
2036-09-14 01:00 | 3850.8 | 1.1868 | 86.3062 | 59.8258 | 1128.5581 |  | 5857 | 21085200 | 52621200 | 84157200 | 115693200
2036-09-15 02:00 | 3432.08 | 1.062 | 85.8914 | 59.8258 | 1005.8434 |  | 5858 | 21088800 | 52624800 | 84160800 | 115696800
2036-09-16 03:00 | 3135.42 | 1 | 86.2343 | 59.8258 | 918.9009 |  | 5859 | 21092400 | 52628400 | 84164400 | 115700400
2036-09-17 04:00 | 3214.55 | 1 | 90.1397 | 59.8258 | 942.0916 |  | 5860 | 21096000 | 52632000 | 84168000 | 115704000
2036-09-18 05:00 | 3179.48 | 1 | 91.4226 | 59.8258 | 931.8136 |  | 5861 | 21099600 | 52635600 | 84171600 | 115707600
2036-09-19 06:00 | 3976.59 | 1.2324 | 84.9015 | 59.8258 | 1165.4235 |  | 5862 | 21103200 | 52639200 | 84175200 | 115711200
2036-09-20 07:00 | 5612.45 | 1.8091 | 84.318 | 59.8258 | 1644.8467 |  | 5863 | 21106800 | 52642800 | 84178800 | 115714800
2036-09-21 08:00 | 5882.01 | 1.9169 | 84.3464 | 59.8258 | 1723.847 |  | 5864 | 21110400 | 52646400 | 84182400 | 115718400
2036-09-22 09:00 | 7936.33 | 2.6885 | 83.9079 | 59.8258 | 2325.9087 |  | 5865 | 21114000 | 52650000 | 84186000 | 115722000
2036-09-23 10:00 | 10195.4 | 3.5466 | 83.8445 | 59.8258 | 2987.9768 |  | 5866 | 21117600 | 52653600 | 84189600 | 115725600
2036-09-24 11:00 | 12176.4 | 4.0603 | 84.8935 | 59.8258 | 3568.5506 |  | 5867 | 21121200 | 52657200 | 84193200 | 115729200
2036-09-25 12:00 | 13201.3 | 4.2943 | 85.7703 | 59.8258 | 3868.9191 |  | 5868 | 21124800 | 52660800 | 84196800 | 115732800
2036-09-26 13:00 | 14074.2 | 4.4314 | 86.6823 | 59.8258 | 4124.7409 |  | 5869 | 21128400 | 52664400 | 84200400 | 115736400
2036-09-27 14:00 | 14295.7 | 4.6102 | 86.7723 | 59.8258 | 4189.6561 |  | 5870 | 21132000 | 52668000 | 84204000 | 115740000
2036-09-28 15:00 | 14387.8 | 4.6965 | 86.9313 | 59.8258 | 4216.6479 |  | 5871 | 21135600 | 52671600 | 84207600 | 115743600
2036-09-29 16:00 | 16566.1 | 5.3265 | 87.3653 | 59.8258 | 4855.0447 |  | 5872 | 21139200 | 52675200 | 84211200 | 115747200
2036-09-30 17:00 | 15351.3 | 4.876 | 88.0301 | 59.8258 | 4499.0219 |  | 5873 | 21142800 | 52678800 | 84214800 | 115750800
2036-10-01 18:00 | 13930.8 | 4.2217 | 88.9073 | 59.8258 | 4082.7145 |  | 5874 | 21146400 | 52682400 | 84218400 | 115754400
2036-10-02 19:00 | 12139.7 | 3.699 | 88.7878 | 59.8258 | 3557.7949 |  | 5875 | 21150000 | 52686000 | 84222000 | 115758000
2036-10-03 20:00 | 10767.5 | 3.3676 | 88.2518 | 59.8258 | 3155.6427 |  | 5876 | 21153600 | 52689600 | 84225600 | 115761600
2036-10-04 21:00 | 9476.12 | 2.9769 | 87.9869 | 59.8258 | 2777.1766 |  | 5877 | 21157200 | 52693200 | 84229200 | 115765200
2036-10-05 22:00 | 8589.41 | 2.6161 | 88.1434 | 59.8258 | 2517.3076 |  | 5878 | 21160800 | 52696800 | 84232800 | 115768800
2036-10-06 23:00 | 5589.73 | 1.6045 | 88.7926 | 59.8258 | 1638.1882 |  | 5879 | 21164400 | 52700400 | 84236400 | 115772400
2036-10-08 | 4712.77 | 1.4112 | 87.5723 | 59.8258 | 1381.1765 |  | 5880 | 21168000 | 52704000 | 84240000 | 115776000
2036-10-09 01:00 | 3989.8 | 1.2214 | 86.7969 | 59.8258 | 1169.295 |  | 5881 | 21171600 | 52707600 | 84243600 | 115779600
2036-10-10 02:00 | 3394.15 | 1.0671 | 86.0473 | 59.8258 | 994.7272 |  | 5882 | 21175200 | 52711200 | 84247200 | 115783200
2036-10-11 03:00 | 3207.41 | 1 | 86.592 | 59.8258 | 939.9991 |  | 5883 | 21178800 | 52714800 | 84250800 | 115786800
2036-10-12 04:00 | 3110.57 | 1 | 89.1678 | 59.8258 | 911.6181 |  | 5884 | 21182400 | 52718400 | 84254400 | 115790400
2036-10-13 05:00 | 3144.67 | 1 | 90.2178 | 59.8258 | 921.6118 |  | 5885 | 21186000 | 52722000 | 84258000 | 115794000
2036-10-14 06:00 | 4243.03 | 1.3192 | 85.1619 | 59.8258 | 1243.5093 |  | 5886 | 21189600 | 52725600 | 84261600 | 115797600
2036-10-15 07:00 | 5416.69 | 1.6843 | 85.1707 | 59.8258 | 1587.4751 |  | 5887 | 21193200 | 52729200 | 84265200 | 115801200
2036-10-16 08:00 | 5399.48 | 1.7085 | 85.0459 | 59.8258 | 1582.4314 |  | 5888 | 21196800 | 52732800 | 84268800 | 115804800
2036-10-17 09:00 | 6315.72 | 1.9974 | 85.07 | 59.8258 | 1850.9548 |  | 5889 | 21200400 | 52736400 | 84272400 | 115808400
2036-10-18 10:00 | 6674.98 | 2.1287 | 85.0434 | 59.8258 | 1956.2435 |  | 5890 | 21204000 | 52740000 | 84276000 | 115812000
2036-10-19 11:00 | 8107.22 | 2.7126 | 84.4696 | 59.8258 | 2375.9916 |  | 5891 | 21207600 | 52743600 | 84279600 | 115815600
2036-10-20 12:00 | 9397.15 | 3.1051 | 84.8554 | 59.8258 | 2754.0328 |  | 5892 | 21211200 | 52747200 | 84283200 | 115819200
2036-10-21 13:00 | 9595.43 | 3.1378 | 85.2742 | 59.8258 | 2812.1429 |  | 5893 | 21214800 | 52750800 | 84286800 | 115822800
2036-10-22 14:00 | 9870.51 | 3.1712 | 85.7069 | 59.8258 | 2892.7609 |  | 5894 | 21218400 | 52754400 | 84290400 | 115826400
2036-10-23 15:00 | 10343.7 | 3.3002 | 85.9505 | 59.8258 | 3031.4392 |  | 5895 | 21222000 | 52758000 | 84294000 | 115830000
2036-10-24 16:00 | 11822.4 | 3.9281 | 85.5353 | 59.8258 | 3464.8034 |  | 5896 | 21225600 | 52761600 | 84297600 | 115833600
2036-10-25 17:00 | 10533.2 | 3.3455 | 86.4828 | 59.8258 | 3086.9762 |  | 5897 | 21229200 | 52765200 | 84301200 | 115837200
2036-10-26 18:00 | 8584.44 | 2.7026 | 86.623 | 59.8258 | 2515.851 |  | 5898 | 21232800 | 52768800 | 84304800 | 115840800
2036-10-27 19:00 | 7050.3 | 2.1959 | 86.5475 | 59.8258 | 2066.239 |  | 5899 | 21236400 | 52772400 | 84308400 | 115844400
2036-10-28 20:00 | 5749.86 | 1.8171 | 86.0571 | 59.8258 | 1685.1176 |  | 5900 | 21240000 | 52776000 | 84312000 | 115848000
2036-10-29 21:00 | 4434.55 | 1.478 | 84.9997 | 59.8258 | 1299.6383 |  | 5901 | 21243600 | 52779600 | 84315600 | 115851600
2036-10-30 22:00 | 3556.72 | 1.1621 | 84.8849 | 59.8258 | 1042.3717 |  | 5902 | 21247200 | 52783200 | 84319200 | 115855200
2036-10-31 23:00 | 2958.73 | 1 | 70.2898 | 59.8258 | 867.1182 |  | 5903 | 21250800 | 52786800 | 84322800 | 115858800
2036-11-02 | 0 | 0 | 70.2601 | 59.8258 | 0 |  | 5904 | 21254400 | 52790400 | 84326400 | 115862400
2036-11-03 01:00 | -349.861 | 1.3834 | 68.4987 | 59.8258 | -102.5341 |  | 5905 | 21258000 | 52794000 | 84330000 | 115866000
2036-11-04 02:00 | -634.753 | 2.0562 | 67.8121 | 59.8258 | -186.0277 |  | 5906 | 21261600 | 52797600 | 84333600 | 115869600
2036-11-05 03:00 | -792.123 | 2.4144 | 67.4015 | 59.8258 | -232.1483 |  | 5907 | 21265200 | 52801200 | 84337200 | 115873200
2036-11-06 04:00 | -884.218 | 2.6315 | 67.053 | 59.8258 | -259.1387 |  | 5908 | 21268800 | 52804800 | 84340800 | 115876800
2036-11-07 05:00 | -635.432 | 1.9767 | 66.8397 | 59.8258 | -186.2267 |  | 5909 | 21272400 | 52808400 | 84344400 | 115880400
2036-11-08 06:00 | -582.481 | 1.8974 | 66.7527 | 59.8258 | -170.7083 |  | 5910 | 21276000 | 52812000 | 84348000 | 115884000
2036-11-09 07:00 | -160.98 | 0.816 | 67.1085 | 59.8258 | -47.1786 |  | 5911 | 21279600 | 52815600 | 84351600 | 115887600
2036-11-10 08:00 | 0 | 0 | 67.9334 | 59.8258 | 0 |  | 5912 | 21283200 | 52819200 | 84355200 | 115891200
2036-11-11 09:00 | 2680.07 | 1 | 67.613 | 59.8258 | 785.451 |  | 5913 | 21286800 | 52822800 | 84358800 | 115894800
2036-11-12 10:00 | 3695.89 | 1.1669 | 82.6127 | 59.8258 | 1083.1584 |  | 5914 | 21290400 | 52826400 | 84362400 | 115898400
2036-11-13 11:00 | 5740.15 | 1.8796 | 82.2736 | 59.8258 | 1682.2719 |  | 5915 | 21294000 | 52830000 | 84366000 | 115902000
2036-11-14 12:00 | 6915.18 | 2.2993 | 82.4305 | 59.8258 | 2026.6392 |  | 5916 | 21297600 | 52833600 | 84369600 | 115905600
2036-11-15 13:00 | 7679.61 | 2.5159 | 83.0049 | 59.8258 | 2250.6715 |  | 5917 | 21301200 | 52837200 | 84373200 | 115909200
2036-11-16 14:00 | 8796.02 | 2.8807 | 83.3381 | 59.8258 | 2577.859 |  | 5918 | 21304800 | 52840800 | 84376800 | 115912800
2036-11-17 15:00 | 9553.06 | 3.241 | 83.1884 | 59.8258 | 2799.7255 |  | 5919 | 21308400 | 52844400 | 84380400 | 115916400
2036-11-18 16:00 | 9750.86 | 3.3377 | 83.3828 | 59.8258 | 2857.695 |  | 5920 | 21312000 | 52848000 | 84384000 | 115920000
2036-11-19 17:00 | 9223.3 | 3.1468 | 83.6519 | 59.8258 | 2703.0824 |  | 5921 | 21315600 | 52851600 | 84387600 | 115923600
2036-11-20 18:00 | 7119.63 | 2.4009 | 83.9251 | 59.8258 | 2086.5576 |  | 5922 | 21319200 | 52855200 | 84391200 | 115927200
2036-11-21 19:00 | 5769.12 | 1.9033 | 84.0683 | 59.8258 | 1690.7622 |  | 5923 | 21322800 | 52858800 | 84394800 | 115930800
2036-11-22 20:00 | 3591.72 | 1.1094 | 84.8009 | 59.8258 | 1052.6292 |  | 5924 | 21326400 | 52862400 | 84398400 | 115934400
2036-11-23 21:00 | 3044.83 | 1 | 89.3812 | 59.8258 | 892.3516 |  | 5925 | 21330000 | 52866000 | 84402000 | 115938000
2036-11-24 22:00 | 0 | 0 | 69.3096 | 59.8258 | 0 |  | 5926 | 21333600 | 52869600 | 84405600 | 115941600
2036-11-25 23:00 | -138.821 | 0.86223 | 67.9542 | 59.8258 | -40.6844 |  | 5927 | 21337200 | 52873200 | 84409200 | 115945200
2036-11-27 | -482.745 | 1.725 | 67.0211 | 59.8258 | -141.4786 |  | 5928 | 21340800 | 52876800 | 84412800 | 115948800
2036-11-28 01:00 | -821.795 | 2.5427 | 66.527 | 59.8258 | -240.8443 |  | 5929 | 21344400 | 52880400 | 84416400 | 115952400
2036-11-29 02:00 | -1085.56 | 3.1738 | 66.163 | 59.8258 | -318.1462 |  | 5930 | 21348000 | 52884000 | 84420000 | 115956000
2036-11-30 03:00 | -1190.97 | 3.4079 | 65.851 | 59.8258 | -349.0389 |  | 5931 | 21351600 | 52887600 | 84423600 | 115959600
2036-12-01 04:00 | -1165.66 | 3.3288 | 65.6494 | 59.8258 | -341.6212 |  | 5932 | 21355200 | 52891200 | 84427200 | 115963200
2036-12-02 05:00 | -865.247 | 2.5489 | 65.5242 | 59.8258 | -253.5789 |  | 5933 | 21358800 | 52894800 | 84430800 | 115966800
2036-12-03 06:00 | -739.952 | 2.2885 | 65.496 | 59.8258 | -216.8585 |  | 5934 | 21362400 | 52898400 | 84434400 | 115970400
2036-12-04 07:00 | -305.535 | 1.1701 | 65.6913 | 59.8258 | -89.5435 |  | 5935 | 21366000 | 52902000 | 84438000 | 115974000
2036-12-05 08:00 | 1432.74 | 1 | 66.743 | 59.8258 | 419.8946 |  | 5936 | 21369600 | 52905600 | 84441600 | 115977600
2036-12-06 09:00 | 3202.86 | 1 | 81.8092 | 59.8258 | 938.6656 |  | 5937 | 21373200 | 52909200 | 84445200 | 115981200
2036-12-07 10:00 | 6090.68 | 1.954 | 81.5982 | 59.8258 | 1785.0021 |  | 5938 | 21376800 | 52912800 | 84448800 | 115984800
2036-12-08 11:00 | 8266.8 | 2.7031 | 81.8563 | 59.8258 | 2422.7599 |  | 5939 | 21380400 | 52916400 | 84452400 | 115988400
2036-12-09 12:00 | 9861.41 | 3.1449 | 82.7989 | 59.8258 | 2890.094 |  | 5940 | 21384000 | 52920000 | 84456000 | 115992000
2036-12-10 13:00 | 10329.3 | 3.2839 | 83.4192 | 59.8258 | 3027.219 |  | 5941 | 21387600 | 52923600 | 84459600 | 115995600
2036-12-11 14:00 | 11231.8 | 3.5884 | 83.7767 | 59.8258 | 3291.7156 |  | 5942 | 21391200 | 52927200 | 84463200 | 115999200
2036-12-12 15:00 | 12773.4 | 4.0998 | 84.1321 | 59.8258 | 3743.514 |  | 5943 | 21394800 | 52930800 | 84466800 | 116002800
2036-12-13 16:00 | 13123.3 | 4.1602 | 84.8043 | 59.8258 | 3846.0596 |  | 5944 | 21398400 | 52934400 | 84470400 | 116006400
2036-12-14 17:00 | 12423.8 | 3.9545 | 85.1306 | 59.8258 | 3641.0564 |  | 5945 | 21402000 | 52938000 | 84474000 | 116010000
2036-12-15 18:00 | 10503.1 | 3.2786 | 85.6195 | 59.8258 | 3078.1548 |  | 5946 | 21405600 | 52941600 | 84477600 | 116013600
2036-12-16 19:00 | 8705.12 | 2.6831 | 85.7777 | 59.8258 | 2551.2188 |  | 5947 | 21409200 | 52945200 | 84481200 | 116017200
2036-12-17 20:00 | 6218.21 | 1.8751 | 85.9474 | 59.8258 | 1822.3775 |  | 5948 | 21412800 | 52948800 | 84484800 | 116020800
2036-12-18 21:00 | 4974.64 | 1.524 | 85.3291 | 59.8258 | 1457.9231 |  | 5949 | 21416400 | 52952400 | 84488400 | 116024400
2036-12-19 22:00 | 3179.34 | 1 | 88.2868 | 59.8258 | 931.7726 |  | 5950 | 21420000 | 52956000 | 84492000 | 116028000
2036-12-20 23:00 | 3144.04 | 1 | 69.3168 | 59.8258 | 921.4272 |  | 5951 | 21423600 | 52959600 | 84495600 | 116031600
2036-12-22 | 3038.08 | 1 | 69.0509 | 59.8258 | 890.3734 |  | 5952 | 21427200 | 52963200 | 84499200 | 116035200
2036-12-23 01:00 | 0 | 0 | 69.1315 | 59.8258 | 0 |  | 5953 | 21430800 | 52966800 | 84502800 | 116038800
2036-12-24 02:00 | -65.5069 | 0.65385 | 68.1197 | 59.8258 | -19.1982 |  | 5954 | 21434400 | 52970400 | 84506400 | 116042400
2036-12-25 03:00 | 331.493 | 1 | 68.1759 | 59.8258 | 97.151 |  | 5955 | 21438000 | 52974000 | 84510000 | 116046000
2036-12-26 04:00 | 904.505 | 1 | 67.9506 | 59.8258 | 265.0842 |  | 5956 | 21441600 | 52977600 | 84513600 | 116049600
2036-12-27 05:00 | 2133.64 | 1 | 67.7298 | 59.8258 | 625.3082 |  | 5957 | 21445200 | 52981200 | 84517200 | 116053200
2036-12-28 06:00 | 2883.7 | 1 | 67.6959 | 59.8258 | 845.129 |  | 5958 | 21448800 | 52984800 | 84520800 | 116056800
2036-12-29 07:00 | 3115.94 | 1 | 67.8047 | 59.8258 | 913.1919 |  | 5959 | 21452400 | 52988400 | 84524400 | 116060400
2036-12-30 08:00 | 3126.05 | 1 | 86.1858 | 59.8258 | 916.1548 |  | 5960 | 21456000 | 52992000 | 84528000 | 116064000
2036-12-31 09:00 | 5638.11 | 1.8266 | 82.2946 | 59.8258 | 1652.3669 |  | 5961 | 21459600 | 52995600 | 84531600 | 116067600
2037-01-01 10:00 | 7414.83 | 2.5811 | 81.6745 | 59.8258 | 2173.0722 |  | 5962 | 21463200 | 52999200 | 84535200 | 116071200
2037-01-02 11:00 | 9255.47 | 3.0921 | 82.6245 | 59.8258 | 2712.5105 |  | 5963 | 21466800 | 53002800 | 84538800 | 116074800
2037-01-03 12:00 | 10529 | 3.4291 | 83.4093 | 59.8258 | 3085.7453 |  | 5964 | 21470400 | 53006400 | 84542400 | 116078400
2037-01-04 13:00 | 10791.8 | 3.4359 | 84.1989 | 59.8258 | 3162.7644 |  | 5965 | 21474000 | 53010000 | 84546000 | 116082000
2037-01-05 14:00 | 11828.9 | 3.7976 | 84.4356 | 59.8258 | 3466.7084 |  | 5966 | 21477600 | 53013600 | 84549600 | 116085600
2037-01-06 15:00 | 13506.6 | 4.3406 | 84.7836 | 59.8258 | 3958.3937 |  | 5967 | 21481200 | 53017200 | 84553200 | 116089200
2037-01-07 16:00 | 13687.6 | 4.3711 | 85.3511 | 59.8258 | 4011.4396 |  | 5968 | 21484800 | 53020800 | 84556800 | 116092800
2037-01-08 17:00 | 13097.6 | 4.1449 | 85.8083 | 59.8258 | 3838.5276 |  | 5969 | 21488400 | 53024400 | 84560400 | 116096400
2037-01-09 18:00 | 10997.3 | 3.4865 | 85.951 | 59.8258 | 3222.9905 |  | 5970 | 21492000 | 53028000 | 84564000 | 116100000
2037-01-10 19:00 | 9270.4 | 2.8838 | 86.1443 | 59.8258 | 2716.886 |  | 5971 | 21495600 | 53031600 | 84567600 | 116103600
2037-01-11 20:00 | 7092.34 | 2.1214 | 86.5554 | 59.8258 | 2078.5597 |  | 5972 | 21499200 | 53035200 | 84571200 | 116107200
2037-01-12 21:00 | 5575.92 | 1.6877 | 86.0143 | 59.8258 | 1634.1408 |  | 5973 | 21502800 | 53038800 | 84574800 | 116110800
2037-01-13 22:00 | 3452.84 | 1.0714 | 85.2597 | 59.8258 | 1011.9275 |  | 5974 | 21506400 | 53042400 | 84578400 | 116114400
2037-01-14 23:00 | 3184.31 | 1 | 89.0635 | 59.8258 | 933.2291 |  | 5975 | 21510000 | 53046000 | 84582000 | 116118000
2037-01-16 | 3175.93 | 1 | 69.3809 | 59.8258 | 930.7732 |  | 5976 | 21513600 | 53049600 | 84585600 | 116121600
2037-01-17 01:00 | 3074.32 | 1 | 69.1891 | 59.8258 | 900.9943 |  | 5977 | 21517200 | 53053200 | 84589200 | 116125200
2037-01-18 02:00 | 3127.54 | 1 | 69.0116 | 59.8258 | 916.5915 |  | 5978 | 21520800 | 53056800 | 84592800 | 116128800
2037-01-19 03:00 | 3214.97 | 1 | 68.8581 | 59.8258 | 942.2147 |  | 5979 | 21524400 | 53060400 | 84596400 | 116132400
2037-01-20 04:00 | 3130.25 | 1 | 68.7756 | 59.8258 | 917.3857 |  | 5980 | 21528000 | 53064000 | 84600000 | 116136000
2037-01-21 05:00 | 3156.1 | 1 | 68.6687 | 59.8258 | 924.9616 |  | 5981 | 21531600 | 53067600 | 84603600 | 116139600
2037-01-22 06:00 | 3208.47 | 1 | 68.5824 | 59.8258 | 940.3097 |  | 5982 | 21535200 | 53071200 | 84607200 | 116143200
2037-01-23 07:00 | 3246.64 | 1 | 91.6318 | 59.8258 | 951.4963 |  | 5983 | 21538800 | 53074800 | 84610800 | 116146800
2037-01-24 08:00 | 3259.81 | 1 | 86.345 | 59.8258 | 955.356 |  | 5984 | 21542400 | 53078400 | 84614400 | 116150400
2037-01-25 09:00 | 5201.37 | 1.6721 | 82.9178 | 59.8258 | 1524.3711 |  | 5985 | 21546000 | 53082000 | 84618000 | 116154000
2037-01-26 10:00 | 8067.87 | 2.6876 | 82.6356 | 59.8258 | 2364.4593 |  | 5986 | 21549600 | 53085600 | 84621600 | 116157600
2037-01-27 11:00 | 10372 | 3.4397 | 83.1718 | 59.8258 | 3039.7331 |  | 5987 | 21553200 | 53089200 | 84625200 | 116161200
2037-01-28 12:00 | 10660.4 | 3.521 | 83.7794 | 59.8258 | 3124.2548 |  | 5988 | 21556800 | 53092800 | 84628800 | 116164800
2037-01-29 13:00 | 11537.6 | 3.7972 | 84.1847 | 59.8258 | 3381.3368 |  | 5989 | 21560400 | 53096400 | 84632400 | 116168400
2037-01-30 14:00 | 12718.8 | 4.0952 | 84.8617 | 59.8258 | 3727.5123 |  | 5990 | 21564000 | 53100000 | 84636000 | 116172000
2037-01-31 15:00 | 14350.4 | 4.5548 | 85.4743 | 59.8258 | 4205.6871 |  | 5991 | 21567600 | 53103600 | 84639600 | 116175600
2037-02-01 16:00 | 14470.8 | 4.5805 | 85.9861 | 59.8258 | 4240.9728 |  | 5992 | 21571200 | 53107200 | 84643200 | 116179200
2037-02-02 17:00 | 14013.5 | 4.4202 | 86.3508 | 59.8258 | 4106.9514 |  | 5993 | 21574800 | 53110800 | 84646800 | 116182800
2037-02-03 18:00 | 11778.6 | 3.7136 | 86.5686 | 59.8258 | 3451.9669 |  | 5994 | 21578400 | 53114400 | 84650400 | 116186400
2037-02-04 19:00 | 10317 | 3.1463 | 86.9815 | 59.8258 | 3023.6142 |  | 5995 | 21582000 | 53118000 | 84654000 | 116190000
2037-02-05 20:00 | 7944.78 | 2.3849 | 87.0864 | 59.8258 | 2328.3852 |  | 5996 | 21585600 | 53121600 | 84657600 | 116193600
2037-02-06 21:00 | 6567.94 | 1.9832 | 86.6514 | 59.8258 | 1924.8732 |  | 5997 | 21589200 | 53125200 | 84661200 | 116197200
2037-02-07 22:00 | 4417.8 | 1.2987 | 86.7029 | 59.8258 | 1294.7294 |  | 5998 | 21592800 | 53128800 | 84664800 | 116200800
2037-02-08 23:00 | 3085.1 | 1 | 88.0711 | 59.8258 | 904.1536 |  | 5999 | 21596400 | 53132400 | 84668400 | 116204400
2037-02-10 | 3154.16 | 1 | 69.8993 | 59.8258 | 924.393 |  | 6000 | 21600000 | 53136000 | 84672000 | 116208000
2037-02-11 01:00 | 3063.85 | 1 | 69.6304 | 59.8258 | 897.9258 |  | 6001 | 21603600 | 53139600 | 84675600 | 116211600
2037-02-12 02:00 | 3140.2 | 1 | 69.41 | 59.8258 | 920.3018 |  | 6002 | 21607200 | 53143200 | 84679200 | 116215200
2037-02-13 03:00 | 3129.83 | 1 | 69.2221 | 59.8258 | 917.2626 |  | 6003 | 21610800 | 53146800 | 84682800 | 116218800
2037-02-14 04:00 | 0 | 0 | 69.3596 | 59.8258 | 0 |  | 6004 | 21614400 | 53150400 | 84686400 | 116222400
2037-02-15 05:00 | 492.309 | 1 | 68.7712 | 59.8258 | 144.2815 |  | 6005 | 21618000 | 53154000 | 84690000 | 116226000
2037-02-16 06:00 | 2041.65 | 1 | 82.0456 | 59.8258 | 598.3486 |  | 6006 | 21621600 | 53157600 | 84693600 | 116229600
2037-02-17 07:00 | 2860.55 | 1.0213 | 81.3583 | 59.8258 | 838.3444 |  | 6007 | 21625200 | 53161200 | 84697200 | 116233200
2037-02-18 08:00 | 2986.45 | 1 | 82.3413 | 59.8258 | 875.2421 |  | 6008 | 21628800 | 53164800 | 84700800 | 116236800
2037-02-19 09:00 | 5411.75 | 1.789 | 82.4034 | 59.8258 | 1586.0274 |  | 6009 | 21632400 | 53168400 | 84704400 | 116240400
2037-02-20 10:00 | 7745.5 | 2.5955 | 82.5444 | 59.8258 | 2269.982 |  | 6010 | 21636000 | 53172000 | 84708000 | 116244000
2037-02-21 11:00 | 8800.18 | 2.918 | 83.1802 | 59.8258 | 2579.0782 |  | 6011 | 21639600 | 53175600 | 84711600 | 116247600
2037-02-22 12:00 | 9219.91 | 3.0877 | 83.4213 | 59.8258 | 2702.0889 |  | 6012 | 21643200 | 53179200 | 84715200 | 116251200
2037-02-23 13:00 | 10284.6 | 3.3744 | 83.9705 | 59.8258 | 3014.1187 |  | 6013 | 21646800 | 53182800 | 84718800 | 116254800
2037-02-24 14:00 | 10630.2 | 3.4295 | 84.5457 | 59.8258 | 3115.4041 |  | 6014 | 21650400 | 53186400 | 84722400 | 116258400
2037-02-25 15:00 | 11243.4 | 3.6556 | 84.6739 | 59.8258 | 3295.1153 |  | 6015 | 21654000 | 53190000 | 84726000 | 116262000
2037-02-26 16:00 | 13248.6 | 4.2326 | 85.1629 | 59.8258 | 3882.7814 |  | 6016 | 21657600 | 53193600 | 84729600 | 116265600
2037-02-27 17:00 | 12206.6 | 3.8519 | 85.7973 | 59.8258 | 3577.4013 |  | 6017 | 21661200 | 53197200 | 84733200 | 116269200
2037-02-28 18:00 | 10645.6 | 3.296 | 86.2546 | 59.8258 | 3119.9174 |  | 6018 | 21664800 | 53200800 | 84736800 | 116272800
2037-03-01 19:00 | 9301.28 | 2.7609 | 86.8282 | 59.8258 | 2725.9361 |  | 6019 | 21668400 | 53204400 | 84740400 | 116276400
2037-03-02 20:00 | 8458.69 | 2.5869 | 86.268 | 59.8258 | 2478.9973 |  | 6020 | 21672000 | 53208000 | 84744000 | 116280000
2037-03-03 21:00 | 7656.15 | 2.3674 | 85.9865 | 59.8258 | 2243.7961 |  | 6021 | 21675600 | 53211600 | 84747600 | 116283600
2037-03-04 22:00 | 7125.07 | 2.2117 | 85.7467 | 59.8258 | 2088.1519 |  | 6022 | 21679200 | 53215200 | 84751200 | 116287200
2037-03-05 23:00 | 4294.92 | 1.2577 | 86.4808 | 59.8258 | 1258.7168 |  | 6023 | 21682800 | 53218800 | 84754800 | 116290800
2037-03-07 | 3261.67 | 1.0138 | 85.1231 | 59.8258 | 955.9011 |  | 6024 | 21686400 | 53222400 | 84758400 | 116294400
2037-03-08 01:00 | 3342.87 | 1 | 90.0162 | 59.8258 | 979.6985 |  | 6025 | 21690000 | 53226000 | 84762000 | 116298000
2037-03-09 02:00 | 3174.91 | 1 | 91.3053 | 59.8258 | 930.4743 |  | 6026 | 21693600 | 53229600 | 84765600 | 116301600
2037-03-10 03:00 | 3272.45 | 1 | 95.0477 | 59.8258 | 959.0604 |  | 6027 | 21697200 | 53233200 | 84769200 | 116305200
2037-03-11 04:00 | 3183.12 | 1 | 69.1487 | 59.8258 | 932.8804 |  | 6028 | 21700800 | 53236800 | 84772800 | 116308800
2037-03-12 05:00 | 3187.78 | 1 | 69.0454 | 59.8258 | 934.2461 |  | 6029 | 21704400 | 53240400 | 84776400 | 116312400
2037-03-13 06:00 | 3186 | 1 | 84.3171 | 59.8258 | 933.7244 |  | 6030 | 21708000 | 53244000 | 84780000 | 116316000
2037-03-14 07:00 | 4166.09 | 1.2921 | 83.8994 | 59.8258 | 1220.9605 |  | 6031 | 21711600 | 53247600 | 84783600 | 116319600
2037-03-15 08:00 | 3309.98 | 1.0027 | 84.3296 | 59.8258 | 970.0594 |  | 6032 | 21715200 | 53251200 | 84787200 | 116323200
2037-03-16 09:00 | 3306.37 | 1.0299 | 83.7997 | 59.8258 | 969.0014 |  | 6033 | 21718800 | 53254800 | 84790800 | 116326800
2037-03-17 10:00 | 4467.21 | 1.3568 | 84.0489 | 59.8258 | 1309.21 |  | 6034 | 21722400 | 53258400 | 84794400 | 116330400
2037-03-18 11:00 | 4816.79 | 1.5063 | 83.696 | 59.8258 | 1411.6618 |  | 6035 | 21726000 | 53262000 | 84798000 | 116334000
2037-03-19 12:00 | 4850.68 | 1.6196 | 82.8394 | 59.8258 | 1421.594 |  | 6036 | 21729600 | 53265600 | 84801600 | 116337600
2037-03-20 13:00 | 7037.01 | 2.4117 | 82.4584 | 59.8258 | 2062.3441 |  | 6037 | 21733200 | 53269200 | 84805200 | 116341200
2037-03-21 14:00 | 8255.26 | 2.8618 | 82.5805 | 59.8258 | 2419.3779 |  | 6038 | 21736800 | 53272800 | 84808800 | 116344800
2037-03-22 15:00 | 8046.57 | 2.6236 | 83.7224 | 59.8258 | 2358.2169 |  | 6039 | 21740400 | 53276400 | 84812400 | 116348400
2037-03-23 16:00 | 9968.27 | 3.3022 | 83.5858 | 59.8258 | 2921.4116 |  | 6040 | 21744000 | 53280000 | 84816000 | 116352000
2037-03-24 17:00 | 9264.43 | 2.939 | 84.528 | 59.8258 | 2715.1364 |  | 6041 | 21747600 | 53283600 | 84819600 | 116355600
2037-03-25 18:00 | 8280.84 | 2.3762 | 86.2008 | 59.8258 | 2426.8746 |  | 6042 | 21751200 | 53287200 | 84823200 | 116359200
2037-03-26 19:00 | 6447.39 | 2.0513 | 84.5903 | 59.8258 | 1889.5435 |  | 6043 | 21754800 | 53290800 | 84826800 | 116362800
2037-03-27 20:00 | 5697.53 | 1.7332 | 85.0295 | 59.8258 | 1669.7812 |  | 6044 | 21758400 | 53294400 | 84830400 | 116366400
2037-03-28 21:00 | 5199.07 | 1.525 | 85.4137 | 59.8258 | 1523.697 |  | 6045 | 21762000 | 53298000 | 84834000 | 116370000
2037-03-29 22:00 | 4615.71 | 1.4291 | 84.4159 | 59.8258 | 1352.7311 |  | 6046 | 21765600 | 53301600 | 84837600 | 116373600
2037-03-30 23:00 | 3128.16 | 1 | 69.2218 | 59.8258 | 916.7732 |  | 6047 | 21769200 | 53305200 | 84841200 | 116377200
2037-04-01 | 3164.97 | 1 | 68.9293 | 59.8258 | 927.5611 |  | 6048 | 21772800 | 53308800 | 84844800 | 116380800
2037-04-02 01:00 | 3241.97 | 1 | 68.7584 | 59.8258 | 950.1276 |  | 6049 | 21776400 | 53312400 | 84848400 | 116384400
2037-04-03 02:00 | 3182.8 | 1 | 68.6641 | 59.8258 | 932.7866 |  | 6050 | 21780000 | 53316000 | 84852000 | 116388000
2037-04-04 03:00 | 3234.35 | 1 | 68.5588 | 59.8258 | 947.8944 |  | 6051 | 21783600 | 53319600 | 84855600 | 116391600
2037-04-05 04:00 | 3161.45 | 1 | 68.4725 | 59.8258 | 926.5295 |  | 6052 | 21787200 | 53323200 | 84859200 | 116395200
2037-04-06 05:00 | 3217.94 | 1 | 91.7853 | 59.8258 | 943.0851 |  | 6053 | 21790800 | 53326800 | 84862800 | 116398800
2037-04-07 06:00 | 3223.17 | 1 | 89.6046 | 59.8258 | 944.6179 |  | 6054 | 21794400 | 53330400 | 84866400 | 116402400
2037-04-08 07:00 | 3270.75 | 1 | 87.8276 | 59.8258 | 958.5622 |  | 6055 | 21798000 | 53334000 | 84870000 | 116406000
2037-04-09 08:00 | 3219.51 | 1 | 68.277 | 59.8258 | 943.5452 |  | 6056 | 21801600 | 53337600 | 84873600 | 116409600
2037-04-10 09:00 | 3360.44 | 1.0636 | 82.9948 | 59.8258 | 984.8477 |  | 6057 | 21805200 | 53341200 | 84877200 | 116413200
2037-04-11 10:00 | 4492.55 | 1.4114 | 83.0276 | 59.8258 | 1316.6364 |  | 6058 | 21808800 | 53344800 | 84880800 | 116416800
2037-04-12 11:00 | 6117.33 | 2.1436 | 81.6384 | 59.8258 | 1792.8124 |  | 6059 | 21812400 | 53348400 | 84884400 | 116420400
2037-04-13 12:00 | 7917.48 | 2.585 | 82.8587 | 59.8258 | 2320.3843 |  | 6060 | 21816000 | 53352000 | 84888000 | 116424000
2037-04-14 13:00 | 9226.24 | 3.1317 | 82.6839 | 59.8258 | 2703.944 |  | 6061 | 21819600 | 53355600 | 84891600 | 116427600
2037-04-15 14:00 | 7946.66 | 2.4368 | 84.5092 | 59.8258 | 2328.9361 |  | 6062 | 21823200 | 53359200 | 84895200 | 116431200
2037-04-16 15:00 | 9995.28 | 3.3897 | 83.131 | 59.8258 | 2929.3274 |  | 6063 | 21826800 | 53362800 | 84898800 | 116434800
2037-04-17 16:00 | 10316.2 | 3.2767 | 84.3686 | 59.8258 | 3023.3798 |  | 6064 | 21830400 | 53366400 | 84902400 | 116438400
2037-04-18 17:00 | 9738.59 | 3.0637 | 84.775 | 59.8258 | 2854.099 |  | 6065 | 21834000 | 53370000 | 84906000 | 116442000
2037-04-19 18:00 | 8180.03 | 2.5751 | 84.8462 | 59.8258 | 2397.3301 |  | 6066 | 21837600 | 53373600 | 84909600 | 116445600
2037-04-20 19:00 | 7003.7 | 2.0855 | 85.5524 | 59.8258 | 2052.5819 |  | 6067 | 21841200 | 53377200 | 84913200 | 116449200
2037-04-21 20:00 | 4929.55 | 1.415 | 85.9933 | 59.8258 | 1444.7085 |  | 6068 | 21844800 | 53380800 | 84916800 | 116452800
2037-04-22 21:00 | 3847.02 | 1.1975 | 84.4159 | 59.8258 | 1127.4503 |  | 6069 | 21848400 | 53384400 | 84920400 | 116456400
2037-04-23 22:00 | 3122.51 | 1 | 69.1265 | 59.8258 | 915.1173 |  | 6070 | 21852000 | 53388000 | 84924000 | 116460000
2037-04-24 23:00 | 3086.57 | 1 | 68.8411 | 59.8258 | 904.5844 |  | 6071 | 21855600 | 53391600 | 84927600 | 116463600
2037-04-26 | 3047.05 | 1 | 68.6423 | 59.8258 | 893.0022 |  | 6072 | 21859200 | 53395200 | 84931200 | 116467200
2037-04-27 01:00 | 3148.78 | 1 | 68.4645 | 59.8258 | 922.8163 |  | 6073 | 21862800 | 53398800 | 84934800 | 116470800
2037-04-28 02:00 | 0 | 0 | 68.6603 | 59.8258 | 0 |  | 6074 | 21866400 | 53402400 | 84938400 | 116474400
2037-04-29 03:00 | 3674.49 | 1 | 67.8062 | 59.8258 | 1076.8867 |  | 6075 | 21870000 | 53406000 | 84942000 | 116478000
2037-04-30 04:00 | 3444.51 | 1 | 67.9966 | 59.8258 | 1009.4862 |  | 6076 | 21873600 | 53409600 | 84945600 | 116481600
2037-05-01 05:00 | 3266.89 | 1 | 68.0571 | 59.8258 | 957.4309 |  | 6077 | 21877200 | 53413200 | 84949200 | 116485200
2037-05-02 06:00 | 3283.22 | 1 | 67.9795 | 59.8258 | 962.2168 |  | 6078 | 21880800 | 53416800 | 84952800 | 116488800
2037-05-03 07:00 | 3259.37 | 1 | 94.1073 | 59.8258 | 955.2271 |  | 6079 | 21884400 | 53420400 | 84956400 | 116492400
2037-05-04 08:00 | 3264.33 | 1 | 89.4841 | 59.8258 | 956.6807 |  | 6080 | 21888000 | 53424000 | 84960000 | 116496000
2037-05-05 09:00 | 3175.09 | 1 | 86.2576 | 59.8258 | 930.527 |  | 6081 | 21891600 | 53427600 | 84963600 | 116499600
2037-05-06 10:00 | 3185.6 | 1 | 83.3543 | 59.8258 | 933.6072 |  | 6082 | 21895200 | 53431200 | 84967200 | 116503200
2037-05-07 11:00 | 5907.22 | 1.9196 | 82.2082 | 59.8258 | 1731.2353 |  | 6083 | 21898800 | 53434800 | 84970800 | 116506800
2037-05-08 12:00 | 7403.68 | 2.5015 | 81.9856 | 59.8258 | 2169.8044 |  | 6084 | 21902400 | 53438400 | 84974400 | 116510400
2037-05-09 13:00 | 8505.3 | 2.8675 | 82.364 | 59.8258 | 2492.6574 |  | 6085 | 21906000 | 53442000 | 84978000 | 116514000
2037-05-10 14:00 | 10023.6 | 3.3626 | 82.7873 | 59.8258 | 2937.6272 |  | 6086 | 21909600 | 53445600 | 84981600 | 116517600
2037-05-11 15:00 | 11778.5 | 3.938 | 83.2276 | 59.8258 | 3451.9376 |  | 6087 | 21913200 | 53449200 | 84985200 | 116521200
2037-05-12 16:00 | 11779 | 3.8173 | 84.1715 | 59.8258 | 3452.0841 |  | 6088 | 21916800 | 53452800 | 84988800 | 116524800
2037-05-13 17:00 | 11462.8 | 3.6052 | 84.9078 | 59.8258 | 3359.4151 |  | 6089 | 21920400 | 53456400 | 84992400 | 116528400
2037-05-14 18:00 | 9475.3 | 2.8836 | 85.5883 | 59.8258 | 2776.9363 |  | 6090 | 21924000 | 53460000 | 84996000 | 116532000
2037-05-15 19:00 | 8135.68 | 2.4298 | 85.8021 | 59.8258 | 2384.3324 |  | 6091 | 21927600 | 53463600 | 84999600 | 116535600
2037-05-16 20:00 | 5598.06 | 1.6584 | 85.7877 | 59.8258 | 1640.6294 |  | 6092 | 21931200 | 53467200 | 85003200 | 116539200
2037-05-17 21:00 | 4426.08 | 1.3705 | 84.7444 | 59.8258 | 1297.156 |  | 6093 | 21934800 | 53470800 | 85006800 | 116542800
2037-05-18 22:00 | 3158.69 | 1 | 93.3796 | 59.8258 | 925.7207 |  | 6094 | 21938400 | 53474400 | 85010400 | 116546400
2037-05-19 23:00 | 3127.21 | 1 | 69.0007 | 59.8258 | 916.4948 |  | 6095 | 21942000 | 53478000 | 85014000 | 116550000
2037-05-21 | 2918.57 | 1 | 68.7905 | 59.8258 | 855.3484 |  | 6096 | 21945600 | 53481600 | 85017600 | 116553600
2037-05-22 01:00 | 207.365 | 1 | 68.8316 | 59.8258 | 60.7727 |  | 6097 | 21949200 | 53485200 | 85021200 | 116557200
2037-05-23 02:00 | -54.415 | 0.66423 | 67.9721 | 59.8258 | -15.9475 |  | 6098 | 21952800 | 53488800 | 85024800 | 116560800
2037-05-24 03:00 | 44.3455 | 1 | 67.9519 | 59.8258 | 12.9964 |  | 6099 | 21956400 | 53492400 | 85028400 | 116564400
2037-05-25 04:00 | -16.83 | 0.56433 | 67.7354 | 59.8258 | -4.9324 |  | 6100 | 21960000 | 53496000 | 85032000 | 116568000
2037-05-26 05:00 | 1991.75 | 1 | 67.306 | 59.8258 | 583.7243 |  | 6101 | 21963600 | 53499600 | 85035600 | 116571600
2037-05-27 06:01 | 2718.74 | 1 | 67.3042 | 59.8258 | 796.784 |  | 6102 | 21967200 | 53503200 | 85039200 | 116575200
2037-05-28 07:01 | 3127.01 | 1 | 67.3937 | 59.8258 | 916.4362 |  | 6103 | 21970800 | 53506800 | 85042800 | 116578800
2037-05-29 08:01 | 3255.43 | 1 | 67.4886 | 59.8258 | 954.0724 |  | 6104 | 21974400 | 53510400 | 85046400 | 116582400
2037-05-30 09:01 | 3612.42 | 1.1066 | 82.806 | 59.8258 | 1058.6958 |  | 6105 | 21978000 | 53514000 | 85050000 | 116586000
2037-05-31 10:01 | 5602.92 | 1.8119 | 82.0855 | 59.8258 | 1642.0538 |  | 6106 | 21981600 | 53517600 | 85053600 | 116589600
2037-06-01 11:01 | 7621.84 | 2.5966 | 81.6543 | 59.8258 | 2233.7408 |  | 6107 | 21985200 | 53521200 | 85057200 | 116593200
2037-06-02 12:01 | 8425.8 | 2.812 | 82.3458 | 59.8258 | 2469.3582 |  | 6108 | 21988800 | 53524800 | 85060800 | 116596800
2037-06-03 13:01 | 8995.56 | 2.9534 | 82.9191 | 59.8258 | 2636.3384 |  | 6109 | 21992400 | 53528400 | 85064400 | 116600400
2037-06-04 14:01 | 9339.87 | 3.0182 | 83.4461 | 59.8258 | 2737.2457 |  | 6110 | 21996000 | 53532000 | 85068000 | 116604000
2037-06-05 15:01 | 11738 | 3.8471 | 83.5024 | 59.8258 | 3440.0682 |  | 6111 | 21999600 | 53535600 | 85071600 | 116607600
2037-06-06 16:01 | 11450.8 | 3.6943 | 84.2314 | 59.8258 | 3355.8982 |  | 6112 | 22003200 | 53539200 | 85075200 | 116611200
2037-06-07 17:01 | 10996.6 | 3.51 | 84.6406 | 59.8258 | 3222.7853 |  | 6113 | 22006800 | 53542800 | 85078800 | 116614800
2037-06-08 18:01 | 9348.59 | 2.9047 | 85.1598 | 59.8258 | 2739.8013 |  | 6114 | 22010400 | 53546400 | 85082400 | 116618400
2037-06-09 19:01 | 7814.93 | 2.3356 | 85.6778 | 59.8258 | 2290.3299 |  | 6115 | 22014000 | 53550000 | 85086000 | 116622000
2037-06-10 20:01 | 5621.56 | 1.6412 | 85.8919 | 59.8258 | 1647.5166 |  | 6116 | 22017600 | 53553600 | 85089600 | 116625600
2037-06-11 21:01 | 4278.19 | 1.3461 | 84.41 | 59.8258 | 1253.8137 |  | 6117 | 22021200 | 53557200 | 85093200 | 116629200
2037-06-12 22:01 | 3078.59 | 1 | 69.2582 | 59.8258 | 902.2457 |  | 6118 | 22024800 | 53560800 | 85096800 | 116632800
2037-06-13 23:01 | 3098.69 | 1 | 68.8737 | 59.8258 | 908.1364 |  | 6119 | 22028400 | 53564400 | 85100400 | 116636400
2037-06-15 00:01 | 1760.57 | 1 | 68.7549 | 59.8258 | 515.9721 |  | 6120 | 22032000 | 53568000 | 85104000 | 116640000
2037-06-16 01:01 | 103.908 | 1 | 68.5651 | 59.8258 | 30.4524 |  | 6121 | 22035600 | 53571600 | 85107600 | 116643600
2037-06-17 02:01 | -132.68 | 0.85742 | 67.4322 | 59.8258 | -38.8847 |  | 6122 | 22039200 | 53575200 | 85111200 | 116647200
2037-06-18 03:01 | -90.5637 | 0.72316 | 67.2339 | 59.8258 | -26.5416 |  | 6123 | 22042800 | 53578800 | 85114800 | 116650800
2037-06-19 04:01 | 119.274 | 1 | 67.5724 | 59.8258 | 34.9558 |  | 6124 | 22046400 | 53582400 | 85118400 | 116654400
2037-06-20 05:01 | 1883.7 | 1 | 67.2165 | 59.8258 | 552.058 |  | 6125 | 22050000 | 53586000 | 85122000 | 116658000
2037-06-21 06:01 | 2848.69 | 1 | 67.2052 | 59.8258 | 834.8686 |  | 6126 | 22053600 | 53589600 | 85125600 | 116661600
2037-06-22 07:01 | 3140.86 | 1 | 67.3298 | 59.8258 | 920.4952 |  | 6127 | 22057200 | 53593200 | 85129200 | 116665200
2037-06-23 08:01 | 3178.76 | 1 | 67.4312 | 59.8258 | 931.6026 |  | 6128 | 22060800 | 53596800 | 85132800 | 116668800
2037-06-24 09:01 | 4379.76 | 1.3315 | 82.842 | 59.8258 | 1283.5809 |  | 6129 | 22064400 | 53600400 | 85136400 | 116672400
2037-06-25 10:01 | 7458.76 | 2.5341 | 81.4209 | 59.8258 | 2185.9468 |  | 6130 | 22068000 | 53604000 | 85140000 | 116676000
2037-06-26 11:01 | 9893.21 | 3.302 | 82.158 | 59.8258 | 2899.4136 |  | 6131 | 22071600 | 53607600 | 85143600 | 116679600
2037-06-27 12:01 | 10741.3 | 3.6016 | 82.6936 | 59.8258 | 3147.9643 |  | 6132 | 22075200 | 53611200 | 85147200 | 116683200
2037-06-28 13:01 | 11196.8 | 3.6626 | 83.5104 | 59.8258 | 3281.4582 |  | 6133 | 22078800 | 53614800 | 85150800 | 116686800
2037-06-29 14:01 | 12642.4 | 4.0693 | 84.1311 | 59.8258 | 3705.1217 |  | 6134 | 22082400 | 53618400 | 85154400 | 116690400
2037-06-30 15:01 | 13679.1 | 4.3836 | 84.6842 | 59.8258 | 4008.9485 |  | 6135 | 22086000 | 53622000 | 85158000 | 116694000
2037-07-01 16:01 | 13438.2 | 4.3044 | 85.1575 | 59.8258 | 3938.3477 |  | 6136 | 22089600 | 53625600 | 85161600 | 116697600
2037-07-02 17:01 | 12884.8 | 4.0466 | 85.6977 | 59.8258 | 3776.1621 |  | 6137 | 22093200 | 53629200 | 85165200 | 116701200
2037-07-03 18:01 | 10583.9 | 3.3186 | 85.8759 | 59.8258 | 3101.8349 |  | 6138 | 22096800 | 53632800 | 85168800 | 116704800
2037-07-04 19:01 | 8964.74 | 2.7345 | 86.1638 | 59.8258 | 2627.3059 |  | 6139 | 22100400 | 53636400 | 85172400 | 116708400
2037-07-05 20:01 | 6665.56 | 1.9669 | 86.4706 | 59.8258 | 1953.4828 |  | 6140 | 22104000 | 53640000 | 85176000 | 116712000
2037-07-06 21:01 | 5521.71 | 1.6629 | 85.788 | 59.8258 | 1618.2535 |  | 6141 | 22107600 | 53643600 | 85179600 | 116715600
2037-07-07 22:01 | 3293.49 | 1 | 87.8698 | 59.8258 | 965.2266 |  | 6142 | 22111200 | 53647200 | 85183200 | 116719200
2037-07-08 23:01 | 3231.62 | 1 | 69.449 | 59.8258 | 947.0943 |  | 6143 | 22114800 | 53650800 | 85186800 | 116722800
2037-07-10 00:01 | 3095.27 | 1 | 69.1425 | 59.8258 | 907.1341 |  | 6144 | 22118400 | 53654400 | 85190400 | 116726400
2037-07-11 01:01 | 3156.08 | 1 | 68.9236 | 59.8258 | 924.9557 |  | 6145 | 22122000 | 53658000 | 85194000 | 116730000
2037-07-12 02:01 | 3105.83 | 1 | 68.7717 | 59.8258 | 910.2289 |  | 6146 | 22125600 | 53661600 | 85197600 | 116733600
2037-07-13 03:01 | 3172.26 | 1 | 68.6168 | 59.8258 | 929.6976 |  | 6147 | 22129200 | 53665200 | 85201200 | 116737200
2037-07-14 04:01 | 3155.37 | 1 | 68.5311 | 59.8258 | 924.7477 |  | 6148 | 22132800 | 53668800 | 85204800 | 116740800
2037-07-15 05:01 | 3159.29 | 1 | 68.4296 | 59.8258 | 925.8965 |  | 6149 | 22136400 | 53672400 | 85208400 | 116744400
2037-07-16 06:01 | 3194.84 | 1 | 68.3456 | 59.8258 | 936.3152 |  | 6150 | 22140000 | 53676000 | 85212000 | 116748000
2037-07-17 07:01 | 3219.68 | 1 | 92.3329 | 59.8258 | 943.5951 |  | 6151 | 22143600 | 53679600 | 85215600 | 116751600
2037-07-18 08:01 | 3264.31 | 1 | 89.0444 | 59.8258 | 956.6748 |  | 6152 | 22147200 | 53683200 | 85219200 | 116755200
2037-07-19 09:01 | 5111.16 | 1.618 | 82.9089 | 59.8258 | 1497.9331 |  | 6153 | 22150800 | 53686800 | 85222800 | 116758800
2037-07-20 10:01 | 6652.87 | 2.1949 | 82.5483 | 59.8258 | 1949.7637 |  | 6154 | 22154400 | 53690400 | 85226400 | 116762400
2037-07-21 11:01 | 9298.05 | 3.1282 | 82.5677 | 59.8258 | 2724.9895 |  | 6155 | 22158000 | 53694000 | 85230000 | 116766000
2037-07-22 12:01 | 10468.8 | 3.5539 | 82.9397 | 59.8258 | 3068.1024 |  | 6156 | 22161600 | 53697600 | 85233600 | 116769600
2037-07-23 13:01 | 10523 | 3.3938 | 84.0948 | 59.8258 | 3083.9869 |  | 6157 | 22165200 | 53701200 | 85237200 | 116773200
2037-07-24 14:01 | 11170.9 | 3.59 | 84.4286 | 59.8258 | 3273.8676 |  | 6158 | 22168800 | 53704800 | 85240800 | 116776800
2037-07-25 15:01 | 12744.4 | 4.1591 | 84.4773 | 59.8258 | 3735.0149 |  | 6159 | 22172400 | 53708400 | 85244400 | 116780400
2037-07-26 16:01 | 12934.9 | 4.119 | 85.2401 | 59.8258 | 3790.845 |  | 6160 | 22176000 | 53712000 | 85248000 | 116784000
2037-07-27 17:01 | 12153.1 | 3.8603 | 85.555 | 59.8258 | 3561.722 |  | 6161 | 22179600 | 53715600 | 85251600 | 116787600
2037-07-28 18:01 | 10136.1 | 3.1209 | 86.1186 | 59.8258 | 2970.5977 |  | 6162 | 22183200 | 53719200 | 85255200 | 116791200
2037-07-29 19:01 | 8660.26 | 2.6719 | 85.9725 | 59.8258 | 2538.0717 |  | 6163 | 22186800 | 53722800 | 85258800 | 116794800
2037-07-30 20:01 | 6293.09 | 1.8844 | 86.2602 | 59.8258 | 1844.3226 |  | 6164 | 22190400 | 53726400 | 85262400 | 116798400
2037-07-31 21:01 | 4969.69 | 1.4915 | 85.8444 | 59.8258 | 1456.4724 |  | 6165 | 22194000 | 53730000 | 85266000 | 116802000
2037-08-01 22:01 | 3183.85 | 1 | 88.2993 | 59.8258 | 933.0943 |  | 6166 | 22197600 | 53733600 | 85269600 | 116805600
2037-08-02 23:01 | 3040.59 | 1 | 69.497 | 59.8258 | 891.109 |  | 6167 | 22201200 | 53737200 | 85273200 | 116809200
2037-08-04 00:01 | 0 | 0 | 69.46 | 59.8258 | 0 |  | 6168 | 22204800 | 53740800 | 85276800 | 116812800
2037-08-05 01:01 | -116.014 | 0.84035 | 68.1999 | 59.8258 | -34.0003 |  | 6169 | 22208400 | 53744400 | 85280400 | 116816400
2037-08-06 02:01 | -255.45 | 1.1422 | 67.3943 | 59.8258 | -74.865 |  | 6170 | 22212000 | 53748000 | 85284000 | 116820000
2037-08-07 03:01 | -509.212 | 1.7748 | 66.7905 | 59.8258 | -149.2353 |  | 6171 | 22215600 | 53751600 | 85287600 | 116823600
2037-08-08 04:01 | -753.813 | 2.3674 | 66.3477 | 59.8258 | -220.9208 |  | 6172 | 22219200 | 53755200 | 85291200 | 116827200
2037-08-09 05:01 | -947.702 | 2.8348 | 65.9691 | 59.8258 | -277.744 |  | 6173 | 22222800 | 53758800 | 85294800 | 116830800
2037-08-10 06:01 | -305.55 | 1.1181 | 66.0249 | 59.8258 | -89.5479 |  | 6174 | 22226400 | 53762400 | 85298400 | 116834400
2037-08-11 07:01 | 2289.84 | 1 | 66.9762 | 59.8258 | 671.0859 |  | 6175 | 22230000 | 53766000 | 85302000 | 116838000
2037-08-12 08:01 | 3021.53 | 1 | 67.169 | 59.8258 | 885.523 |  | 6176 | 22233600 | 53769600 | 85305600 | 116841600
2037-08-13 09:01 | 3166.99 | 1 | 82.1781 | 59.8258 | 928.1531 |  | 6177 | 22237200 | 53773200 | 85309200 | 116845200
2037-08-14 10:01 | 5806.14 | 1.88 | 81.813 | 59.8258 | 1701.6117 |  | 6178 | 22240800 | 53776800 | 85312800 | 116848800
2037-08-15 11:01 | 7547.81 | 2.6042 | 81.3305 | 59.8258 | 2212.0448 |  | 6179 | 22244400 | 53780400 | 85316400 | 116852400
2037-08-16 12:01 | 8866.87 | 2.9963 | 82.0886 | 59.8258 | 2598.6231 |  | 6180 | 22248000 | 53784000 | 85320000 | 116856000
2037-08-17 13:01 | 9563.17 | 3.1461 | 82.8657 | 59.8258 | 2802.6885 |  | 6181 | 22251600 | 53787600 | 85323600 | 116859600
2037-08-18 14:01 | 10170.9 | 3.2572 | 83.5884 | 59.8258 | 2980.7965 |  | 6182 | 22255200 | 53791200 | 85327200 | 116863200
2037-08-19 15:01 | 10218.7 | 3.2944 | 83.8224 | 59.8258 | 2994.8053 |  | 6183 | 22258800 | 53794800 | 85330800 | 116866800
2037-08-20 16:01 | 12166.6 | 3.921 | 84.0384 | 59.8258 | 3565.6785 |  | 6184 | 22262400 | 53798400 | 85334400 | 116870400
2037-08-21 17:01 | 10693.4 | 3.3684 | 84.805 | 59.8258 | 3133.9262 |  | 6185 | 22266000 | 53802000 | 85338000 | 116874000
2037-08-22 18:01 | 8827.86 | 2.7572 | 85.0416 | 59.8258 | 2587.1904 |  | 6186 | 22269600 | 53805600 | 85341600 | 116877600
2037-08-23 19:01 | 7367.74 | 2.2728 | 85.0681 | 59.8258 | 2159.2714 |  | 6187 | 22273200 | 53809200 | 85345200 | 116881200
2037-08-24 20:01 | 6419.06 | 1.9703 | 84.9457 | 59.8258 | 1881.2408 |  | 6188 | 22276800 | 53812800 | 85348800 | 116884800
2037-08-25 21:01 | 5557.14 | 1.6643 | 85.1481 | 59.8258 | 1628.637 |  | 6189 | 22280400 | 53816400 | 85352400 | 116888400
2037-08-26 22:01 | 4416.17 | 1.3235 | 84.9032 | 59.8258 | 1294.2517 |  | 6190 | 22284000 | 53820000 | 85356000 | 116892000
2037-08-27 23:01 | 3085.31 | 1 | 69.0972 | 59.8258 | 904.2151 |  | 6191 | 22287600 | 53823600 | 85359600 | 116895600
2037-08-29 00:01 | 0 | 0 | 69.0421 | 59.8258 | 0 |  | 6192 | 22291200 | 53827200 | 85363200 | 116899200
2037-08-30 01:01 | -113.037 | 0.77811 | 67.7591 | 59.8258 | -33.1279 |  | 6193 | 22294800 | 53830800 | 85366800 | 116902800
2037-08-31 02:01 | -456.086 | 1.6676 | 66.7769 | 59.8258 | -133.6656 |  | 6194 | 22298400 | 53834400 | 85370400 | 116906400
2037-09-01 03:01 | -569.417 | 1.8982 | 66.3462 | 59.8258 | -166.8796 |  | 6195 | 22302000 | 53838000 | 85374000 | 116910000
2037-09-02 04:01 | -858.235 | 2.641 | 65.9387 | 59.8258 | -251.5238 |  | 6196 | 22305600 | 53841600 | 85377600 | 116913600
2037-09-03 05:01 | -870.804 | 2.6205 | 65.6345 | 59.8258 | -255.2075 |  | 6197 | 22309200 | 53845200 | 85381200 | 116917200
2037-09-04 06:01 | -222.638 | 0.92275 | 65.8829 | 59.8258 | -65.2488 |  | 6198 | 22312800 | 53848800 | 85384800 | 116920800
2037-09-05 07:01 | 2196.48 | 1 | 66.728 | 59.8258 | 643.7247 |  | 6199 | 22316400 | 53852400 | 85388400 | 116924400
2037-09-06 08:01 | 2942.99 | 1 | 66.905 | 59.8258 | 862.5052 |  | 6200 | 22320000 | 53856000 | 85392000 | 116928000
2037-09-07 09:01 | 3532.66 | 1.1394 | 81.5541 | 59.8258 | 1035.3204 |  | 6201 | 22323600 | 53859600 | 85395600 | 116931600
2037-09-08 10:01 | 6630.58 | 2.1637 | 81.477 | 59.8258 | 1943.2312 |  | 6202 | 22327200 | 53863200 | 85399200 | 116935200
2037-09-09 11:01 | 8583.48 | 2.9236 | 81.3781 | 59.8258 | 2515.5697 |  | 6203 | 22330800 | 53866800 | 85402800 | 116938800
2037-09-10 12:01 | 9878.84 | 3.3529 | 81.9962 | 59.8258 | 2895.2022 |  | 6204 | 22334400 | 53870400 | 85406400 | 116942400
2037-09-11 13:01 | 10777.2 | 3.5116 | 83.0275 | 59.8258 | 3158.4855 |  | 6205 | 22338000 | 53874000 | 85410000 | 116946000
2037-09-12 14:01 | 11535.2 | 3.7828 | 83.3704 | 59.8258 | 3380.6334 |  | 6206 | 22341600 | 53877600 | 85413600 | 116949600
2037-09-13 15:01 | 11806.5 | 3.8173 | 83.9922 | 59.8258 | 3460.1436 |  | 6207 | 22345200 | 53881200 | 85417200 | 116953200
2037-09-14 16:01 | 13833.7 | 4.3981 | 84.529 | 59.8258 | 4054.2573 |  | 6208 | 22348800 | 53884800 | 85420800 | 116956800
2037-09-15 17:01 | 12013.5 | 3.7983 | 85.1276 | 59.8258 | 3520.8093 |  | 6209 | 22352400 | 53888400 | 85424400 | 116960400
2037-09-16 18:01 | 10095.8 | 3.1134 | 85.6227 | 59.8258 | 2958.7869 |  | 6210 | 22356000 | 53892000 | 85428000 | 116964000
2037-09-17 19:01 | 8345.66 | 2.5818 | 85.4455 | 59.8258 | 2445.8715 |  | 6211 | 22359600 | 53895600 | 85431600 | 116967600
2037-09-18 20:01 | 7307.08 | 2.2638 | 85.2146 | 59.8258 | 2141.4938 |  | 6212 | 22363200 | 53899200 | 85435200 | 116971200
2037-09-19 21:01 | 6194.59 | 1.9092 | 85.1038 | 59.8258 | 1815.4551 |  | 6213 | 22366800 | 53902800 | 85438800 | 116974800
2037-09-20 22:01 | 5308.14 | 1.6508 | 84.6827 | 59.8258 | 1555.6623 |  | 6214 | 22370400 | 53906400 | 85442400 | 116978400
2037-09-21 23:01 | 3299.92 | 1 | 90.8922 | 59.8258 | 967.1111 |  | 6215 | 22374000 | 53910000 | 85446000 | 116982000
2037-09-23 00:01 | 3239.52 | 1 | 69.0177 | 59.8258 | 949.4096 |  | 6216 | 22377600 | 53913600 | 85449600 | 116985600
2037-09-24 01:01 | 3154.55 | 1 | 68.791 | 59.8258 | 924.5073 |  | 6217 | 22381200 | 53917200 | 85453200 | 116989200
2037-09-25 02:01 | 3220.83 | 1 | 68.621 | 59.8258 | 943.9321 |  | 6218 | 22384800 | 53920800 | 85456800 | 116992800
2037-09-26 03:01 | 3195.87 | 1 | 68.4988 | 59.8258 | 936.617 |  | 6219 | 22388400 | 53924400 | 85460400 | 116996400
2037-09-27 04:01 | 3112.96 | 1 | 68.3768 | 59.8258 | 912.3185 |  | 6220 | 22392000 | 53928000 | 85464000 | 117000000
2037-09-28 05:01 | 3127.64 | 1 | 68.2983 | 59.8258 | 916.6208 |  | 6221 | 22395600 | 53931600 | 85467600 | 117003600
2037-09-29 06:01 | 3169.91 | 1 | 68.2409 | 59.8258 | 929.0089 |  | 6222 | 22399200 | 53935200 | 85471200 | 117007200
2037-09-30 07:01 | 3357.38 | 1 | 92.7127 | 59.8258 | 983.9509 |  | 6223 | 22402800 | 53938800 | 85474800 | 117010800
2037-10-01 08:01 | 3241.7 | 1 | 85.0804 | 59.8258 | 950.0485 |  | 6224 | 22406400 | 53942400 | 85478400 | 117014400
2037-10-02 09:01 | 5763.71 | 1.8293 | 82.7864 | 59.8258 | 1689.1767 |  | 6225 | 22410000 | 53946000 | 85482000 | 117018000
2037-10-03 10:01 | 7772.07 | 2.5719 | 82.4773 | 59.8258 | 2277.7689 |  | 6226 | 22413600 | 53949600 | 85485600 | 117021600
2037-10-04 11:01 | 8737.04 | 2.8174 | 83.2564 | 59.8258 | 2560.5737 |  | 6227 | 22417200 | 53953200 | 85489200 | 117025200
2037-10-05 12:01 | 10334.7 | 3.4212 | 83.2192 | 59.8258 | 3028.8016 |  | 6228 | 22420800 | 53956800 | 85492800 | 117028800
2037-10-06 13:01 | 11304.2 | 3.7034 | 83.7796 | 59.8258 | 3312.934 |  | 6229 | 22424400 | 53960400 | 85496400 | 117032400
2037-10-07 14:01 | 11690.5 | 3.7656 | 84.4367 | 59.8258 | 3426.1473 |  | 6230 | 22428000 | 53964000 | 85500000 | 117036000
2037-10-08 15:01 | 13092.7 | 4.1836 | 84.847 | 59.8258 | 3837.0916 |  | 6231 | 22431600 | 53967600 | 85503600 | 117039600
2037-10-09 16:01 | 13337.3 | 4.2035 | 85.419 | 59.8258 | 3908.7768 |  | 6232 | 22435200 | 53971200 | 85507200 | 117043200
2037-10-10 17:01 | 12629.2 | 3.9656 | 85.7859 | 59.8258 | 3701.2532 |  | 6233 | 22438800 | 53974800 | 85510800 | 117046800
2037-10-11 18:01 | 11006.5 | 3.4291 | 86.044 | 59.8258 | 3225.6867 |  | 6234 | 22442400 | 53978400 | 85514400 | 117050400
2037-10-12 19:01 | 9752.37 | 2.9672 | 86.3415 | 59.8258 | 2858.1375 |  | 6235 | 22446000 | 53982000 | 85518000 | 117054000
2037-10-13 20:01 | 7661.01 | 2.2502 | 86.7806 | 59.8258 | 2245.2204 |  | 6236 | 22449600 | 53985600 | 85521600 | 117057600
2037-10-14 21:01 | 6476.02 | 1.9495 | 86.0905 | 59.8258 | 1897.9341 |  | 6237 | 22453200 | 53989200 | 85525200 | 117061200
2037-10-15 22:01 | 4512.68 | 1.3458 | 85.9119 | 59.8258 | 1322.536 |  | 6238 | 22456800 | 53992800 | 85528800 | 117064800
2037-10-16 23:01 | 3960.09 | 1.2065 | 85.1518 | 59.8258 | 1160.5878 |  | 6239 | 22460400 | 53996400 | 85532400 | 117068400
2037-10-18 00:01 | 3370.15 | 1 | 86.6847 | 59.8258 | 987.6935 |  | 6240 | 22464000 | 54000000 | 85536000 | 117072000
2037-10-19 01:01 | 3171.09 | 1 | 87.5167 | 59.8258 | 929.3547 |  | 6241 | 22467600 | 54003600 | 85539600 | 117075600
2037-10-20 02:01 | 3144.74 | 1 | 87.2052 | 59.8258 | 921.6323 |  | 6242 | 22471200 | 54007200 | 85543200 | 117079200
2037-10-21 03:01 | 3288.25 | 1 | 86.5175 | 59.8258 | 963.6909 |  | 6243 | 22474800 | 54010800 | 85546800 | 117082800
2037-10-22 04:01 | 3151.37 | 1 | 83.3996 | 59.8258 | 923.5754 |  | 6244 | 22478400 | 54014400 | 85550400 | 117086400
2037-10-23 05:01 | 4039.28 | 1.2678 | 83.4308 | 59.8258 | 1183.7961 |  | 6245 | 22482000 | 54018000 | 85554000 | 117090000
2037-10-24 06:01 | 4011.26 | 1.2464 | 83.6099 | 59.8258 | 1175.5843 |  | 6246 | 22485600 | 54021600 | 85557600 | 117093600
2037-10-25 07:01 | 5067.05 | 1.604 | 83.3251 | 59.8258 | 1485.0058 |  | 6247 | 22489200 | 54025200 | 85561200 | 117097200
2037-10-26 08:01 | 5240.4 | 1.6757 | 83.3099 | 59.8258 | 1535.8096 |  | 6248 | 22492800 | 54028800 | 85564800 | 117100800
2037-10-27 09:01 | 6887.46 | 2.367 | 82.3936 | 59.8258 | 2018.5153 |  | 6249 | 22496400 | 54032400 | 85568400 | 117104400
2037-10-28 10:01 | 9540.8 | 3.254 | 82.7493 | 59.8258 | 2796.1325 |  | 6250 | 22500000 | 54036000 | 85572000 | 117108000
2037-10-29 11:01 | 10385.5 | 3.5258 | 83.3035 | 59.8258 | 3043.6896 |  | 6251 | 22503600 | 54039600 | 85575600 | 117111600
2037-10-30 12:01 | 11975.1 | 4.0644 | 83.6952 | 59.8258 | 3509.5554 |  | 6252 | 22507200 | 54043200 | 85579200 | 117115200
2037-10-31 13:01 | 13365.2 | 4.5456 | 84.1031 | 59.8258 | 3916.9535 |  | 6253 | 22510800 | 54046800 | 85582800 | 117118800
2037-11-01 14:01 | 14032.7 | 4.5929 | 85.1302 | 59.8258 | 4112.5784 |  | 6254 | 22514400 | 54050400 | 85586400 | 117122400
2037-11-02 15:01 | 15505.6 | 5.0145 | 85.7012 | 59.8258 | 4544.2428 |  | 6255 | 22518000 | 54054000 | 85590000 | 117126000
2037-11-03 16:01 | 15328 | 4.8491 | 86.4748 | 59.8258 | 4492.1934 |  | 6256 | 22521600 | 54057600 | 85593600 | 117129600
2037-11-04 17:01 | 14591.6 | 4.6103 | 86.8059 | 59.8258 | 4276.3758 |  | 6257 | 22525200 | 54061200 | 85597200 | 117133200
2037-11-05 18:01 | 12205.5 | 3.8418 | 87.0247 | 59.8258 | 3577.0789 |  | 6258 | 22528800 | 54064800 | 85600800 | 117136800
2037-11-06 19:01 | 10566.4 | 3.2023 | 87.439 | 59.8258 | 3096.7062 |  | 6259 | 22532400 | 54068400 | 85604400 | 117140400
2037-11-07 20:01 | 8113.26 | 2.452 | 87.2788 | 59.8258 | 2377.7618 |  | 6260 | 22536000 | 54072000 | 85608000 | 117144000
2037-11-08 21:01 | 6785.99 | 2.0299 | 87.0297 | 59.8258 | 1988.7774 |  | 6261 | 22539600 | 54075600 | 85611600 | 117147600
2037-11-09 22:01 | 4428 | 1.2887 | 87.059 | 59.8258 | 1297.7187 |  | 6262 | 22543200 | 54079200 | 85615200 | 117151200
2037-11-10 23:01 | 3364.32 | 1.0577 | 85.3472 | 59.8258 | 985.9849 |  | 6263 | 22546800 | 54082800 | 85618800 | 117154800
2037-11-12 00:01 | 3208.58 | 1 | 89.6723 | 59.8258 | 940.342 |  | 6264 | 22550400 | 54086400 | 85622400 | 117158400
2037-11-13 01:01 | 3097.81 | 1 | 69.7436 | 59.8258 | 907.8785 |  | 6265 | 22554000 | 54090000 | 85626000 | 117162000
2037-11-14 02:01 | 3140.03 | 1 | 69.4991 | 59.8258 | 920.252 |  | 6266 | 22557600 | 54093600 | 85629600 | 117165600
2037-11-15 03:01 | 3156.48 | 1 | 69.2775 | 59.8258 | 925.073 |  | 6267 | 22561200 | 54097200 | 85633200 | 117169200
2037-11-16 04:01 | 3182.62 | 1 | 69.1161 | 59.8258 | 932.7338 |  | 6268 | 22564800 | 54100800 | 85636800 | 117172800
2037-11-17 05:01 | 3136.9 | 1 | 93.0961 | 59.8258 | 919.3346 |  | 6269 | 22568400 | 54104400 | 85640400 | 117176400
2037-11-18 06:01 | 3183.6 | 1 | 93.3897 | 59.8258 | 933.0211 |  | 6270 | 22572000 | 54108000 | 85644000 | 117180000
2037-11-19 07:01 | 3220.12 | 1 | 83.7719 | 59.8258 | 943.724 |  | 6271 | 22575600 | 54111600 | 85647600 | 117183600
2037-11-20 08:01 | 4488.85 | 1.3779 | 83.8787 | 59.8258 | 1315.5521 |  | 6272 | 22579200 | 54115200 | 85651200 | 117187200
2037-11-21 09:01 | 7068.15 | 2.3269 | 82.966 | 59.8258 | 2071.4703 |  | 6273 | 22582800 | 54118800 | 85654800 | 117190800
2037-11-22 10:01 | 9745.35 | 3.2477 | 83.173 | 59.8258 | 2856.0802 |  | 6274 | 22586400 | 54122400 | 85658400 | 117194400
2037-11-23 11:01 | 11915.6 | 3.9104 | 83.9375 | 59.8258 | 3492.1176 |  | 6275 | 22590000 | 54126000 | 85662000 | 117198000
2037-11-24 12:01 | 13094.6 | 4.2407 | 84.7187 | 59.8258 | 3837.6484 |  | 6276 | 22593600 | 54129600 | 85665600 | 117201600
2037-11-25 13:01 | 13179.5 | 4.377 | 84.9021 | 59.8258 | 3862.5302 |  | 6277 | 22597200 | 54133200 | 85669200 | 117205200
2037-11-26 14:01 | 13050.8 | 4.2048 | 85.6955 | 59.8258 | 3824.8119 |  | 6278 | 22600800 | 54136800 | 85672800 | 117208800
2037-11-27 15:01 | 14893.1 | 4.7962 | 85.9254 | 59.8258 | 4364.7368 |  | 6279 | 22604400 | 54140400 | 85676400 | 117212400
2037-11-28 16:01 | 15252.3 | 4.8594 | 86.501 | 59.8258 | 4470.0079 |  | 6280 | 22608000 | 54144000 | 85680000 | 117216000
2037-11-29 17:01 | 14455.3 | 4.546 | 87.0254 | 59.8258 | 4236.4302 |  | 6281 | 22611600 | 54147600 | 85683600 | 117219600
2037-11-30 18:01 | 12301.6 | 3.8343 | 87.3023 | 59.8258 | 3605.2431 |  | 6282 | 22615200 | 54151200 | 85687200 | 117223200
2037-12-01 19:01 | 11020.3 | 3.4064 | 87.3205 | 59.8258 | 3229.7311 |  | 6283 | 22618800 | 54154800 | 85690800 | 117226800
2037-12-02 20:01 | 8524.1 | 2.6389 | 87.1862 | 59.8258 | 2498.1671 |  | 6284 | 22622400 | 54158400 | 85694400 | 117230400
2037-12-03 21:01 | 7371.23 | 2.2498 | 87.028 | 59.8258 | 2160.2943 |  | 6285 | 22626000 | 54162000 | 85698000 | 117234000
2037-12-04 22:01 | 5201.04 | 1.5723 | 86.8189 | 59.8258 | 1524.2744 |  | 6286 | 22629600 | 54165600 | 85701600 | 117237600
2037-12-05 23:01 | 4184.19 | 1.2609 | 86.3668 | 59.8258 | 1226.265 |  | 6287 | 22633200 | 54169200 | 85705200 | 117241200
2037-12-07 00:01 | 3521.19 | 1.0917 | 85.5078 | 59.8258 | 1031.9589 |  | 6288 | 22636800 | 54172800 | 85708800 | 117244800
2037-12-08 01:01 | 3212.22 | 1 | 86.6221 | 59.8258 | 941.4088 |  | 6289 | 22640400 | 54176400 | 85712400 | 117248400
2037-12-09 02:01 | 3203.35 | 1 | 91.3699 | 59.8258 | 938.8092 |  | 6290 | 22644000 | 54180000 | 85716000 | 117252000
2037-12-10 03:01 | 3183.2 | 1 | 89.6051 | 59.8258 | 932.9038 |  | 6291 | 22647600 | 54183600 | 85719600 | 117255600
2037-12-11 04:01 | 3135.92 | 1 | 86.5325 | 59.8258 | 919.0474 |  | 6292 | 22651200 | 54187200 | 85723200 | 117259200
2037-12-12 05:01 | 3576.61 | 1.1307 | 84.0252 | 59.8258 | 1048.2009 |  | 6293 | 22654800 | 54190800 | 85726800 | 117262800
2037-12-13 06:01 | 3452.83 | 1.0831 | 84.0922 | 59.8258 | 1011.9246 |  | 6294 | 22658400 | 54194400 | 85730400 | 117266400
2037-12-14 07:01 | 4694.6 | 1.4414 | 84.325 | 59.8258 | 1375.8514 |  | 6295 | 22662000 | 54198000 | 85734000 | 117270000
2037-12-15 08:01 | 5693.63 | 1.8284 | 83.7703 | 59.8258 | 1668.6382 |  | 6296 | 22665600 | 54201600 | 85737600 | 117273600
2037-12-16 09:01 | 8329.85 | 2.8011 | 83.2852 | 59.8258 | 2441.2381 |  | 6297 | 22669200 | 54205200 | 85741200 | 117277200
2037-12-17 10:01 | 10765.1 | 3.5248 | 84.0648 | 59.8258 | 3154.9394 |  | 6298 | 22672800 | 54208800 | 85744800 | 117280800
2037-12-18 11:01 | 12175.9 | 3.9477 | 84.7487 | 59.8258 | 3568.404 |  | 6299 | 22676400 | 54212400 | 85748400 | 117284400
2037-12-19 12:01 | 13146.9 | 4.1924 | 85.4928 | 59.8258 | 3852.9761 |  | 6300 | 22680000 | 54216000 | 85752000 | 117288000
2037-12-20 13:01 | 13406.9 | 4.3277 | 85.769 | 59.8258 | 3929.1745 |  | 6301 | 22683600 | 54219600 | 85755600 | 117291600
2037-12-21 14:01 | 13331.5 | 4.1214 | 86.7514 | 59.8258 | 3907.077 |  | 6302 | 22687200 | 54223200 | 85759200 | 117295200
2037-12-22 15:01 | 14364.2 | 4.5714 | 86.5447 | 59.8258 | 4209.7315 |  | 6303 | 22690800 | 54226800 | 85762800 | 117298800
2037-12-23 16:01 | 14145.3 | 4.5215 | 86.7824 | 59.8258 | 4145.5782 |  | 6304 | 22694400 | 54230400 | 85766400 | 117302400
2037-12-24 17:01 | 12694.8 | 4.0855 | 86.8779 | 59.8258 | 3720.4786 |  | 6305 | 22698000 | 54234000 | 85770000 | 117306000
2037-12-25 18:01 | 11621.7 | 3.5759 | 87.5021 | 59.8258 | 3405.9841 |  | 6306 | 22701600 | 54237600 | 85773600 | 117309600
2037-12-26 19:01 | 10235.5 | 3.2184 | 87.0963 | 59.8258 | 2999.7289 |  | 6307 | 22705200 | 54241200 | 85777200 | 117313200
2037-12-27 20:01 | 8268.41 | 2.4861 | 87.6151 | 59.8258 | 2423.2318 |  | 6308 | 22708800 | 54244800 | 85780800 | 117316800
2037-12-28 21:01 | 7306.21 | 2.176 | 87.4144 | 59.8258 | 2141.2388 |  | 6309 | 22712400 | 54248400 | 85784400 | 117320400
2037-12-29 22:01 | 5522.49 | 1.596 | 87.5697 | 59.8258 | 1618.4821 |  | 6310 | 22716000 | 54252000 | 85788000 | 117324000
2037-12-30 23:01 | 4347.39 | 1.3908 | 85.6339 | 59.8258 | 1274.0942 |  | 6311 | 22719600 | 54255600 | 85791600 | 117327600
2038-01-01 00:01 | 3750.34 | 1.195 | 85.2759 | 59.8258 | 1099.1162 |  | 6312 | 22723200 | 54259200 | 85795200 | 117331200
2038-01-02 01:01 | 3216.26 | 1.0042 | 85.2306 | 59.8258 | 942.5928 |  | 6313 | 22726800 | 54262800 | 85798800 | 117334800
2038-01-03 02:01 | 3110.8 | 1 | 85.4874 | 59.8258 | 911.6855 |  | 6314 | 22730400 | 54266400 | 85802400 | 117338400
2038-01-04 03:01 | 3201.06 | 1 | 86.1658 | 59.8258 | 938.1381 |  | 6315 | 22734000 | 54270000 | 85806000 | 117342000
2038-01-05 04:01 | 3140.3 | 1 | 85.3824 | 59.8258 | 920.3311 |  | 6316 | 22737600 | 54273600 | 85809600 | 117345600
2038-01-06 05:01 | 3655.26 | 1.183 | 83.8586 | 59.8258 | 1071.251 |  | 6317 | 22741200 | 54277200 | 85813200 | 117349200
2038-01-07 06:01 | 3483.48 | 1.1071 | 84.0777 | 59.8258 | 1020.9072 |  | 6318 | 22744800 | 54280800 | 85816800 | 117352800
2038-01-08 07:01 | 3529.85 | 1.179 | 83.3069 | 59.8258 | 1034.4969 |  | 6319 | 22748400 | 54284400 | 85820400 | 117356400
2038-01-09 08:01 | 3230.3 | 1.0673 | 83.3989 | 59.8258 | 946.7075 |  | 6320 | 22752000 | 54288000 | 85824000 | 117360000
2038-01-10 09:01 | 4111.52 | 1.3726 | 83.1347 | 59.8258 | 1204.9676 |  | 6321 | 22755600 | 54291600 | 85827600 | 117363600
2038-01-11 10:01 | 6345.71 | 2.1102 | 83.1903 | 59.8258 | 1859.744 |  | 6322 | 22759200 | 54295200 | 85831200 | 117367200
2038-01-12 11:01 | 8311.33 | 2.7478 | 83.522 | 59.8258 | 2435.8104 |  | 6323 | 22762800 | 54298800 | 85834800 | 117370800
2038-01-13 12:01 | 9522.21 | 3.106 | 84.0743 | 59.8258 | 2790.6843 |  | 6324 | 22766400 | 54302400 | 85838400 | 117374400
2038-01-14 13:01 | 9729.1 | 3.1408 | 84.5676 | 59.8258 | 2851.3177 |  | 6325 | 22770000 | 54306000 | 85842000 | 117378000
2038-01-15 14:01 | 10554.3 | 3.4145 | 84.7806 | 59.8258 | 3093.16 |  | 6326 | 22773600 | 54309600 | 85845600 | 117381600
2038-01-16 15:01 | 10427.8 | 3.3198 | 85.2812 | 59.8258 | 3056.0865 |  | 6327 | 22777200 | 54313200 | 85849200 | 117385200
2038-01-17 16:01 | 11231.2 | 3.5801 | 85.4083 | 59.8258 | 3291.5398 |  | 6328 | 22780800 | 54316800 | 85852800 | 117388800
2038-01-18 17:01 | 10214.4 | 3.2277 | 85.7381 | 59.8258 | 2993.5451 |  | 6329 | 22784400 | 54320400 | 85856400 | 117392400
2038-01-19 18:01 | 8592.75 | 2.5892 | 86.4604 | 59.8258 | 2518.2864 |  | 6330 | 22788000 | 54324000 | 85860000 | 117396000
2038-01-20 19:01 | 7143.57 | 2.2275 | 85.7859 | 59.8258 | 2093.5737 |  | 6331 | 22791600 | 54327600 | 85863600 | 117399600
2038-01-21 20:01 | 4737.4 | 1.4661 | 85.6777 | 59.8258 | 1388.3949 |  | 6332 | 22795200 | 54331200 | 85867200 | 117403200
2038-01-22 21:01 | 3451.11 | 1.1037 | 84.7887 | 59.8258 | 1011.4205 |  | 6333 | 22798800 | 54334800 | 85870800 | 117406800
2038-01-23 22:01 | 3056.76 | 1 | 69.8075 | 59.8258 | 895.8479 |  | 6334 | 22802400 | 54338400 | 85874400 | 117410400
2038-01-24 23:01 | 0 | 0 | 69.7732 | 59.8258 | 0 |  | 6335 | 22806000 | 54342000 | 85878000 | 117414000
2038-01-26 00:01 | -180.933 | 0.94958 | 68.262 | 59.8258 | -53.0262 |  | 6336 | 22809600 | 54345600 | 85881600 | 117417600
2038-01-27 01:01 | -452.539 | 1.6329 | 67.4263 | 59.8258 | -132.6261 |  | 6337 | 22813200 | 54349200 | 85885200 | 117421200
2038-01-28 02:01 | -638.563 | 2.0656 | 66.9651 | 59.8258 | -187.1443 |  | 6338 | 22816800 | 54352800 | 85888800 | 117424800
2038-01-29 03:01 | -886.663 | 2.6815 | 66.5786 | 59.8258 | -259.8553 |  | 6339 | 22820400 | 54356400 | 85892400 | 117428400
2038-01-30 04:01 | -929.056 | 2.7504 | 66.2434 | 59.8258 | -272.2794 |  | 6340 | 22824000 | 54360000 | 85896000 | 117432000
2038-01-31 05:01 | -1000.93 | 2.9396 | 66.0186 | 59.8258 | -293.3436 |  | 6341 | 22827600 | 54363600 | 85899600 | 117435600
2038-02-01 06:01 | -308.237 | 1.1148 | 66.121 | 59.8258 | -90.3353 |  | 6342 | 22831200 | 54367200 | 85903200 | 117439200
2038-02-02 07:01 | 1058.65 | 1 | 67.2229 | 59.8258 | 310.2597 |  | 6343 | 22834800 | 54370800 | 85906800 | 117442800
2038-02-03 08:01 | 3130.6 | 1 | 67.1458 | 59.8258 | 917.4883 |  | 6344 | 22838400 | 54374400 | 85910400 | 117446400
2038-02-04 09:01 | 3215.75 | 1 | 91.2487 | 59.8258 | 942.4433 |  | 6345 | 22842000 | 54378000 | 85914000 | 117450000
2038-02-05 10:01 | 3233.5 | 1 | 83.9545 | 59.8258 | 947.6453 |  | 6346 | 22845600 | 54381600 | 85917600 | 117453600
2038-02-06 11:01 | 3591.42 | 1.1344 | 82.3574 | 59.8258 | 1052.5413 |  | 6347 | 22849200 | 54385200 | 85921200 | 117457200
2038-02-07 12:01 | 4018.46 | 1.2545 | 82.6116 | 59.8258 | 1177.6944 |  | 6348 | 22852800 | 54388800 | 85924800 | 117460800
2038-02-08 13:01 | 4455.1 | 1.3869 | 82.7382 | 59.8258 | 1305.6609 |  | 6349 | 22856400 | 54392400 | 85928400 | 117464400
2038-02-09 14:01 | 5036.35 | 1.5553 | 82.9131 | 59.8258 | 1476.0085 |  | 6350 | 22860000 | 54396000 | 85932000 | 117468000
2038-02-10 15:01 | 5325.08 | 1.744 | 82.1615 | 59.8258 | 1560.6269 |  | 6351 | 22863600 | 54399600 | 85935600 | 117471600
2038-02-11 16:01 | 7893.77 | 2.6681 | 81.7997 | 59.8258 | 2313.4356 |  | 6352 | 22867200 | 54403200 | 85939200 | 117475200
2038-02-12 17:01 | 7441.22 | 2.3505 | 83.1501 | 59.8258 | 2180.8063 |  | 6353 | 22870800 | 54406800 | 85942800 | 117478800
2038-02-13 18:01 | 6459.84 | 1.9952 | 83.6649 | 59.8258 | 1893.1922 |  | 6354 | 22874400 | 54410400 | 85946400 | 117482400
2038-02-14 19:01 | 5592.8 | 1.7411 | 83.5299 | 59.8258 | 1639.0879 |  | 6355 | 22878000 | 54414000 | 85950000 | 117486000
2038-02-15 20:01 | 5062.55 | 1.555 | 83.6515 | 59.8258 | 1483.6869 |  | 6356 | 22881600 | 54417600 | 85953600 | 117489600
2038-02-16 21:01 | 4598.05 | 1.4308 | 83.398 | 59.8258 | 1347.5554 |  | 6357 | 22885200 | 54421200 | 85957200 | 117493200
2038-02-17 22:01 | 4104.49 | 1.3151 | 82.8653 | 59.8258 | 1202.9073 |  | 6358 | 22888800 | 54424800 | 85960800 | 117496800
2038-02-18 23:01 | 3047.34 | 1 | 68.2345 | 59.8258 | 893.0872 |  | 6359 | 22892400 | 54428400 | 85964400 | 117500400
2038-02-20 00:01 | 3171.54 | 1 | 68.045 | 59.8258 | 929.4866 |  | 6360 | 22896000 | 54432000 | 85968000 | 117504000
2038-02-21 01:01 | 3158.1 | 1 | 67.9744 | 59.8258 | 925.5477 |  | 6361 | 22899600 | 54435600 | 85971600 | 117507600
2038-02-22 02:01 | 1489.04 | 1 | 68.0877 | 59.8258 | 436.3945 |  | 6362 | 22903200 | 54439200 | 85975200 | 117511200
2038-02-23 03:01 | 690.367 | 1 | 67.8987 | 59.8258 | 202.3266 |  | 6363 | 22906800 | 54442800 | 85978800 | 117514800
2038-02-24 04:01 | 100.635 | 1 | 67.6592 | 59.8258 | 29.4932 |  | 6364 | 22910400 | 54446400 | 85982400 | 117518400
2038-02-25 05:01 | 85.0269 | 1 | 67.4188 | 59.8258 | 24.9189 |  | 6365 | 22914000 | 54450000 | 85986000 | 117522000
2038-02-26 06:01 | 2207.39 | 1 | 67.0493 | 59.8258 | 646.9221 |  | 6366 | 22917600 | 54453600 | 85989600 | 117525600
2038-02-27 07:01 | 2890.53 | 1 | 89.6653 | 59.8258 | 847.1307 |  | 6367 | 22921200 | 54457200 | 85993200 | 117529200
2038-02-28 08:01 | 3042.78 | 1 | 67.2356 | 59.8258 | 891.7508 |  | 6368 | 22924800 | 54460800 | 85996800 | 117532800
2038-03-01 09:01 | 3106.46 | 1 | 67.3005 | 59.8258 | 910.4136 |  | 6369 | 22928400 | 54464400 | 86000400 | 117536400
2038-03-02 10:01 | 3163.79 | 1 | 89.8587 | 59.8258 | 927.2153 |  | 6370 | 22932000 | 54468000 | 86004000 | 117540000
2038-03-03 11:01 | 3309.86 | 1.019 | 82.482 | 59.8258 | 970.0242 |  | 6371 | 22935600 | 54471600 | 86007600 | 117543600
2038-03-04 12:01 | 3844.94 | 1.1858 | 82.4669 | 59.8258 | 1126.8407 |  | 6372 | 22939200 | 54475200 | 86011200 | 117547200
2038-03-05 13:01 | 4782.74 | 1.4332 | 82.9362 | 59.8258 | 1401.6827 |  | 6373 | 22942800 | 54478800 | 86014800 | 117550800
2038-03-06 14:01 | 7014.5 | 2.3533 | 81.4405 | 59.8258 | 2055.747 |  | 6374 | 22946400 | 54482400 | 86018400 | 117554400
2038-03-07 15:01 | 7743.23 | 2.5721 | 81.9562 | 59.8258 | 2269.3167 |  | 6375 | 22950000 | 54486000 | 86022000 | 117558000
2038-03-08 16:01 | 9626.65 | 3.1387 | 82.5125 | 59.8258 | 2821.2926 |  | 6376 | 22953600 | 54489600 | 86025600 | 117561600
2038-03-09 17:01 | 8569.65 | 2.6555 | 83.6987 | 59.8258 | 2511.5165 |  | 6377 | 22957200 | 54493200 | 86029200 | 117565200
2038-03-10 18:01 | 7533.13 | 2.18 | 84.8994 | 59.8258 | 2207.7425 |  | 6378 | 22960800 | 54496800 | 86032800 | 117568800
2038-03-11 19:01 | 6265.31 | 1.8804 | 84.329 | 59.8258 | 1836.1811 |  | 6379 | 22964400 | 54500400 | 86036400 | 117572400
2038-03-12 20:01 | 5450.2 | 1.6145 | 84.4105 | 59.8258 | 1597.2959 |  | 6380 | 22968000 | 54504000 | 86040000 | 117576000
2038-03-13 21:01 | 4555.35 | 1.3955 | 83.7696 | 59.8258 | 1335.0413 |  | 6381 | 22971600 | 54507600 | 86043600 | 117579600
2038-03-14 22:01 | 3934.51 | 1.2214 | 83.3736 | 59.8258 | 1153.0911 |  | 6382 | 22975200 | 54511200 | 86047200 | 117583200
2038-03-15 23:01 | 3175.11 | 1 | 68.2101 | 59.8258 | 930.5329 |  | 6383 | 22978800 | 54514800 | 86050800 | 117586800
2038-03-17 00:01 | 3053.89 | 1 | 68.0413 | 59.8258 | 895.0068 |  | 6384 | 22982400 | 54518400 | 86054400 | 117590400
2038-03-18 01:01 | 0 | 0 | 68.198 | 59.8258 | 0 |  | 6385 | 22986000 | 54522000 | 86058000 | 117594000
2038-03-19 02:01 | 165.257 | 1 | 67.6831 | 59.8258 | 48.432 |  | 6386 | 22989600 | 54525600 | 86061600 | 117597600
2038-03-20 03:01 | 604.365 | 1 | 67.3615 | 59.8258 | 177.1219 |  | 6387 | 22993200 | 54529200 | 86065200 | 117601200
2038-03-21 04:01 | 2079.3 | 1 | 67.1004 | 59.8258 | 609.3827 |  | 6388 | 22996800 | 54532800 | 86068800 | 117604800
2038-03-22 05:01 | 2813.18 | 1 | 67.1055 | 59.8258 | 824.4617 |  | 6389 | 23000400 | 54536400 | 86072400 | 117608400
2038-03-23 06:01 | 2971.87 | 1 | 67.1636 | 59.8258 | 870.9691 |  | 6390 | 23004000 | 54540000 | 86076000 | 117612000
2038-03-24 07:01 | 3102.36 | 1 | 67.2257 | 59.8258 | 909.212 |  | 6391 | 23007600 | 54543600 | 86079600 | 117615600
2038-03-25 08:01 | -40.7255 | 0.6517 | 67.2726 | 59.8258 | -11.9355 |  | 6392 | 23011200 | 54547200 | 86083200 | 117619200
2038-03-26 09:01 | 84.582 | 1 | 67.1567 | 59.8258 | 24.7885 |  | 6393 | 23014800 | 54550800 | 86086800 | 117622800
2038-03-27 10:01 | 2990.92 | 1 | 66.6579 | 59.8258 | 876.5521 |  | 6394 | 23018400 | 54554400 | 86090400 | 117626400
2038-03-28 11:01 | 2116.49 | 1 | 66.9843 | 59.8258 | 620.282 |  | 6395 | 23022000 | 54558000 | 86094000 | 117630000
2038-03-29 12:01 | 2879.78 | 1 | 66.8645 | 59.8258 | 843.9802 |  | 6396 | 23025600 | 54561600 | 86097600 | 117633600
2038-03-30 13:01 | 3054.13 | 1 | 66.8756 | 59.8258 | 895.0771 |  | 6397 | 23029200 | 54565200 | 86101200 | 117637200
2038-03-31 14:01 | 3224.57 | 1 | 66.9522 | 59.8258 | 945.0282 |  | 6398 | 23032800 | 54568800 | 86104800 | 117640800
2038-04-01 15:01 | 3835.73 | 1.1719 | 82.2903 | 59.8258 | 1124.1415 |  | 6399 | 23036400 | 54572400 | 86108400 | 117644400
2038-04-02 16:01 | 4824.64 | 1.4782 | 82.2307 | 59.8258 | 1413.9624 |  | 6400 | 23040000 | 54576000 | 86112000 | 117648000
2038-04-03 17:01 | 5176.53 | 1.6529 | 81.7706 | 59.8258 | 1517.0912 |  | 6401 | 23043600 | 54579600 | 86115600 | 117651600
2038-04-04 18:01 | 4335.72 | 1.3361 | 82.4036 | 59.8258 | 1270.6741 |  | 6402 | 23047200 | 54583200 | 86119200 | 117655200
2038-04-05 19:01 | 3396.49 | 1.0678 | 82.0627 | 59.8258 | 995.413 |  | 6403 | 23050800 | 54586800 | 86122800 | 117658800
2038-04-06 20:01 | 3018.91 | 1 | 67.1626 | 59.8258 | 884.7552 |  | 6404 | 23054400 | 54590400 | 86126400 | 117662400
2038-04-07 21:01 | 3052 | 1 | 67.0895 | 59.8258 | 894.4529 |  | 6405 | 23058000 | 54594000 | 86130000 | 117666000
2038-04-08 22:01 | 0 | 0 | 67.299 | 59.8258 | 0 |  | 6406 | 23061600 | 54597600 | 86133600 | 117669600
2038-04-09 23:01 | -371.026 | 1.4921 | 65.7024 | 59.8258 | -108.737 |  | 6407 | 23065200 | 54601200 | 86137200 | 117673200
2038-04-11 00:01 | -581.815 | 1.971 | 65.1655 | 59.8258 | -170.5131 |  | 6408 | 23068800 | 54604800 | 86140800 | 117676800
2038-04-12 01:01 | -594.373 | 1.9686 | 64.9458 | 59.8258 | -174.1935 |  | 6409 | 23072400 | 54608400 | 86144400 | 117680400
2038-04-13 02:01 | -492.454 | 1.7018 | 64.8478 | 59.8258 | -144.324 |  | 6410 | 23076000 | 54612000 | 86148000 | 117684000
2038-04-14 03:01 | -241.598 | 1.062 | 64.9894 | 59.8258 | -70.8054 |  | 6411 | 23079600 | 54615600 | 86151600 | 117687600
2038-04-15 04:01 | -230.8 | 1.0874 | 64.9987 | 59.8258 | -67.6408 |  | 6412 | 23083200 | 54619200 | 86155200 | 117691200
2038-04-16 05:01 | 1069.27 | 1 | 65.7988 | 59.8258 | 313.3721 |  | 6413 | 23086800 | 54622800 | 86158800 | 117694800
2038-04-17 06:01 | 774.832 | 1 | 65.9238 | 59.8258 | 227.0808 |  | 6414 | 23090400 | 54626400 | 86162400 | 117698400
2038-04-18 07:01 | 1679.53 | 1 | 65.8345 | 59.8258 | 492.2217 |  | 6415 | 23094000 | 54630000 | 86166000 | 117702000
2038-04-19 08:01 | -163.555 | 0.98994 | 65.3353 | 59.8258 | -47.9332 |  | 6416 | 23097600 | 54633600 | 86169600 | 117705600
2038-04-20 09:01 | 1830.24 | 1 | 65.7327 | 59.8258 | 536.3904 |  | 6417 | 23101200 | 54637200 | 86173200 | 117709200
2038-04-21 10:01 | 2847.75 | 1 | 65.8035 | 59.8258 | 834.5931 |  | 6418 | 23104800 | 54640800 | 86176800 | 117712800
2038-04-22 11:01 | 3117.45 | 1 | 85.4903 | 59.8258 | 913.6344 |  | 6419 | 23108400 | 54644400 | 86180400 | 117716400
2038-04-23 12:01 | 3207.41 | 1 | 81.9874 | 59.8258 | 939.9991 |  | 6420 | 23112000 | 54648000 | 86184000 | 117720000
2038-04-24 13:01 | 4921.15 | 1.5666 | 80.8327 | 59.8258 | 1442.2467 |  | 6421 | 23115600 | 54651600 | 86187600 | 117723600
2038-04-25 14:01 | 8010.28 | 2.7917 | 79.9034 | 59.8258 | 2347.5813 |  | 6422 | 23119200 | 54655200 | 86191200 | 117727200
2038-04-26 15:01 | 9373.83 | 3.1636 | 80.9192 | 59.8258 | 2747.1984 |  | 6423 | 23122800 | 54658800 | 86194800 | 117730800
2038-04-27 16:01 | 10149.3 | 3.384 | 81.5867 | 59.8258 | 2974.4662 |  | 6424 | 23126400 | 54662400 | 86198400 | 117734400
2038-04-28 17:01 | 9655.8 | 3.0847 | 82.5994 | 59.8258 | 2829.8356 |  | 6425 | 23130000 | 54666000 | 86202000 | 117738000
2038-04-29 18:01 | 8021.85 | 2.4089 | 83.7855 | 59.8258 | 2350.9722 |  | 6426 | 23133600 | 54669600 | 86205600 | 117741600
2038-04-30 19:01 | 6673.22 | 2.0188 | 83.6868 | 59.8258 | 1955.7277 |  | 6427 | 23137200 | 54673200 | 86209200 | 117745200
2038-05-01 20:01 | 4278.46 | 1.2552 | 84.0633 | 59.8258 | 1253.8929 |  | 6428 | 23140800 | 54676800 | 86212800 | 117748800
2038-05-02 21:01 | 3274.7 | 1 | 83.8468 | 59.8258 | 959.7198 |  | 6429 | 23144400 | 54680400 | 86216400 | 117752400
2038-05-03 22:01 | 3052.22 | 1 | 67.5676 | 59.8258 | 894.5174 |  | 6430 | 23148000 | 54684000 | 86220000 | 117756000
2038-05-04 23:01 | 233.398 | 1 | 67.6444 | 59.8258 | 68.4022 |  | 6431 | 23151600 | 54687600 | 86223600 | 117759600
2038-05-06 00:01 | -7.9905 | 0.5785 | 67.1882 | 59.8258 | -2.3418 |  | 6432 | 23155200 | 54691200 | 86227200 | 117763200
2038-05-07 01:01 | -225.283 | 1.0947 | 65.9105 | 59.8258 | -66.0239 |  | 6433 | 23158800 | 54694800 | 86230800 | 117766800
2038-05-08 02:01 | -363.465 | 1.4254 | 65.4567 | 59.8258 | -106.5211 |  | 6434 | 23162400 | 54698400 | 86234400 | 117770400
2038-05-09 03:01 | -482.686 | 1.7166 | 65.1151 | 59.8258 | -141.4613 |  | 6435 | 23166000 | 54702000 | 86238000 | 117774000
2038-05-10 04:01 | -462.66 | 1.6441 | 64.8832 | 59.8258 | -135.5923 |  | 6436 | 23169600 | 54705600 | 86241600 | 117777600
2038-05-11 05:01 | -95.271 | 0.6801 | 65.3736 | 59.8258 | -27.9212 |  | 6437 | 23173200 | 54709200 | 86245200 | 117781200
2038-05-12 06:01 | -142.763 | 0.88702 | 65.199 | 59.8258 | -41.8397 |  | 6438 | 23176800 | 54712800 | 86248800 | 117784800
2038-05-13 07:01 | 2618.1 | 1 | 65.607 | 59.8258 | 767.2894 |  | 6439 | 23180400 | 54716400 | 86252400 | 117788400
2038-05-14 08:01 | 644.517 | 1 | 66.1033 | 59.8258 | 188.8893 |  | 6440 | 23184000 | 54720000 | 86256000 | 117792000
2038-05-15 09:01 | 3032.94 | 1 | 82.6152 | 59.8258 | 888.867 |  | 6441 | 23187600 | 54723600 | 86259600 | 117795600
2038-05-16 10:01 | 5946.02 | 2.0174 | 79.723 | 59.8258 | 1742.6064 |  | 6442 | 23191200 | 54727200 | 86263200 | 117799200
2038-05-17 11:01 | 7806.71 | 2.7681 | 79.716 | 59.8258 | 2287.9209 |  | 6443 | 23194800 | 54730800 | 86266800 | 117802800
2038-05-18 12:01 | 9084.66 | 3.0417 | 81.0535 | 59.8258 | 2662.451 |  | 6444 | 23198400 | 54734400 | 86270400 | 117806400
2038-05-19 13:01 | 9596.68 | 3.1475 | 81.8122 | 59.8258 | 2812.5093 |  | 6445 | 23202000 | 54738000 | 86274000 | 117810000
2038-05-20 14:01 | 10088.7 | 3.3109 | 82.2398 | 59.8258 | 2956.7061 |  | 6446 | 23205600 | 54741600 | 86277600 | 117813600
2038-05-21 15:01 | 11309.5 | 3.6542 | 82.8209 | 59.8258 | 3314.4873 |  | 6447 | 23209200 | 54745200 | 86281200 | 117817200
2038-05-22 16:01 | 11116.4 | 3.542 | 83.4315 | 59.8258 | 3257.8952 |  | 6448 | 23212800 | 54748800 | 86284800 | 117820800
2038-05-23 17:01 | 10444.1 | 3.2241 | 84.151 | 59.8258 | 3060.8636 |  | 6449 | 23216400 | 54752400 | 86288400 | 117824400
2038-05-24 18:01 | 8098.96 | 2.4829 | 84.3845 | 59.8258 | 2373.5709 |  | 6450 | 23220000 | 54756000 | 86292000 | 117828000
2038-05-25 19:01 | 6719.51 | 2.0811 | 84.0544 | 59.8258 | 1969.294 |  | 6451 | 23223600 | 54759600 | 86295600 | 117831600
2038-05-26 20:01 | 4414.79 | 1.348 | 84.0886 | 59.8258 | 1293.8472 |  | 6452 | 23227200 | 54763200 | 86299200 | 117835200
2038-05-27 21:01 | 3442.27 | 1.0829 | 83.2632 | 59.8258 | 1008.8298 |  | 6453 | 23230800 | 54766800 | 86302800 | 117838800
2038-05-28 22:01 | 3141.79 | 1 | 68.1018 | 59.8258 | 920.7678 |  | 6454 | 23234400 | 54770400 | 86306400 | 117842400
2038-05-29 23:01 | 2989.9 | 1 | 67.8676 | 59.8258 | 876.2532 |  | 6455 | 23238000 | 54774000 | 86310000 | 117846000
2038-05-31 00:01 | 0 | 0 | 67.9533 | 59.8258 | 0 |  | 6456 | 23241600 | 54777600 | 86313600 | 117849600
2038-06-01 01:01 | -68.0856 | 0.61445 | 66.8986 | 59.8258 | -19.9539 |  | 6457 | 23245200 | 54781200 | 86317200 | 117853200
2038-06-02 02:01 | -178.789 | 0.97454 | 66.236 | 59.8258 | -52.3979 |  | 6458 | 23248800 | 54784800 | 86320800 | 117856800
2038-06-03 03:01 | -89.1082 | 0.71557 | 66.2756 | 59.8258 | -26.115 |  | 6459 | 23252400 | 54788400 | 86324400 | 117860400
2038-06-04 04:01 | 99.3655 | 1 | 66.6382 | 59.8258 | 29.1212 |  | 6460 | 23256000 | 54792000 | 86328000 | 117864000
2038-06-05 05:01 | 1999.97 | 1 | 66.2983 | 59.8258 | 586.1333 |  | 6461 | 23259600 | 54795600 | 86331600 | 117867600
2038-06-06 06:01 | 1954.16 | 1 | 66.4721 | 59.8258 | 572.7078 |  | 6462 | 23263200 | 54799200 | 86335200 | 117871200
2038-06-07 07:01 | 3064.33 | 1 | 66.4187 | 59.8258 | 898.0665 |  | 6463 | 23266800 | 54802800 | 86338800 | 117874800
2038-06-08 08:01 | 3091.71 | 1 | 84.2772 | 59.8258 | 906.0908 |  | 6464 | 23270400 | 54806400 | 86342400 | 117878400
2038-06-09 09:01 | 5441.89 | 1.7237 | 81.3841 | 59.8258 | 1594.8605 |  | 6465 | 23274000 | 54810000 | 86346000 | 117882000
2038-06-10 10:01 | 7876.7 | 2.6484 | 80.9111 | 59.8258 | 2308.4329 |  | 6466 | 23277600 | 54813600 | 86349600 | 117885600
2038-06-11 11:01 | 9834.54 | 3.2684 | 81.5728 | 59.8258 | 2882.2192 |  | 6467 | 23281200 | 54817200 | 86353200 | 117889200
2038-06-12 12:01 | 11033 | 3.5932 | 82.432 | 59.8258 | 3233.4531 |  | 6468 | 23284800 | 54820800 | 86356800 | 117892800
2038-06-13 13:01 | 11665.9 | 3.7701 | 83.0559 | 59.8258 | 3418.9378 |  | 6469 | 23288400 | 54824400 | 86360400 | 117896400
2038-06-14 14:01 | 12453.6 | 3.963 | 83.727 | 59.8258 | 3649.7899 |  | 6470 | 23292000 | 54828000 | 86364000 | 117900000
2038-06-15 15:01 | 13351.4 | 4.3692 | 83.744 | 59.8258 | 3912.9091 |  | 6471 | 23295600 | 54831600 | 86367600 | 117903600
2038-06-16 16:01 | 12847.7 | 4.0595 | 84.657 | 59.8258 | 3765.2892 |  | 6472 | 23299200 | 54835200 | 86371200 | 117907200
2038-06-17 17:01 | 11517.2 | 3.6345 | 84.8866 | 59.8258 | 3375.3581 |  | 6473 | 23302800 | 54838800 | 86374800 | 117910800
2038-06-18 18:01 | 9611.7 | 2.9327 | 85.4089 | 59.8258 | 2816.9112 |  | 6474 | 23306400 | 54842400 | 86378400 | 117914400
2038-06-19 19:01 | 8419.12 | 2.6126 | 85.0009 | 59.8258 | 2467.4005 |  | 6475 | 23310000 | 54846000 | 86382000 | 117918000
2038-06-20 20:01 | 6573.41 | 1.9111 | 85.8358 | 59.8258 | 1926.4763 |  | 6476 | 23313600 | 54849600 | 86385600 | 117921600
2038-06-21 21:01 | 5364.17 | 1.4991 | 86.152 | 59.8258 | 1572.083 |  | 6477 | 23317200 | 54853200 | 86389200 | 117925200
2038-06-22 22:01 | 3301.61 | 1 | 87.401 | 59.8258 | 967.6064 |  | 6478 | 23320800 | 54856800 | 86392800 | 117928800
2038-06-23 23:01 | 3170.33 | 1 | 93.2089 | 59.8258 | 929.132 |  | 6479 | 23324400 | 54860400 | 86396400 | 117932400
2038-06-25 00:01 | 3179 | 1 | 68.4098 | 59.8258 | 931.6729 |  | 6480 | 23328000 | 54864000 | 86400000 | 117936000
2038-06-26 01:01 | 3078.51 | 1 | 68.2421 | 59.8258 | 902.2222 |  | 6481 | 23331600 | 54867600 | 86403600 | 117939600
2038-06-27 02:01 | 3194.22 | 1 | 68.0698 | 59.8258 | 936.1335 |  | 6482 | 23335200 | 54871200 | 86407200 | 117943200
2038-06-28 03:01 | 3187.33 | 1 | 67.9463 | 59.8258 | 934.1142 |  | 6483 | 23338800 | 54874800 | 86410800 | 117946800
2038-06-29 04:01 | 3205.14 | 1 | 67.8661 | 59.8258 | 939.3338 |  | 6484 | 23342400 | 54878400 | 86414400 | 117950400
2038-06-30 05:01 | 3196.32 | 1 | 90.8107 | 59.8258 | 936.7489 |  | 6485 | 23346000 | 54882000 | 86418000 | 117954000
2038-07-01 06:01 | 3250.36 | 1 | 92.0281 | 59.8258 | 952.5865 |  | 6486 | 23349600 | 54885600 | 86421600 | 117957600
2038-07-02 07:01 | 3194.75 | 1 | 89.8106 | 59.8258 | 936.2888 |  | 6487 | 23353200 | 54889200 | 86425200 | 117961200
2038-07-03 08:01 | 3132.17 | 1 | 67.6514 | 59.8258 | 917.9484 |  | 6488 | 23356800 | 54892800 | 86428800 | 117964800
2038-07-04 09:01 | 3113.58 | 1 | 67.6138 | 59.8258 | 912.5002 |  | 6489 | 23360400 | 54896400 | 86432400 | 117968400
2038-07-05 10:01 | 3174.14 | 1 | 67.5571 | 59.8258 | 930.2486 |  | 6490 | 23364000 | 54900000 | 86436000 | 117972000
2038-07-06 11:01 | 3170.57 | 1 | 89.3015 | 59.8258 | 929.2023 |  | 6491 | 23367600 | 54903600 | 86439600 | 117975600
2038-07-07 12:01 | 3220.86 | 1.0069 | 82.3063 | 59.8258 | 943.9409 |  | 6492 | 23371200 | 54907200 | 86443200 | 117979200
2038-07-08 13:01 | 3643.83 | 1.1529 | 82.0718 | 59.8258 | 1067.9012 |  | 6493 | 23374800 | 54910800 | 86446800 | 117982800
2038-07-09 14:01 | 4085.88 | 1.2317 | 82.7637 | 59.8258 | 1197.4532 |  | 6494 | 23378400 | 54914400 | 86450400 | 117986400
2038-07-10 15:01 | 5776.51 | 1.9013 | 81.4802 | 59.8258 | 1692.928 |  | 6495 | 23382000 | 54918000 | 86454000 | 117990000
2038-07-11 16:01 | 6958.41 | 2.2725 | 81.7795 | 59.8258 | 2039.3087 |  | 6496 | 23385600 | 54921600 | 86457600 | 117993600
2038-07-12 17:01 | 7124.27 | 2.3143 | 82.1075 | 59.8258 | 2087.9174 |  | 6497 | 23389200 | 54925200 | 86461200 | 117997200
2038-07-13 18:01 | 6000.87 | 1.7848 | 83.5792 | 59.8258 | 1758.6814 |  | 6498 | 23392800 | 54928800 | 86464800 | 118000800
2038-07-14 19:01 | 5125.42 | 1.5287 | 83.5092 | 59.8258 | 1502.1123 |  | 6499 | 23396400 | 54932400 | 86468400 | 118004400
2038-07-15 20:01 | 3222.15 | 1 | 84.3463 | 59.8258 | 944.3189 |  | 6500 | 23400000 | 54936000 | 86472000 | 118008000
2038-07-16 21:01 | 3108.48 | 1 | 91.524 | 59.8258 | 911.0056 |  | 6501 | 23403600 | 54939600 | 86475600 | 118011600
2038-07-17 22:01 | 1814.78 | 1 | 67.5236 | 59.8258 | 531.8595 |  | 6502 | 23407200 | 54943200 | 86479200 | 118015200
2038-07-18 23:01 | -102.642 | 0.82081 | 66.8494 | 59.8258 | -30.0814 |  | 6503 | 23410800 | 54946800 | 86482800 | 118018800
2038-07-20 00:01 | -186.576 | 0.98137 | 66.1313 | 59.8258 | -54.68 |  | 6504 | 23414400 | 54950400 | 86486400 | 118022400
2038-07-21 01:01 | -290.965 | 1.2426 | 65.6689 | 59.8258 | -85.2734 |  | 6505 | 23418000 | 54954000 | 86490000 | 118026000
2038-07-22 02:01 | -663.31 | 2.203 | 65.1973 | 59.8258 | -194.397 |  | 6506 | 23421600 | 54957600 | 86493600 | 118029600
2038-07-23 03:01 | -950.031 | 2.8928 | 64.8474 | 59.8258 | -278.4266 |  | 6507 | 23425200 | 54961200 | 86497200 | 118033200
2038-07-24 04:01 | -1275.24 | 3.7113 | 64.5542 | 59.8258 | -373.736 |  | 6508 | 23428800 | 54964800 | 86500800 | 118036800
2038-07-25 05:01 | -1462.3 | 4.1523 | 64.3089 | 59.8258 | -428.5578 |  | 6509 | 23432400 | 54968400 | 86504400 | 118040400
2038-07-26 06:01 | -1011.57 | 2.9086 | 64.1375 | 59.8258 | -296.4619 |  | 6510 | 23436000 | 54972000 | 86508000 | 118044000
2038-07-27 07:01 | -198.051 | 0.84413 | 64.5552 | 59.8258 | -58.043 |  | 6511 | 23439600 | 54975600 | 86511600 | 118047600
2038-07-28 08:01 | 324.214 | 1 | 65.6299 | 59.8258 | 95.0177 |  | 6512 | 23443200 | 54979200 | 86515200 | 118051200
2038-07-29 09:01 | 2434.21 | 1 | 82.8532 | 59.8258 | 713.3965 |  | 6513 | 23446800 | 54982800 | 86518800 | 118054800
2038-07-30 10:01 | 3652.07 | 1.2676 | 79.1193 | 59.8258 | 1070.3161 |  | 6514 | 23450400 | 54986400 | 86522400 | 118058400
2038-07-31 11:01 | 5792.1 | 1.9519 | 79.8326 | 59.8258 | 1697.4969 |  | 6515 | 23454000 | 54990000 | 86526000 | 118062000
2038-08-01 12:01 | 6582.82 | 2.1658 | 80.6146 | 59.8258 | 1929.2341 |  | 6516 | 23457600 | 54993600 | 86529600 | 118065600
2038-08-02 13:01 | 6461.92 | 2.1645 | 80.7452 | 59.8258 | 1893.8018 |  | 6517 | 23461200 | 54997200 | 86533200 | 118069200
2038-08-03 14:01 | 7478.86 | 2.442 | 81.3184 | 59.8258 | 2191.8375 |  | 6518 | 23464800 | 55000800 | 86536800 | 118072800
2038-08-04 15:01 | 7594.89 | 2.4625 | 81.6997 | 59.8258 | 2225.8425 |  | 6519 | 23468400 | 55004400 | 86540400 | 118076400
2038-08-05 16:01 | 9570.72 | 3.0899 | 81.9663 | 59.8258 | 2804.9012 |  | 6520 | 23472000 | 55008000 | 86544000 | 118080000
2038-08-06 17:01 | 7656.48 | 2.4055 | 82.7681 | 59.8258 | 2243.8928 |  | 6521 | 23475600 | 55011600 | 86547600 | 118083600
2038-08-07 18:01 | 5381.64 | 1.6412 | 83.2345 | 59.8258 | 1577.203 |  | 6522 | 23479200 | 55015200 | 86551200 | 118087200
2038-08-08 19:01 | 3931.1 | 1.2257 | 82.6652 | 59.8258 | 1152.0917 |  | 6523 | 23482800 | 55018800 | 86554800 | 118090800
2038-08-09 20:01 | 3172.65 | 1 | 84.1053 | 59.8258 | 929.8119 |  | 6524 | 23486400 | 55022400 | 86558400 | 118094400
2038-08-10 21:01 | 3140.17 | 1 | 90.2036 | 59.8258 | 920.293 |  | 6525 | 23490000 | 55026000 | 86562000 | 118098000
2038-08-11 22:01 | 3151.87 | 1 | 67.0833 | 59.8258 | 923.7219 |  | 6526 | 23493600 | 55029600 | 86565600 | 118101600
2038-08-12 23:01 | -618.363 | 2.1162 | 65.9304 | 59.8258 | -181.2243 |  | 6527 | 23497200 | 55033200 | 86569200 | 118105200
2038-08-14 00:01 | -993.856 | 3.0055 | 65.1753 | 59.8258 | -291.2704 |  | 6528 | 23500800 | 55036800 | 86572800 | 118108800
2038-08-15 01:01 | -1177.72 | 3.4332 | 64.7381 | 59.8258 | -345.1557 |  | 6529 | 23504400 | 55040400 | 86576400 | 118112400
2038-08-16 02:01 | -1293.8 | 3.7171 | 64.4682 | 59.8258 | -379.1754 |  | 6530 | 23508000 | 55044000 | 86580000 | 118116000
2038-08-17 03:01 | -1430.81 | 4.0717 | 64.215 | 59.8258 | -419.329 |  | 6531 | 23511600 | 55047600 | 86583600 | 118119600
2038-08-18 04:01 | -1543.93 | 4.3594 | 63.9376 | 59.8258 | -452.4812 |  | 6532 | 23515200 | 55051200 | 86587200 | 118123200
2038-08-19 05:01 | -1586.05 | 4.4564 | 63.7693 | 59.8258 | -464.8254 |  | 6533 | 23518800 | 55054800 | 86590800 | 118126800
2038-08-20 06:01 | -940.346 | 2.7045 | 63.6798 | 59.8258 | -275.5882 |  | 6534 | 23522400 | 55058400 | 86594400 | 118130400
2038-08-21 07:01 | 0 | 0 | 65.2534 | 59.8258 | 0 |  | 6535 | 23526000 | 55062000 | 86598000 | 118134000
2038-08-22 08:01 | 97.1594 | 1 | 65.3297 | 59.8258 | 28.4746 |  | 6536 | 23529600 | 55065600 | 86601600 | 118137600
2038-08-23 09:01 | 2813.29 | 1 | 65.096 | 59.8258 | 824.4939 |  | 6537 | 23533200 | 55069200 | 86605200 | 118141200
2038-08-24 10:01 | 3992.77 | 1.2821 | 79.9417 | 59.8258 | 1170.1654 |  | 6538 | 23536800 | 55072800 | 86608800 | 118144800
2038-08-25 11:01 | 5711.39 | 1.878 | 79.9251 | 59.8258 | 1673.8432 |  | 6539 | 23540400 | 55076400 | 86612400 | 118148400
2038-08-26 12:01 | 7049.99 | 2.3028 | 80.4327 | 59.8258 | 2066.1481 |  | 6540 | 23544000 | 55080000 | 86616000 | 118152000
2038-08-27 13:01 | 7717.18 | 2.5318 | 80.8123 | 59.8258 | 2261.6822 |  | 6541 | 23547600 | 55083600 | 86619600 | 118155600
2038-08-28 14:01 | 8258.48 | 2.7128 | 81.1828 | 59.8258 | 2420.3216 |  | 6542 | 23551200 | 55087200 | 86623200 | 118159200
2038-08-29 15:01 | 8092.15 | 2.6576 | 81.4992 | 59.8258 | 2371.5751 |  | 6543 | 23554800 | 55090800 | 86626800 | 118162800
2038-08-30 16:01 | 9834.58 | 3.1744 | 81.9278 | 59.8258 | 2882.2309 |  | 6544 | 23558400 | 55094400 | 86630400 | 118166400
2038-08-31 17:01 | 7903.75 | 2.5264 | 82.4714 | 59.8258 | 2316.3605 |  | 6545 | 23562000 | 55098000 | 86634000 | 118170000
2038-09-01 18:01 | 6144.91 | 1.9522 | 82.5898 | 59.8258 | 1800.8953 |  | 6546 | 23565600 | 55101600 | 86637600 | 118173600
2038-09-02 19:01 | 4899.89 | 1.5201 | 82.7624 | 59.8258 | 1436.016 |  | 6547 | 23569200 | 55105200 | 86641200 | 118177200
2038-09-03 20:01 | 3653.01 | 1.1421 | 82.4719 | 59.8258 | 1070.5915 |  | 6548 | 23572800 | 55108800 | 86644800 | 118180800
2038-09-04 21:01 | 3161.54 | 1 | 84.9718 | 59.8258 | 926.5559 |  | 6549 | 23576400 | 55112400 | 86648400 | 118184400
2038-09-05 22:01 | 3146.32 | 1 | 92.0838 | 59.8258 | 922.0954 |  | 6550 | 23580000 | 55116000 | 86652000 | 118188000
2038-09-06 23:01 | 0 | 0 | 67.2521 | 59.8258 | 0 |  | 6551 | 23583600 | 55119600 | 86655600 | 118191600
2038-09-08 00:01 | -626.573 | 2.1431 | 65.4082 | 59.8258 | -183.6304 |  | 6552 | 23587200 | 55123200 | 86659200 | 118195200
2038-09-09 01:01 | -963.109 | 2.9328 | 64.8545 | 59.8258 | -282.2594 |  | 6553 | 23590800 | 55126800 | 86662800 | 118198800
2038-09-10 02:01 | -1197.57 | 3.5012 | 64.5266 | 59.8258 | -350.9731 |  | 6554 | 23594400 | 55130400 | 86666400 | 118202400
2038-09-11 03:01 | -1211.61 | 3.4993 | 64.265 | 59.8258 | -355.0878 |  | 6555 | 23598000 | 55134000 | 86670000 | 118206000
2038-09-12 04:01 | -1085.05 | 3.1684 | 64.0446 | 59.8258 | -317.9968 |  | 6556 | 23601600 | 55137600 | 86673600 | 118209600
2038-09-13 05:01 | -953.469 | 2.8474 | 63.9599 | 59.8258 | -279.4342 |  | 6557 | 23605200 | 55141200 | 86677200 | 118213200
2038-09-14 06:01 | -899.419 | 2.7326 | 63.9058 | 59.8258 | -263.5937 |  | 6558 | 23608800 | 55144800 | 86680800 | 118216800
2038-09-15 07:01 | -426.461 | 1.4738 | 64.0126 | 59.8258 | -124.9834 |  | 6559 | 23612400 | 55148400 | 86684400 | 118220400
2038-09-16 08:01 | 0 | 1 | 65.3393 | 59.8258 | 0 |  | 6560 | 23616000 | 55152000 | 86688000 | 118224000
2038-09-17 09:01 | 3344.67 | 1.0779 | 79.561 | 59.8258 | 980.226 |  | 6561 | 23619600 | 55155600 | 86691600 | 118227600
2038-09-18 10:01 | 6468.97 | 2.1735 | 79.339 | 59.8258 | 1895.868 |  | 6562 | 23623200 | 55159200 | 86695200 | 118231200
2038-09-19 11:01 | 8703.62 | 2.9313 | 79.9414 | 59.8258 | 2550.7792 |  | 6563 | 23626800 | 55162800 | 86698800 | 118234800
2038-09-20 12:01 | 10287 | 3.349 | 81.053 | 59.8258 | 3014.8221 |  | 6564 | 23630400 | 55166400 | 86702400 | 118238400
2038-09-21 13:01 | 10933.6 | 3.4824 | 81.9801 | 59.8258 | 3204.3219 |  | 6565 | 23634000 | 55170000 | 86706000 | 118242000
2038-09-22 14:01 | 11478.4 | 3.7333 | 82.2062 | 59.8258 | 3363.987 |  | 6566 | 23637600 | 55173600 | 86709600 | 118245600
2038-09-23 15:01 | 10950 | 3.5104 | 82.846 | 59.8258 | 3209.1282 |  | 6567 | 23641200 | 55177200 | 86713200 | 118249200
2038-09-24 16:01 | 11607.8 | 3.7192 | 83.0681 | 59.8258 | 3401.9104 |  | 6568 | 23644800 | 55180800 | 86716800 | 118252800
2038-09-25 17:01 | 10411.7 | 3.2653 | 83.6686 | 59.8258 | 3051.3681 |  | 6569 | 23648400 | 55184400 | 86720400 | 118256400
2038-09-26 18:01 | 8627.56 | 2.6529 | 84.0545 | 59.8258 | 2528.4882 |  | 6570 | 23652000 | 55188000 | 86724000 | 118260000
2038-09-27 19:01 | 7243.95 | 2.1953 | 84.1622 | 59.8258 | 2122.9922 |  | 6571 | 23655600 | 55191600 | 86727600 | 118263600
2038-09-28 20:01 | 4978.2 | 1.4586 | 84.5228 | 59.8258 | 1458.9664 |  | 6572 | 23659200 | 55195200 | 86731200 | 118267200
2038-09-29 21:01 | 3524.83 | 1.0806 | 83.4821 | 59.8258 | 1033.0257 |  | 6573 | 23662800 | 55198800 | 86734800 | 118270800
2038-09-30 22:01 | 3193.98 | 1 | 67.8745 | 59.8258 | 936.0631 |  | 6574 | 23666400 | 55202400 | 86738400 | 118274400
2038-10-01 23:01 | 2790.28 | 1 | 67.6391 | 59.8258 | 817.7503 |  | 6575 | 23670000 | 55206000 | 86742000 | 118278000
2038-10-03 00:01 | 0 | 0 | 67.654 | 59.8258 | 0 |  | 6576 | 23673600 | 55209600 | 86745600 | 118281600
2038-10-04 01:01 | -225.692 | 0.97192 | 66.0348 | 59.8258 | -66.1438 |  | 6577 | 23677200 | 55213200 | 86749200 | 118285200
2038-10-05 02:01 | -292.634 | 1.2477 | 65.6581 | 59.8258 | -85.7626 |  | 6578 | 23680800 | 55216800 | 86752800 | 118288800
2038-10-06 03:01 | -267.564 | 1.1631 | 65.4514 | 59.8258 | -78.4153 |  | 6579 | 23684400 | 55220400 | 86756400 | 118292400
2038-10-07 04:01 | -331.093 | 1.3396 | 65.1597 | 59.8258 | -97.0338 |  | 6580 | 23688000 | 55224000 | 86760000 | 118296000
2038-10-08 05:01 | 937.892 | 1 | 66.009 | 59.8258 | 274.869 |  | 6581 | 23691600 | 55227600 | 86763600 | 118299600
2038-10-09 06:01 | 207.863 | 1 | 66.1323 | 59.8258 | 60.9186 |  | 6582 | 23695200 | 55231200 | 86767200 | 118303200
2038-10-10 07:01 | 2246.75 | 1 | 65.8524 | 59.8258 | 658.4574 |  | 6583 | 23698800 | 55234800 | 86770800 | 118306800
2038-10-11 08:01 | 2980.84 | 1 | 82.6214 | 59.8258 | 873.598 |  | 6584 | 23702400 | 55238400 | 86774400 | 118310400
2038-10-12 09:01 | 5224.56 | 1.732 | 80.227 | 59.8258 | 1531.1674 |  | 6585 | 23706000 | 55242000 | 86778000 | 118314000
2038-10-13 10:01 | 7668.85 | 2.6577 | 80.0019 | 59.8258 | 2247.5181 |  | 6586 | 23709600 | 55245600 | 86781600 | 118317600
2038-10-14 11:01 | 9234.3 | 3.0891 | 80.9884 | 59.8258 | 2706.3062 |  | 6587 | 23713200 | 55249200 | 86785200 | 118321200
2038-10-15 12:01 | 10725.7 | 3.5197 | 81.796 | 59.8258 | 3143.3924 |  | 6588 | 23716800 | 55252800 | 86788800 | 118324800
2038-10-16 13:01 | 11491.4 | 3.7344 | 82.4588 | 59.8258 | 3367.7969 |  | 6589 | 23720400 | 55256400 | 86792400 | 118328400
2038-10-17 14:01 | 12496.2 | 4.068 | 82.9045 | 59.8258 | 3662.2747 |  | 6590 | 23724000 | 55260000 | 86796000 | 118332000
2038-10-18 15:01 | 11815.2 | 3.6803 | 84.0076 | 59.8258 | 3462.6933 |  | 6591 | 23727600 | 55263600 | 86799600 | 118335600
2038-10-19 16:01 | 12651.7 | 4.0245 | 83.9207 | 59.8258 | 3707.8473 |  | 6592 | 23731200 | 55267200 | 86803200 | 118339200
2038-10-20 17:01 | 11271.4 | 3.5377 | 84.4263 | 59.8258 | 3303.3213 |  | 6593 | 23734800 | 55270800 | 86806800 | 118342800
2038-10-21 18:01 | 9027.91 | 2.7563 | 84.9289 | 59.8258 | 2645.8192 |  | 6594 | 23738400 | 55274400 | 86810400 | 118346400
2038-10-22 19:01 | 7744.54 | 2.3551 | 84.7948 | 59.8258 | 2269.7006 |  | 6595 | 23742000 | 55278000 | 86814000 | 118350000
2038-10-23 20:01 | 5621.32 | 1.6343 | 85.2849 | 59.8258 | 1647.4463 |  | 6596 | 23745600 | 55281600 | 86817600 | 118353600
2038-10-24 21:01 | 4355.77 | 1.314 | 84.3704 | 59.8258 | 1276.5502 |  | 6597 | 23749200 | 55285200 | 86821200 | 118357200
2038-10-25 22:01 | 3208.86 | 1 | 88.4578 | 59.8258 | 940.424 |  | 6598 | 23752800 | 55288800 | 86824800 | 118360800
2038-10-26 23:01 | 3199.28 | 1 | 68.1681 | 59.8258 | 937.6164 |  | 6599 | 23756400 | 55292400 | 86828400 | 118364400
2038-10-28 00:01 | 3171.07 | 1 | 67.9567 | 59.8258 | 929.3489 |  | 6600 | 23760000 | 55296000 | 86832000 | 118368000
2038-10-29 01:01 | 3143.12 | 1 | 67.7964 | 59.8258 | 921.1575 |  | 6601 | 23763600 | 55299600 | 86835600 | 118371600
2038-10-30 02:01 | 3190.59 | 1 | 67.6658 | 59.8258 | 935.0696 |  | 6602 | 23767200 | 55303200 | 86839200 | 118375200
2038-10-31 03:01 | 3173.44 | 1 | 67.5868 | 59.8258 | 930.0435 |  | 6603 | 23770800 | 55306800 | 86842800 | 118378800
2038-11-01 04:01 | 3229.85 | 1 | 67.5142 | 59.8258 | 946.5756 |  | 6604 | 23774400 | 55310400 | 86846400 | 118382400
2038-11-02 05:01 | 3206.22 | 1 | 67.4636 | 59.8258 | 939.6503 |  | 6605 | 23778000 | 55314000 | 86850000 | 118386000
2038-11-03 06:01 | 3267.29 | 1 | 67.4291 | 59.8258 | 957.5482 |  | 6606 | 23781600 | 55317600 | 86853600 | 118389600
2038-11-04 07:01 | 3277.45 | 1 | 89.7798 | 59.8258 | 960.5258 |  | 6607 | 23785200 | 55321200 | 86857200 | 118393200
2038-11-05 08:01 | 3292.79 | 1 | 93.9626 | 59.8258 | 965.0215 |  | 6608 | 23788800 | 55324800 | 86860800 | 118396800
2038-11-06 09:01 | 3272.72 | 1 | 85.4803 | 59.8258 | 959.1396 |  | 6609 | 23792400 | 55328400 | 86864400 | 118400400
2038-11-07 10:01 | 6840.98 | 2.2818 | 81.3076 | 59.8258 | 2004.8933 |  | 6610 | 23796000 | 55332000 | 86868000 | 118404000
2038-11-08 11:01 | 7357.27 | 2.3803 | 82.1708 | 59.8258 | 2156.203 |  | 6611 | 23799600 | 55335600 | 86871600 | 118407600
2038-11-09 12:01 | 6499.61 | 2.021 | 83.0301 | 59.8258 | 1904.8477 |  | 6612 | 23803200 | 55339200 | 86875200 | 118411200
2038-11-10 13:01 | 6860.25 | 2.1489 | 82.9276 | 59.8258 | 2010.5408 |  | 6613 | 23806800 | 55342800 | 86878800 | 118414800
2038-11-11 14:01 | 6639.21 | 2.0364 | 83.3149 | 59.8258 | 1945.7604 |  | 6614 | 23810400 | 55346400 | 86882400 | 118418400
2038-11-12 15:01 | 7950.16 | 2.5856 | 82.5197 | 59.8258 | 2329.9619 |  | 6615 | 23814000 | 55350000 | 86886000 | 118422000
2038-11-13 16:01 | 9022.06 | 3.0684 | 82.0482 | 59.8258 | 2644.1048 |  | 6616 | 23817600 | 55353600 | 86889600 | 118425600
2038-11-14 17:01 | 8291.18 | 2.6292 | 83.2558 | 59.8258 | 2429.905 |  | 6617 | 23821200 | 55357200 | 86893200 | 118429200
2038-11-15 18:01 | 7221.76 | 2.1982 | 83.9264 | 59.8258 | 2116.4889 |  | 6618 | 23824800 | 55360800 | 86896800 | 118432800
2038-11-16 19:01 | 6481.13 | 1.9412 | 84.1035 | 59.8258 | 1899.4317 |  | 6619 | 23828400 | 55364400 | 86900400 | 118436400
2038-11-17 20:01 | 4305.52 | 1.274 | 84.2418 | 59.8258 | 1261.8234 |  | 6620 | 23832000 | 55368000 | 86904000 | 118440000
2038-11-18 21:01 | 3297.2 | 1.0405 | 82.992 | 59.8258 | 966.3139 |  | 6621 | 23835600 | 55371600 | 86907600 | 118443600
2038-11-19 22:01 | 3103.03 | 1 | 67.9033 | 59.8258 | 909.4083 |  | 6622 | 23839200 | 55375200 | 86911200 | 118447200
2038-11-20 23:01 | 3076.66 | 1 | 67.6995 | 59.8258 | 901.68 |  | 6623 | 23842800 | 55378800 | 86914800 | 118450800
2038-11-22 00:01 | 3143.88 | 1 | 67.5667 | 59.8258 | 921.3803 |  | 6624 | 23846400 | 55382400 | 86918400 | 118454400
2038-11-23 01:01 | 1562.2 | 1 | 67.6143 | 59.8258 | 457.8356 |  | 6625 | 23850000 | 55386000 | 86922000 | 118458000
2038-11-24 02:01 | 688.885 | 1 | 67.4307 | 59.8258 | 201.8923 |  | 6626 | 23853600 | 55389600 | 86925600 | 118461600
2038-11-25 03:01 | 3243.75 | 1 | 66.9148 | 59.8258 | 950.6493 |  | 6627 | 23857200 | 55393200 | 86929200 | 118465200
2038-11-26 04:01 | 3270.19 | 1 | 67.0728 | 59.8258 | 958.3981 |  | 6628 | 23860800 | 55396800 | 86932800 | 118468800
2038-11-27 05:01 | 3262.48 | 1 | 67.1272 | 59.8258 | 956.1385 |  | 6629 | 23864400 | 55400400 | 86936400 | 118472400
2038-11-28 06:01 | 3233.47 | 1 | 67.1042 | 59.8258 | 947.6365 |  | 6630 | 23868000 | 55404000 | 86940000 | 118476000
2038-11-29 07:01 | 3173.18 | 1 | 67.1142 | 59.8258 | 929.9673 |  | 6631 | 23871600 | 55407600 | 86943600 | 118479600
2038-11-30 08:01 | 3116.77 | 1 | 67.1611 | 59.8258 | 913.4351 |  | 6632 | 23875200 | 55411200 | 86947200 | 118483200
2038-12-01 09:01 | 3220.73 | 1 | 67.1306 | 59.8258 | 943.9028 |  | 6633 | 23878800 | 55414800 | 86950800 | 118486800
2038-12-02 10:01 | 3212.34 | 1 | 67.0986 | 59.8258 | 941.4439 |  | 6634 | 23882400 | 55418400 | 86954400 | 118490400
2038-12-03 11:01 | 3214.44 | 1 | 91.9011 | 59.8258 | 942.0594 |  | 6635 | 23886000 | 55422000 | 86958000 | 118494000
2038-12-04 12:01 | 5009.44 | 1.575 | 81.7776 | 59.8258 | 1468.1219 |  | 6636 | 23889600 | 55425600 | 86961600 | 118497600
2038-12-05 13:01 | 4232.72 | 1.2516 | 82.9237 | 59.8258 | 1240.4878 |  | 6637 | 23893200 | 55429200 | 86965200 | 118501200
2038-12-06 14:01 | 4040.61 | 1.2333 | 82.4439 | 59.8258 | 1184.1859 |  | 6638 | 23896800 | 55432800 | 86968800 | 118504800
2038-12-07 15:01 | 5590.58 | 1.8166 | 81.4508 | 59.8258 | 1638.4373 |  | 6639 | 23900400 | 55436400 | 86972400 | 118508400
2038-12-08 16:01 | 5902.33 | 1.8863 | 81.8462 | 59.8258 | 1729.8022 |  | 6640 | 23904000 | 55440000 | 86976000 | 118512000
2038-12-09 17:01 | 6054.74 | 1.917 | 82.1115 | 59.8258 | 1774.4691 |  | 6641 | 23907600 | 55443600 | 86979600 | 118515600
2038-12-10 18:01 | 5039.49 | 1.5284 | 82.8092 | 59.8258 | 1476.9287 |  | 6642 | 23911200 | 55447200 | 86983200 | 118519200
2038-12-11 19:01 | 4346.88 | 1.3357 | 82.5472 | 59.8258 | 1273.9448 |  | 6643 | 23914800 | 55450800 | 86986800 | 118522800
2038-12-12 20:01 | 3120.94 | 1 | 87.3312 | 59.8258 | 914.6572 |  | 6644 | 23918400 | 55454400 | 86990400 | 118526400
2038-12-13 21:01 | 3149.49 | 1 | 67.1192 | 59.8258 | 923.0244 |  | 6645 | 23922000 | 55458000 | 86994000 | 118530000
2038-12-14 22:01 | 0 | 0 | 67.3061 | 59.8258 | 0 |  | 6646 | 23925600 | 55461600 | 86997600 | 118533600
2038-12-15 23:01 | -143.229 | 0.85726 | 66.0474 | 59.8258 | -41.9763 |  | 6647 | 23929200 | 55465200 | 87001200 | 118537200
2038-12-17 00:01 | -240.037 | 1.1233 | 65.5051 | 59.8258 | -70.3479 |  | 6648 | 23932800 | 55468800 | 87004800 | 118540800
2038-12-18 01:01 | -323.988 | 1.3242 | 65.1723 | 59.8258 | -94.9515 |  | 6649 | 23936400 | 55472400 | 87008400 | 118544400
2038-12-19 02:01 | -210.383 | 1.0105 | 65.1827 | 59.8258 | -61.6572 |  | 6650 | 23940000 | 55476000 | 87012000 | 118548000
2038-12-20 03:01 | -49.6992 | 0.61452 | 65.6006 | 59.8258 | -14.5654 |  | 6651 | 23943600 | 55479600 | 87015600 | 118551600
2038-12-21 04:01 | 2105.63 | 1 | 65.7035 | 59.8258 | 617.0992 |  | 6652 | 23947200 | 55483200 | 87019200 | 118555200
2038-12-22 05:01 | 3056.87 | 1 | 65.8203 | 59.8258 | 895.8802 |  | 6653 | 23950800 | 55486800 | 87022800 | 118558800
2038-12-23 06:01 | 3406.08 | 1 | 86.8413 | 59.8258 | 998.2235 |  | 6654 | 23954400 | 55490400 | 87026400 | 118562400
2038-12-24 07:01 | 3660.47 | 1.0521 | 82.3335 | 59.8258 | 1072.7779 |  | 6655 | 23958000 | 55494000 | 87030000 | 118566000
2038-12-25 08:01 | 3403.71 | 1 | 87.9364 | 59.8258 | 997.5289 |  | 6656 | 23961600 | 55497600 | 87033600 | 118569600
2038-12-26 09:01 | 3487.61 | 1 | 85.0303 | 59.8258 | 1022.1176 |  | 6657 | 23965200 | 55501200 | 87037200 | 118573200
2038-12-27 10:01 | 3601.2 | 1 | 86.9489 | 59.8258 | 1055.4075 |  | 6658 | 23968800 | 55504800 | 87040800 | 118576800
2038-12-28 11:01 | 3675.15 | 1 | 87.316 | 59.8258 | 1077.0801 |  | 6659 | 23972400 | 55508400 | 87044400 | 118580400
2038-12-29 12:01 | 3379.78 | 1 | 85.8611 | 59.8258 | 990.5157 |  | 6660 | 23976000 | 55512000 | 87048000 | 118584000
2038-12-30 13:01 | 3184.65 | 1 | 83.1929 | 59.8258 | 933.3288 |  | 6661 | 23979600 | 55515600 | 87051600 | 118587600
2038-12-31 14:01 | 3378.43 | 1.0834 | 80.9618 | 59.8258 | 990.1201 |  | 6662 | 23983200 | 55519200 | 87055200 | 118591200
2039-01-01 15:01 | 5432.36 | 1.7417 | 80.9573 | 59.8258 | 1592.0676 |  | 6663 | 23986800 | 55522800 | 87058800 | 118594800
2039-01-02 16:01 | 6231.63 | 2.0915 | 80.5571 | 59.8258 | 1826.3105 |  | 6664 | 23990400 | 55526400 | 87062400 | 118598400
2039-01-03 17:01 | 6862.01 | 2.2484 | 81.1051 | 59.8258 | 2011.0566 |  | 6665 | 23994000 | 55530000 | 87066000 | 118602000
2039-01-04 18:01 | 5622.49 | 1.7515 | 82.0389 | 59.8258 | 1647.7892 |  | 6666 | 23997600 | 55533600 | 87069600 | 118605600
2039-01-05 19:01 | 5060.72 | 1.5313 | 82.4573 | 59.8258 | 1483.1506 |  | 6667 | 24001200 | 55537200 | 87073200 | 118609200
2039-01-06 20:01 | 3166.04 | 1 | 84.4915 | 59.8258 | 927.8747 |  | 6668 | 24004800 | 55540800 | 87076800 | 118612800
2039-01-07 21:01 | 3068.31 | 1 | 90.3377 | 59.8258 | 899.2329 |  | 6669 | 24008400 | 55544400 | 87080400 | 118616400
2039-01-08 22:01 | 0 | 0 | 66.9612 | 59.8258 | 0 |  | 6670 | 24012000 | 55548000 | 87084000 | 118620000
2039-01-09 23:01 | -321.39 | 1.337 | 65.3612 | 59.8258 | -94.1901 |  | 6671 | 24015600 | 55551600 | 87087600 | 118623600
2039-01-11 00:01 | -386.23 | 1.4738 | 64.9339 | 59.8258 | -113.1928 |  | 6672 | 24019200 | 55555200 | 87091200 | 118627200
2039-01-12 01:01 | -399.659 | 1.5012 | 64.7225 | 59.8258 | -117.1285 |  | 6673 | 24022800 | 55558800 | 87094800 | 118630800
2039-01-13 02:01 | -533.488 | 1.8569 | 64.49 | 59.8258 | -156.3499 |  | 6674 | 24026400 | 55562400 | 87098400 | 118634400
2039-01-14 03:01 | -517.67 | 1.789 | 64.2994 | 59.8258 | -151.7141 |  | 6675 | 24030000 | 55566000 | 87102000 | 118638000
2039-01-15 04:01 | -654.947 | 2.1643 | 64.1171 | 59.8258 | -191.946 |  | 6676 | 24033600 | 55569600 | 87105600 | 118641600
2039-01-16 05:01 | -739.159 | 2.3623 | 63.9257 | 59.8258 | -216.6261 |  | 6677 | 24037200 | 55573200 | 87109200 | 118645200
2039-01-17 06:01 | 13.4547 | 1 | 65.2232 | 59.8258 | 3.9432 |  | 6678 | 24040800 | 55576800 | 87112800 | 118648800
2039-01-18 07:01 | 1790.81 | 1 | 65.0447 | 59.8258 | 524.8346 |  | 6679 | 24044400 | 55580400 | 87116400 | 118652400
2039-01-19 08:01 | 2652.43 | 1 | 80.623 | 59.8258 | 777.3505 |  | 6680 | 24048000 | 55584000 | 87120000 | 118656000
2039-01-20 09:01 | 2915.01 | 1 | 84.2596 | 59.8258 | 854.3051 |  | 6681 | 24051600 | 55587600 | 87123600 | 118659600
2039-01-21 10:01 | 4431.09 | 1.4375 | 79.8254 | 59.8258 | 1298.6243 |  | 6682 | 24055200 | 55591200 | 87127200 | 118663200
2039-01-22 11:01 | 5872.63 | 1.9201 | 80.0359 | 59.8258 | 1721.098 |  | 6683 | 24058800 | 55594800 | 87130800 | 118666800
2039-01-23 12:01 | 6317.56 | 1.9943 | 80.9308 | 59.8258 | 1851.4941 |  | 6684 | 24062400 | 55598400 | 87134400 | 118670400
2039-01-24 13:01 | 8174.15 | 2.6552 | 80.7973 | 59.8258 | 2395.6069 |  | 6685 | 24066000 | 55602000 | 87138000 | 118674000
2039-01-25 14:01 | 8995.01 | 2.9139 | 81.2759 | 59.8258 | 2636.1772 |  | 6686 | 24069600 | 55605600 | 87141600 | 118677600
2039-01-26 15:01 | 8793.64 | 2.9005 | 81.4365 | 59.8258 | 2577.1615 |  | 6687 | 24073200 | 55609200 | 87145200 | 118681200
2039-01-27 16:01 | 10654.5 | 3.5213 | 81.6333 | 59.8258 | 3122.5257 |  | 6688 | 24076800 | 55612800 | 87148800 | 118684800
2039-01-28 17:01 | 8863.32 | 2.7292 | 83.0925 | 59.8258 | 2597.5827 |  | 6689 | 24080400 | 55616400 | 87152400 | 118688400
2039-01-29 18:01 | 6805.21 | 2.0445 | 83.56 | 59.8258 | 1994.4102 |  | 6690 | 24084000 | 55620000 | 87156000 | 118692000
2039-01-30 19:01 | 5272.6 | 1.7576 | 81.8575 | 59.8258 | 1545.2465 |  | 6691 | 24087600 | 55623600 | 87159600 | 118695600
2039-01-31 20:01 | 4170.01 | 1.4011 | 81.5101 | 59.8258 | 1222.1093 |  | 6692 | 24091200 | 55627200 | 87163200 | 118699200
2039-02-01 21:01 | 3177.86 | 1.0174 | 81.9533 | 59.8258 | 931.3388 |  | 6693 | 24094800 | 55630800 | 87166800 | 118702800
2039-02-02 22:01 | 3043.82 | 1 | 89.2948 | 59.8258 | 892.0556 |  | 6694 | 24098400 | 55634400 | 87170400 | 118706400
2039-02-03 23:01 | 0 | 0 | 67.2223 | 59.8258 | 0 |  | 6695 | 24102000 | 55638000 | 87174000 | 118710000
2039-02-05 00:01 | -853.055 | 2.6921 | 65.2595 | 59.8258 | -250.0057 |  | 6696 | 24105600 | 55641600 | 87177600 | 118713600
2039-02-06 01:01 | -1233.65 | 3.6111 | 64.7099 | 59.8258 | -361.5471 |  | 6697 | 24109200 | 55645200 | 87181200 | 118717200
2039-02-07 02:01 | -1513.34 | 4.2969 | 64.3429 | 59.8258 | -443.5162 |  | 6698 | 24112800 | 55648800 | 87184800 | 118720800
2039-02-08 03:01 | -1651.1 | 4.6234 | 64.0384 | 59.8258 | -483.8896 |  | 6699 | 24116400 | 55652400 | 87188400 | 118724400
2039-02-09 04:01 | -1930.54 | 5.3714 | 63.7335 | 59.8258 | -565.7854 |  | 6700 | 24120000 | 55656000 | 87192000 | 118728000
2039-02-10 05:01 | -2161.06 | 5.9499 | 63.4882 | 59.8258 | -633.3442 |  | 6701 | 24123600 | 55659600 | 87195600 | 118731600
2039-02-11 06:01 | -1573.3 | 4.3017 | 63.2712 | 59.8258 | -461.0887 |  | 6702 | 24127200 | 55663200 | 87199200 | 118735200
2039-02-12 07:01 | -985.597 | 2.8544 | 63.2775 | 59.8258 | -288.85 |  | 6703 | 24130800 | 55666800 | 87202800 | 118738800
2039-02-13 08:01 | -682.248 | 2.162 | 63.3969 | 59.8258 | -199.9472 |  | 6704 | 24134400 | 55670400 | 87206400 | 118742400
2039-02-14 09:01 | 2288.15 | 1 | 64.621 | 59.8258 | 670.5906 |  | 6705 | 24138000 | 55674000 | 87210000 | 118746000
2039-02-15 10:01 | 3034.18 | 1 | 64.8966 | 59.8258 | 889.2304 |  | 6706 | 24141600 | 55677600 | 87213600 | 118749600
2039-02-16 11:01 | 3142.41 | 1 | 84.0298 | 59.8258 | 920.9495 |  | 6707 | 24145200 | 55681200 | 87217200 | 118753200
2039-02-17 12:01 | 4656.48 | 1.461 | 80.1629 | 59.8258 | 1364.6796 |  | 6708 | 24148800 | 55684800 | 87220800 | 118756800
2039-02-18 13:01 | 4060.68 | 1.3381 | 79.7913 | 59.8258 | 1190.0678 |  | 6709 | 24152400 | 55688400 | 87224400 | 118760400
2039-02-19 14:01 | 4566.34 | 1.4536 | 80.4101 | 59.8258 | 1338.2621 |  | 6710 | 24156000 | 55692000 | 87228000 | 118764000
2039-02-20 15:01 | 5666.79 | 1.8411 | 80.2244 | 59.8258 | 1660.7722 |  | 6711 | 24159600 | 55695600 | 87231600 | 118767600
2039-02-21 16:01 | 7695.77 | 2.5237 | 80.3078 | 59.8258 | 2255.4075 |  | 6712 | 24163200 | 55699200 | 87235200 | 118771200
2039-02-22 17:01 | 5818.83 | 1.8461 | 81.2165 | 59.8258 | 1705.3307 |  | 6713 | 24166800 | 55702800 | 87238800 | 118774800
2039-02-23 18:01 | 3906.65 | 1.2483 | 81.1219 | 59.8258 | 1144.9261 |  | 6714 | 24170400 | 55706400 | 87242400 | 118778400
2039-02-24 19:01 | 3111.79 | 1 | 86.7297 | 59.8258 | 911.9756 |  | 6715 | 24174000 | 55710000 | 87246000 | 118782000
2039-02-25 20:01 | 3155.27 | 1 | 66.1999 | 59.8258 | 924.7184 |  | 6716 | 24177600 | 55713600 | 87249600 | 118785600
2039-02-26 21:01 | 2995.9 | 1 | 66.151 | 59.8258 | 878.0116 |  | 6717 | 24181200 | 55717200 | 87253200 | 118789200
2039-02-27 22:01 | -51.4516 | 0.69241 | 65.9661 | 59.8258 | -15.079 |  | 6718 | 24184800 | 55720800 | 87256800 | 118792800
2039-02-28 23:01 | -1600.15 | 4.7526 | 64.3105 | 59.8258 | -468.9577 |  | 6719 | 24188400 | 55724400 | 87260400 | 118796400
2039-03-02 00:01 | -2284.56 | 6.108 | 63.6815 | 59.8258 | -669.5384 |  | 6720 | 24192000 | 55728000 | 87264000 | 118800000
2039-03-03 01:01 | -2605.73 | 6.108 | 63.1107 | 59.8258 | -763.6641 |  | 6721 | 24195600 | 55731600 | 87267600 | 118803600
2039-03-04 02:01 | -2774.55 | 6.108 | 62.6985 | 59.8258 | -813.1403 |  | 6722 | 24199200 | 55735200 | 87271200 | 118807200
2039-03-05 03:01 | -3028.39 | 6.108 | 62.2298 | 59.8258 | -887.5335 |  | 6723 | 24202800 | 55738800 | 87274800 | 118810800
2039-03-06 04:01 | -3272.1 | 6.108 | 61.8029 | 59.8258 | -958.9578 |  | 6724 | 24206400 | 55742400 | 87278400 | 118814400
2039-03-07 05:01 | -3402.92 | 6.108 | 61.5053 | 59.8258 | -997.2974 |  | 6725 | 24210000 | 55746000 | 87282000 | 118818000
2039-03-08 06:01 | -2658.53 | 6.108 | 61.8978 | 59.8258 | -779.1382 |  | 6726 | 24213600 | 55749600 | 87285600 | 118821600
2039-03-09 07:01 | -1820.72 | 5.0518 | 62.1986 | 59.8258 | -533.6004 |  | 6727 | 24217200 | 55753200 | 87289200 | 118825200
2039-03-10 08:01 | -1520.1 | 4.2928 | 62.2623 | 59.8258 | -445.4973 |  | 6728 | 24220800 | 55756800 | 87292800 | 118828800
2039-03-11 09:01 | -563.339 | 1.73 | 62.3796 | 59.8258 | -165.0984 |  | 6729 | 24224400 | 55760400 | 87296400 | 118832400
2039-03-12 10:01 | 2670.36 | 1 | 63.7408 | 59.8258 | 782.6053 |  | 6730 | 24228000 | 55764000 | 87300000 | 118836000
2039-03-13 11:01 | 3180.59 | 1 | 81.0462 | 59.8258 | 932.1389 |  | 6731 | 24231600 | 55767600 | 87303600 | 118839600
2039-03-14 12:01 | 4317.05 | 1.3505 | 79.3987 | 59.8258 | 1265.2025 |  | 6732 | 24235200 | 55771200 | 87307200 | 118843200
2039-03-15 13:01 | 5240.86 | 1.6703 | 79.4546 | 59.8258 | 1535.9444 |  | 6733 | 24238800 | 55774800 | 87310800 | 118846800
2039-03-16 14:01 | 6118.59 | 1.9479 | 79.8261 | 59.8258 | 1793.1817 |  | 6734 | 24242400 | 55778400 | 87314400 | 118850400
2039-03-17 15:01 | 6061.37 | 1.9693 | 79.8982 | 59.8258 | 1776.4122 |  | 6735 | 24246000 | 55782000 | 87318000 | 118854000
2039-03-18 16:01 | 7936.79 | 2.568 | 80.1285 | 59.8258 | 2326.0435 |  | 6736 | 24249600 | 55785600 | 87321600 | 118857600
2039-03-19 17:01 | 5910.14 | 1.8436 | 81.0813 | 59.8258 | 1732.0911 |  | 6737 | 24253200 | 55789200 | 87325200 | 118861200
2039-03-20 18:01 | 3766 | 1.2001 | 80.8024 | 59.8258 | 1103.7056 |  | 6738 | 24256800 | 55792800 | 87328800 | 118864800
2039-03-21 19:01 | 3120.54 | 1 | 87.514 | 59.8258 | 914.54 |  | 6739 | 24260400 | 55796400 | 87332400 | 118868400
2039-03-22 20:01 | 3162.9 | 1 | 65.7877 | 59.8258 | 926.9545 |  | 6740 | 24264000 | 55800000 | 87336000 | 118872000
2039-03-23 21:01 | 3001.35 | 1 | 65.7688 | 59.8258 | 879.6089 |  | 6741 | 24267600 | 55803600 | 87339600 | 118875600
2039-03-24 22:01 | -94.2675 | 0.80621 | 65.4004 | 59.8258 | -27.6271 |  | 6742 | 24271200 | 55807200 | 87343200 | 118879200
2039-03-25 23:01 | -1354.19 | 4.111 | 63.9745 | 59.8258 | -396.8739 |  | 6743 | 24274800 | 55810800 | 87346800 | 118882800
2039-03-27 00:01 | -1771.11 | 5.0021 | 63.4582 | 59.8258 | -519.0611 |  | 6744 | 24278400 | 55814400 | 87350400 | 118886400
2039-03-28 01:01 | -2016.98 | 5.6126 | 63.1591 | 59.8258 | -591.1185 |  | 6745 | 24282000 | 55818000 | 87354000 | 118890000
2039-03-29 02:01 | -2155.2 | 5.9557 | 62.8971 | 59.8258 | -631.6268 |  | 6746 | 24285600 | 55821600 | 87357600 | 118893600
2039-03-30 03:01 | -2506.41 | 6.108 | 62.4407 | 59.8258 | -734.5563 |  | 6747 | 24289200 | 55825200 | 87361200 | 118897200
2039-03-31 04:01 | -2413.04 | 6.108 | 62.2916 | 59.8258 | -707.1922 |  | 6748 | 24292800 | 55828800 | 87364800 | 118900800
2039-04-01 05:01 | -1957.85 | 5.414 | 62.3137 | 59.8258 | -573.7892 |  | 6749 | 24296400 | 55832400 | 87368400 | 118904400
2039-04-02 06:01 | -1925.42 | 5.3803 | 62.2973 | 59.8258 | -564.2849 |  | 6750 | 24300000 | 55836000 | 87372000 | 118908000
2039-04-03 07:01 | -1280.7 | 3.6016 | 62.2519 | 59.8258 | -375.3361 |  | 6751 | 24303600 | 55839600 | 87375600 | 118911600
2039-04-04 08:01 | -638.193 | 1.9975 | 62.4327 | 59.8258 | -187.0359 |  | 6752 | 24307200 | 55843200 | 87379200 | 118915200
2039-04-05 09:01 | 2535.7 | 1 | 80.3901 | 59.8258 | 743.1403 |  | 6753 | 24310800 | 55846800 | 87382800 | 118918800
2039-04-06 10:01 | 5031.71 | 1.6413 | 78.3956 | 59.8258 | 1474.6486 |  | 6754 | 24314400 | 55850400 | 87386400 | 118922400
2039-04-07 11:01 | 7394.55 | 2.4524 | 78.7425 | 59.8258 | 2167.1287 |  | 6755 | 24318000 | 55854000 | 87390000 | 118926000
2039-04-08 12:01 | 8740.04 | 2.9594 | 79.1007 | 59.8258 | 2561.4529 |  | 6756 | 24321600 | 55857600 | 87393600 | 118929600
2039-04-09 13:01 | 9608.34 | 3.1535 | 80.1198 | 59.8258 | 2815.9265 |  | 6757 | 24325200 | 55861200 | 87397200 | 118933200
2039-04-10 14:01 | 10478.9 | 3.3692 | 80.9384 | 59.8258 | 3071.0624 |  | 6758 | 24328800 | 55864800 | 87400800 | 118936800
2039-04-11 15:01 | 11619.2 | 3.7358 | 81.4162 | 59.8258 | 3405.2514 |  | 6759 | 24332400 | 55868400 | 87404400 | 118940400
2039-04-12 16:01 | 10993.1 | 3.4935 | 82.0696 | 59.8258 | 3221.7596 |  | 6760 | 24336000 | 55872000 | 87408000 | 118944000
2039-04-13 17:01 | 9476.41 | 2.9463 | 82.6561 | 59.8258 | 2777.2616 |  | 6761 | 24339600 | 55875600 | 87411600 | 118947600
2039-04-14 18:01 | 7002.58 | 2.1725 | 82.7397 | 59.8258 | 2052.2536 |  | 6762 | 24343200 | 55879200 | 87415200 | 118951200
2039-04-15 19:01 | 5243.74 | 1.5753 | 83.0221 | 59.8258 | 1536.7885 |  | 6763 | 24346800 | 55882800 | 87418800 | 118954800
2039-04-16 20:01 | 3240.9 | 1 | 85.5602 | 59.8258 | 949.814 |  | 6764 | 24350400 | 55886400 | 87422400 | 118958400
2039-04-17 21:01 | 3118.01 | 1 | 66.8419 | 59.8258 | 913.7985 |  | 6765 | 24354000 | 55890000 | 87426000 | 118962000
2039-04-18 22:01 | 0 | 0 | 66.879 | 59.8258 | 0 |  | 6766 | 24357600 | 55893600 | 87429600 | 118965600
2039-04-19 23:01 | -589.381 | 1.8949 | 64.8732 | 59.8258 | -172.7305 |  | 6767 | 24361200 | 55897200 | 87433200 | 118969200
2039-04-21 00:01 | -820.635 | 2.5886 | 64.4141 | 59.8258 | -240.5044 |  | 6768 | 24364800 | 55900800 | 87436800 | 118972800
2039-04-22 01:01 | -1208.6 | 3.582 | 64.0327 | 59.8258 | -354.2057 |  | 6769 | 24368400 | 55904400 | 87440400 | 118976400
2039-04-23 02:01 | -1473.92 | 4.226 | 63.7097 | 59.8258 | -431.9633 |  | 6770 | 24372000 | 55908000 | 87444000 | 118980000
2039-04-24 03:01 | -1294.4 | 3.6944 | 63.4154 | 59.8258 | -379.3512 |  | 6771 | 24375600 | 55911600 | 87447600 | 118983600
2039-04-25 04:01 | -1415.98 | 4.0803 | 63.2771 | 59.8258 | -414.9828 |  | 6772 | 24379200 | 55915200 | 87451200 | 118987200
2039-04-26 05:01 | -1150.32 | 3.3277 | 63.1374 | 59.8258 | -337.1255 |  | 6773 | 24382800 | 55918800 | 87454800 | 118990800
2039-04-27 06:01 | -1181.53 | 3.4832 | 63.09 | 59.8258 | -346.2723 |  | 6774 | 24386400 | 55922400 | 87458400 | 118994400
2039-04-28 07:01 | -914.291 | 2.7437 | 63.0423 | 59.8258 | -267.9522 |  | 6775 | 24390000 | 55926000 | 87462000 | 118998000
2039-04-29 08:01 | -143.82 | 0.72144 | 63.6326 | 59.8258 | -42.1495 |  | 6776 | 24393600 | 55929600 | 87465600 | 119001600
2039-04-30 09:01 | 2754.71 | 1.1796 | 75.2914 | 59.8258 | 807.3258 |  | 6777 | 24397200 | 55933200 | 87469200 | 119005200
2039-05-01 10:01 | 5780.73 | 2.0503 | 77.8634 | 59.8258 | 1694.1647 |  | 6778 | 24400800 | 55936800 | 87472800 | 119008800
2039-05-02 11:01 | 8065.62 | 2.7601 | 78.9191 | 59.8258 | 2363.7999 |  | 6779 | 24404400 | 55940400 | 87476400 | 119012400
2039-05-03 12:01 | 9330.56 | 3.1187 | 79.8632 | 59.8258 | 2734.5172 |  | 6780 | 24408000 | 55944000 | 87480000 | 119016000
2039-05-04 13:01 | 10215.4 | 3.3313 | 80.7587 | 59.8258 | 2993.8382 |  | 6781 | 24411600 | 55947600 | 87483600 | 119019600
2039-05-05 14:01 | 10984.5 | 3.5292 | 81.4701 | 59.8258 | 3219.2392 |  | 6782 | 24415200 | 55951200 | 87487200 | 119023200
2039-05-06 15:01 | 11802.5 | 3.8229 | 81.7943 | 59.8258 | 3458.9713 |  | 6783 | 24418800 | 55954800 | 87490800 | 119026800
2039-05-07 16:01 | 11083 | 3.5189 | 82.4898 | 59.8258 | 3248.1067 |  | 6784 | 24422400 | 55958400 | 87494400 | 119030400
2039-05-08 17:01 | 9326.95 | 2.9614 | 82.6964 | 59.8258 | 2733.4592 |  | 6785 | 24426000 | 55962000 | 87498000 | 119034000
2039-05-09 18:01 | 7224.74 | 2.2212 | 83.1465 | 59.8258 | 2117.3623 |  | 6786 | 24429600 | 55965600 | 87501600 | 119037600
2039-05-10 19:01 | 5841.54 | 1.7341 | 83.4805 | 59.8258 | 1711.9864 |  | 6787 | 24433200 | 55969200 | 87505200 | 119041200
2039-05-11 20:01 | 3302.85 | 1 | 84.4377 | 59.8258 | 967.9698 |  | 6788 | 24436800 | 55972800 | 87508800 | 119044800
2039-05-12 21:01 | 3143.38 | 1 | 67.1342 | 59.8258 | 921.2337 |  | 6789 | 24440400 | 55976400 | 87512400 | 119048400
2039-05-13 22:01 | 0 | 0 | 67.1381 | 59.8258 | 0 |  | 6790 | 24444000 | 55980000 | 87516000 | 119052000
2039-05-14 23:01 | -490.714 | 1.6966 | 65.2196 | 59.8258 | -143.8141 |  | 6791 | 24447600 | 55983600 | 87519600 | 119055600
2039-05-16 00:01 | -759.234 | 2.4343 | 64.6777 | 59.8258 | -222.5095 |  | 6792 | 24451200 | 55987200 | 87523200 | 119059200
2039-05-17 01:01 | -1037.42 | 3.1263 | 64.2727 | 59.8258 | -304.0378 |  | 6793 | 24454800 | 55990800 | 87526800 | 119062800
2039-05-18 02:01 | -1047.77 | 3.1042 | 63.9773 | 59.8258 | -307.0711 |  | 6794 | 24458400 | 55994400 | 87530400 | 119066400
2039-05-19 03:01 | -1257.11 | 3.6816 | 63.7091 | 59.8258 | -368.4226 |  | 6795 | 24462000 | 55998000 | 87534000 | 119070000
2039-05-20 04:01 | -1452.75 | 4.1708 | 63.4897 | 59.8258 | -425.759 |  | 6796 | 24465600 | 56001600 | 87537600 | 119073600
2039-05-21 05:01 | -1047.94 | 3.0339 | 63.3259 | 59.8258 | -307.1209 |  | 6797 | 24469200 | 56005200 | 87541200 | 119077200
2039-05-22 06:01 | -1219.25 | 3.6038 | 63.2872 | 59.8258 | -357.3269 |  | 6798 | 24472800 | 56008800 | 87544800 | 119080800
2039-05-23 07:01 | -798.652 | 2.4133 | 63.2246 | 59.8258 | -234.0618 |  | 6799 | 24476400 | 56012400 | 87548400 | 119084400
2039-05-24 08:01 | -236.811 | 1.0005 | 63.637 | 59.8258 | -69.4025 |  | 6800 | 24480000 | 56016000 | 87552000 | 119088000
2039-05-25 09:01 | 2383.4 | 1.0242 | 75.404 | 59.8258 | 698.5056 |  | 6801 | 24483600 | 56019600 | 87555600 | 119091600
2039-05-26 10:01 | 5751.23 | 1.9188 | 78.7686 | 59.8258 | 1685.5191 |  | 6802 | 24487200 | 56023200 | 87559200 | 119095200
2039-05-27 11:01 | 7782.78 | 2.6772 | 78.9474 | 59.8258 | 2280.9077 |  | 6803 | 24490800 | 56026800 | 87562800 | 119098800
2039-05-28 12:01 | 9123.55 | 3.093 | 79.736 | 59.8258 | 2673.8486 |  | 6804 | 24494400 | 56030400 | 87566400 | 119102400
2039-05-29 13:01 | 10105.7 | 3.3033 | 80.7681 | 59.8258 | 2961.6883 |  | 6805 | 24498000 | 56034000 | 87570000 | 119106000
2039-05-30 14:01 | 10904.4 | 3.5388 | 81.3676 | 59.8258 | 3195.7642 |  | 6806 | 24501600 | 56037600 | 87573600 | 119109600
2039-05-31 15:01 | 11737.7 | 3.8586 | 81.626 | 59.8258 | 3439.9803 |  | 6807 | 24505200 | 56041200 | 87577200 | 119113200
2039-06-01 16:01 | 11207.4 | 3.5956 | 82.3756 | 59.8258 | 3284.5647 |  | 6808 | 24508800 | 56044800 | 87580800 | 119116800
2039-06-02 17:01 | 9559.17 | 3.0501 | 82.6848 | 59.8258 | 2801.5162 |  | 6809 | 24512400 | 56048400 | 87584400 | 119120400
2039-06-03 18:01 | 7340.03 | 2.2447 | 83.3106 | 59.8258 | 2151.1504 |  | 6810 | 24516000 | 56052000 | 87588000 | 119124000
2039-06-04 19:01 | 5983.82 | 1.7927 | 83.4183 | 59.8258 | 1753.6845 |  | 6811 | 24519600 | 56055600 | 87591600 | 119127600
2039-06-05 20:01 | 3451.9 | 1.0355 | 83.1969 | 59.8258 | 1011.652 |  | 6812 | 24523200 | 56059200 | 87595200 | 119131200
2039-06-06 21:01 | 3198.48 | 1 | 87.4303 | 59.8258 | 937.382 |  | 6813 | 24526800 | 56062800 | 87598800 | 119134800
2039-06-07 22:01 | 0 | 0 | 67.2373 | 59.8258 | 0 |  | 6814 | 24530400 | 56066400 | 87602400 | 119138400
2039-06-08 23:01 | -148.872 | 0.81278 | 65.7932 | 59.8258 | -43.6301 |  | 6815 | 24534000 | 56070000 | 87606000 | 119142000
2039-06-10 00:01 | -702.395 | 2.3468 | 64.8673 | 59.8258 | -205.8517 |  | 6816 | 24537600 | 56073600 | 87609600 | 119145600
2039-06-11 01:01 | -897.439 | 2.7551 | 64.418 | 59.8258 | -263.0134 |  | 6817 | 24541200 | 56077200 | 87613200 | 119149200
2039-06-12 02:01 | -905.724 | 2.7505 | 64.1333 | 59.8258 | -265.4415 |  | 6818 | 24544800 | 56080800 | 87616800 | 119152800
2039-06-13 03:01 | -1078.67 | 3.2248 | 63.8665 | 59.8258 | -316.127 |  | 6819 | 24548400 | 56084400 | 87620400 | 119156400
2039-06-14 04:01 | -965.607 | 2.8845 | 63.6853 | 59.8258 | -282.9915 |  | 6820 | 24552000 | 56088000 | 87624000 | 119160000
2039-06-15 05:01 | -614.785 | 1.9715 | 63.6543 | 59.8258 | -180.1757 |  | 6821 | 24555600 | 56091600 | 87627600 | 119163600
2039-06-16 06:01 | -815.653 | 2.5937 | 63.5939 | 59.8258 | -239.0443 |  | 6822 | 24559200 | 56095200 | 87631200 | 119167200
2039-06-17 07:01 | -317.435 | 1.199 | 63.7338 | 59.8258 | -93.031 |  | 6823 | 24562800 | 56098800 | 87634800 | 119170800
2039-06-18 08:01 | -102.745 | 0.74529 | 64.321 | 59.8258 | -30.1116 |  | 6824 | 24566400 | 56102400 | 87638400 | 119174400
2039-06-19 09:01 | 2457.96 | 1.017 | 76.0224 | 59.8258 | 720.357 |  | 6825 | 24570000 | 56106000 | 87642000 | 119178000
2039-06-20 10:01 | 6273.32 | 2.2001 | 78.2803 | 59.8258 | 1838.5286 |  | 6826 | 24573600 | 56109600 | 87645600 | 119181600
2039-06-21 11:01 | 8590.21 | 2.9024 | 79.4183 | 59.8258 | 2517.542 |  | 6827 | 24577200 | 56113200 | 87649200 | 119185200
2039-06-22 12:01 | 9960.07 | 3.3213 | 80.2552 | 59.8258 | 2919.0084 |  | 6828 | 24580800 | 56116800 | 87652800 | 119188800
2039-06-23 13:01 | 10530.5 | 3.5307 | 80.7492 | 59.8258 | 3086.1849 |  | 6829 | 24584400 | 56120400 | 87656400 | 119192400
2039-06-24 14:01 | 11354.9 | 3.7389 | 81.4735 | 59.8258 | 3327.7927 |  | 6830 | 24588000 | 56124000 | 87660000 | 119196000
2039-06-25 15:01 | 12607.1 | 4.018 | 82.3747 | 59.8258 | 3694.7763 |  | 6831 | 24591600 | 56127600 | 87663600 | 119199600
2039-06-26 16:01 | 12021.8 | 3.7994 | 82.9634 | 59.8258 | 3523.2418 |  | 6832 | 24595200 | 56131200 | 87667200 | 119203200
2039-06-27 17:01 | 10388 | 3.2502 | 83.3645 | 59.8258 | 3044.4223 |  | 6833 | 24598800 | 56134800 | 87670800 | 119206800
2039-06-28 18:01 | 8254.02 | 2.482 | 83.9746 | 59.8258 | 2419.0145 |  | 6834 | 24602400 | 56138400 | 87674400 | 119210400
2039-06-29 19:01 | 6999.99 | 2.1403 | 83.5536 | 59.8258 | 2051.4946 |  | 6835 | 24606000 | 56142000 | 87678000 | 119214000
2039-06-30 20:01 | 4853.53 | 1.4356 | 83.9026 | 59.8258 | 1422.4292 |  | 6836 | 24609600 | 56145600 | 87681600 | 119217600
2039-07-01 21:01 | 3240.67 | 1 | 83.7334 | 59.8258 | 949.7466 |  | 6837 | 24613200 | 56149200 | 87685200 | 119221200
2039-07-02 22:01 | 3067.65 | 1 | 67.4018 | 59.8258 | 899.0395 |  | 6838 | 24616800 | 56152800 | 87688800 | 119224800
2039-07-03 23:01 | 0 | 0 | 67.42 | 59.8258 | 0 |  | 6839 | 24620400 | 56156400 | 87692400 | 119228400
2039-07-05 00:01 | -192.187 | 0.99794 | 65.9572 | 59.8258 | -56.3244 |  | 6840 | 24624000 | 56160000 | 87696000 | 119232000
2039-07-06 01:01 | -425.563 | 1.5982 | 65.2184 | 59.8258 | -124.7202 |  | 6841 | 24627600 | 56163600 | 87699600 | 119235600
2039-07-07 02:01 | -547.906 | 1.88 | 64.8266 | 59.8258 | -160.5754 |  | 6842 | 24631200 | 56167200 | 87703200 | 119239200
2039-07-08 03:01 | -824.869 | 2.5998 | 64.4594 | 59.8258 | -241.7452 |  | 6843 | 24634800 | 56170800 | 87706800 | 119242800
2039-07-09 04:01 | -892.377 | 2.7279 | 64.1505 | 59.8258 | -261.5299 |  | 6844 | 24638400 | 56174400 | 87710400 | 119246400
2039-07-10 05:01 | -926.515 | 2.8139 | 63.9711 | 59.8258 | -271.5347 |  | 6845 | 24642000 | 56178000 | 87714000 | 119250000
2039-07-11 06:01 | -222.409 | 0.92006 | 64.2387 | 59.8258 | -65.1816 |  | 6846 | 24645600 | 56181600 | 87717600 | 119253600
2039-07-12 07:01 | 1879.63 | 1 | 65.163 | 59.8258 | 550.8652 |  | 6847 | 24649200 | 56185200 | 87721200 | 119257200
2039-07-13 08:01 | -201.918 | 1.095 | 64.742 | 59.8258 | -59.1763 |  | 6848 | 24652800 | 56188800 | 87724800 | 119260800
2039-07-14 09:01 | 2212.88 | 1 | 65.2142 | 59.8258 | 648.5311 |  | 6849 | 24656400 | 56192400 | 87728400 | 119264400
2039-07-15 10:01 | 3090.61 | 1.0299 | 79.3261 | 59.8258 | 905.7684 |  | 6850 | 24660000 | 56196000 | 87732000 | 119268000
2039-07-16 11:01 | 3112.76 | 1 | 82.6946 | 59.8258 | 912.2599 |  | 6851 | 24663600 | 56199600 | 87735600 | 119271600
2039-07-17 12:01 | 3218.79 | 1 | 84.3553 | 59.8258 | 943.3342 |  | 6852 | 24667200 | 56203200 | 87739200 | 119275200
2039-07-18 13:01 | 3216.75 | 1 | 84.2329 | 59.8258 | 942.7364 |  | 6853 | 24670800 | 56206800 | 87742800 | 119278800
2039-07-19 14:01 | 4411.99 | 1.3404 | 80.9586 | 59.8258 | 1293.0266 |  | 6854 | 24674400 | 56210400 | 87746400 | 119282400
2039-07-20 15:01 | 3865 | 1.2249 | 80.4813 | 59.8258 | 1132.7197 |  | 6855 | 24678000 | 56214000 | 87750000 | 119286000
2039-07-21 16:01 | 6411.34 | 2.15 | 79.6563 | 59.8258 | 1878.9783 |  | 6856 | 24681600 | 56217600 | 87753600 | 119289600
2039-07-22 17:01 | 5651.44 | 1.7797 | 80.8781 | 59.8258 | 1656.2736 |  | 6857 | 24685200 | 56221200 | 87757200 | 119293200
2039-07-23 18:01 | 4900.8 | 1.4742 | 81.6763 | 59.8258 | 1436.2827 |  | 6858 | 24688800 | 56224800 | 87760800 | 119296800
2039-07-24 19:01 | 3990.7 | 1.2238 | 81.349 | 59.8258 | 1169.5587 |  | 6859 | 24692400 | 56228400 | 87764400 | 119300400
2039-07-25 20:01 | 3331.85 | 1.0279 | 81.1891 | 59.8258 | 976.4688 |  | 6860 | 24696000 | 56232000 | 87768000 | 119304000
2039-07-26 21:01 | 3195.72 | 1 | 83.2014 | 59.8258 | 936.5731 |  | 6861 | 24699600 | 56235600 | 87771600 | 119307600
2039-07-27 22:01 | 3173.38 | 1 | 85.533 | 59.8258 | 930.0259 |  | 6862 | 24703200 | 56239200 | 87775200 | 119311200
2039-07-28 23:01 | 0 | 0 | 66.1788 | 59.8258 | 0 |  | 6863 | 24706800 | 56242800 | 87778800 | 119314800
2039-07-30 00:01 | -273.749 | 1.2089 | 64.7044 | 59.8258 | -80.2279 |  | 6864 | 24710400 | 56246400 | 87782400 | 119318400
2039-07-31 01:01 | -352.638 | 1.4052 | 64.3231 | 59.8258 | -103.348 |  | 6865 | 24714000 | 56250000 | 87786000 | 119322000
2039-08-01 02:01 | -478.169 | 1.7268 | 64.0521 | 59.8258 | -140.1375 |  | 6866 | 24717600 | 56253600 | 87789600 | 119325600
2039-08-02 03:01 | -478.926 | 1.705 | 63.8893 | 59.8258 | -140.3594 |  | 6867 | 24721200 | 56257200 | 87793200 | 119329200
2039-08-03 04:01 | -510.151 | 1.7938 | 63.7104 | 59.8258 | -149.5105 |  | 6868 | 24724800 | 56260800 | 87796800 | 119332800
2039-08-04 05:01 | -465.791 | 1.6686 | 63.651 | 59.8258 | -136.5099 |  | 6869 | 24728400 | 56264400 | 87800400 | 119336400
2039-08-05 06:01 | 1084.09 | 1 | 64.769 | 59.8258 | 317.7154 |  | 6870 | 24732000 | 56268000 | 87804000 | 119340000
2039-08-06 07:01 | 2679.91 | 1 | 64.7687 | 59.8258 | 785.4041 |  | 6871 | 24735600 | 56271600 | 87807600 | 119343600
2039-08-07 08:01 | 0 | 0 | 65.3 | 59.8258 | 0 |  | 6872 | 24739200 | 56275200 | 87811200 | 119347200
2039-08-08 09:01 | -177.223 | 0.94292 | 64.1947 | 59.8258 | -51.9389 |  | 6873 | 24742800 | 56278800 | 87814800 | 119350800
2039-08-09 10:01 | -30.7259 | 0.57575 | 64.8909 | 59.8258 | -9.0049 |  | 6874 | 24746400 | 56282400 | 87818400 | 119354400
2039-08-10 11:01 | 359.293 | 1 | 64.7886 | 59.8258 | 105.2984 |  | 6875 | 24750000 | 56286000 | 87822000 | 119358000
2039-08-11 12:01 | -31.8892 | 0.63526 | 64.5575 | 59.8258 | -9.3458 |  | 6876 | 24753600 | 56289600 | 87825600 | 119361600
2039-08-12 13:01 | -458.185 | 1.7442 | 63.4303 | 59.8258 | -134.2808 |  | 6877 | 24757200 | 56293200 | 87829200 | 119365200
2039-08-13 14:01 | -549.636 | 1.9085 | 63.1624 | 59.8258 | -161.0824 |  | 6878 | 24760800 | 56296800 | 87832800 | 119368800
2039-08-14 15:01 | -442.293 | 1.6057 | 63.0943 | 59.8258 | -129.6233 |  | 6879 | 24764400 | 56300400 | 87836400 | 119372400
2039-08-15 16:01 | 2536.78 | 1 | 64.0233 | 59.8258 | 743.4568 |  | 6880 | 24768000 | 56304000 | 87840000 | 119376000
2039-08-16 17:01 | 2925.56 | 1 | 64.2887 | 59.8258 | 857.397 |  | 6881 | 24771600 | 56307600 | 87843600 | 119379600
2039-08-17 18:01 | -42.4148 | 0.67324 | 64.4496 | 59.8258 | -12.4306 |  | 6882 | 24775200 | 56311200 | 87847200 | 119383200
2039-08-18 19:01 | -528.494 | 1.9363 | 63.1492 | 59.8258 | -154.8863 |  | 6883 | 24778800 | 56314800 | 87850800 | 119386800
2039-08-19 20:01 | -980.015 | 3.0716 | 62.7374 | 59.8258 | -287.214 |  | 6884 | 24782400 | 56318400 | 87854400 | 119390400
2039-08-20 21:01 | -1252.28 | 3.7249 | 62.5323 | 59.8258 | -367.007 |  | 6885 | 24786000 | 56322000 | 87858000 | 119394000
2039-08-21 22:01 | -1314.12 | 3.8452 | 62.3209 | 59.8258 | -385.1306 |  | 6886 | 24789600 | 56325600 | 87861600 | 119397600
2039-08-22 23:01 | -2405.2 | 6.108 | 61.9408 | 59.8258 | -704.8945 |  | 6887 | 24793200 | 56329200 | 87865200 | 119401200
2039-08-24 00:01 | -2895.95 | 6.108 | 61.3667 | 59.8258 | -848.7192 |  | 6888 | 24796800 | 56332800 | 87868800 | 119404800
2039-08-25 01:01 | -3267.41 | 6.108 | 60.8967 | 59.8258 | -957.5833 |  | 6889 | 24800400 | 56336400 | 87872400 | 119408400
2039-08-26 02:01 | -3184.1 | 6.108 | 60.7942 | 59.8258 | -933.1676 |  | 6890 | 24804000 | 56340000 | 87876000 | 119412000
2039-08-27 03:01 | -3136.43 | 6.108 | 60.7209 | 59.8258 | -919.1969 |  | 6891 | 24807600 | 56343600 | 87879600 | 119415600
2039-08-28 04:01 | -3244.19 | 6.108 | 60.5146 | 59.8258 | -950.7782 |  | 6892 | 24811200 | 56347200 | 87883200 | 119419200
2039-08-29 05:01 | -2679.55 | 6.108 | 60.8101 | 59.8258 | -785.2986 |  | 6893 | 24814800 | 56350800 | 87886800 | 119422800
2039-08-30 06:01 | -2886.06 | 6.108 | 60.6449 | 59.8258 | -845.8207 |  | 6894 | 24818400 | 56354400 | 87890400 | 119426400
2039-08-31 07:01 | -2059.4 | 5.8133 | 61.114 | 59.8258 | -603.5506 |  | 6895 | 24822000 | 56358000 | 87894000 | 119430000
2039-09-01 08:01 | -1641.72 | 4.621 | 61.166 | 59.8258 | -481.1406 |  | 6896 | 24825600 | 56361600 | 87897600 | 119433600
2039-09-02 09:01 | 0 | 0 | 62.8553 | 59.8258 | 0 |  | 6897 | 24829200 | 56365200 | 87901200 | 119437200
2039-09-03 10:01 | 2663.39 | 1 | 76.4696 | 59.8258 | 780.5626 |  | 6898 | 24832800 | 56368800 | 87904800 | 119440800
2039-09-04 11:01 | 4790.23 | 1.5578 | 77.6119 | 59.8258 | 1403.8778 |  | 6899 | 24836400 | 56372400 | 87908400 | 119444400
2039-09-05 12:01 | 5500.95 | 1.8498 | 77.7158 | 59.8258 | 1612.1693 |  | 6900 | 24840000 | 56376000 | 87912000 | 119448000
2039-09-06 13:01 | 5655.27 | 1.9394 | 77.8948 | 59.8258 | 1657.396 |  | 6901 | 24843600 | 56379600 | 87915600 | 119451600
2039-09-07 14:01 | 6176.88 | 2.118 | 78.2296 | 59.8258 | 1810.2648 |  | 6902 | 24847200 | 56383200 | 87919200 | 119455200
2039-09-08 15:01 | 6891.06 | 2.3626 | 78.562 | 59.8258 | 2019.5703 |  | 6903 | 24850800 | 56386800 | 87922800 | 119458800
2039-09-09 16:01 | 6013.6 | 2.0885 | 78.7072 | 59.8258 | 1762.4122 |  | 6904 | 24854400 | 56390400 | 87926400 | 119462400
2039-09-10 17:01 | 4379.89 | 1.4968 | 79.012 | 59.8258 | 1283.619 |  | 6905 | 24858000 | 56394000 | 87930000 | 119466000
2039-09-11 18:01 | 2933.85 | 1 | 83.7945 | 59.8258 | 859.8266 |  | 6906 | 24861600 | 56397600 | 87933600 | 119469600
2039-09-12 19:01 | 2792.72 | 1 | 65.1055 | 59.8258 | 818.4654 |  | 6907 | 24865200 | 56401200 | 87937200 | 119473200
2039-09-13 20:01 | -805.976 | 2.6899 | 63.9198 | 59.8258 | -236.2082 |  | 6908 | 24868800 | 56404800 | 87940800 | 119476800
2039-09-14 21:01 | -1273.05 | 3.7855 | 63.2141 | 59.8258 | -373.0941 |  | 6909 | 24872400 | 56408400 | 87944400 | 119480400
2039-09-15 22:01 | -2203.92 | 6.108 | 62.7096 | 59.8258 | -645.9052 |  | 6910 | 24876000 | 56412000 | 87948000 | 119484000
2039-09-16 23:01 | -2763.43 | 6.108 | 61.9493 | 59.8258 | -809.8814 |  | 6911 | 24879600 | 56415600 | 87951600 | 119487600
2039-09-18 00:01 | -3117.39 | 6.108 | 61.3648 | 59.8258 | -913.6168 |  | 6912 | 24883200 | 56419200 | 87955200 | 119491200
2039-09-19 01:01 | -3299.01 | 6.108 | 60.9288 | 59.8258 | -966.8444 |  | 6913 | 24886800 | 56422800 | 87958800 | 119494800
2039-09-20 02:01 | -3431.51 | 6.108 | 60.6207 | 59.8258 | -1005.6763 |  | 6914 | 24890400 | 56426400 | 87962400 | 119498400
2039-09-21 03:01 | -3316.02 | 6.108 | 60.505 | 59.8258 | -971.8295 |  | 6915 | 24894000 | 56430000 | 87966000 | 119502000
2039-09-22 04:01 | -3325.29 | 6.108 | 60.3577 | 59.8258 | -974.5463 |  | 6916 | 24897600 | 56433600 | 87969600 | 119505600
2039-09-23 05:01 | -3088.44 | 6.108 | 60.4187 | 59.8258 | -905.1324 |  | 6917 | 24901200 | 56437200 | 87973200 | 119509200
2039-09-24 06:01 | -3158.9 | 6.108 | 60.2999 | 59.8258 | -925.7822 |  | 6918 | 24904800 | 56440800 | 87976800 | 119512800
2039-09-25 07:01 | -2548.23 | 6.108 | 60.6623 | 59.8258 | -746.8125 |  | 6919 | 24908400 | 56444400 | 87980400 | 119516400
2039-09-26 08:01 | -1646.22 | 4.6334 | 60.9768 | 59.8258 | -482.4595 |  | 6920 | 24912000 | 56448000 | 87984000 | 119520000
2039-09-27 09:01 | 0 | 0 | 62.7147 | 59.8258 | 0 |  | 6921 | 24915600 | 56451600 | 87987600 | 119523600
2039-09-28 10:01 | 2722.97 | 1 | 78.1059 | 59.8258 | 798.0237 |  | 6922 | 24919200 | 56455200 | 87991200 | 119527200
2039-09-29 11:01 | 4877.75 | 1.5569 | 77.7572 | 59.8258 | 1429.5274 |  | 6923 | 24922800 | 56458800 | 87994800 | 119530800
2039-09-30 12:01 | 6514.43 | 2.1071 | 78.1272 | 59.8258 | 1909.191 |  | 6924 | 24926400 | 56462400 | 87998400 | 119534400
2039-10-01 13:01 | 7321.47 | 2.3872 | 78.5707 | 59.8258 | 2145.711 |  | 6925 | 24930000 | 56466000 | 88002000 | 119538000
2039-10-02 14:01 | 8025.94 | 2.5902 | 79.1912 | 59.8258 | 2352.1708 |  | 6926 | 24933600 | 56469600 | 88005600 | 119541600
2039-10-03 15:01 | 9135.33 | 2.9707 | 79.5066 | 59.8258 | 2677.3009 |  | 6927 | 24937200 | 56473200 | 88009200 | 119545200
2039-10-04 16:01 | 8539.75 | 2.7627 | 80.0278 | 59.8258 | 2502.7537 |  | 6928 | 24940800 | 56476800 | 88012800 | 119548800
2039-10-05 17:01 | 6703.11 | 2.1506 | 80.392 | 59.8258 | 1964.4876 |  | 6929 | 24944400 | 56480400 | 88016400 | 119552400
2039-10-06 18:01 | 3982.16 | 1.28 | 80.3471 | 59.8258 | 1167.0559 |  | 6930 | 24948000 | 56484000 | 88020000 | 119556000
2039-10-07 19:01 | 3068.96 | 1 | 90.5978 | 59.8258 | 899.4234 |  | 6931 | 24951600 | 56487600 | 88023600 | 119559600
2039-10-08 20:01 | 0 | 0 | 65.6358 | 59.8258 | 0 |  | 6932 | 24955200 | 56491200 | 88027200 | 119563200
2039-10-09 21:01 | -554.469 | 1.9708 | 63.8284 | 59.8258 | -162.4988 |  | 6933 | 24958800 | 56494800 | 88030800 | 119566800
2039-10-10 22:01 | -1936.81 | 5.6612 | 63.1577 | 59.8258 | -567.623 |  | 6934 | 24962400 | 56498400 | 88034400 | 119570400
2039-10-11 23:01 | -2494.28 | 6.108 | 62.4362 | 59.8258 | -731.0013 |  | 6935 | 24966000 | 56502000 | 88038000 | 119574000
2039-10-13 00:01 | -3201.76 | 6.108 | 61.5571 | 59.8258 | -938.3432 |  | 6936 | 24969600 | 56505600 | 88041600 | 119577600
2039-10-14 01:01 | -3619.16 | 6.108 | 60.8912 | 59.8258 | -1060.6711 |  | 6937 | 24973200 | 56509200 | 88045200 | 119581200
2039-10-15 02:01 | -3888.05 | 6.108 | 60.4016 | 59.8258 | -1139.475 |  | 6938 | 24976800 | 56512800 | 88048800 | 119584800
2039-10-16 03:01 | -4182.12 | 6.108 | 59.9044 | 59.8258 | -1225.6584 |  | 6939 | 24980400 | 56516400 | 88052400 | 119588400
2039-10-17 04:01 | -4117.37 | 6.108 | 59.7037 | 59.8258 | -1206.682 |  | 6940 | 24984000 | 56520000 | 88056000 | 119592000
2039-10-18 05:01 | -3758.57 | 6.108 | 59.7884 | 59.8258 | -1101.5281 |  | 6941 | 24987600 | 56523600 | 88059600 | 119595600
2039-10-19 06:01 | -3608.91 | 6.108 | 59.8195 | 59.8258 | -1057.6671 |  | 6942 | 24991200 | 56527200 | 88063200 | 119599200
2039-10-20 07:01 | -3078.45 | 6.108 | 60.143 | 59.8258 | -902.2046 |  | 6943 | 24994800 | 56530800 | 88066800 | 119602800
2039-10-21 08:01 | -2551 | 6.108 | 60.5532 | 59.8258 | -747.6243 |  | 6944 | 24998400 | 56534400 | 88070400 | 119606400
2039-10-22 09:01 | -1064.2 | 2.9968 | 60.8781 | 59.8258 | -311.8862 |  | 6945 | 25002000 | 56538000 | 88074000 | 119610000
2039-10-23 10:01 | 2783.49 | 1 | 62.4433 | 59.8258 | 815.7604 |  | 6946 | 25005600 | 56541600 | 88077600 | 119613600
2039-10-24 11:01 | 4608.19 | 1.4347 | 77.9907 | 59.8258 | 1350.5272 |  | 6947 | 25009200 | 56545200 | 88081200 | 119617200
2039-10-25 12:01 | 6190.52 | 2.0295 | 77.7573 | 59.8258 | 1814.2623 |  | 6948 | 25012800 | 56548800 | 88084800 | 119620800
2039-10-26 13:01 | 7626.92 | 2.4209 | 78.7336 | 59.8258 | 2235.2296 |  | 6949 | 25016400 | 56552400 | 88088400 | 119624400
2039-10-27 14:01 | 8297.83 | 2.6614 | 79.1304 | 59.8258 | 2431.8539 |  | 6950 | 25020000 | 56556000 | 88092000 | 119628000
2039-10-28 15:01 | 9212.07 | 2.964 | 79.5488 | 59.8258 | 2699.7912 |  | 6951 | 25023600 | 56559600 | 88095600 | 119631600
2039-10-29 16:01 | 8324.59 | 2.6616 | 80.0619 | 59.8258 | 2439.6965 |  | 6952 | 25027200 | 56563200 | 88099200 | 119635200
2039-10-30 17:01 | 6404.36 | 1.9981 | 80.6192 | 59.8258 | 1876.9326 |  | 6953 | 25030800 | 56566800 | 88102800 | 119638800
2039-10-31 18:01 | 4478.16 | 1.3896 | 80.6441 | 59.8258 | 1312.4191 |  | 6954 | 25034400 | 56570400 | 88106400 | 119642400
2039-11-01 19:01 | 3134.37 | 1 | 81.7659 | 59.8258 | 918.5932 |  | 6955 | 25038000 | 56574000 | 88110000 | 119646000
2039-11-02 20:01 | 2442.07 | 1 | 65.2763 | 59.8258 | 715.7001 |  | 6956 | 25041600 | 56577600 | 88113600 | 119649600
2039-11-03 21:01 | -372.295 | 1.55 | 64.201 | 59.8258 | -109.1089 |  | 6957 | 25045200 | 56581200 | 88117200 | 119653200
2039-11-04 22:01 | -1465.02 | 4.3984 | 63.2702 | 59.8258 | -429.355 |  | 6958 | 25048800 | 56584800 | 88120800 | 119656800
2039-11-05 23:01 | -1841.89 | 5.2156 | 62.7379 | 59.8258 | -539.8047 |  | 6959 | 25052400 | 56588400 | 88124400 | 119660400
2039-11-07 00:01 | -2449.05 | 6.108 | 62.2199 | 59.8258 | -717.7457 |  | 6960 | 25056000 | 56592000 | 88128000 | 119664000
2039-11-08 01:01 | -3023.79 | 6.108 | 61.4826 | 59.8258 | -886.1854 |  | 6961 | 25059600 | 56595600 | 88131600 | 119667600
2039-11-09 02:01 | -3316.6 | 6.108 | 60.9351 | 59.8258 | -971.9995 |  | 6962 | 25063200 | 56599200 | 88135200 | 119671200
2039-11-10 03:01 | -3226.21 | 6.108 | 60.7427 | 59.8258 | -945.5088 |  | 6963 | 25066800 | 56602800 | 88138800 | 119674800
2039-11-11 04:01 | -3164.68 | 6.108 | 60.6127 | 59.8258 | -927.4762 |  | 6964 | 25070400 | 56606400 | 88142400 | 119678400
2039-11-12 05:01 | -2615.27 | 6.108 | 60.8879 | 59.8258 | -766.46 |  | 6965 | 25074000 | 56610000 | 88146000 | 119682000
2039-11-13 06:01 | -3018.9 | 6.108 | 60.5524 | 59.8258 | -884.7523 |  | 6966 | 25077600 | 56613600 | 88149600 | 119685600
2039-11-14 07:01 | -2648.99 | 6.108 | 60.7263 | 59.8258 | -776.3423 |  | 6967 | 25081200 | 56617200 | 88153200 | 119689200
2039-11-15 08:01 | -1857.24 | 5.2311 | 61.0481 | 59.8258 | -544.3033 |  | 6968 | 25084800 | 56620800 | 88156800 | 119692800
2039-11-16 09:01 | 0 | 1 | 62.75 | 59.8258 | 0 |  | 6969 | 25088400 | 56624400 | 88160400 | 119696400
2039-11-17 10:01 | 3220.51 | 1 | 80.7866 | 59.8258 | 943.8383 |  | 6970 | 25092000 | 56628000 | 88164000 | 119700000
2039-11-18 11:01 | 6045.7 | 1.9025 | 78.0353 | 59.8258 | 1771.8198 |  | 6971 | 25095600 | 56631600 | 88167600 | 119703600
2039-11-19 12:01 | 7688.19 | 2.4644 | 78.4422 | 59.8258 | 2253.1861 |  | 6972 | 25099200 | 56635200 | 88171200 | 119707200
2039-11-20 13:01 | 8454.39 | 2.7188 | 79.0061 | 59.8258 | 2477.7371 |  | 6973 | 25102800 | 56638800 | 88174800 | 119710800
2039-11-21 14:01 | 9006.36 | 2.8912 | 79.5349 | 59.8258 | 2639.5036 |  | 6974 | 25106400 | 56642400 | 88178400 | 119714400
2039-11-22 15:01 | 10124.3 | 3.2557 | 79.9346 | 59.8258 | 2967.1394 |  | 6975 | 25110000 | 56646000 | 88182000 | 119718000
2039-11-23 16:01 | 9301.29 | 2.9599 | 80.5406 | 59.8258 | 2725.939 |  | 6976 | 25113600 | 56649600 | 88185600 | 119721600
2039-11-24 17:01 | 7264.69 | 2.2837 | 80.9319 | 59.8258 | 2129.0705 |  | 6977 | 25117200 | 56653200 | 88189200 | 119725200
2039-11-25 18:01 | 5311.13 | 1.6639 | 80.9183 | 59.8258 | 1556.5386 |  | 6978 | 25120800 | 56656800 | 88192800 | 119728800
2039-11-26 19:01 | 3199.87 | 1 | 81.2576 | 59.8258 | 937.7893 |  | 6979 | 25124400 | 56660400 | 88196400 | 119732400
2039-11-27 20:01 | 3164.65 | 1 | 65.5382 | 59.8258 | 927.4674 |  | 6980 | 25128000 | 56664000 | 88200000 | 119736000
2039-11-28 21:01 | 0 | 0 | 65.6663 | 59.8258 | 0 |  | 6981 | 25131600 | 56667600 | 88203600 | 119739600
2039-11-29 22:01 | -999.48 | 3.0877 | 63.6592 | 59.8258 | -292.9187 |  | 6982 | 25135200 | 56671200 | 88207200 | 119743200
2039-11-30 23:01 | -1558.86 | 4.5345 | 63.108 | 59.8258 | -456.8568 |  | 6983 | 25138800 | 56674800 | 88210800 | 119746800
2039-12-02 00:01 | -2091.28 | 5.893 | 62.7196 | 59.8258 | -612.8937 |  | 6984 | 25142400 | 56678400 | 88214400 | 119750400
2039-12-03 01:01 | -2359.64 | 6.108 | 62.2747 | 59.8258 | -691.5422 |  | 6985 | 25146000 | 56682000 | 88218000 | 119754000
2039-12-04 02:01 | -2433.95 | 6.108 | 61.927 | 59.8258 | -713.3203 |  | 6986 | 25149600 | 56685600 | 88221600 | 119757600
2039-12-05 03:01 | -2357.58 | 6.108 | 61.7753 | 59.8258 | -690.9385 |  | 6987 | 25153200 | 56689200 | 88225200 | 119761200
2039-12-06 04:01 | -2710.63 | 6.108 | 61.3586 | 59.8258 | -794.4072 |  | 6988 | 25156800 | 56692800 | 88228800 | 119764800
2039-12-07 05:01 | -2173.21 | 6.0893 | 61.5828 | 59.8258 | -636.905 |  | 6989 | 25160400 | 56696400 | 88232400 | 119768400
2039-12-08 06:01 | -2439.82 | 6.108 | 61.3441 | 59.8258 | -715.0407 |  | 6990 | 25164000 | 56700000 | 88236000 | 119772000
2039-12-09 07:01 | -1871.25 | 5.2322 | 61.4588 | 59.8258 | -548.4092 |  | 6991 | 25167600 | 56703600 | 88239600 | 119775600
2039-12-10 08:01 | -1464.79 | 4.1638 | 61.4787 | 59.8258 | -429.2876 |  | 6992 | 25171200 | 56707200 | 88243200 | 119779200
2039-12-11 09:01 | 0 | 1 | 63.1301 | 59.8258 | 0 |  | 6993 | 25174800 | 56710800 | 88246800 | 119782800
2039-12-12 10:01 | 3835.57 | 1.18 | 78.2051 | 59.8258 | 1124.0946 |  | 6994 | 25178400 | 56714400 | 88250400 | 119786400
2039-12-13 11:01 | 6835.5 | 2.2096 | 78.0059 | 59.8258 | 2003.2873 |  | 6995 | 25182000 | 56718000 | 88254000 | 119790000
2039-12-14 12:01 | 8627.23 | 2.8267 | 78.5242 | 59.8258 | 2528.3915 |  | 6996 | 25185600 | 56721600 | 88257600 | 119793600
2039-12-15 13:01 | 9400.04 | 3.0233 | 79.42 | 59.8258 | 2754.8798 |  | 6997 | 25189200 | 56725200 | 88261200 | 119797200
2039-12-16 14:01 | 10053.7 | 3.2255 | 79.9753 | 59.8258 | 2946.4486 |  | 6998 | 25192800 | 56728800 | 88264800 | 119800800
2039-12-17 15:01 | 10771.4 | 3.4798 | 80.3356 | 59.8258 | 3156.7857 |  | 6999 | 25196400 | 56732400 | 88268400 | 119804400
2039-12-18 16:01 | 9807.34 | 3.1158 | 81.0004 | 59.8258 | 2874.2476 |  | 7000 | 25200000 | 56736000 | 88272000 | 119808000
2039-12-19 17:01 | 8100.75 | 2.5482 | 81.3243 | 59.8258 | 2374.0955 |  | 7001 | 25203600 | 56739600 | 88275600 | 119811600
2039-12-20 18:01 | 6181.15 | 1.9069 | 81.5713 | 59.8258 | 1811.5162 |  | 7002 | 25207200 | 56743200 | 88279200 | 119815200
2039-12-21 19:01 | 4448.66 | 1.3451 | 81.6941 | 59.8258 | 1303.7735 |  | 7003 | 25210800 | 56746800 | 88282800 | 119818800
2039-12-22 20:01 | 3148.97 | 1 | 66.0437 | 59.8258 | 922.872 |  | 7004 | 25214400 | 56750400 | 88286400 | 119822400
2039-12-23 21:01 | 3038.34 | 1 | 65.7778 | 59.8258 | 890.4496 |  | 7005 | 25218000 | 56754000 | 88290000 | 119826000
2039-12-24 22:01 | -595.389 | 2.1143 | 64.5878 | 59.8258 | -174.4913 |  | 7006 | 25221600 | 56757600 | 88293600 | 119829600
2039-12-25 23:01 | -1278.97 | 3.8265 | 63.7393 | 59.8258 | -374.8291 |  | 7007 | 25225200 | 56761200 | 88297200 | 119833200
2039-12-27 00:01 | -1659.57 | 4.738 | 63.2036 | 59.8258 | -486.372 |  | 7008 | 25228800 | 56764800 | 88300800 | 119836800
2039-12-28 01:01 | -1835.82 | 5.1588 | 62.862 | 59.8258 | -538.0257 |  | 7009 | 25232400 | 56768400 | 88304400 | 119840400
2039-12-29 02:01 | -2112.32 | 5.9033 | 62.5826 | 59.8258 | -619.0599 |  | 7010 | 25236000 | 56772000 | 88308000 | 119844000
2039-12-30 03:01 | -2366.24 | 6.108 | 62.1541 | 59.8258 | -693.4765 |  | 7011 | 25239600 | 56775600 | 88311600 | 119847600
2039-12-31 04:01 | -2401.85 | 6.108 | 61.9164 | 59.8258 | -703.9127 |  | 7012 | 25243200 | 56779200 | 88315200 | 119851200
2040-01-01 05:01 | -2728.24 | 6.108 | 61.5101 | 59.8258 | -799.5682 |  | 7013 | 25246800 | 56782800 | 88318800 | 119854800
2040-01-02 06:01 | -2052.7 | 5.7371 | 61.7522 | 59.8258 | -601.587 |  | 7014 | 25250400 | 56786400 | 88322400 | 119858400
2040-01-03 07:01 | -1664.76 | 4.6605 | 61.7207 | 59.8258 | -487.893 |  | 7015 | 25254000 | 56790000 | 88326000 | 119862000
2040-01-04 08:01 | -2049.09 | 5.835 | 61.7589 | 59.8258 | -600.529 |  | 7016 | 25257600 | 56793600 | 88329600 | 119865600
2040-01-05 09:01 | -1214.72 | 3.4031 | 61.6278 | 59.8258 | -355.9993 |  | 7017 | 25261200 | 56797200 | 88333200 | 119869200
2040-01-06 10:01 | -1134.38 | 3.403 | 61.7619 | 59.8258 | -332.454 |  | 7018 | 25264800 | 56800800 | 88336800 | 119872800
2040-01-07 11:01 | -1384.18 | 4.0979 | 61.7306 | 59.8258 | -405.6631 |  | 7019 | 25268400 | 56804400 | 88340400 | 119876400
2040-01-08 12:01 | -1344.11 | 3.9285 | 61.6004 | 59.8258 | -393.9198 |  | 7020 | 25272000 | 56808000 | 88344000 | 119880000
2040-01-09 13:01 | -904.969 | 2.7267 | 61.5374 | 59.8258 | -265.2202 |  | 7021 | 25275600 | 56811600 | 88347600 | 119883600
2040-01-10 14:01 | -655.28 | 2.1451 | 61.6209 | 59.8258 | -192.0436 |  | 7022 | 25279200 | 56815200 | 88351200 | 119887200
2040-01-11 15:01 | 2462.49 | 1 | 62.7464 | 59.8258 | 721.6846 |  | 7023 | 25282800 | 56818800 | 88354800 | 119890800
2040-01-12 16:01 | 2995.69 | 1 | 79.6449 | 59.8258 | 877.9501 |  | 7024 | 25286400 | 56822400 | 88358400 | 119894400
2040-01-13 17:01 | 2805.39 | 1 | 63.3228 | 59.8258 | 822.1786 |  | 7025 | 25290000 | 56826000 | 88362000 | 119898000
2040-01-14 18:01 | -212.333 | 1.1287 | 62.8331 | 59.8258 | -62.2287 |  | 7026 | 25293600 | 56829600 | 88365600 | 119901600
2040-01-15 19:01 | -587.701 | 2.0867 | 62.1047 | 59.8258 | -172.2382 |  | 7027 | 25297200 | 56833200 | 88369200 | 119905200
2040-01-16 20:01 | -1444.91 | 4.3845 | 61.7279 | 59.8258 | -423.4613 |  | 7028 | 25300800 | 56836800 | 88372800 | 119908800
2040-01-17 21:01 | -1991.22 | 5.7239 | 61.4247 | 59.8258 | -583.569 |  | 7029 | 25304400 | 56840400 | 88376400 | 119912400
2040-01-18 22:01 | -2459.77 | 6.108 | 60.9547 | 59.8258 | -720.8874 |  | 7030 | 25308000 | 56844000 | 88380000 | 119916000
2040-01-19 23:01 | -4306.03 | 6.108 | 59.3664 | 59.8258 | -1261.9728 |  | 7031 | 25311600 | 56847600 | 88383600 | 119919600
2040-01-21 00:01 | -4754.33 | 6.108 | 58.6877 | 59.8258 | -1393.3566 |  | 7032 | 25315200 | 56851200 | 88387200 | 119923200
2040-01-22 01:01 | -5065.23 | 6.108 | 58.1785 | 59.8258 | -1484.4724 |  | 7033 | 25318800 | 56854800 | 88390800 | 119926800
2040-01-23 02:01 | -5292.8 | 6.108 | 57.7972 | 59.8258 | -1551.1666 |  | 7034 | 25322400 | 56858400 | 88394400 | 119930400
2040-01-24 03:01 | -5294 | 6.108 | 57.5661 | 59.8258 | -1551.5182 |  | 7035 | 25326000 | 56862000 | 88398000 | 119934000
2040-01-25 04:01 | -5550.74 | 6.108 | 57.1724 | 59.8258 | -1626.7613 |  | 7036 | 25329600 | 56865600 | 88401600 | 119937600
2040-01-26 05:01 | -5677.52 | 6.108 | 56.8924 | 59.8258 | -1663.9169 |  | 7037 | 25333200 | 56869200 | 88405200 | 119941200
2040-01-27 06:01 | -5032.65 | 6.108 | 57.2282 | 59.8258 | -1474.9241 |  | 7038 | 25336800 | 56872800 | 88408800 | 119944800
2040-01-28 07:01 | -4275.47 | 6.108 | 57.7584 | 59.8258 | -1253.0166 |  | 7039 | 25340400 | 56876400 | 88412400 | 119948400
2040-01-29 08:01 | -3902.36 | 6.108 | 58.0889 | 59.8258 | -1143.6688 |  | 7040 | 25344000 | 56880000 | 88416000 | 119952000
2040-01-30 09:01 | -3446.26 | 6.108 | 58.4599 | 59.8258 | -1009.9991 |  | 7041 | 25347600 | 56883600 | 88419600 | 119955600
2040-01-31 10:01 | -2402.6 | 6.108 | 59.2785 | 59.8258 | -704.1326 |  | 7042 | 25351200 | 56887200 | 88423200 | 119959200
2040-02-01 11:01 | -1578.87 | 4.5159 | 59.6314 | 59.8258 | -462.7211 |  | 7043 | 25354800 | 56890800 | 88426800 | 119962800
2040-02-02 12:01 | -1803.5 | 5.2893 | 59.8478 | 59.8258 | -528.5537 |  | 7044 | 25358400 | 56894400 | 88430400 | 119966400
2040-02-03 13:01 | -1508.68 | 4.3699 | 59.8681 | 59.8258 | -442.1505 |  | 7045 | 25362000 | 56898000 | 88434000 | 119970000
2040-02-04 14:01 | -1211.79 | 3.6078 | 59.9647 | 59.8258 | -355.1406 |  | 7046 | 25365600 | 56901600 | 88437600 | 119973600
2040-02-05 15:01 | 0 | 1 | 61.5568 | 59.8258 | 0 |  | 7047 | 25369200 | 56905200 | 88441200 | 119977200
2040-02-06 16:01 | 2933.23 | 1 | 61.4666 | 59.8258 | 859.6449 |  | 7048 | 25372800 | 56908800 | 88444800 | 119980800
2040-02-07 17:01 | 0 | 0 | 62.2127 | 59.8258 | 0 |  | 7049 | 25376400 | 56912400 | 88448400 | 119984400
2040-02-08 18:01 | -742.948 | 2.3838 | 60.684 | 59.8258 | -217.7366 |  | 7050 | 25380000 | 56916000 | 88452000 | 119988000
2040-02-09 19:01 | -1326 | 4.0915 | 60.4885 | 59.8258 | -388.6122 |  | 7051 | 25383600 | 56919600 | 88455600 | 119991600
2040-02-10 20:01 | -1804.43 | 5.2997 | 60.3378 | 59.8258 | -528.8262 |  | 7052 | 25387200 | 56923200 | 88459200 | 119995200
2040-02-11 21:01 | -2147.24 | 6.108 | 60.1792 | 59.8258 | -629.2939 |  | 7053 | 25390800 | 56926800 | 88462800 | 119998800
2040-02-12 22:01 | -2731.32 | 6.108 | 59.5708 | 59.8258 | -800.4709 |  | 7054 | 25394400 | 56930400 | 88466400 | 120002400
2040-02-13 23:01 | -3909.1 | 6.108 | 58.5475 | 59.8258 | -1145.6441 |  | 7055 | 25398000 | 56934000 | 88470000 | 120006000
2040-02-15 00:01 | -4135.61 | 6.108 | 58.1432 | 59.8258 | -1212.0276 |  | 7056 | 25401600 | 56937600 | 88473600 | 120009600
2040-02-16 01:01 | -4451.8 | 6.108 | 57.7417 | 59.8258 | -1304.6938 |  | 7057 | 25405200 | 56941200 | 88477200 | 120013200
2040-02-17 02:01 | -4503.4 | 6.108 | 57.5584 | 59.8258 | -1319.8163 |  | 7058 | 25408800 | 56944800 | 88480800 | 120016800
2040-02-18 03:01 | -4559.16 | 6.108 | 57.3856 | 59.8258 | -1336.1579 |  | 7059 | 25412400 | 56948400 | 88484400 | 120020400
2040-02-19 04:01 | -4455.14 | 6.108 | 57.3199 | 59.8258 | -1305.6726 |  | 7060 | 25416000 | 56952000 | 88488000 | 120024000
2040-02-20 05:01 | -4192.75 | 6.108 | 57.4533 | 59.8258 | -1228.7737 |  | 7061 | 25419600 | 56955600 | 88491600 | 120027600
2040-02-21 06:01 | -4775.36 | 6.108 | 56.9935 | 59.8258 | -1399.5199 |  | 7062 | 25423200 | 56959200 | 88495200 | 120031200
2040-02-22 07:01 | -3555.62 | 6.108 | 57.7897 | 59.8258 | -1042.0494 |  | 7063 | 25426800 | 56962800 | 88498800 | 120034800
2040-02-23 08:01 | -2792.77 | 6.108 | 58.4419 | 59.8258 | -818.4801 |  | 7064 | 25430400 | 56966400 | 88502400 | 120038400
2040-02-24 09:01 | -837.003 | 2.4175 | 59.0762 | 59.8258 | -245.3014 |  | 7065 | 25434000 | 56970000 | 88506000 | 120042000
2040-02-25 10:01 | 2718.56 | 1 | 60.7305 | 59.8258 | 796.7313 |  | 7066 | 25437600 | 56973600 | 88509600 | 120045600
2040-02-26 11:01 | 4515.96 | 1.4133 | 76.2696 | 59.8258 | 1323.4972 |  | 7067 | 25441200 | 56977200 | 88513200 | 120049200
2040-02-27 12:01 | 6081.86 | 1.9812 | 76.287 | 59.8258 | 1782.4172 |  | 7068 | 25444800 | 56980800 | 88516800 | 120052800
2040-02-28 13:01 | 7500.69 | 2.3893 | 77.2049 | 59.8258 | 2198.2352 |  | 7069 | 25448400 | 56984400 | 88520400 | 120056400
2040-02-29 14:01 | 8351.43 | 2.6878 | 77.6813 | 59.8258 | 2447.5625 |  | 7070 | 25452000 | 56988000 | 88524000 | 120060000
2040-03-01 15:01 | 9469.74 | 3.0717 | 78.1144 | 59.8258 | 2775.3068 |  | 7071 | 25455600 | 56991600 | 88527600 | 120063600
2040-03-02 16:01 | 8768.26 | 2.8198 | 78.7421 | 59.8258 | 2569.7233 |  | 7072 | 25459200 | 56995200 | 88531200 | 120067200
2040-03-03 17:01 | 6596.87 | 2.1085 | 79.1304 | 59.8258 | 1933.3517 |  | 7073 | 25462800 | 56998800 | 88534800 | 120070800
2040-03-04 18:01 | 4022.43 | 1.2774 | 79.2204 | 59.8258 | 1178.8579 |  | 7074 | 25466400 | 57002400 | 88538400 | 120074400
2040-03-05 19:01 | 3106.94 | 1 | 83.8913 | 59.8258 | 910.5542 |  | 7075 | 25470000 | 57006000 | 88542000 | 120078000
2040-03-06 20:01 | 0 | 0 | 64.3995 | 59.8258 | 0 |  | 7076 | 25473600 | 57009600 | 88545600 | 120081600
2040-03-07 21:01 | -726.932 | 2.3499 | 62.476 | 59.8258 | -213.0427 |  | 7077 | 25477200 | 57013200 | 88549200 | 120085200
2040-03-08 22:01 | -1986.19 | 5.8562 | 61.9291 | 59.8258 | -582.0948 |  | 7078 | 25480800 | 57016800 | 88552800 | 120088800
2040-03-09 23:01 | -2555.62 | 6.108 | 61.1719 | 59.8258 | -748.9783 |  | 7079 | 25484400 | 57020400 | 88556400 | 120092400
2040-03-11 00:01 | -3319.16 | 6.108 | 60.2689 | 59.8258 | -972.7498 |  | 7080 | 25488000 | 57024000 | 88560000 | 120096000
2040-03-12 01:01 | -3351.79 | 6.108 | 59.8915 | 59.8258 | -982.3127 |  | 7081 | 25491600 | 57027600 | 88563600 | 120099600
2040-03-13 02:01 | -3642.18 | 6.108 | 59.4427 | 59.8258 | -1067.4176 |  | 7082 | 25495200 | 57031200 | 88567200 | 120103200
2040-03-14 03:01 | -4026.59 | 6.108 | 58.9157 | 59.8258 | -1180.077 |  | 7083 | 25498800 | 57034800 | 88570800 | 120106800
2040-03-15 04:01 | -3680.05 | 6.108 | 58.9381 | 59.8258 | -1078.5162 |  | 7084 | 25502400 | 57038400 | 88574400 | 120110400
2040-03-16 05:01 | -3223.01 | 6.108 | 59.1584 | 59.8258 | -944.571 |  | 7085 | 25506000 | 57042000 | 88578000 | 120114000
2040-03-17 06:01 | -3455.22 | 6.108 | 58.9678 | 59.8258 | -1012.625 |  | 7086 | 25509600 | 57045600 | 88581600 | 120117600
2040-03-18 07:01 | -2777.32 | 6.108 | 59.3883 | 59.8258 | -813.9521 |  | 7087 | 25513200 | 57049200 | 88585200 | 120121200
2040-03-19 08:01 | -1707.66 | 4.8862 | 59.9067 | 59.8258 | -500.4657 |  | 7088 | 25516800 | 57052800 | 88588800 | 120124800
2040-03-20 09:01 | 0 | 1 | 61.6603 | 59.8258 | 0 |  | 7089 | 25520400 | 57056400 | 88592400 | 120128400
2040-03-21 10:01 | 3486.06 | 1.0668 | 76.9189 | 59.8258 | 1021.6633 |  | 7090 | 25524000 | 57060000 | 88596000 | 120132000
2040-03-22 11:01 | 6007.05 | 1.9377 | 76.6933 | 59.8258 | 1760.4926 |  | 7091 | 25527600 | 57063600 | 88599600 | 120135600
2040-03-23 12:01 | 7421.82 | 2.3998 | 77.3426 | 59.8258 | 2175.1207 |  | 7092 | 25531200 | 57067200 | 88603200 | 120139200
2040-03-24 13:01 | 8482.92 | 2.7068 | 78.1202 | 59.8258 | 2486.0984 |  | 7093 | 25534800 | 57070800 | 88606800 | 120142800
2040-03-25 14:01 | 8940.82 | 2.9147 | 78.3577 | 59.8258 | 2620.2957 |  | 7094 | 25538400 | 57074400 | 88610400 | 120146400
2040-03-26 15:01 | 10178.2 | 3.2394 | 79.1443 | 59.8258 | 2982.936 |  | 7095 | 25542000 | 57078000 | 88614000 | 120150000
2040-03-27 16:01 | 9339.34 | 2.9888 | 79.5395 | 59.8258 | 2737.0904 |  | 7096 | 25545600 | 57081600 | 88617600 | 120153600
2040-03-28 17:01 | 7295.83 | 2.2699 | 80.191 | 59.8258 | 2138.1967 |  | 7097 | 25549200 | 57085200 | 88621200 | 120157200
2040-03-29 18:01 | 4655.28 | 1.4864 | 79.7771 | 59.8258 | 1364.3279 |  | 7098 | 25552800 | 57088800 | 88624800 | 120160800
2040-03-30 19:01 | 3117.33 | 1 | 80.1163 | 59.8258 | 913.5992 |  | 7099 | 25556400 | 57092400 | 88628400 | 120164400
2040-03-31 20:01 | 3019.18 | 1 | 64.6398 | 59.8258 | 884.8343 |  | 7100 | 25560000 | 57096000 | 88632000 | 120168000
2040-04-01 21:01 | 3087.6 | 1 | 64.488 | 59.8258 | 904.8862 |  | 7101 | 25563600 | 57099600 | 88635600 | 120171600
2040-04-02 22:01 | -451.858 | 1.7712 | 63.5065 | 59.8258 | -132.4265 |  | 7102 | 25567200 | 57103200 | 88639200 | 120175200
2040-04-03 23:01 | -761.849 | 2.4923 | 62.7282 | 59.8258 | -223.2759 |  | 7103 | 25570800 | 57106800 | 88642800 | 120178800
2040-04-05 00:01 | -910.787 | 2.8483 | 62.3238 | 59.8258 | -266.9253 |  | 7104 | 25574400 | 57110400 | 88646400 | 120182400
2040-04-06 01:01 | -1430.19 | 4.2591 | 62.056 | 59.8258 | -419.1473 |  | 7105 | 25578000 | 57114000 | 88650000 | 120186000
2040-04-07 02:01 | -1595.49 | 4.6054 | 61.7586 | 59.8258 | -467.592 |  | 7106 | 25581600 | 57117600 | 88653600 | 120189600
2040-04-08 03:01 | -1625.09 | 4.6705 | 61.5018 | 59.8258 | -476.2669 |  | 7107 | 25585200 | 57121200 | 88657200 | 120193200
2040-04-09 04:01 | -1593.9 | 4.5849 | 61.3644 | 59.8258 | -467.126 |  | 7108 | 25588800 | 57124800 | 88660800 | 120196800
2040-04-10 05:01 | -1251.33 | 3.6389 | 61.2805 | 59.8258 | -366.7286 |  | 7109 | 25592400 | 57128400 | 88664400 | 120200400
2040-04-11 06:01 | -1042.29 | 3.1431 | 61.3177 | 59.8258 | -305.465 |  | 7110 | 25596000 | 57132000 | 88668000 | 120204000
2040-04-12 07:01 | -1154.74 | 3.5017 | 61.337 | 59.8258 | -338.4209 |  | 7111 | 25599600 | 57135600 | 88671600 | 120207600
2040-04-13 08:01 | -1302.85 | 3.8846 | 61.279 | 59.8258 | -381.8276 |  | 7112 | 25603200 | 57139200 | 88675200 | 120211200
2040-04-14 09:01 | -842.762 | 2.5676 | 61.2374 | 59.8258 | -246.9892 |  | 7113 | 25606800 | 57142800 | 88678800 | 120214800
2040-04-15 10:01 | -384.957 | 1.4166 | 61.5039 | 59.8258 | -112.8198 |  | 7114 | 25610400 | 57146400 | 88682400 | 120218400
2040-04-16 11:01 | 0 | 1 | 62.7757 | 59.8258 | 0 |  | 7115 | 25614000 | 57150000 | 88686000 | 120222000
2040-04-17 12:01 | -296.997 | 1.3431 | 61.7803 | 59.8258 | -87.0412 |  | 7116 | 25617600 | 57153600 | 88689600 | 120225600
2040-04-18 13:01 | -297.189 | 1.2839 | 61.6696 | 59.8258 | -87.0975 |  | 7117 | 25621200 | 57157200 | 88693200 | 120229200
2040-04-19 14:01 | 2337.86 | 1 | 62.4634 | 59.8258 | 685.1591 |  | 7118 | 25624800 | 57160800 | 88696800 | 120232800
2040-04-20 15:01 | 4576.64 | 1.6343 | 75.7832 | 59.8258 | 1341.2808 |  | 7119 | 25628400 | 57164400 | 88700400 | 120236400
2040-04-21 16:01 | 4715.25 | 1.6937 | 76.1087 | 59.8258 | 1381.9034 |  | 7120 | 25632000 | 57168000 | 88704000 | 120240000
2040-04-22 17:01 | 3379.58 | 1.1349 | 77.2454 | 59.8258 | 990.4571 |  | 7121 | 25635600 | 57171600 | 88707600 | 120243600
2040-04-23 18:01 | 3032.34 | 1 | 86.2961 | 59.8258 | 888.6911 |  | 7122 | 25639200 | 57175200 | 88711200 | 120247200
2040-04-24 19:01 | 2884.9 | 1 | 63.4304 | 59.8258 | 845.4807 |  | 7123 | 25642800 | 57178800 | 88714800 | 120250800
2040-04-25 20:01 | -631.208 | 2.2558 | 62.4647 | 59.8258 | -184.9888 |  | 7124 | 25646400 | 57182400 | 88718400 | 120254400
2040-04-26 21:01 | -1140.52 | 3.5233 | 61.8002 | 59.8258 | -334.2534 |  | 7125 | 25650000 | 57186000 | 88722000 | 120258000
2040-04-27 22:01 | -2437.87 | 6.108 | 61.1485 | 59.8258 | -714.4692 |  | 7126 | 25653600 | 57189600 | 88725600 | 120261600
2040-04-28 23:01 | -3192.27 | 6.108 | 60.2787 | 59.8258 | -935.562 |  | 7127 | 25657200 | 57193200 | 88729200 | 120265200
2040-04-30 00:01 | -3479.01 | 6.108 | 59.762 | 59.8258 | -1019.5972 |  | 7128 | 25660800 | 57196800 | 88732800 | 120268800
2040-05-01 01:01 | -3836.32 | 6.108 | 59.2482 | 59.8258 | -1124.3144 |  | 7129 | 25664400 | 57200400 | 88736400 | 120272400
2040-05-02 02:01 | -3791.8 | 6.108 | 59.0812 | 59.8258 | -1111.2669 |  | 7130 | 25668000 | 57204000 | 88740000 | 120276000
2040-05-03 03:01 | -4335.98 | 6.108 | 58.4981 | 59.8258 | -1270.7503 |  | 7131 | 25671600 | 57207600 | 88743600 | 120279600
2040-05-04 04:01 | -4155.88 | 6.108 | 58.4189 | 59.8258 | -1217.9682 |  | 7132 | 25675200 | 57211200 | 88747200 | 120283200
2040-05-05 05:01 | -3505.57 | 6.108 | 58.7751 | 59.8258 | -1027.3812 |  | 7133 | 25678800 | 57214800 | 88750800 | 120286800
2040-05-06 06:01 | -4170.46 | 6.108 | 58.2536 | 59.8258 | -1222.2412 |  | 7134 | 25682400 | 57218400 | 88754400 | 120290400
2040-05-07 07:01 | -3438.34 | 6.108 | 58.6489 | 59.8258 | -1007.678 |  | 7135 | 25686000 | 57222000 | 88758000 | 120294000
2040-05-08 08:01 | -2421.79 | 6.108 | 59.4091 | 59.8258 | -709.7566 |  | 7136 | 25689600 | 57225600 | 88761600 | 120297600
2040-05-09 09:01 | -1034.13 | 2.951 | 59.7424 | 59.8258 | -303.0736 |  | 7137 | 25693200 | 57229200 | 88765200 | 120301200
2040-05-10 10:01 | 2381.13 | 1 | 61.3644 | 59.8258 | 697.8403 |  | 7138 | 25696800 | 57232800 | 88768800 | 120304800
2040-05-11 11:01 | 3344.04 | 1.0704 | 76.4576 | 59.8258 | 980.0414 |  | 7139 | 25700400 | 57236400 | 88772400 | 120308400
2040-05-12 12:01 | 4929.49 | 1.5745 | 76.9035 | 59.8258 | 1444.6909 |  | 7140 | 25704000 | 57240000 | 88776000 | 120312000
2040-05-13 13:01 | 5839.04 | 1.8924 | 77.1841 | 59.8258 | 1711.2537 |  | 7141 | 25707600 | 57243600 | 88779600 | 120315600
2040-05-14 14:01 | 6758.07 | 2.1746 | 77.7336 | 59.8258 | 1980.5948 |  | 7142 | 25711200 | 57247200 | 88783200 | 120319200
2040-05-15 15:01 | 6847.55 | 2.1877 | 78.261 | 59.8258 | 2006.8188 |  | 7143 | 25714800 | 57250800 | 88786800 | 120322800
2040-05-16 16:01 | 6648.92 | 2.1019 | 78.6882 | 59.8258 | 1948.6061 |  | 7144 | 25718400 | 57254400 | 88790400 | 120326400
2040-05-17 17:01 | 4963.58 | 1.6021 | 78.5976 | 59.8258 | 1454.6817 |  | 7145 | 25722000 | 57258000 | 88794000 | 120330000
2040-05-18 18:01 | 3096.69 | 1 | 80.9837 | 59.8258 | 907.5503 |  | 7146 | 25725600 | 57261600 | 88797600 | 120333600
2040-05-19 19:01 | 2999.94 | 1 | 63.9291 | 59.8258 | 879.1956 |  | 7147 | 25729200 | 57265200 | 88801200 | 120337200
2040-05-20 20:01 | -244.464 | 1.2048 | 63.204 | 59.8258 | -71.6453 |  | 7148 | 25732800 | 57268800 | 88804800 | 120340800
2040-05-21 21:01 | -1083.96 | 3.4326 | 62.2324 | 59.8258 | -317.6773 |  | 7149 | 25736400 | 57272400 | 88808400 | 120344400
2040-05-22 22:01 | -2273.86 | 6.108 | 61.5802 | 59.8258 | -666.4026 |  | 7150 | 25740000 | 57276000 | 88812000 | 120348000
2040-05-23 23:01 | -2702.91 | 6.108 | 60.8929 | 59.8258 | -792.1447 |  | 7151 | 25743600 | 57279600 | 88815600 | 120351600
2040-05-25 00:01 | -2884.73 | 6.108 | 60.4557 | 59.8258 | -845.4309 |  | 7152 | 25747200 | 57283200 | 88819200 | 120355200
2040-05-26 01:01 | -3170.06 | 6.108 | 59.9785 | 59.8258 | -929.0529 |  | 7153 | 25750800 | 57286800 | 88822800 | 120358800
2040-05-27 02:01 | -3211.73 | 6.108 | 59.7337 | 59.8258 | -941.2651 |  | 7154 | 25754400 | 57290400 | 88826400 | 120362400
2040-05-28 03:01 | -3004.02 | 6.108 | 59.7135 | 59.8258 | -880.3914 |  | 7155 | 25758000 | 57294000 | 88830000 | 120366000
2040-05-29 04:01 | -2932.72 | 6.108 | 59.6599 | 59.8258 | -859.4954 |  | 7156 | 25761600 | 57297600 | 88833600 | 120369600
2040-05-30 05:01 | -2462.12 | 6.108 | 59.9276 | 59.8258 | -721.5761 |  | 7157 | 25765200 | 57301200 | 88837200 | 120373200
2040-05-31 06:01 | -2872.11 | 6.108 | 59.6198 | 59.8258 | -841.7324 |  | 7158 | 25768800 | 57304800 | 88840800 | 120376800
2040-06-01 07:01 | -2323 | 6.108 | 59.9451 | 59.8258 | -680.8041 |  | 7159 | 25772400 | 57308400 | 88844400 | 120380400
2040-06-02 08:01 | -1820.38 | 5.1749 | 60.1026 | 59.8258 | -533.5007 |  | 7160 | 25776000 | 57312000 | 88848000 | 120384000
2040-06-03 09:01 | 0 | 0 | 61.781 | 59.8258 | 0 |  | 7161 | 25779600 | 57315600 | 88851600 | 120387600
2040-06-04 10:01 | 2814.32 | 1.0565 | 74.2482 | 59.8258 | 824.7958 |  | 7162 | 25783200 | 57319200 | 88855200 | 120391200
2040-06-05 11:01 | 5097.07 | 1.6743 | 76.444 | 59.8258 | 1493.8038 |  | 7163 | 25786800 | 57322800 | 88858800 | 120394800
2040-06-06 12:01 | 6673.75 | 2.1535 | 77.2713 | 59.8258 | 1955.8831 |  | 7164 | 25790400 | 57326400 | 88862400 | 120398400
2040-06-07 13:01 | 6721.3 | 2.1395 | 78.0249 | 59.8258 | 1969.8186 |  | 7165 | 25794000 | 57330000 | 88866000 | 120402000
2040-06-08 14:01 | 5549 | 1.7827 | 78.2709 | 59.8258 | 1626.2514 |  | 7166 | 25797600 | 57333600 | 88869600 | 120405600
2040-06-09 15:01 | 6428.21 | 2.1034 | 78.1107 | 59.8258 | 1883.9224 |  | 7167 | 25801200 | 57337200 | 88873200 | 120409200
2040-06-10 16:01 | 6035.83 | 1.8655 | 79.1582 | 59.8258 | 1768.9272 |  | 7168 | 25804800 | 57340800 | 88876800 | 120412800
2040-06-11 17:01 | 5036.52 | 1.6079 | 78.8124 | 59.8258 | 1476.0583 |  | 7169 | 25808400 | 57344400 | 88880400 | 120416400
2040-06-12 18:01 | 3931.85 | 1.2377 | 78.9866 | 59.8258 | 1152.3115 |  | 7170 | 25812000 | 57348000 | 88884000 | 120420000
2040-06-13 19:01 | 3159.93 | 1 | 83.6123 | 59.8258 | 926.0841 |  | 7171 | 25815600 | 57351600 | 88887600 | 120423600
2040-06-14 20:01 | 3079.79 | 1 | 64.003 | 59.8258 | 902.5974 |  | 7172 | 25819200 | 57355200 | 88891200 | 120427200
2040-06-15 21:01 | -62.1064 | 0.72298 | 63.8606 | 59.8258 | -18.2016 |  | 7173 | 25822800 | 57358800 | 88894800 | 120430800
2040-06-16 22:01 | -998.507 | 3.2251 | 62.3984 | 59.8258 | -292.6335 |  | 7174 | 25826400 | 57362400 | 88898400 | 120434400
2040-06-17 23:01 | -1623.12 | 4.7719 | 61.8773 | 59.8258 | -475.6895 |  | 7175 | 25830000 | 57366000 | 88902000 | 120438000
2040-06-19 00:01 | -2088.16 | 5.9518 | 61.5336 | 59.8258 | -611.9793 |  | 7176 | 25833600 | 57369600 | 88905600 | 120441600
2040-06-20 01:01 | -2286.8 | 6.108 | 61.1538 | 59.8258 | -670.1949 |  | 7177 | 25837200 | 57373200 | 88909200 | 120445200
2040-06-21 02:01 | -2570.93 | 6.108 | 60.7054 | 59.8258 | -753.4652 |  | 7178 | 25840800 | 57376800 | 88912800 | 120448800
2040-06-22 03:01 | -2600.85 | 6.108 | 60.498 | 59.8258 | -762.2339 |  | 7179 | 25844400 | 57380400 | 88916400 | 120452400
2040-06-23 04:01 | -2849.3 | 6.108 | 60.1708 | 59.8258 | -835.0474 |  | 7180 | 25848000 | 57384000 | 88920000 | 120456000
2040-06-24 05:01 | -2975.2 | 6.108 | 59.9323 | 59.8258 | -871.945 |  | 7181 | 25851600 | 57387600 | 88923600 | 120459600
2040-06-25 06:01 | -2236.35 | 6.108 | 60.3664 | 59.8258 | -655.4095 |  | 7182 | 25855200 | 57391200 | 88927200 | 120463200
2040-06-26 07:01 | -1261.58 | 3.5632 | 60.4225 | 59.8258 | -369.7326 |  | 7183 | 25858800 | 57394800 | 88930800 | 120466800
2040-06-27 08:01 | -1737.5 | 5.1412 | 60.5996 | 59.8258 | -509.211 |  | 7184 | 25862400 | 57398400 | 88934400 | 120470400
2040-06-28 09:01 | -2035.97 | 5.8453 | 60.5253 | 59.8258 | -596.6839 |  | 7185 | 25866000 | 57402000 | 88938000 | 120474000
2040-06-29 10:01 | -1737.31 | 4.9351 | 60.4125 | 59.8258 | -509.1553 |  | 7186 | 25869600 | 57405600 | 88941600 | 120477600
2040-06-30 11:01 | -1319.87 | 3.8388 | 60.4158 | 59.8258 | -386.8157 |  | 7187 | 25873200 | 57409200 | 88945200 | 120481200
2040-07-01 12:01 | -1360.39 | 4.0566 | 60.444 | 59.8258 | -398.691 |  | 7188 | 25876800 | 57412800 | 88948800 | 120484800
2040-07-02 13:01 | -1239.28 | 3.6973 | 60.3681 | 59.8258 | -363.1971 |  | 7189 | 25880400 | 57416400 | 88952400 | 120488400
2040-07-03 14:01 | -1039.1 | 3.1669 | 60.3443 | 59.8258 | -304.5301 |  | 7190 | 25884000 | 57420000 | 88956000 | 120492000
2040-07-04 15:01 | -812.187 | 2.577 | 60.3681 | 59.8258 | -238.0285 |  | 7191 | 25887600 | 57423600 | 88959600 | 120495600
2040-07-05 16:01 | 2123.46 | 1 | 61.6059 | 59.8258 | 622.3247 |  | 7192 | 25891200 | 57427200 | 88963200 | 120499200
2040-07-06 17:01 | 94.391 | 1 | 62.1565 | 59.8258 | 27.6633 |  | 7193 | 25894800 | 57430800 | 88966800 | 120502800
2040-07-07 18:01 | -30.2836 | 0.66561 | 61.885 | 59.8258 | -8.8752 |  | 7194 | 25898400 | 57434400 | 88970400 | 120506400
2040-07-08 19:01 | -463.508 | 1.8099 | 60.8408 | 59.8258 | -135.8408 |  | 7195 | 25902000 | 57438000 | 88974000 | 120510000
2040-07-09 20:01 | -614.235 | 2.1395 | 60.651 | 59.8258 | -180.0145 |  | 7196 | 25905600 | 57441600 | 88977600 | 120513600
2040-07-10 21:01 | -890.63 | 2.8866 | 60.5331 | 59.8258 | -261.0179 |  | 7197 | 25909200 | 57445200 | 88981200 | 120517200
2040-07-11 22:01 | -1049.77 | 3.2715 | 60.3893 | 59.8258 | -307.6572 |  | 7198 | 25912800 | 57448800 | 88984800 | 120520800
2040-07-12 23:01 | -2440.58 | 6.108 | 59.9937 | 59.8258 | -715.2634 |  | 7199 | 25916400 | 57452400 | 88988400 | 120524400
2040-07-14 00:01 | -2792.51 | 6.108 | 59.5251 | 59.8258 | -818.4039 |  | 7200 | 25920000 | 57456000 | 88992000 | 120528000
2040-07-15 01:01 | -2743.95 | 6.108 | 59.404 | 59.8258 | -804.1724 |  | 7201 | 25923600 | 57459600 | 88995600 | 120531600
2040-07-16 02:01 | -2866.64 | 6.108 | 59.2328 | 59.8258 | -840.1293 |  | 7202 | 25927200 | 57463200 | 88999200 | 120535200
2040-07-17 03:01 | -2874.52 | 6.108 | 59.1436 | 59.8258 | -842.4387 |  | 7203 | 25930800 | 57466800 | 89002800 | 120538800
2040-07-18 04:01 | -3021.7 | 6.108 | 58.9258 | 59.8258 | -885.5729 |  | 7204 | 25934400 | 57470400 | 89006400 | 120542400
2040-07-19 05:01 | -3124.57 | 6.108 | 58.7794 | 59.8258 | -915.7211 |  | 7205 | 25938000 | 57474000 | 89010000 | 120546000
2040-07-20 06:01 | -3160.24 | 6.108 | 58.6835 | 59.8258 | -926.1749 |  | 7206 | 25941600 | 57477600 | 89013600 | 120549600
2040-07-21 07:01 | -2365.8 | 6.108 | 59.2103 | 59.8258 | -693.3475 |  | 7207 | 25945200 | 57481200 | 89017200 | 120553200
2040-07-22 08:01 | -1987.81 | 5.7073 | 59.4418 | 59.8258 | -582.5696 |  | 7208 | 25948800 | 57484800 | 89020800 | 120556800
2040-07-23 09:01 | -2396.97 | 6.108 | 59.2994 | 59.8258 | -702.4826 |  | 7209 | 25952400 | 57488400 | 89024400 | 120560400
2040-07-24 10:01 | -1964.98 | 5.6432 | 59.4468 | 59.8258 | -575.8788 |  | 7210 | 25956000 | 57492000 | 89028000 | 120564000
2040-07-25 11:01 | -1687.65 | 4.8716 | 59.4769 | 59.8258 | -494.6014 |  | 7211 | 25959600 | 57495600 | 89031600 | 120567600
2040-07-26 12:01 | -1017.12 | 3.0217 | 59.5698 | 59.8258 | -298.0884 |  | 7212 | 25963200 | 57499200 | 89035200 | 120571200
2040-07-27 13:01 | -264.489 | 1.0584 | 60.0567 | 59.8258 | -77.5141 |  | 7213 | 25966800 | 57502800 | 89038800 | 120574800
2040-07-28 14:01 | -381.145 | 1.5624 | 60.2225 | 59.8258 | -111.7026 |  | 7214 | 25970400 | 57506400 | 89042400 | 120578400
2040-07-29 15:01 | -662.903 | 2.3123 | 60.0828 | 59.8258 | -194.2777 |  | 7215 | 25974000 | 57510000 | 89046000 | 120582000
2040-07-30 16:01 | -321.846 | 1.2845 | 60.2202 | 59.8258 | -94.3238 |  | 7216 | 25977600 | 57513600 | 89049600 | 120585600
2040-07-31 17:01 | 2678.8 | 1 | 61.1845 | 59.8258 | 785.0788 |  | 7217 | 25981200 | 57517200 | 89053200 | 120589200
2040-08-01 18:01 | -261.936 | 1.2971 | 60.9419 | 59.8258 | -76.7659 |  | 7218 | 25984800 | 57520800 | 89056800 | 120592800
2040-08-02 19:01 | -816.281 | 2.7562 | 60.3524 | 59.8258 | -239.2283 |  | 7219 | 25988400 | 57524400 | 89060400 | 120596400
2040-08-03 20:01 | -1298.49 | 4.0025 | 60.0599 | 59.8258 | -380.5499 |  | 7220 | 25992000 | 57528000 | 89064000 | 120600000
2040-08-04 21:01 | -2021.93 | 5.9607 | 59.9208 | 59.8258 | -592.5692 |  | 7221 | 25995600 | 57531600 | 89067600 | 120603600
2040-08-05 22:01 | -2553.46 | 6.108 | 59.4271 | 59.8258 | -748.3453 |  | 7222 | 25999200 | 57535200 | 89071200 | 120607200
2040-08-06 23:01 | -3134.51 | 6.108 | 58.7855 | 59.8258 | -918.6342 |  | 7223 | 26002800 | 57538800 | 89074800 | 120610800
2040-08-08 00:01 | -4311.78 | 6.108 | 57.7373 | 59.8258 | -1263.658 |  | 7224 | 26006400 | 57542400 | 89078400 | 120614400
2040-08-09 01:01 | -4744.56 | 6.108 | 57.1407 | 59.8258 | -1390.4933 |  | 7225 | 26010000 | 57546000 | 89082000 | 120618000
2040-08-10 02:01 | -4896.18 | 6.108 | 56.7967 | 59.8258 | -1434.9287 |  | 7226 | 26013600 | 57549600 | 89085600 | 120621600
2040-08-11 03:01 | -5412.35 | 6.108 | 56.2451 | 59.8258 | -1586.2032 |  | 7227 | 26017200 | 57553200 | 89089200 | 120625200
2040-08-12 04:01 | -5194.87 | 6.108 | 56.2049 | 59.8258 | -1522.4661 |  | 7228 | 26020800 | 57556800 | 89092800 | 120628800
2040-08-13 05:01 | -4975.02 | 6.108 | 56.2105 | 59.8258 | -1458.0344 |  | 7229 | 26024400 | 57560400 | 89096400 | 120632400
2040-08-14 06:01 | -4640.06 | 6.108 | 56.3965 | 59.8258 | -1359.8673 |  | 7230 | 26028000 | 57564000 | 89100000 | 120636000
2040-08-15 07:01 | -3585.06 | 6.108 | 57.1539 | 59.8258 | -1050.6774 |  | 7231 | 26031600 | 57567600 | 89103600 | 120639600
2040-08-16 08:01 | -1691.3 | 4.9786 | 58.3753 | 59.8258 | -495.6711 |  | 7232 | 26035200 | 57571200 | 89107200 | 120643200
2040-08-17 09:01 | -913.728 | 2.7453 | 58.7034 | 59.8258 | -267.7872 |  | 7233 | 26038800 | 57574800 | 89110800 | 120646800
2040-08-18 10:01 | 0 | 0 | 60.4824 | 59.8258 | 0 |  | 7234 | 26042400 | 57578400 | 89114400 | 120650400
2040-08-19 11:01 | 3091.54 | 1 | 81.3241 | 59.8258 | 906.0409 |  | 7235 | 26046000 | 57582000 | 89118000 | 120654000
2040-08-20 12:01 | 3535.96 | 1.1931 | 74.887 | 59.8258 | 1036.2876 |  | 7236 | 26049600 | 57585600 | 89121600 | 120657600
2040-08-21 13:01 | 4339.47 | 1.4354 | 75.6079 | 59.8258 | 1271.7731 |  | 7237 | 26053200 | 57589200 | 89125200 | 120661200
2040-08-22 14:01 | 4436.53 | 1.4746 | 75.9118 | 59.8258 | 1300.2186 |  | 7238 | 26056800 | 57592800 | 89128800 | 120664800
2040-08-23 15:01 | 4087.81 | 1.3601 | 76.2113 | 59.8258 | 1198.0189 |  | 7239 | 26060400 | 57596400 | 89132400 | 120668400
2040-08-24 16:01 | 4750.62 | 1.5362 | 76.8002 | 59.8258 | 1392.2693 |  | 7240 | 26064000 | 57600000 | 89136000 | 120672000
2040-08-25 17:01 | 3010.97 | 1 | 77.216 | 59.8258 | 882.4282 |  | 7241 | 26067600 | 57603600 | 89139600 | 120675600
2040-08-26 18:01 | 3015.93 | 1 | 62.5887 | 59.8258 | 883.8818 |  | 7242 | 26071200 | 57607200 | 89143200 | 120679200
2040-08-27 19:01 | 0 | 0 | 62.8827 | 59.8258 | 0 |  | 7243 | 26074800 | 57610800 | 89146800 | 120682800
2040-08-28 20:01 | -702.222 | 2.3237 | 61.1481 | 59.8258 | -205.801 |  | 7244 | 26078400 | 57614400 | 89150400 | 120686400
2040-08-29 21:01 | -1854.62 | 5.5752 | 60.7446 | 59.8258 | -543.5355 |  | 7245 | 26082000 | 57618000 | 89154000 | 120690000
2040-08-30 22:01 | -2683.48 | 6.108 | 59.9558 | 59.8258 | -786.4504 |  | 7246 | 26085600 | 57621600 | 89157600 | 120693600
2040-08-31 23:01 | -3549.65 | 6.108 | 58.9961 | 59.8258 | -1040.2997 |  | 7247 | 26089200 | 57625200 | 89161200 | 120697200
2040-09-02 00:01 | -4207.15 | 6.108 | 58.1633 | 59.8258 | -1232.994 |  | 7248 | 26092800 | 57628800 | 89164800 | 120700800
2040-09-03 01:01 | -4552.81 | 6.108 | 57.6142 | 59.8258 | -1334.2969 |  | 7249 | 26096400 | 57632400 | 89168400 | 120704400
2040-09-04 02:01 | -4891.88 | 6.108 | 57.1064 | 59.8258 | -1433.6685 |  | 7250 | 26100000 | 57636000 | 89172000 | 120708000
2040-09-05 03:01 | -4856 | 6.108 | 56.908 | 59.8258 | -1423.1531 |  | 7251 | 26103600 | 57639600 | 89175600 | 120711600
2040-09-06 04:01 | -4908.24 | 6.108 | 56.6905 | 59.8258 | -1438.4631 |  | 7252 | 26107200 | 57643200 | 89179200 | 120715200
2040-09-07 05:01 | -4543.5 | 6.108 | 56.8253 | 59.8258 | -1331.5684 |  | 7253 | 26110800 | 57646800 | 89182800 | 120718800
2040-09-08 06:01 | -4060.23 | 6.108 | 57.1145 | 59.8258 | -1189.936 |  | 7254 | 26114400 | 57650400 | 89186400 | 120722400
2040-09-09 07:01 | -3567.66 | 6.108 | 57.4897 | 59.8258 | -1045.5779 |  | 7255 | 26118000 | 57654000 | 89190000 | 120726000
2040-09-10 08:01 | -2310.31 | 6.108 | 58.468 | 59.8258 | -677.085 |  | 7256 | 26121600 | 57657600 | 89193600 | 120729600
2040-09-11 09:01 | -1303.19 | 3.7629 | 58.7802 | 59.8258 | -381.9273 |  | 7257 | 26125200 | 57661200 | 89197200 | 120733200
2040-09-12 10:01 | 2251.6 | 1 | 60.3834 | 59.8258 | 659.8788 |  | 7258 | 26128800 | 57664800 | 89200800 | 120736800
2040-09-13 11:01 | 3126.06 | 1 | 60.8855 | 59.8258 | 916.1577 |  | 7259 | 26132400 | 57668400 | 89204400 | 120740400
2040-09-14 12:01 | 4055.07 | 1.3182 | 75.7153 | 59.8258 | 1188.4237 |  | 7260 | 26136000 | 57672000 | 89208000 | 120744000
2040-09-15 13:01 | 4996.8 | 1.6048 | 76.2305 | 59.8258 | 1464.4175 |  | 7261 | 26139600 | 57675600 | 89211600 | 120747600
2040-09-16 14:01 | 3991.18 | 1.2825 | 76.6406 | 59.8258 | 1169.6994 |  | 7262 | 26143200 | 57679200 | 89215200 | 120751200
2040-09-17 15:01 | 4237.07 | 1.3304 | 77.1396 | 59.8258 | 1241.7626 |  | 7263 | 26146800 | 57682800 | 89218800 | 120754800
2040-09-18 16:01 | 4399.35 | 1.3747 | 77.3483 | 59.8258 | 1289.3222 |  | 7264 | 26150400 | 57686400 | 89222400 | 120758400
2040-09-19 17:01 | 3112.75 | 1 | 78.9326 | 59.8258 | 912.257 |  | 7265 | 26154000 | 57690000 | 89226000 | 120762000
2040-09-20 18:01 | 3086.47 | 1 | 82.3114 | 59.8258 | 904.5551 |  | 7266 | 26157600 | 57693600 | 89229600 | 120765600
2040-09-21 19:01 | 3155.88 | 1 | 62.5742 | 59.8258 | 924.8971 |  | 7267 | 26161200 | 57697200 | 89233200 | 120769200
2040-09-22 20:01 | 0 | 0 | 62.9512 | 59.8258 | 0 |  | 7268 | 26164800 | 57700800 | 89236800 | 120772800
2040-09-23 21:01 | -715.254 | 2.3596 | 61.2104 | 59.8258 | -209.6203 |  | 7269 | 26168400 | 57704400 | 89240400 | 120776400
2040-09-24 22:01 | -1008.43 | 3.1853 | 60.8418 | 59.8258 | -295.5417 |  | 7270 | 26172000 | 57708000 | 89244000 | 120780000
2040-09-25 23:01 | -1934.36 | 5.7368 | 60.5809 | 59.8258 | -566.905 |  | 7271 | 26175600 | 57711600 | 89247600 | 120783600
2040-09-27 00:01 | -2143 | 6.108 | 60.2614 | 59.8258 | -628.0513 |  | 7272 | 26179200 | 57715200 | 89251200 | 120787200
2040-09-28 01:01 | -2323.92 | 6.108 | 59.8941 | 59.8258 | -681.0737 |  | 7273 | 26182800 | 57718800 | 89254800 | 120790800
2040-09-29 02:01 | -2637.04 | 6.108 | 59.5333 | 59.8258 | -772.8401 |  | 7274 | 26186400 | 57722400 | 89258400 | 120794400
2040-09-30 03:01 | -2782.6 | 6.108 | 59.2874 | 59.8258 | -815.4996 |  | 7275 | 26190000 | 57726000 | 89262000 | 120798000
2040-10-01 04:01 | -2465.72 | 6.108 | 59.3963 | 59.8258 | -722.6312 |  | 7276 | 26193600 | 57729600 | 89265600 | 120801600
2040-10-02 05:01 | -2585.56 | 6.108 | 59.2739 | 59.8258 | -757.7528 |  | 7277 | 26197200 | 57733200 | 89269200 | 120805200
2040-10-03 06:01 | -2104.29 | 6.0485 | 59.5564 | 59.8258 | -616.7065 |  | 7278 | 26200800 | 57736800 | 89272800 | 120808800
2040-10-04 07:01 | -1874.48 | 5.3652 | 59.5437 | 59.8258 | -549.3559 |  | 7279 | 26204400 | 57740400 | 89276400 | 120812400
2040-10-05 08:01 | -2048.4 | 5.9303 | 59.5962 | 59.8258 | -600.3268 |  | 7280 | 26208000 | 57744000 | 89280000 | 120816000
2040-10-06 09:01 | -2113.98 | 6.0669 | 59.5642 | 59.8258 | -619.5464 |  | 7281 | 26211600 | 57747600 | 89283600 | 120819600
2040-10-07 10:01 | -1843.86 | 5.2786 | 59.5025 | 59.8258 | -540.382 |  | 7282 | 26215200 | 57751200 | 89287200 | 120823200
2040-10-08 11:01 | -1530.39 | 4.4532 | 59.513 | 59.8258 | -448.513 |  | 7283 | 26218800 | 57754800 | 89290800 | 120826800
2040-10-09 12:01 | -1033.19 | 3.1083 | 59.5617 | 59.8258 | -302.7981 |  | 7284 | 26222400 | 57758400 | 89294400 | 120830400
2040-10-10 13:01 | -1011.64 | 3.1721 | 59.6518 | 59.8258 | -296.4824 |  | 7285 | 26226000 | 57762000 | 89298000 | 120834000
2040-10-11 14:01 | -1082.85 | 3.3692 | 59.645 | 59.8258 | -317.352 |  | 7286 | 26229600 | 57765600 | 89301600 | 120837600
2040-10-12 15:01 | -1226.08 | 3.7611 | 59.6018 | 59.8258 | -359.3286 |  | 7287 | 26233200 | 57769200 | 89305200 | 120841200
2040-10-13 16:01 | -536.128 | 1.7602 | 59.6417 | 59.8258 | -157.1236 |  | 7288 | 26236800 | 57772800 | 89308800 | 120844800
2040-10-14 17:01 | -297.596 | 1.2705 | 60.0256 | 59.8258 | -87.2168 |  | 7289 | 26240400 | 57776400 | 89312400 | 120848400
2040-10-15 18:01 | 0 | 0 | 61.1472 | 59.8258 | 0 |  | 7290 | 26244000 | 57780000 | 89316000 | 120852000
2040-10-16 19:01 | -392.34 | 1.636 | 60.1046 | 59.8258 | -114.9835 |  | 7291 | 26247600 | 57783600 | 89319600 | 120855600
2040-10-17 20:01 | -619.341 | 2.1884 | 59.9108 | 59.8258 | -181.5109 |  | 7292 | 26251200 | 57787200 | 89323200 | 120859200
2040-10-18 21:01 | -1238.78 | 3.8991 | 59.7512 | 59.8258 | -363.0506 |  | 7293 | 26254800 | 57790800 | 89326800 | 120862800
2040-10-19 22:01 | -1322.44 | 3.9856 | 59.6139 | 59.8258 | -387.5689 |  | 7294 | 26258400 | 57794400 | 89330400 | 120866400
2040-10-20 23:01 | -1820.1 | 5.4088 | 59.5552 | 59.8258 | -533.4187 |  | 7295 | 26262000 | 57798000 | 89334000 | 120870000
2040-10-22 00:01 | -1988.56 | 5.7664 | 59.4277 | 59.8258 | -582.7894 |  | 7296 | 26265600 | 57801600 | 89337600 | 120873600
2040-10-23 01:01 | -1868.45 | 5.3899 | 59.3482 | 59.8258 | -547.5886 |  | 7297 | 26269200 | 57805200 | 89341200 | 120877200
2040-10-24 02:01 | -1655.64 | 4.813 | 59.3411 | 59.8258 | -485.2202 |  | 7298 | 26272800 | 57808800 | 89344800 | 120880800
2040-10-25 03:01 | -1355.04 | 4.0019 | 59.3908 | 59.8258 | -397.123 |  | 7299 | 26276400 | 57812400 | 89348400 | 120884400
2040-10-26 04:01 | -1085.98 | 3.3059 | 59.4798 | 59.8258 | -318.2693 |  | 7300 | 26280000 | 57816000 | 89352000 | 120888000
2040-10-27 05:01 | -888.044 | 2.8038 | 59.5972 | 59.8258 | -260.26 |  | 7301 | 26283600 | 57819600 | 89355600 | 120891600
2040-10-28 06:01 | -467.65 | 1.6547 | 59.8138 | 59.8258 | -137.0547 |  | 7302 | 26287200 | 57823200 | 89359200 | 120895200
2040-10-29 07:01 | 4.0801 | 1 | 61.2064 | 59.8258 | 1.1958 |  | 7303 | 26290800 | 57826800 | 89362800 | 120898800
2040-10-30 08:01 | 2259.6 | 1 | 77.1058 | 59.8258 | 662.2234 |  | 7304 | 26294400 | 57830400 | 89366400 | 120902400
2040-10-31 09:01 | 3134.84 | 1.0461 | 75.4131 | 59.8258 | 918.7309 |  | 7305 | 26298000 | 57834000 | 89370000 | 120906000
2040-11-01 10:01 | 4058.23 | 1.3195 | 76.119 | 59.8258 | 1189.3498 |  | 7306 | 26301600 | 57837600 | 89373600 | 120909600
2040-11-02 11:01 | 4151.31 | 1.339 | 76.569 | 59.8258 | 1216.6289 |  | 7307 | 26305200 | 57841200 | 89377200 | 120913200
2040-11-03 12:01 | 5763.53 | 1.9051 | 76.4715 | 59.8258 | 1689.1239 |  | 7308 | 26308800 | 57844800 | 89380800 | 120916800
2040-11-04 13:01 | 5827.83 | 1.8132 | 77.7559 | 59.8258 | 1707.9684 |  | 7309 | 26312400 | 57848400 | 89384400 | 120920400
2040-11-05 14:01 | 5540.44 | 1.6503 | 78.6907 | 59.8258 | 1623.7427 |  | 7310 | 26316000 | 57852000 | 89388000 | 120924000
2040-11-06 15:01 | 5639.82 | 1.7425 | 78.2954 | 59.8258 | 1652.8681 |  | 7311 | 26319600 | 57855600 | 89391600 | 120927600
2040-11-07 16:01 | 5348.64 | 1.6878 | 78.1465 | 59.8258 | 1567.5316 |  | 7312 | 26323200 | 57859200 | 89395200 | 120931200
2040-11-08 17:01 | 4157.81 | 1.3247 | 78.1306 | 59.8258 | 1218.5338 |  | 7313 | 26326800 | 57862800 | 89398800 | 120934800
2040-11-09 18:01 | 2995.27 | 1 | 79.4877 | 59.8258 | 877.827 |  | 7314 | 26330400 | 57866400 | 89402400 | 120938400
2040-11-10 19:01 | 2993.7 | 1 | 63.2967 | 59.8258 | 877.3669 |  | 7315 | 26334000 | 57870000 | 89406000 | 120942000
2040-11-11 20:01 | 2968.23 | 1 | 63.2545 | 59.8258 | 869.9023 |  | 7316 | 26337600 | 57873600 | 89409600 | 120945600
2040-11-12 21:01 | -598.456 | 2.1908 | 62.2482 | 59.8258 | -175.3901 |  | 7317 | 26341200 | 57877200 | 89413200 | 120949200
2040-11-13 22:01 | -1016.53 | 3.1965 | 61.5368 | 59.8258 | -297.9155 |  | 7318 | 26344800 | 57880800 | 89416800 | 120952800
2040-11-14 23:01 | -1929.34 | 5.6824 | 61.1153 | 59.8258 | -565.4337 |  | 7319 | 26348400 | 57884400 | 89420400 | 120956400
2040-11-16 00:01 | -2293.1 | 6.108 | 60.6589 | 59.8258 | -672.0413 |  | 7320 | 26352000 | 57888000 | 89424000 | 120960000
2040-11-17 01:01 | -2616.32 | 6.108 | 60.1408 | 59.8258 | -766.7677 |  | 7321 | 26355600 | 57891600 | 89427600 | 120963600
2040-11-18 02:01 | -2793.45 | 6.108 | 59.7435 | 59.8258 | -818.6794 |  | 7322 | 26359200 | 57895200 | 89431200 | 120967200
2040-11-19 03:01 | -2948.39 | 6.108 | 59.4497 | 59.8258 | -864.0878 |  | 7323 | 26362800 | 57898800 | 89434800 | 120970800
2040-11-20 04:01 | -2844.83 | 6.108 | 59.3592 | 59.8258 | -833.7374 |  | 7324 | 26366400 | 57902400 | 89438400 | 120974400
2040-11-21 05:01 | -2671.04 | 6.108 | 59.3831 | 59.8258 | -782.8046 |  | 7325 | 26370000 | 57906000 | 89442000 | 120978000
2040-11-22 06:01 | -2206.03 | 6.108 | 59.6658 | 59.8258 | -646.5236 |  | 7326 | 26373600 | 57909600 | 89445600 | 120981600
2040-11-23 07:01 | -2080.92 | 5.947 | 59.7039 | 59.8258 | -609.8575 |  | 7327 | 26377200 | 57913200 | 89449200 | 120985200
2040-11-24 08:01 | -1930.87 | 5.5294 | 59.6661 | 59.8258 | -565.8821 |  | 7328 | 26380800 | 57916800 | 89452800 | 120988800
2040-11-25 09:01 | -2123.27 | 6.108 | 59.6673 | 59.8258 | -622.269 |  | 7329 | 26384400 | 57920400 | 89456400 | 120992400
2040-11-26 10:01 | -1834.58 | 5.2414 | 59.5993 | 59.8258 | -537.6623 |  | 7330 | 26388000 | 57924000 | 89460000 | 120996000
2040-11-27 11:01 | -1468.52 | 4.2737 | 59.6153 | 59.8258 | -430.3807 |  | 7331 | 26391600 | 57927600 | 89463600 | 120999600
2040-11-28 12:01 | -1105.33 | 3.3268 | 59.6746 | 59.8258 | -323.9402 |  | 7332 | 26395200 | 57931200 | 89467200 | 121003200
2040-11-29 13:01 | -892.591 | 2.8089 | 59.766 | 59.8258 | -261.5926 |  | 7333 | 26398800 | 57934800 | 89470800 | 121006800
2040-11-30 14:01 | -906.213 | 2.8949 | 59.8088 | 59.8258 | -265.5848 |  | 7334 | 26402400 | 57938400 | 89474400 | 121010400
2040-12-01 15:01 | -727.252 | 2.3789 | 59.8423 | 59.8258 | -213.1365 |  | 7335 | 26406000 | 57942000 | 89478000 | 121014000
2040-12-02 16:01 | 63.9833 | 1 | 61.2481 | 59.8258 | 18.7517 |  | 7336 | 26409600 | 57945600 | 89481600 | 121017600
2040-12-03 17:01 | -125.105 | 0.90804 | 60.7303 | 59.8258 | -36.6647 |  | 7337 | 26413200 | 57949200 | 89485200 | 121021200
2040-12-04 18:01 | -449.02 | 1.7651 | 60.2224 | 59.8258 | -131.5948 |  | 7338 | 26416800 | 57952800 | 89488800 | 121024800
2040-12-05 19:01 | -1062.07 | 3.4259 | 59.9353 | 59.8258 | -311.262 |  | 7339 | 26420400 | 57956400 | 89492400 | 121028400
2040-12-06 20:01 | -1538.07 | 4.6401 | 59.7492 | 59.8258 | -450.7638 |  | 7340 | 26424000 | 57960000 | 89496000 | 121032000
2040-12-07 21:01 | -2602.98 | 6.108 | 59.2341 | 59.8258 | -762.8581 |  | 7341 | 26427600 | 57963600 | 89499600 | 121035600
2040-12-08 22:01 | -3126.65 | 6.108 | 58.6436 | 59.8258 | -916.3307 |  | 7342 | 26431200 | 57967200 | 89503200 | 121039200
2040-12-09 23:01 | -4099.09 | 6.108 | 57.731 | 59.8258 | -1201.3247 |  | 7343 | 26434800 | 57970800 | 89506800 | 121042800
2040-12-11 00:01 | -4738.11 | 6.108 | 57.0081 | 59.8258 | -1388.603 |  | 7344 | 26438400 | 57974400 | 89510400 | 121046400
2040-12-12 01:01 | -4874.09 | 6.108 | 56.6616 | 59.8258 | -1428.4548 |  | 7345 | 26442000 | 57978000 | 89514000 | 121050000
2040-12-13 02:01 | -5045.66 | 6.108 | 56.3522 | 59.8258 | -1478.737 |  | 7346 | 26445600 | 57981600 | 89517600 | 121053600
2040-12-14 03:01 | -5050.55 | 6.108 | 56.1959 | 59.8258 | -1480.1701 |  | 7347 | 26449200 | 57985200 | 89521200 | 121057200
2040-12-15 04:01 | -5270.84 | 6.108 | 55.8938 | 59.8258 | -1544.7307 |  | 7348 | 26452800 | 57988800 | 89524800 | 121060800
2040-12-16 05:01 | -5447.26 | 6.108 | 55.6218 | 59.8258 | -1596.4343 |  | 7349 | 26456400 | 57992400 | 89528400 | 121064400
2040-12-17 06:01 | -5680.44 | 6.108 | 55.3102 | 59.8258 | -1664.7726 |  | 7350 | 26460000 | 57996000 | 89532000 | 121068000
2040-12-18 07:01 | -4389.34 | 6.108 | 56.1324 | 59.8258 | -1286.3886 |  | 7351 | 26463600 | 57999600 | 89535600 | 121071600
2040-12-19 08:01 | -2581.46 | 6.108 | 57.5383 | 59.8258 | -756.5512 |  | 7352 | 26467200 | 58003200 | 89539200 | 121075200
2040-12-20 09:01 | -1780.82 | 5.2092 | 58.147 | 59.8258 | -521.9068 |  | 7353 | 26470800 | 58006800 | 89542800 | 121078800
2040-12-21 10:01 | -732.592 | 2.2104 | 58.3907 | 59.8258 | -214.7015 |  | 7354 | 26474400 | 58010400 | 89546400 | 121082400
2040-12-22 11:01 | 2114.51 | 1 | 59.9686 | 59.8258 | 619.7017 |  | 7355 | 26478000 | 58014000 | 89550000 | 121086000
2040-12-23 12:01 | 2930.04 | 1 | 60.4451 | 59.8258 | 858.71 |  | 7356 | 26481600 | 58017600 | 89553600 | 121089600
2040-12-24 13:01 | 2930.68 | 1 | 83.7019 | 59.8258 | 858.8975 |  | 7357 | 26485200 | 58021200 | 89557200 | 121093200
2040-12-25 14:01 | 2799.81 | 1 | 79.2137 | 59.8258 | 820.5433 |  | 7358 | 26488800 | 58024800 | 89560800 | 121096800
2040-12-26 15:01 | 2836.62 | 1 | 81.3455 | 59.8258 | 831.3313 |  | 7359 | 26492400 | 58028400 | 89564400 | 121100400
2040-12-27 16:01 | 2754.51 | 1 | 61.4907 | 59.8258 | 807.2672 |  | 7360 | 26496000 | 58032000 | 89568000 | 121104000
2040-12-28 17:01 | 2923.51 | 1 | 61.5917 | 59.8258 | 856.7962 |  | 7361 | 26499600 | 58035600 | 89571600 | 121107600
2040-12-29 18:01 | -297.747 | 1.3789 | 60.987 | 59.8258 | -87.261 |  | 7362 | 26503200 | 58039200 | 89575200 | 121111200
2040-12-30 19:01 | -1114.23 | 3.5918 | 60.2257 | 59.8258 | -326.5486 |  | 7363 | 26506800 | 58042800 | 89578800 | 121114800
2040-12-31 20:01 | -1812.55 | 5.4055 | 59.8375 | 59.8258 | -531.206 |  | 7364 | 26510400 | 58046400 | 89582400 | 121118400
2041-01-01 21:01 | -2461.8 | 6.108 | 59.326 | 59.8258 | -721.4824 |  | 7365 | 26514000 | 58050000 | 89586000 | 121122000
2041-01-02 22:01 | -3141.76 | 6.108 | 58.5889 | 59.8258 | -920.759 |  | 7366 | 26517600 | 58053600 | 89589600 | 121125600
2041-01-03 23:01 | -3716.75 | 6.108 | 57.8718 | 59.8258 | -1089.2719 |  | 7367 | 26521200 | 58057200 | 89593200 | 121129200
2041-01-05 00:01 | -5533.41 | 6.108 | 56.2772 | 59.8258 | -1621.6824 |  | 7368 | 26524800 | 58060800 | 89596800 | 121132800
2041-01-06 01:01 | -5822.84 | 6.108 | 55.652 | 59.8258 | -1706.5059 |  | 7369 | 26528400 | 58064400 | 89600400 | 121136400
2041-01-07 02:01 | -6080.48 | 6.108 | 55.1552 | 59.8258 | -1782.0128 |  | 7370 | 26532000 | 58068000 | 89604000 | 121140000
2041-01-08 03:01 | -6113.17 | 6.108 | 54.8859 | 59.8258 | -1791.5933 |  | 7371 | 26535600 | 58071600 | 89607600 | 121143600
2041-01-09 04:01 | -6290.98 | 6.108 | 54.5455 | 59.8258 | -1843.7042 |  | 7372 | 26539200 | 58075200 | 89611200 | 121147200
2041-01-10 05:01 | -6401.3 | 6.108 | 54.2536 | 59.8258 | -1876.0358 |  | 7373 | 26542800 | 58078800 | 89614800 | 121150800
2041-01-11 06:01 | -6553.08 | 6.108 | 54.0041 | 59.8258 | -1920.5182 |  | 7374 | 26546400 | 58082400 | 89618400 | 121154400
2041-01-12 07:01 | -4959.77 | 6.108 | 55.0609 | 59.8258 | -1453.5651 |  | 7375 | 26550000 | 58086000 | 89622000 | 121158000
2041-01-13 08:01 | -3136.12 | 6.108 | 56.5258 | 59.8258 | -919.106 |  | 7376 | 26553600 | 58089600 | 89625600 | 121161600
2041-01-14 09:01 | -2257.66 | 6.108 | 57.4497 | 59.8258 | -661.6548 |  | 7377 | 26557200 | 58093200 | 89629200 | 121165200
2041-01-15 10:01 | -1016.56 | 2.9699 | 57.7991 | 59.8258 | -297.9243 |  | 7378 | 26560800 | 58096800 | 89632800 | 121168800
2041-01-16 11:01 | 1964.76 | 1 | 59.4709 | 59.8258 | 575.8143 |  | 7379 | 26564400 | 58100400 | 89636400 | 121172400
2041-01-17 12:01 | 2932.77 | 1 | 82.9354 | 59.8258 | 859.51 |  | 7380 | 26568000 | 58104000 | 89640000 | 121176000
2041-01-18 13:01 | 2854.89 | 1 | 74.7553 | 59.8258 | 836.6857 |  | 7381 | 26571600 | 58107600 | 89643600 | 121179600
2041-01-19 14:01 | 2912.34 | 1 | 74.8399 | 59.8258 | 853.5226 |  | 7382 | 26575200 | 58111200 | 89647200 | 121183200
2041-01-20 15:01 | 2907.13 | 1 | 75.4632 | 59.8258 | 851.9957 |  | 7383 | 26578800 | 58114800 | 89650800 | 121186800
2041-01-21 16:01 | 2871.32 | 1 | 61.1925 | 59.8258 | 841.5008 |  | 7384 | 26582400 | 58118400 | 89654400 | 121190400
2041-01-22 17:01 | 2921.16 | 1 | 85.1002 | 59.8258 | 856.1075 |  | 7385 | 26586000 | 58122000 | 89658000 | 121194000
2041-01-23 18:01 | 0 | 0 | 61.7301 | 59.8258 | 0 |  | 7386 | 26589600 | 58125600 | 89661600 | 121197600
2041-01-24 19:01 | -843.494 | 2.7519 | 60.0581 | 59.8258 | -247.2037 |  | 7387 | 26593200 | 58129200 | 89665200 | 121201200
2041-01-25 20:01 | -1707.3 | 5.1888 | 59.7246 | 59.8258 | -500.3602 |  | 7388 | 26596800 | 58132800 | 89668800 | 121204800
2041-01-26 21:01 | -2485.62 | 6.108 | 59.1647 | 59.8258 | -728.4633 |  | 7389 | 26600400 | 58136400 | 89672400 | 121208400
2041-01-27 22:01 | -3009.07 | 6.108 | 58.5328 | 59.8258 | -881.8714 |  | 7390 | 26604000 | 58140000 | 89676000 | 121212000
2041-01-28 23:01 | -3370.4 | 6.108 | 57.9975 | 59.8258 | -987.7667 |  | 7391 | 26607600 | 58143600 | 89679600 | 121215600
2041-01-30 00:01 | -4711.16 | 6.108 | 56.8048 | 59.8258 | -1380.7047 |  | 7392 | 26611200 | 58147200 | 89683200 | 121219200
2041-01-31 01:01 | -5171.92 | 6.108 | 56.1468 | 59.8258 | -1515.7401 |  | 7393 | 26614800 | 58150800 | 89686800 | 121222800
2041-02-01 02:01 | -5433.87 | 6.108 | 55.685 | 59.8258 | -1592.5101 |  | 7394 | 26618400 | 58154400 | 89690400 | 121226400
2041-02-02 03:01 | -5632.71 | 6.108 | 55.3244 | 59.8258 | -1650.7843 |  | 7395 | 26622000 | 58158000 | 89694000 | 121230000
2041-02-03 04:01 | -5544.41 | 6.108 | 55.1963 | 59.8258 | -1624.9062 |  | 7396 | 26625600 | 58161600 | 89697600 | 121233600
2041-02-04 05:01 | -5351.29 | 6.108 | 55.1881 | 59.8258 | -1568.3083 |  | 7397 | 26629200 | 58165200 | 89701200 | 121237200
2041-02-05 06:01 | -4942.63 | 6.108 | 55.4345 | 59.8258 | -1448.5419 |  | 7398 | 26632800 | 58168800 | 89704800 | 121240800
2041-02-06 07:01 | -4280.97 | 6.108 | 55.9183 | 59.8258 | -1254.6285 |  | 7399 | 26636400 | 58172400 | 89708400 | 121244400
2041-02-07 08:01 | -2813.32 | 6.108 | 57.0634 | 59.8258 | -824.5027 |  | 7400 | 26640000 | 58176000 | 89712000 | 121248000
2041-02-08 09:01 | -1630.93 | 4.7997 | 57.8138 | 59.8258 | -477.9784 |  | 7401 | 26643600 | 58179600 | 89715600 | 121251600
2041-02-09 10:01 | 0 | 1 | 59.6159 | 59.8258 | 0 |  | 7402 | 26647200 | 58183200 | 89719200 | 121255200
2041-02-10 11:01 | 2986.42 | 1 | 77.9037 | 59.8258 | 875.2333 |  | 7403 | 26650800 | 58186800 | 89722800 | 121258800
2041-02-11 12:01 | 4486.51 | 1.4519 | 74.6516 | 59.8258 | 1314.8663 |  | 7404 | 26654400 | 58190400 | 89726400 | 121262400
2041-02-12 13:01 | 5619.26 | 1.8077 | 75.3037 | 59.8258 | 1646.8425 |  | 7405 | 26658000 | 58194000 | 89730000 | 121266000
2041-02-13 14:01 | 5827.46 | 1.8766 | 75.7902 | 59.8258 | 1707.8599 |  | 7406 | 26661600 | 58197600 | 89733600 | 121269600
2041-02-14 15:01 | 6019.31 | 1.918 | 76.3283 | 59.8258 | 1764.0856 |  | 7407 | 26665200 | 58201200 | 89737200 | 121273200
2041-02-15 16:01 | 5537.58 | 1.7846 | 76.4948 | 59.8258 | 1622.9045 |  | 7408 | 26668800 | 58204800 | 89740800 | 121276800
2041-02-16 17:01 | 3691.65 | 1.1939 | 76.6242 | 59.8258 | 1081.9158 |  | 7409 | 26672400 | 58208400 | 89744400 | 121280400
2041-02-17 18:01 | 3004.28 | 1 | 81.2007 | 59.8258 | 880.4676 |  | 7410 | 26676000 | 58212000 | 89748000 | 121284000
2041-02-18 19:01 | 3010.36 | 1 | 62.0845 | 59.8258 | 882.2494 |  | 7411 | 26679600 | 58215600 | 89751600 | 121287600
2041-02-19 20:01 | 0 | 0 | 62.3846 | 59.8258 | 0 |  | 7412 | 26683200 | 58219200 | 89755200 | 121291200
2041-02-20 21:01 | -1267.75 | 3.8927 | 60.5233 | 59.8258 | -371.5408 |  | 7413 | 26686800 | 58222800 | 89758800 | 121294800
2041-02-21 22:01 | -1939.02 | 5.7208 | 60.0909 | 59.8258 | -568.2707 |  | 7414 | 26690400 | 58226400 | 89762400 | 121298400
2041-02-22 23:01 | -3238.76 | 6.108 | 58.9414 | 59.8258 | -949.1869 |  | 7415 | 26694000 | 58230000 | 89766000 | 121302000
2041-02-24 00:01 | -3867.6 | 6.108 | 58.1109 | 59.8258 | -1133.4817 |  | 7416 | 26697600 | 58233600 | 89769600 | 121305600
2041-02-25 01:01 | -4274.85 | 6.108 | 57.4485 | 59.8258 | -1252.8349 |  | 7417 | 26701200 | 58237200 | 89773200 | 121309200
2041-02-26 02:01 | -4460.57 | 6.108 | 57.0458 | 59.8258 | -1307.264 |  | 7418 | 26704800 | 58240800 | 89776800 | 121312800
2041-02-27 03:01 | -4661.73 | 6.108 | 56.6796 | 59.8258 | -1366.2182 |  | 7419 | 26708400 | 58244400 | 89780400 | 121316400
2041-02-28 04:01 | -4680.27 | 6.108 | 56.4674 | 59.8258 | -1371.6517 |  | 7420 | 26712000 | 58248000 | 89784000 | 121320000
2041-03-01 05:01 | -4589.75 | 6.108 | 56.4018 | 59.8258 | -1345.1229 |  | 7421 | 26715600 | 58251600 | 89787600 | 121323600
2041-03-02 06:01 | -4309.23 | 6.108 | 56.5179 | 59.8258 | -1262.9106 |  | 7422 | 26719200 | 58255200 | 89791200 | 121327200
2041-03-03 07:01 | -3700.44 | 6.108 | 56.9134 | 59.8258 | -1084.4919 |  | 7423 | 26722800 | 58258800 | 89794800 | 121330800
2041-03-04 08:01 | -2245.55 | 6.108 | 58.03 | 59.8258 | -658.1057 |  | 7424 | 26726400 | 58262400 | 89798400 | 121334400
2041-03-05 09:01 | -1809.25 | 5.2626 | 58.3295 | 59.8258 | -530.2388 |  | 7425 | 26730000 | 58266000 | 89802000 | 121338000
2041-03-06 10:01 | -827.958 | 2.4771 | 58.5099 | 59.8258 | -242.6505 |  | 7426 | 26733600 | 58269600 | 89805600 | 121341600
2041-03-07 11:01 | -512.833 | 1.8317 | 58.9424 | 59.8258 | -150.2965 |  | 7427 | 26737200 | 58273200 | 89809200 | 121345200
2041-03-08 12:01 | -177.104 | 0.93105 | 59.4989 | 59.8258 | -51.9041 |  | 7428 | 26740800 | 58276800 | 89812800 | 121348800
2041-03-09 13:01 | 44.3044 | 1 | 60.4916 | 59.8258 | 12.9843 |  | 7429 | 26744400 | 58280400 | 89816400 | 121352400
2041-03-10 14:01 | 30.6016 | 1 | 60.5835 | 59.8258 | 8.9684 |  | 7430 | 26748000 | 58284000 | 89820000 | 121356000
2041-03-11 15:01 | 2802.34 | 1 | 60.3927 | 59.8258 | 821.2848 |  | 7431 | 26751600 | 58287600 | 89823600 | 121359600
2041-03-12 16:01 | 3163.05 | 1 | 60.7658 | 59.8258 | 926.9984 |  | 7432 | 26755200 | 58291200 | 89827200 | 121363200
2041-03-13 17:01 | 3074.13 | 1 | 61.0761 | 59.8258 | 900.9386 |  | 7433 | 26758800 | 58294800 | 89830800 | 121366800
2041-03-14 18:01 | 2930.83 | 1 | 61.2658 | 59.8258 | 858.9415 |  | 7434 | 26762400 | 58298400 | 89834400 | 121370400
2041-03-15 19:01 | -202.562 | 1.1432 | 60.8572 | 59.8258 | -59.3651 |  | 7435 | 26766000 | 58302000 | 89838000 | 121374000
2041-03-16 20:01 | -627.022 | 2.2451 | 60.1212 | 59.8258 | -183.762 |  | 7436 | 26769600 | 58305600 | 89841600 | 121377600
2041-03-17 21:01 | -1575.44 | 4.8572 | 59.7184 | 59.8258 | -461.7159 |  | 7437 | 26773200 | 58309200 | 89845200 | 121381200
2041-03-18 22:01 | -2018.52 | 5.907 | 59.431 | 59.8258 | -591.5698 |  | 7438 | 26776800 | 58312800 | 89848800 | 121384800
2041-03-19 23:01 | -3045.26 | 6.108 | 58.5225 | 59.8258 | -892.4776 |  | 7439 | 26780400 | 58316400 | 89852400 | 121388400
2041-03-21 00:01 | -3399.86 | 6.108 | 57.9902 | 59.8258 | -996.4006 |  | 7440 | 26784000 | 58320000 | 89856000 | 121392000
2041-03-22 01:01 | -3657.55 | 6.108 | 57.629 | 59.8258 | -1071.9221 |  | 7441 | 26787600 | 58323600 | 89859600 | 121395600
2041-03-23 02:01 | -3835.56 | 6.108 | 57.3599 | 59.8258 | -1124.0917 |  | 7442 | 26791200 | 58327200 | 89863200 | 121399200
2041-03-24 03:01 | -3961.68 | 6.108 | 57.1239 | 59.8258 | -1161.0538 |  | 7443 | 26794800 | 58330800 | 89866800 | 121402800
2041-03-25 04:01 | -4060.11 | 6.108 | 56.9165 | 59.8258 | -1189.9008 |  | 7444 | 26798400 | 58334400 | 89870400 | 121406400
2041-03-26 05:01 | -4189.5 | 6.108 | 56.7091 | 59.8258 | -1227.8212 |  | 7445 | 26802000 | 58338000 | 89874000 | 121410000
2041-03-27 06:01 | -4046.56 | 6.108 | 56.7048 | 59.8258 | -1185.9297 |  | 7446 | 26805600 | 58341600 | 89877600 | 121413600
2041-03-28 07:01 | -3638.23 | 6.108 | 56.963 | 59.8258 | -1066.26 |  | 7447 | 26809200 | 58345200 | 89881200 | 121417200
2041-03-29 08:01 | -2210.17 | 6.108 | 58.0293 | 59.8258 | -647.7369 |  | 7448 | 26812800 | 58348800 | 89884800 | 121420800
2041-03-30 09:01 | -1394.61 | 4.0511 | 58.2765 | 59.8258 | -408.7198 |  | 7449 | 26816400 | 58352400 | 89888400 | 121424400
2041-03-31 10:01 | 0 | 1 | 60.03 | 59.8258 | 0 |  | 7450 | 26820000 | 58356000 | 89892000 | 121428000
2041-04-01 11:01 | 3036.33 | 1 | 60.0319 | 59.8258 | 889.8605 |  | 7451 | 26823600 | 58359600 | 89895600 | 121431600
2041-04-02 12:01 | 3379.6 | 1.1193 | 74.7176 | 59.8258 | 990.463 |  | 7452 | 26827200 | 58363200 | 89899200 | 121435200
2041-04-03 13:01 | 4236.24 | 1.3999 | 75.0866 | 59.8258 | 1241.5194 |  | 7453 | 26830800 | 58366800 | 89902800 | 121438800
2041-04-04 14:01 | 4253.26 | 1.4172 | 75.319 | 59.8258 | 1246.5075 |  | 7454 | 26834400 | 58370400 | 89906400 | 121442400
2041-04-05 15:01 | 3966.66 | 1.3298 | 75.4922 | 59.8258 | 1162.5133 |  | 7455 | 26838000 | 58374000 | 89910000 | 121446000
2041-04-06 16:01 | 3617.05 | 1.2194 | 75.5712 | 59.8258 | 1060.0527 |  | 7456 | 26841600 | 58377600 | 89913600 | 121449600
2041-04-07 17:01 | 2940.34 | 1 | 61.8096 | 59.8258 | 861.7286 |  | 7457 | 26845200 | 58381200 | 89917200 | 121453200
2041-04-08 18:01 | 2896.92 | 1 | 61.8183 | 59.8258 | 849.0034 |  | 7458 | 26848800 | 58384800 | 89920800 | 121456800
2041-04-09 19:01 | -382.557 | 1.6228 | 61.0335 | 59.8258 | -112.1164 |  | 7459 | 26852400 | 58388400 | 89924400 | 121460400
2041-04-10 20:01 | -1058.43 | 3.4121 | 60.3087 | 59.8258 | -310.1952 |  | 7460 | 26856000 | 58392000 | 89928000 | 121464000
2041-04-11 21:01 | -2406 | 6.108 | 59.6481 | 59.8258 | -705.129 |  | 7461 | 26859600 | 58395600 | 89931600 | 121467600
2041-04-12 22:01 | -3071.92 | 6.108 | 58.8331 | 59.8258 | -900.2909 |  | 7462 | 26863200 | 58399200 | 89935200 | 121471200
2041-04-13 23:01 | -4095.01 | 6.108 | 57.7519 | 59.8258 | -1200.129 |  | 7463 | 26866800 | 58402800 | 89938800 | 121474800
2041-04-15 00:01 | -4482.9 | 6.108 | 57.0936 | 59.8258 | -1313.8083 |  | 7464 | 26870400 | 58406400 | 89942400 | 121478400
2041-04-16 01:01 | -4915.33 | 6.108 | 56.4987 | 59.8258 | -1440.541 |  | 7465 | 26874000 | 58410000 | 89946000 | 121482000
2041-04-17 02:01 | -5193.59 | 6.108 | 56.0347 | 59.8258 | -1522.091 |  | 7466 | 26877600 | 58413600 | 89949600 | 121485600
2041-04-18 03:01 | -5444.13 | 6.108 | 55.6271 | 59.8258 | -1595.517 |  | 7467 | 26881200 | 58417200 | 89953200 | 121489200
2041-04-19 04:01 | -5149.94 | 6.108 | 55.6436 | 59.8258 | -1509.2984 |  | 7468 | 26884800 | 58420800 | 89956800 | 121492800
2041-04-20 05:01 | -4808.82 | 6.108 | 55.7917 | 59.8258 | -1409.326 |  | 7469 | 26888400 | 58424400 | 89960400 | 121496400
2041-04-21 06:01 | -4146.22 | 6.108 | 56.2268 | 59.8258 | -1215.1371 |  | 7470 | 26892000 | 58428000 | 89964000 | 121500000
2041-04-22 07:01 | -4023.22 | 6.108 | 56.3596 | 59.8258 | -1179.0894 |  | 7471 | 26895600 | 58431600 | 89967600 | 121503600
2041-04-23 08:01 | -3500.55 | 6.108 | 56.7573 | 59.8258 | -1025.9099 |  | 7472 | 26899200 | 58435200 | 89971200 | 121507200
2041-04-24 09:01 | -3861.44 | 6.108 | 56.5482 | 59.8258 | -1131.6764 |  | 7473 | 26902800 | 58438800 | 89974800 | 121510800
2041-04-25 10:01 | -3201.06 | 6.108 | 57.0061 | 59.8258 | -938.1381 |  | 7474 | 26906400 | 58442400 | 89978400 | 121514400
2041-04-26 11:01 | -1875.58 | 5.542 | 57.8911 | 59.8258 | -549.6782 |  | 7475 | 26910000 | 58446000 | 89982000 | 121518000
2041-04-27 12:01 | 0 | 0 | 59.6158 | 59.8258 | 0 |  | 7476 | 26913600 | 58449600 | 89985600 | 121521600
2041-04-28 13:01 | 2862.28 | 1 | 59.6944 | 59.8258 | 838.8515 |  | 7477 | 26917200 | 58453200 | 89989200 | 121525200
2041-04-29 14:01 | 3079.34 | 1 | 60.2369 | 59.8258 | 902.4655 |  | 7478 | 26920800 | 58456800 | 89992800 | 121528800
2041-04-30 15:01 | -137.315 | 0.96254 | 60.224 | 59.8258 | -40.2431 |  | 7479 | 26924400 | 58460400 | 89996400 | 121532400
2041-05-01 16:01 | 880.835 | 1 | 60.6007 | 59.8258 | 258.1473 |  | 7480 | 26928000 | 58464000 | 90000000 | 121536000
2041-05-02 17:01 | 264.895 | 1 | 60.7401 | 59.8258 | 77.6331 |  | 7481 | 26931600 | 58467600 | 90003600 | 121539600
2041-05-03 18:01 | -73.8096 | 0.76855 | 60.3321 | 59.8258 | -21.6315 |  | 7482 | 26935200 | 58471200 | 90007200 | 121543200
2041-05-04 19:01 | -654.037 | 2.3702 | 59.4343 | 59.8258 | -191.6793 |  | 7483 | 26938800 | 58474800 | 90010800 | 121546800
2041-05-05 20:01 | -1053.9 | 3.3829 | 59.1556 | 59.8258 | -308.8676 |  | 7484 | 26942400 | 58478400 | 90014400 | 121550400
2041-05-06 21:01 | -2018.45 | 6.08 | 59.0289 | 59.8258 | -591.5493 |  | 7485 | 26946000 | 58482000 | 90018000 | 121554000
2041-05-07 22:01 | -2449.83 | 6.108 | 58.5638 | 59.8258 | -717.9743 |  | 7486 | 26949600 | 58485600 | 90021600 | 121557600
2041-05-08 23:01 | -3385.9 | 6.108 | 57.7324 | 59.8258 | -992.3093 |  | 7487 | 26953200 | 58489200 | 90025200 | 121561200
2041-05-10 00:01 | -3639.47 | 6.108 | 57.3324 | 59.8258 | -1066.6234 |  | 7488 | 26956800 | 58492800 | 90028800 | 121564800
2041-05-11 01:01 | -3848.9 | 6.108 | 56.9841 | 59.8258 | -1128.0012 |  | 7489 | 26960400 | 58496400 | 90032400 | 121568400
2041-05-12 02:01 | -4071.36 | 6.108 | 56.6531 | 59.8258 | -1193.1978 |  | 7490 | 26964000 | 58500000 | 90036000 | 121572000
2041-05-13 03:01 | -4176.23 | 6.108 | 56.4608 | 59.8258 | -1223.9322 |  | 7491 | 26967600 | 58503600 | 90039600 | 121575600
2041-05-14 04:01 | -4115.01 | 6.108 | 56.395 | 59.8258 | -1205.9904 |  | 7492 | 26971200 | 58507200 | 90043200 | 121579200
2041-05-15 05:01 | -4020.12 | 6.108 | 56.4028 | 59.8258 | -1178.1809 |  | 7493 | 26974800 | 58510800 | 90046800 | 121582800
2041-05-16 06:01 | -3608.56 | 6.108 | 56.6651 | 59.8258 | -1057.5645 |  | 7494 | 26978400 | 58514400 | 90050400 | 121586400
2041-05-17 07:01 | -3215.55 | 6.108 | 56.9707 | 59.8258 | -942.3847 |  | 7495 | 26982000 | 58518000 | 90054000 | 121590000
2041-05-18 08:01 | -2802.47 | 6.108 | 57.3172 | 59.8258 | -821.3229 |  | 7496 | 26985600 | 58521600 | 90057600 | 121593600
2041-05-19 09:01 | -2242.48 | 6.108 | 57.8038 | 59.8258 | -657.206 |  | 7497 | 26989200 | 58525200 | 90061200 | 121597200
2041-05-20 10:01 | -2037.76 | 5.959 | 58.0176 | 59.8258 | -597.2085 |  | 7498 | 26992800 | 58528800 | 90064800 | 121600800
2041-05-21 11:01 | -1401.71 | 4.0926 | 58.0805 | 59.8258 | -410.8006 |  | 7499 | 26996400 | 58532400 | 90068400 | 121604400
2041-05-22 12:01 | -895.179 | 2.7943 | 58.2827 | 59.8258 | -262.3511 |  | 7500 | 27000000 | 58536000 | 90072000 | 121608000
2041-05-23 13:01 | -670.71 | 2.2653 | 58.495 | 59.8258 | -196.5657 |  | 7501 | 27003600 | 58539600 | 90075600 | 121611600
2041-05-24 14:01 | -762.955 | 2.5788 | 58.5686 | 59.8258 | -223.6 |  | 7502 | 27007200 | 58543200 | 90079200 | 121615200
2041-05-25 15:01 | -929.488 | 3.0298 | 58.5546 | 59.8258 | -272.406 |  | 7503 | 27010800 | 58546800 | 90082800 | 121618800
2041-05-26 16:01 | -223.628 | 0.95447 | 58.8852 | 59.8258 | -65.5389 |  | 7504 | 27014400 | 58550400 | 90086400 | 121622400
2041-05-27 17:01 | 405.704 | 1 | 60.0296 | 59.8258 | 118.9001 |  | 7505 | 27018000 | 58554000 | 90090000 | 121626000
2041-05-28 18:01 | 2210.91 | 1 | 60.0138 | 59.8258 | 647.9538 |  | 7506 | 27021600 | 58557600 | 90093600 | 121629600
2041-05-29 19:01 | 174.107 | 1 | 60.5289 | 59.8258 | 51.0257 |  | 7507 | 27025200 | 58561200 | 90097200 | 121633200
2041-05-30 20:01 | -79.2097 | 0.78045 | 60.0174 | 59.8258 | -23.2141 |  | 7508 | 27028800 | 58564800 | 90100800 | 121636800
2041-05-31 21:01 | -753.933 | 2.6603 | 59.1539 | 59.8258 | -220.956 |  | 7509 | 27032400 | 58568400 | 90104400 | 121640400
2041-06-01 22:01 | -1058.29 | 3.3767 | 58.9673 | 59.8258 | -310.1542 |  | 7510 | 27036000 | 58572000 | 90108000 | 121644000
2041-06-02 23:01 | -1832.46 | 5.5543 | 58.8402 | 59.8258 | -537.041 |  | 7511 | 27039600 | 58575600 | 90111600 | 121647600
2041-06-04 00:01 | -2355.24 | 6.108 | 58.4234 | 59.8258 | -690.2527 |  | 7512 | 27043200 | 58579200 | 90115200 | 121651200
2041-06-05 01:01 | -2456.92 | 6.108 | 58.2142 | 59.8258 | -720.0522 |  | 7513 | 27046800 | 58582800 | 90118800 | 121654800
2041-06-06 02:01 | -2580.96 | 6.108 | 58.0401 | 59.8258 | -756.4047 |  | 7514 | 27050400 | 58586400 | 90122400 | 121658400
2041-06-07 03:01 | -2602.79 | 6.108 | 57.9686 | 59.8258 | -762.8025 |  | 7515 | 27054000 | 58590000 | 90126000 | 121662000
2041-06-08 04:01 | -2604.58 | 6.108 | 57.9173 | 59.8258 | -763.327 |  | 7516 | 27057600 | 58593600 | 90129600 | 121665600
2041-06-09 05:01 | -2599.16 | 6.108 | 57.8851 | 59.8258 | -761.7386 |  | 7517 | 27061200 | 58597200 | 90133200 | 121669200
2041-06-10 06:01 | -2556.87 | 6.108 | 57.8686 | 59.8258 | -749.3446 |  | 7518 | 27064800 | 58600800 | 90136800 | 121672800
2041-06-11 07:01 | -1847.51 | 5.401 | 58.1962 | 59.8258 | -541.4517 |  | 7519 | 27068400 | 58604400 | 90140400 | 121676400
2041-06-12 08:01 | -1348.02 | 3.9806 | 58.2826 | 59.8258 | -395.0657 |  | 7520 | 27072000 | 58608000 | 90144000 | 121680000
2041-06-13 09:01 | -1758.17 | 5.3092 | 58.4226 | 59.8258 | -515.2688 |  | 7521 | 27075600 | 58611600 | 90147600 | 121683600
2041-06-14 10:01 | -1559.93 | 4.6027 | 58.3775 | 59.8258 | -457.1704 |  | 7522 | 27079200 | 58615200 | 90151200 | 121687200
2041-06-15 11:01 | -988.184 | 3.0075 | 58.4467 | 59.8258 | -289.6081 |  | 7523 | 27082800 | 58618800 | 90154800 | 121690800
2041-06-16 12:01 | -557.277 | 1.9132 | 58.717 | 59.8258 | -163.3218 |  | 7524 | 27086400 | 58622400 | 90158400 | 121694400
2041-06-17 13:01 | -448.778 | 1.7022 | 58.9384 | 59.8258 | -131.5238 |  | 7525 | 27090000 | 58626000 | 90162000 | 121698000
2041-06-18 14:01 | -608.303 | 2.1768 | 58.9214 | 59.8258 | -178.276 |  | 7526 | 27093600 | 58629600 | 90165600 | 121701600
2041-06-19 15:01 | -737.448 | 2.504 | 58.88 | 59.8258 | -216.1247 |  | 7527 | 27097200 | 58633200 | 90169200 | 121705200
2041-06-20 16:01 | -924.834 | 3.013 | 58.826 | 59.8258 | -271.0421 |  | 7528 | 27100800 | 58636800 | 90172800 | 121708800
2041-06-21 17:01 | 0 | 1 | 60.2086 | 59.8258 | 0 |  | 7529 | 27104400 | 58640400 | 90176400 | 121712400
2041-06-22 18:01 | -502.266 | 1.9725 | 59.1407 | 59.8258 | -147.1996 |  | 7530 | 27108000 | 58644000 | 90180000 | 121716000
2041-06-23 19:01 | -948.329 | 3.1267 | 58.9117 | 59.8258 | -277.9278 |  | 7531 | 27111600 | 58647600 | 90183600 | 121719600
2041-06-24 20:01 | -1398.92 | 4.3255 | 58.7531 | 59.8258 | -409.983 |  | 7532 | 27115200 | 58651200 | 90187200 | 121723200
2041-06-25 21:01 | -1657.26 | 4.967 | 58.6369 | 59.8258 | -485.695 |  | 7533 | 27118800 | 58654800 | 90190800 | 121726800
2041-06-26 22:01 | -1838.66 | 5.4382 | 58.5597 | 59.8258 | -538.8581 |  | 7534 | 27122400 | 58658400 | 90194400 | 121730400
2041-06-27 23:01 | -1952.49 | 5.7306 | 58.4781 | 59.8258 | -572.2183 |  | 7535 | 27126000 | 58662000 | 90198000 | 121734000
2041-06-29 00:01 | -3354 | 6.108 | 57.4712 | 59.8258 | -982.9604 |  | 7536 | 27129600 | 58665600 | 90201600 | 121737600
2041-06-30 01:01 | -3749.8 | 6.108 | 56.9505 | 59.8258 | -1098.9579 |  | 7537 | 27133200 | 58669200 | 90205200 | 121741200
2041-07-01 02:01 | -3931.55 | 6.108 | 56.6337 | 59.8258 | -1152.2236 |  | 7538 | 27136800 | 58672800 | 90208800 | 121744800
2041-07-02 03:01 | -4144.64 | 6.108 | 56.3475 | 59.8258 | -1214.6741 |  | 7539 | 27140400 | 58676400 | 90212400 | 121748400
2041-07-03 04:01 | -4254.32 | 6.108 | 56.1401 | 59.8258 | -1246.8181 |  | 7540 | 27144000 | 58680000 | 90216000 | 121752000
2041-07-04 05:01 | -4339.36 | 6.108 | 55.9464 | 59.8258 | -1271.7409 |  | 7541 | 27147600 | 58683600 | 90219600 | 121755600
2041-07-05 06:01 | -4400.87 | 6.108 | 55.8084 | 59.8258 | -1289.7677 |  | 7542 | 27151200 | 58687200 | 90223200 | 121759200
2041-07-06 07:01 | -3639.32 | 6.108 | 56.2943 | 59.8258 | -1066.5794 |  | 7543 | 27154800 | 58690800 | 90226800 | 121762800
2041-07-07 08:01 | -3080.61 | 6.108 | 56.7411 | 59.8258 | -902.8377 |  | 7544 | 27158400 | 58694400 | 90230400 | 121766400
2041-07-08 09:01 | -3608.14 | 6.108 | 56.4153 | 59.8258 | -1057.4415 |  | 7545 | 27162000 | 58698000 | 90234000 | 121770000
2041-07-09 10:01 | -3355.55 | 6.108 | 56.5409 | 59.8258 | -983.4146 |  | 7546 | 27165600 | 58701600 | 90237600 | 121773600
2041-07-10 11:01 | -2987.85 | 6.108 | 56.789 | 59.8258 | -875.6524 |  | 7547 | 27169200 | 58705200 | 90241200 | 121777200
2041-07-11 12:01 | -2644.62 | 6.108 | 57.0845 | 59.8258 | -775.0616 |  | 7548 | 27172800 | 58708800 | 90244800 | 121780800
2041-07-12 13:01 | -2600.93 | 6.108 | 57.1575 | 59.8258 | -762.2573 |  | 7549 | 27176400 | 58712400 | 90248400 | 121784400
2041-07-13 14:01 | -2684.57 | 6.108 | 57.0997 | 59.8258 | -786.7698 |  | 7550 | 27180000 | 58716000 | 90252000 | 121788000
2041-07-14 15:01 | -2910.19 | 6.108 | 56.9253 | 59.8258 | -852.8925 |  | 7551 | 27183600 | 58719600 | 90255600 | 121791600
2041-07-15 16:01 | -2990.07 | 6.108 | 56.8274 | 59.8258 | -876.303 |  | 7552 | 27187200 | 58723200 | 90259200 | 121795200
2041-07-16 17:01 | -1813.09 | 5.3748 | 57.4759 | 59.8258 | -531.3642 |  | 7553 | 27190800 | 58726800 | 90262800 | 121798800
2041-07-17 18:01 | -2302.24 | 6.108 | 57.4177 | 59.8258 | -674.7199 |  | 7554 | 27194400 | 58730400 | 90266400 | 121802400
2041-07-18 19:01 | -2762.11 | 6.108 | 57.0682 | 59.8258 | -809.4945 |  | 7555 | 27198000 | 58734000 | 90270000 | 121806000
2041-07-19 20:01 | -3214.73 | 6.108 | 56.6491 | 59.8258 | -942.1444 |  | 7556 | 27201600 | 58737600 | 90273600 | 121809600
2041-07-20 21:01 | -3478.2 | 6.108 | 56.3707 | 59.8258 | -1019.3598 |  | 7557 | 27205200 | 58741200 | 90277200 | 121813200
2041-07-21 22:01 | -3634.3 | 6.108 | 56.1814 | 59.8258 | -1065.1082 |  | 7558 | 27208800 | 58744800 | 90280800 | 121816800
2041-07-22 23:01 | -3671.57 | 6.108 | 56.0647 | 59.8258 | -1076.0309 |  | 7559 | 27212400 | 58748400 | 90284400 | 121820400
2041-07-24 00:01 | -5031.06 | 6.108 | 54.9897 | 59.8258 | -1474.4581 |  | 7560 | 27216000 | 58752000 | 90288000 | 121824000
2041-07-25 01:01 | -5246.22 | 6.108 | 54.6048 | 59.8258 | -1537.5153 |  | 7561 | 27219600 | 58755600 | 90291600 | 121827600
2041-07-26 02:01 | -5436.19 | 6.108 | 54.3025 | 59.8258 | -1593.19 |  | 7562 | 27223200 | 58759200 | 90295200 | 121831200
2041-07-27 03:01 | -5505.76 | 6.108 | 54.1338 | 59.8258 | -1613.579 |  | 7563 | 27226800 | 58762800 | 90298800 | 121834800
2041-07-28 04:01 | -5527.5 | 6.108 | 54.0147 | 59.8258 | -1619.9503 |  | 7564 | 27230400 | 58766400 | 90302400 | 121838400
2041-07-29 05:01 | -5565.36 | 6.108 | 53.8785 | 59.8258 | -1631.046 |  | 7565 | 27234000 | 58770000 | 90306000 | 121842000
2041-07-30 06:01 | -5538.6 | 6.108 | 53.825 | 59.8258 | -1623.2034 |  | 7566 | 27237600 | 58773600 | 90309600 | 121845600
2041-07-31 07:01 | -4600.82 | 6.108 | 54.4629 | 59.8258 | -1348.3672 |  | 7567 | 27241200 | 58777200 | 90313200 | 121849200
2041-08-01 08:01 | -3943.11 | 6.108 | 55.0229 | 59.8258 | -1155.6115 |  | 7568 | 27244800 | 58780800 | 90316800 | 121852800
2041-08-02 09:01 | -4305.8 | 6.108 | 54.8621 | 59.8258 | -1261.9054 |  | 7569 | 27248400 | 58784400 | 90320400 | 121856400
2041-08-03 10:01 | -3912.26 | 6.108 | 55.1451 | 59.8258 | -1146.5702 |  | 7570 | 27252000 | 58788000 | 90324000 | 121860000
2041-08-04 11:01 | -3157.85 | 6.108 | 55.7438 | 59.8258 | -925.4745 |  | 7571 | 27255600 | 58791600 | 90327600 | 121863600
2041-08-05 12:01 | -2656.86 | 6.108 | 56.2542 | 59.8258 | -778.6488 |  | 7572 | 27259200 | 58795200 | 90331200 | 121867200
2041-08-06 13:01 | -2340.85 | 6.108 | 56.614 | 59.8258 | -686.0354 |  | 7573 | 27262800 | 58798800 | 90334800 | 121870800
2041-08-07 14:01 | -2183.83 | 6.108 | 56.8309 | 59.8258 | -640.0174 |  | 7574 | 27266400 | 58802400 | 90338400 | 121874400
2041-08-08 15:01 | -2053.71 | 6.0853 | 57.023 | 59.8258 | -601.883 |  | 7575 | 27270000 | 58806000 | 90342000 | 121878000
2041-08-09 16:01 | -2042.49 | 6.0394 | 57.1079 | 59.8258 | -598.5947 |  | 7576 | 27273600 | 58809600 | 90345600 | 121881600
2041-08-10 17:01 | -858.308 | 2.5308 | 57.1507 | 59.8258 | -251.5452 |  | 7577 | 27277200 | 58813200 | 90349200 | 121885200
2041-08-11 18:01 | -1131.54 | 3.6671 | 57.498 | 59.8258 | -331.6216 |  | 7578 | 27280800 | 58816800 | 90352800 | 121888800
2041-08-12 19:01 | -1424.08 | 4.4169 | 57.524 | 59.8258 | -417.3566 |  | 7579 | 27284400 | 58820400 | 90356400 | 121892400
2041-08-13 20:01 | -1628.67 | 4.9477 | 57.5114 | 59.8258 | -477.3161 |  | 7580 | 27288000 | 58824000 | 90360000 | 121896000
2041-08-14 21:01 | -1745.66 | 5.2406 | 57.5151 | 59.8258 | -511.6024 |  | 7581 | 27291600 | 58827600 | 90363600 | 121899600
2041-08-15 22:01 | -1887.3 | 5.6297 | 57.5313 | 59.8258 | -553.113 |  | 7582 | 27295200 | 58831200 | 90367200 | 121903200
2041-08-16 23:01 | -2051.31 | 6.0794 | 57.5088 | 59.8258 | -601.1796 |  | 7583 | 27298800 | 58834800 | 90370800 | 121906800
2041-08-18 00:01 | -3223.16 | 6.108 | 56.6294 | 59.8258 | -944.6149 |  | 7584 | 27302400 | 58838400 | 90374400 | 121910400
2041-08-19 01:01 | -3510.01 | 6.108 | 56.2639 | 59.8258 | -1028.6824 |  | 7585 | 27306000 | 58842000 | 90378000 | 121914000
2041-08-20 02:01 | -3744.63 | 6.108 | 55.9761 | 59.8258 | -1097.4427 |  | 7586 | 27309600 | 58845600 | 90381600 | 121917600
2041-08-21 03:01 | -3807.7 | 6.108 | 55.8438 | 59.8258 | -1115.9267 |  | 7587 | 27313200 | 58849200 | 90385200 | 121921200
2041-08-22 04:01 | -3633.98 | 6.108 | 55.907 | 59.8258 | -1065.0144 |  | 7588 | 27316800 | 58852800 | 90388800 | 121924800
2041-08-23 05:01 | -3483.41 | 6.108 | 55.9788 | 59.8258 | -1020.8867 |  | 7589 | 27320400 | 58856400 | 90392400 | 121928400
2041-08-24 06:01 | -3000.22 | 6.108 | 56.3417 | 59.8258 | -879.2777 |  | 7590 | 27324000 | 58860000 | 90396000 | 121932000
2041-08-25 07:01 | -2915.4 | 6.108 | 56.4589 | 59.8258 | -854.4194 |  | 7591 | 27327600 | 58863600 | 90399600 | 121935600
2041-08-26 08:01 | -2740.79 | 6.108 | 56.6227 | 59.8258 | -803.2463 |  | 7592 | 27331200 | 58867200 | 90403200 | 121939200
2041-08-27 09:01 | -2908.64 | 6.108 | 56.5368 | 59.8258 | -852.4382 |  | 7593 | 27334800 | 58870800 | 90406800 | 121942800
2041-08-28 10:01 | -2377.41 | 6.108 | 56.9305 | 59.8258 | -696.7501 |  | 7594 | 27338400 | 58874400 | 90410400 | 121946400
2041-08-29 11:01 | -1852.07 | 5.4771 | 57.2249 | 59.8258 | -542.7881 |  | 7595 | 27342000 | 58878000 | 90414000 | 121950000
2041-08-30 12:01 | -1406.61 | 4.1952 | 57.3413 | 59.8258 | -412.2367 |  | 7596 | 27345600 | 58881600 | 90417600 | 121953600
2041-08-31 13:01 | 0 | 0 | 58.9925 | 59.8258 | 0 |  | 7597 | 27349200 | 58885200 | 90421200 | 121957200
2041-09-01 14:01 | 2797.92 | 1 | 59.0084 | 59.8258 | 819.9894 |  | 7598 | 27352800 | 58888800 | 90424800 | 121960800
2041-09-02 15:01 | 3102.31 | 1 | 59.5355 | 59.8258 | 909.1973 |  | 7599 | 27356400 | 58892400 | 90428400 | 121964400
2041-09-03 16:01 | 3040.46 | 1 | 59.9152 | 59.8258 | 891.0709 |  | 7600 | 27360000 | 58896000 | 90432000 | 121968000
2041-09-04 17:01 | 0 | 0 | 60.4128 | 59.8258 | 0 |  | 7601 | 27363600 | 58899600 | 90435600 | 121971600
2041-09-05 18:01 | -622.55 | 2.0152 | 58.7873 | 59.8258 | -182.4514 |  | 7602 | 27367200 | 58903200 | 90439200 | 121975200
2041-09-06 19:01 | -1290 | 4.119 | 58.6258 | 59.8258 | -378.0617 |  | 7603 | 27370800 | 58906800 | 90442800 | 121978800
2041-09-07 20:01 | -1814.72 | 5.4644 | 58.3848 | 59.8258 | -531.8419 |  | 7604 | 27374400 | 58910400 | 90446400 | 121982400
2041-09-08 21:01 | -3082.54 | 6.108 | 57.4271 | 59.8258 | -903.4033 |  | 7605 | 27378000 | 58914000 | 90450000 | 121986000
2041-09-09 22:01 | -3662.58 | 6.108 | 56.6994 | 59.8258 | -1073.3962 |  | 7606 | 27381600 | 58917600 | 90453600 | 121989600
2041-09-10 23:01 | -4715.17 | 6.108 | 55.6959 | 59.8258 | -1381.8799 |  | 7607 | 27385200 | 58921200 | 90457200 | 121993200
2041-09-12 00:01 | -5174.52 | 6.108 | 55.0897 | 59.8258 | -1516.5021 |  | 7608 | 27388800 | 58924800 | 90460800 | 121996800
2041-09-13 01:01 | -5462.16 | 6.108 | 54.6315 | 59.8258 | -1600.8011 |  | 7609 | 27392400 | 58928400 | 90464400 | 122000400
2041-09-14 02:01 | -5700.85 | 6.108 | 54.2156 | 59.8258 | -1670.7542 |  | 7610 | 27396000 | 58932000 | 90468000 | 122004000
2041-09-15 03:01 | -5811.55 | 6.108 | 53.9213 | 59.8258 | -1703.1972 |  | 7611 | 27399600 | 58935600 | 90471600 | 122007600
2041-09-16 04:01 | -6039.9 | 6.108 | 53.5602 | 59.8258 | -1770.12 |  | 7612 | 27403200 | 58939200 | 90475200 | 122011200
2041-09-17 05:01 | -6118.6 | 6.108 | 53.3523 | 59.8258 | -1793.1846 |  | 7613 | 27406800 | 58942800 | 90478800 | 122014800
2041-09-18 06:01 | -6074.52 | 6.108 | 53.2569 | 59.8258 | -1780.2661 |  | 7614 | 27410400 | 58946400 | 90482400 | 122018400
2041-09-19 07:01 | -5560.2 | 6.108 | 53.5414 | 59.8258 | -1629.5338 |  | 7615 | 27414000 | 58950000 | 90486000 | 122022000
2041-09-20 08:01 | -4186.87 | 6.108 | 54.5476 | 59.8258 | -1227.0505 |  | 7616 | 27417600 | 58953600 | 90489600 | 122025600
2041-09-21 09:01 | -3085.17 | 6.108 | 55.5262 | 59.8258 | -904.1741 |  | 7617 | 27421200 | 58957200 | 90493200 | 122029200
2041-09-22 10:01 | -1655.35 | 4.9725 | 56.526 | 59.8258 | -485.1352 |  | 7618 | 27424800 | 58960800 | 90496800 | 122032800
2041-09-23 11:01 | -642.641 | 2.0105 | 56.888 | 59.8258 | -188.3395 |  | 7619 | 27428400 | 58964400 | 90500400 | 122036400
2041-09-24 12:01 | 937.873 | 1 | 58.5965 | 59.8258 | 274.8634 |  | 7620 | 27432000 | 58968000 | 90504000 | 122040000
2041-09-25 13:01 | 2927.6 | 1 | 58.8353 | 59.8258 | 857.9949 |  | 7621 | 27435600 | 58971600 | 90507600 | 122043600
2041-09-26 14:01 | 2915.11 | 1 | 59.3538 | 59.8258 | 854.3344 |  | 7622 | 27439200 | 58975200 | 90511200 | 122047200
2041-09-27 15:01 | 2897.73 | 1 | 59.6758 | 59.8258 | 849.2408 |  | 7623 | 27442800 | 58978800 | 90514800 | 122050800
2041-09-28 16:01 | 2883.97 | 1 | 59.897 | 59.8258 | 845.2082 |  | 7624 | 27446400 | 58982400 | 90518400 | 122054400
2041-09-29 17:01 | -422.095 | 1.7654 | 59.2666 | 59.8258 | -123.7038 |  | 7625 | 27450000 | 58986000 | 90522000 | 122058000
2041-09-30 18:01 | -903.531 | 3.0236 | 58.7224 | 59.8258 | -264.7988 |  | 7626 | 27453600 | 58989600 | 90525600 | 122061600
2041-10-01 19:01 | -1689.28 | 5.2008 | 58.4151 | 59.8258 | -495.0791 |  | 7627 | 27457200 | 58993200 | 90529200 | 122065200
2041-10-02 20:01 | -2407.01 | 6.108 | 57.9321 | 59.8258 | -705.425 |  | 7628 | 27460800 | 58996800 | 90532800 | 122068800
2041-10-03 21:01 | -3717.38 | 6.108 | 56.7434 | 59.8258 | -1089.4565 |  | 7629 | 27464400 | 59000400 | 90536400 | 122072400
2041-10-04 22:01 | -4364.59 | 6.108 | 55.9271 | 59.8258 | -1279.1351 |  | 7630 | 27468000 | 59004000 | 90540000 | 122076000
2041-10-05 23:01 | -5533.85 | 6.108 | 54.8026 | 59.8258 | -1621.8113 |  | 7631 | 27471600 | 59007600 | 90543600 | 122079600
2041-10-07 00:01 | -6051.16 | 6.108 | 54.0887 | 59.8258 | -1773.4199 |  | 7632 | 27475200 | 59011200 | 90547200 | 122083200
2041-10-08 01:01 | -6284.03 | 6.108 | 53.6053 | 59.8258 | -1841.6674 |  | 7633 | 27478800 | 59014800 | 90550800 | 122086800
2041-10-09 02:01 | -6449.24 | 6.108 | 53.2299 | 59.8258 | -1890.0857 |  | 7634 | 27482400 | 59018400 | 90554400 | 122090400
2041-10-10 03:01 | -6510.3 | 6.108 | 52.9724 | 59.8258 | -1907.9806 |  | 7635 | 27486000 | 59022000 | 90558000 | 122094000
2041-10-11 04:01 | -6505.02 | 6.108 | 52.79 | 59.8258 | -1906.4332 |  | 7636 | 27489600 | 59025600 | 90561600 | 122097600
2041-10-12 05:01 | -6391.66 | 6.108 | 52.7629 | 59.8258 | -1873.2106 |  | 7637 | 27493200 | 59029200 | 90565200 | 122101200
2041-10-13 06:01 | -6086.13 | 6.108 | 52.9127 | 59.8258 | -1783.6686 |  | 7638 | 27496800 | 59032800 | 90568800 | 122104800
2041-10-14 07:01 | -5585.74 | 6.108 | 53.2532 | 59.8258 | -1637.0188 |  | 7639 | 27500400 | 59036400 | 90572400 | 122108400
2041-10-15 08:01 | -4503.44 | 6.108 | 54.0792 | 59.8258 | -1319.828 |  | 7640 | 27504000 | 59040000 | 90576000 | 122112000
2041-10-16 09:01 | -3528.38 | 6.108 | 54.9445 | 59.8258 | -1034.0661 |  | 7641 | 27507600 | 59043600 | 90579600 | 122115600
2041-10-17 10:01 | -1994.51 | 6.0529 | 56.2635 | 59.8258 | -584.5332 |  | 7642 | 27511200 | 59047200 | 90583200 | 122119200
2041-10-18 11:01 | -1042.76 | 3.0965 | 56.5268 | 59.8258 | -305.6028 |  | 7643 | 27514800 | 59050800 | 90586800 | 122122800
2041-10-19 12:01 | 61.6458 | 1 | 58.3632 | 59.8258 | 18.0666 |  | 7644 | 27518400 | 59054400 | 90590400 | 122126400
2041-10-20 13:01 | 2865.58 | 1 | 58.432 | 59.8258 | 839.8186 |  | 7645 | 27522000 | 59058000 | 90594000 | 122130000
2041-10-21 14:01 | 2888.49 | 1 | 59.0044 | 59.8258 | 846.5329 |  | 7646 | 27525600 | 59061600 | 90597600 | 122133600
2041-10-22 15:01 | -248.677 | 1.2976 | 58.7382 | 59.8258 | -72.88 |  | 7647 | 27529200 | 59065200 | 90601200 | 122137200
2041-10-23 16:01 | -273.278 | 1.2668 | 58.4231 | 59.8258 | -80.0899 |  | 7648 | 27532800 | 59068800 | 90604800 | 122140800
2041-10-24 17:01 | -579.996 | 2.1539 | 58.1519 | 59.8258 | -169.98 |  | 7649 | 27536400 | 59072400 | 90608400 | 122144400
2041-10-25 18:01 | -808.544 | 2.7381 | 58.0517 | 59.8258 | -236.9609 |  | 7650 | 27540000 | 59076000 | 90612000 | 122148000
2041-10-26 19:01 | -1405.71 | 4.4307 | 57.8988 | 59.8258 | -411.9729 |  | 7651 | 27543600 | 59079600 | 90615600 | 122151600
2041-10-27 20:01 | -1780.68 | 5.3814 | 57.7203 | 59.8258 | -521.8658 |  | 7652 | 27547200 | 59083200 | 90619200 | 122155200
2041-10-28 21:01 | -2874.67 | 6.108 | 57.0291 | 59.8258 | -842.4826 |  | 7653 | 27550800 | 59086800 | 90622800 | 122158800
2041-10-29 22:01 | -3330.88 | 6.108 | 56.5149 | 59.8258 | -976.1846 |  | 7654 | 27554400 | 59090400 | 90626400 | 122162400
2041-10-30 23:01 | -4196.94 | 6.108 | 55.7137 | 59.8258 | -1230.0017 |  | 7655 | 27558000 | 59094000 | 90630000 | 122166000
2041-11-01 00:01 | -4525.27 | 6.108 | 55.259 | 59.8258 | -1326.2257 |  | 7656 | 27561600 | 59097600 | 90633600 | 122169600
2041-11-02 01:01 | -4697.38 | 6.108 | 54.9264 | 59.8258 | -1376.6662 |  | 7657 | 27565200 | 59101200 | 90637200 | 122173200
2041-11-03 02:01 | -4957.4 | 6.108 | 54.5636 | 59.8258 | -1452.8705 |  | 7658 | 27568800 | 59104800 | 90640800 | 122176800
2041-11-04 03:01 | -5025.85 | 6.108 | 54.3914 | 59.8258 | -1472.9312 |  | 7659 | 27572400 | 59108400 | 90644400 | 122180400
2041-11-05 04:01 | -4894.43 | 6.108 | 54.3916 | 59.8258 | -1434.4158 |  | 7660 | 27576000 | 59112000 | 90648000 | 122184000
2041-11-06 05:01 | -4870.92 | 6.108 | 54.3644 | 59.8258 | -1427.5257 |  | 7661 | 27579600 | 59115600 | 90651600 | 122187600
2041-11-07 06:01 | -4424.01 | 6.108 | 54.66 | 59.8258 | -1296.5493 |  | 7662 | 27583200 | 59119200 | 90655200 | 122191200
2041-11-08 07:01 | -4031.7 | 6.108 | 54.9752 | 59.8258 | -1181.5746 |  | 7663 | 27586800 | 59122800 | 90658800 | 122194800
2041-11-09 08:01 | -3012.08 | 6.108 | 55.7864 | 59.8258 | -882.7535 |  | 7664 | 27590400 | 59126400 | 90662400 | 122198400
2041-11-10 09:01 | -1948.89 | 5.848 | 56.6726 | 59.8258 | -571.1633 |  | 7665 | 27594000 | 59130000 | 90666000 | 122202000
2041-11-11 10:01 | -652.357 | 1.9512 | 56.8783 | 59.8258 | -191.187 |  | 7666 | 27597600 | 59133600 | 90669600 | 122205600
2041-11-12 11:01 | 2799.03 | 1 | 58.463 | 59.8258 | 820.3147 |  | 7667 | 27601200 | 59137200 | 90673200 | 122209200
2041-11-13 12:01 | 3056.48 | 1 | 75.3174 | 59.8258 | 895.7659 |  | 7668 | 27604800 | 59140800 | 90676800 | 122212800
2041-11-14 13:01 | 3829.7 | 1.2162 | 74.1416 | 59.8258 | 1122.3743 |  | 7669 | 27608400 | 59144400 | 90680400 | 122216400
2041-11-15 14:01 | 3670.5 | 1.1823 | 74.2954 | 59.8258 | 1075.7174 |  | 7670 | 27612000 | 59148000 | 90684000 | 122220000
2041-11-16 15:01 | 3734.17 | 1.2025 | 74.5741 | 59.8258 | 1094.3772 |  | 7671 | 27615600 | 59151600 | 90687600 | 122223600
2041-11-17 16:01 | 3236.89 | 1.0487 | 74.7242 | 59.8258 | 948.6388 |  | 7672 | 27619200 | 59155200 | 90691200 | 122227200
2041-11-18 17:01 | 3040.71 | 1 | 60.4365 | 59.8258 | 891.1441 |  | 7673 | 27622800 | 59158800 | 90694800 | 122230800
2041-11-19 18:01 | 2965.67 | 1 | 60.5417 | 59.8258 | 869.1521 |  | 7674 | 27626400 | 59162400 | 90698400 | 122234400
2041-11-20 19:01 | -237.262 | 1.2343 | 60.017 | 59.8258 | -69.5346 |  | 7675 | 27630000 | 59166000 | 90702000 | 122238000
2041-11-21 20:01 | -1028.92 | 3.4066 | 59.1802 | 59.8258 | -301.5467 |  | 7676 | 27633600 | 59169600 | 90705600 | 122241600
2041-11-22 21:01 | -2438.64 | 6.108 | 58.478 | 59.8258 | -714.6948 |  | 7677 | 27637200 | 59173200 | 90709200 | 122245200
2041-11-23 22:01 | -2989.21 | 6.108 | 57.7684 | 59.8258 | -876.051 |  | 7678 | 27640800 | 59176800 | 90712800 | 122248800
2041-11-24 23:01 | -4022.29 | 6.108 | 56.7042 | 59.8258 | -1178.8168 |  | 7679 | 27644400 | 59180400 | 90716400 | 122252400
2041-11-26 00:01 | -4539.45 | 6.108 | 55.9677 | 59.8258 | -1330.3815 |  | 7680 | 27648000 | 59184000 | 90720000 | 122256000
2041-11-27 01:01 | -4889.02 | 6.108 | 55.4304 | 59.8258 | -1432.8303 |  | 7681 | 27651600 | 59187600 | 90723600 | 122259600
2041-11-28 02:01 | -5218.18 | 6.108 | 54.9478 | 59.8258 | -1529.2976 |  | 7682 | 27655200 | 59191200 | 90727200 | 122263200
2041-11-29 03:01 | -5449.81 | 6.108 | 54.5629 | 59.8258 | -1597.1816 |  | 7683 | 27658800 | 59194800 | 90730800 | 122266800
2041-11-30 04:01 | -5666.76 | 6.108 | 54.2051 | 59.8258 | -1660.7634 |  | 7684 | 27662400 | 59198400 | 90734400 | 122270400
2041-12-01 05:01 | -5786.17 | 6.108 | 53.9403 | 59.8258 | -1695.759 |  | 7685 | 27666000 | 59202000 | 90738000 | 122274000
2041-12-02 06:01 | -5921.8 | 6.108 | 53.6755 | 59.8258 | -1735.5083 |  | 7686 | 27669600 | 59205600 | 90741600 | 122277600
2041-12-03 07:01 | -4808 | 6.108 | 54.3831 | 59.8258 | -1409.0857 |  | 7687 | 27673200 | 59209200 | 90745200 | 122281200
2041-12-04 08:01 | -3098.25 | 6.108 | 55.7088 | 59.8258 | -908.0074 |  | 7688 | 27676800 | 59212800 | 90748800 | 122284800
2041-12-05 09:01 | -2251.02 | 6.108 | 56.5749 | 59.8258 | -659.7088 |  | 7689 | 27680400 | 59216400 | 90752400 | 122288400
2041-12-06 10:01 | -896.923 | 2.6501 | 56.9159 | 59.8258 | -262.8622 |  | 7690 | 27684000 | 59220000 | 90756000 | 122292000
2041-12-07 11:01 | 2612.12 | 1 | 58.5155 | 59.8258 | 765.5368 |  | 7691 | 27687600 | 59223600 | 90759600 | 122295600
2041-12-08 12:01 | 3118.16 | 1 | 77.0252 | 59.8258 | 913.8425 |  | 7692 | 27691200 | 59227200 | 90763200 | 122299200
2041-12-09 13:01 | 3644.99 | 1.1667 | 74.1142 | 59.8258 | 1068.2411 |  | 7693 | 27694800 | 59230800 | 90766800 | 122302800
2041-12-10 14:01 | 3785.1 | 1.2169 | 74.3826 | 59.8258 | 1109.3033 |  | 7694 | 27698400 | 59234400 | 90770400 | 122306400
2041-12-11 15:01 | 3662.02 | 1.181 | 74.626 | 59.8258 | 1073.2321 |  | 7695 | 27702000 | 59238000 | 90774000 | 122310000
2041-12-12 16:01 | 3090.18 | 1 | 80.4002 | 59.8258 | 905.6424 |  | 7696 | 27705600 | 59241600 | 90777600 | 122313600
2041-12-13 17:01 | 3224.19 | 1.0324 | 75.0042 | 59.8258 | 944.9168 |  | 7697 | 27709200 | 59245200 | 90781200 | 122317200
2041-12-14 18:01 | 3011.59 | 1 | 60.5852 | 59.8258 | 882.6099 |  | 7698 | 27712800 | 59248800 | 90784800 | 122320800
2041-12-15 19:01 | 2822.93 | 1 | 60.7076 | 59.8258 | 827.3191 |  | 7699 | 27716400 | 59252400 | 90788400 | 122324400
2041-12-16 20:01 | -298.565 | 1.4204 | 60.0588 | 59.8258 | -87.5008 |  | 7700 | 27720000 | 59256000 | 90792000 | 122328000
2041-12-17 21:01 | -887.491 | 2.9841 | 59.3242 | 59.8258 | -260.0979 |  | 7701 | 27723600 | 59259600 | 90795600 | 122331600
2041-12-18 22:01 | -1498.91 | 4.6159 | 58.972 | 59.8258 | -439.2872 |  | 7702 | 27727200 | 59263200 | 90799200 | 122335200
2041-12-19 23:01 | -2001.67 | 5.9376 | 58.7131 | 59.8258 | -586.6316 |  | 7703 | 27730800 | 59266800 | 90802800 | 122338800
2041-12-21 00:01 | -3977.44 | 6.108 | 57.0646 | 59.8258 | -1165.6726 |  | 7704 | 27734400 | 59270400 | 90806400 | 122342400
2041-12-22 01:01 | -4520.45 | 6.108 | 56.2236 | 59.8258 | -1324.8131 |  | 7705 | 27738000 | 59274000 | 90810000 | 122346000
2041-12-23 02:01 | -5044.19 | 6.108 | 55.5258 | 59.8258 | -1478.3062 |  | 7706 | 27741600 | 59277600 | 90813600 | 122349600
2041-12-24 03:01 | -5368.32 | 6.108 | 55.0213 | 59.8258 | -1573.2993 |  | 7707 | 27745200 | 59281200 | 90817200 | 122353200
2041-12-25 04:01 | -5632.72 | 6.108 | 54.5874 | 59.8258 | -1650.7873 |  | 7708 | 27748800 | 59284800 | 90820800 | 122356800
2041-12-26 05:01 | -5743.25 | 6.108 | 54.2797 | 59.8258 | -1683.1804 |  | 7709 | 27752400 | 59288400 | 90824400 | 122360400
2041-12-27 06:01 | -5931.2 | 6.108 | 53.9718 | 59.8258 | -1738.2631 |  | 7710 | 27756000 | 59292000 | 90828000 | 122364000
2041-12-28 07:01 | -4615.67 | 6.108 | 54.7858 | 59.8258 | -1352.7193 |  | 7711 | 27759600 | 59295600 | 90831600 | 122367600
2041-12-29 08:01 | -2737.24 | 6.108 | 56.2497 | 59.8258 | -802.2059 |  | 7712 | 27763200 | 59299200 | 90835200 | 122371200
2041-12-30 09:01 | -2123.46 | 6.108 | 56.9594 | 59.8258 | -622.3247 |  | 7713 | 27766800 | 59302800 | 90838800 | 122374800
2041-12-31 10:01 | -1064.11 | 3.1309 | 57.1698 | 59.8258 | -311.8599 |  | 7714 | 27770400 | 59306400 | 90842400 | 122378400
2042-01-01 11:01 | 2397.4 | 1 | 58.7175 | 59.8258 | 702.6086 |  | 7715 | 27774000 | 59310000 | 90846000 | 122382000
2042-01-02 12:01 | 3103.4 | 1 | 77.7062 | 59.8258 | 909.5168 |  | 7716 | 27777600 | 59313600 | 90849600 | 122385600
2042-01-03 13:01 | 3407.31 | 1.0897 | 74.2714 | 59.8258 | 998.584 |  | 7717 | 27781200 | 59317200 | 90853200 | 122389200
2042-01-04 14:01 | 3786.18 | 1.2124 | 74.5497 | 59.8258 | 1109.6198 |  | 7718 | 27784800 | 59320800 | 90856800 | 122392800
2042-01-05 15:01 | 4130.66 | 1.341 | 74.6423 | 59.8258 | 1210.5769 |  | 7719 | 27788400 | 59324400 | 90860400 | 122396400
2042-01-06 16:01 | 3249.7 | 1.0472 | 75.0389 | 59.8258 | 952.3931 |  | 7720 | 27792000 | 59328000 | 90864000 | 122400000
2042-01-07 17:01 | 3712.64 | 1.2086 | 74.9546 | 59.8258 | 1088.0674 |  | 7721 | 27795600 | 59331600 | 90867600 | 122403600
2042-01-08 18:01 | 2961.11 | 1 | 60.7973 | 59.8258 | 867.8157 |  | 7722 | 27799200 | 59335200 | 90871200 | 122407200
2042-01-09 19:01 | 2748.96 | 1 | 60.8668 | 59.8258 | 805.6406 |  | 7723 | 27802800 | 59338800 | 90874800 | 122410800
2042-01-10 20:01 | -535.477 | 2.0783 | 59.963 | 59.8258 | -156.9328 |  | 7724 | 27806400 | 59342400 | 90878400 | 122414400
2042-01-11 21:01 | -1344.97 | 4.2366 | 59.3085 | 59.8258 | -394.1718 |  | 7725 | 27810000 | 59346000 | 90882000 | 122418000
2042-01-12 22:01 | -1868.69 | 5.5699 | 58.9428 | 59.8258 | -547.659 |  | 7726 | 27813600 | 59349600 | 90885600 | 122421600
2042-01-13 23:01 | -2349.96 | 6.108 | 58.479 | 59.8258 | -688.7053 |  | 7727 | 27817200 | 59353200 | 90889200 | 122425200
2042-01-15 00:01 | -3831 | 6.108 | 57.1471 | 59.8258 | -1122.7553 |  | 7728 | 27820800 | 59356800 | 90892800 | 122428800
2042-01-16 01:01 | -4330.85 | 6.108 | 56.3969 | 59.8258 | -1269.2468 |  | 7729 | 27824400 | 59360400 | 90896400 | 122432400
2042-01-17 02:01 | -4710.86 | 6.108 | 55.8444 | 59.8258 | -1380.6168 |  | 7730 | 27828000 | 59364000 | 90900000 | 122436000
2042-01-18 03:01 | -4878.45 | 6.108 | 55.4957 | 59.8258 | -1429.7326 |  | 7731 | 27831600 | 59367600 | 90903600 | 122439600
2042-01-19 04:01 | -4882.01 | 6.108 | 55.3103 | 59.8258 | -1430.7759 |  | 7732 | 27835200 | 59371200 | 90907200 | 122443200
2042-01-20 05:01 | -4849.15 | 6.108 | 55.1809 | 59.8258 | -1421.1456 |  | 7733 | 27838800 | 59374800 | 90910800 | 122446800
2042-01-21 06:01 | -4519.19 | 6.108 | 55.3282 | 59.8258 | -1324.4438 |  | 7734 | 27842400 | 59378400 | 90914400 | 122450400
2042-01-22 07:01 | -4149.42 | 6.108 | 55.5502 | 59.8258 | -1216.075 |  | 7735 | 27846000 | 59382000 | 90918000 | 122454000
2042-01-23 08:01 | -2717.77 | 6.108 | 56.626 | 59.8258 | -796.4998 |  | 7736 | 27849600 | 59385600 | 90921600 | 122457600
2042-01-24 09:01 | -1799.66 | 5.334 | 57.2896 | 59.8258 | -527.4283 |  | 7737 | 27853200 | 59389200 | 90925200 | 122461200
2042-01-25 10:01 | 0 | 0 | 59.0295 | 59.8258 | 0 |  | 7738 | 27856800 | 59392800 | 90928800 | 122464800
2042-01-26 11:01 | 2879.37 | 1 | 75.8282 | 59.8258 | 843.86 |  | 7739 | 27860400 | 59396400 | 90932400 | 122468400
2042-01-27 12:01 | 5116.9 | 1.5867 | 74.6466 | 59.8258 | 1499.6154 |  | 7740 | 27864000 | 59400000 | 90936000 | 122472000
2042-01-28 13:01 | 6018.54 | 1.9477 | 74.6739 | 59.8258 | 1763.86 |  | 7741 | 27867600 | 59403600 | 90939600 | 122475600
2042-01-29 14:01 | 6340.16 | 2.0467 | 75.2189 | 59.8258 | 1858.1175 |  | 7742 | 27871200 | 59407200 | 90943200 | 122479200
2042-01-30 15:01 | 6087.6 | 1.9825 | 75.5056 | 59.8258 | 1784.0994 |  | 7743 | 27874800 | 59410800 | 90946800 | 122482800
2042-01-31 16:01 | 5880.76 | 1.8738 | 76.108 | 59.8258 | 1723.4806 |  | 7744 | 27878400 | 59414400 | 90950400 | 122486400
2042-02-01 17:01 | 4068.06 | 1.3079 | 76.185 | 59.8258 | 1192.2307 |  | 7745 | 27882000 | 59418000 | 90954000 | 122490000
2042-02-02 18:01 | 3276.02 | 1.0603 | 76.018 | 59.8258 | 960.1067 |  | 7746 | 27885600 | 59421600 | 90957600 | 122493600
2042-02-03 19:01 | 3057.77 | 1 | 61.5217 | 59.8258 | 896.1439 |  | 7747 | 27889200 | 59425200 | 90961200 | 122497200
2042-02-04 20:01 | 2964.71 | 1 | 61.5235 | 59.8258 | 868.8707 |  | 7748 | 27892800 | 59428800 | 90964800 | 122500800
2042-02-05 21:01 | -763.714 | 2.6901 | 60.5044 | 59.8258 | -223.8225 |  | 7749 | 27896400 | 59432400 | 90968400 | 122504400
2042-02-06 22:01 | -1444.51 | 4.438 | 59.8262 | 59.8258 | -423.3441 |  | 7750 | 27900000 | 59436000 | 90972000 | 122508000
2042-02-07 23:01 | -2741.68 | 6.108 | 58.9117 | 59.8258 | -803.5071 |  | 7751 | 27903600 | 59439600 | 90975600 | 122511600
2042-02-09 00:01 | -3423.75 | 6.108 | 58.046 | 59.8258 | -1003.4021 |  | 7752 | 27907200 | 59443200 | 90979200 | 122515200
2042-02-10 01:01 | -3640.27 | 6.108 | 57.5318 | 59.8258 | -1066.8578 |  | 7753 | 27910800 | 59446800 | 90982800 | 122518800
2042-02-11 02:01 | -3665.06 | 6.108 | 57.218 | 59.8258 | -1074.1231 |  | 7754 | 27914400 | 59450400 | 90986400 | 122522400
2042-02-12 03:01 | -3628.99 | 6.108 | 57.0723 | 59.8258 | -1063.552 |  | 7755 | 27918000 | 59454000 | 90990000 | 122526000
2042-02-13 04:01 | -3410.26 | 6.108 | 57.0959 | 59.8258 | -999.4485 |  | 7756 | 27921600 | 59457600 | 90993600 | 122529600
2042-02-14 05:01 | -3145.9 | 6.108 | 57.2328 | 59.8258 | -921.9723 |  | 7757 | 27925200 | 59461200 | 90997200 | 122533200
2042-02-15 06:01 | -2552.35 | 6.108 | 57.6614 | 59.8258 | -748.0199 |  | 7758 | 27928800 | 59464800 | 91000800 | 122536800
2042-02-16 07:01 | -2326.42 | 6.108 | 57.8733 | 59.8258 | -681.8064 |  | 7759 | 27932400 | 59468400 | 91004400 | 122540400
2042-02-17 08:01 | -1228.16 | 3.5799 | 58.0582 | 59.8258 | -359.9382 |  | 7760 | 27936000 | 59472000 | 91008000 | 122544000
2042-02-18 09:01 | -259.118 | 1.005 | 58.6115 | 59.8258 | -75.94 |  | 7761 | 27939600 | 59475600 | 91011600 | 122547600
2042-02-19 10:01 | 2821.2 | 1 | 78.1701 | 59.8258 | 826.8121 |  | 7762 | 27943200 | 59479200 | 91015200 | 122551200
2042-02-20 11:01 | 4605.52 | 1.4114 | 75.4294 | 59.8258 | 1349.7447 |  | 7763 | 27946800 | 59482800 | 91018800 | 122554800
2042-02-21 12:01 | 6247.14 | 1.9777 | 75.4837 | 59.8258 | 1830.856 |  | 7764 | 27950400 | 59486400 | 91022400 | 122558400
2042-02-22 13:01 | 6963.01 | 2.1768 | 76.2018 | 59.8258 | 2040.6568 |  | 7765 | 27954000 | 59490000 | 91026000 | 122562000
2042-02-23 14:01 | 6890.87 | 2.1626 | 76.5982 | 59.8258 | 2019.5146 |  | 7766 | 27957600 | 59493600 | 91029600 | 122565600
2042-02-24 15:01 | 6430.26 | 1.9979 | 77.0714 | 59.8258 | 1884.5232 |  | 7767 | 27961200 | 59497200 | 91033200 | 122569200
2042-02-25 16:01 | 6435.31 | 2.012 | 77.1516 | 59.8258 | 1886.0032 |  | 7768 | 27964800 | 59500800 | 91036800 | 122572800
2042-02-26 17:01 | 5146.22 | 1.5694 | 77.6943 | 59.8258 | 1508.2082 |  | 7769 | 27968400 | 59504400 | 91040400 | 122576400
2042-02-27 18:01 | 4070.94 | 1.3095 | 76.8906 | 59.8258 | 1193.0747 |  | 7770 | 27972000 | 59508000 | 91044000 | 122580000
2042-02-28 19:01 | 3148.57 | 1 | 79.3517 | 59.8258 | 922.7548 |  | 7771 | 27975600 | 59511600 | 91047600 | 122583600
2042-03-01 20:01 | 3174.18 | 1 | 62.1494 | 59.8258 | 930.2603 |  | 7772 | 27979200 | 59515200 | 91051200 | 122587200
2042-03-02 21:01 | 0 | 0 | 62.4244 | 59.8258 | 0 |  | 7773 | 27982800 | 59518800 | 91054800 | 122590800
2042-03-03 22:01 | -439.108 | 1.6305 | 60.7411 | 59.8258 | -128.6899 |  | 7774 | 27986400 | 59522400 | 91058400 | 122594400
2042-03-04 23:01 | -1307.29 | 4.117 | 60.2145 | 59.8258 | -383.1289 |  | 7775 | 27990000 | 59526000 | 91062000 | 122598000
2042-03-06 00:01 | -1771.51 | 5.2373 | 59.8438 | 59.8258 | -519.1783 |  | 7776 | 27993600 | 59529600 | 91065600 | 122601600
2042-03-07 01:01 | -2078.2 | 6.0324 | 59.5564 | 59.8258 | -609.0603 |  | 7777 | 27997200 | 59533200 | 91069200 | 122605200
2042-03-08 02:01 | -2496.45 | 6.108 | 59.0196 | 59.8258 | -731.6373 |  | 7778 | 28000800 | 59536800 | 91072800 | 122608800
2042-03-09 03:01 | -2721.3 | 6.108 | 58.6623 | 59.8258 | -797.5343 |  | 7779 | 28004400 | 59540400 | 91076400 | 122612400
2042-03-10 04:01 | -2637.95 | 6.108 | 58.548 | 59.8258 | -773.1068 |  | 7780 | 28008000 | 59544000 | 91080000 | 122616000
2042-03-11 05:01 | -2429.05 | 6.108 | 58.5993 | 59.8258 | -711.8843 |  | 7781 | 28011600 | 59547600 | 91083600 | 122619600
2042-03-12 06:01 | -1974.98 | 5.724 | 58.7841 | 59.8258 | -578.8095 |  | 7782 | 28015200 | 59551200 | 91087200 | 122623200
2042-03-13 07:01 | -1821 | 5.2949 | 58.7939 | 59.8258 | -533.6824 |  | 7783 | 28018800 | 59554800 | 91090800 | 122626800
2042-03-14 08:01 | -1351.32 | 3.9744 | 58.7989 | 59.8258 | -396.0328 |  | 7784 | 28022400 | 59558400 | 91094400 | 122630400
2042-03-15 09:01 | -914.697 | 2.8388 | 58.9391 | 59.8258 | -268.0712 |  | 7785 | 28026000 | 59562000 | 91098000 | 122634000
2042-03-16 10:01 | -396.387 | 1.4599 | 59.2353 | 59.8258 | -116.1696 |  | 7786 | 28029600 | 59565600 | 91101600 | 122637600
2042-03-17 11:01 | 2092.14 | 1 | 60.3722 | 59.8258 | 613.1457 |  | 7787 | 28033200 | 59569200 | 91105200 | 122641200
2042-03-18 12:01 | 2979.17 | 1 | 60.6419 | 59.8258 | 873.1085 |  | 7788 | 28036800 | 59572800 | 91108800 | 122644800
2042-03-19 13:01 | 4009.95 | 1.2681 | 75.7038 | 59.8258 | 1175.2003 |  | 7789 | 28040400 | 59576400 | 91112400 | 122648400
2042-03-20 14:01 | 4139.62 | 1.3187 | 75.8515 | 59.8258 | 1213.2029 |  | 7790 | 28044000 | 59580000 | 91116000 | 122652000
2042-03-21 15:01 | 4046.06 | 1.2901 | 76.0593 | 59.8258 | 1185.7831 |  | 7791 | 28047600 | 59583600 | 91119600 | 122655600
2042-03-22 16:01 | 4338.25 | 1.3734 | 76.3165 | 59.8258 | 1271.4156 |  | 7792 | 28051200 | 59587200 | 91123200 | 122659200
2042-03-23 17:01 | 3701.15 | 1.1761 | 76.4169 | 59.8258 | 1084.7 |  | 7793 | 28054800 | 59590800 | 91126800 | 122662800
2042-03-24 18:01 | 3219.85 | 1.0411 | 76.2075 | 59.8258 | 943.6449 |  | 7794 | 28058400 | 59594400 | 91130400 | 122666400
2042-03-25 19:01 | 3076.03 | 1 | 86.7375 | 59.8258 | 901.4954 |  | 7795 | 28062000 | 59598000 | 91134000 | 122670000
2042-03-26 20:01 | 3080.93 | 1 | 61.7726 | 59.8258 | 902.9315 |  | 7796 | 28065600 | 59601600 | 91137600 | 122673600
2042-03-27 21:01 | -487.809 | 1.908 | 60.9453 | 59.8258 | -142.9627 |  | 7797 | 28069200 | 59605200 | 91141200 | 122677200
2042-03-28 22:01 | -1017.12 | 3.2737 | 60.2641 | 59.8258 | -298.0884 |  | 7798 | 28072800 | 59608800 | 91144800 | 122680800
2042-03-29 23:01 | -2055.07 | 6.108 | 59.8474 | 59.8258 | -602.2816 |  | 7799 | 28076400 | 59612400 | 91148400 | 122684400
2042-03-31 00:01 | -2911.77 | 6.108 | 58.9233 | 59.8258 | -853.3555 |  | 7800 | 28080000 | 59616000 | 91152000 | 122688000
2042-04-01 01:01 | -3216.89 | 6.108 | 58.3664 | 59.8258 | -942.7774 |  | 7801 | 28083600 | 59619600 | 91155600 | 122691600
2042-04-02 02:01 | -3394.28 | 6.108 | 57.9497 | 59.8258 | -994.7653 |  | 7802 | 28087200 | 59623200 | 91159200 | 122695200
2042-04-03 03:01 | -3571 | 6.108 | 57.6405 | 59.8258 | -1046.5568 |  | 7803 | 28090800 | 59626800 | 91162800 | 122698800
2042-04-04 04:01 | -3756.07 | 6.108 | 57.3297 | 59.8258 | -1100.7955 |  | 7804 | 28094400 | 59630400 | 91166400 | 122702400
2042-04-05 05:01 | -3881.7 | 6.108 | 57.0833 | 59.8258 | -1137.614 |  | 7805 | 28098000 | 59634000 | 91170000 | 122706000
2042-04-06 06:01 | -3970.95 | 6.108 | 56.8844 | 59.8258 | -1163.7706 |  | 7806 | 28101600 | 59637600 | 91173600 | 122709600
2042-04-07 07:01 | -2951.33 | 6.108 | 57.5214 | 59.8258 | -864.9494 |  | 7807 | 28105200 | 59641200 | 91177200 | 122713200
2042-04-08 08:01 | -1964.1 | 5.7681 | 58.1902 | 59.8258 | -575.6209 |  | 7808 | 28108800 | 59644800 | 91180800 | 122716800
2042-04-09 09:01 | -2014.22 | 5.8898 | 58.3182 | 59.8258 | -590.3096 |  | 7809 | 28112400 | 59648400 | 91184400 | 122720400
2042-04-10 10:01 | -662.311 | 1.9417 | 58.3473 | 59.8258 | -194.1042 |  | 7810 | 28116000 | 59652000 | 91188000 | 122724000
2042-04-11 11:01 | 1127.65 | 1 | 59.9875 | 59.8258 | 330.4816 |  | 7811 | 28119600 | 59655600 | 91191600 | 122727600
2042-04-12 12:01 | 2994.65 | 1 | 60.1656 | 59.8258 | 877.6453 |  | 7812 | 28123200 | 59659200 | 91195200 | 122731200
2042-04-13 13:01 | 3146 | 1 | 80.5676 | 59.8258 | 922.0016 |  | 7813 | 28126800 | 59662800 | 91198800 | 122734800
2042-04-14 14:01 | 3773.02 | 1.1959 | 75.512 | 59.8258 | 1105.763 |  | 7814 | 28130400 | 59666400 | 91202400 | 122738400
2042-04-15 15:01 | 3058.37 | 1 | 78.2257 | 59.8258 | 896.3198 |  | 7815 | 28134000 | 59670000 | 91206000 | 122742000
2042-04-16 16:01 | 3090.32 | 1 | 83.8906 | 59.8258 | 905.6834 |  | 7816 | 28137600 | 59673600 | 91209600 | 122745600
2042-04-17 17:01 | 3889.98 | 1.2301 | 76.0019 | 59.8258 | 1140.0406 |  | 7817 | 28141200 | 59677200 | 91213200 | 122749200
2042-04-18 18:01 | 3040.05 | 1 | 79.6475 | 59.8258 | 890.9507 |  | 7818 | 28144800 | 59680800 | 91216800 | 122752800
2042-04-19 19:01 | 3134.73 | 1 | 61.4951 | 59.8258 | 918.6987 |  | 7819 | 28148400 | 59684400 | 91220400 | 122756400
2042-04-20 20:01 | 3071.49 | 1 | 61.5435 | 59.8258 | 900.1649 |  | 7820 | 28152000 | 59688000 | 91224000 | 122760000
2042-04-21 21:01 | 3156.27 | 1 | 61.634 | 59.8258 | 925.0114 |  | 7821 | 28155600 | 59691600 | 91227600 | 122763600
2042-04-22 22:01 | 3111.24 | 1 | 61.7381 | 59.8258 | 911.8144 |  | 7822 | 28159200 | 59695200 | 91231200 | 122767200
2042-04-23 23:01 | 3168.55 | 1 | 61.7961 | 59.8258 | 928.6103 |  | 7823 | 28162800 | 59698800 | 91234800 | 122770800
2042-04-25 00:01 | -490.757 | 1.9244 | 60.9868 | 59.8258 | -143.8267 |  | 7824 | 28166400 | 59702400 | 91238400 | 122774400
2042-04-26 01:01 | -692.184 | 2.3548 | 60.3833 | 59.8258 | -202.8591 |  | 7825 | 28170000 | 59706000 | 91242000 | 122778000
2042-04-27 02:01 | -797.898 | 2.6214 | 60.0862 | 59.8258 | -233.8408 |  | 7826 | 28173600 | 59709600 | 91245600 | 122781600
2042-04-28 03:01 | -775.935 | 2.5387 | 59.9619 | 59.8258 | -227.4041 |  | 7827 | 28177200 | 59713200 | 91249200 | 122785200
2042-04-29 04:01 | -710.361 | 2.3634 | 59.884 | 59.8258 | -208.1863 |  | 7828 | 28180800 | 59716800 | 91252800 | 122788800
2042-04-30 05:01 | -626.804 | 2.1453 | 59.8222 | 59.8258 | -183.6981 |  | 7829 | 28184400 | 59720400 | 91256400 | 122792400
2042-05-01 06:01 | -349.238 | 1.3802 | 59.9994 | 59.8258 | -102.3516 |  | 7830 | 28188000 | 59724000 | 91260000 | 122796000
2042-05-02 07:01 | -112.994 | 0.78467 | 60.525 | 59.8258 | -33.1153 |  | 7831 | 28191600 | 59727600 | 91263600 | 122799600
2042-05-03 08:01 | 2446.92 | 1 | 61.0012 | 59.8258 | 717.1215 |  | 7832 | 28195200 | 59731200 | 91267200 | 122803200
2042-05-04 09:01 | 3058.87 | 1 | 61.3 | 59.8258 | 896.4663 |  | 7833 | 28198800 | 59734800 | 91270800 | 122806800
2042-05-05 10:01 | 3345.91 | 1.0657 | 76.2336 | 59.8258 | 980.5894 |  | 7834 | 28202400 | 59738400 | 91274400 | 122810400
2042-05-06 11:01 | 3857.68 | 1.2599 | 75.9902 | 59.8258 | 1130.5744 |  | 7835 | 28206000 | 59742000 | 91278000 | 122814000
2042-05-07 12:01 | 4704.42 | 1.5794 | 75.8152 | 59.8258 | 1378.7294 |  | 7836 | 28209600 | 59745600 | 91281600 | 122817600
2042-05-08 13:01 | 5050.56 | 1.5916 | 76.9794 | 59.8258 | 1480.173 |  | 7837 | 28213200 | 59749200 | 91285200 | 122821200
2042-05-09 14:01 | 3685.85 | 1.1597 | 77.2016 | 59.8258 | 1080.216 |  | 7838 | 28216800 | 59752800 | 91288800 | 122824800
2042-05-10 15:01 | 3132.02 | 1.0195 | 76.6707 | 59.8258 | 917.9045 |  | 7839 | 28220400 | 59756400 | 91292400 | 122828400
2042-05-11 16:01 | 4746.13 | 1.4673 | 77.3416 | 59.8258 | 1390.9534 |  | 7840 | 28224000 | 59760000 | 91296000 | 122832000
2042-05-12 17:01 | 4885.96 | 1.5227 | 77.4431 | 59.8258 | 1431.9335 |  | 7841 | 28227600 | 59763600 | 91299600 | 122835600
2042-05-13 18:01 | 4920.05 | 1.5932 | 77.0453 | 59.8258 | 1441.9243 |  | 7842 | 28231200 | 59767200 | 91303200 | 122839200
2042-05-14 19:01 | 4080.8 | 1.2362 | 78.1109 | 59.8258 | 1195.9644 |  | 7843 | 28234800 | 59770800 | 91306800 | 122842800
2042-05-15 20:01 | 3322.75 | 1 | 79.649 | 59.8258 | 973.8019 |  | 7844 | 28238400 | 59774400 | 91310400 | 122846400
2042-05-16 21:01 | 3199.32 | 1 | 62.6384 | 59.8258 | 937.6281 |  | 7845 | 28242000 | 59778000 | 91314000 | 122850000
2042-05-17 22:01 | 0 | 0 | 62.8842 | 59.8258 | 0 |  | 7846 | 28245600 | 59781600 | 91317600 | 122853600
2042-05-18 23:01 | -603.184 | 2.1126 | 61.1198 | 59.8258 | -176.7758 |  | 7847 | 28249200 | 59785200 | 91321200 | 122857200
2042-05-20 00:01 | -1031.08 | 3.2786 | 60.6507 | 59.8258 | -302.1797 |  | 7848 | 28252800 | 59788800 | 91324800 | 122860800
2042-05-21 01:01 | -1410.13 | 4.2559 | 60.341 | 59.8258 | -413.2683 |  | 7849 | 28256400 | 59792400 | 91328400 | 122864400
2042-05-22 02:01 | -1815.71 | 5.333 | 60.0943 | 59.8258 | -532.1321 |  | 7850 | 28260000 | 59796000 | 91332000 | 122868000
2042-05-23 03:01 | -2254.8 | 6.108 | 59.7485 | 59.8258 | -660.8166 |  | 7851 | 28263600 | 59799600 | 91335600 | 122871600
2042-05-24 04:01 | -2570.73 | 6.108 | 59.3262 | 59.8258 | -753.4066 |  | 7852 | 28267200 | 59803200 | 91339200 | 122875200
2042-05-25 05:01 | -2823.19 | 6.108 | 58.9584 | 59.8258 | -827.3953 |  | 7853 | 28270800 | 59806800 | 91342800 | 122878800
2042-05-26 06:01 | -3024.28 | 6.108 | 58.6341 | 59.8258 | -886.329 |  | 7854 | 28274400 | 59810400 | 91346400 | 122882400
2042-05-27 07:01 | -2305.92 | 6.108 | 59.0086 | 59.8258 | -675.7984 |  | 7855 | 28278000 | 59814000 | 91350000 | 122886000
2042-05-28 08:01 | -1956.63 | 5.6394 | 59.1012 | 59.8258 | -573.4316 |  | 7856 | 28281600 | 59817600 | 91353600 | 122889600
2042-05-29 09:01 | -2509.96 | 6.108 | 58.7829 | 59.8258 | -735.5967 |  | 7857 | 28285200 | 59821200 | 91357200 | 122893200
2042-05-30 10:01 | -2211.2 | 6.108 | 58.8907 | 59.8258 | -648.0387 |  | 7858 | 28288800 | 59824800 | 91360800 | 122896800
2042-05-31 11:01 | -1832.92 | 5.2891 | 58.9034 | 59.8258 | -537.1758 |  | 7859 | 28292400 | 59828400 | 91364400 | 122900400
2042-06-01 12:01 | -1312.1 | 3.8553 | 58.9224 | 59.8258 | -384.5386 |  | 7860 | 28296000 | 59832000 | 91368000 | 122904000
2042-06-02 13:01 | -1083.81 | 3.3337 | 59.0065 | 59.8258 | -317.6334 |  | 7861 | 28299600 | 59835600 | 91371600 | 122907600
2042-06-03 14:01 | -999.836 | 3.1412 | 59.0437 | 59.8258 | -293.023 |  | 7862 | 28303200 | 59839200 | 91375200 | 122911200
2042-06-04 15:01 | -910.222 | 2.9014 | 59.0757 | 59.8258 | -266.7597 |  | 7863 | 28306800 | 59842800 | 91378800 | 122914800
2042-06-05 16:01 | -955.275 | 3.0532 | 59.0782 | 59.8258 | -279.9635 |  | 7864 | 28310400 | 59846400 | 91382400 | 122918400
2042-06-06 17:01 | 1638.91 | 1 | 60.3453 | 59.8258 | 480.3171 |  | 7865 | 28314000 | 59850000 | 91386000 | 122922000
2042-06-07 18:01 | -89.8245 | 0.83566 | 60.3244 | 59.8258 | -26.325 |  | 7866 | 28317600 | 59853600 | 91389600 | 122925600
2042-06-08 19:01 | -411.963 | 1.6795 | 59.6332 | 59.8258 | -120.7344 |  | 7867 | 28321200 | 59857200 | 91393200 | 122929200
2042-06-09 20:01 | -737.087 | 2.5341 | 59.3299 | 59.8258 | -216.0189 |  | 7868 | 28324800 | 59860800 | 91396800 | 122932800
2042-06-10 21:01 | -915.063 | 2.9682 | 59.1996 | 59.8258 | -268.1785 |  | 7869 | 28328400 | 59864400 | 91400400 | 122936400
2042-06-11 22:01 | -1039.67 | 3.2866 | 59.1353 | 59.8258 | -304.6972 |  | 7870 | 28332000 | 59868000 | 91404000 | 122940000
2042-06-12 23:01 | -1112.97 | 3.4711 | 59.0347 | 59.8258 | -326.1793 |  | 7871 | 28335600 | 59871600 | 91407600 | 122943600
2042-06-14 00:01 | -2340.33 | 6.108 | 58.7227 | 59.8258 | -685.883 |  | 7872 | 28339200 | 59875200 | 91411200 | 122947200
2042-06-15 01:01 | -2693.59 | 6.108 | 58.2766 | 59.8258 | -789.4133 |  | 7873 | 28342800 | 59878800 | 91414800 | 122950800
2042-06-16 02:01 | -2930.88 | 6.108 | 57.9512 | 59.8258 | -858.9561 |  | 7874 | 28346400 | 59882400 | 91418400 | 122954400
2042-06-17 03:01 | -3029.49 | 6.108 | 57.7655 | 59.8258 | -887.8559 |  | 7875 | 28350000 | 59886000 | 91422000 | 122958000
2042-06-18 04:01 | -3028.12 | 6.108 | 57.6719 | 59.8258 | -887.4544 |  | 7876 | 28353600 | 59889600 | 91425600 | 122961600
2042-06-19 05:01 | -2987.65 | 6.108 | 57.5945 | 59.8258 | -875.5938 |  | 7877 | 28357200 | 59893200 | 91429200 | 122965200
2042-06-20 06:01 | -2915.55 | 6.108 | 57.5969 | 59.8258 | -854.4634 |  | 7878 | 28360800 | 59896800 | 91432800 | 122968800
2042-06-21 07:01 | -2016.78 | 5.9229 | 58.1837 | 59.8258 | -591.0599 |  | 7879 | 28364400 | 59900400 | 91436400 | 122972400
2042-06-22 08:01 | -1183.41 | 3.4511 | 58.2459 | 59.8258 | -346.8232 |  | 7880 | 28368000 | 59904000 | 91440000 | 122976000
2042-06-23 09:01 | -825.132 | 2.6459 | 58.5286 | 59.8258 | -241.8223 |  | 7881 | 28371600 | 59907600 | 91443600 | 122979600
2042-06-24 10:01 | -170.021 | 0.83657 | 59.1342 | 59.8258 | -49.8282 |  | 7882 | 28375200 | 59911200 | 91447200 | 122983200
2042-06-25 11:01 | 2278.49 | 1 | 60.0059 | 59.8258 | 667.7595 |  | 7883 | 28378800 | 59914800 | 91450800 | 122986800
2042-06-26 12:01 | 2934.65 | 1 | 81.7996 | 59.8258 | 860.061 |  | 7884 | 28382400 | 59918400 | 91454400 | 122990400
2042-06-27 13:01 | 3205.91 | 1 | 60.6806 | 59.8258 | 939.5595 |  | 7885 | 28386000 | 59922000 | 91458000 | 122994000
2042-06-28 14:01 | 3187.36 | 1 | 60.9319 | 59.8258 | 934.123 |  | 7886 | 28389600 | 59925600 | 91461600 | 122997600
2042-06-29 15:01 | 3228.29 | 1 | 61.1212 | 59.8258 | 946.1184 |  | 7887 | 28393200 | 59929200 | 91465200 | 123001200
2042-06-30 16:01 | 3239.58 | 1 | 61.2904 | 59.8258 | 949.4272 |  | 7888 | 28396800 | 59932800 | 91468800 | 123004800
2042-07-01 17:01 | 3299.33 | 1 | 77.6036 | 59.8258 | 966.9382 |  | 7889 | 28400400 | 59936400 | 91472400 | 123008400
2042-07-02 18:01 | 3193.31 | 1 | 86.4083 | 59.8258 | 935.8668 |  | 7890 | 28404000 | 59940000 | 91476000 | 123012000
2042-07-03 19:01 | 3062.62 | 1 | 61.5659 | 59.8258 | 897.5653 |  | 7891 | 28407600 | 59943600 | 91479600 | 123015600
2042-07-04 20:01 | 2969.28 | 1 | 61.6398 | 59.8258 | 870.2101 |  | 7892 | 28411200 | 59947200 | 91483200 | 123019200
2042-07-05 21:01 | 2946.62 | 1 | 61.6972 | 59.8258 | 863.5691 |  | 7893 | 28414800 | 59950800 | 91486800 | 123022800
2042-07-06 22:01 | 0 | 0 | 62.0251 | 59.8258 | 0 |  | 7894 | 28418400 | 59954400 | 91490400 | 123026400
2042-07-07 23:01 | 0 | 1 | 61.6673 | 59.8258 | 0 |  | 7895 | 28422000 | 59958000 | 91494000 | 123030000
2042-07-09 00:01 | -966.517 | 3.2245 | 60.1115 | 59.8258 | -283.2582 |  | 7896 | 28425600 | 59961600 | 91497600 | 123033600
2042-07-10 01:01 | -1520.82 | 4.6104 | 59.7645 | 59.8258 | -445.7083 |  | 7897 | 28429200 | 59965200 | 91501200 | 123037200
2042-07-11 02:01 | -1961.33 | 5.7609 | 59.4921 | 59.8258 | -574.8091 |  | 7898 | 28432800 | 59968800 | 91504800 | 123040800
2042-07-12 03:01 | -2470.72 | 6.108 | 58.9812 | 59.8258 | -724.0966 |  | 7899 | 28436400 | 59972400 | 91508400 | 123044400
2042-07-13 04:01 | -2595.36 | 6.108 | 58.7118 | 59.8258 | -760.6249 |  | 7900 | 28440000 | 59976000 | 91512000 | 123048000
2042-07-14 05:01 | -2773.47 | 6.108 | 58.4296 | 59.8258 | -812.8238 |  | 7901 | 28443600 | 59979600 | 91515600 | 123051600
2042-07-15 06:01 | -2507.9 | 6.108 | 58.503 | 59.8258 | -734.9929 |  | 7902 | 28447200 | 59983200 | 91519200 | 123055200
2042-07-16 07:01 | -2436.19 | 6.108 | 58.4865 | 59.8258 | -713.9768 |  | 7903 | 28450800 | 59986800 | 91522800 | 123058800
2042-07-17 08:01 | -2155.24 | 6.108 | 58.6296 | 59.8258 | -631.6385 |  | 7904 | 28454400 | 59990400 | 91526400 | 123062400
2042-07-18 09:01 | -2033.62 | 5.892 | 58.6335 | 59.8258 | -595.9952 |  | 7905 | 28458000 | 59994000 | 91530000 | 123066000
2042-07-19 10:01 | -1155.74 | 3.3577 | 58.6294 | 59.8258 | -338.714 |  | 7906 | 28461600 | 59997600 | 91533600 | 123069600
2042-07-20 11:01 | 0 | 1 | 60.2892 | 59.8258 | 0 |  | 7907 | 28465200 | 60001200 | 91537200 | 123073200
2042-07-21 12:01 | 2913.91 | 1 | 60.2137 | 59.8258 | 853.9827 |  | 7908 | 28468800 | 60004800 | 91540800 | 123076800
2042-07-22 13:01 | 3000.34 | 1 | 60.6936 | 59.8258 | 879.3129 |  | 7909 | 28472400 | 60008400 | 91544400 | 123080400
2042-07-23 14:01 | 3075.89 | 1 | 60.9779 | 59.8258 | 901.4544 |  | 7910 | 28476000 | 60012000 | 91548000 | 123084000
2042-07-24 15:01 | 3057.39 | 1 | 61.1788 | 59.8258 | 896.0326 |  | 7911 | 28479600 | 60015600 | 91551600 | 123087600
2042-07-25 16:01 | 3136.42 | 1 | 61.3432 | 59.8258 | 919.194 |  | 7912 | 28483200 | 60019200 | 91555200 | 123091200
2042-07-26 17:01 | 2983.35 | 1 | 61.5041 | 59.8258 | 874.3336 |  | 7913 | 28486800 | 60022800 | 91558800 | 123094800
2042-07-27 18:01 | 0 | 0 | 61.8304 | 59.8258 | 0 |  | 7914 | 28490400 | 60026400 | 91562400 | 123098400
2042-07-28 19:01 | -426.856 | 1.7265 | 60.3545 | 59.8258 | -125.0991 |  | 7915 | 28494000 | 60030000 | 91566000 | 123102000
2042-07-29 20:01 | -917.862 | 3.0245 | 59.8719 | 59.8258 | -268.9988 |  | 7916 | 28497600 | 60033600 | 91569600 | 123105600
2042-07-30 21:01 | -1866.9 | 5.6326 | 59.582 | 59.8258 | -547.1344 |  | 7917 | 28501200 | 60037200 | 91573200 | 123109200
2042-07-31 22:01 | -2446.15 | 6.108 | 59.0203 | 59.8258 | -716.8958 |  | 7918 | 28504800 | 60040800 | 91576800 | 123112800
2042-08-01 23:01 | -3501.3 | 6.108 | 57.9664 | 59.8258 | -1026.1297 |  | 7919 | 28508400 | 60044400 | 91580400 | 123116400
2042-08-03 00:01 | -3932.3 | 6.108 | 57.3506 | 59.8258 | -1152.4434 |  | 7920 | 28512000 | 60048000 | 91584000 | 123120000
2042-08-04 01:01 | -4225.08 | 6.108 | 56.8735 | 59.8258 | -1238.2487 |  | 7921 | 28515600 | 60051600 | 91587600 | 123123600
2042-08-05 02:01 | -4330.34 | 6.108 | 56.5716 | 59.8258 | -1269.0974 |  | 7922 | 28519200 | 60055200 | 91591200 | 123127200
2042-08-06 03:01 | -4447.1 | 6.108 | 56.3034 | 59.8258 | -1303.3164 |  | 7923 | 28522800 | 60058800 | 91594800 | 123130800
2042-08-07 04:01 | -4403.69 | 6.108 | 56.1681 | 59.8258 | -1290.5941 |  | 7924 | 28526400 | 60062400 | 91598400 | 123134400
2042-08-08 05:01 | -4401.8 | 6.108 | 56.0445 | 59.8258 | -1290.0402 |  | 7925 | 28530000 | 60066000 | 91602000 | 123138000
2042-08-09 06:01 | -4100.22 | 6.108 | 56.1888 | 59.8258 | -1201.6559 |  | 7926 | 28533600 | 60069600 | 91605600 | 123141600
2042-08-10 07:01 | -3494.68 | 6.108 | 56.6081 | 59.8258 | -1024.1896 |  | 7927 | 28537200 | 60073200 | 91609200 | 123145200
2042-08-11 08:01 | -2082.43 | 6.108 | 57.6965 | 59.8258 | -610.3 |  | 7928 | 28540800 | 60076800 | 91612800 | 123148800
2042-08-12 09:01 | -1352.84 | 3.9454 | 57.874 | 59.8258 | -396.4783 |  | 7929 | 28544400 | 60080400 | 91616400 | 123152400
2042-08-13 10:01 | -329.969 | 1.1759 | 58.3398 | 59.8258 | -96.7044 |  | 7930 | 28548000 | 60084000 | 91620000 | 123156000
2042-08-14 11:01 | 2791.04 | 1 | 59.6111 | 59.8258 | 817.9731 |  | 7931 | 28551600 | 60087600 | 91623600 | 123159600
2042-08-15 12:01 | 3071.88 | 1 | 75.3726 | 59.8258 | 900.2792 |  | 7932 | 28555200 | 60091200 | 91627200 | 123163200
2042-08-16 13:01 | 3639.99 | 1.1324 | 75.46 | 59.8258 | 1066.7758 |  | 7933 | 28558800 | 60094800 | 91630800 | 123166800
2042-08-17 14:01 | 3226.88 | 1 | 79.2644 | 59.8258 | 945.7052 |  | 7934 | 28562400 | 60098400 | 91634400 | 123170400
2042-08-18 15:01 | 3214.03 | 1 | 78.7126 | 59.8258 | 941.9392 |  | 7935 | 28566000 | 60102000 | 91638000 | 123174000
2042-08-19 16:01 | 3144.38 | 1 | 77.553 | 59.8258 | 921.5268 |  | 7936 | 28569600 | 60105600 | 91641600 | 123177600
2042-08-20 17:01 | 3111.58 | 1 | 61.1818 | 59.8258 | 911.9141 |  | 7937 | 28573200 | 60109200 | 91645200 | 123181200
2042-08-21 18:01 | 3002.13 | 1 | 61.2935 | 59.8258 | 879.8375 |  | 7938 | 28576800 | 60112800 | 91648800 | 123184800
2042-08-22 19:01 | 0 | 0 | 61.6283 | 59.8258 | 0 |  | 7939 | 28580400 | 60116400 | 91652400 | 123188400
2042-08-23 20:01 | -337.88 | 1.3853 | 60.1713 | 59.8258 | -99.0229 |  | 7940 | 28584000 | 60120000 | 91656000 | 123192000
2042-08-24 21:01 | -1233.77 | 3.9558 | 59.6544 | 59.8258 | -361.5823 |  | 7941 | 28587600 | 60123600 | 91659600 | 123195600
2042-08-25 22:01 | -1523.26 | 4.5709 | 59.3558 | 59.8258 | -446.4234 |  | 7942 | 28591200 | 60127200 | 91663200 | 123199200
2042-08-26 23:01 | -2048.88 | 6.0467 | 59.127 | 59.8258 | -600.4675 |  | 7943 | 28594800 | 60130800 | 91666800 | 123202800
2042-08-28 00:01 | -2001.08 | 5.7825 | 58.8696 | 59.8258 | -586.4587 |  | 7944 | 28598400 | 60134400 | 91670400 | 123206400
2042-08-29 01:01 | -1987.32 | 5.7762 | 58.7673 | 59.8258 | -582.426 |  | 7945 | 28602000 | 60138000 | 91674000 | 123210000
2042-08-30 02:01 | -2053.71 | 5.9767 | 58.6905 | 59.8258 | -601.883 |  | 7946 | 28605600 | 60141600 | 91677600 | 123213600
2042-08-31 03:01 | -2031.19 | 5.8965 | 58.6192 | 59.8258 | -595.283 |  | 7947 | 28609200 | 60145200 | 91681200 | 123217200
2042-09-01 04:01 | -2126.75 | 6.108 | 58.5495 | 59.8258 | -623.2889 |  | 7948 | 28612800 | 60148800 | 91684800 | 123220800
2042-09-02 05:01 | -2321.69 | 6.108 | 58.3513 | 59.8258 | -680.4202 |  | 7949 | 28616400 | 60152400 | 91688400 | 123224400
2042-09-03 06:01 | -2318.74 | 6.108 | 58.2766 | 59.8258 | -679.5556 |  | 7950 | 28620000 | 60156000 | 91692000 | 123228000
2042-09-04 07:01 | -2528.07 | 6.108 | 58.0863 | 59.8258 | -740.9042 |  | 7951 | 28623600 | 60159600 | 91695600 | 123231600
2042-09-05 08:01 | -2688.17 | 6.108 | 57.9059 | 59.8258 | -787.8249 |  | 7952 | 28627200 | 60163200 | 91699200 | 123235200
2042-09-06 09:01 | -3117.16 | 6.108 | 57.5193 | 59.8258 | -913.5494 |  | 7953 | 28630800 | 60166800 | 91702800 | 123238800
2042-09-07 10:01 | -2939.88 | 6.108 | 57.538 | 59.8258 | -861.5938 |  | 7954 | 28634400 | 60170400 | 91706400 | 123242400
2042-09-08 11:01 | -2984.61 | 6.108 | 57.4321 | 59.8258 | -874.7028 |  | 7955 | 28638000 | 60174000 | 91710000 | 123246000
2042-09-09 12:01 | -2732.75 | 6.108 | 57.534 | 59.8258 | -800.89 |  | 7956 | 28641600 | 60177600 | 91713600 | 123249600
2042-09-10 13:01 | -2044.69 | 6.0125 | 57.9689 | 59.8258 | -599.2395 |  | 7957 | 28645200 | 60181200 | 91717200 | 123253200
2042-09-11 14:01 | -1824.1 | 5.3313 | 57.9904 | 59.8258 | -534.5909 |  | 7958 | 28648800 | 60184800 | 91720800 | 123256800
2042-09-12 15:01 | -601.992 | 1.829 | 58.0684 | 59.8258 | -176.4264 |  | 7959 | 28652400 | 60188400 | 91724400 | 123260400
2042-09-13 16:01 | -312.94 | 1.3274 | 58.6482 | 59.8258 | -91.7137 |  | 7960 | 28656000 | 60192000 | 91728000 | 123264000
2042-09-14 17:01 | -1113.94 | 3.6752 | 58.4576 | 59.8258 | -326.4636 |  | 7961 | 28659600 | 60195600 | 91731600 | 123267600
2042-09-15 18:01 | -1667.55 | 5.083 | 58.2992 | 59.8258 | -488.7107 |  | 7962 | 28663200 | 60199200 | 91735200 | 123271200
2042-09-16 19:01 | -2405.39 | 6.108 | 57.9205 | 59.8258 | -704.9502 |  | 7963 | 28666800 | 60202800 | 91738800 | 123274800
2042-09-17 20:01 | -3023.8 | 6.108 | 57.3368 | 59.8258 | -886.1883 |  | 7964 | 28670400 | 60206400 | 91742400 | 123278400
2042-09-18 21:01 | -4155.63 | 6.108 | 56.3324 | 59.8258 | -1217.8949 |  | 7965 | 28674000 | 60210000 | 91746000 | 123282000
2042-09-19 22:01 | -4649.36 | 6.108 | 55.7057 | 59.8258 | -1362.5929 |  | 7966 | 28677600 | 60213600 | 91749600 | 123285600
2042-09-20 23:01 | -5648.34 | 6.108 | 54.745 | 59.8258 | -1655.365 |  | 7967 | 28681200 | 60217200 | 91753200 | 123289200
2042-09-22 00:01 | -6062.65 | 6.108 | 54.1648 | 59.8258 | -1776.7873 |  | 7968 | 28684800 | 60220800 | 91756800 | 123292800
2042-09-23 01:01 | -6375.07 | 6.108 | 53.6893 | 59.8258 | -1868.3486 |  | 7969 | 28688400 | 60224400 | 91760400 | 123296400
2042-09-24 02:01 | -6466.08 | 6.108 | 53.408 | 59.8258 | -1895.021 |  | 7970 | 28692000 | 60228000 | 91764000 | 123300000
2042-09-25 03:01 | -6572.07 | 6.108 | 53.1479 | 59.8258 | -1926.0836 |  | 7971 | 28695600 | 60231600 | 91767600 | 123303600
2042-09-26 04:01 | -6510.23 | 6.108 | 53.0233 | 59.8258 | -1907.9601 |  | 7972 | 28699200 | 60235200 | 91771200 | 123307200
2042-09-27 05:01 | -6327.73 | 6.108 | 53.0398 | 59.8258 | -1854.4746 |  | 7973 | 28702800 | 60238800 | 91774800 | 123310800
2042-09-28 06:01 | -5925.11 | 6.108 | 53.2611 | 59.8258 | -1736.4783 |  | 7974 | 28706400 | 60242400 | 91778400 | 123314400
2042-09-29 07:01 | -6103.53 | 6.108 | 53.1029 | 59.8258 | -1788.7681 |  | 7975 | 28710000 | 60246000 | 91782000 | 123318000
2042-09-30 08:01 | -5859.8 | 6.108 | 53.2112 | 59.8258 | -1717.3379 |  | 7976 | 28713600 | 60249600 | 91785600 | 123321600
2042-10-01 09:01 | -5927.16 | 6.108 | 53.1313 | 59.8258 | -1737.0791 |  | 7977 | 28717200 | 60253200 | 91789200 | 123325200
2042-10-02 10:01 | -4758.69 | 6.108 | 53.959 | 59.8258 | -1394.6344 |  | 7978 | 28720800 | 60256800 | 91792800 | 123328800
2042-10-03 11:01 | -5056.89 | 6.108 | 53.8368 | 59.8258 | -1482.0282 |  | 7979 | 28724400 | 60260400 | 91796400 | 123332400
2042-10-04 12:01 | -5498.71 | 6.108 | 53.4916 | 59.8258 | -1611.5128 |  | 7980 | 28728000 | 60264000 | 91800000 | 123336000
2042-10-05 13:01 | -5370.24 | 6.108 | 53.4902 | 59.8258 | -1573.862 |  | 7981 | 28731600 | 60267600 | 91803600 | 123339600
2042-10-06 14:01 | -4693.35 | 6.108 | 53.9478 | 59.8258 | -1375.4851 |  | 7982 | 28735200 | 60271200 | 91807200 | 123343200
2042-10-07 15:01 | -4400.73 | 6.108 | 54.2142 | 59.8258 | -1289.7266 |  | 7983 | 28738800 | 60274800 | 91810800 | 123346800
2042-10-08 16:01 | -4219.29 | 6.108 | 54.3649 | 59.8258 | -1236.5518 |  | 7984 | 28742400 | 60278400 | 91814400 | 123350400
2042-10-09 17:01 | -4741.42 | 6.108 | 53.9836 | 59.8258 | -1389.573 |  | 7985 | 28746000 | 60282000 | 91818000 | 123354000
2042-10-10 18:01 | -4947.33 | 6.108 | 53.757 | 59.8258 | -1449.9193 |  | 7986 | 28749600 | 60285600 | 91821600 | 123357600
2042-10-11 19:01 | -5565.5 | 6.108 | 53.2296 | 59.8258 | -1631.087 |  | 7987 | 28753200 | 60289200 | 91825200 | 123361200
2042-10-12 20:01 | -5912.79 | 6.108 | 52.8366 | 59.8258 | -1732.8677 |  | 7988 | 28756800 | 60292800 | 91828800 | 123364800
2042-10-13 21:01 | -6876.4 | 6.108 | 51.9827 | 59.8258 | -2015.2739 |  | 7989 | 28760400 | 60296400 | 91832400 | 123368400
2042-10-14 22:01 | -7154.11 | 6.108 | 51.5421 | 59.8258 | -2096.6627 |  | 7990 | 28764000 | 60300000 | 91836000 | 123372000
2042-10-15 23:01 | -8153.94 | 6.108 | 50.6131 | 59.8258 | -2389.6839 |  | 7991 | 28767600 | 60303600 | 91839600 | 123375600
2042-10-17 00:01 | -8397.49 | 6.108 | 50.1765 | 59.8258 | -2461.0614 |  | 7992 | 28771200 | 60307200 | 91843200 | 123379200
2042-10-18 01:01 | -8689.55 | 6.108 | 49.7536 | 59.8258 | -2546.6557 |  | 7993 | 28774800 | 60310800 | 91846800 | 123382800
2042-10-19 02:01 | -8971.97 | 6.108 | 49.3479 | 59.8258 | -2629.4248 |  | 7994 | 28778400 | 60314400 | 91850400 | 123386400
2042-10-20 03:01 | -9164.01 | 6.108 | 49.0164 | 59.8258 | -2685.7062 |  | 7995 | 28782000 | 60318000 | 91854000 | 123390000
2042-10-21 04:01 | -9272.86 | 6.108 | 48.752 | 59.8258 | -2717.607 |  | 7996 | 28785600 | 60321600 | 91857600 | 123393600
2042-10-22 05:01 | -9181.01 | 6.108 | 48.6729 | 59.8258 | -2690.6884 |  | 7997 | 28789200 | 60325200 | 91861200 | 123397200
2042-10-23 06:01 | -8979.98 | 6.108 | 48.7071 | 59.8258 | -2631.7723 |  | 7998 | 28792800 | 60328800 | 91864800 | 123400800
2042-10-24 07:01 | -8684.26 | 6.108 | 48.8528 | 59.8258 | -2545.1054 |  | 7999 | 28796400 | 60332400 | 91868400 | 123404400
2042-10-25 08:01 | -7708.94 | 6.108 | 49.5429 | 59.8258 | -2259.2673 |  | 8000 | 28800000 | 60336000 | 91872000 | 123408000
2042-10-26 09:01 | -8041.41 | 6.108 | 49.3778 | 59.8258 | -2356.7046 |  | 8001 | 28803600 | 60339600 | 91875600 | 123411600
2042-10-27 10:01 | -6616.6 | 6.108 | 50.4141 | 59.8258 | -1939.134 |  | 8002 | 28807200 | 60343200 | 91879200 | 123415200
2042-10-28 11:01 | -4820.57 | 6.108 | 51.9189 | 59.8258 | -1412.7696 |  | 8003 | 28810800 | 60346800 | 91882800 | 123418800
2042-10-29 12:01 | -3661.12 | 6.108 | 53.1152 | 59.8258 | -1072.9684 |  | 8004 | 28814400 | 60350400 | 91886400 | 123422400
2042-10-30 13:01 | -2836.1 | 6.108 | 54.0593 | 59.8258 | -831.1789 |  | 8005 | 28818000 | 60354000 | 91890000 | 123426000
2042-10-31 14:01 | -2448.55 | 6.108 | 54.6359 | 59.8258 | -717.5992 |  | 8006 | 28821600 | 60357600 | 91893600 | 123429600
2042-11-01 15:01 | -2172.12 | 6.108 | 55.1002 | 59.8258 | -636.5855 |  | 8007 | 28825200 | 60361200 | 91897200 | 123433200
2042-11-02 16:01 | -2060.57 | 6.108 | 55.395 | 59.8258 | -603.8935 |  | 8008 | 28828800 | 60364800 | 91900800 | 123436800
2042-11-03 17:01 | -3211.32 | 6.108 | 54.695 | 59.8258 | -941.145 |  | 8009 | 28832400 | 60368400 | 91904400 | 123440400
2042-11-04 18:01 | -3706.73 | 6.108 | 54.2907 | 59.8258 | -1086.3353 |  | 8010 | 28836000 | 60372000 | 91908000 | 123444000
2042-11-05 19:01 | -4487.45 | 6.108 | 53.6515 | 59.8258 | -1315.1418 |  | 8011 | 28839600 | 60375600 | 91911600 | 123447600
2042-11-06 20:01 | -4942.11 | 6.108 | 53.2022 | 59.8258 | -1448.3895 |  | 8012 | 28843200 | 60379200 | 91915200 | 123451200
2042-11-07 21:01 | -5874.79 | 6.108 | 52.4021 | 59.8258 | -1721.731 |  | 8013 | 28846800 | 60382800 | 91918800 | 123454800
2042-11-08 22:01 | -5982.81 | 6.108 | 52.1301 | 59.8258 | -1753.3885 |  | 8014 | 28850400 | 60386400 | 91922400 | 123458400
2042-11-09 23:01 | -6646.06 | 6.108 | 51.5131 | 59.8258 | -1947.7679 |  | 8015 | 28854000 | 60390000 | 91926000 | 123462000
2042-11-11 00:01 | -6923.12 | 6.108 | 51.1363 | 59.8258 | -2028.9662 |  | 8016 | 28857600 | 60393600 | 91929600 | 123465600
2042-11-12 01:01 | -6807.77 | 6.108 | 51.0698 | 59.8258 | -1995.1604 |  | 8017 | 28861200 | 60397200 | 91933200 | 123469200
2042-11-13 02:01 | -6587.72 | 6.108 | 51.1452 | 59.8258 | -1930.6701 |  | 8018 | 28864800 | 60400800 | 91936800 | 123472800
2042-11-14 03:01 | -6217.71 | 6.108 | 51.3862 | 59.8258 | -1822.2309 |  | 8019 | 28868400 | 60404400 | 91940400 | 123476400
2042-11-15 04:01 | -6014.14 | 6.108 | 51.5382 | 59.8258 | -1762.5704 |  | 8020 | 28872000 | 60408000 | 91944000 | 123480000
2042-11-16 05:01 | -6542.53 | 6.108 | 51.167 | 59.8258 | -1917.4263 |  | 8021 | 28875600 | 60411600 | 91947600 | 123483600