## Carbon (hidden)
|  |  |  | lb/MWh | tons/kBtu
|  | Carbon factors | natural gas | - | 5.3e-05 |  | $/kWh | 0.1 |  |  |  |  | DTE renewable portfolio standard
|  |  | 2024 grid | 1141 | 0.00015159 |  | $/therm | 0.75 |  |  |  |  | 2030 - 50% renewable mandate
|  |  | 2030 grid | 500 | 6.6431e-05 | [7 empty] | 2040 - 100% renewable mandate
|  |  | 100% Renewable energy (2040) | 0 | 0 |  | DHW HP COP | 3
[7 empty] | Geo HP COP | 4
Appliance - per appliance consumption | EUI | Annual use (if gas - therm) | Annual use (if elec - kWh) | Carbon (nat. gas) | Carbon (elec 2024 grid) | Carbon (elec. 2030 grid) | Carbon (elec. Renewable - 2040) | Utility cost (gas) | Utility cost (elec) | kBtu gas | kBtu elec
Stove/range | - | 45 | 604 | 0.2385 | 0.31269 | 0.13702 | 0 | 33.75 | 60.4 | 4500 | 2062.66
Standard Dryer | - | 52.9 | 835 | 0.28037 | 0.43228 | 0.18943 | 0 | 39.675 | 83.5 | 5290 | 2851.525
Heat Pump Dryer | - | - | 278.3333 | - | 0.14409 | 0.063143 | 0 | - | 27.8333
Standard DHW | 10 | 100 | 2928.2577 | 0.53 | 1.5159 | 0.66431 | 0 | 75 | 292.8258
Heat Pump DHW | 3.3333 | - | 976.0859 | - | 0.50531 | 0.22144 | 0 | - | 97.6086
Carbon savings (tons) for neighborhood |  |  | Current (gas) | 274.8039 | - | - | - | 38887.35
262 | homes |  | All electric | - | 592.3579 | 259.5784 | 0 | - | 98597.3514
|  |  | All heat pump | - | 252.0688 | 110.4596 | 0 | - | 32865.7838
Pathway - stay at 275 always or go to 252 today, 110 by 2030 and 0 by 2040 with DTE renewable goal
|  |  |  | Current (gas) | 274.8039
|  |  |  | All Elec HP (2024 grid) | 252.0688
|  |  |  | All Elec HP (2030 grid) | 110.4596
|  |  |  | All Elec HP (2040 grid) | 0
Carbon (tons) and cost for heating/cooling only - leave DHW as gas. So we don't double count with savings above.
Building | sf footage | Total Elec EUI | Cooling EUI | Heating EUI (elec) | Total Gas EUI | Heating EUI (gas) | Annual heating use (gas - therms) | Annual heating + cooling use (elec - kWh) | Carbon (nat. gas) | Carbon (elec 2024 grid) | Carbon (elec. 2030 grid) | Carbon (elec. Renewable) | Total Carbon (gas+elec 2024 grid) | Total Carbon (gas+elec. 2030 grid) | Total Carbon (gas+elec. Renewable 2040 grid) | Heating utility cost (gas) | Htg+Clg utility cost (elec) | Total heating+cooling utility cost
Typical home (current) | 1000 | 25 | 10 | 0 | 60 | 50 | 500 | 2928.2577 | 3.18 | 3.7899 | 1.6608 | 0 | 6.9699 | 4.8408 | 3.18 | 375 | 292.8258 | 667.8258
Typical home (geo) | 1000 | 29.375 | 5 | 9.375 | 10 | 0 | 0 | 4209.3704 | 0.53 | 4.4531 | 1.9514 | 0 | 4.9831 | 2.4814 | 0.53 | 0 | 420.937 | 420.937
Bryant Elementary (current) | 60000 | 20 | 5 | 0 | 30 | 25 | 15000 | 87847.7306 | 95.4 | 181.9134 | 79.7166 | 0 | 277.3134 | 175.1166 | 95.4 | 11250 | 8784.7731 | 20034.7731
Bryant Elementary (geo) | 60000 | 22.1875 | 2.5 | 4.6875 | 5 | 0 | 0 | 126281.1127 | 15.9 | 201.8101 | 88.4356 | 0 | 217.7101 | 104.3356 | 15.9 | 0 | 12628.1113 | 12628.1113
County Health (current) | 30000 | 25 | 4 | 0 | 40 | 35 | 10500 | 35139.0922 | 63.6 | 113.6958 | 49.8229 | 0 | 177.2958 | 113.4229 | 63.6 | 7875 | 3513.9092 | 11388.9092
County Health (geo) | 30000 | 29.5625 | 2 | 6.5625 | 5 | 0 | 0 | 75219.6193 | 7.95 | 134.4453 | 58.9156 | 0 | 142.3953 | 66.8656 | 7.95 | 0 | 7521.9619 | 7521.9619
PW Main (current) | 40000 | 25 | 5 | 0 | 47 | 42 | 16800 | 58565.1537 | 99.64 | 151.5945 | 66.4305 | 0 | 251.2345 | 166.0705 | 99.64 | 12600 | 5856.5154 | 18456.5154
PW Main (geo) | 40000 | 30.375 | 2.5 | 7.875 | 5 | 0 | 0 | 121522.694 | 10.6 | 184.1873 | 80.7131 | 0 | 194.7873 | 91.3131 | 10.6 | 0 | 12152.2694 | 12152.2694
PW South Fleet/Maint (current) | 40000 | 25 | 2 | 0 | 130 | 90 | 36000 | 23426.0615 | 275.6 | 151.5945 | 66.4305 | 0 | 427.1945 | 342.0305 | 275.6 | 27000 | 2342.6061 | 29342.6061
PW South Fleet/Maint (geo) | 40000 | 40.875 | 1 | 16.875 | 40 | 0 | 0 | 209370.4246 | 84.8 | 247.857 | 108.6139 | 0 | 332.657 | 193.4139 | 84.8 | 0 | 20937.0425 | 20937.0425
Public works east fleet (current) | 65000 | 25 | 0 | 0 | 130 | 90 | 58500 | 0 | 447.85 | 246.341 | 107.9496 | 0 | 694.191 | 555.7996 | 447.85 | 43875 | 0 | 43875
Public works east fleet (geo) | 65000 | 41.875 | 0 | 16.875 | 40 | 0 | 0 | 321193.265 | 137.8 | 412.6212 | 180.8156 | 0 | 550.4212 | 318.6156 | 137.8 | 0 | 32119.3265 | 32119.3265
Bryant CC | 4500 | 40 | 11 | 0 | 78 | 75 | 3375 | 14494.8755 | 18.603 | 27.287 | 11.9575 | 0 | 45.89 | 30.5605 | 18.603 | 2531.25 | 1449.4876 | 3980.7376
Bryant CC | 4500 | 48.5625 | 5.5 | 14.0625 | 3 | 0 | 0 | 25777.8184 | 0.7155 | 33.1281 | 14.5171 | 0 | 33.8436 | 15.2326 | 0.7155 | 0 | 2577.7818 | 2577.7818
[8 empty] | Total carbon: 262 homes + commercial |  |  |  | Current | 3699.2229 | 2651.2807 | 1833.853 | total carbon |  | 302048.8928 | heating/cooling only
[12 empty] | with geo | 2777.3834 | 1439.9024 | 396.6255 | total carbon |  | 198221.9985 | heating/cooling only
*leftover geo carbon is DHW - those savings for homes are in the other table. DHW for commercial feasibility and cost is TBD

## Costs (hidden)
Very high level estimate for grant submittal purposes. These numbers will be re-visited in a couple months for DOE project submittal purposes.
*all buildings will be served condenser water from a centralized geothermal field with pumping stations - separate budget. Assume ductwork stays in place. Assume electric service is adequate for the compressor. Scope is to replace the main AHU/terminal system with the listed heat pump option.
Building | sf footage | Current HVAC system | Geothermal system option | ROM budget (total or per sf) | ROM budget - Total per building
Typical home | 1000 | Furnace and DX split | Geothermal water to air heat pump | 20000 per home | 5240000 | 262 homes
Bryant Elementary | 60000 | (14) Package RTU DX/gas fired: 12-20 tons each (HW boiler reheat?) | (14) Heat Pump RTUs : 15-20 tons each, (2) 35 ton WTW heat pump | $50 - $55 per sq ft | 3180000
County Health | 30000 | Packaged AHU: DX/gas fired: (2) 5 ton RTU, (2) 20 ton at grade, (4) 5-10 ton at grade | (8) Heat pump RTU. Electric reheat - 10 zones VAV boxes | $48 per sq ft | 1440000
PW Main | 40000 | (7) 20 ton Packaged AHU: DX/gas fired, (1) gas fired MAU, (5) DOAS units with ERW, (2) 500 Mbh boilers for terminal heat | (7) 20 ton Heat Pump RTU, (1) heat pump MAU, (5) 5-ton heat pump DOAS with ERW, (2) 35 ton WTW Heat pump | $50 - $55 per sq ft | 2120000
PW South Fleet/Maint | 40000 | (4) 500 Mbh Direct fired MAU - heating only | (4) 40 ton Heat Pump RTU | $38 - $40 per sq ft | 1560000
Public works east fleet | 65000 | (6) 500 Mbh Direct fired MAU - heating only, (3) 7.5 ton Packaged RTU, DX, gas fired heating | (6) 40 ton Heat Pump RTU, (3) 7.5 ton Heat Pump RTU | $38 - $40 per sq ft | 2535000
General allowance if new electrical service is required to the building ($/sf) |  |  |  | $10 - $12 per sq ft (does not include utility fees) | $300k-$500k per building if needed
[8 empty] | Btu | tons | # units | Btu | tons
[7 empty] | PW South Fleet/Maint | 1800000 | 150 | 4 | 450000 | 37.5
[7 empty] | Public works east fleet | 2925000 | 243.75 | 6 | 487500 | 40.625
Bryant Elementary |  | County Mental Health
PW Main
[5 empty] | Public works east fleet | [7 empty] | PW South Fleet/Maint

## Carbon - Q3 (hidden)
|  |  |  | lb/MWh | tons/kBtu
|  | Carbon factors | natural gas | - | 5.3e-05 |  | $/kWh | 0.1 |  |  |  |  | DTE renewable portfolio standard
|  |  | 2024 grid | 1438 | 0.00019105 |  | $/therm | 0.75 |  |  |  |  | 2030 - 50% renewable mandate
|  |  | 2030 grid | 500 | 6.6431e-05 | [7 empty] | 2040 - 100% renewable mandate
|  |  | 100% Renewable energy (2040) | 0 | 0 |  | DHW HP COP | 3
[7 empty] | Geo HP COP | 4
Appliance - per appliance consumption | EUI | Annual use (if gas - therm) | Annual use (if elec - kWh) | Carbon (nat. gas) | Carbon (elec 2024 grid) | Carbon (elec. 2030 grid) | Carbon (elec. Renewable - 2040) | Utility cost (gas) | Utility cost (elec) | kBtu gas | kBtu elec
Stove/range | - | 45 | 604 | 0.2385 | 0.39408 | 0.13702 | 0 | 33.75 | 60.4 | 4500 | 2062.66
Standard Dryer | - | 52.9 | 835 | 0.28037 | 0.5448 | 0.18943 | 0 | 39.675 | 83.5 | 5290 | 2851.525
Heat Pump Dryer | - | - | 278.3333 | - | 0.1816 | 0.063143 | 0 | - | 27.8333
Standard DHW | 10 | 21944.6 | 642594.4363 | 116.3064 | 419.2608 | 145.7791 | 0 | 16458.45 | 64259.4436
Heat Pump DHW | 3.3333 | - | 214198.1454 | - | 139.7536 | 48.593 | 0 | - | 21419.8145
Carbon savings (tons) for neighborhood |  |  | Current (gas) | 30608.2155 | - | - | - | 4331351.25
262 | homes |  | All electric | - | 110092.3146 | 38279.6643 | 0 | - | 16857851.2313
|  |  | All heat pump | - | 36766.2708 | 12783.8216 | 0 | - | 5619283.7438
Pathway - stay at 275 always or go to 252 today, 110 by 2030 and 0 by 2040 with DTE renewable goal
|  |  |  | Current (gas) | 30608.2155
|  |  |  | All Elec HP (2024 grid) | 36766.2708
|  |  |  | All Elec HP (2030 grid) | 12783.8216
|  |  |  | All Elec HP (2040 grid) | 0
Carbon (tons) and cost for heating/cooling only - leave DHW as gas. So we don't double count with savings above.
Building | sf footage | Total Elec EUI | Cooling EUI | Heating EUI (elec) | Total Gas EUI | Heating EUI (gas) | Annual heating use (gas - therms) | Annual heating + cooling use (elec - kWh) | Carbon (nat. gas) | Carbon (elec 2024 grid) | Carbon (elec. 2030 grid) | Carbon (elec. Renewable) | Total Carbon (gas+elec 2024 grid) | Total Carbon (gas+elec. 2030 grid) | Total Carbon (gas+elec. Renewable 2040 grid) | Heating utility cost (gas) | Htg+Clg utility cost (elec) | Total heating+cooling utility cost
Typical home (current) | 219446 | 28.6 | 7.4 | 0 | 82.2 | 73.4 | 161073.364 | 475519.8829 | 956.0384 | 1199.0859 | 416.9283 | 0 | 2155.1243 | 1372.9668 | 956.0384 | 120805.023 | 47551.9883 | 168357.0113
Typical home (geo) | 219446 | 36.5 | 4.7 | 14.5 | 8.8 | 0 | 0 | 1233781.3177 | 102.3496 | 1530.3019 | 532.0939 | 0 | 1632.6515 | 634.4435 | 102.3496 | 0 | 123378.1318 | 123378.1318
Bryant Elementary (current) | 56175 | 22.8 | 5.1 | 0 | 34 | 30.2 | 16964.85 | 83892.3865 | 101.2274 | 244.7003 | 85.0836 | 0 | 345.9277 | 186.3109 | 101.2274 | 12723.6375 | 8389.2387 | 21112.8762
Bryant Elementary (geo) | 56175 | 32.6 | 3.3 | 11.4 | 3.8 | 0 | 0 | 241807.4671 | 11.3136 | 349.8785 | 121.6546 | 0 | 361.1922 | 132.9682 | 11.3136 | 0 | 24180.7467 | 24180.7467
County Health (current) | 31278 | 24.8 | 4.2 | 0 | 36 | 30.8 | 9633.624 | 38467.8184 | 59.6784 | 148.1997 | 51.5298 | 0 | 207.8781 | 111.2082 | 59.6784 | 7225.218 | 3846.7818 | 11071.9998
County Health (geo) | 31278 | 34.9 | 2.7 | 11.6 | 5.2 | 0 | 0 | 130973.7628 | 8.6202 | 208.5552 | 72.5157 | 0 | 217.1754 | 81.1359 | 8.6202 | 0 | 13097.3763 | 13097.3763
PW Main (current) | 40824 | 32.1 | 6.3 | 0 | 39.3 | 34.3 | 14002.632 | 75312.2108 | 85.0323 | 250.3671 | 87.0539 | 0 | 335.3994 | 172.0862 | 85.0323 | 10501.974 | 7531.2211 | 18033.1951
PW Main (geo) | 40824 | 42.8 | 4 | 13 | 5 | 0 | 0 | 203223.4261 | 10.8184 | 333.8227 | 116.0719 | 0 | 344.6411 | 126.8902 | 10.8184 | 0 | 20322.3426 | 20322.3426
PW South Fleet/Maint (current) | 42604 | 38 | 2.4 | 0 | 34.3 | 29.3 | 12482.972 | 29941.3177 | 77.4498 | 309.3076 | 107.5478 | 0 | 386.7574 | 184.9976 | 77.4498 | 9362.229 | 2994.1318 | 12356.3608
PW South Fleet/Maint (geo) | 42604 | 48.2 | 1.6 | 11.1 | 5 | 0 | 0 | 158439.4729 | 11.2901 | 392.3322 | 136.4159 | 0 | 403.6223 | 147.706 | 11.2901 | 0 | 15843.9473 | 15843.9473
Public works east fleet (current) | 67506 | 34.4 | 0 | 0 | 40.7 | 35.7 | 24099.642 | 0 | 145.6172 | 443.6673 | 154.2654 | 0 | 589.2845 | 299.8826 | 145.6172 | 18074.7315 | 0 | 18074.7315
Public works east fleet (geo) | 67506 | 47.9 | 0 | 13.5 | 5 | 0 | 0 | 266861.2006 | 17.8891 | 617.7809 | 214.8056 | 0 | 635.67 | 232.6947 | 17.8891 | 0 | 26686.1201 | 26686.1201
Bryant CC | 4454 | 35.8 | 9.9 | 0 | 73.7 | 70.8 | 3153.432 | 12912.0351 | 17.3978 | 30.4642 | 10.5926 | 0 | 47.862 | 27.9903 | 17.3978 | 2365.074 | 1291.2035 | 3656.2775
Bryant CC | 4454 | 48.9 | 7 | 17.1 | 2.9 | 0 | 0 | 31432.328 | 0.68458 | 41.6117 | 14.4686 | 0 | 42.2963 | 15.1532 | 0.68458 | 0 | 3143.2328 | 3143.2328
[8 empty] | Total carbon: 262 homes + commercial |  |  |  | Current | 4068.2333 | 2355.4427 | 1442.4413 | total carbon |  | 252662.4522 | heating/cooling only
[12 empty] | with geo | 3637.2488 | 1370.9917 | 162.9656 | total carbon |  | 226651.8975 | heating/cooling only
*leftover geo carbon is DHW - those savings for homes are in the other table. DHW for commercial feasibility and cost is TBD

## Carbon - Final
|  |  |  | lb/MWh | tons/kBtu
|  | Carbon factors | natural gas | - | 5.3e-05 |  | $/kWh | 0.1 |  |  |  |  | DTE renewable portfolio standard
|  |  | 2024 grid | 1438 | 0.00019105 |  | $/therm | 0.75 |  |  |  |  | 2030 - 50% renewable mandate
|  |  | 2030 grid | 500 | 6.6431e-05 | [7 empty] | 2040 - 100% renewable mandate
|  |  | 100% Renewable energy (2040) | 0 | 0 |  | DHW HP COP | 3
[7 empty] | Geo HP COP | 4
Appliance - per appliance consumption | EUI | Annual use (if gas - therm) | Annual use (if elec - kWh) | Carbon (nat. gas) | Carbon (elec 2024 grid) | Carbon (elec. 2030 grid) | Carbon (elec. Renewable - 2040) | Utility cost (gas) | Utility cost (elec) | kBtu gas | kBtu elec
Stove/range | - | 45 | 604 | 0.2385 | 0.39408 | 0.13702 | 0 | 33.75 | 60.4 | 4500 | 2062.66
Standard Dryer | - | 52.9 | 835 | 0.28037 | 0.5448 | 0.18943 | 0 | 39.675 | 83.5 | 5290 | 2851.525
Heat Pump Dryer | - | - | 278.3333 | - | 0.1816 | 0.063143 | 0 | - | 27.8333
Standard DHW | 10 | 21944.6 | 642594.4363 | 116.3064 | 419.2608 | 145.7791 | 0 | 16458.45 | 64259.4436
Heat Pump DHW | 3.3333 | - | 214198.1454 | - | 139.7536 | 48.593 | 0 | - | 21419.8145
Carbon savings (tons) for neighborhood |  |  | Current (gas) | 30608.2155 | - | - | - | 4331351.25
262 | homes |  | All electric | - | 110092.3146 | 38279.6643 | 0 | - | 16857851.2313
|  |  | All heat pump | - | 36766.2708 | 12783.8216 | 0 | - | 5619283.7438
Pathway - stay at 275 always or go to 252 today, 110 by 2030 and 0 by 2040 with DTE renewable goal
|  |  |  | Current (gas) | 30608.2155
|  |  |  | All Elec HP (2024 grid) | 36766.2708
|  |  |  | All Elec HP (2030 grid) | 12783.8216
|  |  |  | All Elec HP (2040 grid) | 0
Carbon (tons) and cost for heating/cooling only - leave DHW as gas. So we don't double count with savings above.
Building | sf footage | Total Elec EUI | Cooling EUI | Heating EUI (elec) | Total Gas EUI | Heating EUI (gas) | Annual heating use (gas - therms) | Annual heating + cooling use (elec - kWh) | Carbon (nat. gas) | Carbon (elec 2024 grid) | Carbon (elec. 2030 grid) | Carbon (elec. Renewable) | Total Carbon (gas+elec 2024 grid) | Total Carbon (gas+elec. 2030 grid) | Total Carbon (gas+elec. Renewable 2040 grid)
262 homes (current) | 219446 | 28.6 | 7.4 | 0 | 82.2 | 73.4 | 161073.364 | 475519.8829 | 956.0384 | 1199.0859 | 416.9283 | 0 | 2155.1243 | 1372.9668 | 956.0384
262 homes (geo) | 219446 | 37.7 | 5.1 | 15.7 | 8.8 | 0 | 0 | 1336596.4275 | 102.3496 | 1580.6132 | 549.5873 | 0 | 1682.9628 | 651.937 | 102.3496
262 homes (geo+wx) | 219446 | 34.3 |  |  | 8.8 | 0 | 0 |  | 102.3496 | 1438.0645 | 500.0224 | 0 | 1540.4142 | 602.3721 | 102.3496
262 homes (geo + wx + pv) | 219446 | 8.04 |  |  | 8.8 | 0 | 0 |  | 102.3496 | 337.0857 | 117.2064 | 0 | 439.4353 | 219.556 | 102.3496
Bryant Elementary (current) | 56175 | 22.8 | 5.1 | 0 | 34 | 30.2 | 16964.85 | 83892.3865 | 101.2274 | 244.7003 | 85.0836 | 0 | 345.9277 | 186.3109 | 101.2274
Bryant Elementary (geo) | 56175 | 34.7 | 4.2 | 10.6 | 3.8 | 0 | 0 | 243452.4158 | 11.3136 | 372.4167 | 129.4912 | 0 | 383.7303 | 140.8048 | 11.3136
County Health (current) | 31278 | 24.8 | 4.2 | 0 | 36 | 30.8 | 9633.624 | 38467.8184 | 59.6784 | 148.1997 | 51.5298 | 0 | 207.8781 | 111.2082 | 59.6784
County Health (geo) | 31278 | 37.1 | 3.5 | 10.9 | 5.2 | 0 | 0 | 131889.6633 | 8.6202 | 221.7019 | 77.0869 | 0 | 230.3221 | 85.7071 | 8.6202
PW Main (current) | 40824 | 32.1 | 6.3 | 0 | 39.3 | 34.3 | 14002.632 | 75312.2108 | 85.0323 | 250.3671 | 87.0539 | 0 | 335.3994 | 172.0862 | 85.0323
PW Main (geo) | 40824 | 43.4 | 5.2 | 12.1 | 5 | 0 | 0 | 206809.7218 | 10.8184 | 338.5025 | 117.6991 | 0 | 349.3209 | 128.5174 | 10.8184
PW South Fleet/Maint (current) | 42604 | 38 | 2.4 | 0 | 34.3 | 29.3 | 12482.972 | 29941.3177 | 77.4498 | 309.3076 | 107.5478 | 0 | 386.7574 | 184.9976 | 77.4498
PW South Fleet/Maint (geo) | 42604 | 44.9 | 2 | 10.4 | 5 | 0 | 0 | 154696.8082 | 11.2901 | 365.4713 | 127.0763 | 0 | 376.7614 | 138.3663 | 11.2901
Public works east fleet (current) | 67506 | 34.4 | 0 | 0 | 40.7 | 35.7 | 24099.642 | 0 | 145.6172 | 443.6673 | 154.2654 | 0 | 589.2845 | 299.8826 | 145.6172
Public works east fleet (geo) | 67506 | 44.4 | 0 | 12.6 | 5 |  | 0 | 249070.4539 | 17.8891 | 572.6403 | 199.11 | 0 | 590.5294 | 216.9991 | 17.8891
Bryant CC | 4454 | 35.8 | 9.9 | 0 | 73.7 | 70.8 | 3153.432 | 12912.0351 | 17.3978 | 30.4642 | 10.5926 | 0 | 47.862 | 27.9903 | 17.3978
Bryant CC (geo) | 4454 | 49 | 8.6 | 14.4 | 2.9 | 0 | 0 | 29997.6574 | 0.68458 | 41.6968 | 14.4982 | 0 | 42.3814 | 15.1828 | 0.68458
Geo Pumping Homes | 219446 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.3561 | 48.1071 | 0 | 138.3561 | 48.1071 | 0
[8 empty] | Total carbon: 262 homes + commercial |  |  |  | BAU - Gas Heat | 4068.2333 | 2355.4427 | 1442.4413 | total carbon
[12 empty] | With Geothermal | 3794.3644 | 1425.6216 | 162.9656 | total carbon
[13 empty] | 6.732% | 39.48% | *leftover geo carbon is DHW - those savings for homes are in the other table. DHW for commercial feasibility and cost is TBD
[12 empty] | With Geothermal + Wx | 3651.8158 | 1376.0567 | 162.9656
[12 empty] | With Geothermal + Wx + PV | 2550.8369 | 993.2407 | 162.9656
[13 empty] | Homes | North Loop | Whole Neighborhood
[12 empty] | current | 2155.1243 | 2548.914 | 4068.2333
[12 empty] | geo | 1821.3189 | 2247.4306 | 3794.3644
[12 empty] | geo+2030 | 700.0441 | 856.0317 | 1425.6216