## T3D-Report Tables (hidden)
| System/Plant | Energy Cost |  | EUI |  | CO2 |  | Climate Zone: 5A | Baseline | Proposed: 1 | Proposed: 2 | Proposed: 3 | Proposed: 4 | Proposed: 5 | Proposed: 6 | Proposed: 7 | Proposed: 8 | ***Other Alternatives are Hidden
Index |  | ($/yr) | % Savings | (kBtu/sqft/yr) | % Savings | (metric tons) | % Savings | Envelope Construction
1 | Baseline | 0 | - | 0 | - | 0 | - | Exterior Walls | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065 | 90.1-10: U-0.065
2 | Proposed: 1 | 0 | - | 0 | - | 0 | - | Roof | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048 | 90.1-10: U-0.048
3 | Proposed: 2 | 0 | - | 0 | - | 0 | - | Slab on Grade | F-0.73 | F-0.74 | F-0.75 | F-0.76 | F-0.77 | F-0.76 | F-0.77 | F-0.76 | F-0.77
4 | Proposed: 3 | 0 | - | 0 | - | 0 | - | Windows | 90.1-10: U-0.45; SHGC: 0.40 | 90.1-10: U-0.45; SHGC: 0.41 | 90.1-10: U-0.45; SHGC: 0.42 | 90.1-10: U-0.45; SHGC: 0.43 | 90.1-10: U-0.45; SHGC: 0.44 | 90.1-10: U-0.45; SHGC: 0.43 | 90.1-10: U-0.45; SHGC: 0.44 | 90.1-10: U-0.45; SHGC: 0.43 | 90.1-10: U-0.45; SHGC: 0.44
5 | Proposed: 4 | 0 | - | 0 | - | 0 | - | Window to Wall Ratio | 20.6% | 120.6% | 220.6% | 320.6% | 420.6% | 320.6% | 420.6% | 320.6% | 420.6%
6 | Proposed: 5 | 0 | - | 0 | - | 0 | - | Electrical Systems
7 | Proposed: 6 | 0 | - | 0 | - | 0 | - | Lighting (W/sqft) | bar: F-0.73 to F-0.77
8 | Proposed: 7 | 0 | - | 0 | - | 0 | - | Receptacle Power (W/sqft) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
9 | Proposed: 8 | 0 | - | 0 | - | 0 | - | Mechanical and Plumbing Systems
[8 empty] | HVAC System Types | System 5 Sytem 10 System 7 | System 5 Sytem 10 System 8 | System 5 Sytem 10 System 9 | System 5 Sytem 10 System 10 | System 5 Sytem 10 System 11 | System 5 Sytem 10 System 10 | System 5 Sytem 10 System 11 | System 5 Sytem 10 System 10 | System 5 Sytem 10 System 11
| General Building Information | [6 empty] | Cooling Performance | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER | Air Cooled Unitary Dx - 9.5 EER
| Project Location | CITY | [5 empty] | Heating Performance | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80% | Hot Water Boiler - 80%
| Facility Use Type | TYPE | [5 empty] | Domestic Water Heating | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80% | Gas Water Heater - 80%
| Floor Area in Energy Model (ft2) | 8303 | [5 empty] | Other
| Total Number of Floors | # | [5 empty] | Schedule | F-0.73: M-F: 7 am - 7 pm, Sat: 8 am - 12 pm, Sunday Closed 12 months per year
Utility Rates: EIA State Average Rates
| Electricity | $/kWh | [5 empty] | IMEG INTERNAL MATRIX
| Natural Gas | $/Therm | [5 empty] | Total outside air (cfm) | bar: F-0.73; F-0.75
Heat Recovery | bar: F-0.73; F-0.75
| Utility Rates | [6 empty] | Economizer | bar: F-0.73; F-0.75
| Electric | 0.024597 | $/kBtu | 0.084 | /kWh
| Gas | 0.00757 | $/kBtu | 0.757 | /therms
| District Htg | 0.01229 | $/kBtu | 1.229 | /therms
| District Clg | 0.005964 | $/kBtu | 0.5964 | /therms
| Add Fuel | 0.013953 | $/kBtu | 1.3953 | /therms
| Carbon Emissions | lbs/MWH | tons of CO2/kBtu
| Electric | 1179 | 0.00015664
| Gas | - | 5.3e-05
| District Htg | -
| District Clg | - | 0.000157
| Add Fuel | -
Notes:
• Create bullet with Alt+7

## T3D Data (hidden)
|  |  | End Use Selection | [6 empty] | Baseline | [6 empty] | Proposed: 1 | [6 empty] | Proposed: 2 | [6 empty] | Proposed: 3 | [6 empty] | Proposed: 4 | [6 empty] | Proposed: 5 | [6 empty] | Proposed: 6 | [6 empty] | Proposed: 7 | [6 empty] | Proposed: 8
|  |  | Lighting | Heating | Cooling | Pump | Fan | Recep | DHW |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu) |  |  | Electricity (kWh) | Gas (Mbtu) | District Cooling (Mbtu) | District Heating (Mbtu) | Other Utilities (Mbtu)
|  |  |  | x | [5 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating
[5 empty] | x |  |  |  |  | Cooling | [6 empty] | Cooling | [6 empty] | Cooling | [6 empty] | Cooling | [6 empty] | Cooling | [6 empty] | Cooling | [6 empty] | Cooling | [6 empty] | Cooling | [6 empty] | Cooling
[7 empty] | x |  |  | Fans | [6 empty] | Fans | [6 empty] | Fans | [6 empty] | Fans | [6 empty] | Fans | [6 empty] | Fans | [6 empty] | Fans | [6 empty] | Fans | [6 empty] | Fans
[6 empty] | x |  |  |  | Pumps | [6 empty] | Pumps | [6 empty] | Pumps | [6 empty] | Pumps | [6 empty] | Pumps | [6 empty] | Pumps | [6 empty] | Pumps | [6 empty] | Pumps | [6 empty] | Pumps
[5 empty] | x |  |  |  |  | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection | [6 empty] | Heat Rejection
|  |  |  | x | [5 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification | [6 empty] | Humidification
|  |  |  | x | [5 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery | [6 empty] | Heat Recovery
[10 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC | [6 empty] | HVAC
[9 empty] | x | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems | [6 empty] | Water Systems
|  |  | x | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting | [6 empty] | Interior Lighting
|  |  | x | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting | [6 empty] | Exterior Lighting
[8 empty] | x |  | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment | [6 empty] | Interior Equipment
[8 empty] | x |  | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment | [6 empty] | Exterior Equipment
[5 empty] | x |  |  |  |  | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration | [6 empty] | Refrigeration
[10 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC | [6 empty] | Non-HVAC
[8 empty] | x |  | Generators | [6 empty] | Generators | [6 empty] | Generators | [6 empty] | Generators | [6 empty] | Generators | [6 empty] | Generators | [6 empty] | Generators | [6 empty] | Generators | [6 empty] | Generators
[10 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation | [6 empty] | Site Generation
[10 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total | [6 empty] | Grand Total
Index | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Baseline | Proposed: 1 | Proposed: 2 | Proposed: 3 | Proposed: 4 | Proposed: 5 | Proposed: 6 | Proposed: 7 | Proposed: 8 |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI |  | Electric | Gas | District Clg | District Htg | Add Fuel | EUI
Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0
Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0
Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0
DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0
EUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | 0
| Savings: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0
Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0
Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0
DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0
Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0
| Savings: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Carbon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0
| Savings: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## T3D-End Use (hidden)
EUI End Use Breakdown
Energy Category | Baseline | Proposed: 1 | Proposed: 2 | Proposed: 3 | Proposed: 4 | Proposed: 5 | Proposed: 6 | Proposed: 7 | Proposed: 8
Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savings | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Savings: | - | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Energy Cost Breakdown
Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savings | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost Savings: | - | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%

## T-End Use (hidden)
EUI End Use Breakdown
Energy Category | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Lighting | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cooling | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Fans | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Receptacles | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Savings | - | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total: | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0
Energy Savings: | - | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Energy Cost Breakdown
Lighting | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Heating | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Cooling | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Pumps | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Fans | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Receptacles | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DHW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Savings | - | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total: | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0
Cost Savings: | - | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%

## Audit Screenshots
Elevate Data
Majority of the measured homes are 860 sf
Snugg Pro Base
Snugg Pro Improved
Wall R-Value | [6 empty] | Heating Setpoints | ach input | https://efficiencymatrix.com/air-leakage-unit-conversion/
Roof R-Value
Cooling Setpoints
Total EUI
NREL Data
Michigan EUI Breakdown
|  | Process |  | 2.2 | EUI
|  | Plug |  | 9.6 | EUI
|  | Cooling |  | 4.2
EIA | https://experience.arcgis.com/experience/cbf6875974554a74823232f84f563253
DOE | https://www.energycodes.gov/prototype-building-models#Residential
5 MCF
| 61200 | kBtu
71.1628
Different Scenarios
33%
Worst One | 50% | 25% | 25%
25%
Ave = 70
Ave = 15
Ave = 85
Ave = 25
Ave = 33
Ave = 10
Ave: R-12
Ave: R-11.7
Ave: R-11.5
Ave: R-37
Ave: R-28.6
Ave: R-23.7
Best Performing
Total Average = 66
Gas Ave = 50.7
Elec Ave = 15.7
Mid Performing
Total Average = 88
Gas Ave = 68.5
Elec Ave = 20
Worst Performing
Total Average = 120
Gas Ave = 96.9
Elec Ave = 22.9
14 count
36%
12 count
31%
13 count
33%
Best
Worst
Mid
Ave: 67/65
Ave: 70/68
Ave: 71/69
Ave: 73/74
Ave: 73/73
Ave: 70/70
Ave: 30
Ave: 34
Ave: 47
Best
Worst
Mid
Best
Worst
Mid
Best
Worst
Mid
Best
Worst
Mid

## Modeling Journal (hidden)
Bryant Neighborhood, Ann Arbor, Michigan |  | Energy Model |  |  | Geothemal
|  | 262 households |  |  | City Park
|  | Community Center |  |  | School Grassy Area
|  | Public School |  |  | County Mental Health Facility Parking Lot
|  | County Mental Health Facility |  |  | City's Public Works Open Land
|  | City's Public Works Facility |  |  | Sidewalks | lots of courts
1000-1500 ton system
[5 empty] | 1 borehole = 3tons |  |  | 500 | bores
[5 empty] | 500 sf = 1 borehold |  |  | 250000 | sf of space
[8 empty] | 5.7392 | acres
[5 empty] | Need a central space for the tank building |  |  |  | could use as an educational building
if the field is all over the place, wouldn't that make maintenance hard? But then think about resilience
| 5GDHC | 5th Generation District Heating and Cooling System
| Gen 4 | [8 empty] | Gen 5
| Baseline Energy Model of exisitng buildings |  |  |  | we have data to go off of
| Proposed Energy Model with improvements |  |  |  | geothermal or weatherization or hybrid
|  | Could model the homes and just multiply by 262 |  |  |  | Zone multiplier
Model the other commercial buildings seperately
|  | What do we want as an end product? |  |  |  | hourly load profile data? |  |  |  | provide these profiles
our geothermal load profiles will be sent to DOE
will likely have to explain how we modeled it
similar buildings can be grouped
zone multiplied
[7 empty] | setpoints | system types | weatherization level
maybe depends on our data and how it's looking
internal and external loads are same
setpoint schedules
occupancy schedules
throw them into a power bi
DHW is currently gas, how do we do geothermal DHW?
Are there any resources that they plan to make available to the project?
Want to reach NREL for residential energy model template?
[8 empty] | ResStock | data nationally
this looks good I think. the narrative needs to show progress - not any type of verification of final results. I am thinking if we can share the following, we would be in good shape
1. scatter plot/line charts/power bi of the existing home energy use (chuck can do the commercial buildings)
1. screenshot of the database from Elevate
2. Indication of energy model progress (some combination of)
1. screenshot of building geometry/setup in design builder
2. plots showing relative alignment with some segment of the existing home energy usage
3. Key inputs matrix - what is driving the model at this point
start the narrative?
first quarter (oct-end of dec)
the em is owed in month 4
NREL Research | Look for schedules |  | DHW, Lighting, Plug
| Setpoints |  | Averages
EUI breakdown of Michigan
Next steps
Align DB results with excel
Look at NREL packages and the results from that
2024-07-03 | Prep for the NREL Q4 ComGeo |  |  |  |  | Add generic background information?
20 minute – ComGeo Coalition / Team representative reviews project data they plan to upload to the DOE Geothermal Data Repository (GDR) and in what format they plan to upload it. GDR data curators will be available for the first 20 minutes of the call to assist with any questions about the type of data that should be uploaded and in what format. References to the relevant project data may be found in the Statement of Project Objectives (SOPO).
|  |  |  | ELEVATE Energy Audits |  | Do they want the power bi?
|  |  |  | DTE Utility Data |  | Do they want the raw data or the editted data?
Do they want this benchmarking material?
Energy Model
20 minute – ComGeo Team reviews information they plan to include in preliminary case studies and asks any questions they may have.
20 minutes – ComGeo Teams and GTO discuss the Q3 report highlights or concerns.

## Garcia PV Study - mid data (hidden)
Date/Time | Existing - Electric/Cooling | Existing - Heating/Natural Gas | Cost | Electric - PV | NG-PV-Heating | Cost | Cooling - Geo | Heating - Geo | Cost | Cooling - Geo - PV | Heating - Geo - PV | Cost
Jan | 1446.2814 | 13922.5178 | 195.2645 | 875.3808 | 13922.5178 | 162.1522 | 1446.2814 | 3521.6706 | 260.6412 | 875.3808 | 3521.6706 | 227.529
Feb | 1305.7919 | 10503.0763 | 159.7605 | 629.2714 | 10503.0763 | 120.5224 | 1305.7919 | 2761.7947 | 208.42 | 629.2714 | 2761.7947 | 169.1818
Mar | 1415.1926 | 8032.8341 | 146.3438 | 358.4534 | 8032.8341 | 85.053 | 1415.1926 | 2212.852 | 182.9266 | 358.4534 | 2212.852 | 121.6357
Apr | 1321.4173 | 5456.7779 | 120.2964 | 215.165 | 5456.7779 | 56.1338 | 550.5905 | 1640.3951 | 99.5772 | -555.6618 | 1640.3951 | 35.4145
May | 1579.5757 | 1945.6368 | 107.1805 | 166.2711 | 1945.6368 | 25.2088 | 658.1565 | 860.1415 | 60.5613 | -755.148 | 860.1415 | -21.4104
Jun | 2128.4329 | 1007.8813 | 131.5122 | 49.01 | 1007.8813 | 10.9056 | 886.847 | 651.7514 | 61.7387 | -1192.5759 | 651.7514 | -44.6871
Jul | 2506.761 | 887.7162 | 152.4939 | 0 | 887.7162 | 7.1017 | 1044.4838 | 625.048 | 69.3328 | -1462.2773 | 625.048 | -58.0253
Aug | 2311.0966 | 928.5936 | 141.4724 | 266.0802 | 928.5936 | 22.8614 | 962.9569 | 634.1319 | 65.1312 | -1082.0595 | 634.1319 | -40.5067
Sep | 1544.3856 | 1510.69 | 101.6599 | 302.2728 | 1510.69 | 29.6173 | 643.494 | 763.4867 | 54.1049 | -598.6188 | 763.4867 | -17.9377
Oct | 1285.7024 | 4247.4443 | 108.5503 | 537.1191 | 4247.4443 | 65.1325 | 1285.7024 | 1371.6543 | 126.6267 | 537.1191 | 1371.6543 | 83.2089
Nov | 1313.3975 | 7102.7054 | 132.9987 | 715.024 | 7102.7054 | 98.293 | 1313.3975 | 2006.1567 | 165.0341 | 715.024 | 2006.1567 | 130.3285
Dec | 1445.4087 | 10766.936 | 169.9692 | 953.3041 | 10766.936 | 141.4271 | 1445.4087 | 2820.4302 | 219.9187 | 953.3041 | 2820.4302 | 191.3766
|  |  | 1667.5022 |  |  | 824.4089 |  |  | 1574.0134 |  | 0 | 776.1078
| 23.6186 | 79.895 |  |  |  | 50.56% |  |  | 5.607% |  |  | 53.46%
NG | 0.008 | /kbtu | [9 empty] | 5.859%
Inflow Electric | 0.058 | /kbtu
Outflow Electric | 0.045 | /kbtu | [8 empty] | Because geo is more efficient than the AC, cooling energy should decrease & PV can be used for more receptacle load
PV will be connected to the grid a half price back
AC COP | 2.5
Geo Cooling COP | 6 |  |  | 20 | 80 | 100
Geo Heating COP | 4.5 |  |  | 20 | 560 | 580
5.8
Note on B19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Joe DTE Rate Changes and Solar

## Homes - Inputs
| System/Plant | Energy Cost |  | EUI |  | CO2 |  | Climate Zone: 5A | Worst - Existing | Mid - Existing | Best - Existing | DOE Benchmark - Homes | Worst - Wx | Mid - Wx | Best - Wx | Worst - Geo | Mid - Geo | Best - Geo | Worst - Geo + Wx | Mid - Geo + Wx | Best - Geo + Wx
Index |  | ($/yr) | % Savings | (kBtu/sqft/yr) | % Savings | (metric tons) | % Savings | Envelope Construction
1 | Worst - Existing | 2113.9399 | - | 130.1433 | - | 9.2648 | - | Exterior Walls | R-11.5 | R-11.6 | R-12 | ASHRAE 2006 | R-12 | R-12 | R-12 | R-11.5 | R-11.6 | R-12 | R-12 | R-12 | R-12
2 | Mid - Existing | 1652.374 | 21.83% | 102.6453 | 21.13% | 7.2657 | 21.58% | Roof | R-23.7 | R-28.6 | R-37 |  | R-37 | R-37 | R-37 | R-23.7 | R-28.6 | R-37 | R-37 | R-37 | R-37
3 | Best - Existing | 1322.0343 | 37.46% | 81.1807 | 37.62% | 5.7887 | 37.52% | Slab on Grade | F-0.73 | F-0.73 | F-0.73 |  | F-0.73 | F-0.73 | F-0.73 | F-0.73 | F-0.73 | F-0.73 | F-0.73 | F-0.73 | F-0.73
4 | DOE Benchmark - Homes | 0 | - | 90.3175 | 30.6% | 0 | - | Windows | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 |  | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55 | U-0.55, SHGC-0.55
5 | Worst - Wx | 1867.511 | 11.66% | 109.0603 | 16.2% | 8.0312 | 13.31% | Window to Wall Ratio | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% |  | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% | 2 sides: 20% | 2 sides: 20%
6 | Mid - Wx | 1554.2546 | 26.48% | 93.6705 | 28.03% | 6.7595 | 27.04% | Infiltration (ach) | 1.85 | 1.65 | 1.45 |  | 1.45 | 1.45 | 1.45 | 1.85 | 1.65 | 1.45 | 1.45 | 1.45 | 1.45
7 | Best - Wx | 1322.0343 | 37.46% | 81.1807 | 37.62% | 5.7887 | 37.52% | Electrical Systems
8 | Worst - Geo | 1902.9196 | 9.982% | 49.7536 | 61.77% | 6.5895 | 28.88% | Lighting (W/sqft) (2-3% of EUI) | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
9 | Mid - Geo | 1507.9022 | 28.67% | 40.1902 | 69.12% | 5.2414 | 43.43% | Receptacle Power (W/sqft) (12-16% of EUI) | 0.35 | 0.3 | 0.25 |  | 0.35 | 0.3 | 0.25 | 0.35 | 0.3 | 0.25 | 0.35 | 0.3 | 0.25
10 | Best - Geo | 1196.8505 | 43.38% | 32.9166 | 74.71% | 4.1866 | 54.81% | Process Load (W/sf) | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
11 | Worst - Geo + Wx | 1671.8484 | 20.91% | 44.9643 | 65.45% | 5.8218 | 37.16% | Mechanical and Plumbing Systems
12 | Mid - Geo + Wx | 1399.2834 | 33.81% | 37.9353 | 70.85% | 4.8805 | 47.32% | HVAC System Types | Furnace + AC | Furnace + AC | Furnace + AC |  | Furnace + AC | Furnace + AC | Furnace + AC | Geothermal HP | Geothermal HP | Geothermal HP | Geothermal HP | Geothermal HP | Geothermal HP
13 | Best - Geo + Wx | 1196.8505 | 43.38% | 32.9166 | 74.71% | 4.1866 | 54.81% | Cooling Performance | Air Cooled Unitary Dx - 8.5 EER | Air Cooled Unitary Dx - 8.5 EER | Air Cooled Unitary Dx - 8.5 EER |  | Air Cooled Unitary Dx - 8.5 EER | Air Cooled Unitary Dx - 8.5 EER | Air Cooled Unitary Dx - 8.5 EER | 20 EER, COP 5.8 | 20 EER, COP 5.8 | 20 EER, COP 5.8 | 20 EER, COP 5.8 | 20 EER, COP 5.8 | 20 EER, COP 5.8
[8 empty] | Heating Performance | Furnace - 75% | Furnace - 80% | Furnace - 85% |  | Furnace - 75% | Furnace - 80% | Furnace - 85% | COP - 4 | COP - 4 | COP - 4 | COP - 4 | COP - 4 | COP - 4
[8 empty] | Domestic Water Heating (9-11% of EUI) | 0.030 gal/sf/day Gas Water Heater - 80% | 0.025 gal/sf/day Gas Water Heater - 80% | 0.02 gal/sf/day Gas Water Heater - 80% |  | 0.030 gal/sf/day Gas Water Heater - 80% | 0.025 gal/sf/day Gas Water Heater - 80% | 0.02 gal/sf/day Gas Water Heater - 80% | 0.030 gal/sf/day Gas Water Heater - 80% | 0.025 gal/sf/day Gas Water Heater - 80% | 0.02 gal/sf/day Gas Water Heater - 80% | 0.030 gal/sf/day Gas Water Heater - 80% | 0.025 gal/sf/day Gas Water Heater - 80% | 0.02 gal/sf/day Gas Water Heater - 80%
Other
[8 empty] | Schedule | Residential Home Schedule |  |  |  | Residential Home Schedule |  |  | Residential Home Schedule |  |  | Residential Home Schedule
[8 empty] | Setpoints | H: 71/69, C: 70/70 | H: 70/68, C: 73/73 | H: 67/65, C: 74/74 |  | H: 71/69, C: 70/70 | H: 70/68, C: 73/73 | H: 67/65, C: 74/74 | H: 71/69, C: 70/70 | H: 70/68, C: 73/73 | H: 67/65, C: 74/74 | H: 71/69, C: 70/70 | H: 70/68, C: 73/73 | H: 67/65, C: 74/74
[8 empty] | Zone Sizing | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F |  | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F | H: 95 F, C: 45 F
General Building Information
| Project Location | Ann Arbor
| Facility Use Type | Bryant Neighborhood Residential | DOE Prototype Building sf
| Floor Area in Energy Model (ft2) | 837.58 | 2377
| Total Number of Floors | 1
Utility Rates: EIA State Average Rates
| Electricity | $/kWh
| Natural Gas | $/Therm
| Utility Rates |  |  | Residential |  | Outflow Cost
| Electric | 0.057511 | $/kBtu | 0.1964 | /kWh | 0.0877 | /kWh
| Gas | 0.0078998 | $/kBtu | 0.78998 | /therms
| District Htg | 0 | $/kBtu |  | /therms
| District Clg | 0 | $/kBtu |  | /therms
| Add Fuel | 0 | $/kBtu |  | /therms
| Carbon Emissions | lbs/MWH | tons of CO2/kBtu
| Electric | 1438.38 | 0.0001911
| Gas | - | 5.3e-05
| District Htg | -
| District Clg | -
| Add Fuel | -
[9 empty] | All 262 homes - Existing - TMY3 | All 262 homes - Wx - TMY3 | Savings
[8 empty] | Heating Modeled Peak (tons) | 655.4474 | 570.1653 | 13.01%
[8 empty] | Cooling Modeled Peak (tons) | 441.6854 | 396.8039 | 10.16%
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Green Text = based on data from energy audits. Red Text = assumptions
Note on F35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thea - DTE/Utility provided information, general estimates
Note on H35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Joe - DTE Solar Outflow Values
Note on D42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thea - DTE Electricity Emissions Estimate and Forecast

## Homes - 2022
|  |  | End Use Selection | [11 empty] | Worst - Existing | [8 empty] | Mid - Existing | [8 empty] | Best - Existing | [8 empty] | DOE Benchmark - Homes | [7 empty] | Worst - Wx | [6 empty] | Mid - Wx | [6 empty] | Best - Wx | [6 empty] | Worst - Geo | [6 empty] | Mid - Geo | [6 empty] | Best - Geo | [6 empty] | Worst - Geo + Wx | [6 empty] | Mid - Geo + Wx | [6 empty] | Best - Geo + Wx
|  |  | Lighting | Heating | Cooling | Pump | Fan | Recep | DHW | [6 empty] | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal]
|  |  |  | x | [10 empty] | Heating | 0 | 73803.52 | [6 empty] | Heating | 0 | 57729 | [6 empty] | Heating | 0 | 44339.3 | [6 empty] | Heating | 0 | 141512.23 | [5 empty] | Heating | 0 | 58300.92 |  |  |  |  | Heating | 0 | 50992.98 |  |  |  |  | Heating | 0 | 44339.3 |  |  |  |  | Heating | 15663.39 | 0 |  |  |  |  | Heating | 11846.21 | 0 |  |  |  |  | Heating | 8815.45 | 0 |  |  |  |  | Heating | 12174.65 | 0 |  |  |  |  | Heating | 10371.55 | 0 |  |  |  |  | Heating | 8815.45 | 0
[5 empty] | x | [9 empty] | Cooling | 8298.2 | 0 | [6 empty] | Cooling | 5297.66 | 0 | [6 empty] | Cooling | 4199.95 | 0 | [6 empty] | Cooling | 4618.12 | 0 | [5 empty] | Cooling | 7580.72 | 0 |  |  |  |  | Cooling | 5152.04 | 0 |  |  |  |  | Cooling | 4199.95 | 0 |  |  |  |  | Cooling | 3802.25 | 0 |  |  |  |  | Cooling | 2341.07 | 0 |  |  |  |  | Cooling | 1971.62 | 0 |  |  |  |  | Cooling | 4034.15 | 0 |  |  |  |  | Cooling | 2332.68 | 0 |  |  |  |  | Cooling | 1971.62 | 0
|  |  | x | [11 empty] | Interior Lighting | 2400.63 | 0 | [6 empty] | Interior Lighting | 2400.63 | 0 | [6 empty] | Interior Lighting | 2400.63 | 0 | [6 empty] | Interior Lighting | 5537.46 | 0 | [5 empty] | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0 |  |  |  |  | Interior Lighting | 2400.63 | 0
|  |  | x | [11 empty] | Exterior Lighting | 0 | 0 | [6 empty] | Exterior Lighting | 0 | 0 | [6 empty] | Exterior Lighting | 0 | 0 | [6 empty] | Exterior Lighting | 1312.91 | 0 | [5 empty] | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0
[8 empty] | x | [6 empty] | Interior Equipment | 7087.09 | 2024.88 | [6 empty] | Interior Equipment | 6074.65 | 2024.88 | [6 empty] | Interior Equipment | 5062.21 | 2024.88 | [6 empty] | Interior Equipment | 24063.37 | 11013.86 | [5 empty] | Interior Equipment | 7087.09 | 2024.88 |  |  |  |  | Interior Equipment | 6074.65 | 2024.88 |  |  |  |  | Interior Equipment | 5062.21 | 2024.88 |  |  |  |  | Interior Equipment | 7087.09 | 2024.88 |  |  |  |  | Interior Equipment | 6074.65 | 2024.88 |  |  |  |  | Interior Equipment | 5062.21 | 2024.88 |  |  |  |  | Interior Equipment | 7087.09 | 2024.88 |  |  |  |  | Interior Equipment | 6074.65 | 2024.88 |  |  |  |  | Interior Equipment | 5062.21 | 2024.88
[8 empty] | x | [6 empty] | Exterior Equipment | 0 | 0 | [6 empty] | Exterior Equipment | 0 | 0 | [6 empty] | Exterior Equipment | 0 | 0 | [6 empty] | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0
[7 empty] | x | [7 empty] | Fans | 7465.88 | 0 | [6 empty] | Fans | 5842.81 | 0 | [6 empty] | Fans | 4157.23 | 0 | [6 empty] | Fans | 6054.68 | 0 | [5 empty] | Fans | 6028.03 | 0 |  |  |  |  | Fans | 5207.64 | 0 |  |  |  |  | Fans | 4157.23 | 0 |  |  |  |  | Fans | 2479.58 | 0 |  |  |  |  | Fans | 2150.02 | 0 |  |  |  |  | Fans | 1308.05 | 0 |  |  |  |  | Fans | 1753.72 | 0 |  |  |  |  | Fans | 1763.29 | 0 |  |  |  |  | Fans | 1308.05 | 0
[6 empty] | x | [8 empty] | Pumps | 0.94 | 0 | [6 empty] | Pumps | 0.78 | 0 | [6 empty] | Pumps | 0.69 | 0 | [6 empty] | Pumps | 0 | 0 | [5 empty] | Pumps | 0.94 | 0 |  |  |  |  | Pumps | 0.78 | 0 |  |  |  |  | Pumps | 0.69 | 0 |  |  |  |  | Pumps | 288.02 | 0 |  |  |  |  | Pumps | 221.6 | 0 |  |  |  |  | Pumps | 176.52 | 0 |  |  |  |  | Pumps | 251.83 | 0 |  |  |  |  | Pumps | 202.71 | 0 |  |  |  |  | Pumps | 176.52 | 0
[5 empty] | x | [9 empty] | Heat Rejection | 0 | 0 | [6 empty] | Heat Rejection | 0 | 0 | [6 empty] | Heat Rejection | 0 | 0 | [6 empty] | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0
|  |  |  | x | [10 empty] | Humidification | 0 | 0 | [6 empty] | Humidification | 0 | 0 | [6 empty] | Humidification | 0 | 0 | [6 empty] | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0
|  |  |  | x | [10 empty] | Heat Recovery | 0 | 0 | [6 empty] | Heat Recovery | 0 | 0 | [6 empty] | Heat Recovery | 0 | 0 | [6 empty] | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0
[9 empty] | x | [5 empty] | Water Systems | 0 | 7924.28 | [6 empty] | Water Systems | 0 | 6603.2 | [6 empty] | Water Systems | 0 | 5810.48 | [6 empty] | Water Systems | 0 | 20572.16 | [5 empty] | Water Systems | 0 | 7923.5 |  |  |  |  | Water Systems | 0 | 6602.92 |  |  |  |  | Water Systems | 0 | 5810.48 |  |  |  |  | Water Systems | 0 | 7926.76 |  |  |  |  | Water Systems | 0 | 6603.43 |  |  |  |  | Water Systems | 0 | 5810.9 |  |  |  |  | Water Systems | 0 | 7934.25 |  |  |  |  | Water Systems | 0 | 6603.48 |  |  |  |  | Water Systems | 0 | 5810.9
[5 empty] | x | [9 empty] | Refrigeration | 0 | 0 | [6 empty] | Refrigeration | 0 | 0 | [6 empty] | Refrigeration | 0 | 0 | [6 empty] | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0
[15 empty] | Generators | 0 | 0 | [6 empty] | Generators | 0 | 0 | [6 empty] | Generators | 0 | 0 | [6 empty] | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0
[15 empty] | Total End Uses | 25252.74 | 83752.68 | [6 empty] | Total End Uses | 19616.53 | 66357.09 | [6 empty] | Total End Uses | 15820.72 | 52174.67 | [6 empty] | Total End Uses | 41586.55 | 173098.25 | [5 empty] | Total End Uses | 23097.42 | 68249.3 |  |  |  |  | Total End Uses | 18835.74 | 59620.78 |  |  |  |  | Total End Uses | 15820.72 | 52174.67 |  |  |  |  | Total End Uses | 31720.96 | 9951.64 |  |  |  |  | Total End Uses | 25034.18 | 8628.31 |  |  |  |  | Total End Uses | 19734.48 | 7835.78 |  |  |  |  | Total End Uses | 27702.07 | 9959.13 |  |  |  |  | Total End Uses | 23145.52 | 8628.37 |  |  |  |  | Total End Uses | 19734.48 | 7835.78
Index | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Worst - Existing | Mid - Existing | Best - Existing | DOE Benchmark - Homes | Worst - Wx | Mid - Wx | Best - Wx | Worst - Geo | Mid - Geo | Best - Geo | Worst - Geo + Wx | Mid - Geo + Wx | Best - Geo + Wx |  |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | % Contribution | Target |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | % Contribution | Target |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | % Contribution | Target |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | % Contribution |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI
Lighting | 2.8662 | 2.8662 | 2.8662 | 2.8819 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 2.8662 |  | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | 2.388% |  | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | 2.792% |  | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | 3.531% |  | Lighting | 6850.37 | 0 | 0 | 0 | 0 | 2.8819 | 3.191% | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662 | Lighting | 2400.63 | 0 | 0 | 0 | 0 | 2.8662
Heating | 88.1152 | 68.9236 | 52.9374 | 59.534 | 69.6064 | 60.8813 | 52.9374 | 18.7008 | 14.1434 | 10.5249 | 14.5355 | 12.3828 | 10.5249 |  | Heating | 0 | 73803.52 | 0 | 0 | 0 | 88.1152 | 73.43% | 97 | Heating | 0 | 57729 | 0 | 0 | 0 | 68.9236 | 67.15% | 68.5 | Heating | 0 | 44339.3 | 0 | 0 | 0 | 52.9374 | 65.21% | 50 | Heating | 0 | 141512.23 | 0 | 0 | 0 | 59.534 | 65.92% | Heating | 0 | 58300.92 | 0 | 0 | 0 | 69.6064 | Heating | 0 | 50992.98 | 0 | 0 | 0 | 60.8813 | Heating | 0 | 44339.3 | 0 | 0 | 0 | 52.9374 | Heating | 15663.39 | 0 | 0 | 0 | 0 | 18.7008 | Heating | 11846.21 | 0 | 0 | 0 | 0 | 14.1434 | Heating | 8815.45 | 0 | 0 | 0 | 0 | 10.5249 | Heating | 12174.65 | 0 | 0 | 0 | 0 | 14.5355 | Heating | 10371.55 | 0 | 0 | 0 | 0 | 12.3828 | Heating | 8815.45 | 0 | 0 | 0 | 0 | 10.5249
Cooling | 9.9074 | 6.325 | 5.0144 | 1.9428 | 9.0507 | 6.1511 | 5.0144 | 4.5396 | 2.795 | 2.3539 | 4.8164 | 2.785 | 2.3539 |  | Cooling | 8298.2 | 0 | 0 | 0 | 0 | 9.9074 | 8.256% | 23 | Cooling | 5297.66 | 0 | 0 | 0 | 0 | 6.325 | 6.162% | 20 | Cooling | 4199.95 | 0 | 0 | 0 | 0 | 5.0144 | 6.177% | 16 | Cooling | 4618.12 | 0 | 0 | 0 | 0 | 1.9428 | 2.151% | Cooling | 7580.72 | 0 | 0 | 0 | 0 | 9.0507 | Cooling | 5152.04 | 0 | 0 | 0 | 0 | 6.1511 | Cooling | 4199.95 | 0 | 0 | 0 | 0 | 5.0144 | Cooling | 3802.25 | 0 | 0 | 0 | 0 | 4.5396 | Cooling | 2341.07 | 0 | 0 | 0 | 0 | 2.795 | Cooling | 1971.62 | 0 | 0 | 0 | 0 | 2.3539 | Cooling | 4034.15 | 0 | 0 | 0 | 0 | 4.8164 | Cooling | 2332.68 | 0 | 0 | 0 | 0 | 2.785 | Cooling | 1971.62 | 0 | 0 | 0 | 0 | 2.3539
Pumps | 0.0011223 | 0.00093125 | 0.0008238 | 0 | 0.0011223 | 0.00093125 | 0.0008238 | 0.34387 | 0.26457 | 0.21075 | 0.30066 | 0.24202 | 0.21075 |  | Pumps | 0.94 | 0 | 0 | 0 | 0 | 0.0011223 | 0.0009352% |  | Pumps | 0.78 | 0 | 0 | 0 | 0 | 0.00093125 | 0.0009073% |  | Pumps | 0.69 | 0 | 0 | 0 | 0 | 0.0008238 | 0.001015% |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0% | Pumps | 0.94 | 0 | 0 | 0 | 0 | 0.0011223 | Pumps | 0.78 | 0 | 0 | 0 | 0 | 0.00093125 | Pumps | 0.69 | 0 | 0 | 0 | 0 | 0.0008238 | Pumps | 288.02 | 0 | 0 | 0 | 0 | 0.34387 | Pumps | 221.6 | 0 | 0 | 0 | 0 | 0.26457 | Pumps | 176.52 | 0 | 0 | 0 | 0 | 0.21075 | Pumps | 251.83 | 0 | 0 | 0 | 0 | 0.30066 | Pumps | 202.71 | 0 | 0 | 0 | 0 | 0.24202 | Pumps | 176.52 | 0 | 0 | 0 | 0 | 0.21075
Fans | 8.9136 | 6.9758 | 4.9634 | 2.5472 | 7.197 | 6.2175 | 4.9634 | 2.9604 | 2.5669 | 1.5617 | 2.0938 | 2.1052 | 1.5617 |  | Fans | 7465.88 | 0 | 0 | 0 | 0 | 8.9136 | 7.428% |  | Fans | 5842.81 | 0 | 0 | 0 | 0 | 6.9758 | 6.796% |  | Fans | 4157.23 | 0 | 0 | 0 | 0 | 4.9634 | 6.114% |  | Fans | 6054.68 | 0 | 0 | 0 | 0 | 2.5472 | 2.82% | Fans | 6028.03 | 0 | 0 | 0 | 0 | 7.197 | Fans | 5207.64 | 0 | 0 | 0 | 0 | 6.2175 | Fans | 4157.23 | 0 | 0 | 0 | 0 | 4.9634 | Fans | 2479.58 | 0 | 0 | 0 | 0 | 2.9604 | Fans | 2150.02 | 0 | 0 | 0 | 0 | 2.5669 | Fans | 1308.05 | 0 | 0 | 0 | 0 | 1.5617 | Fans | 1753.72 | 0 | 0 | 0 | 0 | 2.0938 | Fans | 1763.29 | 0 | 0 | 0 | 0 | 2.1052 | Fans | 1308.05 | 0 | 0 | 0 | 0 | 1.5617
Receptacles | 10.8789 | 9.6702 | 8.4614 | 14.7569 | 10.8789 | 9.6702 | 8.4614 | 10.8789 | 9.6702 | 8.4614 | 10.8789 | 9.6702 | 8.4614 |  | Receptacles | 7087.09 | 2024.88 | 0 | 0 | 0 | 10.8789 | 9.066% |  | Receptacles | 6074.65 | 2024.88 | 0 | 0 | 0 | 9.6702 | 9.421% |  | Receptacles | 5062.21 | 2024.88 | 0 | 0 | 0 | 8.4614 | 10.42% |  | Receptacles | 24063.37 | 11013.86 | 0 | 0 | 0 | 14.7569 | 16.34% | Receptacles | 7087.09 | 2024.88 | 0 | 0 | 0 | 10.8789 | Receptacles | 6074.65 | 2024.88 | 0 | 0 | 0 | 9.6702 | Receptacles | 5062.21 | 2024.88 | 0 | 0 | 0 | 8.4614 | Receptacles | 7087.09 | 2024.88 | 0 | 0 | 0 | 10.8789 | Receptacles | 6074.65 | 2024.88 | 0 | 0 | 0 | 9.6702 | Receptacles | 5062.21 | 2024.88 | 0 | 0 | 0 | 8.4614 | Receptacles | 7087.09 | 2024.88 | 0 | 0 | 0 | 10.8789 | Receptacles | 6074.65 | 2024.88 | 0 | 0 | 0 | 9.6702 | Receptacles | 5062.21 | 2024.88 | 0 | 0 | 0 | 8.4614
DHW | 9.4609 | 7.8837 | 6.9372 | 8.6547 | 9.46 | 7.8833 | 6.9372 | 9.4639 | 7.8839 | 6.9377 | 9.4728 | 7.884 | 6.9377 |  | DHW | 0 | 7924.28 | 0 | 0 | 0 | 9.4609 | 7.884% |  | DHW | 0 | 6603.2 | 0 | 0 | 0 | 7.8837 | 7.68% |  | DHW | 0 | 5810.48 | 0 | 0 | 0 | 6.9372 | 8.545% |  | DHW | 0 | 20572.16 | 0 | 0 | 0 | 8.6547 | 9.582% | DHW | 0 | 7923.5 | 0 | 0 | 0 | 9.46 | DHW | 0 | 6602.92 | 0 | 0 | 0 | 7.8833 | DHW | 0 | 5810.48 | 0 | 0 | 0 | 6.9372 | DHW | 0 | 7926.76 | 0 | 0 | 0 | 9.4639 | DHW | 0 | 6603.43 | 0 | 0 | 0 | 7.8839 | DHW | 0 | 5810.9 | 0 | 0 | 0 | 6.9377 | DHW | 0 | 7934.25 | 0 | 0 | 0 | 9.4728 | DHW | 0 | 6603.48 | 0 | 0 | 0 | 7.884 | DHW | 0 | 5810.9 | 0 | 0 | 0 | 6.9377
EUI | 130.1433 | 102.6453 | 81.1807 | 90.3175 | 109.0603 | 93.6705 | 81.1807 | 49.7536 | 40.1902 | 32.9166 | 44.9643 | 37.9353 | 32.9166 |  | kBtu | 25252.74 | 83752.68 | 0 | 0 | 0 | 130.1433 |  | 120 | kBtu | 19616.53 | 66357.08 | 0 | 0 | 0 | 102.6453 |  | 88.5 | kBtu | 15820.71 | 52174.66 | 0 | 0 | 0 | 81.1807 |  | 66 | kBtu | 41586.54 | 173098.25 | 0 | 0 | 0 | 90.3175 |  | kBtu | 23097.41 | 68249.3 | 0 | 0 | 0 | 109.0603 | kBtu | 18835.74 | 59620.78 | 0 | 0 | 0 | 93.6705 | kBtu | 15820.71 | 52174.66 | 0 | 0 | 0 | 81.1807 | kBtu | 31720.96 | 9951.64 | 0 | 0 | 0 | 49.7536 | kBtu | 25034.18 | 8628.31 | 0 | 0 | 0 | 40.1902 | kBtu | 19734.48 | 7835.78 | 0 | 0 | 0 | 32.9166 | kBtu | 27702.07 | 9959.13 | 0 | 0 | 0 | 44.9643 | kBtu | 23145.51 | 8628.36 | 0 | 0 | 0 | 37.9353 | kBtu | 19734.48 | 7835.78 | 0 | 0 | 0 | 32.9166
| Savings: | 27.498 | 48.9625 | 39.8258 | 21.083 | 36.4728 | 48.9625 | 80.3897 | 89.9531 | 97.2267 | 85.179 | 92.208 | 97.2267
|  | 21.13% | 37.62% | 30.6% | 16.2% | 28.03% | 37.62% | 61.77% | 69.12% | 74.71% | 65.45% | 70.85% | 74.71%
Lighting | 138.0626 | 138.0626 | 138.0626 | 0 | 138.0626 | 138.0626 | 138.0626 | 138.0626 | 138.0626 | 138.0626 | 138.0626 | 138.0626 | 138.0626 |  | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 |  |  | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 |  |  | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 |  |  | Lighting | 393.9715 | 0 | 0 | 0 | 0 | 393.9715 |  | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626 | Lighting | 138.0626 | 0 | 0 | 0 | 0 | 138.0626
Heating | 583.0336 | 456.048 | 350.2719 | 0 | 460.566 | 402.8347 | 350.2719 | 900.8169 | 681.2872 | 506.9852 | 700.1761 | 596.478 | 506.9852 |  | Heating | 0 | 583.0336 | 0 | 0 | 0 | 583.0336 |  |  | Heating | 0 | 456.048 | 0 | 0 | 0 | 456.048 |  |  | Heating | 0 | 350.2719 | 0 | 0 | 0 | 350.2719 |  |  | Heating | 0 | 1117.9194 | 0 | 0 | 0 | 1117.9194 |  | Heating | 0 | 460.566 | 0 | 0 | 0 | 460.566 | Heating | 0 | 402.8347 | 0 | 0 | 0 | 402.8347 | Heating | 0 | 350.2719 | 0 | 0 | 0 | 350.2719 | Heating | 900.8169 | 0 | 0 | 0 | 0 | 900.8169 | Heating | 681.2872 | 0 | 0 | 0 | 0 | 681.2872 | Heating | 506.9852 | 0 | 0 | 0 | 0 | 506.9852 | Heating | 700.1761 | 0 | 0 | 0 | 0 | 700.1761 | Heating | 596.478 | 0 | 0 | 0 | 0 | 596.478 | Heating | 506.9852 | 0 | 0 | 0 | 0 | 506.9852
Cooling | 477.2376 | 304.6736 | 241.5432 | 0 | 435.9746 | 296.2989 | 241.5432 | 218.6711 | 134.6372 | 113.3898 | 232.0079 | 134.1547 | 113.3898 |  | Cooling | 477.2376 | 0 | 0 | 0 | 0 | 477.2376 |  |  | Cooling | 304.6736 | 0 | 0 | 0 | 0 | 304.6736 |  |  | Cooling | 241.5432 | 0 | 0 | 0 | 0 | 241.5432 |  |  | Cooling | 265.5926 | 0 | 0 | 0 | 0 | 265.5926 |  | Cooling | 435.9746 | 0 | 0 | 0 | 0 | 435.9746 | Cooling | 296.2989 | 0 | 0 | 0 | 0 | 296.2989 | Cooling | 241.5432 | 0 | 0 | 0 | 0 | 241.5432 | Cooling | 218.6711 | 0 | 0 | 0 | 0 | 218.6711 | Cooling | 134.6372 | 0 | 0 | 0 | 0 | 134.6372 | Cooling | 113.3898 | 0 | 0 | 0 | 0 | 113.3898 | Cooling | 232.0079 | 0 | 0 | 0 | 0 | 232.0079 | Cooling | 134.1547 | 0 | 0 | 0 | 0 | 134.1547 | Cooling | 113.3898 | 0 | 0 | 0 | 0 | 113.3898
Pumps | 0.05406 | 0.044859 | 0.039683 | 0 | 0.05406 | 0.044859 | 0.039683 | 16.5643 | 12.7444 | 10.1518 | 14.483 | 11.6581 | 10.1518 |  | Pumps | 0.05406 | 0 | 0 | 0 | 0 | 0.05406 |  |  | Pumps | 0.044859 | 0 | 0 | 0 | 0 | 0.044859 |  |  | Pumps | 0.039683 | 0 | 0 | 0 | 0 | 0.039683 |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 |  | Pumps | 0.05406 | 0 | 0 | 0 | 0 | 0.05406 | Pumps | 0.044859 | 0 | 0 | 0 | 0 | 0.044859 | Pumps | 0.039683 | 0 | 0 | 0 | 0 | 0.039683 | Pumps | 16.5643 | 0 | 0 | 0 | 0 | 16.5643 | Pumps | 12.7444 | 0 | 0 | 0 | 0 | 12.7444 | Pumps | 10.1518 | 0 | 0 | 0 | 0 | 10.1518 | Pumps | 14.483 | 0 | 0 | 0 | 0 | 14.483 | Pumps | 11.6581 | 0 | 0 | 0 | 0 | 11.6581 | Pumps | 10.1518 | 0 | 0 | 0 | 0 | 10.1518
Fans | 429.3701 | 336.0257 | 239.0864 | 0 | 346.6779 | 299.4965 | 239.0864 | 142.6031 | 123.6498 | 75.2272 | 100.8582 | 101.4085 | 75.2272 |  | Fans | 429.3701 | 0 | 0 | 0 | 0 | 429.3701 |  |  | Fans | 336.0257 | 0 | 0 | 0 | 0 | 336.0257 |  |  | Fans | 239.0864 | 0 | 0 | 0 | 0 | 239.0864 |  |  | Fans | 348.2106 | 0 | 0 | 0 | 0 | 348.2106 |  | Fans | 346.6779 | 0 | 0 | 0 | 0 | 346.6779 | Fans | 299.4965 | 0 | 0 | 0 | 0 | 299.4965 | Fans | 239.0864 | 0 | 0 | 0 | 0 | 239.0864 | Fans | 142.6031 | 0 | 0 | 0 | 0 | 142.6031 | Fans | 123.6498 | 0 | 0 | 0 | 0 | 123.6498 | Fans | 75.2272 | 0 | 0 | 0 | 0 | 75.2272 | Fans | 100.8582 | 0 | 0 | 0 | 0 | 100.8582 | Fans | 101.4085 | 0 | 0 | 0 | 0 | 101.4085 | Fans | 75.2272 | 0 | 0 | 0 | 0 | 75.2272
Receptacles | 423.5817 | 365.3552 | 307.1288 | 0 | 423.5817 | 365.3552 | 307.1288 | 423.5817 | 365.3552 | 307.1288 | 423.5817 | 365.3552 | 307.1288 |  | Receptacles | 407.5855 | 15.9962 | 0 | 0 | 0 | 423.5817 |  |  | Receptacles | 349.3591 | 15.9962 | 0 | 0 | 0 | 365.3552 |  |  | Receptacles | 291.1327 | 15.9962 | 0 | 0 | 0 | 307.1288 |  |  | Receptacles | 1383.908 | 87.0074 | 0 | 0 | 0 | 1470.9154 |  | Receptacles | 407.5855 | 15.9962 | 0 | 0 | 0 | 423.5817 | Receptacles | 349.3591 | 15.9962 | 0 | 0 | 0 | 365.3552 | Receptacles | 291.1327 | 15.9962 | 0 | 0 | 0 | 307.1288 | Receptacles | 407.5855 | 15.9962 | 0 | 0 | 0 | 423.5817 | Receptacles | 349.3591 | 15.9962 | 0 | 0 | 0 | 365.3552 | Receptacles | 291.1327 | 15.9962 | 0 | 0 | 0 | 307.1288 | Receptacles | 407.5855 | 15.9962 | 0 | 0 | 0 | 423.5817 | Receptacles | 349.3591 | 15.9962 | 0 | 0 | 0 | 365.3552 | Receptacles | 291.1327 | 15.9962 | 0 | 0 | 0 | 307.1288
DHW | 62.6003 | 52.164 | 45.9017 | 0 | 62.5941 | 52.1618 | 45.9017 | 62.6199 | 52.1658 | 45.905 | 62.679 | 52.1662 | 45.905 |  | DHW | 0 | 62.6003 | 0 | 0 | 0 | 62.6003 |  |  | DHW | 0 | 52.164 | 0 | 0 | 0 | 52.164 |  |  | DHW | 0 | 45.9017 | 0 | 0 | 0 | 45.9017 |  |  | DHW | 0 | 162.5161 | 0 | 0 | 0 | 162.5161 |  | DHW | 0 | 62.5941 | 0 | 0 | 0 | 62.5941 | DHW | 0 | 52.1618 | 0 | 0 | 0 | 52.1618 | DHW | 0 | 45.9017 | 0 | 0 | 0 | 45.9017 | DHW | 0 | 62.6199 | 0 | 0 | 0 | 62.6199 | DHW | 0 | 52.1658 | 0 | 0 | 0 | 52.1658 | DHW | 0 | 45.905 | 0 | 0 | 0 | 45.905 | DHW | 0 | 62.679 | 0 | 0 | 0 | 62.679 | DHW | 0 | 52.1662 | 0 | 0 | 0 | 52.1662 | DHW | 0 | 45.905 | 0 | 0 | 0 | 45.905
Cost | 2113.9399 | 1652.374 | 1322.0343 | 0 | 1867.511 | 1554.2546 | 1322.0343 | 1902.9196 | 1507.9022 | 1196.8505 | 1671.8484 | 1399.2834 | 1196.8505 |  | Cost | 1452.3098 | 661.63 | 0 | 0 | 0 | 2113.9399 |  |  | Cost | 1128.1659 | 524.2081 | 0 | 0 | 0 | 1652.374 |  |  | Cost | 909.8646 | 412.1698 | 0 | 0 | 0 | 1322.0343 |  |  | Cost | 2391.6827 | 1367.4428 | 0 | 0 | 0 | 3759.1255 |  | Cost | 1328.3547 | 539.1563 | 0 | 0 | 0 | 1867.511 | Cost | 1083.2619 | 470.9927 | 0 | 0 | 0 | 1554.2546 | Cost | 909.8646 | 412.1698 | 0 | 0 | 0 | 1322.0343 | Cost | 1824.3035 | 78.616 | 0 | 0 | 0 | 1902.9196 | Cost | 1439.7402 | 68.162 | 0 | 0 | 0 | 1507.9022 | Cost | 1134.9493 | 61.9012 | 0 | 0 | 0 | 1196.8505 | Cost | 1593.1732 | 78.6752 | 0 | 0 | 0 | 1671.8484 | Cost | 1331.121 | 68.1624 | 0 | 0 | 0 | 1399.2834 | Cost | 1134.9493 | 61.9012 | 0 | 0 | 0 | 1196.8505
| Savings: | 461.5659 | 791.9056 | 2113.9399 | 246.4289 | 559.6853 | 791.9056 | 211.0203 | 606.0376 | 917.0894 | 442.0915 | 714.6565 | 917.0894
|  | 21.83% | 37.46% | 100% | 11.66% | 26.48% | 37.46% | 9.982% | 28.67% | 43.38% | 20.91% | 33.81% | 43.38%
Carbon | 9.2648 | 7.2657 | 5.7887 | 0 | 8.0312 | 6.7595 | 5.7887 | 6.5895 | 5.2414 | 4.1866 | 5.8218 | 4.8805 | 4.1866 |  | Carbon | 4.8259 | 4.4389 | 0 | 0 | 0 | 9.2648 |  |  | Carbon | 3.7488 | 3.5169 | 0 | 0 | 0 | 7.2657 |  |  | Carbon | 3.0234 | 2.7653 | 0 | 0 | 0 | 5.7887 |  |  | Carbon | 7.9474 | 9.1742 | 0 | 0 | 0 | 17.1216 |  | Carbon | 4.414 | 3.6172 | 0 | 0 | 0 | 8.0312 | Carbon | 3.5996 | 3.1599 | 0 | 0 | 0 | 6.7595 | Carbon | 3.0234 | 2.7653 | 0 | 0 | 0 | 5.7887 | Carbon | 6.062 | 0.52744 | 0 | 0 | 0 | 6.5895 | Carbon | 4.7841 | 0.4573 | 0 | 0 | 0 | 5.2414 | Carbon | 3.7714 | 0.4153 | 0 | 0 | 0 | 4.1866 | Carbon | 5.294 | 0.52783 | 0 | 0 | 0 | 5.8218 | Carbon | 4.4232 | 0.4573 | 0 | 0 | 0 | 4.8805 | Carbon | 3.7714 | 0.4153 | 0 | 0 | 0 | 4.1866
| Savings: | 1.9991 | 3.4761 | 9.2648 | 1.2336 | 2.5053 | 3.4761 | 2.6753 | 4.0234 | 5.0782 | 3.443 | 4.3843 | 5.0782
|  | 21.58% | 37.52% | 100% | 13.31% | 27.04% | 37.52% | 28.88% | 43.43% | 54.81% | 37.16% | 47.32% | 54.81%
Peak Heating | 2.8799 | 2.6131 | 2.2792 | 0 | 2.4043 | 2.3777 | 2.2792 | 2.8799 | 2.6131 | 2.2792 | 2.4043 | 2.3777 | 2.2792 |  | Peak Heating (Btu/h) | [5 empty] | 34559 |  |  | Peak Heating (Btu/h) | [5 empty] | 31357 |  |  | Peak Heating (Btu/h) | [5 empty] | 27350 | [10 empty] | Peak Heating (Btu/h) | [5 empty] | 28852 | Peak Heating (Btu/h) | [5 empty] | 28533 | Peak Heating (Btu/h) | [5 empty] | 27350 | Peak Heating (Btu/h) | [5 empty] | 34559 | Peak Heating (Btu/h) | [5 empty] | 31357 | Peak Heating (Btu/h) | [5 empty] | 27350 | Peak Heating (Btu/h) | [5 empty] | 28852 | Peak Heating (Btu/h) | [5 empty] | 28533 | Peak Heating (Btu/h) | [5 empty] | 27350
Peak Cooling | 1.9353 | 1.5914 | 1.406 | 0 | 1.6979 | 1.4913 | 1.4059 | 1.9353 | 1.5914 | 1.406 | 1.6979 | 1.4913 | 1.4059 |  | Peak Cooling (Btu/h) | [5 empty] | 23223.0904 |  |  | Peak Cooling (Btu/h) | [5 empty] | 19097.3253 |  |  | Peak Cooling (Btu/h) | [5 empty] | 16871.7142 | [10 empty] | Peak Cooling (Btu/h) | [5 empty] | 20375 | Peak Cooling (Btu/h) | [5 empty] | 17896 | Peak Cooling (Btu/h) | [5 empty] | 16871 | Peak Cooling (Btu/h) | [5 empty] | 23223.0904 | Peak Cooling (Btu/h) | [5 empty] | 19097.3253 | Peak Cooling (Btu/h) | [5 empty] | 16871.7142 | Peak Cooling (Btu/h) | [5 empty] | 20375 | Peak Cooling (Btu/h) | [5 empty] | 17896 | Peak Cooling (Btu/h) | [5 empty] | 16871
[11 empty] | 9.626% | 5.61% | 0% | 7.497%
[11 empty] | 12.14% | 7.203% | 0% | 9.495%
[11 empty] | 11.65% | 6.886% | 0% | 9.102%

## Homes w PV
Bryant Neighborhood Geothermal Project - Electric and Gas Usage and Cost | [18 empty] | Bryant Neighborhood Geothermal Project - Carbon | [9 empty] | 2024-05-22
* cost includes consumption fees only, no fixed costs included
[30 empty] | System/Plant | Energy Cost |  | Energy Consumption |  | CO2
[10 empty] | 262 Residential Homes | [8 empty] | 262 Residential Homes | [11 empty] | ($/yr) | % Savings | (kBtu/sf/yr) | % Savings | (metric tons) | % Savings
[30 empty] | 262 Homes - Existing | 477465.0698 | - | 110.7104 | - | 2083.2517 | -
Existing | [6 empty] | Total 262 Homes |  |  |  | All 262 Homes - Existing Conditions |  |  |  |  | Assumed Utility Costs |  |  |  | All 262 Homes - Existing Conditions |  |  |  |  | Assumed Carbon Rates |  |  |  |  | 262 Homes - Geo | 464222.7227 | 2.773% | 46.4306 | 58.06% | 1607.14 | 22.85%
|  |  | Mid - Elec (Btu) | Mid - Gas (Btu) |  |  | Electricity:Facility [Btu] | NaturalGas:Facility [Btu] | Total (Btu) | Month | Existing: Electric [kWh] | Existing: Natural Gas [therm] | Elec Cost ($) | Gas Cost ($) |  | Electric | 0.1964 | /kWh | Month | Existing: Electric [kWh] | Existing: Natural Gas [therm] | Elec (Tons) | Gas (Tons) |  | Electric | 0.0001911 | tons of CO2/kBtu | DTE Electricity Emissions Estimate and Forecast |  | 262 Homes - Geo + Solar (Net Metered) | 134270.7227 | 71.88% | 20.3096 | 81.66% | 511.4739 | 75.45%
2022-01-31 |  |  | 1446281.38 | 13922517.78 |  |  | 404188350.6 | 3714273183 | 4118461533.6 | 2022-01-31 | 118460.8296 | 37142.7318 | 23265.7069 | 29342.0425 |  | Gas | 0.78998 | /therms | 2022-01-31 | 118460.8296 | 37142.7318 | 77.2423 | 196.8565 |  | Gas | 5.3e-05 | tons of CO2/kBtu |  |  | 262 Homes - Geo + Solar (Utility Buyback) | 155070.4338 | 67.52% | 20.3096 | 81.66% | 511.4739 | 75.45%
2022-02-28 |  |  | 1305791.905 | 10503076.29 |  |  | 365173691.8 | 3247071924 | 3612245615.8 | 2022-02-28 | 107026.2872 | 32470.7192 | 21019.9628 | 25651.2426 |  | Electric - Outflow | 0.0877 | /kWh | 2022-02-28 | 107026.2872 | 32470.7192 | 69.7864 | 172.0948
2022-03-31 |  |  | 1415192.629 | 8032834.123 |  |  | 384646870.3 | 1817127845 | 2201774715.3 | 2022-03-31 | 112733.5493 | 18171.2784 | 22140.8691 | 14354.9599 |  |  |  |  | 2022-03-31 | 112733.5493 | 18171.2784 | 73.5078 | 96.3078
2022-04-30 |  |  | 1321417.304 | 5456777.867 |  |  | 393714129 | 1220688639 | 1614402768 | 2022-04-30 | 115391.0108 | 12206.8864 | 22662.7945 | 9643.205 |  |  |  |  | 2022-04-30 | 115391.0108 | 12206.8864 | 75.2406 | 64.6965
2022-05-31 |  |  | 1579575.711 | 1945636.841 |  |  | 434744898.8 | 1052047199 | 1486792097.8 | 2022-05-31 | 127416.4416 | 10520.472 | 25024.5891 | 8310.9702 |  |  |  |  | 2022-05-31 | 127416.4416 | 10520.472 | 83.0818 | 55.7585
2022-06-30 |  |  | 2128432.885 | 1007881.274 |  |  | 687127855.5 | 402470409.8 | 1089598265.3 | 2022-06-30 | 201385.6552 | 4024.7041 | 39552.1427 | 3179.4387 |  |  |  |  | 2022-06-30 | 201385.6552 | 4024.7041 | 131.3134 | 21.3309
2022-07-31 |  |  | 2506761.021 | 887716.2021 |  |  | 715918835.2 | 396080336.9 | 1111999172.1 | 2022-07-31 | 209823.8087 | 3960.8034 | 41209.396 | 3128.9583 |  |  |  |  | 2022-07-31 | 209823.8087 | 3960.8034 | 136.8154 | 20.9923
2022-08-31 |  |  | 2311096.63 | 928593.5561 |  |  | 743962351 | 358354108.2 | 1102316459.2 | 2022-08-31 | 218042.893 | 3583.5411 | 42823.6242 | 2830.9284 |  |  |  |  | 2022-08-31 | 218042.893 | 3583.5411 | 142.1747 | 18.9928
2022-09-30 |  |  | 1544385.609 | 1510690.045 |  |  | 459264624.6 | 664808689.9 | 1124073314.5 | 2022-09-30 | 134602.7622 | 6648.0869 | 26435.9825 | 5251.8606 |  |  |  |  | 2022-09-30 | 134602.7622 | 6648.0869 | 87.7676 | 35.2349
2022-10-31 |  |  | 1285702.419 | 4247444.337 |  |  | 387971200.4 | 1276339313 | 1664310513.4 | 2022-10-31 | 113707.8547 | 12763.3931 | 22332.2227 | 10082.8346 |  |  |  |  | 2022-10-31 | 113707.8547 | 12763.3931 | 74.1431 | 67.646
2022-11-30 |  |  | 1313397.541 | 7102705.375 |  |  | 375167342 | 1580347001 | 1955514343 | 2022-11-30 | 109955.2585 | 15803.47 | 21595.2128 | 12484.4368 |  |  |  |  | 2022-11-30 | 109955.2585 | 15803.47 | 71.6962 | 83.7584
2022-12-31 |  |  | 1445408.723 | 10766936.02 |  |  | 396625749.1 | 2816897747 | 3213523496.1 | 2022-12-31 | 116244.3579 | 28168.9775 | 22830.3919 | 22252.9494 |  |  |  |  | 2022-12-31 | 116244.3579 | 28168.9775 | 75.797 | 149.2956
[9 empty] | 24295012294.1 |  |  |  | 330892.8952 | 146513.827 | 477406.7222 | [6 empty] | 1098.5664 | 982.9648 | 2081.5313
Geo | Single Homes | [5 empty] | Total 262 Homes |  |  |  | All 262 Homes - Geo Conditions | [8 empty] | All 262 Homes - Geo Conditions
| Best - Elec (Btu) | Best - Gas (Btu) | Mid - Elec (Btu) | Mid - Gas (Btu) | Worst - Elec (Btu) | Best - Gas (Btu) | Electricity:Facility [Btu] | NaturalGas:Facility [Btu] |  | Month | Geo: Electric [kWh] | Geo: Natural Gas [therm] | Elec Cost ($) | Gas Cost ($) |  |  |  |  | Month | Geo: Electric [kWh] | Geo: Natural Gas [therm] | Elec (Tons) | Gas (Tons)
2022-01-31 | 3151074.3276 | 717225.317 | 4037880.618 | 791550.5432 | 4916931.1617 | 915637.6084 | 1176406749.4557 | 222246114.2466 | 1398652863.7023 | 2022-01-31 | 344785.0966 | 2222.4611 | 67715.793 | 1755.7015 |  |  |  |  | 2022-01-31 | 344785.0966 | 2222.4611 | 224.8168 | 11.779
2022-02-28 | 2406405.4802 | 654566.5155 | 3097487.416 | 722625.9233 | 3811853.419 | 836217.7651 | 1030158052.8992 | 200834112.5223 | 1230992165.4216 | 2022-02-28 | 301922.0554 | 2008.3411 | 59297.4917 | 1586.5508 |  |  |  |  | 2022-02-28 | 301922.0554 | 2008.3411 | 196.868 | 10.6442
2022-03-31 | 1881543.5299 | 715525.1197 | 2432993.375 | 789633.5496 | 3032652.6646 | 913277.5989 | 602366842.1013 | 222252057.6103 | 824618899.7116 | 2022-03-31 | 176543.6231 | 2222.5206 | 34673.1676 | 1755.7484 |  |  |  |  | 2022-03-31 | 176543.6231 | 2222.5206 | 115.1151 | 11.7794
2022-04-30 | 1353394.373 | 672986.3409 | 1770977.067 | 742059.8246 | 2235468.6286 | 857362.4216 | 417084931.7537 | 214826116.0351 | 631911047.7888 | 2022-04-30 | 122240.6013 | 2148.2612 | 24008.0541 | 1697.0849 |  |  |  |  | 2022-04-30 | 122240.6013 | 2148.2612 | 79.7069 | 11.3858
2022-05-31 | 941381.3244 | 664580.1689 | 1215214.369 | 731835.9707 | 1618651.2476 | 844119.2302 | 417687432.8313 | 211832764.472 | 629520197.3033 | 2022-05-31 | 122417.1843 | 2118.3276 | 24042.735 | 1673.438 |  |  |  |  | 2022-05-31 | 122417.1843 | 2118.3276 | 79.822 | 11.2271
2022-06-30 | 1201726.4843 | 613594.6747 | 1439507.688 | 674656.685 | 1922644.3387 | 776552.2638 | 587040426.285 | 193184828.9347 | 780225255.2197 | 2022-06-30 | 172051.7076 | 1931.8483 | 33790.9554 | 1526.1229 |  |  |  |  | 2022-06-30 | 172051.7076 | 1931.8483 | 112.1862 | 10.2388
2022-07-31 | 1369201.8735 | 612849.5487 | 1604064.223 | 673059.3397 | 2142746.9683 | 773356.4709 | 616703594.2253 | 192194484.4082 | 808898078.6335 | 2022-07-31 | 180745.4848 | 1921.9448 | 35498.4132 | 1518.2994 |  |  |  |  | 2022-07-31 | 180745.4848 | 1921.9448 | 117.8549 | 10.1863
2022-08-31 | 1256788.7064 | 605293.9321 | 1471323.714 | 664436.7099 | 2006122.23 | 763115.0857 | 646854127.7696 | 189652455.3946 | 836506583.1642 | 2022-08-31 | 189582.1008 | 1896.5246 | 37233.9246 | 1498.2179 |  |  |  |  | 2022-08-31 | 189582.1008 | 1896.5246 | 123.6169 | 10.0516
2022-09-30 | 882459.9244 | 593984.8289 | 1118005.208 | 652446.4938 | 1511290.6798 | 749952.5537 | 375287314.2489 | 186375154.6495 | 561662468.8984 | 2022-09-30 | 109990.4204 | 1863.7515 | 21602.1186 | 1472.3278 |  |  |  |  | 2022-09-30 | 109990.4204 | 1863.7515 | 71.7192 | 9.8779
2022-10-31 | 1099919.2867 | 636459.4438 | 1476126.973 | 699819.7733 | 1901209.1224 | 805996.6544 | 440120922.4056 | 200464994.6607 | 640585917.0663 | 2022-10-31 | 128992.064 | 2004.6499 | 25334.0414 | 1583.6348 |  |  |  |  | 2022-10-31 | 128992.064 | 2004.6499 | 84.1092 | 10.6246
2022-11-30 | 1684217.4861 | 646171.9543 | 2170239.787 | 711505.196 | 2702072.3748 | 820973.7037 | 523242449.3883 | 206262403.9304 | 729504853.3187 | 2022-11-30 | 153353.5901 | 2062.624 | 30118.6451 | 1629.4332 |  |  |  |  | 2022-11-30 | 153353.5901 | 2062.624 | 99.9941 | 10.9319
2022-12-31 | 2493203.8098 | 697314.5153 | 3183654.742 | 768923.2431 | 3898154.3487 | 888440.8356 | 893947172.9118 | 222010578.161 | 1115957751.0728 | 2022-12-31 | 262000.9299 | 2220.1058 | 51456.9826 | 1753.8408 |  |  |  |  | 2022-12-31 | 262000.9299 | 2220.1058 | 170.8375 | 11.7666
[9 empty] | 10189036081.301 |  |  |  | 444772.3222 | 19450.4005 | 464222.7227 | [6 empty] | 1476.6468 | 130.4932 | 1607.14
[9 empty] | 58.06% | [5 empty] | 2.762% | [8 empty] | 22.79%
Geo + Solar (1680 MWh) | Single Homes | [5 empty] | Total 262 Homes |  |  |  | All 262 Homes - Geo + Solar Conditions - Net Metered
| Best - Elec (Btu) | Best - Gas (Btu) | Mid - Elec (Btu) | Mid - Gas (Btu) | Worst - Elec (Btu) | Best - Gas (Btu) | Electricity:Facility [Btu] | NaturalGas:Facility [Btu] |  | Month | Geo: Electric [kWh] | Geo: Natural Gas [therm] | Elec Cost ($) | Gas Cost ($) |  | Solar Ratio | Solar production (kWh)
2022-01-31 | 3151074.3276 | 717225.317 | 4037880.618 | 791550.5432 | 4916931.1617 | 915637.6084 | 908183236.1003 | 222246114.2466 | 1130429350.3468 | 2022-01-31 | 266173.2814 | 2222.4611 | 52276.4325 | 1755.7015 |  | 0.39474 | 78611.8152
2022-02-28 | 2406405.4802 | 654566.5155 | 3097487.416 | 722625.9233 | 3811853.419 | 836217.7651 | 678114691.6202 | 200834112.5223 | 878948804.1426 | 2022-02-28 | 198744.048 | 2008.3411 | 39033.331 | 1586.5508 |  | 0.51809 | 103178.0074
2022-03-31 | 1881543.5299 | 715525.1197 | 2432993.375 | 789633.5496 | 3032652.6646 | 913277.5989 | 94977362.6706 | 222252057.6103 | 317229420.2809 | 2022-03-31 | 27836.2728 | 2222.5206 | 5467.044 | 1755.7484 |  | 0.74671 | 148707.3504
2022-04-30 | 1353394.373 | 672986.3409 | 1770977.067 | 742059.8246 | 2235468.6286 | 857362.4216 | -151772436.1543 | 214826116.0351 | 63053679.8808 | 2022-04-30 | -44481.9567 | 2148.2612 | -8736.2563 | 1697.0849 |  | 0.83717 | 166722.558
2022-05-31 | 941381.3244 | 664580.1689 | 1215214.369 | 731835.9707 | 1618651.2476 | 844119.2302 | -190285864.1077 | 211832764.472 | 21546900.3643 | 2022-05-31 | -55769.5967 | 2118.3276 | -10953.1488 | 1673.438 |  | 0.89474 | 178186.781
2022-06-30 | 1201726.4843 | 613594.6747 | 1439507.688 | 674656.685 | 1922644.3387 | 776552.2638 | -76812769.2697 | 193184828.9347 | 116372059.665 | 2022-06-30 | -22512.535 | 1931.8483 | -4421.4619 | 1526.1229 |  | 0.97697 | 194564.2425 |  |  | All 262 Homes - Geo + Solar Conditions
2022-07-31 | 1369201.8735 | 612849.5487 | 1604064.223 | 673059.3397 | 2142746.9683 | 773356.4709 | -62795972.9418 | 192194484.4082 | 129398511.4664 | 2022-07-31 | -18404.4469 | 1921.9448 | -3614.6334 | 1518.2994 |  | 1 | 199149.9318 |  | Month | Geo: Electric [kWh] | Geo: Natural Gas [therm] | Elec (Tons) | Gas (Tons)
2022-08-31 | 1256788.7064 | 605293.9321 | 1471323.714 | 664436.7099 | 2006122.23 | 763115.0857 | 45586418.6645 | 189652455.3946 | 235238874.0591 | 2022-08-31 | 13360.6151 | 1896.5246 | 2624.0248 | 1498.2179 |  | 0.88487 | 176221.4857 |  | 2022-01-31 | 266173.2814 | 2222.4611 | 173.4563 | 11.779
2022-09-30 | 882459.9244 | 593984.8289 | 1118005.208 | 652446.4938 | 1511290.6798 | 749952.5537 | -171218094.2128 | 186375154.6495 | 15157060.4367 | 2022-09-30 | -50181.1531 | 1863.7515 | -9855.5785 | 1472.3278 |  | 0.80428 | 160171.5734 |  | 2022-02-28 | 198744.048 | 2008.3411 | 129.5149 | 10.6442
2022-10-31 | 1099919.2867 | 636459.4438 | 1476126.973 | 699819.7733 | 1901209.1224 | 805996.6544 | 44491240.2063 | 200464994.6607 | 244956234.867 | 2022-10-31 | 13039.6366 | 2004.6499 | 2560.9846 | 1583.6348 |  | 0.58224 | 115952.4274 |  | 2022-03-31 | 27836.2728 | 2222.5206 | 18.14 | 11.7794
2022-11-30 | 1684217.4861 | 646171.9543 | 2170239.787 | 711505.196 | 2702072.3748 | 820973.7037 | 213667811.0572 | 206262403.9304 | 419930214.9877 | 2022-11-30 | 62622.4534 | 2062.624 | 12299.0499 | 1629.4332 |  | 0.45559 | 90731.1367 |  | 2022-04-30 | -44481.9567 | 2148.2612 | -28.9874 | 11.3858
2022-12-31 | 2493203.8098 | 697314.5153 | 3183654.742 | 768923.2431 | 3898154.3487 | 888440.8356 | 662604392.6427 | 222010578.161 | 884614970.8037 | 2022-12-31 | 194198.2393 | 2220.1058 | 38140.5342 | 1753.8408 |  | 0.34046 | 67802.6906 |  | 2022-05-31 | -55769.5967 | 2118.3276 | -36.3432 | 11.2271
[9 empty] | 4456876081.301 |  |  |  | 114820.3222 | 19450.4005 | 134270.7227 | 8.4359 | 1680000 |  | 2022-06-30 | -22512.535 | 1931.8483 | -14.6707 | 10.2388
[9 empty] | 81.66% | [5 empty] | 71.87% |  |  |  | 2022-07-31 | -18404.4469 | 1921.9448 | -11.9936 | 10.1863
Geo + Solar (1680 MWh) | Single Homes | [5 empty] | Total 262 Homes |  |  |  | All 262 Homes - Geo + Solar Conditions - Utility Buyback | [7 empty] | 2022-08-31 | 13360.6151 | 1896.5246 | 8.7067 | 10.0516
| Best - Elec (Btu) | Best - Gas (Btu) | Mid - Elec (Btu) | Mid - Gas (Btu) | Worst - Elec (Btu) | Best - Gas (Btu) | Electricity:Facility [Btu] | NaturalGas:Facility [Btu] |  | Month | Geo: Electric [kWh] | Geo: Natural Gas [therm] | Elec Cost ($) | Gas Cost ($) |  | Solar Ratio | Solar production (kWh) |  | 2022-09-30 | -50181.1531 | 1863.7515 | -32.7014 | 9.8779
2022-01-31 | 3151074.3276 | 717225.317 | 4037880.618 | 791550.5432 | 4916931.1617 | 915637.6084 | 908183236.1003 | 222246114.2466 | 1130429350.3468 | 2022-01-31 | 266173.2814 | 2222.4611 | 52276.4325 | 1755.7015 |  | 0.39474 | 78611.8152 |  | 2022-10-31 | 13039.6366 | 2004.6499 | 8.4975 | 10.6246
2022-02-28 | 2406405.4802 | 654566.5155 | 3097487.416 | 722625.9233 | 3811853.419 | 836217.7651 | 678114691.6202 | 200834112.5223 | 878948804.1426 | 2022-02-28 | 198744.048 | 2008.3411 | 39033.331 | 1586.5508 |  | 0.51809 | 103178.0074 |  | 2022-11-30 | 62622.4534 | 2062.624 | 40.809 | 10.9319
2022-03-31 | 1881543.5299 | 715525.1197 | 2432993.375 | 789633.5496 | 3032652.6646 | 913277.5989 | 94977362.6706 | 222252057.6103 | 317229420.2809 | 2022-03-31 | 27836.2728 | 2222.5206 | 5467.044 | 1755.7484 |  | 0.74671 | 148707.3504 |  | 2022-12-31 | 194198.2393 | 2220.1058 | 126.5526 | 11.7666
2022-04-30 | 1353394.373 | 672986.3409 | 1770977.067 | 742059.8246 | 2235468.6286 | 857362.4216 | -151772436.1543 | 214826116.0351 | 63053679.8808 | 2022-04-30 | -44481.9567 | 2148.2612 | -3901.0676 | 1697.0849 |  | 0.83717 | 166722.558 |  |  |  |  | 380.9807 | 130.4932 | 511.4739
2022-05-31 | 941381.3244 | 664580.1689 | 1215214.369 | 731835.9707 | 1618651.2476 | 844119.2302 | -190285864.1077 | 211832764.472 | 21546900.3643 | 2022-05-31 | -55769.5967 | 2118.3276 | -4890.9936 | 1673.438 |  | 0.89474 | 178186.781 | [6 empty] | 75.43%
2022-06-30 | 1201726.4843 | 613594.6747 | 1439507.688 | 674656.685 | 1922644.3387 | 776552.2638 | -76812769.2697 | 193184828.9347 | 116372059.665 | 2022-06-30 | -22512.535 | 1931.8483 | -1974.3493 | 1526.1229 |  | 0.97697 | 194564.2425
2022-07-31 | 1369201.8735 | 612849.5487 | 1604064.223 | 673059.3397 | 2142746.9683 | 773356.4709 | -62795972.9418 | 192194484.4082 | 129398511.4664 | 2022-07-31 | -18404.4469 | 1921.9448 | -1614.07 | 1518.2994 |  | 1 | 199149.9318
2022-08-31 | 1256788.7064 | 605293.9321 | 1471323.714 | 664436.7099 | 2006122.23 | 763115.0857 | 45586418.6645 | 189652455.3946 | 235238874.0591 | 2022-08-31 | 13360.6151 | 1896.5246 | 2624.0248 | 1498.2179 |  | 0.88487 | 176221.4857
2022-09-30 | 882459.9244 | 593984.8289 | 1118005.208 | 652446.4938 | 1511290.6798 | 749952.5537 | -171218094.2128 | 186375154.6495 | 15157060.4367 | 2022-09-30 | -50181.1531 | 1863.7515 | -4400.8871 | 1472.3278 |  | 0.80428 | 160171.5734
2022-10-31 | 1099919.2867 | 636459.4438 | 1476126.973 | 699819.7733 | 1901209.1224 | 805996.6544 | 44491240.2063 | 200464994.6607 | 244956234.867 | 2022-10-31 | 13039.6366 | 2004.6499 | 2560.9846 | 1583.6348 |  | 0.58224 | 115952.4274
2022-11-30 | 1684217.4861 | 646171.9543 | 2170239.787 | 711505.196 | 2702072.3748 | 820973.7037 | 213667811.0572 | 206262403.9304 | 419930214.9877 | 2022-11-30 | 62622.4534 | 2062.624 | 12299.0499 | 1629.4332 |  | 0.45559 | 90731.1367
2022-12-31 | 2493203.8098 | 697314.5153 | 3183654.742 | 768923.2431 | 3898154.3487 | 888440.8356 | 662604392.6427 | 222010578.161 | 884614970.8037 | 2022-12-31 | 194198.2393 | 2220.1058 | 38140.5342 | 1753.8408 |  | 0.34046 | 67802.6906
[9 empty] | 4456876081.301 |  |  |  | 135620.0333 | 19450.4005 | 155070.4338 | 8.4359 | 1680000
[9 empty] | 81.66% | [5 empty] | 67.52%
Single Average Residential Home
Existing | [10 empty] | Average Home - Existing Conditions
|  |  | Mid - Elec (kBtu) | Mid - Gas (kBtu) | [5 empty] | Month | Existing: Electric [kWh] | Existing: Natural Gas [therm] | Elec Cost ($) | Gas Cost ($)
2022-01-31 |  |  | 1446.2814 | 13922.5178 | [5 empty] | 2022-01-31 | 423.8808 | 139.2252 | 83.2502 | 109.9852
2022-02-28 |  |  | 1305.7919 | 10503.0763 | [5 empty] | 2022-02-28 | 382.7057 | 105.0308 | 75.1634 | 82.9723
2022-03-31 |  |  | 1415.1926 | 8032.8341 | [5 empty] | 2022-03-31 | 414.7692 | 80.3283 | 81.4607 | 63.4578
2022-04-30 |  |  | 1321.4173 | 5456.7779 | [5 empty] | 2022-04-30 | 387.2853 | 54.5678 | 76.0628 | 43.1075
2022-05-31 |  |  | 1579.5757 | 1945.6368 | [5 empty] | 2022-05-31 | 462.9472 | 19.4564 | 90.9228 | 15.3702
2022-06-30 |  |  | 2128.4329 | 1007.8813 | [5 empty] | 2022-06-30 | 623.808 | 10.0788 | 122.5159 | 7.9621
2022-07-31 |  |  | 2506.761 | 887.7162 | [5 empty] | 2022-07-31 | 734.6896 | 8.8772 | 144.293 | 7.0128
2022-08-31 |  |  | 2311.0966 | 928.5936 | [5 empty] | 2022-08-31 | 677.3437 | 9.2859 | 133.0303 | 7.3357
2022-09-30 |  |  | 1544.3856 | 1510.69 | [5 empty] | 2022-09-30 | 452.6335 | 15.1069 | 88.8972 | 11.9342
2022-10-31 |  |  | 1285.7024 | 4247.4443 | [5 empty] | 2022-10-31 | 376.8178 | 42.4744 | 74.007 | 33.554
2022-11-30 |  |  | 1313.3975 | 7102.7054 | [5 empty] | 2022-11-30 | 384.9348 | 71.0271 | 75.6012 | 56.11
2022-12-31 |  |  | 1445.4087 | 10766.936 | [5 empty] | 2022-12-31 | 423.6251 | 107.6694 | 83.2 | 85.0567
[13 empty] | 1128.4046 | 523.8584 | 1652.263
Geo | [10 empty] | Average Home - Geo Conditions
|  |  | Mid - Elec (kBtu) | Mid - Gas (kBtu) | [5 empty] | Month | Geo: Electric [kWh] | Geo: Natural Gas [therm] | Elec Cost ($) | Gas Cost ($)
2022-01-31 |  |  | 4037.8806 | 791.5505 | [5 empty] | 2022-01-31 | 1183.4351 | 7.9155 | 232.4267 | 6.2531
2022-02-28 |  |  | 3097.4874 | 722.6259 | [5 empty] | 2022-02-28 | 907.8216 | 7.2263 | 178.2962 | 5.7086
2022-03-31 |  |  | 2432.9934 | 789.6335 | [5 empty] | 2022-03-31 | 713.0696 | 7.8963 | 140.0469 | 6.238
2022-04-30 |  |  | 1770.9771 | 742.0598 | [5 empty] | 2022-04-30 | 519.0437 | 7.4206 | 101.9402 | 5.8621
2022-05-31 |  |  | 1215.2144 | 731.836 | [5 empty] | 2022-05-31 | 356.159 | 7.3184 | 69.9496 | 5.7814
2022-06-30 |  |  | 1439.5077 | 674.6567 | [5 empty] | 2022-06-30 | 421.8956 | 6.7466 | 82.8603 | 5.3297
2022-07-31 |  |  | 1604.0642 | 673.0593 | [5 empty] | 2022-07-31 | 470.1243 | 6.7306 | 92.3324 | 5.317
2022-08-31 |  |  | 1471.3237 | 664.4367 | [5 empty] | 2022-08-31 | 431.2203 | 6.6444 | 84.6917 | 5.2489
2022-09-30 |  |  | 1118.0052 | 652.4465 | [5 empty] | 2022-09-30 | 327.6686 | 6.5245 | 64.3541 | 5.1542
2022-10-31 |  |  | 1476.127 | 699.8198 | [5 empty] | 2022-10-31 | 432.6281 | 6.9982 | 84.9682 | 5.5284
2022-11-30 |  |  | 2170.2398 | 711.5052 | [5 empty] | 2022-11-30 | 636.0609 | 7.1151 | 124.9224 | 5.6208
2022-12-31 |  |  | 3183.6547 | 768.9232 | [5 empty] | 2022-12-31 | 933.0758 | 7.6892 | 183.2561 | 6.0743
[13 empty] | 1440.0446 | 68.1165 | 1508.1611
Note on A22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Replace with values from the geothermal model switch

## PV Production Ratio
| kWh | Ratio
January | 240 | 0.39474
February | 315 | 0.51809
March | 454 | 0.74671
April | 509 | 0.83717
May | 544 | 0.89474
June | 594 | 0.97697
July | 608 | 1
August | 538 | 0.88487
September | 489 | 0.80428
October | 354 | 0.58224
November | 277 | 0.45559
December | 207 | 0.34046
Total | 5129 | 8.4359
Note on B1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PV Watts?

## Neighborhood Inputs
| System/Plant | Energy Cost |  | EUI |  | CO2 |  |  |  | Climate Zone: 5A | 262 Homes - Existing | 262 Homes - Geo | Community Center - Existing | Community Center - Geo | Bryant Elementary - Existing | Bryant Elementary - Geo | County Health - Existing | County Health - Geo | Wheeler Center - Existing | Wheeler Center - Geo | Wheeler Maintenance (S) - Existing | Wheeler Maintenance (S) - Geo | Wheeler Vehicle Storage (E) - Existing | Wheeler Vehicle Storage (E) - Geo | Central Geo Pumping (Homes Only)
Index |  | ($/yr) | % Savings | (kBtu/sqft/yr) | % Savings | (metric tons) | % Savings |  |  | Envelope Construction
1 | 262 Homes - Existing | 477465.0698 | - | 110.8205 | - | 2083.2517 | - |  |  | Exterior Walls | 26 - Best 78 - Mid 162 - Worst See Homes Inputs Tab |  | Wood Framed: R-13/R-19 |  | Code: U-0.055 |  | R-18 |  | R-10 |  | R-10 |  | R-10
2 | 262 Homes - Geo | 465189.1946 | 2.571% | 46.5446 | 58% | 1611.6938 | 22.64% |  |  | Roof |  |  | Wood Framed Attic: R-30/R-38 |  | U-0.063 |  | R-15 |  | R-15 |  | R-15 |  | R-15
3 | Community Center - Existing | 421020.1505 | - | 43.0553 | - | 1465.0048 | - |  |  | Slab on Grade |  |  | Crawl Space: R-13 |  | F-0.73 |  | F-0.73 |  | F-0.73 |  | F-0.73 |  | F-0.73
4 | Community Center - Geo | 110920.3421 | 73.65% | 16.8405 | 60.89% | 365.2077 | 75.07% |  |  | Windows |  |  | U-0.33-0.5 |  | U-0.45, SHGC-0.4 |  | U-0.55, SHGC-0.55 |  | U-0.50 |  | U-0.50 |  | U-0.50
5 | Bryant Elementary - Existing | 9001.4196 | - | 109.4569 | - | 47.8337 | - |  |  | Window to Wall Ratio |  |  | 20% |  | 20% |  | 20% |  | 0-20% |  | 0% |  | 0%
6 | Bryant Elementary - Geo | 8083.3995 | 10.2% | 51.8754 | 52.61% | 42.3659 | 11.43% |  |  | Infiltration (ach) |  |  | 1.3 |  | 0.2 |  | 0.4 |  | 0.25 |  | 0.8 |  | 1
7 | County Health - Existing | 65374.0298 | - | 56.8394 | - | 346.4072 | - |  |  | Electrical Systems
8 | County Health - Geo | 73149.5947 | -11.89% | 38.5083 | 32.25% | 383.5901 | -10.73% |  |  | Lighting (W/sqft) | See Homes Inputs Tab |  | 0.85 W/sf assumed |  | 1 W/sf |  | 0.76 W/sf (Interior) |  | 0.6 W/sf |  | 0.6 W/sf |  | 0.6 W/sf
9 | Wheeler Center - Existing | 39189.9214 | - | 60.737 | - | 207.6206 | - |  |  | Receptacle Power (W/sqft) |  |  | 7 fridges, 2 freezers, computers 0.9 W/sf |  | 1 W/sf |  | 1 W/sf |  | 1 W/sf |  | 1 W/sf |  | 1 W/sf
10 | Wheeler Center - Geo | 43889.8397 | -11.99% | 42.2684 | 30.41% | 230.2233 | -10.89% |  |  | Process Load (W/sf) |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
11 | Wheeler Maintenance (S) - Existing | 63421.2404 | - | 71.4335 | - | 335.5425 | - |  |  | Mechanical and Plumbing Systems
12 | Wheeler Maintenance (S) - Geo | 66674.364 | -5.129% | 48.4258 | 32.21% | 349.6494 | -4.204% |  |  | HVAC System Types | See Homes Inputs Tab |  | Furnace + AC | Geothermal HP | Packaged RTUs | Geothermal HP | 8 packaged units 6 units go to VAV | Geothermal HP | RTU with VAV w/ energy recovery (70%) Boiler for perimeter heat | Geothermal HP | Office: RTU w/ ERW (70%) Warehouse: Heating Only - ERU | Geothermal HP | MAU Heating Only | Geothermal HP | Pump Head = 160 ft
13 | Wheeler Vehicle Storage (E) - Existing | 73280.0913 | - | 72.3368 | - | 386.8825 | - |  |  | Cooling Performance |  |  | AC: SEER 10/13, 2.5 COP | 20 EER, COP 5.8 | AC: 2.5 COP | 20 EER, COP 5.8 | AC: 2.5 COP | 20 EER, COP 5.8 | RTU: EER 12, COP 3.5 | 20 EER, COP 5.8 | RTU: COP 3.5 | 20 EER, COP 5.8 | N/A | 20 EER, COP 5.8 | Pump gpm = 2500 gpm
14 | Wheeler Vehicle Storage (E) - Geo | 71869.4442 | 1.925% | 49.906 | 31.01% | 376.8795 | 2.586% |  |  | Heating Performance |  |  | AFUE: 95% | COP - 4 | RTU: 80% | COP - 4 | AFUE: 80% | COP - 4 | RTU: 80% Gas Boiler: 85% | COP - 4 | RTU: 80% ERU: 80% | COP - 4 | Gas Fired Unit Heater: 80% | COP - 4 | See Pump Calcs on next page
15 | Central Geo Pumping (Homes Only) | 111466.2632 | - | 75.1003 | - | 589.5755 | - |  |  | Domestic Water Heating |  |  | 0.02 gal/sf/day Gas Water Heater - 80% |  | Gas Water Heater = 80% eff |  | 0.035 gal/sf/day 2 electric boilers, 1 NG boiler 95% eff |  | Gas Water Heater = 80% eff |  | Gas Water Heater = 80% eff |  | Gas Water Heater = 80% eff
Other
[10 empty] | Schedule | See Homes Inputs Tab |  | Weekdays: 6 am - 6pm 200 sf/person |  | Shutdown from June 1 - Aug 1 |  | Weekdays: 7 am - 5pm 100 people total (300 sf/person) |  | 7 am - 5 pm |  | 7 am - 5 pm |  | 7 am - 5 pm
[10 empty] | Setpoints |  |  | H: 70/66, C: 70/74 |  | H: 70/68, C:72/74 |  | H: 70/68, C:74/76 |  | H: 72/70, C:74/76 |  | H: 60, C: 85 |  | H: 60, C: 85
General Building Information
| Project Location | Ann Arbor
| Facility Use Type | 262 Homes | Community Center | Elementary | County Health | Wheeler Center | Wheeler Maintenance | Wheeler Vehicle Services
| Floor Area in Energy Model (ft2) | 219446.43 | 4454 | 56175 | 31278 | 40823.98 | 42604.16 | 67506
| Total Number of Floors | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Utility Rates | Residential |  |  |  | Commercial
| Electric | 0.057511 | $/kBtu | 0.1964 | /kWh | 0.036486 | $/kBtu | 0.1246 | /kWh
| Gas | 0.0078998 | $/kBtu | 0.78998 | /therms | 0.0097195 | $/kBtu | 0.97195 | /therm
| District Htg | 0 | $/kBtu |  | /therms
| District Clg | 0 | $/kBtu |  | /therms
| Add Fuel | 0 | $/kBtu |  | /therms
| Carbon Emissions | lbs/MWH | tons of CO2/kBtu
| Electric | 1438.38 | 0.0001911
| Gas | - | 5.3e-05
| District Htg | -
| District Clg | -
| Add Fuel | -
Note on AB2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This includes the pump energy required by the geothermal field, not the homeowner pumping energy
Note on P7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From CC Full Report
Note on R17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hook up RTU to Geo, Electric Reheat Reply: Cop will be 10-15% lower than the homes
Note on T17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Flips okay to geo using elem
Note on F35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thea - DTE Electricity Emissions Estimate and Forecast
Note on J35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EIA 2022
Note on F36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thea - DTE Electricity Emissions Estimate and Forecast
Note on J36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EIA 2023
Note on D42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Thea - DTE Electricity Emissions Estimate and Forecast Reply: 1216.4 lbs/MWH on power profile

## Neighborhood - TMY3
[5 empty] | End Use Selection | [18 empty] | 262 Homes - Existing | [6 empty] | 262 Homes - Geo | [7 empty] | Community Center - Existing | [6 empty] | Community Center - Geo | [7 empty] | Bryant Elementary - Existing | [6 empty] | Bryant Elementary - Geo | [7 empty] | County Health - Existing | [6 empty] | County Health - Geo | [6 empty] | Wheeler Center - Existing | [6 empty] | Wheeler Center - Geo | [6 empty] | Wheeler Maintenance (S) - Existing | [6 empty] | Wheeler Maintenance (S) - Geo | [6 empty] | Wheeler Vehicle Storage (E) - Existing | [6 empty] | Wheeler Vehicle Storage (E) - Geo | [6 empty] | Central Geo Pumping (Homes Only)
[5 empty] | Lighting | Heating | Cooling | Pump | Fan | Recep | DHW | [13 empty] | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal]
[6 empty] | x | [17 empty] | Heating | 0 | 16103569.63 |  |  |  |  | Heating | 3443159.32 | 0 | [5 empty] | Heating | 0 | 315318.81 |  |  |  |  | Heating | 64124.07 | 0 | [5 empty] | Heating | 0 | 1694126.74 |  |  |  |  | Heating | 597928.16 | 0 | [5 empty] | Heating | 0 | 963010.22 |  |  |  |  | Heating | 339886.5712 | [5 empty] | Heating | 68.49 | 1401867.35 |  |  |  |  | Heating | 494777.6016 | [5 empty] | Heating | 27.84 | 1249958 |  |  |  |  | Heating | 441190.2804 | [5 empty] | Heating | 0 | 2410604.96 |  |  |  |  | Heating | 850803.2806 | [5 empty] | Heating
[7 empty] | x | [16 empty] | Cooling | 1627426.68 | 0 |  |  |  |  | Cooling | 1116471.81 | 0 | [5 empty] | Cooling | 43945.64 | 0 |  |  |  |  | Cooling | 38203.93 | 0 | [5 empty] | Cooling | 285262.1 | 0 |  |  |  |  | Cooling | 238568.12 | 0 | [5 empty] | Cooling | 131034.73 | 0 |  |  |  |  | Cooling | 109585.9183 | 0 |  |  |  |  | Cooling | 256239.89 | 0 |  |  |  |  | Cooling | 214296.4972 | 0 |  |  |  |  | Cooling | 104128.44 | 0 |  |  |  |  | Cooling | 87083.8649 | 0 |  |  |  |  | Cooling | 0 | 0 |  |  |  |  | Cooling | 0 | 0 |  |  |  |  | Cooling
[5 empty] | x | [18 empty] | Interior Lighting | 628966.31 | 0 |  |  |  |  | Interior Lighting | 628966.31 | 0 | [5 empty] | Interior Lighting | 37174 | 0 |  |  |  |  | Interior Lighting | 37174 | 0 | [5 empty] | Interior Lighting | 485362.19 | 0 |  |  |  |  | Interior Lighting | 485362.19 | 0 | [5 empty] | Interior Lighting | 233706.24 | 0 |  |  |  |  | Interior Lighting | 233706.24 | 0 |  |  |  |  | Interior Lighting | 240811.81 | 0 |  |  |  |  | Interior Lighting | 240811.81 | 0 |  |  |  |  | Interior Lighting | 251312.67 | 0 |  |  |  |  | Interior Lighting | 251312.67 | 0 |  |  |  |  | Interior Lighting | 398206.7 | 0 |  |  |  |  | Interior Lighting | 398206.7 | 0 |  |  |  |  | Interior Lighting
[5 empty] | x | [18 empty] | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting
[10 empty] | x | [13 empty] | Interior Equipment | 1725200.53 | 530519.41 |  |  |  |  | Interior Equipment | 1725200.53 | 530519.41 | [5 empty] | Interior Equipment | 40791.83 | 0 |  |  |  |  | Interior Equipment | 40791.83 | 0 | [5 empty] | Interior Equipment | 328427.45 | 0 |  |  |  |  | Interior Equipment | 328427.45 | 0 | [5 empty] | Interior Equipment | 318687.37 | 0 |  |  |  |  | Interior Equipment | 318687.37 | 0 |  |  |  |  | Interior Equipment | 466123.76 | 0 |  |  |  |  | Interior Equipment | 466123.76 | 0 |  |  |  |  | Interior Equipment | 486449.59 | 0 |  |  |  |  | Interior Equipment | 486449.59 | 0 |  |  |  |  | Interior Equipment | 770782.8 | 0 |  |  |  |  | Interior Equipment | 770782.8 | 0 |  |  |  |  | Interior Equipment
[10 empty] | x | [13 empty] | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment
[9 empty] | x | [14 empty] | Fans | 1769874.65 | 0 |  |  |  |  | Fans | 745406.98 | 0 | [5 empty] | Fans | 37350.69 | 0 |  |  |  |  | Fans | 19761.18 | 0 | [5 empty] | Fans | 183863.02 | 0 |  |  |  |  | Fans | 121679.88 | 0 | [5 empty] | Fans | 90850.82 | 0 |  |  |  |  | Fans | 60124.7433 | 0 |  |  |  |  | Fans | 346950.68 | 0 |  |  |  |  | Fans | 229610.7021 | 0 |  |  |  |  | Fans | 776539.58 | 0 |  |  |  |  | Fans | 513911.0785 | 0 |  |  |  |  | Fans | 1154425.96 | 0 |  |  |  |  | Fans | 763994.9147 | 0 |  |  |  |  | Fans
[8 empty] | x | [15 empty] | Pumps | 227.67 | 0 |  |  |  |  | Pumps | 91068.1125 | 0 | [5 empty] | Pumps | 1.56 | 0 |  |  |  |  | Pumps | 18040.75 | 0 | [5 empty] | Pumps | 30.71 | 0 |  |  |  |  | Pumps | 175400.0375 | 0 | [5 empty] | Pumps | 23.25 | 0 |  |  |  |  | Pumps | 97661.9915 | 0 |  |  |  |  | Pumps | 289.64 | 0 |  |  |  |  | Pumps | 127468.2265 | 0 |  |  |  |  | Pumps | 202.08 | 0 |  |  |  |  | Pumps | 133026.6357 | 0 |  |  |  |  | Pumps | 40.47 | 0 |  |  |  |  | Pumps | 210779.7941 | 0 |  |  |  |  | Pumps | 724183.9625
[7 empty] | x | [16 empty] | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection
[6 empty] | x | [17 empty] | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 |  |  |  |  | Humidification
[6 empty] | x | [17 empty] | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery
[11 empty] | x | [12 empty] | Water Systems | 0 | 1933376.45 |  |  |  |  | Water Systems | 0 | 1933260.68 | [5 empty] | Water Systems | 0 | 12938.54 |  |  |  |  | Water Systems | 0 | 12957.18 | [5 empty] | Water Systems | 0 | 215878.57 |  |  |  |  | Water Systems | 0 | 215836.23 | [5 empty] | Water Systems | 0 | 162419.39 |  |  |  |  | Water Systems | 0 | 162419.39 |  |  |  |  | Water Systems | 0 | 203846.41 |  |  |  |  | Water Systems | 0 | 203846.41 |  |  |  |  | Water Systems | 0 | 213230.02 |  |  |  |  | Water Systems | 0 | 213230.02 |  |  |  |  | Water Systems | 0 | 335661.92 |  |  |  |  | Water Systems | 0 | 335661.92 |  |  |  |  | Water Systems
[7 empty] | x | [16 empty] | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration
[24 empty] | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 |  |  |  |  | Generators
[24 empty] | Total End Uses | 5751695.85 | 18567465.48 |  |  |  |  | Total End Uses | 7732059.45 | 2463780.09 | [5 empty] | Total End Uses | 159263.72 | 328257.35 |  |  |  |  | Total End Uses | 214487.62 | 12957.18 | [5 empty] | Total End Uses | 1282945.46 | 1910005.31 |  |  |  |  | Total End Uses | 1912285.83 | 215836.23 | [5 empty] | Total End Uses | 774302.4 | 1125429.61 |  |  |  |  | Total End Uses | 774302.4 | 1125429.61 |  |  |  |  | Total End Uses | 1310484.28 | 1605713.76 |  |  |  |  | Total End Uses | 1310484.28 | 1605713.76 |  |  |  |  | Total End Uses | 1618660.2 | 1463188.02 |  |  |  |  | Total End Uses | 1618660.2 | 1463188.02 |  |  |  |  | Total End Uses | 2323455.93 | 2746266.88 |  |  |  |  | Total End Uses | 2323455.93 | 2746266.88 |  |  |  |  | Total End Uses
Index | 0 | 1 |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
| 262 Homes - Existing | 262 Homes - Geo | 262 Homes - Geo + Wx | 262 Homes - Geo + PV + Wx | Community Center - Existing | Community Center - Geo | Bryant Elementary - Existing | Bryant Elementary - Geo | County Health - Existing | County Health - Geo | Wheeler Center - Existing | Wheeler Center - Geo | Wheeler Maintenance (S) - Existing | Wheeler Maintenance (S) - Geo | Wheeler Vehicle Storage (E) - Existing | Wheeler Vehicle Storage (E) - Geo | Central Geo Pumping (Homes Only) |  | Whole Neighborhood - Existing | Whole Neighborhood - Geo | Whole Neighborhood - Geo + Wx | Whole Neighborhood - Geo + PV + Wx | Whole Neighborhood - Geo + PV + Wx + 2030 Grid |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI
Lighting | 2.8661 | 2.8661 |  |  | 8.3462 | 8.3462 | 8.6402 | 8.6402 | 7.4719 | 7.4719 | 5.8988 | 5.8988 | 5.8988 | 5.8988 | 5.8988 | 5.8988 | [7 empty] | Lighting | 628966.31 | 0 | 0 | 0 | 0 | 2.8661 | Lighting | 628966.31 | 0 | 0 | 0 | 0 | 2.8661 |  | Lighting | 37174 | 0 | 0 | 0 | 0 | 8.3462 | Lighting | 37174 | 0 | 0 | 0 | 0 | 8.3462 |  | Lighting | 485362.19 | 0 | 0 | 0 | 0 | 8.6402 | Lighting | 485362.19 | 0 | 0 | 0 | 0 | 8.6402 |  | Lighting | 233706.24 | 0 | 0 | 0 | 0 | 7.4719 | Lighting | 233706.24 | 0 | 0 | 0 | 0 | 7.4719 | Lighting | 240811.81 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 240811.81 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 251312.67 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 251312.67 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 398206.7 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 398206.7 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 0 | 0 | 0 | 0 | 0 | 0
Heating | 73.3827 | 15.6902 |  |  | 70.7945 | 14.397 | 30.158 | 10.644 | 30.7887 | 10.8666 | 34.341 | 12.1198 | 29.3395 | 10.3556 | 35.7095 | 12.6034 |  |  | 24138552.04 | 6231869.2839 |  |  |  | Heating | 0 | 16103569.63 | 0 | 0 | 0 | 73.3827 | Heating | 3443159.32 | 0 | 0 | 0 | 0 | 15.6902 | 4.677 | Heating | 0 | 315318.81 | 0 | 0 | 0 | 70.7945 | Heating | 64124.07 | 0 | 0 | 0 | 0 | 14.397 | 4.9173 | Heating | 0 | 1694126.74 | 0 | 0 | 0 | 30.158 | Heating | 597928.16 | 0 | 0 | 0 | 0 | 10.644 | 2.8333 | Heating | 0 | 963010.22 | 0 | 0 | 0 | 30.7887 | Heating | 339886.5712 | 0 | 0 | 0 | 0 | 10.8666 | Heating | 68.49 | 1401867.35 | 0 | 0 | 0 | 34.341 | Heating | 494777.6016 | 0 | 0 | 0 | 0 | 12.1198 | Heating | 27.84 | 1249958 | 0 | 0 | 0 | 29.3395 | Heating | 441190.2804 | 0 | 0 | 0 | 0 | 10.3556 | Heating | 0 | 2410604.96 | 0 | 0 | 0 | 35.7095 | Heating | 850803.2806 | 0 | 0 | 0 | 0 | 12.6034 | Heating | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 7.4161 | 5.0877 |  |  | 9.8666 | 8.5774 | 5.0781 | 4.2469 | 4.1894 | 3.5036 | 6.2767 | 5.2493 | 2.4441 | 2.044 | 0 | 0 |  |  | 2448037.48 | 1804210.1404 |  |  |  | Cooling | 1627426.68 | 0 | 0 | 0 | 0 | 7.4161 | Cooling | 1116471.81 | 0 | 0 | 0 | 0 | 5.0877 | 1.4577 | Cooling | 43945.64 | 0 | 0 | 0 | 0 | 9.8666 | Cooling | 38203.93 | 0 | 0 | 0 | 0 | 8.5774 | 1.1503 | Cooling | 285262.1 | 0 | 0 | 0 | 0 | 5.0781 | Cooling | 238568.12 | 0 | 0 | 0 | 0 | 4.2469 | 1.1957 | Cooling | 131034.73 | 0 | 0 | 0 | 0 | 4.1894 | Cooling | 109585.9183 | 0 | 0 | 0 | 0 | 3.5036 | Cooling | 256239.89 | 0 | 0 | 0 | 0 | 6.2767 | Cooling | 214296.4972 | 0 | 0 | 0 | 0 | 5.2493 | Cooling | 104128.44 | 0 | 0 | 0 | 0 | 2.4441 | Cooling | 87083.8649 | 0 | 0 | 0 | 0 | 2.044 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 0.0010375 | 0.41499 |  |  | 0.00035025 | 4.0505 | 0.00054668 | 3.1224 | 0.00074333 | 3.1224 | 0.0070948 | 3.1224 | 0.0047432 | 3.1224 | 0.0005995 | 3.1224 | 3.3 |  | 26586589.52 | 8036079.4243 |  |  |  | Pumps | 227.67 | 0 | 0 | 0 | 0 | 0.0010375 | Pumps | 91068.1125 | 0 | 0 | 0 | 0 | 0.41499 |  | Pumps | 1.56 | 0 | 0 | 0 | 0 | 0.00035025 | Pumps | 18040.75 | 0 | 0 | 0 | 0 | 4.0505 |  | Pumps | 30.71 | 0 | 0 | 0 | 0 | 0.00054668 | Pumps | 175400.0375 | 0 | 0 | 0 | 0 | 3.1224 |  | Pumps | 23.25 | 0 | 0 | 0 | 0 | 0.00074333 | Pumps | 97661.9915 | 0 | 0 | 0 | 0 | 3.1224 | Pumps | 289.64 | 0 | 0 | 0 | 0 | 0.0070948 | Pumps | 127468.2265 | 0 | 0 | 0 | 0 | 3.1224 | Pumps | 202.08 | 0 | 0 | 0 | 0 | 0.0047432 | Pumps | 133026.6357 | 0 | 0 | 0 | 0 | 3.1224 | Pumps | 40.47 | 0 | 0 | 0 | 0 | 0.0005995 | Pumps | 210779.7941 | 0 | 0 | 0 | 0 | 3.1224 | Pumps | 724183.9625 | 0 | 0 | 0 | 0 | 3.3
Fans | 8.0652 | 3.3968 |  |  | 8.3859 | 4.4367 | 3.273 | 2.1661 | 2.9046 | 1.9223 | 8.4987 | 5.6244 | 18.2268 | 12.0625 | 17.1011 | 11.3174 |  |  | Savings: | 69.77% |  |  |  | Fans | 1769874.65 | 0 | 0 | 0 | 0 | 8.0652 | Fans | 745406.98 | 0 | 0 | 0 | 0 | 3.3968 | 2.3744 | Fans | 37350.69 | 0 | 0 | 0 | 0 | 8.3859 | Fans | 19761.18 | 0 | 0 | 0 | 0 | 4.4367 | 1.8901 | Fans | 183863.02 | 0 | 0 | 0 | 0 | 3.273 | Fans | 121679.88 | 0 | 0 | 0 | 0 | 2.1661 | 1.511 | Fans | 90850.82 | 0 | 0 | 0 | 0 | 2.9046 | Fans | 60124.7433 | 0 | 0 | 0 | 0 | 1.9223 | Fans | 346950.68 | 0 | 0 | 0 | 0 | 8.4987 | Fans | 229610.7021 | 0 | 0 | 0 | 0 | 5.6244 | Fans | 776539.58 | 0 | 0 | 0 | 0 | 18.2268 | Fans | 513911.0785 | 0 | 0 | 0 | 0 | 12.0625 | Fans | 1154425.96 | 0 | 0 | 0 | 0 | 17.1011 | Fans | 763994.9147 | 0 | 0 | 0 | 0 | 11.3174 | Fans | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 10.2791 | 10.2791 |  |  | 9.1585 | 9.1585 | 5.8465 | 5.8465 | 10.1889 | 10.1889 | 11.4179 | 11.4179 | 11.4179 | 11.4179 | 11.418 | 11.418 | [7 empty] | Receptacles | 1725200.53 | 530519.41 | 0 | 0 | 0 | 10.2791 | Receptacles | 1725200.53 | 530519.41 | 0 | 0 | 0 | 10.2791 |  | Receptacles | 40791.83 | 0 | 0 | 0 | 0 | 9.1585 | Receptacles | 40791.83 | 0 | 0 | 0 | 0 | 9.1585 |  | Receptacles | 328427.45 | 0 | 0 | 0 | 0 | 5.8465 | Receptacles | 328427.45 | 0 | 0 | 0 | 0 | 5.8465 |  | Receptacles | 318687.37 | 0 | 0 | 0 | 0 | 10.1889 | Receptacles | 318687.37 | 0 | 0 | 0 | 0 | 10.1889 | Receptacles | 466123.76 | 0 | 0 | 0 | 0 | 11.4179 | Receptacles | 466123.76 | 0 | 0 | 0 | 0 | 11.4179 | Receptacles | 486449.59 | 0 | 0 | 0 | 0 | 11.4179 | Receptacles | 486449.59 | 0 | 0 | 0 | 0 | 11.4179 | Receptacles | 770782.8 | 0 | 0 | 0 | 0 | 11.418 | Receptacles | 770782.8 | 0 | 0 | 0 | 0 | 11.418 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0
DHW | 8.8102 | 8.8097 |  |  | 2.9049 | 2.9091 | 3.843 | 3.8422 | 5.1928 | 5.1928 | 4.9933 | 4.9933 | 5.0049 | 5.0049 | 4.9723 | 4.9723 |  |  | kbtu |  |  |  |  | DHW | 0 | 1933376.45 | 0 | 0 | 0 | 8.8102 | DHW | 0 | 1933260.68 | 0 | 0 | 0 | 8.8097 |  | DHW | 0 | 12938.54 | 0 | 0 | 0 | 2.9049 | DHW | 0 | 12957.18 | 0 | 0 | 0 | 2.9091 |  | DHW | 0 | 215878.57 | 0 | 0 | 0 | 3.843 | DHW | 0 | 215836.23 | 0 | 0 | 0 | 3.8422 |  | DHW | 0 | 162419.39 | 0 | 0 | 0 | 5.1928 | DHW | 0 | 162419.39 | 0 | 0 | 0 | 5.1928 | DHW | 0 | 203846.41 | 0 | 0 | 0 | 4.9933 | DHW | 0 | 203846.41 | 0 | 0 | 0 | 4.9933 | DHW | 0 | 213230.02 | 0 | 0 | 0 | 5.0049 | DHW | 0 | 213230.02 | 0 | 0 | 0 | 5.0049 | DHW | 0 | 335661.92 | 0 | 0 | 0 | 4.9723 | DHW | 0 | 335661.92 | 0 | 0 | 0 | 4.9723 | DHW | 0 | 0 | 0 | 0 | 0 | 0
EUI | 110.8205 | 46.5446 | 43.0553 | 16.8405 | 109.4569 | 51.8754 | 56.8394 | 38.5083 | 60.737 | 42.2684 | 71.4335 | 48.4258 | 72.3368 | 49.906 | 75.1003 | 49.3323 | 3.3 |  | 40967134.26 | 22087932.9032 | 21322217.1044 | 15569470.1302 |  | kBtu | 5751695.84 | 18567465.49 | 0 | 0 | 0 | 110.8205 | kBtu | 7750273.0625 | 2463780.09 | 0 | 0 | 0 | 46.5446 |  | kBtu | 159263.72 | 328257.35 | 0 | 0 | 0 | 109.4569 | kBtu | 218095.76 | 12957.18 | 0 | 0 | 0 | 51.8754 |  | kBtu | 1282945.47 | 1910005.31 | 0 | 0 | 0 | 56.8394 | kBtu | 1947365.8375 | 215836.23 | 0 | 0 | 0 | 38.5083 |  | kBtu | 774302.41 | 1125429.61 | 0 | 0 | 0 | 60.737 | kBtu | 1159652.8343 | 162419.39 | 0 | 0 | 0 | 42.2684 | kBtu | 1310484.27 | 1605713.76 | 0 | 0 | 0 | 71.4335 | kBtu | 1773088.5974 | 203846.41 | 0 | 0 | 0 | 48.4258 | kBtu | 1618660.2 | 1463188.02 | 0 | 0 | 0 | 72.3368 | kBtu | 1912974.1196 | 213230.02 | 0 | 0 | 0 | 49.906 | kBtu | 2323455.93 | 2746266.88 | 0 | 0 | 0 | 75.1003 | kBtu | 2994567.4894 | 335661.92 | 0 | 0 | 0 | 49.3323 | kBtu | 724183.9625 | 0 | 0 | 0 | 0 | 3.3
| Savings: | 64.2759 | 67.7652 | 93.98 | Savings: | 57.5815 | Savings: | 18.3311 | Savings: | 18.4686 | Savings: | 23.0076 | Savings: | 22.4308 | Savings: | 25.768 |  |  | Savings: | 18879201.3568 | 19644917.1556 | 25397664.1298
|  | 58% | 61.15% | 84.8% | 3: 52.61%; 5: 32.25%; 7: 30.41%; 9: 32.21%; 11: 31.01%; 13: 34.31% |  |  | 46.08% | 47.95% | 62%
Lighting | 36172.4695 | 36172.4695 |  |  | 1356.3339 | 1356.3339 | 17708.9689 | 17708.9689 | 8527.0271 | 8527.0271 | 8786.2816 | 8786.2816 | 9169.4169 | 9169.4169 | 14529.0058 | 14529.0058 | [7 empty] | Lighting | 36172.4695 | 0 | 0 | 0 | 0 | 36172.4695 | Lighting | 36172.4695 | 0 | 0 | 0 | 0 | 36172.4695 |  | Lighting | 1356.3339 | 0 | 0 | 0 | 0 | 1356.3339 | Lighting | 1356.3339 | 0 | 0 | 0 | 0 | 1356.3339 |  | Lighting | 17708.9689 | 0 | 0 | 0 | 0 | 17708.9689 | Lighting | 17708.9689 | 0 | 0 | 0 | 0 | 17708.9689 |  | Lighting | 8527.0271 | 0 | 0 | 0 | 0 | 8527.0271 | Lighting | 8527.0271 | 0 | 0 | 0 | 0 | 8527.0271 | Lighting | 8786.2816 | 0 | 0 | 0 | 0 | 8786.2816 | Lighting | 8786.2816 | 0 | 0 | 0 | 0 | 8786.2816 | Lighting | 9169.4169 | 0 | 0 | 0 | 0 | 9169.4169 | Lighting | 9169.4169 | 0 | 0 | 0 | 0 | 9169.4169 | Lighting | 14529.0058 | 0 | 0 | 0 | 0 | 14529.0058 | Lighting | 14529.0058 | 0 | 0 | 0 | 0 | 14529.0058 | Lighting | 0 | 0 | 0 | 0 | 0 | 0
Heating | 127215.0973 | 198019.4701 |  |  | 3064.7525 | 2339.6366 | 16466.1255 | 21816.0611 | 9360.0123 | 12401.1323 | 13627.9988 | 18052.5005 | 12150.0273 | 16097.3086 | 23429.9612 | 31042.4857 | [7 empty] | Heating | 0 | 127215.0973 | 0 | 0 | 0 | 127215.0973 | Heating | 198019.4701 | 0 | 0 | 0 | 0 | 198019.4701 |  | Heating | 0 | 3064.7525 | 0 | 0 | 0 | 3064.7525 | Heating | 2339.6366 | 0 | 0 | 0 | 0 | 2339.6366 |  | Heating | 0 | 16466.1255 | 0 | 0 | 0 | 16466.1255 | Heating | 21816.0611 | 0 | 0 | 0 | 0 | 21816.0611 |  | Heating | 0 | 9360.0123 | 0 | 0 | 0 | 9360.0123 | Heating | 12401.1323 | 0 | 0 | 0 | 0 | 12401.1323 | Heating | 2.4989 | 13625.4999 | 0 | 0 | 0 | 13627.9988 | Heating | 18052.5005 | 0 | 0 | 0 | 0 | 18052.5005 | Heating | 1.0158 | 12149.0115 | 0 | 0 | 0 | 12150.0273 | Heating | 16097.3086 | 0 | 0 | 0 | 0 | 16097.3086 | Heating | 0 | 23429.9612 | 0 | 0 | 0 | 23429.9612 | Heating | 31042.4857 | 0 | 0 | 0 | 0 | 31042.4857 | Heating | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 93594.9048 | 64209.389 |  |  | 1603.4046 | 1393.9121 | 10408.0989 | 8704.4181 | 4780.9451 | 3998.3618 | 9349.1919 | 7818.8415 | 3799.2397 | 3177.3498 | 0 | 0 | [7 empty] | Cooling | 93594.9048 | 0 | 0 | 0 | 0 | 93594.9048 | Cooling | 64209.389 | 0 | 0 | 0 | 0 | 64209.389 |  | Cooling | 1603.4046 | 0 | 0 | 0 | 0 | 1603.4046 | Cooling | 1393.9121 | 0 | 0 | 0 | 0 | 1393.9121 |  | Cooling | 10408.0989 | 0 | 0 | 0 | 0 | 10408.0989 | Cooling | 8704.4181 | 0 | 0 | 0 | 0 | 8704.4181 |  | Cooling | 4780.9451 | 0 | 0 | 0 | 0 | 4780.9451 | Cooling | 3998.3618 | 0 | 0 | 0 | 0 | 3998.3618 | Cooling | 9349.1919 | 0 | 0 | 0 | 0 | 9349.1919 | Cooling | 7818.8415 | 0 | 0 | 0 | 0 | 7818.8415 | Cooling | 3799.2397 | 0 | 0 | 0 | 0 | 3799.2397 | Cooling | 3177.3498 | 0 | 0 | 0 | 0 | 3177.3498 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 13.0935 | 5237.4165 |  |  | 0.056918 | 658.2364 | 1.1205 | 6399.6617 | 0.8483 | 3563.3043 | 10.5678 | 4650.8173 | 7.3731 | 4853.6219 | 1.4766 | 7690.5307 | [7 empty] | Pumps | 13.0935 | 0 | 0 | 0 | 0 | 13.0935 | Pumps | 5237.4165 | 0 | 0 | 0 | 0 | 5237.4165 |  | Pumps | 0.056918 | 0 | 0 | 0 | 0 | 0.056918 | Pumps | 658.2364 | 0 | 0 | 0 | 0 | 658.2364 |  | Pumps | 1.1205 | 0 | 0 | 0 | 0 | 1.1205 | Pumps | 6399.6617 | 0 | 0 | 0 | 0 | 6399.6617 |  | Pumps | 0.8483 | 0 | 0 | 0 | 0 | 0.8483 | Pumps | 3563.3043 | 0 | 0 | 0 | 0 | 3563.3043 | Pumps | 10.5678 | 0 | 0 | 0 | 0 | 10.5678 | Pumps | 4650.8173 | 0 | 0 | 0 | 0 | 4650.8173 | Pumps | 7.3731 | 0 | 0 | 0 | 0 | 7.3731 | Pumps | 4853.6219 | 0 | 0 | 0 | 0 | 4853.6219 | Pumps | 1.4766 | 0 | 0 | 0 | 0 | 1.4766 | Pumps | 7690.5307 | 0 | 0 | 0 | 0 | 7690.5307 | Pumps | 41648.5301 | 0 | 0 | 0 | 0 | 41648.5301
Fans | 101787.2273 | 42869.0866 |  |  | 1362.7807 | 721.0082 | 6708.4428 | 4439.6231 | 3314.7913 | 2193.7168 | 12658.874 | 8377.5969 | 28332.8936 | 18750.6063 | 42120.4904 | 27875.1878 | [7 empty] | Fans | 101787.2273 | 0 | 0 | 0 | 0 | 101787.2273 | Fans | 42869.0866 | 0 | 0 | 0 | 0 | 42869.0866 |  | Fans | 1362.7807 | 0 | 0 | 0 | 0 | 1362.7807 | Fans | 721.0082 | 0 | 0 | 0 | 0 | 721.0082 |  | Fans | 6708.4428 | 0 | 0 | 0 | 0 | 6708.4428 | Fans | 4439.6231 | 0 | 0 | 0 | 0 | 4439.6231 |  | Fans | 3314.7913 | 0 | 0 | 0 | 0 | 3314.7913 | Fans | 2193.7168 | 0 | 0 | 0 | 0 | 2193.7168 | Fans | 12658.874 | 0 | 0 | 0 | 0 | 12658.874 | Fans | 8377.5969 | 0 | 0 | 0 | 0 | 8377.5969 | Fans | 28332.8936 | 0 | 0 | 0 | 0 | 28332.8936 | Fans | 18750.6063 | 0 | 0 | 0 | 0 | 18750.6063 | Fans | 42120.4904 | 0 | 0 | 0 | 0 | 42120.4904 | Fans | 27875.1878 | 0 | 0 | 0 | 0 | 27875.1878 | Fans | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 103408.976 | 103408.976 |  |  | 1488.3344 | 1488.3344 | 11983.0338 | 11983.0338 | 11627.6563 | 11627.6563 | 17007.0338 | 17007.0338 | 17748.6439 | 17748.6439 | 28122.8512 | 28122.8512 | [7 empty] | Receptacles | 99217.9748 | 4191.0011 | 0 | 0 | 0 | 103408.976 | Receptacles | 99217.9748 | 4191.0011 | 0 | 0 | 0 | 103408.976 |  | Receptacles | 1488.3344 | 0 | 0 | 0 | 0 | 1488.3344 | Receptacles | 1488.3344 | 0 | 0 | 0 | 0 | 1488.3344 |  | Receptacles | 11983.0338 | 0 | 0 | 0 | 0 | 11983.0338 | Receptacles | 11983.0338 | 0 | 0 | 0 | 0 | 11983.0338 |  | Receptacles | 11627.6563 | 0 | 0 | 0 | 0 | 11627.6563 | Receptacles | 11627.6563 | 0 | 0 | 0 | 0 | 11627.6563 | Receptacles | 17007.0338 | 0 | 0 | 0 | 0 | 17007.0338 | Receptacles | 17007.0338 | 0 | 0 | 0 | 0 | 17007.0338 | Receptacles | 17748.6439 | 0 | 0 | 0 | 0 | 17748.6439 | Receptacles | 17748.6439 | 0 | 0 | 0 | 0 | 17748.6439 | Receptacles | 28122.8512 | 0 | 0 | 0 | 0 | 28122.8512 | Receptacles | 28122.8512 | 0 | 0 | 0 | 0 | 28122.8512 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0
DHW | 15273.3014 | 15272.3869 |  |  | 125.7566 | 125.9378 | 2098.2395 | 2097.828 | 1578.6411 | 1578.6411 | 1981.2925 | 1981.2925 | 2072.4968 | 2072.4968 | 3262.478 | 3262.478 |  |  | $ |  |  |  |  | DHW | 0 | 15273.3014 | 0 | 0 | 0 | 15273.3014 | DHW | 0 | 15272.3869 | 0 | 0 | 0 | 15272.3869 |  | DHW | 0 | 125.7566 | 0 | 0 | 0 | 125.7566 | DHW | 0 | 125.9378 | 0 | 0 | 0 | 125.9378 |  | DHW | 0 | 2098.2395 | 0 | 0 | 0 | 2098.2395 | DHW | 0 | 2097.828 | 0 | 0 | 0 | 2097.828 |  | DHW | 0 | 1578.6411 | 0 | 0 | 0 | 1578.6411 | DHW | 0 | 1578.6411 | 0 | 0 | 0 | 1578.6411 | DHW | 0 | 1981.2925 | 0 | 0 | 0 | 1981.2925 | DHW | 0 | 1981.2925 | 0 | 0 | 0 | 1981.2925 | DHW | 0 | 2072.4968 | 0 | 0 | 0 | 2072.4968 | DHW | 0 | 2072.4968 | 0 | 0 | 0 | 2072.4968 | DHW | 0 | 3262.478 | 0 | 0 | 0 | 3262.478 | DHW | 0 | 3262.478 | 0 | 0 | 0 | 3262.478 | DHW | 0 | 0 | 0 | 0 | 0 | 0
Cost | 477465.0698 | 465189.1946 | 421020.1505 | 110920.3421 | 9001.4196 | 8083.3995 | 65374.0298 | 73149.5947 | 39189.9214 | 43889.8397 | 63421.2404 | 66674.364 | 73280.0913 | 71869.4442 | 111466.2632 | 112522.5393 | 41648.5301 |  | 839198.0355 | 883026.9059 | 838857.8619 | 528758.0534 |  | Cost | 330785.67 | 146679.3998 | 0 | 0 | 0 | 477465.0698 | Cost | 445725.8066 | 19463.388 | 0 | 0 | 0 | 465189.1946 |  | Cost | 5810.9105 | 3190.5091 | 0 | 0 | 0 | 9001.4196 | Cost | 7957.4617 | 125.9378 | 0 | 0 | 0 | 8083.3995 |  | Cost | 46809.6649 | 18564.365 | 0 | 0 | 0 | 65374.0298 | Cost | 71051.7667 | 2097.828 | 0 | 0 | 0 | 73149.5947 |  | Cost | 28251.268 | 10938.6534 | 0 | 0 | 0 | 39189.9214 | Cost | 42311.1986 | 1578.6411 | 0 | 0 | 0 | 43889.8397 | Cost | 47814.448 | 15606.7923 | 0 | 0 | 0 | 63421.2404 | Cost | 64693.0715 | 1981.2925 | 0 | 0 | 0 | 66674.364 | Cost | 59058.583 | 14221.5083 | 0 | 0 | 0 | 73280.0913 | Cost | 69796.9474 | 2072.4968 | 0 | 0 | 0 | 71869.4442 | Cost | 84773.824 | 26692.4392 | 0 | 0 | 0 | 111466.2632 | Cost | 109260.0613 | 3262.478 | 0 | 0 | 0 | 112522.5393 | Cost | 41648.5301 | 0 | 0 | 0 | 0 | 41648.5301
| Savings: | 12275.8752 | 56444.9193 | 366544.7277 | Savings: | 918.0201 | Savings: | -7775.5648 | Savings: | -4699.9183 | Savings: | -3253.1236 | Savings: | 1410.6471 | Savings: | -1056.2761 |  |  | Savings: | -43828.8704 | 340.1736 | 310439.9821
| 0 | 2.571% | 11.82% | 76.77% | 3: 10.2%; 5: -11.89%; 7: -11.99%; 9: -5.129%; 11: 1.925%; 13: -0.9476% |  |  | -5.223% | 0.04054% | 36.99%
Metric Tons
Carbon | 2083.2517 | 1611.6938 | 1465.0048 | 365.2077 | 47.8337 | 42.3659 | 346.4072 | 383.5901 | 207.6206 | 230.2233 | 335.5425 | 349.6494 | 386.8825 | 376.8795 | 589.5755 | 590.066 | 138.3949 |  | 3997.1136 | 3722.8629 | 3576.1739 | 2476.3767 | 993.2 | Carbon | 1099.176 | 984.0757 | 0 | 0 | 0 | 2083.2517 | Carbon | 1481.1135 | 130.5803 | 0 | 0 | 0 | 1611.6938 |  | Carbon | 30.436 | 17.3976 | 0 | 0 | 0 | 47.8337 | Carbon | 41.6791 | 0.68673 | 0 | 0 | 0 | 42.3659 |  | Carbon | 245.1769 | 101.2303 | 0 | 0 | 0 | 346.4072 | Carbon | 372.1507 | 11.4393 | 0 | 0 | 0 | 383.5901 |  | Carbon | 147.9728 | 59.6478 | 0 | 0 | 0 | 207.6206 | Carbon | 221.6151 | 8.6082 | 0 | 0 | 0 | 230.2233 | Carbon | 250.4397 | 85.1028 | 0 | 0 | 0 | 335.5425 | Carbon | 338.8455 | 10.8039 | 0 | 0 | 0 | 349.6494 | Carbon | 309.3336 | 77.549 | 0 | 0 | 0 | 386.8825 | Carbon | 365.5783 | 11.3012 | 0 | 0 | 0 | 376.8795 | Carbon | 444.0233 | 145.5521 | 0 | 0 | 0 | 589.5755 | Carbon | 572.2759 | 17.7901 | 0 | 0 | 0 | 590.066 | Carbon | 138.3949 | 0 | 0 | 0 | 0 | 138.3949
| Savings: | 471.5579 | 618.2469 | 1718.044 | Savings: | 5.4678 | Savings: | -37.1829 | Savings: | -22.6027 | Savings: | -14.1069 | Savings: | 10.003 | Savings: | -0.4905 |  |  | Savings: | 274.2507 | 420.9397 | 1520.7369 | 3003.9136
|  | 22.64% | 29.68% | 82.47% | 3: 11.43%; 5: -10.73%; 7: -10.89%; 9: -4.204%; 11: 2.586%; 13: -0.0832% |  |  | 6.861% | 10.53% | 38.05% | 75.15%
[25 empty] | Heating | Cooling | [13 empty] | Heating | Cooling | [13 empty] | Heating | Cooling | [13 empty] | Heating | Cooling | [12 empty] | Heating | Cooling | [12 empty] | Heating | Cooling | [12 empty] | Heating
Peak Heating | 655.4475 |  |  |  | 2: 15.829; 4: 96.8602; 6: 34.736; 8: 76.6265; 10: 75.5847; 12: 181.3115 | [6 empty] | Peak Load | 655.4475 | 441.6855 | 0 | 0 | 0 | 1097.1329 | [8 empty] | Peak Load | 15.829 | 13.9749 | 0 | 0 | 0 | 29.8038 | [8 empty] | Peak Load | 96.8602 | 106.5978 | 0 | 0 | 0 | 203.458 | [8 empty] | Peak Load | 34.736 | 47.1445 | 0 | 0 | 0 | 81.8806 | [7 empty] | Carbon | 76.6265 | 84.8401 | 0 | 0 | 0 | 161.4666 | [7 empty] | Peak Load | 75.5847 | 27.6516 | 0 | 0 | 0 | 103.2363 | [7 empty] | Peak Load | 181.3115 |  | 0 | 0 | 0 | 181.3115
Peak Cooling | 441.6855 |  |  |  | 2: 13.9749; 4: 106.5978; 6: 47.1445; 8: 84.8401; 10: 27.6516; 12: 0
Central Pump Assumptions | North Loop |  |  |  | 6: South Loop
% of loop heating tons | 85.33% |  |  |  | 2: 2.061%; 4: 12.61%; 6: 9.433%; 8: 20.81%; 10: 20.52%; 12: 49.23%
Max gpm | 2133.2384 |  |  |  | 2: 51.5175; 4: 315.2441
approx # of bores (500 ft) | 233.3393 |  |  |  | 2: 5.6351; 4: 34.4822
ft/ton | 178 |  |  |  | 2: 178; 4: 178
Central Pump kBtu |  | 724183.9625 |  |  | 3: 18040.75; 5: 175400.0375; 7: 97661.9915; 9: 127468.2265; 11: 133026.6357; 13: 210779.7941; 14: 1486561.3978 | total kBtu
$ |  | 41648.5301 |  |  | 3: 658.2364; 5: 6399.6617; 7: 3563.3043; 9: 4650.8173; 11: 4853.6219; 13: 7690.5307; 14: 69464.7024 | central pumping
$/ton |  | 63.5421 |  |  | 3: 41.5843; 5: 66.0711; 7: 102.5824; 9: 60.6946; 11: 64.2144; 13: 42.4161; 14: 63.015 | /heating ton average
Weatherization | System/Plant | Energy Cost |  | Energy Consumption | 3: CO2
|  | ($/yr) | % Savings | (kBtu/sf/yr) | 2: % Savings; 3: (metric tons); 4: % Savings
| 262 Homes - Existing | 477465.0698 | - | 110.8205 | 2: -; 3: 2083.2517; 4: -
| 262 Homes - Geo | 465189.1946 | 2.571% | 46.5446 | 2: 58%; 3: 1611.6938; 4: 22.64%
| 262 Homes - Geo + Wx | 421020.1505 | 11.82% | 43.0553 | 2: 61.15%; 3: 1465.0048; 4: 29.68%
Note on CE2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The heating, cooling, fans, and pumps were scaled using the ratios between the Existing and Geo models for the Elementary School
Note on CU2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The heating, cooling, fans, and pumps were scaled using the ratios between the Existing and Geo models for the Elementary School
Note on DK2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The heating, cooling, fans, and pumps were scaled using the ratios between the Existing and Geo models for the Elementary School
Note on EA2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The heating, cooling, fans, and pumps were scaled using the ratios between the Existing and Geo models for the Elementary School
Note on AJ11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on AZ11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on BP11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on CF11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on CV11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on DL11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on EB11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on EJ11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Buffer of 25%
Note on Y46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pulled from Carbon Grid Emissions spreadsheet
Note on B52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pumps have a buffer of 25% for contingency

## Load Summary
| Homes only | All north loads | All south loads | All loads | Community Center | Elementary | County Health | Wheeler Center | Wheeler Maintenance | Wheeler veh storage
Cooling peaks (tons) | 441.6855 | 562.2581 | 159.6363 | 721.8944 | 13.9749 | 106.5978 | 47.1445 | 84.8401 | 27.6516 | 0
Heating peaks (tons) | 655.4475 | 768.1367 | 368.2587 | 1136.3954 | 15.829 | 96.8602 | 34.736 | 76.6265 | 75.5847 | 181.3115
# bores (@700') | 180 | 200 | 90 | 280
# bores (@500') | 260 | 280 | 130 | 400
ln ft bore/heating ton | 202 | 185 | 184 | 180
Cooling gpm | 1325 | 1617 | 473 | 1930
Heating gpm | 1928 | 2273 | 1061 | 3334
Min loop temp | 35.6 | 35.5 | 35.5 | 35.2
Max loop temp | 72.9 | 73.5 | 67.2 | 71.2
based on peak from the energy model hourly profile

## Std Calcs (hidden)
[11 empty] | Single Home |  |  |  | School | [5 empty] | Community Center
DesignBuilder Fan Pressure Calc | [10 empty] | DesignBuilder Heat Pump Plant Load Estimation |  |  | Typical Range | DesignBuilder Heat Pump Plant Load Estimation |  |  | Typical Range |  |  | DesignBuilder Heat Pump Plant Load Estimation |  |  | Typical Range
[11 empty] | Inputs | Sqft | 837.58 | - | Inputs | Sqft | 56175 | - |  |  | Inputs | Sqft | 4454 | -
Inputs | [11 empty] | Htg (btu/sqft) | 38.4166 | 35-45 btu/sqft |  | Htg (btu/sqft) | 20.6911 | 35-45 btu/sqft |  |  |  | Htg (btu/sqft) | 42.6466 | 35-45 btu/sqft
[12 empty] | Clg (sqft/ton) | 595.7537 | 250-400 sqft/ton |  | Clg (sqft/ton) | 526.9808 | 250-400 sqft/ton |  |  |  | Clg (sqft/ton) | 318.7151 | 250-400 sqft/ton
AHU |  | Supply | Exhaust | Supply |  |  | Exhaust |  |  |  |  | Htg (COP) | 2.5 |  |  | Htg (COP) | 4 |  |  |  |  | Htg (COP) | 4
Tag | CFM | BHP | BHP | Eff | SP | kW | Eff | SP | kW | W/cfm |  | Clg (COP) | 4 |  |  | Clg (COP) | 4.8 |  |  |  |  | Clg (COP) | 4.8
HP | 1350 | 3.25 |  | 60% | 9.2003 | 2.4375 | 70% | 0 | 0 | 1.8056
|  |  |  | 60% | #DIV/0! | 0 | 70% | #DIV/0! | 0 |  |  | Cooling Heat Pump |  |  |  | Cooling Heat Pump | [5 empty] | Cooling Heat Pump
|  |  |  | 60% | #DIV/0! | 0 | 70% | #DIV/0! | 0 |  |  | Load Side Flow Rate (GPM) | 3.3742 | 2.4 gpm/ton |  | Load Side Flow Rate (GPM) | 255.8347 | 2.4 gpm/ton |  |  |  | Load Side Flow Rate (GPM) | 33.5397 | 2.4 gpm/ton
|  |  |  | 60% | #DIV/0! | 0 | 70% | #DIV/0! | 0 |  |  | Source Side Flow Rate (GPM) | 4.2178 | 3 gpm/ton |  | Source Side Flow Rate (GPM) | 319.7934 | 3 gpm/ton |  |  |  | Source Side Flow Rate (GPM) | 41.9246 | 3 gpm/ton
|  |  |  | 60% | #DIV/0! | 0 | 70% | #DIV/0! | 0 |  |  | Cooling Capacity (W) | 4940.2635 | - |  | Cooling Capacity (W) | 374575.0125 | - | 639024.9714 | Total Btu/h per AHU |  | Cooling Capacity (W) | 49106.3989 | - | 251326.5495 | Total Btu/h per AHU
[12 empty] | Cooling Capacity (tons) | 1.4059 |  |  | Cooling Capacity (tons) | 106.5978 |  | 447317.48 | Sensible Btu/h per AHU |  | Cooling Capacity (tons) | 13.9749 |  | 175928.5846 | Sensible Btu/h per AHU
|  |  |  | 70% | #DIV/0! | 0 | 70% | #DIV/0! | 0 |  |  | Cooling Power Consumption (W) | 1235.0659 | - |  | Cooling Power Consumption (W) | 78036.4609 | - |  |  |  | Cooling Power Consumption (W) | 10230.4998 | -
[12 empty] | Heating Heat Pump |  |  |  | Heating Heat Pump | [5 empty] | Heating Heat Pump
FCU | [11 empty] | Load Side Flow Rate (GPM) | 3.2177 | 1 gpm/10,000 Btu |  | Load Side Flow Rate (GPM) | 116.2323 | 1 gpm/10,000 Btu |  |  |  | Load Side Flow Rate (GPM) | 18.9948 | 1 gpm/10,000 Btu
Tag | CFM | SP | HP | Qty | [7 empty] | Source Side Flow Rate (GPM) | 4.2178 | 3 gpm/ton |  | Source Side Flow Rate (GPM) | 319.7934 | 3 gpm/ton |  |  |  | Source Side Flow Rate (GPM) | 41.9246 | 3 gpm/ton
[12 empty] | Heating Capacity (W) | 9422.2548 | - |  | Heating Capacity (W) | 340358.0376 | - |  |  |  | Heating Capacity (W) | 55621.6046 | -
[12 empty] | Heating capacity (Btu/h) | 32177 |  |  | Heating capacity (Btu/h) | 1162322.6984 |  | 387440.8995 | Btu/h per AHU |  | Heating capacity (Btu/h) | 189947.7798 |  | 189947.7798 | Btu/h per AHU
[12 empty] | Heating Power Consumption (W) | 3768.9019 | - |  | Heating Power Consumption (W) | 85089.5094 | - |  |  |  | Heating Power Consumption (W) | 13905.4012 | -
[12 empty] | Geothermal Loop |  |  |  | Geothermal Loop | [5 empty] | Geothermal Loop
[12 empty] | Source Side Flow Rate (GPM) [Htg+Clg Geo] | 8.4355 |  |  | Source Side Flow Rate (GPM) [Htg+Clg Geo] | 319.7934 |  |  |  |  | Source Side Flow Rate (GPM) [Htg+Clg Geo] | 83.8492
[5 empty] | Eff | SP | kW | W/CFM
Total | 0 |  | 0 |  |  | #DIV/0! | 0 | #DIV/0! |  |  |  | Ground Heat Exchanger |  |  |  | Ground Heat Exchanger | [5 empty] | Ground Heat Exchanger
[12 empty] | # boreholes based on cooling load (250 ft bores) | 0.70296 | each 250 ft borehole is about 2 tons cooling capacity |  | # boreholes based on cooling load (250 ft bores) | 106.5978 | each 250 ft borehole is about 1 tons cooling capacity |  |  |  | # boreholes based on cooling load (250 ft bores) | 13.9749 | each 250 ft borehole is about 1 tons cooling capacity
[12 empty] | # of Ground heat exchangers as per documents | 1 |  |  | # of Ground heat exchangers as per documents | 1 |  |  |  |  | # of Ground heat exchangers as per documents | 1
DesignBuilder Pump Head Calc | [11 empty] | Design flow Rate (GPM) | 8.4355 |  |  | Design flow Rate (GPM) | 319.7934 |  |  |  |  | Design flow Rate (GPM) | 83.8492
Inputs | [11 empty] | Air Flow | 1350 | /3 tons |  | Air Flow | 71953.5188 | cfm total |  |  |  | Air Flow | 9433.0323 | cfm
[13 empty] | 450 | /tons |  |  | 23984.5063 | cfm per AHU
Pump |  |  |  |  | Head
Tag | HP | GPM | Eff |  | ft of H2O | PSI | kW
North Pri + Secondary | 158 | 2500 | 82% |  | 159.9506 | 69.1551 | 117.71
South Pri + Sec | 100 | 2400 | 83% |  | 106.7387 | 46.1488 | 74.5
Connecting (2) | 30 | 600 | 73% |  | 112.6543 | 48.7064 | 22.35
[5 empty] | #DIV/0! | #DIV/0! | 0
[5 empty] | #DIV/0! | #DIV/0! | 0
[5 empty] | #DIV/0! | #DIV/0! | 0
Notes:
Enter the Pressure and Efficiency in the 'Fan' in Designbuilder. Look at the 'Equipment Summary' and Fan table output to check that the kW matches for the selected fans.
Enter the Head (ft of H2O) and Efficiency in the 'Pump' in Designbuilder. Look at the 'Equipment Summary' and Pump table output to check that the kW matches for the selected pumps.
GPM can be found in 'Edit Plant Loop'

## Neighborhood - 2022 (hidden)
|  |  | End Use Selection | [6 empty] | 262 Homes - Existing | [7 empty] | 262 Homes - Geo | [7 empty] | Community Center - Existing | [7 empty] | Community Center - Geo | [6 empty] | Bryant Elementary - Existing | [7 empty] | Bryant Elementary - Geo | [7 empty] | County Health - Existing | [6 empty] | County Health - Geo | [6 empty] | Wheeler Center - Geo
|  |  | Lighting | Heating | Cooling | Pump | Fan | Recep | DHW |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal] |  | Electricity [kBtu] | Natural Gas [kBtu] | Additional Fuel [kBtu] | District Cooling [kBtu] | District Heating [kBtu] | Water [gal]
|  |  |  | x | [5 empty] | Heating | 0 | 342634.12 | [5 empty] | Heating | 0 | 1071438.26 | [5 empty] | Heating | 76.22 | 1602396.36 | [5 empty] | Heating | 29.54 | 1422313.73 |  |  |  |  | Heating | 0 | 3006009.4 | [5 empty] | Heating | 0 | 1986034.87
[5 empty] | x |  |  |  |  | Cooling | 48024.42 | 0 | [5 empty] | Cooling | 148851.68 | 0 | [5 empty] | Cooling | 276345.86 | 0 | [5 empty] | Cooling | 103768.01 | 0 |  |  |  |  | Cooling | 0 | 0 | [5 empty] | Cooling | 317909.03 | 0
|  |  | x | [6 empty] | Interior Lighting | 37174 | 0 | [5 empty] | Interior Lighting | 233706.24 | 0 | [5 empty] | Interior Lighting | 240811.81 | 0 | [5 empty] | Interior Lighting | 251312.67 | 0 |  |  |  |  | Interior Lighting | 398206.7 | 0 | [5 empty] | Interior Lighting | 485362.19 | 0
|  |  | x | [6 empty] | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0 |  |  |  |  | Exterior Lighting | 0 | 0 | [5 empty] | Exterior Lighting | 0 | 0
[8 empty] | x |  | Interior Equipment | 40791.83 | 0 | [5 empty] | Interior Equipment | 318687.37 | 0 | [5 empty] | Interior Equipment | 466123.76 | 0 | [5 empty] | Interior Equipment | 486449.59 | 0 |  |  |  |  | Interior Equipment | 770782.8 | 0 | [5 empty] | Interior Equipment | 328427.45 | 0
[8 empty] | x |  | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0 |  |  |  |  | Exterior Equipment | 0 | 0 | [5 empty] | Exterior Equipment | 0 | 0
[7 empty] | x |  |  | Fans | 37858.53 | 0 | [5 empty] | Fans | 95328.42 | 0 | [5 empty] | Fans | 364514.09 | 0 | [5 empty] | Fans | 822812.68 | 0 |  |  |  |  | Fans | 1149814.34 | 0 | [5 empty] | Fans | 197576.56 | 0
[6 empty] | x |  |  |  | Pumps | 1.56 | 0 | [5 empty] | Pumps | 23.25 | 0 | [5 empty] | Pumps | 329.07 | 0 | [5 empty] | Pumps | 216.68 | 0 |  |  |  |  | Pumps | 40.47 | 0 | [5 empty] | Pumps | 30.71 | 0
[5 empty] | x |  |  |  |  | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0 |  |  |  |  | Heat Rejection | 0 | 0 | [5 empty] | Heat Rejection | 0 | 0
|  |  |  | x | [5 empty] | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0 |  |  |  |  | Humidification | 0 | 0 | [5 empty] | Humidification | 0 | 0
|  |  |  | x | [5 empty] | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0 |  |  |  |  | Heat Recovery | 0 | 0 | [5 empty] | Heat Recovery | 0 | 0
[9 empty] | x | Water Systems | 0 | 12940.41 | [5 empty] | Water Systems | 0 | 162460.98 | [5 empty] | Water Systems | 0 | 204015.37 | [5 empty] | Water Systems | 0 | 213204.18 |  |  |  |  | Water Systems | 0 | 335684.29 | [5 empty] | Water Systems | 0 | 215899.95
[5 empty] | x |  |  |  |  | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0 |  |  |  |  | Refrigeration | 0 | 0 | [5 empty] | Refrigeration | 0 | 0
[10 empty] | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0 |  |  |  |  | Generators | 0 | 0 | [5 empty] | Generators | 0 | 0
therm
[10 empty] | Total End Uses | 163850.33 | 355574.54 | [5 empty] | Total End Uses | 796596.96 | 1233899.24 |  |  |  |  | kbtu | Total End Uses | 1348200.82 | 1806411.73 | [5 empty] | Total End Uses | 1664589.18 | 1635517.91 |  |  |  |  | Total End Uses | 2318844.31 | 3341693.69 | [5 empty] | Total End Uses | 1329305.93 | 2201934.82
CF
Index | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| 262 Homes - Existing | 262 Homes - Geo | Community Center - Existing | Community Center - Geo | Bryant Elementary - Existing | Bryant Elementary - Geo | County Health - Existing | County Health - Geo | Wheeler Center - Geo |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | Target |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | 2011 Target |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI | Target |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI |  | Electric | Gas | Add Fuel | District Clg | District Htg | EUI
Lighting | 8.3462 | 7.4719 | 5.8988 | 5.8988 | 5.8988 | 8.6402 | 0 | #REF! | #REF! | Lighting | 37174 | 0 | 0 | 0 | 0 | 8.3462 |  | Lighting | 233706.24 | 0 | 0 | 0 | 0 | 7.4719 | 26% | Lighting | 240811.81 | 0 | 0 | 0 | 0 | 5.8988 |  | Lighting | 251312.67 | 0 | 0 | 0 | 0 | 5.8988 | Lighting | 398206.7 | 0 | 0 | 0 | 0 | 5.8988 |  | Lighting | 485362.19 | 0 | 0 | 0 | 0 | 8.6402 |  | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | #REF! | Lighting | 0 | 0 | 0 | 0 | 0 | #REF!
Heating | 76.9273 | 34.2553 | 39.2532 | 33.3851 | 44.5295 | 35.3544 | 0 | #REF! | #REF! | Heating | 0 | 342634.12 | 0 | 0 | 0 | 76.9273 | 68 | Heating | 0 | 1071438.26 | 0 | 0 | 0 | 34.2553 | 25% | Heating | 76.22 | 1602396.36 | 0 | 0 | 0 | 39.2532 | 40 | Heating | 29.54 | 1422313.73 | 0 | 0 | 0 | 33.3851 | Heating | 0 | 3006009.4 | 0 | 0 | 0 | 44.5295 | 52 | Heating | 0 | 1986034.87 | 0 | 0 | 0 | 35.3544 | 35 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | #REF! | Heating | 0 | 0 | 0 | 0 | 0 | #REF!
Cooling | 10.7823 | 4.759 | 6.7692 | 2.4356 | 0 | 5.6593 | 0 | #REF! | #REF! | Cooling | 48024.42 | 0 | 0 | 0 | 0 | 10.7823 | 36 | Cooling | 148851.68 | 0 | 0 | 0 | 0 | 4.759 | 8% | Cooling | 276345.86 | 0 | 0 | 0 | 0 | 6.7692 | 30 | Cooling | 103768.01 | 0 | 0 | 0 | 0 | 2.4356 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 |  | Cooling | 317909.03 | 0 | 0 | 0 | 0 | 5.6593 | 25 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | #REF! | Cooling | 0 | 0 | 0 | 0 | 0 | #REF!
Pumps | 0.00035025 | 0.00074333 | 0.0080607 | 0.0050859 | 0.0005995 | 0.00054668 | 0 | #REF! | #REF! | Pumps | 1.56 | 0 | 0 | 0 | 0 | 0.00035025 |  | Pumps | 23.25 | 0 | 0 | 0 | 0 | 0.00074333 | 0% | Pumps | 329.07 | 0 | 0 | 0 | 0 | 0.0080607 |  | Pumps | 216.68 | 0 | 0 | 0 | 0 | 0.0050859 | Pumps | 40.47 | 0 | 0 | 0 | 0 | 0.0005995 |  | Pumps | 30.71 | 0 | 0 | 0 | 0 | 0.00054668 |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | #REF! | Pumps | 0 | 0 | 0 | 0 | 0 | #REF!
Fans | 8.4999 | 3.0478 | 8.9289 | 19.313 | 17.0328 | 3.5172 | 0 | #REF! | #REF! | Fans | 37858.53 | 0 | 0 | 0 | 0 | 8.4999 |  | Fans | 95328.42 | 0 | 0 | 0 | 0 | 3.0478 | 2% | Fans | 364514.09 | 0 | 0 | 0 | 0 | 8.9289 |  | Fans | 822812.68 | 0 | 0 | 0 | 0 | 19.313 | Fans | 1149814.34 | 0 | 0 | 0 | 0 | 17.0328 |  | Fans | 197576.56 | 0 | 0 | 0 | 0 | 3.5172 |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | #REF! | Fans | 0 | 0 | 0 | 0 | 0 | #REF!
Receptacles | 9.1585 | 10.1889 | 11.4179 | 11.4179 | 11.418 | 5.8465 | 0 | #REF! | #REF! | Receptacles | 40791.83 | 0 | 0 | 0 | 0 | 9.1585 |  | Receptacles | 318687.37 | 0 | 0 | 0 | 0 | 10.1889 | 36% | Receptacles | 466123.76 | 0 | 0 | 0 | 0 | 11.4179 |  | Receptacles | 486449.59 | 0 | 0 | 0 | 0 | 11.4179 | Receptacles | 770782.8 | 0 | 0 | 0 | 0 | 11.418 |  | Receptacles | 328427.45 | 0 | 0 | 0 | 0 | 5.8465 |  | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | #REF! | Receptacles | 0 | 0 | 0 | 0 | 0 | #REF!
DHW | 2.9053 | 5.1941 | 4.9974 | 5.0043 | 4.9727 | 3.8433 | 0 | #REF! | #REF! | DHW | 0 | 12940.41 | 0 | 0 | 0 | 2.9053 |  | DHW | 0 | 162460.98 | 0 | 0 | 0 | 5.1941 | 3% | DHW | 0 | 204015.37 | 0 | 0 | 0 | 4.9974 |  | DHW | 0 | 213204.18 | 0 | 0 | 0 | 5.0043 | DHW | 0 | 335684.29 | 0 | 0 | 0 | 4.9727 |  | DHW | 0 | 215899.95 | 0 | 0 | 0 | 3.8433 |  | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | #REF! | DHW | 0 | 0 | 0 | 0 | 0 | #REF!
EUI | 116.6199 | 64.9177 | 77.2735 | 77.4597 | 83.8524 | 62.8614 | 0 | #REF! | #REF! | kBtu | 163850.34 | 355574.53 | 0 | 0 | 0 | 116.6199 | 104 | kBtu | 796596.96 | 1233899.24 | 0 | 0 | 0 | 64.9177 | 100% | kBtu | 1348200.81 | 1806411.73 | 0 | 0 | 0 | 77.2735 |  | kBtu | 1664589.17 | 1635517.91 | 0 | 0 | 0 | 77.4597 | kBtu | 2318844.31 | 3341693.69 | 0 | 0 | 0 | 83.8524 |  | kBtu | 1329305.94 | 2201934.82 | 0 | 0 | 0 | 62.8614 | 60 | kBtu | 0 | 0 | 0 | 0 | 0 | 0 | kBtu | 0 | 0 | 0 | 0 | 0 | #REF! | kBtu | 0 | 0 | 0 | 0 | 0 | #REF!
| Savings: | 51.7022 | 39.3463 | 39.1601 | 32.7675 | 53.7584 | 116.6199 | #REF! | #REF! |  |  | Gas EUI |  |  |  | 79.8326 |  |  |  | Gas EUI |  |  |  | 39.4494 | 35 |  |  | Gas EUI |  |  |  | 44.2507 |  |  |  | Gas EUI |  |  |  | 38.3894 |  |  | Gas EUI |  |  |  | 49.5022 |  |  |  | Gas EUI |  |  |  | 39.1978
|  | 44.33% | 33.74% | 33.58% | 28.1% | 46.1% | 100% | #REF! | #REF! |  |  | Elec EUI |  |  |  | 36.7872 |  |  |  | Elec EUI |  |  |  | 25.4683 | 27 |  |  | Elec EUI |  |  |  | 33.0229 |  |  |  | Elec EUI |  |  |  | 39.0704 |  |  | Elec EUI |  |  |  | 34.3502 |  |  |  | Elec EUI |  |  |  | 23.6637
Lighting | 2137.9132 | 13440.6751 | 13849.3234 | 14453.2382 | 22901.2579 | 27913.6557 | 0 | 0 | 0 | Lighting | 2137.9132 | 0 | 0 | 0 | 0 | 2137.9132 |  | Lighting | 13440.6751 | 0 | 0 | 0 | 0 | 13440.6751 |  | Lighting | 13849.3234 | 0 | 0 | 0 | 0 | 13849.3234 |  | Lighting | 14453.2382 | 0 | 0 | 0 | 0 | 14453.2382 | Lighting | 22901.2579 | 0 | 0 | 0 | 0 | 22901.2579 |  | Lighting | 27913.6557 | 0 | 0 | 0 | 0 | 27913.6557 |  | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0 | Lighting | 0 | 0 | 0 | 0 | 0 | 0
Heating | 2706.7435 | 8464.1558 | 12663.006 | 11237.7033 | 23746.8951 | 15689.2928 | 0 | 0 | 0 | Heating | 0 | 2706.7435 | 0 | 0 | 0 | 2706.7435 |  | Heating | 0 | 8464.1558 | 0 | 0 | 0 | 8464.1558 |  | Heating | 4.3835 | 12658.6225 | 0 | 0 | 0 | 12663.006 |  | Heating | 1.6989 | 11236.0044 | 0 | 0 | 0 | 11237.7033 | Heating | 0 | 23746.8951 | 0 | 0 | 0 | 23746.8951 |  | Heating | 0 | 15689.2928 | 0 | 0 | 0 | 15689.2928 |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0 | Heating | 0 | 0 | 0 | 0 | 0 | 0
Cooling | 2761.9315 | 8560.6061 | 15892.9215 | 5967.8 | 0 | 18283.2602 | 0 | 0 | 0 | Cooling | 2761.9315 | 0 | 0 | 0 | 0 | 2761.9315 |  | Cooling | 8560.6061 | 0 | 0 | 0 | 0 | 8560.6061 |  | Cooling | 15892.9215 | 0 | 0 | 0 | 0 | 15892.9215 |  | Cooling | 5967.8 | 0 | 0 | 0 | 0 | 5967.8 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 |  | Cooling | 18283.2602 | 0 | 0 | 0 | 0 | 18283.2602 |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | Cooling | 0 | 0 | 0 | 0 | 0 | 0
Pumps | 0.089717 | 1.3371 | 18.9251 | 12.4615 | 2.3275 | 1.7662 | 0 | 0 | 0 | Pumps | 0.089717 | 0 | 0 | 0 | 0 | 0.089717 |  | Pumps | 1.3371 | 0 | 0 | 0 | 0 | 1.3371 |  | Pumps | 18.9251 | 0 | 0 | 0 | 0 | 18.9251 |  | Pumps | 12.4615 | 0 | 0 | 0 | 0 | 12.4615 | Pumps | 2.3275 | 0 | 0 | 0 | 0 | 2.3275 |  | Pumps | 1.7662 | 0 | 0 | 0 | 0 | 1.7662 |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | Pumps | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2177.2812 | 5482.4309 | 20963.5629 | 47320.7644 | 66126.9506 | 11362.8218 | 0 | 0 | 0 | Fans | 2177.2812 | 0 | 0 | 0 | 0 | 2177.2812 |  | Fans | 5482.4309 | 0 | 0 | 0 | 0 | 5482.4309 |  | Fans | 20963.5629 | 0 | 0 | 0 | 0 | 20963.5629 |  | Fans | 47320.7644 | 0 | 0 | 0 | 0 | 47320.7644 | Fans | 66126.9506 | 0 | 0 | 0 | 0 | 66126.9506 |  | Fans | 11362.8218 | 0 | 0 | 0 | 0 | 11362.8218 |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0 | Fans | 0 | 0 | 0 | 0 | 0 | 0
Receptacles | 2345.9782 | 18328.0233 | 26807.2347 | 27976.1931 | 44328.4749 | 18888.1848 | 0 | 0 | 0 | Receptacles | 2345.9782 | 0 | 0 | 0 | 0 | 2345.9782 |  | Receptacles | 18328.0233 | 0 | 0 | 0 | 0 | 18328.0233 |  | Receptacles | 26807.2347 | 0 | 0 | 0 | 0 | 26807.2347 |  | Receptacles | 27976.1931 | 0 | 0 | 0 | 0 | 27976.1931 | Receptacles | 44328.4749 | 0 | 0 | 0 | 0 | 44328.4749 |  | Receptacles | 18888.1848 | 0 | 0 | 0 | 0 | 18888.1848 |  | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0 | Receptacles | 0 | 0 | 0 | 0 | 0 | 0
DHW | 102.2267 | 1283.4104 | 1611.6821 | 1684.2719 | 2651.8412 | 1705.568 | 0 | 0 | 0 | DHW | 0 | 102.2267 | 0 | 0 | 0 | 102.2267 |  | DHW | 0 | 1283.4104 | 0 | 0 | 0 | 1283.4104 |  | DHW | 0 | 1611.6821 | 0 | 0 | 0 | 1611.6821 |  | DHW | 0 | 1684.2719 | 0 | 0 | 0 | 1684.2719 | DHW | 0 | 2651.8412 | 0 | 0 | 0 | 2651.8412 |  | DHW | 0 | 1705.568 | 0 | 0 | 0 | 1705.568 |  | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0 | DHW | 0 | 0 | 0 | 0 | 0 | 0
Cost | 12232.1641 | 55560.6389 | 91806.6557 | 108652.4324 | 159757.7473 | 93844.5494 | 0 | 0 | 0 | Cost | 9423.1938 | 2808.9703 | 0 | 0 | 0 | 12232.1641 |  | Cost | 45813.0726 | 9747.5663 | 0 | 0 | 0 | 55560.6389 |  | Cost | 77536.3511 | 14270.3046 | 0 | 0 | 0 | 91806.6557 |  | Cost | 95732.1561 | 12920.2764 | 0 | 0 | 0 | 108652.4324 | Cost | 133359.011 | 26398.7363 | 0 | 0 | 0 | 159757.7473 |  | Cost | 76449.6886 | 17394.8608 | 0 | 0 | 0 | 93844.5494 |  | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0 | Cost | 0 | 0 | 0 | 0 | 0 | 0
| Savings: | -43328.4748 | -79574.4917 | -96420.2684 | -147525.5832 | -81612.3854 | 12232.1641 | 12232.1641 | 12232.1641
|  | -354.2% | -650.5% | -788.3% | -1206% | -667.2% | 100% | 100% | 100%
Carbon | 50.158 | 217.6301 | 353.3873 | 404.7932 | 620.2518 | 370.7391 | 0 | 0 | 0 | Carbon | 31.3126 | 18.8455 | 0 | 0 | 0 | 50.158 |  | Carbon | 152.2334 | 65.3967 | 0 | 0 | 0 | 217.6301 |  | Carbon | 257.6475 | 95.7398 | 0 | 0 | 0 | 353.3873 |  | Carbon | 318.1108 | 86.6824 | 0 | 0 | 0 | 404.7932 | Carbon | 443.142 | 177.1098 | 0 | 0 | 0 | 620.2518 |  | Carbon | 254.0366 | 116.7025 | 0 | 0 | 0 | 370.7391 |  | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0 | Carbon | 0 | 0 | 0 | 0 | 0 | 0
| Savings: | -167.4721 | -303.2293 | -354.6352 | -570.0938 | -320.5811 | 50.158 | 50.158 | 50.158
|  | -333.9% | -604.5% | -707% | -1137% | -639.1% | 100% | 100% | 100%
Peak Heating | [9 empty] | Peak Heating | [7 empty] | Peak Heating | [7 empty] | Peak Heating | [7 empty] | Peak Heating | [6 empty] | Peak Heating | [7 empty] | Peak Heating
Peak Cooling | [9 empty] | Peak Cooling | [7 empty] | Peak Cooling | [7 empty] | Peak Cooling | [7 empty] | Peak Cooling | [6 empty] | Peak Cooling | [7 empty] | Peak Cooling

## DB-End Use (hidden)
EUI End Use Breakdown
Energy Category | Worst - Existing | Mid - Existing | Best - Existing | DOE Benchmark - Homes | Worst - Wx | Mid - Wx | Best - Wx | Worst - Geo | Mid - Geo
Lighting | 2.8662 | 2.8662 | 2.8662 | 2.8819 | 2.8662 | 2.8662 | 2.8662 | 2.8662 | 2.8662
Heating | 88.1152 | 68.9236 | 52.9374 | 59.534 | 69.6064 | 60.8813 | 52.9374 | 18.7008 | 14.1434
Cooling | 9.9074 | 6.325 | 5.0144 | 1.9428 | 9.0507 | 6.1511 | 5.0144 | 4.5396 | 2.795
Pumps | 0.0011223 | 0.00093125 | 0.0008238 | 0 | 0.0011223 | 0.00093125 | 0.0008238 | 0.34387 | 0.26457
Fans | 8.9136 | 6.9758 | 4.9634 | 2.5472 | 7.197 | 6.2175 | 4.9634 | 2.9604 | 2.5669
Receptacles | 10.8789 | 9.6702 | 8.4614 | 14.7569 | 10.8789 | 9.6702 | 8.4614 | 10.8789 | 9.6702
DHW | 9.4609 | 7.8837 | 6.9372 | 8.6547 | 9.46 | 7.8833 | 6.9372 | 9.4639 | 7.8839
Savings | - | 27.498 | 48.9625 | 39.8258 | 21.083 | 36.4728 | 48.9625 | 80.3897 | 89.9531 | 130.1433 | 130.1433 | 130.1433
Total: | 130.1433 | 102.6453 | 81.1807 | 90.3175 | 109.0603 | 93.6705 | 81.1807 | 49.7536 | 40.1902 | 0 | 0 | 0
Energy Savings: | - | 21.13% | 37.62% | 30.6% | 16.2% | 28.03% | 37.62% | 61.77% | 69.12% | 100% | 100% | 100%
|  | Energy Savings: 21% | Energy Savings: 38% | Energy Savings: 31% | Energy Savings: 16% | Energy Savings: 28% | Energy Savings: 38% | Energy Savings: 62% | Energy Savings: 69% | Energy Savings: 100% | Energy Savings: 100% | Energy Savings: 100%
Energy Cost Breakdown
Lighting | 138.0626 | 138.0626 | 138.0626 | 0 | 138.0626 | 138.0626 | 138.0626 | 138.0626 | 138.0626
Heating | 583.0336 | 456.048 | 350.2719 | 0 | 460.566 | 402.8347 | 350.2719 | 900.8169 | 681.2872
Cooling | 477.2376 | 304.6736 | 241.5432 | 0 | 435.9746 | 296.2989 | 241.5432 | 218.6711 | 134.6372
Pumps | 0.05406 | 0.044859 | 0.039683 | 0 | 0.05406 | 0.044859 | 0.039683 | 16.5643 | 12.7444
Fans | 429.3701 | 336.0257 | 239.0864 | 0 | 346.6779 | 299.4965 | 239.0864 | 142.6031 | 123.6498
Receptacles | 423.5817 | 365.3552 | 307.1288 | 0 | 423.5817 | 365.3552 | 307.1288 | 423.5817 | 365.3552
DHW | 62.6003 | 52.164 | 45.9017 | 0 | 62.5941 | 52.1618 | 45.9017 | 62.6199 | 52.1658
Savings | - | 461.5659 | 791.9056 | 2113.9399 | 246.4289 | 559.6853 | 791.9056 | 211.0203 | 606.0376 | 2113.9399 | 2113.9399 | 2113.9399
Total: | 2113.9399 | 1652.374 | 1322.0343 | 0 | 1867.511 | 1554.2546 | 1322.0343 | 1902.9196 | 1507.9022 | 0 | 0 | 0
Cost Savings: | - | 21.83% | 37.46% | 100% | 11.66% | 26.48% | 37.46% | 9.982% | 28.67% | 100% | 100% | 100%
|  | Cost Savings: 22% | Cost Savings: 37% | Cost Savings: 100% | Cost Savings: 12% | Cost Savings: 26% | Cost Savings: 37% | Cost Savings: 10% | Cost Savings: 29% | Cost Savings: 100% | Cost Savings: 100% | Cost Savings: 100%