## All Ordinances
This data was collected with the help of generative AI. The Large Language Models used for this effort make mistakes. Always validate the data for critical use cases.
State | County | Subdivision | Jurisdiction Type | County Subdivision FIPS Code | Feature | Value | Units | Summary | Section | Ordinance Year | Source URL
Massachusetts |  |  |  | 25000 | Definition: Geothermal Heat Pump |  |  | Closed-Loop GSHP System - A GSHO system that utilizes closed-loop well Closed-loop well - A GSHP well that uses a closed-loop fluid system to prevent the discharge or escape of its fluid into the subsurface. Closed-loop heat pump wells shall not be used to produce. Direct exchange (DX) well - A GSHP well that circulates a refrigerant through a closed-loop fluid/vapor system to prevent the discharge or escape of its fluid into the subsurface. DX wells shall not be used to produce water. Direct exchange GSHP systems are also commonly referred to as direct expansion systems. |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts |  |  |  | 25000 | Setback - Property Lines | 10 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts |  |  |  | 25000 | Setback - Private Water | 10 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts |  |  |  | 25000 | Setback - Sewer Lines | 10 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts |  |  |  | 25000 | Setback - Hazardous Materials/Fertilizers | 25 | feet | existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks. |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts |  |  |  | 25000 | Maximum Well Depth | 20 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts |  |  |  | 25000 | Licensed Driller |  |  | Must be Mass DEP certified well driller |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Michigan |  |  |  | 26000 | Definition: Geothermal Heat Pump |  |  | Geothermal Heat Pump System - a mechanical device, also known as a ground source heat pump or geoexchange system, which uses the geothermal exchange properties and the relatively constant temperature of earth formations for heating or cooling a building space. A GHPS consists of three parts: 1) heat pump unit, 2) heat exchanger, and 3) heating/cooling distribution system (e.g., duct work). |  | 2013 | https://www.michigan.gov/-/media/Project/Websites/egle/Documents/Programs/DWEHD/Water-Well-Construction/Geothermal-Heat-Pump-Systems.pdf?rev=9af2da6143b84b5a9ca8278362dd67cb
Missouri |  |  |  | 29000 | Setback - Animal Enclosures | 100 | feet |  |  | 2024 | https://www.sos.mo.gov/cmsimages/adrules/csr/current/10csr/10c23-5.pdf
Missouri |  |  |  | 29000 | Setback - Hazardous Materials/Fertilizers | 300 | feet |  |  | 2024 | https://www.sos.mo.gov/cmsimages/adrules/csr/current/10csr/10c23-5.pdf
Missouri |  |  |  | 29000 | Maximum Well Depth | 500 | feet |  |  | 2024 | https://www.sos.mo.gov/cmsimages/adrules/csr/current/10csr/10c23-5.pdf
Montana |  |  |  | 30000 | Definition: Geothermal Heat Pump |  |  | Closed-Loop System – Horizontal Horizontal ground source heat pump installation is generally most cost-effective for residential installations, particularly for new construction where sufficient land is available. It requires trenches at least four feet deep. The most common layouts either use two pipes, one buried at six feet, and the other at four feet, or two pipes placed side-by-side at five feet in the ground in a two-foot wide trench. The method of looping pipe allows more pipe in a shorter trench, which cuts down on installation costs and makes horizontal installation possible in areas it would not be with conventional horizontal applications. Closed-Loop System – Vertical Vertical systems are often used for large commercial buildings and schools because the land area required for horizontal loops would be prohibitive. Vertical loops are also used where the soil is too shallow for trenching, and they minimize the disturbance to existing landscaping. For a vertical system, holes approximately four inches in diameter are drilled about 20 feet apart and 100 to 400 feet deep. Into these holes go two pipes that are connected at the bottom with a U-bend to form a loop. The vertical loops are connected with horizontal pipe, placed in trenches, and connected to the heat pump in the building. Closed-Loop System – Pond/Lake If your site has an adequate water body, this may be the lowest cost option. A supply line pipe is run underground from the building to the water and coiled into circles at least eight feet under the surface to prevent freezing. The coils should only be placed in a water source that meets minimum volume, depth, and quality criteria. Open-Loop System An open-loop system uses a well or surface water body such as a pond or lake as the heat exchange fluid that circulates directly through the ground source heat pump system. Once the water has circulated through the system, it returns to the ground through the well, a recharge well, or surface discharge. This option is only practical where there is an adequate supply of relatively clean water, and all regulations regarding ground water discharge are met. |  |  | https://deq.mt.gov/files/Energy/EnergizeMT/Renewables/Geothermal%20Pub/5%20HeatPumps.pdf
New Hampshire |  |  |  | 33000 | Setback - Public Water | 50 | feet | Fifty feet from a well used for potable water supply |  | 2017 | https://www.law.cornell.edu/regulations/new-hampshire/N-H-Admin-Code-SS-We-602.37
New Hampshire |  |  |  | 33000 | Setback - Hazardous Materials/Fertilizers | 25 | feet | Twenty five feet from a septic tank or effluent disposal area |  | 2017 | https://www.law.cornell.edu/regulations/new-hampshire/N-H-Admin-Code-SS-We-602.37
North Carolina |  |  |  | 37000 | Definition: Geothermal Heat Pump |  |  | Geothermal Direct Expansion Closed-Loop Wells" means wells used to house a subsurface system of closed-loop pipe that circulates refrigerant gas for heating and cooling purposes. |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Building Foundation | 15 | feet |  |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Wastewater | 50 | feet | Septic systems, including drainfield, waste application area, and repair area |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Fuel (above ground) | 50 | feet | Above ground or underground storage tanks that contain petroleum fuels used for heating equipment, boilers, or furnaces, except for tanks used solely for storage of propane, natural gas, or liquefied petroleum gas |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Fuel (below ground) | 50 | feet | Chemical or petroleum fuel underground storage tank systems regulated under 15A NCAC 02N with secondary containment |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Fuel (below ground) | 100 | feet | Chemical or petroleum fuel underground storage tank systems regulated under 15A NCAC 02N without secondary containment |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Subsurface Drains | 50 | feet | Land-based or subsurface waste storage or disposal systems |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Sewer Lines | 15 | feet | Water-tight sewer lateral lines from a residence or other non-public system to a sewer main or other wastewater disposal system |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina |  |  |  | 37000 | Setback - Sewer Lines | 25 | feet | Other industrial or municipal sewage or liquid waste collection or transmission sewer mains |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
Oklahoma |  |  |  | 40000 | Setback - Public Water | 10 | feet | A vertical heat exchange well shall be located on a site so that surface water will not pool or pond around or within ten (10) feet of the heat exchange well location |  | 2008 | https://regulations.justia.com/states/oklahoma/title-785/chapter-35/subchapter-7/section-785-35-7-1-1/
Tennessee |  |  |  | 47000 | Definition: Well |  |  | "Geothermal well" means a hole drilled into the earth, by boring or otherwise, greater than twenty feet in depth constructed for the primary purpose of adding or removing British Thermal Units (BTU) from the earth for heating or cooling. This is also referred to as a closed loop geothermal borehole. |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.17
Tennessee |  |  |  | 47000 | Setback - Wastewater | 10 | feet | house to septic tank connection |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee |  |  |  | 47000 | Setback - Wastewater | 100 | feet |  |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee |  |  |  | 47000 | Setback - Private Water | 100 | feet |  |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee |  |  |  | 47000 | Setback - Sewer Lines | 10 | feet | house to sewer line connection |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee |  |  |  | 47000 | Setback - Sewer Lines | 25 | feet | septic tank |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee |  |  |  | 47000 | Setback - Sewer Lines | 10 | feet | Applies only to locations of Closed Loop Geothermal Boreholes |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Texas |  |  |  | 48000 | Licensed Driller |  |  | Closed-loop geothermal wells must be drilled and completed by a water well driller licensed in Texas. |  | 2023 | https://www.rrc.texas.gov/oil-and-gas/applications-and-permits/injection-storage-permits/geothermal/
Utah |  |  |  | 49000 | Licensed Driller |  |  | Must be drilled by a licensed driller and the owner or applicant must have an approved application for that specific purpose |  | 2022 | https://www.law.cornell.edu/regulations/utah/Utah-Admin-Code-R655-4-12
Delaware | Sussex | Laurel-Delmar | City | 1000591628 | Permit |  |  | "Private wells are permitted for geothermal heating and cooling and must be approved by DNREC and Town of Laurel prior to installation." | §170-35.B. Wells | 2009 | https://delawaresourcewater.org/wp-content/uploads/2013/05/Laurel_ord2009_14.pdf
Delaware | Sussex | Laurel-Delmar | City | 1000591628 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal wells shall be permitted in the Town of Laurel..." | §170-35.B. Wells | 2009 | https://delawaresourcewater.org/wp-content/uploads/2013/05/Laurel_ord2009_14.pdf
Delaware |  | Blades | Town | 1006730 | Open-loop Prohibitions |  |  | "Only vertical loop closed systems will be allowed in the Town of Blades. No horizontal, pond, or open loop systems permitted." | Section 33. GEOTHERMAL HEATING SYSTEMS | 2007 | https://blades.delaware.gov/files/2014/07/411-Water-Service-within-the-Town-of-Blades-Effective-10.08.2012.pdf
Delaware |  | Blades | Town | 1006730 | Other Prohibitions/Regulations |  |  | "Only vertical loop closed systems will be allowed in the Town of Blades. No horizontal, pond, or open loop systems permitted." | Section 33. GEOTHERMAL HEATING SYSTEMS | 2007 | https://blades.delaware.gov/files/2014/07/411-Water-Service-within-the-Town-of-Blades-Effective-10.08.2012.pdf
Delaware | Sussex | Millsboro | Town | 1047940 | Other Prohibitions/Regulations |  |  | "Geothermal heating/cooling systems shall not be connected to the Town's public water system. Such system shall be served solely by private wells subject to federal, state, county, and Town regulations." | § 206-1 Connection required. | 2024 | https://ecode360.com/8027891
District Of Columbia | District of Columbia |  | County | 11001 | Definition: Geothermal |  |  | "geothermal energy: heat extracted from the Earth's interior and used to produce electricity or mechanical power or provide thermal energy for heating buildings or processes. Geothermal energy does not include systems such as heat pumps that use energy independent of the geothermal source to raise the temperature of the extracted heat." | 3.2 Definitions | 2020 | https://dob.dc.gov/sites/default/files/dc/sites/dob/publication/attachments/2017%20DC%20Energy%20Code.pdf
Florida | Alachua |  | County | 12001 | Definition: Geothermal |  |  | "Renewable Energy (see also Alternative Energy): Systems that generate energy from non-fossil fuel resources that are locally harvested, collected or concentrated in such a way as to not deplete nor imperil the resource base from which they are derived... (e.g. solar photovoltaic panels or solar thermal systems, geothermal energy for heating or cooling of structures, biomass, biodiesel, cellulosic ethanol, wind turbines, methane production via anaerobic digestion from organic materials and discarded foodstuffs)" | ATTACHMENT 'B' - ENERGY ELEMENT DEFINITIONS | 2011 | https://growth-management.alachuacounty.us/formsdocs/Ordinance_11_01.pdf
Florida | Lee |  | County | 12071 | Definition: Well |  |  | "GEOTHERMAL WELLS -means a combination of a supply well and an injection well installed to utilize the natural thermal characteristics of groundwater for heating and cooling. Groundwater withdrawn by geothermal wells does not typically result in changes in water quality or consumptive use (i.e., the same quality and quantity of water withdrawn from the supply well is returned to the same aquifer through the injection well)." | SECTION FIVE: DEFINITIONS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee |  | County | 12071 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL CLOSED LOOP SYSTEMS -means a system that uses water and an antifreeze solution circulated through a closed-loop system of pipes buried in the earth commonly referred to as a loop field. The solution acts as a medium for heat transfer. These loops are heat fused at the joints and pressurized. (The loop field is what sets these systems apart from conventional heating and cooling equipment.)" | SECTION FIVE: DEFINITIONS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee |  | County | 12071 | Permit |  |  | Section 9.1(1): "A valid permit issued by the DNR is required to drill, construct, repair, rehabilitate, plug, enlarge or deepen any well..." Appendix A specifically lists permit application requirements for "Geo-Thermal Supply and Injection Well (single family, replacement)" and "Geo-Thermal Supply and Injection Well (commercial, farm, replacement)," including "A properly completed State of Florida Water Well Application," site plan materials, and for single-family: "Copy of exemption from SFWMD; Copy of exemption from DEP"; for commercial/farm: "Florida Department of Environmental Protection ('FDEP') injection well permit; WUP Number and copy of WUP; Copy of exemption from SFWMD; Copy of exemption from DEP." | SECTION NINE: PERMITS; APPENDIX "A" SECTION I PERMITS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee |  | County | 12071 | Inspection |  |  | Section 12.2(1): "The DNR or appropriate state agency will conduct inspection of well construction, alterations, and plugging." Section 12.2(2): "It is the Contractor's responsibility to advise the DNR of the date(s) and time(s) when construction will begin, when various portions of the work will be completed..." Section 13.10: "The DNR must be notified by the Contractor at least twenty-four (24) hours prior to plugging the replacement well, so that an inspector can be present during plugging operation." | SECTION TWELVE: DRILLING INSPECTORS AND INSPECTIONS; SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee |  | County | 12071 | Licensed Driller |  |  | Section 13.1(2): "Only licensed State of Florida Water Well contractors are authorized to drill, construct, repair, rehabilitate, plug, enlarge, or deepen wells." Appendix A, "Geo-Thermal Supply and Injection Well" permit requirements: "A valid State of Florida water well contractor license." | SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES; APPENDIX "A" SECTION I PERMITS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee |  | County | 12071 | Decommissioning |  |  | Section 13.8(1): "Generally, a well may be plugged provided: It is filled from bottom to the land surface with an appropriate grouting material... and work done in accordance with the requirements of the DNR and the SFWMD." Section 13.9(1): "Prior to plugging any well, a permit must be obtained from the DNR." Section 13.10: "The Contractor shall ensure that the existing well is plugged from bottom to the land surface with approved grouting material and in accordance with the requirements of this Ordinance within 2 weeks following completion of installation of the replacement well." | SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee |  | County | 12071 | Other Prohibitions/Regulations |  |  | Section 13.12 states for "GEOTHERMAL CLOSED LOOP HOLES" that "Holes may not exceed the Water-Table Aquifer... The open hole or any installed pipe may not exceed the first confining unit below the Water Table aquifer." | SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | St. Lucie |  | County | 12111 | Permit |  |  | "Unless expressly exempt by statute or this rule, all wells must be permitted prior to construction, repair or abandonment." "Unless expressly exempted by statute or District rule, a permit must be obtained from the District or delegated agency prior to the construction, repair or abandonment of any water well within the District's jurisdiction." Also, "a permit shall be required before beginning construction or repair of any water well within such area." | 40E-3.040 Scope of Part I; 40E-3.041 Permits Required; 62-532.400 Permit for Water Well Construction or Repair | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie |  | County | 12111 | Inspection |  |  | The agreement states the HEALTH DEPARTMENT "shall review, evaluate and make final inspections and disposition of permit applications for the construction, repair and abandonment of all water wells." Rule 40E-3.461 adds: "The District or delegated agency is authorized to inspect any well or abandoned well within its jurisdiction... Inspections shall be done as necessary to insure conformity with applicable standards." Rule 62-532.510 similarly provides inspections "as is necessary to ensure conformity with applicable standards." | III. SCOPE OF DELEGATION; 40E-3.461 Inspection; 62-532.510 Water Well Inspections | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie |  | County | 12111 | Licensed Driller |  |  | "Unless expressly exempt by statute or this rule, all wells must be permitted prior to construction, repair or abandonment and must be constructed, repaired or abandoned by a licensed water well contractor." "The work shall be performed by a licensed water well contractor." Also, "It is unlawful for any person to... Construct, repair, or abandon a water well, or operate drilling equipment for such purpose, unless employed by or under the supervision of a licensed water well contractor." | 40E-3.040 Scope of Part I; 40E-3.531 Abandoned Well Plugging; 62-531.450 Unlawful Acts, Grounds for Disciplinary Actions, and Penalties | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie |  | County | 12111 | Certification |  |  | "Water Well Contractor means an individual who is responsible for the location, construction, repair, or abandonment of a water well and who is licensed under Chapter 62-531, F.A.C., to engage in the business of construction, repair, or abandonment of water wells." Rule 40E-3.036 incorporates "Chapter 62-531, F.A.C., Well Contractor Licensing Requirements." | 40E-3.021(30) Definitions; 40E-3.036 Rules and Publications Incorporated by Reference; 62-531.200(11) Definitions Used in Water Well Contractor Rules | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie |  | County | 12111 | Decommissioning |  |  | "All abandoned wells shall be plugged by filling them from bottom to top with grout within a time specified by the District. The work shall be performed by a licensed water well contractor." "The owner of the property... shall be responsible for ensuring that all abandoned wells on the property are properly plugged." Also, "All abandoned wells shall be filled and sealed in accordance with Rule 62-532.500(4), F.A.C." and "All abandoned wells shall be plugged by filling them from bottom to top with neat cement grout or bentonite and capped with a minimum of one foot of neat cement grout." | 40E-3.531 Abandoned Well Plugging; 62-532.440 Abandonment of Water Wells; 62-532.500(4) Plugging | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | Volusia | DeBary-Orange | City | 1212790793 | Screening |  |  | "Service areas and mechanical equipment located on the ground ... shall be located in the rear or to the side of buildings and screened from public view ... Screening shall, at a minimum, be at the same height as the equipment." Also, "If mechanical equipment is located at-grade, and is visible from an adjacent street or sidewalk, it shall be inset into the building façade and screened with doors, or screened by a fence or street wall ... mechanical equipment shall include any heating, ventilation, and air conditioning (HVAC) or electrical machinery ... generators, geothermal wells, and similar elements." | Sec. 5.34. Service Areas and Mechanical Equipment | 2024 | https://debary.org/DocumentCenter/View/969/2024-Land-Development-Code
Florida |  | DeBary | City | 1216675 | Screening |  |  | Sec. 5.34(a): "Service areas and mechanical equipment ... shall be located in the rear or to the side of buildings and screened from public view ... Screening shall, at a minimum, be at the same height as the equipment." Sec. 5.34(b): if visible from a street or sidewalk, equipment "shall be inset into the building façade and screened with doors, or screened by a fence or street wall"; the definition of mechanical equipment includes "generators, geothermal wells, and similar elements." Sec. 5.34(c): "All rooftop mounted equipment and appurtenances shall be fully screened from view from all public rights-of-way." | Sec. 5.34. Service Areas and Mechanical Equipment | 2024 | https://mccmeetings.blob.core.usgovcloudapi.net/debaryfl-pubu/MEET-Packet-5f732c36ab36436db587e8dac069e437.pdf
Florida |  | Holmes Beach | City | 1232150 | Screening |  |  | "Allowable encroachments into the secondary front yard setback... Heat and pool pumps not exceeding 48 inches in height (measured from adjacent grade) and used to heat a swimming pool, provided the unit is ... screened to a height equal to or greater than the height of the heat pump by vegetation a hedge along all sides of the heat pump that do not face exterior wall of the principal structure." | Section 2; 6.8 - Supplemental development standards, Z. Permitted setback Yard encroachments, 7.8 | 2024 | https://pub-holmesbeachfl.escribemeetings.com/filestream.ashx?DocumentId=3155
Florida |  | Jacksonville | City | 1235000 | Definition: Geothermal Heat Pump |  |  | "RR. Water Cooled Heat Pumps or Water Source Heat Pump: Single or reverse cycle mechanical devices for heating or cooling which require the use of water as a medium for heat transfer." Also under "V. Heat Pump Systems": "2. Earth Coupled Closed Loop - a closed tube heat exchanger installed in the ground either vertically or horizontally and filled with International Ground Source Heat Pump Association (IGSHPA) approved fluid circulating under pressure between the loop and the heat pump." | 8.102 Definitions | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | City | 1235000 | Setback - Wastewater | 50 | feet | "Injection wells shall be no closer than 50 feet from any potential source of contamination such as a septic tank or drainfield and shall not adversely impact the operation of on-site waste treatment or drainage systems." | 8.805 Water Cooled Heat Pumps (Geothermal Heat Pump Systems) | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | City | 1235000 | Permit |  |  | "Unless expressly exempted by Florida Statutes or Chapter 40C-3, FAC, a well construction permit must be obtained from the Department prior to the construction, repair or abandonment of all wells less than six (6) inches in diameter." Rule 8.806 also states: "A well construction permit shall be required for all injection wells." | 8.503 Permit Requirements; 8.806 Injection Wells | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | City | 1235000 | Inspection |  |  | "Inspection of well construction, repair and abandonment will be conducted by the Department." Also, "Upon completion of well construction, but prior to installation of any pumping related items or other well or site changes that might limit access to the well, the property owner or authorized agent shall notify the Department and may be required to make the well available for down hole logging or other testing by the Department or its representatives, if requested." | 8.509 Inspections | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | City | 1235000 | Certification |  |  | Rule 8.805 states: "No substances shall be introduced into closed loop installations other than IGSHPA approved fluids." Rule 8.601 requires annual contractor registration by filing "a copy of the current State Water Well Contractor license and/or certification with the Department." | 8.805 Water Cooled Heat Pumps (Geothermal Heat Pump Systems); 8.601 Registration Required | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | City | 1235000 | Decommissioning |  |  | "All well abandonments regulated by the Department under this Rule shall be done in accordance with the standards and requirements of Rules 62-532.440 and 40C 3.531, FAC." Further, if violations are found, "the Department may require the well to be properly abandoned or plugged... If abandonment is required, the property owner or applicant must properly abandon the well within 30 days of notification by the Department." | 8.804 Well Abandonment Requirements; 8.507 Criteria for Permit Issuance, Denial or Revocation | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | City | 1235000 | Other Prohibitions/Regulations |  |  | "Heat Pump injection wells are prohibited on a Superfund or ash site subject to an EPA Consent Decree or on a site with institutional controls where the use of groundwater or the installation of wells is restricted." | 8.805 Water Cooled Heat Pumps (Geothermal Heat Pump Systems) | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Lake Alfred | City | 1237525 | Definition: Geothermal Heat Pump |  |  | "Renewable energy devices and other sustainable development technologies including, but not limited to, solar photovoltaic (pv) panels, solar hot water, solar pool heaters, tankless water heaters, geothermal heat pumps, gray-water systems, and rainwater harvesting devices, such as rain barrels and cisterns." | Sec. 3.8. Accessory Uses and Structures Defined | 2025 | https://www.mylakealfred.com/DocumentCenter/View/2510/Unified-Land-Development-Code-ULDC---Interim-SB180---Effective-11032025
Florida |  | Lake Alfred | City | 1237525 | Screening |  |  | "Renewable energy devices and other sustainable development technologies including... geothermal heat pumps... Development standards within residential districts. Ancillary equipment shall comply with the following: ... Screening. The sides of any new or replacement equipment facing or visible from a street, excluding alleys, shall be landscaped as required in the landscaping and irrigation section, unless installed above the ground story." | Development standards within residential districts | 2025 | https://www.mylakealfred.com/DocumentCenter/View/2510/Unified-Land-Development-Code-ULDC---Interim-SB180---Effective-11032025
Florida | Volusia | Ormond Beach | City | 1253150 | Definition: Geothermal Heat Pump |  |  | "Open-loop heat pump system means a two-well (2) installation consisting of supply and injection wells into the same aquifer for thermal transfer." Also, "Open recharge heat pump system means a single-well installation producing water from an aquifer and partially returning water through infiltration to the aquifer of origin." |  | 2023 | https://library.municode.com/fl/ormond_beach/codes/land_development_code?nodeId=CH1GEAD_ARTIIADEN_S1-15PLBO
Florida | Pinellas | St. Petersburg | City | 1263000 | Definition: Geothermal Heat Pump |  |  | 'For the purposes of this section, "ancillary equipment" means: ... Renewable energy devices and other sustainable development technologies including, but not limited to, solar photovoltaic (pv) panels, solar hot water, solar pool heaters, tankless water heaters, geothermal heat pumps, gray-water systems and rainwater harvesting devices, such as rain barrels and cisterns.' | 16.50.020.4.2. - Ancillary equipment |  | https://cms5.revize.com/revize/stpete/Residential%20LDR%20Update%202024-2025.pdf
Florida | Pinellas | St. Petersburg | City | 1263000 | Screening |  |  | 'The sides of any new or replacement equipment facing or visible from a street, excluding alleys, shall be landscaped as required in the landscaping and irrigation section, except that equipment installed above the first floor [shall be] screened with material that is compatible with the architectural style of the principal structure, landscaping, or a six-foot-tall decorative fence or wall.' Also, 'In all other zoning districts ... All ancillary equipment shall be shielded from view from the adjacent properties and streets, excluding alleys, by a solid enclosure such as a fence or wall.' | 16.50.020.4.2. - Ancillary equipment |  | https://cms5.revize.com/revize/stpete/Residential%20LDR%20Update%202024-2025.pdf
Idaho | Elmore |  | County | 16039 | Maximum Well Depth | 18 | feet | In Wellhead Protection Zones II and III, "Injection well is a prohibited use except for the following: a. Deep well injection (below eighteen (18°) feet in depth): (1) Geothermal heat; or (2) Heat pump return; or (3) Cooling water return." The ordinance also distinguishes "Shallow well injection only (less than eighteen (18°) feet in depth)" for other listed uses. | Section 6-25-5(C)-(D): Allowed Uses and Notice Requirements by Zone |  | http://elmorecounty.org/wp-content/uploads/2018/11/chapter-25-wellhead-protection.pdf
Idaho | Elmore |  | County | 16039 | Other Prohibitions/Regulations |  |  | Within Wellhead Protection Zone IA, permitted uses are limited to "Necessary public water supply wellhead equipment including, wellhead facility buildings, water storage tanks, disinfections equipment, disinfections chemical storage and landscaping as required by this Title. All other uses shall be prohibited." | Section 6-25-5(A): Wellhead Protection Zone IA |  | http://elmorecounty.org/wp-content/uploads/2018/11/chapter-25-wellhead-protection.pdf
Idaho | Minidoka |  | County | 16067 | Other Prohibitions/Regulations |  |  | Zone IB: 'Injection well is a prohibited use except for the following: a. Closed systems or as approved by IDEQ.' Zone II: 'Injection well is a prohibited use except for the following: a. Deep well injection (below 18 feet in depth): (1) Geothermal heat; or (2) Heat pump return; or (3) Cooling water return; b. Shallow well injection only (less than 18 feet in depth)...' Zone III: 'Injection wells except for the following: a. Deep well injection (below 18 feet in depth): (1) Geothermal heat; or (2) Heat pump return; or (3) Cooling water return...'. | 8-15-5: ALLOWED USES AND NOTICE REQUIREMENTS BY ZONE | 2016 | https://codelibrary.amlegal.com/codes/minidokaco_id/latest/minidokaco_id/0-0-0-3538
Idaho | Twin Falls |  | County | 16083 | Minimum Well Depth | 18 | feet | 'District 2 ... Injection wells except for the following: a. Deep well injection (eighteen (18) feet or deeper in depth) of one or more of the following types: i. Geothermal heat, ii. Heat pump return, or iii. Cooling water return.' The same deep-well exception also appears in 'District 3.' | 8-7E-3: PROHIBITED USES |  | https://twinfallscounty.org/wp-content/uploads/TFCO-ZONE-CODE-2022.pdf
Idaho | Twin Falls |  | County | 16083 | Other Prohibitions/Regulations |  |  | 'District 2: The following uses or conditions are prohibited within Wellhead Protection Overlay District 2: ... Injection wells except for the following: a. Deep well injection (eighteen (18) feet or deeper in depth) of one or more of the following types: i. Geothermal heat, ii. Heat pump return, or iii. Cooling water return ...' and 'District 3: The following uses or conditions are prohibited within Wellhead Protection Overlay District 3: 1. Injection wells except for the following: a. Deep well injection (eighteen (18) feet or deeper in depth) of one or more of the following types: i. Geothermal heat, ii. Heat pump return, or iii. Cooling water return ...' | 8-7E-3: PROHIBITED USES |  | https://twinfallscounty.org/wp-content/uploads/TFCO-ZONE-CODE-2022.pdf
Idaho | Ada | Boise City | City | 1608830 | Permit |  |  | "Any person desiring to connect a building or structure to the City geothermal system may apply for such service connection with the Department of Public Works on forms provided for that purpose. The Director of Public Works, or his authorized representative, shall approve or deny said application within thirty (30) days of its filing." Also, "It shall be a violation of this chapter for any person to construct or cause the construction of a service line or tap-in without approval of the Department of Public Works." | 10-3-3: SERVICE CONNECTION PROCEDURES | 2021 | https://codelibrary.amlegal.com/codes/boise_id/latest/boise/0-0-0-12610
Idaho | Ada | Boise City | City | 1608830 | Inspection |  |  | "Upon completion of the permitted service connection, the applicant shall promptly notify the Department of Public Works to request a service connection inspection." "Upon inspection by the Department of Public Works, the applicant may be required to reperform his work... if... the initial service connection work does not comply..." "All requests for inspection must be made to the Department of Public Works at least twenty four (24) hours prior to the requested inspection." "Should the applicant... connect facilities to the geothermal system without the facilities being inspected and approved by the Department of Public Works, the party responsible... shall be required... to excavate the connection, if necessary, and disconnect the connection... in order that a proper inspection can be made." | 10-3-3(F), (H), (I): SERVICE CONNECTION STANDARDS AND INSPECTIONS; INSPECTION; FAILURE TO INSPECT | 2021 | https://codelibrary.amlegal.com/codes/boise_id/latest/boise/0-0-0-12610
Idaho | Blaine | Carey | City | 1612790 | Definition: Geothermal Heat Pump |  |  | "Underground Injection Well (closed system). Closed-loop systems use an underground network of sealed, high-strength plastic piping, which acts as the earth-coupled heat exchanger. The most commonly used closed-loop piping material is high-density polyethylene (HDPE). The ground loop piping is filled with a working fluid that is continuously re-circulated without ever directly contacting the soil or water in which the loop is buried or immersed. Once filled with fluid and purged of air, nothing enters or leaves the closed loop. This eliminates the potential shortcomings of water quality and availability associated with open-loop systems." | Section 2 (W) Underground Injection Well (closed system) | 2022 | https://www.cityofcarey.org/local-codes-regulations/files/zoning-ordinance
Idaho | Blaine | Carey | City | 1612790 | Permit |  |  | "Whenever there is a request that requires a Conditional Use Permit for land lying within a Drinking Water Protection Zone, the Commission shall make recommendations to the Council which shall make the final decision. Both entities shall hold a duly noticed public hearing on the application at its earliest convenience." Also, Sections 10.5(i), 10.6 10.65, and 10.75 allow certain hazardous-material-related uses "except upon issuance of a Conditional Use Permit." | SECTION 10.8 CONDITIONAL USE PERMIT PROCESS | 2022 | https://www.cityofcarey.org/local-codes-regulations/files/zoning-ordinance
Idaho | Blaine | Carey | City | 1612790 | Other Prohibitions/Regulations |  |  | Section 10.5(d) states: "Injection well except for the following: (1) Closed systems." In Zone 1B, injection wells are prohibited except closed systems, so non-closed geothermal/open injection well configurations are banned there while closed systems remain allowed. | SECTION 10.5 PROHIBTED USES WITHIN ZONE 1B OF THE DRINKING WATER PROTECTION AREA | 2022 | https://www.cityofcarey.org/local-codes-regulations/files/zoning-ordinance
Illinois | McHenry | Algonquin | Village | 1700685 | Definition: Geothermal Heat Pump |  |  | "Geothermal heating and cooling system installed." | Section 21.4(Q) Density Bonuses for Open Space and Innovative Design | 2003 | https://www.algonquin.org/egov/documents/1663162194_91694.pdf
Illinois | McHenry | Algonquin | Village | 1700685 | Permit |  |  | "No application for a building permit or other permit or license or for a certificate of occupancy shall be approved... that would authorize the use or change in use of any land or building contrary to the provisions of this Chapter..." and "No Village building permit shall be issued until the appropriate local, state, or federal agencies have issued all necessary permits for the particular use." | Section 21.4(F) PERMITS | 2003 | https://www.algonquin.org/egov/documents/1663162194_91694.pdf
Illinois |  | Arlington Heights | Village | 1702154 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System. A renewable energy system using equipment that circulates relatively constant ground temperatures throughout buildings using an underground based piping system and a heat pump." | Section 28-3 - Definitions | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | Village | 1702154 | Setback - Right of Way | 3 | feet | Section 6.17-1(a)(3) states: "The system shall not be located within any utility easements, unless permission is granted by the applicable public and private agencies." Section 6.17-1(b)(3) adds: "The system shall be setback at least three feet from all lot lines." | Section 28-6 - General Provisions; 6.17-1(a)(3) and 6.17-1(b)(3) | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | Village | 1702154 | Setback - Property Lines | 3 | feet | "The system shall be setback at least three feet from all lot lines." | Section 28-6 - General Provisions; 6.17-1(b)(3) | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | Village | 1702154 | Permit |  |  | "No application for a building permit or other permit or license, or for a certificate of occupancy, shall be approved... and no permit or license shall be issued... which would authorize the use or change in use of any land or building contrary to the provisions of this Code..." This applies to geothermal energy systems because Section 6.17 establishes geothermal-specific zoning standards within this Code. | Section 28-6 - General Provisions; 6.4 Permits | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | Village | 1702154 | Other Prohibitions/Regulations |  |  | Geothermal systems are limited as follows: "The system shall be used only for the property on which it is located." "The system shall not be located within any utility easements, unless permission is granted by the applicable public and private agencies." "Each zoning lot is permitted one geothermal system." | Section 28-6 - General Provisions; 6.17-1(a)(1), 6.17-1(a)(3), 6.17-1(b)(1) | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois | Clinton |  | County | 17027 | Definition: Well |  |  | "Closed Loop Well means a sealed, watertight loop of pipe buried outside of a building foundation intended to recirculate a liquid solution through a heat exchanger but is limited to the construction of the bore hole, piping in the bore hole, heat exchange fluid, and the grouting of the bore hole and does not include the piping and appurtenances used in any other capacity. 'Closed Loop Well' does not include any horizontal closed loop well systems where grouting is not necessary by law or standard industry practice." | Section 18-3-1 - Definitions | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Definition: Geothermal Heat Pump |  |  | "Geothermal Closed Loop System means the entire system containing the horizontal closed loop well or wells, the vertical closed loop well or wells, and the horizontal header piping." | Section 18-4-1 - Definitions | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Building Foundation | 5 | feet | The setback table requires separation from "Pits, Crawl Spaces or Basements" of "5" feet for closed-loop wells. Section 18-3-7 also requires permit applications to show locations and distances to potential contamination sources, and the table provides the controlling numeric lateral distance. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Wastewater | 150 | feet | The setback table lists wastewater-related separations for closed-loop wells, including: "Cess Pools 150"; "Leaching Pit 25"; "Pit Privy 25"; "Subsurface Seepage Pipe/Tile From Private Sewage Systems 25"; and "Septic Tank 25" for USP food grade propylene glycol closed-loop wells, with larger distances for other authorized coolants in some cases. The controlling most restrictive wastewater setback shown is "Cess Pools 150." | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Private Water | 25 | feet | "When USP food grade propylene glycol is used as the geothermal coolant, the minimum setback of a closed loop well from a water well shall be twenty-five (25) feet." The setback table likewise lists "Existing Private Water Well ... 25" feet for USP food grade propylene glycol closed-loop wells. | Section 18-4-5 - Setback Distances | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Animal Enclosures | 25 | feet | The setback table requires closed-loop wells to be set back from "Barnyard or Animal Confinement Lot" by "25" feet for USP food grade propylene glycol systems. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Fuel (above ground) | 25 | feet | The table includes setback distances from contamination sources and specifically lists "buried fuel tanks" in the permit-application siting information in Section 18-3-7, but the explicit numeric lateral distances table governs sources including contamination routes. The only explicit fuel-tank reference in the ordinance text is "buried fuel tanks" within application requirements. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Subsurface Drains | 10 | feet | The setback table lists "Footing Drains (No connection to a sewer or sump handling sewage is allowed.)" with a minimum distance of "10" feet for closed-loop wells. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Sewer Lines | 50 | feet | The setback table provides: "Sewers 50 feet. A well or closed loop well may be located to within 10 feet of a sewer provided the sewer consists of cast iron pipe with watertight mechanical joints or rubber gasket sealed joints which meet ASTM Standard C564-09a, SDR 26 or schedule 40 PVC pipe or heavier with solvent welded watertight joints or elastomeric seals (gaskets) used for push-on joints which meet ASTM Standard F477-02e1." | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Setback - Water Bodies | 25 | feet | The setback table states: "Lakes, Ponds, Streams, or Cisterns 25" feet for closed-loop wells. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Permit |  |  | Section 18-3-6 states: "No water well or closed loop well system shall be constructed, modified or deepened except in accordance with this Code, and it shall be unlawful to proceed with such work unless a permit has first been obtained from the Health Department." Section 18-4-7 adds: "No geothermal closed loop system shall be constructed or modified in the County... without first registering the location and type of geothermal closed loop system with the Department." | Section 18-3-6 - Permit Required; Section 18-4-7 - Registration of Geothermal Closed Loop System | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Inspection |  |  | Section 18-3-16: "A water well or closed loop well system shall not be placed into operation until the installation of the water well, its components and closed loop well systems have been inspected to verify compliance with the applicable provisions of this Code and approval issued by the Health Department." Section 18-4-9: "A geothermal closed loop system shall not be placed into operation until the geothermal closed loop system has been inspected by the Department to verify compliance with this Article and until written approval has been issued by the Department." Section 18-4-2 also requires the system to "be pressure tested at a minimum pressure of twenty (20) pounds per square inch... after installation to ensure that there are no leaks." | Section 18-3-16 - Inspection of Completed Work; Section 18-4-9 - Inspections | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Licensed Driller |  |  | "No person shall install a vertical closed loop well unless that person is a Geothermal Closed Loop Well Driller." | Section 18-4-6 - Registration of Contractor/Driller | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Certification |  |  | "To register with the Department, a person shall have a valid accreditation from the International Ground Source Heat Pump Association (IGSHPA) or can show that he or she has an equivalent accreditation." Also, "A Geothermal Closed Loop Well Driller shall have a valid water well contractor’s license issued under the Illinois Water Well and Pump Installation License Act (225 ILCS 345/1) or shall have a valid certification for the drilling of closed loop wells from the National Ground Water Association (NGWA) or can show that he or she has an equivalent certification." | Section 18-4-6 - Registration of Contractor/Driller | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton |  | County | 17027 | Decommissioning |  |  | Section 18-4-12 provides: "Closed loop wells shall be sealed in accordance with the Illinois Water Well Construction Code. The Department shall be notified by telephone or writing at least forty-eight (48) hours prior to the commencement of any work to abandon a closed loop well." Section 18-3-5 similarly states: "Water wells or closed loop well systems that are abandoned shall be sealed in a manner prescribed by the Health Department and the 'Illinois Water Well Construction Code'." | Section 18-4-12 - Closed Loop Well Abandonment; Section 18-3-5 - Abandoned Wells or Closed Loop Well | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Henry |  | County | 17073 | Definition: Well |  |  | "Closed Loop Well means a sealed, watertight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger but is limited to the construction of the bore hole, piping in the bore hole, heat exchange fluid, and the grouting of the bore hole and does not include the piping and appurtenances used in any other capacity. 'Closed Loop Well' does not include any horizontal closed loop well systems where grouting is not necessary by law or standard industry practice." | SECTION I. A. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry |  | County | 17073 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Heat Exchange System (Geothermal Exchange Systems) means sealed, water tight loop of pipe buries outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger. The term includes, but is not limited to, closed loop wells, horizontal closed loop and body of water loop systems." | SECTION I. A. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry |  | County | 17073 | Setback - Building Foundation | 15 | feet | "In order to protect the sewage disposal system and a horizontal closed loop well system, there shall be a minimum set back of fifteen (15) feet between components of the systems." The ordinance definitions also state a closed loop heat exchange system and closed loop well are "buried outside of a building foundation." | SECTION IV. COMPLIANCE PROVISION, B. SEPTIC SYSTEM SET BACK FOR HORIZONTAL CLOSED LOOP WELL SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry |  | County | 17073 | Setback - Wastewater | 15 | feet | "In order to protect the sewage disposal system and a horizontal closed loop well system, there shall be a minimum set back of fifteen (15) feet between components of the systems." | SECTION IV. COMPLIANCE PROVISION, B. SEPTIC SYSTEM SET BACK FOR HORIZONTAL CLOSED LOOP WELL SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry |  | County | 17073 | Permit |  |  | "No water well nor closed loop heat exchange system well shall be constructed, deepened, modified or sealed after abandonment, except in accordance with these regulations, and it shall be unlawful to proceed with the construction, deepening, modification or sealing of a water well without first obtaining a permit from the Henry County Health Department." | SECTION IV. COMPLIANCE PROVISION, A. PERMIT | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry |  | County | 17073 | Inspection |  |  | "Henry County Health Department shall inspect all new closed loop well systems..."; "The inspection for a closed loop well system shall include observation of the critical aspects of construction, including, at a minimum, inspecting the grouting and documenting the setback distances."; "In the case of a closed loop well, the critical elements shall include placement of the sealing grout to assure that proper materials and methods are used." | SECTION IV. E. INSPECTIONS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry |  | County | 17073 | Certification |  |  | "All individuals who install closed loop well systems shall possess a valid certificate of registration issued by the Illinois Department of Public Health. All Horizontal Closed Loop contractors shall annually register with Henry County Health Department. The registration shall expire on November 30 th of the year of issue." | SECTION IV. D. REGISTRATION, 2. WATER WELL CONTRACTORS, WATER WELL PUMP INSTALLERS AND CLOSED LOOP WELL CONTRACORS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Jo Daviess |  | County | 17085 | Definition: Well |  |  | "HORIZONTAL CLOSED LOOP WELL: A closed loop well constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed twenty feet (20') in depth." "VERTICAL CLOSED LOOP WELL: A closed loop well constructed to contain vertical piping and the installation and grouting of the vertical loop piping when such piping exceeds twenty feet (20') in depth." | 5-7B-3: DEFINITIONS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL CLOSED LOOP SYSTEM: The entire system containing the horizontal closed loop well or wells, the vertical closed loop well or wells and the horizontal header piping." | 5-7B-3: DEFINITIONS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Setback - Public Water | 25 | feet | "When USP food grade propylene glycol is used as the geothermal coolant, the minimum setback of a closed loop well from a water well shall be twenty five feet (25')." | 5-7B-7: SETBACK DISTANCES | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Minimum Well Depth | 20 | feet | "HORIZONTAL CLOSED LOOP WELL: ... when such piping does not exceed twenty feet (20') in depth." "VERTICAL CLOSED LOOP WELL: ... when such piping exceeds twenty feet (20') in depth." | 5-7B-3: DEFINITIONS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Permit |  |  | "Application for registration for a geothermal closed loop system shall be in writing..." "A separate application is required for every ten (10) vertical wells or ten (10) horizontal loop trenches." "After an application to construct a geothermal closed loop system has been reviewed and approved, a notice to proceed shall be issued..." "No construction of a geothermal closed loop system shall commence prior to approval of the application by the department." | 5-7B-9: APPLICATION FOR REGISTRATION; 5-7B-12: APPROVAL OF APPLICATION | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Inspection |  |  | "The department shall have the authority to enter the property at any reasonable time for inspection purposes to determine compliance with this chapter." "A geothermal closed loop system shall not be placed into operation until the geothermal closed loop well has been inspected by the department to verify compliance with this chapter and until written approval has been issued by the department." "The geothermal closed loop system shall be pressure tested at a minimum pressure of twenty (20) pounds per square inch by the geothermal closed loop system contractor after installation to ensure that there are no leaks in the piping or in the equipment system." | 5-7B-10: INSPECTIONS; 5-7B-4: MATERIALS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Licensed Driller |  |  | "No person shall install a vertical closed loop well unless that person is a geothermal closed loop well driller." "A geothermal closed loop well driller shall have a valid water well contractor's license issued under the Illinois water well and pump installation contractor's license act..." | 5-7B-8: REGISTRATION OF CONTRACTOR/DRILLER | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Certification |  |  | "To register with the department, a person shall have a valid accreditation from the International Ground Source Heat Pump Association (IGSHPA) or can show that he or she has an equivalent accreditation." "A geothermal closed loop well driller shall have a valid water well contractor's license issued under the Illinois water well and pump installation contractor's license act... or shall have a valid certification for the drilling of closed loop wells from the National Ground Water Association (NGWA) or can show that he or she has an equivalent certification." | 5-7B-8: REGISTRATION OF CONTRACTOR/DRILLER | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess |  | County | 17085 | Decommissioning |  |  | "Closed loop wells shall be sealed in accordance with the Illinois water well construction code. The department shall be notified by telephone or writing at least forty eight (48) hours prior to the commencement of any work to abandon a closed loop well." | 5-7B-14: CLOSED LOOP WELL ABANDONMENT | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Lake |  | County | 17097 | Definition: Well |  |  | "The term 'well' shall include, but not be limited to the following types or categories of wells: all types or categories of water wells (including community water wells), monitoring wells, closed loop wells and injection wells (where the depth is greater than the largest surface dimension)." | § 170.01 GENERAL PROVISIONS. | 2015 | https://codelibrary.amlegal.com/codes/lakecountyil/latest/lakecounty_il/0-0-0-14327
Illinois | Lake |  | County | 17097 | Permit |  |  | "The Health Officer shall receive applications and issue permits for the installation and modification of water wells, closed loop wells and closed loop well systems, the sealing of wells, the operation of non-community water systems..." | § 170.02 HEALTH OFFICER, DUTIES AND POWERS. | 2015 | https://codelibrary.amlegal.com/codes/lakecountyil/latest/lakecounty_il/0-0-0-14327
Illinois | Lake |  | County | 17097 | Inspection |  |  | "The Health Officer shall receive applications and issue permits for the installation and modification of water wells, closed loop wells and closed loop well systems, the sealing of wells, the operation of non-community water systems, and shall inspect the premises for which the permits have been issued..." Also: "The Health Officer... shall have the authority to enter any property at any reasonable time to inspect for health and sanitation purposes, and for compliance with the provisions of this subchapter." | § 170.02 HEALTH OFFICER, DUTIES AND POWERS. | 2015 | https://codelibrary.amlegal.com/codes/lakecountyil/latest/lakecounty_il/0-0-0-14327
Illinois | McHenry |  | County | 17111 | Permit |  |  | "No person shall construct, deepen, modify, cap, or seal a water well until a permit has been issued by the Department." The ordinance also states: "A permit may be issued for a closed loop or irrigation well, when a community public water supply is reasonably available, provided that the owner/operator of the community public water supply provides written confirmation of no objection." | § 8.04.790 Permit Requirements |  | https://pub-countyofmchenry.escribemeetings.com/filestream.ashx?DocumentId=105790
Illinois | McHenry |  | County | 17111 | Inspection |  |  | "Department personnel shall have access to the property any time after a permit application has been filed in order to determine satisfactory compliance with the provisions set forth in this Ordinance." Access is deemed essential for "1. On-site layout review 2. Any stage of construction or modification of a system; and 3. Final inspection." The ordinance also states: "Department staff shall be present when a water well is sealed by a homeowner or environmental consultant." | § 8.04.790(M)-(N) Permit Requirements |  | https://pub-countyofmchenry.escribemeetings.com/filestream.ashx?DocumentId=105790
Illinois | Macon |  | County | 17115 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A sealed, watertight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger. May also be referred to as a closed loop system." | § 54.01 DEFINITIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Setback - Wastewater | 75 | feet | "there shall be a minimum set back of 75 feet between the septic field and the vertical geothermal system, and a minimum setback of 25 feet between the septic field and the horizontal geothermal system." | § 54.04 SEPTIC SYSTEM AND WELL SETBACK. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Setback - Private Water | 75 | feet | "Geothermal systems shall not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 54.04 SEPTIC SYSTEM AND WELL SETBACK. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Setback - Public Water | 200 | feet | "Geothermal systems shall not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 54.04 SEPTIC SYSTEM AND WELL SETBACK. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Minimum Well Depth | 20 | feet | "HORIZONTAL GEOTHERMAL SYSTEM. A geothermal system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth." "VERTICAL GEOTHERMAL SYSTEM. Geothermal system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth." | § 54.01 DEFINITIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Permit |  |  | § 54.02: "it shall be unlawful to proceed with the construction or modification of a geothermal system without first registering the location and type of geothermal system with the County Health Department." § 54.07(B): "No construction of a geothermal system can commence prior to approval of the application by the County Health Department." | § 54.02 REGISTRATION REQUIREMENT.; § 54.07 APPLICATION FOR INSPECTION. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Inspection |  |  | § 54.03: "Geothermal systems installed shall be exempt from the inspection requirement of this chapter provided the municipality has a geothermal system inspection process in place." § 54.07(A): "Application for inspection for a geothermal system shall be in writing." § 54.10(B): "the drilling and grouting of the holes should be witnessed (audited) by a representative of the County Health Department for each contractor annually." § 54.10(C): "The geothermal system shall be pressure tested at a minimum pressure of 20 pounds per square inch by the contractor, driller, and/or excavator after installation to ensure that there are no leaks in the piping or in the equipment system." | § 54.03 EXEMPTION.; § 54.07 APPLICATION FOR INSPECTION.; § 54.10 INSPECTIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Certification |  |  | § 54.11: "All geothermal systems shall use USP or food grade propylene glycol as the coolant in the county." § 54.01: "The product container shall be labeled 'Propylene Glycol USP' or equivalent. Any product not containing the letters 'USP' will not be acceptable for this use, unless vendor documentation is produced to demonstrate equivalency." § 54.10(D): "All plastic piping shall be watertight and conform to ASTM D2447-03 or D3035-08." | § 54.11 USE OF FOOD GRADE PROPYLENE GLYCOL AS COOLANT.; § 54.01 DEFINITIONS.; § 54.10 INSPECTIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon |  | County | 17115 | Decommissioning |  |  | The chapter includes an enacted section titled "§ 54.13 ABANDONMENT OF GEOTHERMAL SYSTEMS." | § 54.13 ABANDONMENT OF GEOTHERMAL SYSTEMS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Madison |  | County | 17119 | Closed-loop Prohibitions |  |  | In the Groundwater Protection Overlay District, Zone 1 and Zone 2 regulations state: "No injection wells (including closed loop heat pump wells)." | § 93.040(D)(1)(h) and § 93.040(D)(2)(h) | 2014 | https://cms4files.revize.com/madisoncountyilus/document_center/Planning_Development/Zoning%20Ordinance.pdf
Illinois | Randolph |  | County | 17157 | Permit |  |  | "It shall be unlawful for any person to construct and/or reconstruct any individual water supply system or geothermal well within Randolph County unless he holds a valid permit issued by the Health Officer." "It shall be the responsibility of the property owner to obtain a Permit before any construction is begun on the system." | 18-5-2 PERMITS; 18-5-3 PERMIT PRIOR TO CONSTRUCTION | 2016 | https://randolphcountyil.gov/wp-content/uploads/County-Ordinances.pdf
Illinois | Randolph |  | County | 17157 | Inspection |  |  | "The Health Officer is, hereby, authorized and directed to make such inspections as are necessary to determine satisfactory compliance with this Code." "It shall be the duty of the owner or occupant of a property to give the Health Officer free access to the property for the purpose of making such inspections as are necessary to determine compliance with the requirements of this Code." | 18-5-9 INSPECTIONS BY HEALTH OFFICER; 18-10-1 RIGHT OF INSPECTION | 2016 | https://randolphcountyil.gov/wp-content/uploads/County-Ordinances.pdf
Illinois | St. Clair |  | County | 17163 | Permit |  |  | "Any owner or authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical ... system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." (IRC R105.1, Section 7-2-27). Also: "An owner, authorized agent or contractor who desires to erect, install, enlarge, alter, repair, remove, convert or replace a mechanical system, the installation of which is regulated by this code ... shall first make application to the code official and obtain the required permit for the work." (IMC 106.1, Section 7-3-34). | 7-2-27 Required; 7-3-34 When required | 2017 | https://www.co.st-clair.il.us/webdocuments/CountyCode/Building%20Regulations.pdf
Illinois | St. Clair |  | County | 17163 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to framing inspection." (IRC R109.1.2, Section 7-2-51(B)). "Exception: Backfilling of ground-source heat pump loop systems tested in accordance with Section M2105.1 prior to inspection shall be permitted." Also: "The code official ... shall make the following inspections ... 1. Underground inspection ... before backfill is put in place ... 3. Final inspection shall be made upon completion of the mechanical system." (IMC 107.2, Section 7-3-40). "Exception: Ground-source heat pump loop systems tested in accordance with Section 1208.1.1 shall be permitted to be back filled prior to inspection." | 7-2-51(B) Plumbing, mechanical, gas and electrical systems inspection; 7-3-40 Required inspections and testing | 2017 | https://www.co.st-clair.il.us/webdocuments/CountyCode/Building%20Regulations.pdf
Illinois | Stark |  | County | 17175 | Definition: Well |  |  | "Closed Loop Well means a sealed, watertight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger but is limited to the construction of the bore hole, piping in the bore hole, heat exchange fluid, and the grouting of the bore hole and does not include the piping and appurtenances used in any other capacity. 'Closed Loop Well' does not include any horizontal closed loop well systems where grouting is not necessary by law or standard industry practice." | SECTION I.A.5. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark |  | County | 17175 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Heat Exchange System (Geothermal Exchange Systems) means sealed, water tight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger. The term includes, but is not limited to, closed loop wells, horizontal closed loop and body of water loop systems." | SECTION I.A.3. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark |  | County | 17175 | Setback - Wastewater | 15 | feet | "In order to protect the sewage disposal system and a horizontal closed loop well system, there shall be a minimum set back of fifteen (15) feet between components of the systems." | SECTION IV.B. SEPTIC SYSTEM SET BACK FOR HORIZONTAL CLOSED LOOP WELL SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark |  | County | 17175 | Permit |  |  | "No water neither well nor closed loop heat exchange system well shall be constructed, deepened, modified or sealed after abandonment, except in accordance with these regulations, and it shall be unlawful to proceed with the construction, deepening, modification or sealing of a water well without first obtaining a permit from the Stark County Health Department." | SECTION IV.A. COMPLIANCE PROVISION - PERMIT | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark |  | County | 17175 | Inspection |  |  | "For the required inspection, the Stark County Health Department shall be notified... at least 48 hours prior to the commencement of any work to construct, modify or seal after abandonment of a water well or closed loop well for which a permit has been issued." Also, "Stark County Health Department shall inspect all new closed loop well systems" and "The inspection for a closed loop well system shall include observation of the critical aspects of construction, including, at a minimum, inspecting the grouting and documenting the setback distances." | SECTION IV.C. NOTIFICATION; SECTION IV.E. INSPECTIONS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark |  | County | 17175 | Certification |  |  | "All individuals who install close loop well systems shall possess a valid certificate of registration issued by the Illinois Department of Public Health. All Horizontal Closed Loop contractors shall annually register with Stark County Health Department." | SECTION IV.D.2. REGISTRATION | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark |  | County | 17175 | Decommissioning |  |  | "No... closed loop heat exchange system well shall be... sealed after abandonment, except in accordance with these regulations." Also, "Stark County Health Department shall be present at the site during at least one well sealing performed by each licensed /registered contractor..." and "In the case of a closed loop well, the critical elements shall include placement of the sealing grout to assure that proper materials and methods are used." | SECTION IV.A. PERMIT; SECTION IV.E.3. ABANDONED WELL AND CLOSED LOOP WELL SEALING INSPECTIONS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Tazewell |  | County | 17179 | Permit |  |  | "The owner/developer will submit soil investigations conducted by certified soil classifier for determination of type of septic systems and minimum size of lots. The size of each lot will include area for a replacement system similar to the proposed septic system. The information on the plat must include location of proposed septic system, future site of replacement system, well and geothermal closed loop wells. This information must be submitted on forms provided by the county." | 94.32. Approval of Proposed Subdivision Plats | 2005 | https://tazewellhealth.org/225/Sewage-Disposal
Illinois |  | Deerfield | Village | 1718992 | Definition: Geothermal Heat Pump |  |  | 'Geothermal Energy System: A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems.' | 2.10-B Definitions | 2015 | https://www.deerfield.il.us/DocumentCenter/View/621/Article-2-General-Provisions-PDF
Illinois |  | Deerfield | Village | 1718992 | Permit |  |  | 'Geothermal Energy Systems shall be allowed as a Permitted Use in any zoning district, provided that a building permit is obtained and all permit requirements and general regulations are met, including: the Building Code, the Zoning Ordinance, the Lake or Cook County Health Ordinance (whichever is applicable based on the property's location), and the requirements referenced herein.' Also: 'An application for permit for all Geothermal Energy Systems shall contain the following information' including applicant/contact information and a 'Project summary including site plan and manufacturer information with specifications of materials and devices.' | 2.10-E Geothermal Energy Systems, 1. General Requirements; 2. Application Requirements | 2015 | https://www.deerfield.il.us/DocumentCenter/View/621/Article-2-General-Provisions-PDF
Illinois |  | Deerfield | Village | 1718992 | Certification |  |  | 'Geothermal Energy System components shall conform to applicable industry standards including those of the American National Standards Institute (ANSI). Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by Underwriters Laboratories (UL) or other approved independent testing agency.' | 2.10-E Geothermal Energy Systems, 1. General Requirements | 2015 | https://www.deerfield.il.us/DocumentCenter/View/621/Article-2-General-Provisions-PDF
Illinois |  | East Dundee | Village | 1721696 | Definition: Geothermal Heat Pump |  |  | "A GES is a central renewable heating and cooling exchange system that uses heat generated beneath the earth's surface to heat or cool buildings via underground or underwater systems that pump heat energy into a building or visa versa. Geothermal energy systems use the earth as a heat source in the winter or a heat sink in the summer." "Geothermal heat pump energy systems, or ground source heat pumps, are installed indoors and underground via a system of looped coils or piping and invisible after installation..." | SECTION 6-314.F. Geothermal Energy System (GES) Regulations; 1. Geothermal Heat Pump System (GHPS) | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Setback - Right of Way | 10 | feet | "GHPS loop fields, coils, piping or other similar underground infrastructure shall not encroach into public right-of-ways, ComEd transmission easements and right-of-ways, access roads, natural gas, fuel and other pipeline easements..." and "GHPS must maintain a minimum distance of ten (10') feet from existing storm water, sewer and water main utilities..." | SECTION 6-314.F.1.b Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Setback - Building Foundation | 20 | feet | "GHPS must maintain a minimum distance of ... twenty (20') feet from neighboring buildings or structures (except parking lots)." | SECTION 6-314.F.1.b Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Setback - Water Lines | 10 | feet | "GHPS must maintain a minimum distance of ten (10') feet from existing storm water, sewer and water main utilities..." | SECTION 6-314.F.1.b Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Setback - Sewer Lines | 10 | feet | "GHPS must maintain a minimum distance of ten (10') feet from existing storm water, sewer and water main utilities"; for irrigated systems, "Such systems must maintain a minimum distance of ten (10') feet from existing storm water infrastructure, such as culverts, and sewer utilities." | SECTION 6-314.F.1.b Setbacks; SECTION 6-314.F.2.b Width and Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Minimum Well Depth | 8 | feet | For irrigated geothermal heat pump systems, "Loop fields, coils, pipes or other similar and associated underground/underwater infrastructure must be below the frost line and a minimum of eight (8') feet below the normal water line of a detention/retention basin." Section 6-314.F.1.a also states: "GHPS loop fields, coils, piping or other similar and associated underground infrastructure must be below the frost line." | SECTION 6-314.F.2.a Depth | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Permit |  |  | "Petitioners seeking to construct or install an ECT must submit a complete petition to the Development Services Department and apply for building permits." ECTs "include but are not limited to ... geothermal energy systems (GES)." Also, "Geothermal heat pump energy systems, or ground source heat pumps, are ... permitted in all zoning districts via an ECT Review" and "The necessary building permits shall be obtained for a GES per the Village Building Code (e.g. electrical, plumbing, mechanical etc.)." | SECTION 6-314.C. Environmental Clean Technology Review and Notification Process; SECTION 6-314.F.3.f Design and Permitting | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | Village | 1721696 | Other Prohibitions/Regulations |  |  | "A GES shall access the earth's thermal energy below grade and shall not be visible from the public right-of-way or neighboring properties." "Tree removal for a GES is not permitted." | SECTION 6-314.F.3.a Access; SECTION 6-314.F.3.1 Tree Removal | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Moline | City | 1722073 | Definition: Geothermal |  |  | "Geothermal Energy. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | City | 1722073 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump System refers to a system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site. Closed Loop Ground Source Heat Pump System refers to a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | City | 1722073 | Setback - Yards | 5 | feet | "All components of Ground Source Heat Pump System including pumps, borings and loops shall be set back at least five (5) feet from interior and rear lot lines." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | City | 1722073 | Certification |  |  | "Only closed loop Ground Source Heat Pump System utilizing Illinois Department of Public Health approved heat transfer fluids are permitted." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | City | 1722073 | Decommissioning |  |  | "A Ground Source Heat Pump System that is allowed to remain in a nonfunctional or inoperative state for a period of twelve (12) consecutive months, and which is not brought in operation within the time specified by the city after notification to the owner or operator of the Ground Source Heat Pump System, shall be presumed abandoned and may be declared a public nuisance subject to removal at the expense of the operator." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | City | 1722073 | Open-loop Prohibitions |  |  | "Only closed loop Ground Source Heat Pump System utilizing Illinois Department of Public Health approved heat transfer fluids are permitted." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | City | 1722073 | Other Prohibitions/Regulations |  |  | "Ground Source Heat Pump System are prohibited in surface waters, except for storm water ponds where they are permitted." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | La Grange | Village | 1740767 | Inspection |  |  | "All testing as required by this Subsection shall be witnessed by the Building Official or his designee. An inspection performed by the Building Official or his designee shall be required prior to the closing of any trench or ground opening associated with ground source heat pump system loop piping." | § 150.23 INTERNATIONAL RESIDENTIAL CODE, (B)(73) Subsection M2105.1 | 2021 | https://lagrangeil.gov/DocumentCenter/View/2709/Code-Update-Draft-for-Publication-6-1-21
Illinois |  | Lake Barrington | Village | 1740884 | Other Prohibitions/Regulations |  |  | "Geothermal Energy Systems shall be prohibited within all Zoning Districts of the Village as they present a risk to the aquifer which is relied upon by most of the Village for its potable water supply." | 8-3-12-5: PROHIBITED RENEWABLE ENERGY SYSTEMS | 2023 | https://codelibrary.amlegal.com/codes/lakebarringtonil/latest/lakebarrington_il/0-0-0-23666
Illinois | Lake | Lake Villa | Village | 1741586 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM: A system which utilizes renewable energy generated from the interior of the Earth and used to produce energy for heating buildings or serving building commercial or industrial processes. A geothermal energy system does not include systems that use energy independent of the geothermal source to raise the temperature of the extracted heat, such as heat pumps." | 10-2-2: DEFINITIONS AND ABBREVIATIONS | 2024 | https://codelibrary.amlegal.com/codes/lakevillail/latest/lakevilla_il/0-0-0-7271
Illinois |  | Oak Brook | Village | 1754534 | Setback - Property Lines | 10 | feet | "1301.7.1. No geothermal well or water intake shall be located in any easement and/or within ten feet (10') from any property lot line." The same requirement appears in IMC 303.10.1: "No geothermal well or water intake shall be located in any easement and/or within ten feet (10') from any property lot line." | 1301.7.1; 303.10.1 | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois |  | Oak Brook | Village | 1754534 | Permit |  |  | The code states that permits are generally required except for listed exemptions: "105.2 Work Exempt From Permit. Exemptions from permit requirements of this code shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code... Permits shall not be required for the following... Mechanical: 1. Portable heating appliance... 3. Portable cooling unit... 4. Steam, hot or chilled water piping within any heating or cooling equipment regulated by this code..." The same structure appears in the residential code at "R105.2 Work Exempt From Permit." The code also provides: "109.2 Schedule Of Permit Fees. On buildings, structures, electrical, gas, mechanical and plumbing systems or alterations requiring a permit, a fee for each permit shall be paid..." and IMC "106.5.2 Fee Schedule. On buildings, structures, electrical, gas, mechanical and plumbing systems or alterations requiring a permit, a fee for each permit shall be paid..." | 105.2 Work Exempt From Permit; R105.2 Work Exempt From Permit; 106.5.2 Fee Schedule | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois |  | Oak Brook | Village | 1754534 | Inspection |  |  | "Any 90 day period of validity shall commence when the permit is issued, each time the work is inspected by the building official, or when an extension is granted by the building official." The residential code similarly states: "Any 90 day period of validity shall commence when the permit is issued, each time the work is inspected by the building official, or an extension is granted by the building official." | 105.5.2 Method For Determining Permit Expiration Date; R105.5.2 Method For Determining Permit Expiration Date | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois |  | Oak Brook | Village | 1754534 | Screening |  |  | The ordinance requires concealment of exterior mechanical equipment: "M1301.6 Mechanical Equipment To Be Screened. All exterior heating, air conditioning, ventilating, generators, pool heaters, or other mechanical equipment shall be fully screened to prevent view of the equipment from any point along the finished grade at any front lot line or side lot line of the lot on which the equipment is located. Screening materials shall be as approved by the building official. Deciduous or annual plants shall not be approved as screening materials." Similar language appears in IMC 303.11 and IBC 2801.2 requiring exterior mechanical equipment to be "fully screened to prevent view." | M1301.6 Mechanical Equipment To Be Screened; 303.11 Mechanical Equipment To Be Screened; 2801.2 Exterior Mechanical Equipment To Be Screened | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois | Cook | Oak Park | Village | 1754885 | Definition: Geothermal Heat Pump |  |  | "All heating and air conditioning shall be provided by cold climate air source or ground source heat pumps." | APPENDIX P, SECTION P301 - ELECTRIFICATION REQUIREMENTS | 2023 | https://codelibrary.amlegal.com/codes/oakparkil/latest/oakpark_il/0-0-0-2372
Illinois | Cook | Oak Park | Village | 1754885 | Permit |  |  | "Any owner or owner's authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical or plumbing system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." Appendix P also expressly regulates geothermal HVAC use: "All heating and air conditioning shall be provided by cold climate air source or ground source heat pumps." | SECTION 105 - PERMITS; 105.1 Required | 2023 | https://codelibrary.amlegal.com/codes/oakparkil/latest/oakpark_il/0-0-0-2372
Illinois | Cook | Oak Park | Village | 1754885 | Inspection |  |  | For emergency work affecting "heating, air conditioning, or other essential utility service," work may begin before a permit only if "(1) the work is performed in conformance with this code; (2) a permit is obtained the next regular work day; and (3) the work is inspected and approved within 48 hours of permit issuance." | SECTION 105 - PERMITS; Emergency Work | 2023 | https://codelibrary.amlegal.com/codes/oakparkil/latest/oakpark_il/0-0-0-2372
Illinois |  | Orland Park | Village | 1756640 | Definition: Geothermal |  |  | "Renewable Energy. Refers to energy derived from existing flows of energy generated by on-going natural processes, including, but not limited to, energy generated from the sun, flowing water, wind flows, and geothermal heat flows." | SECTION 2 | 2010 | https://orlandpark.legistar.com/LegislationDetail.aspx?ID=7810611&GUID=4B86E6FD-2564-4ACA-95E6-B39B94A2EA39&Options=&Search=&FullText=1
Illinois |  | Orland Park | Village | 1756640 | Definition: Geothermal Heat Pump |  |  | "Environmental/Clean Technology (ECT). ... Includes renewable energy (wind, solar, hydro, geo, and biomass), information technology, sustainable transportation, electric motors, lighting and other appliances and systems such as devices that are sustainable and part of or accessory to a building or site as a feature, and/or a utility that serves multiple economic and environmental purposes including, but not limited to, ... ground source heat pumps ..." | SECTION 2 | 2010 | https://orlandpark.legistar.com/LegislationDetail.aspx?ID=7810611&GUID=4B86E6FD-2564-4ACA-95E6-B39B94A2EA39&Options=&Search=&FullText=1
Illinois |  | South Barrington | Village | 1770564 | Noise Limits | 50 | dBA | Under "Location And Manner of Installation," alternative energy systems are subject to: "Sound: Sound may not exceed fifty (50) dB at lot line." | 10-6-4(A)(3)(b) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | Village | 1770564 | Maximum Well Depth | 20 | feet | "Closed Loop Systems: Geothermal heat pump systems are limited to a maximum below-ground depth of twenty feet (20')." | 10-6-4(C)(2) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | Village | 1770564 | Permit |  |  | "Building Permit Required: A building permit must be obtained before the installation of any alternative energy system." | 10-6-4(A)(2) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | Village | 1770564 | Inspection |  |  | "System Testing: Pipes for geothermal systems permitted under this section must be tested hydrostatically at 1.5 times the maximum system design pressure, but not less than 100 psi (689 kPa), for a duration of not less than fifteen (15) minutes. All geothermal systems must be pressure checked by a licensed geothermal system contractor every five (5) years from the date of its initial successful test. Results must be filed with the building officer. If the test results show the system fails to meet these requirements, system shutdown and repairs must be made at the direction of the building officer." | 10-6-4(C)(3) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | Village | 1770564 | Certification |  |  | "Drilling: Any and all drilling associated with the installation of a ground source heat pump system must be performed by a certified geothermal drill operator." | 10-6-4(C)(4) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | Village | 1770564 | Decommissioning |  |  | "When any alternative energy system equipment has become inoperable or damaged for a period of one hundred and eighty (180) days or more, or otherwise violates the requirements of this ordinance, it is deemed abandoned. The owner of abandoned alternative energy system equipment must remove the alternative energy system equipment within thirty (30) days following the mailing of written notice that removal is required... Upon removal the site must be restored to the condition that existed before installation of the equipment." | 10-6-4(A)(1) Inoperable or Damaged Equipment | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | Village | 1770564 | Open-loop Prohibitions |  |  | "Open Loop Systems: Open loop systems are prohibited." | 10-6-4(C)(1) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois | Whiteside | Sterling | City | 1772546 | Setback - Wastewater | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Setback - Private Water | 50 | feet | "Closed-loop and direct exchange wells shall be sited at least 50 feet from private potable water supply wells." | Sec. 102-631(E)(6)(a)(iv) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Setback - Animal Enclosures | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Setback - Fuel (above ground) | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Setback - Water Bodies | 10 | feet | "Closed-loop and direct exchange wells shall be sited at least ten feet from surface water bodies." | Sec. 102-631(E)(6)(a)(vii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Setback - Hazardous Materials/Fertilizers | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Permit |  |  | "The owner/operator/installer of the GSHP system shall submit to the city a BSO plan and comply with the regulations outlined in section 102-924." "A City of Sterling Zoning Permit shall be required as outlined under section 102-910." "A City of Sterling Building Permit shall be required as outlined under chapter 18 of the Municipal Code." "The owner/operator/installer of the GSHP system shall submit to the building and zoning superintendent approval for the system by the IDPH." "Prior to the construction of a gshp system, the owner/operator/installer must submit to the IDPH a notification of intent to construct. This notification requirement includes GSHP systems that do not include the use of wells." | Sec. 102-631(E)(1)-(3) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Licensed Driller |  |  | "Only contractors complying with 77 Ill. Adm. Code Part 915 shall be permitted to construct, alter, or decommission wells for geothermal heating and cooling systems." | Sec. 102-631(E)(4)(a) - Contractors, Well drilling | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Certification |  |  | "All construction plans must be designed and stamped by a professional engineer licensed in the State of Illinois or an individual that is certified by the ... International Ground Source Heat Pump Association (IGSHPA)." "All plumbing installation/modification shall be performed by a licensed Illinois plumber." "The installation or modification of all GSHP equipment shall be performed by an individual certified by the IGSHPA." | Sec. 102-631(E)(1), (4)(b), (4)(c) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | City | 1772546 | Other Prohibitions/Regulations |  |  | "GSHP wells or systems shall not be located, constructed, or operated in a manner that will cause further degradation of aquifers, wetlands, or surface water bodies." "The use of refrigerants, antifreeze chemicals, and lubricating oils is prohibited in water that is returned to the subsurface via openloop GSHP systems." "The use of plasticizers in grout used in well construction is prohibited for open-loop GSHP wells." "Closed-loop and direct exchange wells shall not be permitted within the Zone 1 of public water supply wells." "An open-loop GSHP well that does not also serve as a public water supply well shall not be permitted within the Zone 1 of a public water supply well." | Sec. 102-631(C); Sec. 102-631(E)(5)(a)-(b); Sec. 102-631(E)(6)(a)(v)-(vi) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois |  | Westmont | Village | 1780645 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Exchange System Equipment that exchanges thermal energy between the ground (or a water source) and a building. This includes vertical closed loop, horizontal closed loop, water body closed loop system and open loop systems. Also known as ground source heat pumps and geothermal heat pumps." | Sec. 17.06 Definition of Words and Terms | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Illinois |  | Westmont | Village | 1780645 | Permit |  |  | "To engage in the use of a building, structure or land, the use or installation of a sign, or any other activity requiring one or more permits or approvals under this zoning ordinance without obtaining such required permits or approvals" is a violation; and "The zoning administrator" is responsible for "Receiving and processing all applications for permits and development approvals under this zoning ordinance." | Sec. 15.02 Enforcement | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Illinois |  | Westmont | Village | 1780645 | Inspection |  |  | The zoning administrator has authority for "Conducting needed inspections of structures and uses of land to determine compliance with this zoning ordinance." | Sec. 15.01 Administration | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Illinois |  | Westmont | Village | 1780645 | Other Prohibitions/Regulations |  |  | "Underground equipment, piping and devices may be located in yard areas but may not be located in any public easement or right-of-way." | Sec. 7.17 Geothermal Heat Exchange Systems | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Indiana | Allen |  | County | 18003 | Definition: Geothermal Heat Pump |  |  | Accessory buildings, structures, and uses shall be permitted, including but not limited to: "Geothermal system." | 3-2-3-4 Accessory Buildings, Structures and Uses | 2025 | https://www.allencounty.in.gov/DocumentCenter/View/11296/2024-AC-Solar-Amendment---Staff-report-ZORD-2025-0005?bidId=
Indiana | Boone | Zionsville | Town | 1801186372 | Open-loop Prohibitions |  |  | "The construction of new geothermal open-loop heating and/or cooling systems within the municipal boundaries is prohibited." | § 52.002 SEPTIC SYSTEMS AND GEOTHERMAL OPEN-LOOP SYSTEMS PROHIBITED | 1991 | https://codelibrary.amlegal.com/codes/zionsville/latest/zionsville_in/0-0-0-1573
Indiana | Floyd |  | County | 18043 | Permit |  |  | "No person shall cause or allow the construction of any outbuilding or the installation of any swimming pool, geothermal heat system, underground utility connection, or underground lawn sprinkler system in association with an existing residence or commercial facility without first obtaining a Site Approval Permit for such construction." Article VI, Section 3 adds that "Site Approval Permits for the construction of any outbuilding or the installation of any swimming pool, ... geothermal heat system, underground utility connection, or underground lawn sprinkler system shall be issued upon: (1) proper application ... (2) the payment of the fee ... and (3) a determination by the Health Officer that the proposed location of such construction or installation conforms with Residential Rule 410, and shall not damage the residential sewage disposal system or interfere with its proper operation." | ARTICLE V. PROHIBITED ACTS, SECTION 5; ARTICLE VI. RESIDENTIAL PERMITS, SECTION 3 | 2010 | https://www.in.gov/counties/floyd/health-department/files/Floyd-County-Ordinances2.pdf
Indiana | Hendricks |  | County | 18063 | Setback - Property Lines | 5 | feet | Both open-loop geothermal separation tables include "Property lines — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Setback - Building Foundation | 5 | feet | Both open-loop geothermal separation tables include "Buildings and building overhangs — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Setback - Wastewater | 100 | feet | The ordinance provides minimum separation distances for open loop geothermal heat pump systems. For residential service, listed wastewater-related sources include "Septic tanks and absorption fields — 50 feet" and "Sewage pits and dry wells — 100 feet." For systems "serving other than a residence consisting of not more than two dwelling units," the table lists "Septic tanks, absorption fields, filters — 100 feet" and "Privies — 100 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Setback - Animal Enclosures | 50 | feet | For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units," the table requires separation from "Stables, livestock runs, manure piles, etc — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Setback - Sewer Lines | 30 | feet | For "open loop geothermal heat pump systems serving a residence(s)," the ordinance states they "shall maintain the following minimum separation distances from sources of contamination," including "Sewer Pipe ... 30 feet" and "Gravity sewers outside of building foundations..." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units," the table likewise lists "Sewer Pipes — 30 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Setback - Water Bodies | 50 | feet | The ordinance sets minimum separations for open loop geothermal heat pump systems from surface waters. One table lists "Streams, lakes, ponds — 25 feet" and another for systems "serving other than a residence consisting of not more than two dwelling units" lists "Streams, lakes, ponds — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Permit |  |  | "Before commencement of construction of a well or geothermal heat pump system utilizing a well, a well repair or a pump installation, the owner or agent shall obtain a written permit signed by the Health Officer. No person shall perform any work on such project until such permit is obtained." The permit application must be made on a form provided by the Health Officer, and "such permit shall be void if the installation is not completed in one year." | SECTION III PERMITS | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Inspection |  |  | "It shall be the duty of the well driller and the owner of the property on which the well is drilled to notify the Hendricks County Health Department when the well and appurtenances are available for inspection. The Health Officer must be permitted to inspect the well and appurtenances at any reasonable time." | SECTION VI COMPLIANCE AND INSPECTION - Inspection | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Licensed Driller |  |  | "All water well drillers and pump installers operating in Hendricks County shall comply with the licensing requirements of Indiana Code 25-39-3." | SECTION V MINIMUM REQUIREMENTS - Water Well Drillers and Pump Installers | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks |  | County | 18063 | Decommissioning |  |  | "Groundwater wells must be properly abandoned in accordance with 312 IAC 13." The ordinance further states: "Any groundwater well connected to an existing structure that is scheduled for demolition must be either: a. Properly abandoned in accordance with 312 IAC 13 ... with written verification submitted to the Local Health Officer prior to initiating demolition of the structure, or b. Located by global positioning system for later abandonment, with written notification and well location submitted to the Local Health Officer prior to initiating demolition of the structure." | SECTION V MINIMUM REQUIREMENTS - Well Abandonment | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | Center | Township | 1806311386 | Definition: Well |  |  | "Well as defined in IC 25-39-2 a hole drilled or driven to: (1) obtain geologic information on aquifers; (2) monitor the quality or quantity of ground water; (3) obtain ground water; or (4) utilize the geothermal properties of earth formations." | SECTION I DEFINITIONS | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Setback - Property Lines | 5 | feet | Both open-loop geothermal setback tables state "Property lines — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Setback - Building Foundation | 5 | feet | Both open-loop geothermal setback tables state "Buildings and building overhangs — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Setback - Wastewater | 100 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table lists "Privies — 50 feet," "Septic tanks and absorption fields — 50 feet," and "Sewage pits and dry wells — 100 feet." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units" the table lists "Septic tanks, absorption fields, filters — 100 feet" and "Privies — 100 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Setback - Animal Enclosures | 50 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table requires separation from "Stables, livestock runs, manure piles, etc — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Setback - Sewer Lines | 30 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table includes "Sewer Pipes — 30 feet." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units" the table includes "Sewer Pipe ... 30 feet" and also "Sewers and Drains — 100 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Setback - Water Bodies | 50 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table lists "Streams, lakes, ponds — 25 feet." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units" the table lists "Streams, lakes, ponds — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Permit |  |  | "Before commencement of construction of a well or geothermal heat pump system utilizing a well, a well repair or a pump installation, the owner or agent shall obtain a written permit signed by the Health Officer. No person shall perform any work on such project until such permit is obtained." The ordinance also states: "In emergency situations, the applicant for the well permit shall notify the Health Department of the pending well installation prior to such installation" and submit the application within 24 hours of the next regular workday. | SECTION IH PERMITS | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Inspection |  |  | "It shall be the duty of the well driller and the owner of the property on which the well is drilled to notify the Hendricks County Health Department when the well and appurtenances are available for inspection. The Health Officer must be permitted to inspect the well and appurtenances at any reasonable time." | SECTION VI COMPLIANCE AND INSPECTION - Inspection | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | Township | 1806311386 | Decommissioning |  |  | "Groundwater wells must be properly abandoned in accordance with 312 IAC 13." The ordinance further provides: "Any groundwater well connected to an existing structure that is scheduled for demolition must be either: a. Properly abandoned in accordance with 312 TAC 13 ... with written verification submitted to the Local Health Officer prior to initiating demolition ... or b. Located by global positioning system for later abandonment, with written notification and well location submitted to the Local Health Officer prior to initiating demolition." | SECTION V MINIMUM REQUIREMENTS - Well Abandonment | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Lake |  | County | 18089 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System (Geothermal Heat Exchange) Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. Geothermal energy systems consist of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump. This includes vertical closed loop, horizontal closed loop and water body closed loop systems." | 154-22-110. Definition of Words and Terms Beginning with 'G' | 2025 | https://lakecountyin.gov/departments/planning-commission/ordinances-c/unified%20development%20ordinance%20no.%202560.pdf
Indiana | Lake |  | County | 18089 | Permit |  |  | It is a civil zoning violation for the "failure to obtain a building, zoning, or other permit required under this UDO," and Article 20 states officials "may not issue permits or licenses for any use, building, activity or purpose that would be in conflict with the provisions of this UDO." | 154-20-040.E.1.b | 2025 | https://lakecountyin.gov/departments/planning-commission/ordinances-c/unified%20development%20ordinance%20no.%202560.pdf
Indiana |  | Carmel | City | 1810342 | Definition: Well |  |  | "A Well is any hole or shaft drilled, augured, sunk, or inserted into the earth for extraction, injection, or disposal of any material. A well shall include all mechanical and plumbing appliances connected thereto. This includes any device inserted into the earth which is intended for geothermal or heat exchange purposes whether or not said device pumps water from or into the earth directly." | § 7-51 Definitions | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | City | 1810342 | Permit |  |  | § 7-57(c): "Each business person shall obtain from Carmel Utilities a permit, which shall be valid for one year, from date of issue, unless otherwise revoked." § 7-62: "Within a reasonable time after an application is presented to Carmel Utilities, but before drilling is started, the owner, or his agent shall request well site approval from Carmel Utilities." § 7-75(a): "Prior to the drilling of a new well an application must be completed, approved and on file at the Carmel Utilities Office... Both a well application and inspection request must be made prior to the drilling procedure, otherwise the well drilling operation shall be stopped until arrangements satisfactory with Carmel Utilities can be established." | § 7-57 Requirements for Registration and Permits; § 7-62 Well Site Approval Required; § 7-75 Well and Permit Application and Fees | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | City | 1810342 | Inspection |  |  | § 7-57(d): "All wells must comply with the City's specifications as revised from time-to-time and be inspected and certified by Carmel Utilities, prior to being placed into service." § 7-70(a): "All wells are required to have two inspections: (1) During the grouting procedure; and (2) A final inspection made after all appurtenances are installed and just prior to placing the well in service." § 7-70(b): "No well shall be placed in service prior to passing final inspection." § 7-74(a): "If a well is drilled and no inspection is requested or made in accordance with this article, that well must be abandoned and sealed off..." | § 7-57(d); § 7-70 Two Well Inspections Required; § 7-74 Failure to Request Well Inspections | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | City | 1810342 | Licensed Driller |  |  | "All persons drilling wells must have a current drilling license from the State of Indiana." | § 7-55 State Licensing Required | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | City | 1810342 | Decommissioning |  |  | "If a well is drilled and no inspection is requested or made in accordance with this article, that well must be abandoned and sealed off according to the City and State specifications. A new well must be drilled unless otherwise excepted in writing by the manager of the Carmel Utilities and inspection occurs in accordance with this article." | § 7-74 Failure to Request Well Inspections | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana | Pulaski |  | County | 18131 | Definition: Geothermal Heat Pump |  |  | "PRIVATE WATER WELLS. Any water well, including those serving geothermal heat pump systems, constructed to provide water to one- or two-family dwellings, totally or in part." | TITLE V: PUBLIC WORKS - PRIVATE WATER WELLS | 2014 | https://www.in.gov/localhealth/pulaskicounty/files/Pulaski-Co-Code.pdf
Indiana | St. Joseph |  | County | 18141 | Definition: Well |  |  | 'GEOTHERMAL WELL. A well that supplies water for use solely to heat and/or cool a structure.' | § 52.034 DEFINITIONS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph |  | County | 18141 | Setback - Building Foundation | 10 | feet | 'Wells shall be at least five feet outside of any existing building overhang and at least ten feet from any building foundation except geothermal, dewatering, fire suppression and monitoring wells.' | § 52.041(D) SITING OF NONPOTABLE WATER WELLS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph |  | County | 18141 | Permit |  |  | 'The owner of the real estate on which a nonpotable water well is to be constructed or his or her authorized agent shall obtain a water well permit.' 'No person shall install a well until and unless a permit is first obtained from the Health Officer and posted in a conspicuous place on the premises...' Geothermal wells are included as nonpotable wells in § 52.035(A)(2): 'Nonpotable wells... including but not limited to irrigation wells, geothermal wells, monitoring wells, dewatering wells, waterscape wells and fire suppression wells.' | § 52.038 PERMITS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph |  | County | 18141 | Inspection |  |  | For nonpotable well permits, 'The Health Officer will review the application and the proposed well location and may conduct an on-site inspection of the proposed location of the well.' The site must be staked 'at the time of the on-site inspection by the Health Officer or the permit application may be denied.' The ordinance also states, 'Upon the receipt of an application to install a well, the Health Officer shall be permitted to inspect the location, installation, condition and sampling of the wells at any stage.' | § 52.038 PERMITS; § 52.049 ENFORCEMENT | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph |  | County | 18141 | Licensed Driller |  |  | 'Any person that installs or abandons a potable or nonpotable water well ... shall first be licensed by the state in accordance with I.C. 25-39 et seq.' 'Any person that installs or abandons a potable or nonpotable water well in the county shall first obtain an annual registration from the Health Officer.' 'A licensed well driller shall be present during all well drilling or well abandonment activities.' | § 52.036 LICENSING AND REGISTRATION OF WELL DRILLERS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph |  | County | 18141 | Decommissioning |  |  | 'No person shall abandon a well until and unless a well abandonment permit is first obtained from the Health Officer...' 'Any person who abandons any type of water well listed in § 52.035 shall have a current well drilling license.' 'Any potable or nonpotable well not in use for more than one year shall be abandoned according to the requirements of the Health Officer.' 'All wells shall be abandoned in a manner that restricts the movement of water within the well casing and annular space surrounding the well casing to the zone in which it originated...' 'The preferred method of abandoning wells is to remove the well casing and fill the well with a bentonite slurry or, at a minimum, bentonite pellets.' | § 52.038(D) Well abandonment permits; § 52.046 WELL ABANDONMENT PROCEDURES | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | Wabash |  | County | 18169 | Definition: Geothermal |  |  | "Geothermal" means a system that extracts heat from the earth in heating mode and/or rejects heat into the earth in cooling mode. | Chapter 1, Definitions | 2012 | https://www.in.gov/counties/wabash/files/ordinances/Current-Wabash-County-Zoning-Ordinance.pdf
Indiana | Wabash |  | County | 18169 | Permit |  |  | "Open Loop and Closed Loop Geothermal renewable energy systems may be permitted within the jurisdictional area of this Ordinance. Discharge and drainage plans for open loop systems, which are required to drain into a pond, stream, creek, or drainage tile shall be reviewed and approved by the Wabash County Drainage Board prior to completion of the ILP." | 6.1.16. Geothermal | 2012 | https://www.in.gov/counties/wabash/files/ordinances/Current-Wabash-County-Zoning-Ordinance.pdf
Indiana | Whitley |  | County | 18183 | Definition: Well |  |  | "GEO-THERMAL WELL. A hole drilled in the earth for the purposes of utilizing the inherent cooling and heating qualities of the earth, including open loop and closed loop systems." | § 51.03 DEFINITIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Definition: Geothermal Heat Pump |  |  | The geothermal-system-type language appears within the geothermal well definition: 'GEO-THERMAL WELL. A hole drilled in the earth for the purposes of utilizing the inherent cooling and heating qualities of the earth, including open loop and closed loop systems.' | § 51.03 DEFINITIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Property Lines | 5 | feet | In the table 'Minimal Horizontal Separation Distances From Water Wells,' the ordinance lists: 'Side, rear or front lot lines 5 feet.' Because § 51.03 defines 'WATER WELL' to include 'a geo-thermal well,' this setback applies to geothermal wells covered by the chapter. | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Building Foundation | 10 | feet | In the table 'Minimal Horizontal Separation Distances From Water Wells,' the ordinance lists: 'Dwelling or other inhibiting structure 10 feet.' Because § 51.03 states that 'WATER WELL' includes 'a geo-thermal well,' this applies to geothermal wells governed by the chapter. | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Wastewater | 100 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' includes: 'Private sewage disposal systems 50 feet,' 'Commercial sewage disposal systems 100 feet,' and 'Private sewage disposal systems 100 feet (in soils where aquifers are in danger of contamination).' § 51.03 provides that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Fuel (above ground) | 50 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Permanently fixed aboveground storage tanks for fuel or chemicals 50 feet (300 gallons or more)' and 'Permanently fixed aboveground storage tanks for fuel or chemicals 25 feet (0-299 gallons).' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Fuel (below ground) | 50 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Underground storage tanks for fuel or chemicals 50 feet.' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Sewer Lines | 10 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' lists: 'Sanitary sewage lines 10 feet (horizontal).' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Water Bodies | 25 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Lake, pond, river, stream or public ditches 25 feet.' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Setback - Hazardous Materials/Fertilizers | 50 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Underground storage tanks for fuel or chemicals 50 feet,' plus aboveground fuel or chemical storage tank setbacks of '50 feet (300 gallons or more)' and '25 feet (0-299 gallons).' § 51.03 includes geo-thermal wells within 'WATER WELL.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Permit |  |  | "The owner(s) ... of any parcel of ground unto which a water well is to be installed ... shall obtain a written permit signed by the Whitley County Health Officer before any construction begins." "The water well permit is valid for a term of one year from the date of issue." "In cases of extreme emergency ... a water well may be installed without first obtaining a local permit, provided that the property owner or his or her agent obtains a local well permit within the next working day." § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(H), (N), (O) CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Inspection |  |  | § 51.05(H): "The Health Officer shall then make a site review of the area proposed, in person, within two working days of the filed application." § 51.05(I): "The Health Officer shall be allowed to inspect the work at any stage of construction... The Whitley County Health Officer shall make the inspection within two working days of the receipt of notice from the applicant." § 51.06: "The Whitley County Health Department may be present at the drilling of a water well to determine if proper drilling practices and grouting practices are being observed." § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(H)-(J); § 51.06 | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Licensed Driller |  |  | "No person shall install a water well in Whitley County, without being licensed by the State of Indiana Department of Natural Resources, under authority of I.C. 25-39-3." § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(P) CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Certification |  |  | § 51.05(P): "No person shall install a water well in Whitley County, without being licensed by the State of Indiana Department of Natural Resources, under authority of I.C. 25-39-3." § 51.10(C): 'A well abandoned after December 31, 1987, shall be plugged ... by a registered and licensed well driller.' § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(P); § 51.10(C) | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Decommissioning |  |  | § 51.03 defines 'ABANDON' as: 'To terminate operations of a well for water supply, monitoring, dewatering or geothermal purposes and to restore the site of the well in a manner that will protect ground water resources from contamination.' § 51.10(C) states: 'A well abandoned after December 31, 1987, shall be plugged with an impervious grouting material ... by a registered and licensed well driller.' § 51.10(J) adds: 'The division shall be notified in writing of a well abandonment with 30 days after plugging is completed.' | § 51.10 WELL ABANDONMENT | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley |  | County | 18183 | Other Prohibitions/Regulations |  |  | "A closed loop geo-thermal well system must be located so as to be easily accessed and must not be built over or placed under impervious materials." | § 51.05(S) | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Iowa | Boone |  | County | 19015 | Setback - Property Lines | 10 | feet | Table I states that a "Groundwater heat pump borehole" must be at least "10" feet from "Property lines (unless a mutual easement is signed and recorded)." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone |  | County | 19015 | Setback - Building Foundation | 10 | feet | Table I lists "Groundwater heat pump borehole" with a required minimum distance of "10" feet from "Dwelling or other structure." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone |  | County | 19015 | Setback - Private Water | 50 | feet | Table I provides a row for "Groundwater heat pump borehole" and shows a minimum distance of "50" feet from a "Private water supply well." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone |  | County | 19015 | Setback - Public Water | 400 | feet | Table I states: "ALL PRIVATE SEWAGE DISPOSAL SYSTEMS SHALL BE LOCATED IN ACCORDANCE WITH THE MINIMUM DISTANCES SHOWN IN TABLE I." For "Groundwater heat pump borehole," the minimum distance is "400" feet from a "Shallow public water supply well@" and "200" feet from a "Deep public water supply well®." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone |  | County | 19015 | Setback - Subsurface Drains | 10 | feet | Table I requires a "Groundwater heat pump borehole" to be at least "10" feet from "Foundation drains or subsurface tiles." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone |  | County | 19015 | Setback - Water Lines | 100 | feet | Table I gives minimum distances from a "Groundwater heat pump borehole" to water lines: "10" feet from "Water lines continually under pressure" and "100" feet from "Suction water lines." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone |  | County | 19015 | Setback - Water Bodies | 100 | feet | Table I lists minimum distances for a "Groundwater heat pump borehole" from surface waters: "100" feet from "Lake or reservoir" and "25" feet from "Stream or pond." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Definition: Geothermal |  |  | "Alternative energy system: An energy system that generates electrical power or heat management by the means of wind, solar, or geothermal energy." | Section 100.28(C) Definitions | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils, or plates, a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." Also: "Closed loop ground source heat pump system: a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." And: "Open loop ground source heat pump system: a system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | Section 100.28(C) Definitions | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings, and loops shall be set back at least 5 feet from interior side lot lines and at least 10 feet from rear lot lines." | Section 100.28(G)(2) Setbacks | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Permit |  |  | "Alternative energy systems shall require plans to be approved by the zoning official through a permit procedure as outlined in the City Code..." "Building and electrical permits must be issued through Bremer County Zoning." Under permitted uses, "Closed Loop Ground Source Heat Pump System" and "Open Loop Ground Source Heat Pump System" are listed as permitted uses. For GHPs specifically: "Open loop ground source heat pump systems are permitted only in non-residential applications and require approval through the Public Works Department subject to all applicable conditions described in this section." | Section 100.28(D) Permit Process; Section 100.28(G) Ground Source Heat Pump Systems | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Inspection |  |  | "Building permit applications for open loop ground source heat pump systems shall be accompanied by documentation of ground water quality test results that fulfill the needs of The City Public Works Department for inspection. Prior to permit approval, follow up tests are to take place and given to the City Public Works Department upon completion of the installation of the system to ensure water quality of the groundwater aquifer. The City may conduct follow up tests at the site as needed to ensure water quality of the groundwater aquifer." | Section 100.28(G)(4) Groundwater Testing | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Certification |  |  | "Building permit applications for ground source heat pump systems shall be accompanied by standard drawings of the total energy system structure, including the pumps, borings, and loops. An engineering analysis of the system showing compliance with the International Building Code and certified by a licensed professional engineer shall also be submitted. This analysis is frequently supplied by the manufacturer. Wet stamps shall not be required." | Section 100.28(G)(5) Compliance with International Building Code | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | City | 1901794607 | Decommissioning |  |  | For abandoned open-loop systems: "If the open loop ground source heat pump system is determined to be abandoned, the owner, at their sole expense, shall restore site to original condition. To complete the removal of said system, the owner must remove the heat pump and any external mechanical equipment; fill pipes and coils with grout to displace heat transfer fluid. The heat transfer fluid must be removed from site and be disposed of in accordance with applicable regulations, documentation is required for removal. A final ground water quality test must be taken to ensure protection of ground water. Any piping or coiling 5 feet or less from the surface shall be removed. Removal and vegetation must be restored on site in 120 days from date of the determination of abandonment." | Section 100.28(G)(9) Maintenance | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Cedar |  | County | 19031 | Definition: Well |  |  | "Well" means any excavation that is drilled, cored, driven, dug, bored, augered, jetted, washed or is otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. "Well" does not include ... lateral geothermal heat exchange systems less than 20 feet deep ... | 567--49.2(455B) Definitions | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Definition: Geothermal Heat Pump |  |  | "Closed circuit vertical heat exchangers. These provisions apply to closed circuit vertical heat exchanger construction." | 567-49.29(455B) Closed circuit vertical heat exchangers | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Property Lines | 4 | feet | Table 49.6(1): "Property lines (unless a mutual easement is signed and recorded by both parties)" — minimum lateral distance "4" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Wastewater | 1000 | feet | Table 49.6(1): "Earthen manure storage basin, runoff control basins and anaerobic lagoons" — "1000" feet; "Domestic wastewater lagoon" — "400" feet; "Sanitary landfills" — "1000" feet; "Soil absorption field, any sewage treatment system with an open discharge, pit privy or septic tank discharge line" — "100" feet; and "Septic tank, concrete vault privy" — "50" feet. Rule 49.6(2) provides an exception reducing the lagoon/basin distance to "400 feet" in specified cases. | 49.6(1) Minimum distances; 49.6(2) Exception to minimum lateral distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Public Water | 400 | feet | Table 49.6(1): "Public water supply well" — minimum lateral distance "400" feet for shallow wells and "200" feet for deep wells. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Animal Enclosures | 200 | feet | Table 49.6(1): "Formed manure storage structure, confinement building, feedlot solids settling facility, open feedlot" — minimum lateral distance "200" feet for shallow wells and "100" feet for deep wells. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Fuel (above ground) | 100 | feet | Table 49.6(1): "Liquid hydrocarbon storage tanks" — minimum lateral distance "100" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Water Lines | 10 | feet | Table 49.6(1): "Hydrants" — minimum lateral distance "10" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Sewer Lines | 50 | feet | Table 49.6(1): "Sewer of tightly joined tile or equivalent material, sewer-connected foundation drain, or sewers under pressure" — "50" feet; and "Sewer of cast iron with leaded or mechanical joints, sewer of plastic pipe with glued or compression joints" — "10" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Water Bodies | 25 | feet | Table 49.6(1): "Ditches, streams, ponds, or lakes" — minimum lateral distance "25" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table 49.6(1): "Preparation or storage area for spray materials, commercial fertilizers or chemicals that may result in groundwater contamination" — minimum lateral distance "100" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Minimum Well Depth | 60 | feet | "In no case shall less than 20 feet of permanent casing be installed in wells drilled in unconsolidated materials. If the alluvial aquifer where the water is to be drawn from is covered by less than 40 feet of low permeability materials, the well screen shall be set at the bottom of the water-bearing aquifer or at least 60 feet from the surface." | 49.8(1)a.(1) Depth | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Permit |  |  | County ordinance: "No water well shall be constructed in Cedar County without a permit first being obtained from the Cedar County Environmental Health Department before construction begins." State rule: "No well construction or reconstruction shall be initiated until a permit has been issued by the proper authority." | CEDAR COUNTY ORDINANCE NUMBER 27; 567-49.4(455B) General | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Inspection |  |  | "The administrative authority shall have the authority to visit wellsites during any phase of the work without prior notice." | 567-49.4(455B) General | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Licensed Driller |  |  | "All well services shall be performed by a certified well contractor or the property owner as specified in 567-Chapter 82." Also, "'Well driller' means a person certified by the department to perform well drilling services." | 567-49.4(455B) General | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Certification |  |  | "'Well driller' means a person certified by the department to perform well drilling services." | 567--49.2(455B) Definitions | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar |  | County | 19031 | Decommissioning |  |  | "Abandoned wells shall be properly plugged as required in 567-Chapter 39." | 567-49.28(455B) Abandonment of wells | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Clay | Lone Tree | Township | 1904192709 | Permit |  |  | "This chapter shall not apply to closed loop, vertical, geothermal heating and cooling loop fields. However, prior to the installation of the loop field a City permit must be obtained." | 93.09 EXCEPTIONS | 2025 | http://ww.lonetreeiowa.com/docs/Public%20Notices/Code%20Lone%20Tree%20Ver%202025%2006-June.pdf
Iowa | Dallas |  | County | 19049 | Definition: Well |  |  | "Geothermal Heat Pump Well" means an excavation exceeding a 20-ft depth that is drilled, cased, bored, augured, washed, driven, dug, jetted, or otherwise constructed for the purpose of utilizing the geothermal properties of the ground. | II. 32.02 Definitions |  | https://www.dallascountyiowa.gov/408/Private-Well-Information
Iowa | Dallas |  | County | 19049 | Permit |  |  | "Permit required. When obtaining a permit to install a geothermal heat pump system, the contractor or homeowner must apply for a permit within the Dallas County Health Department prior to construction." | IV. 32.04 Additional Requirements for Geothermal Heat Pump Wells |  | https://www.dallascountyiowa.gov/408/Private-Well-Information
Iowa | Dallas |  | County | 19049 | Inspection |  |  | "Notify County Sanitarian. The driller shall notify the County Sanitarian prior to the burial of any geothermal loops for the purpose of inspection." | IV. 32.04 Additional Requirements for Geothermal Heat Pump Wells |  | https://www.dallascountyiowa.gov/408/Private-Well-Information
Iowa | Dubuque | Dubuque | City | 1906191085 | Definition: Well |  |  | "WELL: Any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed or is otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems ..." | 16-11-20-1: DEFINITIONS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM: A mechanism for heat transfer by fluid to air processes and heat transfer by fluid to fluid processes which consists of the following basic elements: Underground loops of piping; heat transfer fluid; a heat pump; an air distribution system. 1. Open Loop Geothermal System: Ground water is pumped from a water well into a heat exchanger located in a surface building and is then pumped back into the aquifer through a different well, the same well, or to the surface of the ground or to a surface body of water, also known as pump and dump. 2. Closed Vertical Loop or Horizontal Geothermal System: A borehole extends beneath the surface. Pipes are installed with U-bends at the bottom or at the end of the boreholes. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." | 16-11-20-1: DEFINITIONS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Setback - Public Water | 1000 | feet | "Major systems may not be located within one thousand feet (1,000 feet) of a current city well or water source. Minor systems may not be located within two hundred (200) feet of a city deep (Jordan/Cambrian-Ordovician) well or within four hundred (400) feet of a city shallow (alluvial aquifer) well." | 16-11-20-3(E): LOCATION OF GEOTHERMAL SYSTEMS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Setback - Hazardous Materials/Fertilizers | 500 | feet | "No geothermal system is allowed to be constructed within a 500-foot radius of an identified leaking underground storage tank (LUST) site." | 16-11-20-3(E): LOCATION OF GEOTHERMAL SYSTEMS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Permit |  |  | "Prior to the construction of any well, the well contractor must obtain a private water well construction permit from the Dubuque County Health Department and a permit from the Building Services Department, and where applicable, an Iowa Department of Natural Resources permit ..." and "No person may dig, bore, drill, replace, modify, repair or destroy a geothermal well or any other excavation that may intersect ground water without first applying for and receiving a permit from the Building Services Department." | 16-11-20-3(B): PERMIT REQUIRED | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Inspection |  |  | "Geothermal piping systems must be tested as required by the Building Services Manager prior to operation of the system and every three (3) years thereafter. All geothermal systems must be pressure checked by a certified contractor not less than every three (3) years from the certification system date. Results of the tests must be submitted to the Building Services Department." | 16-11-20-3(I): TESTING OF SYSTEM | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Licensed Driller |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82. The certified well contractor must be on-site and in direct control of all well services being performed." | 16-11-20-3(A): GEOTHERMAL WELL STANDARDS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Certification |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82." | 16-11-20-3(A): GEOTHERMAL WELL STANDARDS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Decommissioning |  |  | "Abandonment of geothermal systems must be as required in 567 Iowa Administrative Code Section 49.28. The heat transfer fluid must be removed by a displacement with grout and the loop pipes properly capped or sealed by an approved method. The top of the borehole must also be uncovered and properly capped or sealed by an approved method." | 16-11-20-3(J): ABANDONMENT OF GEOTHERMAL SYSTEMS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | City | 1906191085 | Open-loop Prohibitions |  |  | "Open loop systems are prohibited." Section 16-11-20-3(A) also states: "this section is intended to prohibit all open loop geothermal systems." | 16-11-20-3(H): OPEN LOOP SYSTEMS PROHIBITED | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Floyd | Charles City | City | 1906790645 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 11. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 12. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 13. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 14. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 1: General Provisions | 2022 | https://www.cityofcharlescity.org/206/UDOZoning-Ordinance
Iowa | Hancock |  | County | 19081 | Definition: Well |  |  | 'Well' means any excavation that is drilled, cored, driven, dug, bored, augered, jetted, washed or is otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems less than 20 feet deep. | 567-49.2(455B) Definitions | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Setback - Property Lines | 4 | feet | Table 49.6(1) lists 'Property lines (unless a mutual easement is signed and recorded by both parties)' with a minimum lateral distance of '4' feet for 'All Wells.' | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Setback - Wastewater | 1000 | feet | Table 49.6(1) requires setbacks for wastewater-related sources, including 'Earthen manure storage basin, runoff control basins and anaerobic lagoons ... 1000' feet; 'Domestic wastewater lagoon ... 400' feet; 'Soil absorption field, any sewage treatment system with an open discharge, privy or septic tank discharge line ... 100' feet; and 'Septic tank, concrete vault privy ... 50' feet. Rule 49.6(2) states an exception: 'The minimum separation distance between a well and an anaerobic lagoon, earthen manure slurry storage basin, earthen manure storage basin, or runoff control basin shall be 400 feet' in specified cases. | 49.6(1) Minimum distances; 49.6(2) Exception to minimum lateral distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Setback - Public Water | 400 | feet | Table 49.6(1) lists 'Public water supply well' with minimum lateral distances of '400' feet for shallow wells and '200' feet for deep wells. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Setback - Fuel (above ground) | 100 | feet | Table 49.6(1) lists 'Liquid hydrocarbon storage tanks' with a minimum lateral distance of '100' feet for all wells. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Setback - Sewer Lines | 50 | feet | Table 49.6(1) lists 'sewer of tightly joined tile or equivalent material, sewer-connected foundation drain, or sewers under pressure' at '50' feet, and 'Sewer of cast iron with leaded or mechanical joints, sewer of plastic pipe with glued or compression joints' at '10' feet. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Setback - Water Bodies | 25 | feet | Table 49.6(1) lists 'Ditches, streams, ponds, or lakes' with a minimum lateral distance of '25' feet for all wells. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Minimum Well Depth | 60 | feet | 'In no case shall less than 20 feet of permanent casing be installed in wells drilled in unconsolidated materials. If the alluvial aquifer where the water is to be drawn from is covered by less than 40 feet of low permeability materials, the well screen shall be set at the bottom of the waterbearing aquifer or at least 60 feet from the surface.' | 49.8(1)a(1) Drilled wells in unconsolidated materials — Depth | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Permit |  |  | 'No well construction or reconstruction shall be initiated until a permit has been issued by the proper authority.' The administrative authority 'shall by rule require the issuance of permits.' | 567-49.4(455B) General | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Inspection |  |  | 'The administrative authority shall have the authority to visit well sites during any phase of the work without prior notice.' | 567-49.4(455B) General | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Licensed Driller |  |  | 'All well services shall be performed by a certified well contractor or the property owner as specified in 567-Chapter 82.' Also, 'Well driller' means 'a person certified by the department to perform well drilling services.' | 567-49.4(455B) General | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock |  | County | 19081 | Decommissioning |  |  | 'Abandoned wells shall be properly plugged as required in 567-Chapter 39.' Also, 'Under no circumstances shall abandoned wells be used for the disposal of debris, solid waste, septic tank sludge or effluents, or for any other type of unauthorized disposal of waste materials, or as a receptacle for field tile drainage.' | 567-49.28(455B) Abandonment of wells | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Johnson |  | County | 19103 | Definition: Well |  |  | 'Well' means any excavation that is drilled, cored, driven, dug, bored, augered, jetted, washed or is otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems less than 20 feet deep. | 567-49.2(455B) Definitions | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Setback - Property Lines | 4 | feet | Table 49.6(1) requires a minimum lateral distance from 'Property lines' of '4' feet, with footnote '1 Unless a mutual easement is signed and recorded by both parties.' | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Setback - Wastewater | 1000 | feet | Table 49.6(1) requires setbacks from multiple wastewater-related sources, including 'Earthen manure storage basin, runoff control basins and anaerobic lagoons' at '1000' feet; 'Domestic wastewater lagoon' at '400' feet; and 'Soil absorption field, any sewage treatment system with an open discharge, pit privy or septic tank discharge line' at '100' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Setback - Public Water | 400 | feet | Table 49.6(1) lists 'Public water supply well' with minimum lateral distances of '400' feet for a shallow well and '200' feet for a deep well. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Setback - Fuel (above ground) | 100 | feet | Table 49.6(1) lists 'Liquid hydrocarbon storage tanks' with a minimum lateral distance of '100' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Setback - Sewer Lines | 10 | feet | Table 49.6(1) lists 'Sewer of tightly joined tile or equivalent material, sewer-connected foundation drain, or sewers under pressure' and 'Sewer of cast iron with leaded or mechanical joints, sewer of plastic pipe with glued or compression joints' with a minimum lateral distance of '10' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Setback - Water Bodies | 25 | feet | Table 49.6(1) lists 'Ditches, streams, ponds, or lakes' with a minimum lateral distance of '25' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Permit |  |  | 'The administrative authority shall by rule require the issuance of permits ... No well construction or reconstruction shall be initiated until a permit has been issued by the proper authority.' | 567-49.4(455B) General | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Inspection |  |  | 'The administrative authority shall have the authority to visit well sites during any phase of the work without prior notice.' Also, for vertical heat exchangers, 'Piping must be pressure-tested with air or potable water for 15 minutes at a pressure of 1.5 times the system operating pressure after installation in the borehole.' | 567-49.4(455B) General; 567-49.29(455B) Closed circuit vertical heat exchangers | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Licensed Driller |  |  | 'All well services shall be performed by a certified well contractor or the property owner as specified in 567-Chapter 82.' Also, 'Well driller' means 'a person certified by the department to perform well drilling services.' | 567-49.4(455B) General | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Certification |  |  | 'Well driller' means 'a person certified by the department to perform well drilling services.' 'Pump installer' means 'a person certified by the department to perform pump services.' | 567-49.2(455B) Definitions | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson |  | County | 19103 | Decommissioning |  |  | 'Abandoned wells shall be properly plugged as required in 567-Chapter 39.' | 567-49.28(455B) Abandonment of wells | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Definition: Well |  |  | "Well: Any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed, or otherwise constructed for the purpose of exploring for or monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems ..." | CHAPTER 12 WATER SERVICE | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Definition: Geothermal Heat Pump |  |  | "Geothermal System: A mechanism for heat transfer by fluid to air processes and heat transfer processes consisting of the following basic elements: underground loops of piping, heat transfer fluid, a heat pump, and an air distribution system." "Open Loop Geothermal System: A geothermal system in which groundwater is pumped from a water well into a heat exchanger located in a surface building. The water is then pumped back into the aquifer through a different well or the same well, or pumped to the surface of the ground or a surface body of water, also known as pump and dump." "Closed Vertical Loop or Horizontal Geothermal System: A geothermal system in which a borehole extends beneath the surface. Pipes are installed with U-bends at the bottom or at the end of the boreholes. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." | CHAPTER 12 WATER SERVICE | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Permit |  |  | "Open loop systems require review and approval by the City Utilities Director or their designee." "Prior to the construction of any geothermal well, the well contractor must obtain a private water well construction permit from the LCPH and a permit from the City Building Services Department, and, where applicable, an Iowa Department of Natural Resources water use permit or registration ..." "No person may dig, bore, drill, replace, modify, repair, or destroy a geothermal well ... without first applying for and receiving a permit from LCPH and a permit from the Building Services Department." "Applications for building services permits required by this Section must be made on forms provided by the Building Services Department ..." | 12.43 PRIVATE WELLS, (b)(2), (b)(4), (b)(5) | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Inspection |  |  | "The Utilities Director or their designee or the Building Official may suspend or revoke any permit issued pursuant to this Section whenever ... D. The system fails any of its mandated testing requirements." | 12.43 PRIVATE WELLS, (b)(8) Permit Suspension And Revocation | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Licensed Driller |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82. The certified well contractor must be on site and in direct control of all well services being performed." | 12.43 PRIVATE WELLS, (b)(3) Closed Loop Systems | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Certification |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82. The certified well contractor must be on site and in direct control of all well services being performed." | 12.43 PRIVATE WELLS, (b)(3) Closed Loop Systems | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Decommissioning |  |  | "Geothermal wells must be abandoned as required in 567 Iowa Administrative Code Section 49.28. The heat transfer fluid must be removed by displacement with grout and the loop pipes properly capped or sealed by an approved method. All heat transfer fluid must be safely disposed of according state and federal regulations. The top of the borehole must also be uncovered and properly capped or sealed by an approved method." | 12.43 PRIVATE WELLS, (b)(9) Abandonment Of Geothermal Systems | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | City | 1911390577 | Other Prohibitions/Regulations |  |  | "All loops must be located within the property boundaries of the building lot and not encroach on any easements." | 12.43 PRIVATE WELLS, (b)(6)(E) Site Plan Requirements | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Mahaska |  | County | 19123 | Setback - Private Water | 100 | feet | Table I lists minimum distances for on-site wastewater systems from "Private water supply well" as "50" feet for the closed portion and "100" feet for the open portion of the treatment system. | 2.4: Minimum Distances | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska |  | County | 19123 | Setback - Public Water | 200 | feet | Table I lists minimum distances for on-site wastewater systems from "Public water supply well" as "200" feet for both the closed and open portions of the treatment system. | 2.4: Minimum Distances | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska |  | County | 19123 | Permit |  |  | "No on-site wastewater treatment and disposal system shall be installed, altered, expanded or repaired until an application for a permit has been submitted and a permit issued by the Mahaska County Board of Health or the Administrative Authority." | 1.4: Permit Requirements | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska |  | County | 19123 | Inspection |  |  | "No on-site wastewater treatment system shall be covered so as to deny final inspection by the Administrative Authority" and "No on-site wastewater treatment system for which a permit has been issued shall be put into operation until the construction, repair, alteration, or remodeling shall have been inspected and approved by the Administration Authority." | 1.4: Permit Requirements | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska |  | County | 19123 | Decommissioning |  |  | "All primary treatment sections of the sewage disposal facilities (vault or septic tank) replaced by connections to a publicly operated sewage system or when an existing sewage disposal facility is replaced or use discontinued, shall be abandoned as specified by the Administrative Authority. No sewage disposal facilities shall be abandoned until the pumping contractor has cleaned said sewage disposal facilities." | 1.8: Abandonment of an On-Site Wastewater Treatment and Disposal System | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Marion |  | County | 19125 | Permit |  |  | "When obtaining a permit to install a geothermal heat pump system, the contractor or homeowner must apply for a permit within the County EH Department office prior to construction." The section also states: "The fee for obtaining a permit to install the system shall be set by the Board of Health. The additional IDNR fee still applies." | 43.07 CLOSED CIRCUIT VERTICAL HEAT EXCHANGERS |  | https://codelibrary.amlegal.com/codes/marioncounty/latest/marioncounty_ia/0-0-0-658
Iowa | Marion |  | County | 19125 | Inspection |  |  | The ordinance requires multiple inspections: "The Department shall be given no less than 24-hour notice to perform a pre-site inspection of the flagged area prior to well construction"; "The Department shall be given no less than 24-hour notice that the drilling process has begun to perform an on-site drilling inspection"; and "The Department shall be notified no less than 24 hours prior to pressurization of the system with the State approved antifreeze solution on-site during the final hook up, to perform a final inspection." | 43.07 CLOSED CIRCUIT VERTICAL HEAT EXCHANGERS |  | https://codelibrary.amlegal.com/codes/marioncounty/latest/marioncounty_ia/0-0-0-658
Iowa | Story |  | County | 19169 | Permit |  |  | Section 65.11 requires an application for a septic construction permit to include a site evaluation/design and other materials. Section 65.17 states: "Site evaluations are required prior to issuance of a construction permit." Section 65.24 provides that the site evaluation report must include a "Diagram showing the location and setbacks of existing/proposed water wells, geothermal wells, horizontal geothermal loops..." | 65.11 DOCUMENTS NEEDED FOR SEPTIC CONSTRUCTION PERMIT; 65.17 SITE EVALUATION; 65.24 SEPTIC CONSTRUCTION PERMIT TO BE ISSUED BY EH | 2021 | https://www.storycountyiowa.gov/DocumentCenter/View/11613/Signed-Ordinance-287
Iowa | Warren |  | County | 19181 | Definition: Well |  |  | "'Geothermal Heat Pump Well' means an excavation exceeding a 20-ft depth that is drilled, cased, bored, augured, washed, driven, dug, jetted, or otherwise constructed for the purpose of utilizing the geothermal properties of the ground." | 33.02 Definitions | 2021 | https://www.warrencountyia.gov/wp-content/uploads/2022/10/Chapter33.pdf
Iowa | Warren |  | County | 19181 | Permit |  |  | "Permit required. When obtaining a permit to install a geothermal heat pump system, the contractor or homeowner must apply for a permit within the Warren County Environmental Health Office prior to construction." | 33.04 Geothermal Heat Pump Wells | 2021 | https://www.warrencountyia.gov/wp-content/uploads/2022/10/Chapter33.pdf
Iowa | Crawford | Denison | City | 1919945 | Permit |  |  | "No groundwater heat pump may be installed without prior issuance of a permit issued by the Building Inspector." | 91.04 GROUNDWATER HEAT PUMPS. |  | https://codelibrary.amlegal.com/codes/denison/latest/denison_ia/0-0-0-2880
Iowa | Crawford | Denison | City | 1919945 | Other Prohibitions/Regulations |  |  | "This chapter does not prohibit the installation of self-contained groundwater heat pumps which do not inject materials into the surrounding soil or water." This clause expressly limits the allowed groundwater heat pump installations to self-contained systems that do not inject materials into surrounding soil or water. | 91.04 GROUNDWATER HEAT PUMPS. |  | https://codelibrary.amlegal.com/codes/denison/latest/denison_ia/0-0-0-2880
Iowa | Scott | Le Claire | City | 1944085 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | City | 1944085 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump System refers to a system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site. Closed Loop Ground Source Heat Pump System refers to a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | City | 1944085 | Setback - Property Lines | 5 | feet | "All components of Ground Source Heat Pump System including pumps, borings and loops shall be set back at least five (5) feet from interior and rear lot lines." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | City | 1944085 | Permit |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of the city's zoning ordinance." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | City | 1944085 | Decommissioning |  |  | "A Ground Source Heat Pump System that is allowed to remain in a nonfunctional or inoperative state for a period of twelve (12) consecutive months, and which is not brought in operation within the time specified by the city after notification to the owner or operator of the Ground Source Heat Pump System, shall be presumed abandoned and may be declared a public nuisance subject to removal at the expense of the operator." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | City | 1944085 | Open-loop Prohibitions |  |  | "Only closed loop Ground Source Heat Pump System utilizing Iowa Department of Public Health approved heat transfer fluids are permitted." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | City | 1944085 | Other Prohibitions/Regulations |  |  | "Ground Source Heat Pump System are prohibited in surface waters, except for storm water ponds where they are permitted." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa |  | Robins | City | 1967800 | Definition: Well |  |  | "Geothermal Borehole - A hole drilled or bored into the earth into which piping is inserted for use in a geothermal system." Also: "Well - any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed or is otherwise construction for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer." | 162.02 DEFINITIONS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Definition: Geothermal Heat Pump |  |  | "Geothermal System - A geothermal system uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also: "Geothermal System - A mechanism for heat exchange, which consists of the following basic elements: Underground loops of piping; heat transfer fluid; a heat pump; an air distribution system... The pipes form a 'closed loop' and are filled with a heat transfer fluid." | 162.02 DEFINITIONS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Permit |  |  | "No person shall dig, bore, drill, replace, modify, repair or destroy a geothermal well or any other excavation that may intersect ground water without first applying for and receiving a permit from the City of Robins, Iowa. A permit is required for all closed loop horizontal and closed loop vertical systems." Also: "All proposed well drillers must obtain a permit from the Linn County Health Department..." | 162.03 PERMIT REQUIRED; 162.08 WELL PERMITS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Inspection |  |  | "Geothermal piping systems shall be tested hydrostatically at one and one half times the maximum system design pressure, but not less than 100 psi (689 kPa). The duration of each test shall be not less than 15 minutes." Also: "All geothermal systems must be checked by a licensed geothermal contractor, every year from the certification system date. Results shall be submitted to the Community Development Department..." | 162.12 TESTING OF SYSTEM |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Licensed Driller |  |  | Supporting documents must include: "Certification of the well driller as required under Iowa Administrative Code 567-49 and 567-82." | 162.04 APPLICATION PROCEDURE |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Certification |  |  | The application must include "Certification of the well driller as required under Iowa Administrative Code 567-49 and 567-82." Section 162.08 also requires drillers to "conform to Chapter 149 of the Iowa Administrative Code Section 567-49.29(455B)." | 162.04 APPLICATION PROCEDURE; 162.08 WELL PERMITS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Decommissioning |  |  | "The procedure used for abandonment of geothermal systems must be the same as currently described in Chapter 39 of the Iowa Administrative Code for Plugging Abandoned Wells. The heat transfer fluid must be removed by a displacement with grout. The top of the borehole must be uncovered and capped with grout." | 162.14 ABANDONMENT OF GEOTHERMAL SYSTEMS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | City | 1967800 | Open-loop Prohibitions |  |  | "Due to the serious potential adverse environmental impact with open loop systems, open loop systems are prohibited." | 162.11 OPEN LOOP SYSTEMS PROHIBITED |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Spillville | City | 1974370 | Permit |  |  | "This chapter shall not apply to closed loop, vertical, geothermal heating and cooling loop fields. However, prior to the installation of the vertical loop field a city permit must be obtained. In order to receive a permit from the city, a map of the proposed loop must be provided along with a completed well installation permit signed by the county sanitarian or a member of the water supply section of the Iowa Department of Natural Resources authorized to provide water well installation permits." | 6-2-22 PRIVATE WELLS, 2.c |  | https://www.spillville.org/wp-content/uploads/2023/01/Spillville-2022-Code-of-Ordinances.pdf
Kansas | Decatur | Oberlin | City | 2003952000 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertically Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2024 | https://towncloud.io/go/oberlin-ks/agendas/652/pdf_packet/get_agenda_document_link
Kansas | Ellis | Ellis | City | 2005120450 | Permit |  |  | "It shall be unlawful to install, alter or reconstruct any plumbing or plumbing system, as defined by the plumbing code and section 4-301, in any building in the city without first making application to and receiving a permit therefor from the building inspector. The application for such permit shall be made and the permit obtained before any plumbing work is commenced." | 4-310. PLUMBING PERMIT REQUIRED; EXCEPTION | 2009 | https://ellis.ks.us/wp-content/uploads/2020/04/Ellis-City-Code-09.21.2009.pdf
Kansas | Ellis | Ellis | City | 2005120450 | Inspection |  |  | "Upon the completion of any plumbing work covered by this article, it shall be the duty of the person doing such work to notify the plumbing inspector and request that it be inspected." Also, when plumbing is to be concealed, "such equipment shall not be concealed until it has been inspected, approved or authorized by the plumbing inspector." The inspector may require concealed work to be opened, and "in no case shall the inspector issue a certificate of approval until satisfied that the work is in accordance with the provisions of this article." | 4-315. REQUEST FOR INSPECTION; 4-316. INSPECTION; CONCEALMENT OF PRIOR WORK; 4-318. CERTIFICATE OF APPROVAL | 2009 | https://ellis.ks.us/wp-content/uploads/2020/04/Ellis-City-Code-09.21.2009.pdf
Kansas | Ellis | Ellis | City | 2005120450 | Certification |  |  | "The contractor shall provide to the city clerk proof of passing the ICBO/Experior Exam." | 4-324(d). PLUMBER'S OR PLUMBING CONTRACTOR'S LICENSE REQUIRED; PLUMBING PERMITS; UNLAWFUL ACTS | 2009 | https://ellis.ks.us/wp-content/uploads/2020/04/Ellis-City-Code-09.21.2009.pdf
Kansas | Harvey | Newton | City | 2007950475 | Permit |  |  | "Any permit required by IMC shall be issued only to those persons who hold a current license from the City authorizing them to perform the type and nature of work described in the permit." The ordinance also states: "Any person, firm, or corporation who does any work without a permit or who fails to report permitted work as ready for inspection when completed shall pay a civil penalty as prescribed in Newton City Code 6-116." | 6-404. Permits, fees. | 2025 | https://newtonkansas.citycode.net/articleMechanicalCode.htm
Kansas | Harvey | Newton | City | 2007950475 | Inspection |  |  | The ordinance provides: "Any person, firm, or corporation who does any work without a permit or who fails to report permitted work as ready for inspection when completed shall pay a civil penalty as prescribed in Newton City Code 6-116." | 6-404. Permits, fees. | 2025 | https://newtonkansas.citycode.net/articleMechanicalCode.htm
Kansas | Johnson | Leawood | City | 2009139075 | Permit |  |  | "Any owner or authorized agent who intends to do work subject to this code ... or to erect, install, enlarge, alter, repair, remove, convert or replace any electrical, gas, mechanical, plumbing, or elevator system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." | 4-904. SECTION R105.1. PERMITS, REQUIRED | 2020 | https://www.leawood.org/DocumentCenter/View/375/2018-International-Residential-Code-Amendments-PDF
Kansas | Johnson | Leawood | City | 2009139075 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to framing inspection." Exception: "Back-filling of ground-source heat pump loop systems tested in accordance with Section M2105.28 prior to inspection shall be permitted." | 4-922. SECTION R109.1.3. PLUMBING, MECHANICAL, GAS AND ELECTRICAL SYSTEMS INSPECTION | 2020 | https://www.leawood.org/DocumentCenter/View/375/2018-International-Residential-Code-Amendments-PDF
Kansas | Johnson | Mission Hills | City | 2009147350 | Setback - Property Lines | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Setback - Building Foundation | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Setback - Water Lines | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Setback - Sewer Lines | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Permit |  |  | Vertical systems: "Prior to beginning any construction activity, the contractor must provide to the City Administrator or his or her designee ... (ii) a completed City permit application ..." Decommissioning: "A City permit is required prior to decommissioning a Closed Loop Geothermal Heat Pump System." | 5-130.1.E.2.(a); 5-130.1.F | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Inspection |  |  | "Before grouting or backfilling installed piping, the piping must be pressure tested with water at one hundred pounds per square inch (100 PSI) for at least one (1) hour with no leaks." | 5-130.1.E.1. Piping | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Licensed Driller |  |  | "Prior to beginning any construction activity, the contractor must provide to the City Administrator or his or her designee ... (i) a copy of the contractor's Kansas water well contractor's license ..." | 5-130.1.E.2.(a) Vertical Closed Loop Geothermal Heat Pump Systems | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Certification |  |  | "Prior to beginning any construction activity, the contractor must provide to the City Administrator or his or her designee ... (i) a copy of the contractor's Kansas water well contractor's license ..." | 5-130.1.E.2.(a) Vertical Closed Loop Geothermal Heat Pump Systems | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Decommissioning |  |  | "A City permit is required prior to decommissioning a Closed Loop Geothermal Heat Pump System. To decommission the Closed Loop Geothermal Heat Pump System, the heat transfer fluid must first be removed and properly disposed in accordance with KDHE regulations. After removal of the heat transfer fluid, the loop piping must be cut off five feet (5') below the surface, filled with grout mixture that has been approved by KDHE for this purpose, and sealed with a permanent fusion cap. Following these decommissioning procedures, the excavation site must be filled and leveled." | 5-130.1.F. Decommissioning | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | City | 2009147350 | Open-loop Prohibitions |  |  | "Closed Loop Geothermal Heat Pump Systems may be installed in any district in accordance with the provisions of this Section 5-130.1. Open Loop Geothermal Heat Pump Systems are prohibited in the City." | 5-130.1.B. Limitation | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Montgomery | Coffeyville | City | 2012514600 | Permit |  |  | "Any owner or authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical ... system, the installation of which is regulated by this Article ... shall first make application to the Building Official and shall obtain the required permit." Section 8-1-110 states the International Mechanical Code applies to "heating, cooling, air-conditioning and refrigeration systems, incinerators and other energy-related systems." | 8-1-138 PERMITS REQUIRED | 2025 | https://www.coffeyville.com/DocumentCenter/View/2950/Building-and-Construction-Code-Book?bidId=
Kansas | Montgomery | Coffeyville | City | 2012514600 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas, and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to framing inspection. Exception: Back-filling of ground-source heat pump loop systems tested in accordance with Section M2105 of the International Residential Code, as adopted by the City at Article 3 of this Chapter, as amended, prior to inspection shall be permitted." Related provisions also state: "All work for which a permit is required shall be subject to inspection" (8-1-177), "The Building Official, upon notification, shall make the inspections" (8-1-179), and "The final inspection shall be made after all work required by the building permit is completed" (8-1-190). | 8-1-182 PLUMBING, MECHANICAL, GAS AND ELECTRICAL SYSTEMS INSPECTION | 2025 | https://www.coffeyville.com/DocumentCenter/View/2950/Building-and-Construction-Code-Book?bidId=
Kansas | Stafford |  | County | 20185 | Definition: Geothermal |  |  | "RENEWABLE ENERGY : Shall include wind (CWEP), solar (CSEP), battery (CESS) & (BESS), photovoltaic, biomass, hydropower, geothermal and landfill gas resources or technologies." | Section 2-102 / Renewable Energy definition | 2026 | https://www.staffordcounty.org/uploads/1/3/3/6/133660997/updated_zoning_regulations_2026.pdf
Louisiana | Orleans | New Orleans | City | 2207198000 | Setback - Property Lines | 2 | feet | "Ground-based or wall-mounted mechanical equipment (with less than 7 feet of vertical clearance) including, but not limited to, heating, ventilating, geothermal energy, and air-conditioning (HVAC) units, swimming pool equipment, and back-up electrical generators, may be located in an interior side or rear yard and shall be located at least two (2) feet from the interior side or rear property line." | 21.6.T Mechanical Equipment | 2025 | https://czo.nola.gov/article-21/
Louisiana | Orleans | New Orleans | City | 2207198000 | Screening |  |  | "All approved ground-based mechanical equipment, including, but not limited to HVAC units, shall be screened when readily visible from the public right-of-way, excluding alleys. Screening materials may be masonry, wood, or landscape, and shall effectively screen mechanical equipment so no portion is readily visible from that public right-of-way. ... If ground-based mechanical equipment is screened by an existing structure, fence or landscape, such that it is not readily visible from that public right-of-way, it will be considered to have met these requirements." | 21.6.T Mechanical Equipment | 2025 | https://czo.nola.gov/article-21/
Maine | Androscoggin | Mechanic Falls | Town | 2300144585 | Permit |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | Definitions | 2005 | https://www.mechanicfalls.org/2024%200110%20PB%20Packet.pdf?t=202401041100500
Maine | Androscoggin | Minot | Town | 2300146160 | Permit |  |  | "Start of Construction - means the date the building permit was issued, provided the actual start of construction... was within 180 days of the permit date." | 14-101.2 Definitions | 2022 | https://minotme.org/vertical/Sites/%7B1666B81B-370A-463B-B8FB-32BAA0E22AAF%7D/uploads/2022_Land_Use_Code(1).pdf
Maine | Aroostook | Presque Isle | City | 2300360825 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C". | 41. Definitions | 2024 | https://presqueislemaine.gov/Document%20Center/Government/Ordinances/CHAPTER%2016A%20-Shoreland%20Zoning%2006-05-2024.pdf?t=202408121500510
Maine | Cumberland | Brunswick | Town | 2300508430 | Screening |  |  | "Accessory use geothermal energy collection facilities shall be located entirely underground, except that facilities connecting underground collection facilities to an aboveground structure are permitted provided: The facilities are located on a side or rear side of the building not abutting a public or private right-of-way unless screened by a vegetative buffer of at least 50 percent opacity at the time of installation, not to exceed six (6) feet in height." Also, "Primary use geothermal energy collection facilities shall be located entirely underground, except that aboveground monitoring and control equipment are permitted provided: ... The facilities are screened from view from adjacent public or private rights-of-way by a vegetative buffer of at least 50 percent opacity at the time of installation, not to exceed six (6) feet in height." | Chapter 3 - Property Use Standards Section 3.4 - Supplementary Use Standards, Geothermal Energy Collection Facilities | 2021 | https://evocloud-prod3-public.s3.us-east-2.amazonaws.com/meetings/47/attachments/4561.pdf
Maine | Cumberland | Chebeague Island | Town | 2300512300 | Permit |  |  | "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C)"; and "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure." | Section 108 Definitions; Section 502 Permits Required | 2018 | https://www.townofchebeagueisland.org/vertical/Sites/%7B984705D3-C709-4324-9040-19247D095968%7D/uploads/Shoreland_Zoning_Ord_eff_4-7-18.pdf
Maine | Cumberland | Freeport | Town | 2300526525 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | Chapter 76 Definitions / Structure | 2024 | https://www.freeportmaine.com/DocumentCenter/View/2553/05-28-24_chapter_65_shoreland_zoning_ordinance
Maine | Cumberland | Harpswell | Town | 2300531390 | Definition: Well |  |  | "A subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; a geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8 are not structures." | Structure | 2026 | https://www.harpswell.maine.gov/vertical/sites/%7B3F690C92-5208-4D62-BAFB-2559293F6CAE%7D/uploads/DEFINITIONS_March_14_2026.pdf
Maine | Cumberland | Long Island | Town | 2300541067 | Permit |  |  | Section 4.15(B)(1)(d) states the Code Enforcement Officer may issue "a permit to place a single accessory structure" in a setback area. Section 4.17 defines "Structure" and expressly excludes "geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C" from that term: "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | 4.15 B. Principal and Accessory Structures / 4.17 Definitions | 2021 | https://townoflongisland.us/wp/wp-content/uploads/2021/05/Chapter-14-Land-Use-Ordinance.pdf
Maine | Cumberland | Pownal | Town | 2300560685 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur..." and "Any permit required by this Ordinance shall be in addition to any other permit required by other law or ordinance." | SECTION 16. Administration; B. Permits Required | 2021 | https://www.pownalmaine.org/vertical/sites/%7BE22E4F8E-90D9-49E3-A5FC-00AC79420AA6%7D/uploads/2021_Ordinance_Amendment_Packet.pdf
Maine | Cumberland | Pownal | Town | 2300560685 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | SECTION 16. I. Enforcement; 2. Code Enforcement Officer | 2021 | https://www.pownalmaine.org/vertical/sites/%7BE22E4F8E-90D9-49E3-A5FC-00AC79420AA6%7D/uploads/2021_Ordinance_Amendment_Packet.pdf
Maine | Cumberland | Raymond | Town | 2300561945 | Definition: Geothermal Heat Pump |  |  | "Structure - Anything built for the support, shelter, or enclosure of persons, animals, goods, or property of any kind, together with anything constructed or erected with a fixed location on or in the ground, exclusive of vegetation, boundary walls, fences, mailboxes, lampposts, birdhouses, doghouses, tree houses designed for children's use, bus shelters, subsurface wastewater disposal systems as defined in Title 30-A, § 4201, subsection 5, geothermal heat exchange wells as defined in Title 32, § 4700-E, subsection 3-C, wells or water wells as defined in Title 32, § 4700-E, subsection 8, or other similar construction." | ARTICLE 3 - DEFINITIONS | 2025 | https://www.raymondmaine.gov/uploads/subdivision-ordinance-2025.pdf
Maine | Cumberland | Scarborough | Town | 2300566145 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | Section 17. Definitions, Structure | 2025 | https://resources.finalsite.net/images/v1748353098/scarboroughmaineorg/yfkwzbiilgg6qrpau4mv/405C-Shoreland-Zoning-Ordinance.pdf
Maine | Cumberland | Scarborough | Town | 2300566145 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure; or renew a discontinued nonconforming use." | Section 16. Administration, B. Permits Required | 2025 | https://resources.finalsite.net/images/v1748353098/scarboroughmaineorg/yfkwzbiilgg6qrpau4mv/405C-Shoreland-Zoning-Ordinance.pdf
Maine | Cumberland | Scarborough | Town | 2300566145 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | Section 16. Administration, H. Enforcement, 2.b | 2025 | https://resources.finalsite.net/images/v1748353098/scarboroughmaineorg/yfkwzbiilgg6qrpau4mv/405C-Shoreland-Zoning-Ordinance.pdf
Maine | Cumberland | South Portland | City | 2300571990 | Permit |  |  | "The City hereby adopts ... the International Energy Conservation Code ... (the 'Stretch Energy Code') as the energy conservation and efficiency requirements for the City..." and "the requirements of this Division shall become applicable April 1, 2022 to any project that is not a 'Protected Project.'" | Sec. 5-169A. International Energy Conservation Code Adopted | 2025 | https://www.southportland.gov/DocumentCenter/View/1421/Ch-05-Buildings
Maine | Cumberland | Windham | Town | 2300586025 | Definition: Well |  |  | "'Structure' does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface wastewater disposal systems as defined in 30-A M.R.S.A. § 4201, Subsection 5; geothermal heat exchange wells as defined in 32 M.R.S.A. § 4700-E, Subsection 3-C; or wells or water wells as defined in 32 M.R.S.A. § 4700-E, Subsection 8." | § 185-17 Definitions | 2024 | https://ecode360.com/37098623
Maine | Cumberland | Windham | Town | 2300586025 | Permit |  |  | "Permits required. After the effective date of this chapter, no person shall, without first obtaining a permit or site plan approval, as applicable, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur..." and "Any permit required by this chapter shall be in addition to any other permit required by other law or ordinance." | § 185-16 Administration / Permits required | 2024 | https://ecode360.com/37098623
Maine | Cumberland | Windham | Town | 2300586025 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | § 185-16 Administration / Enforcement / Code Enforcement Officer | 2024 | https://ecode360.com/37098623
Maine | Franklin | Farmington | Town | 2300724775 | Permit |  |  | The ordinance refers to "conditions attached to permit approvals" and states that an "application fee" must accompany "the application," with appeal rights for an applicant dissatisfied with a Planning Board decision: "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." Also, "A non-refundable application fee of fifty ($50.00) dollars shall be paid to the Town Clerk and a copy of a receipt for the same shall accompany the application." | I. Enforcement, 2.b; 11-1.18 Fees | 2016 | https://farmington-maine.org/files/Ordinances%20and%20Policies/Shoreland_Zoning_Ordinance_07012018_.pdf
Maine | Franklin | Farmington | Town | 2300724775 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement, 2.b | 2016 | https://farmington-maine.org/files/Ordinances%20and%20Policies/Shoreland_Zoning_Ordinance_07012018_.pdf
Maine | Franklin | Rangeley | Town | 2300761840 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, Section 4700-E, subsection 3-C". | Section 38.13 Definitions | 2020 | https://www.townofrangeley.com/DocumentCenter/View/1672/Chapter-38-FINAL-DRAFT-051421
Maine | Hancock | Bar Harbor | Town | 2300902865 | Permit |  |  | "If it is determined, based on the Federal Emergency Management Agency's Flood Boundary and Floodway Maps and Flood Insurance Rate Maps and information presented by the applicant, that the proposed development, or any part of it, is in a flood-prone area, the site plan shall not be approved until the applicant has obtained a Flood Hazard Development Permit pursuant to Chapter 90, Floodplain Management, of the Bar Harbor Code." | Flood permit | 2025 | https://ecode360.com/8374632
Maine | Hancock | Cranberry Isles | Town | 2300914905 | Definition: Well |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | 18. Definitions | 2020 | https://www.cranberryisles-me.gov/wp-content/uploads/2021/02/Land-Use-Shoreland-Zoning-Ordinance-October-1-2020.pdf
Maine | Hancock | Mount Desert | Town | 2300947630 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S. §4700-E.3-C ..." | Section 8 Definitions - Structure | 2026 | https://www.mtdesert.org/DocumentCenter/View/503/Subdivision-Ordinance-PDF
Maine | Hancock | Surry | Town | 2300975280 | Permit |  |  | The ordinance expressly recognizes "geothermal heat exchange wells" in the definition of Structure: "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C... Setback requirements apply to structures." The Land Use Table also states that "For any proposed activity or use not specifically listed in the Land Use Table, the CEO will determine the permissibility and the permitting authority for such an activity or use, using the existing table for guidance." | Chapter 3, Unified Development Ordinance, Chapter 2 Definitions / Chapter 3 Section II Land Use Table 1 | 2025 | https://cms8.revize.com/revize/surryme/Conservation%20Commission/Surry%20Code%20of%20Ordinances%20v7.0%204-16-2026.pdf
Maine | Hancock | Tremont | Town | 2300977345 | Permit |  |  | "No building, structure or land shall hereafter be used or occupied; no building or structure or part thereof shall hereafter be erected, constructed, expanded, moved, altered to change the use, or demolished... except in conformity with all of the regulations herein specified... A permit shall be obtained from the Code Enforcement officer after approval of the appropriate review authority." In Article XI, "Structure does not include... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | ARTICLE VIII, PERMIT APPLICATION AND REVIEW PROCEDURE; ARTICLE VIII.A. Permit Applicability | 2022 | https://webgen1files1.revize.com/townoftremontma/LAND%20USE%20ORDINANCE%20FINAL%202025-05-13.pdf
Maine | Hancock | Trenton | Town | 2300977415 | Definition: Geothermal Heat Pump |  |  | "Structure – anything temporarily or permanently located, built, constructed or erected for the support, shelter or enclosure of persons, animals, goods or property of any kind or anything constructed or erected on or in the ground. ... Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | 70. Definitions | 2020 | https://www.trentonme.com/images/pdf/Trenton%20Shoreland%20Zoning.pdf
Maine | Kennebec | Benton | Town | 2301104475 | Definition: Well |  |  | "Structure does not include fences, signs, power poles and wiring, and subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; and wells or water wells as defined in Title 32, section 4700-E, subsection 8." | Section II: Definitions Terms Used in this Ordinance | 2022 | https://www.bentonmaine.info/sites/g/files/vyhlif6671/f/uploads/land_use_ordinance_revision_march_2022_5.pdf
Maine | Kennebec | Benton | Town | 2301104475 | Permit |  |  | "A Permit shall be obtained prior to the commencement of construction or placement of any structure within the Town of Benton..." and "1. Land Use Permit: This permit is required for the erection, alteration, rebuilding, repair, remodel, enlargement, or relocation of any proposed or existing building..." The ordinance also states in the definitions that a "Structure" "does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | Section III: Administration, Enforcement and Fees, C. Permit Requirements | 2022 | https://www.bentonmaine.info/sites/g/files/vyhlif6671/f/uploads/land_use_ordinance_revision_march_2022_5.pdf
Maine | Kennebec | Benton | Town | 2301104475 | Inspection |  |  | The Code Enforcement Officer shall "Conduct inspections as frequently as may be necessary to insure compliance with Town Ordinances and State laws." | Section III: Administration, Enforcement and Fees, E. Code Enforcement Officer (CEO) | 2022 | https://www.bentonmaine.info/sites/g/files/vyhlif6671/f/uploads/land_use_ordinance_revision_march_2022_5.pdf
Maine | Kennebec | Fayette | Town | 2301124950 | Definition: Well |  |  | "Structure - anything temporarily or permanently located, built, constructed, or erected ... exclusive of subsurface waste water disposal systems (as defined in 30-A M.R.S. §4201, sub-§5), geothermal heat exchange wells (as defined in 32 M.R.S. 470-E, sub-§ 3-C), or water wells (as defined in 32 M.R.S. §4700-E, sub-§ 8) ..." | ARTICLE XI. DEFINITIONS | 2024 | https://fayettemaine.org/uploads/2024-town-of-fayette-land-use-ordinance.pdf
Maine | Kennebec | Hallowell | City | 2301130550 | Definition: Geothermal Heat Pump |  |  | "Structure does not include patios, fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in 30-A M.R.S. § 4201(5); geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C); or wells or water wells as defined in 32 M.R.S. § 4700-E(8)." | Section 9.99 | 2021 | https://hallowell.govoffice.com/vertical/sites/%7B9B342949-3E79-4064-B52A-92C27ED57113%7D/uploads/2025.07.07_Item_11.3_-_Affordable_Housing_-_Full_Mark-up.pdf
Maine | Kennebec | Litchfield | Town | 2301140175 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | SECTION 7 Definitions | 2022 | http://www.litchfieldmaine.org/wp-content/uploads/SHORELAND-ZONE-ORDINANCE-2022-2.pdf
Maine | Kennebec | Mount Vernon | Town | 2301147770 | Permit |  |  | The ordinance key states: 'Yes: Allowed (no permit required but the use must comply with all applicable land use standards)'; 'PB: Requires approval by the Planning Board prior to the CEO issuing a permit'; 'CEO: Requires permit issued by the Code Enforcement Officer'; 'LPI: Requires permit issued by the Local Plumbing Inspector'; 'BI: Requires permit from the Building Inspector.' The text also defines geothermal-related scope in the 'Structure' definition by excluding 'geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C).' | Table 4-1 and Table 4-2 / Key to Table 4-1 and Table 4-2 | 2022 | https://webgen1files1.revize.com/thetownofmountvernonme/Mt_Vernon_LUO_4-5-2023.pdf
Maine | Kennebec | Winthrop | Town | 2301186970 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure." | 109. Administration B. Permits Required | 2024 | https://www.winthropmaine.gov/DocumentCenter/View/398/Zoning-Ordinance-March-18-2019-amended-February-2-2026
Maine | Kennebec | Winthrop | Town | 2301186970 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | 109. Administration J. Enforcement (2)(b) | 2024 | https://www.winthropmaine.gov/DocumentCenter/View/398/Zoning-Ordinance-March-18-2019-amended-February-2-2026
Maine | Knox | North Haven | Town | 2301351620 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure; or renew a discontinued nonconforming use." | 16. Administration; B. Permits Required | 2023 | https://www.northhavenmaine.org/Shoreland%20Zone%20Ordinance%20for%20the%20Municipality%20of%20North%20Haven%20Enacted%20November%2020,%202023.pdf?t=202311201110110
Maine | Knox | North Haven | Town | 2301351620 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | 16. Administration; I. Enforcement; (2)(b) | 2023 | https://www.northhavenmaine.org/Shoreland%20Zone%20Ordinance%20for%20the%20Municipality%20of%20North%20Haven%20Enacted%20November%2020,%202023.pdf?t=202311201110110
Maine | Knox | Owls Head | Town | 2301356135 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles; wiring, guy wires, guy anchors and other aerial equipment normally associated with service drops; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; and wells or water wells as defined in Title 32, section 4700-E, subsection 8." | 17. Definitions | 2024 | https://webgen1files1.revize.com/owlsheadme/Final%20PH%202024%20Shoreland%20Zoning%20Ordinance%2042624.pdf
Maine | Knox | Owls Head | Town | 2301356135 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement; (2) Code Enforcement Officer | 2024 | https://webgen1files1.revize.com/owlsheadme/Final%20PH%202024%20Shoreland%20Zoning%20Ordinance%2042624.pdf
Maine | Knox | Rockport | Town | 2301363660 | Inspection |  |  | "The Certificate of Occupancy shall be based on inspections by the Code Officer or Third-Party Inspector, Plumbing Inspector, and Fire Chief or their designee, to ensure that the structure conforms with the Plumbing Code, National Fire Protection Life Safety Code, the Maine Uniform Building and Energy Code (MUBEC), and the Rockport Land Use Ordinance." | CHAPTER 600 - ADMINISTRATION; § 603 Certificates of Occupancy | 2026 | https://rockportmaine.gov/uploads/dm/10693/Land_Use_Ordinance__June_9_2026.pdf
Maine | Knox | South Thomaston | Town | 2301372585 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement (2) Code Enforcement Officer | 2024 | https://souththomaston.me/wp-content/uploads/2025/01/shoreland-signed-attested-june-2024.pdf
Maine | Knox | Thomaston | Town | 2301376365 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface wastewater disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32. section 4700-E, subsection 8." | Structure | 2026 | https://thomastonmaine.gov/vertical/sites/%7B96E8F1E7-2E12-4DA6-B00A-A7D31940B917%7D/uploads/2026_LUO_June_10_FINAL.pdf
Maine | Lincoln | Bremen | Town | 2301506855 | Definition: Geothermal Heat Pump |  |  | "Structure does not include subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | STRUCTURE | 2022 | http://www.bremenmaine.org/wp-content/uploads/2024/03/3-22-24-Revised-Land-Use-Ordinance.pdf
Maine | Lincoln | Newcastle | Town | 2301548645 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | IV. DEFINITIONS | 2024 | https://www.newcastlemaine.us/sites/g/files/vyhlif6211/f/uploads/shoreland_ordinance_2024.12.10.pdf
Maine | Lincoln | Wiscasset | Town | 2301587075 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | 1.16 Definitions | 2024 | https://www.wiscasset.gov/DocumentCenter/View/204/June-2024-Ordinance-Book-PDF
Maine | Oxford | Fryeburg | Town | 2301726910 | Definition: Well |  |  | "Structure: Anything built, constructed or erected on or in the ground... Structures do not include ... geothermal heat exchange wells as defined in Title 32, Section 4700-E subsection 3-c, or wells or water wells as defined in Title 32, Section 4700-E subsection 8." | Section 25 Definitions and Word Usage, B. Definitions | 2024 | https://www.fryeburgmaine.org/DocumentCenter/View/260/Land-Use-Ordinance
Maine | Oxford | Otisfield | Town | 2301755960 | Definition: Well |  |  | "Structure does not include fences, poles and wiring, and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | STRUCTURE-SHORELAND ZONE | 2017 | https://otisfieldme.gov/DocumentCenter/View/961/Definitions-for-the-Town-of-Otisfields-Ordinances
Maine | Oxford | Peru | Town | 2301758270 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur..." and "Any permit required by this Ordinance shall be in addition to any other permit required by other law or ordinance." | 16.B. Permits Required | 2018 | https://townofperumaine.org/wp-content/uploads/2021/06/Town-of-Peru-Shoreland-Zoning-Ordinance-Rev19Mar2018.pdf
Maine | Oxford | Peru | Town | 2301758270 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | 16.I(2)(b) Code Enforcement Officer | 2018 | https://townofperumaine.org/wp-content/uploads/2021/06/Town-of-Peru-Shoreland-Zoning-Ordinance-Rev19Mar2018.pdf
Maine | Oxford | Sweden | Town | 2301775595 | Definition: Well |  |  | In the definition of "Structure," the ordinance states: "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | XV. DEFINITIONS |  | https://swedenmaine.org/wp-content/uploads/2024/01/Sweden-Zoning-Ord-draft_2024-1-18_CLEAN-Indesign2.pdf
Maine | Oxford | Sweden | Town | 2301775595 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | XII.F.2.b. On-site Inspections |  | https://swedenmaine.org/wp-content/uploads/2024/01/Sweden-Zoning-Ord-draft_2024-1-18_CLEAN-Indesign2.pdf
Maine | Penobscot | Dixmont | Town | 2301917950 | Definition: Well |  |  | "Structure does not include fences; poles; wiring, guy wires, guy anchors and other aerial equipment normally associated with service drops; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; and wells or water wells as defined in Title 32, section 4700-E, subsection 8." | Definitions - Structure | 2016 | https://storage.googleapis.com/dixmont-media-dixmont/planning-board/ordinances/Dixmont_Shoreland_Zoning_Ordinance_Attested.pdf
Maine | Penobscot | Dixmont | Town | 2301917950 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | Section 16(I)(2)(b) | 2016 | https://storage.googleapis.com/dixmont-media-dixmont/planning-board/ordinances/Dixmont_Shoreland_Zoning_Ordinance_Attested.pdf
Maine | Penobscot | Enfield | Town | 2301923620 | Permit |  |  | The ordinance defines "Structure" to include "geothermal heat exchange wells as defined in Title 32, Section 4700-E, Subsection 3-C." Table 1 states "Structures accessory to allowed uses" require approval in shoreland districts: "PB" in Spring Protection and Resource Protection, "CEO" in Limited Residential and Limited Resource Lot, and "Yes" in General Development. | DEPARTMENT OF ENVIRONMENTAL PROTECTION TABLE 1 - LAND USES IN THE SHORELAND ZONE | 2017 | https://a.storyblok.com/f/63995/x/5e37863366/enfiled_shoreland_zoning_2017.pdf
Maine | Penobscot | Howland | Town | 2301934190 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure..." and "Any permit required by this Ordinance shall be in addition to any other permit required by other law or ordinance." | Section 2691(3) B. Permits Required | 2018 | https://storage.googleapis.com/juniper-media-library/158/2024/10/Shoreland-Zoning-Amended.pdf
Maine | Penobscot | Howland | Town | 2301934190 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | Section 2691(3) I(2)(b) Code Enforcement Officer | 2018 | https://storage.googleapis.com/juniper-media-library/158/2024/10/Shoreland-Zoning-Amended.pdf
Maine | Penobscot | Lincoln | Town | 2301939475 | Permit |  |  | The ordinance defines a geothermal-related eligible improvement only within the PACE financing program: '"Renewable energy installation" means a fixture, product, system, device, or interacting group of devices ... that produces energy or heat from renewable resources, including ... geothermal systems....' It then establishes 'a PACE program allowing owners of qualifying property ... to access financing for energy saving improvements ... through PACE loans administered by the Trust,' and states that 'the Trust will enter into PACE agreements with owners of qualifying property.' | 2008.2.2.10; 2008.3.1; 2008.5.1.A | 2025 | https://www.lincolnmaine.org/wp-content/uploads/2025/12/Code-Master-December-2025.pdf
Maine | Piscataquis | Greenville | Town | 2302129535 | Definition: Well |  |  | Within the shoreland zone, the ordinance states that 'Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C.' | ## Structure - | 2025 | https://greenvilleme.gov/wp-content/uploads/Greenville-Land-Use-Ordinance-9.17.2025-edit-9.18.2025.pdf
Maine | Sagadahoc | Phippsburg | Town | 2302358515 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface wastewater disposal systems as defined in Title 30-A, Section 4201, Subsection 5; geothermal heat exchange wells as defined in Title 32, Section 4700-E, Subsection 3-C; or wells or water wells as defined in Title 32, Section 4700-E, Subsection 8." | Section 18. Definitions | 2025 | https://phippsburg.com/vertical/sites/%7B80D70921-4572-4200-8876-61A701FD14B2%7D/uploads/Shoreland_Zoning_Ordinance_(2025).pdf
Maine | Sagadahoc | Phippsburg | Town | 2302358515 | Permit |  |  | Section 16(A)(1): "It shall be unlawful to construct, add to, alter or to commence the construction, addition, or alteration of a building, mobile home, or structure where the value of such construction or addition exceeds one thousand ($1,000) dollars without first filing with the Codes Enforcement Officer an application in writing and obtaining a permit, therefor." Section 17(B)(20): "After the effective date of this Ordinance no person shall, without first obtaining a permit from the Codes Enforcement Officer or the Planning Board, as appropriate, engage in any activity, use of land, or structure requiring a permit in the district in which such activity or use would occur..." The definitions section states: "Structure does not include... geothermal heat exchange wells as defined in Title 32, Section 4700-E, Subsection 3-C." | Section 16. General Building Requirements A. Permits Required; Section 17. Administration B. Permits Required | 2025 | https://phippsburg.com/vertical/sites/%7B80D70921-4572-4200-8876-61A701FD14B2%7D/uploads/Shoreland_Zoning_Ordinance_(2025).pdf
Maine | Sagadahoc | Phippsburg | Town | 2302358515 | Inspection |  |  | "The Codes Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | Section 17. Administration I. Enforcement 44(b) | 2025 | https://phippsburg.com/vertical/sites/%7B80D70921-4572-4200-8876-61A701FD14B2%7D/uploads/Shoreland_Zoning_Ordinance_(2025).pdf
Maine | Somerset | Norridgewock | Town | 2302549835 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | 17. DEFINITIONS |  | https://www.norridgewock.gov/DocumentCenter/View/441/Proposed-ordinance-PDF
Maine | Somerset | Norridgewock | Town | 2302549835 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. ENFORCEMENT; (2) Code Enforcement Officer |  | https://www.norridgewock.gov/DocumentCenter/View/441/Proposed-ordinance-PDF
Maine | Somerset | Solon | Town | 2302569505 | Permit |  |  | "Prior to the construction or placement of any structure, accessory, or principal, over two hundred (200) square feet in size, or an addition which exceeds one hundred (100) square feet, the landowner or designated agent is responsible for applying for and obtaining a Building Permit from the Town." The Definitions section also states: "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C)." | SECTION II: PERMIT & APPLICATION, 1. PERMIT REQUIREMENT | 2024 | https://solon.maine.gov/uploads/2024.01-building-ordinance-replaces-2003.01-07-23-24-.pdf
Maine | Waldo | Lincolnville | Town | 2302739755 | Definition: Well |  |  | "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S.A. § 4700-E(3-C) ..." | SECTION 22 - DEFINITIONS | 2023 | https://lincolnvilleme.govoffice3.com/vertical/Sites/%7B0EE09280-1571-4126-B77C-44B66AF5BC58%7D/uploads/Land_Use_Ordinance_as_Amended_June_15_2023.pdf
Maine | Washington | Calais | City | 2302909585 | Inspection |  |  | The ordinance states the Code Enforcement Officer has authority for the "Inspection of each property in the Area to determine whether the property is in compliance" and for "Review and inspection of the rehabilitation of properties at various stages of completion to ensure that the same is conducted and completed in accordance with any approved designs or plans and the requirements of this Ordinance." | SECTION 3. ADMINISTRATION AND ENFORCEMENT / 3.2. Powers and Duties | 2017 | https://storage.googleapis.com/juniper-media-library/63/2024/01/LAND-USE-CODES-July-2017-amendments-2021.pdf
Maine | Washington | Cherryfield | Town | 2302912455 | Definition: Well |  |  | Within the shoreland-zone definition of “Structure,” the ordinance states: '“Structure” includes structures temporarily or permanently located, such as parking lots, decks, patios, and satellite dishes. This definition does not include ... geothermal heat exchange wells as defined in 32 M.R.S.A. § 4700-E(3-C) ...' | Section VI-3. Definitions | 2025 | http://www.cherryfieldmaine.us/wp-content/uploads/2025/12/LUO_2025.pdf
Maine | Washington | Cherryfield | Town | 2302912455 | Inspection |  |  | The ordinance states: 'The CEO may conduct site inspections to ensure compliance with all applicable laws and all terms and conditions attached to permits and approvals under this Ordinance.' It also states for projects with performance guarantees: 'the permit holder must deposit in escrow with the Town funds to cover the costs of site inspections to be conducted by an engineer mutually acceptable to the permit holder and the Planning Board,' and 'If the inspector finds, upon inspection ... that any of the site infrastructure or work has not been done in accordance with the plans ... the inspector must so report...' | Section VII-8.C. Inspections; Investigation of Complaints; Section VII-9.E. Inspections | 2025 | http://www.cherryfieldmaine.us/wp-content/uploads/2025/12/LUO_2025.pdf
Maine | Washington | Cherryfield | Town | 2302912455 | Decommissioning |  |  | For projects where a performance guarantee is required, the ordinance provides that the guarantee must cover 'decommissioning of any facilities or infrastructure associated with the proposal.' It further states: 'For reclamation and decommissioning work, the permit holder must arrange for the costs to be recalculated by an engineer every five years,' the guarantee must include a schedule for 'decommissioning work,' escrow must be provided for inspections before 'commencing any ... decommissioning work,' and before release of the guarantee 'the inspector must certify ... that all required ... decommissioning work has been satisfactorily completed.' | Section VII-9.C. Scope; Amount; Section VII-9.D. Schedule; Section VII-9.E. Inspections | 2025 | http://www.cherryfieldmaine.us/wp-content/uploads/2025/12/LUO_2025.pdf
Maine | York | Limerick | Town | 2303139195 | Permit |  |  | Article II defines "Structure" to exclude "H. Geothermal heat exchange wells as defined in 32 M.R.S.A. §4700-E, Subsection 3-C." In the Land Use Chart note, "* - Definition provided in Article II. ... Requires permit from Selectmen." Government/Municipal Facilities* are listed as a permitted use in all districts. | Article II - Definitions / Article V - District Regulations | 2022 | https://0201.nccdn.net/1_2/000/000/143/c85/zoningordinance_march2022.pdf
Maine | York | Lyman | Town | 2303141750 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C". | 17. Definitions; Structure | 2021 | https://lyman-me.gov/wp-content/uploads/2022/05/Shoreland-zoning-ordinance-amended-06-08-2021.pdf
Maine | York | Lyman | Town | 2303141750 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement; (2) Code Enforcement Officer; (b) | 2021 | https://lyman-me.gov/wp-content/uploads/2022/05/Shoreland-zoning-ordinance-amended-06-08-2021.pdf
Maine | York | Saco | City | 2303164675 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | Structure | 2021 | https://ecode360.com/SA1647/laws/LF1294073.pdf
Maryland | Anne Arundel |  | County | 24003 | Definition: Geothermal Heat Pump |  |  | "In this section, 'geothermal energy device' means a heating or cooling device that is installed using ground loop technology." | § 4-2-310. Geothermal energy | 2020 | https://codelibrary.amlegal.com/codes/annearundel/latest/annearundelco_md/0-0-0-151648
Maryland | Baltimore |  | County | 24005 | Definition: Geothermal Heat Pump |  |  | 'Geothermal energy device' means an energy device that: (a) Uses geothermal energy to heat or cool a structure or to provide hot water for use in the structure; and (b) Meets national safety and performance standards set by a nationally recognized testing laboratory for that type of device. | .01 Definitions | 2014 | https://www.baltimorecountymd.gov/files/Documents/Law/COBAR/cobarenergyconservdeviceschapter5.pdf
Maryland | Baltimore |  | County | 24005 | Permit |  |  | The applicant shall provide copies of: '(1) Receipts of all expenses paid for the purchase and installation of the energy conservation device or system; and (2) Any electrical, plumbing or other permits required by the county for the installation of the energy conservation device or system.' | .03 Administration | 2014 | https://www.baltimorecountymd.gov/files/Documents/Law/COBAR/cobarenergyconservdeviceschapter5.pdf
Maryland | Baltimore | 5 | District | 2400590380 | Definition: Geothermal Heat Pump |  |  | Table 408.3 includes the term: "GROUND SOURCE HEAT PUMP (GREATER THAN OR EQUAL TO 3.5 COP GROUND SOURCE HEAT PUMP.)" with a "6%" percentage increase for Climate Zone 4. | SECTION R408.3 MARYLAND ALTERNATIVE ADDITIONAL EFFICIENCY PACKAGE OPTIONS; TABLE 408.3 ADDITIONAL ENERGY FEATURES | 2024 | https://mgaleg.maryland.gov/pubs/LegisLegal/County-Legislation/2025-Baltimore-County-49-24.pdf
Maryland | Cecil | 5, North East | District | 2401590396 | Permit |  |  | "The Town of North East may issue a building permit or other approval to authorize a non-water dependent project for a smallscale renewable energy system on a pier located on State or private wetlands within the Critical Area if the project: (a) Involves the installation or placement of a small-scale renewable energy system ..." and "(iv) A closed-loop geothermal heat exchanger under a pier if the geothermal heat exchanger or any associated devices or equipment do not: (A) Extend beyond the length, width, or channelward encroachment of the pier; (B) Deleteriously alter longshore drift; or (C) Cause significant individual or cumulative thermal impacts to aquatic resources." | Section 5-12, §9(l)(3) | 2025 | https://www.northeastmd.org/wp-content/uploads/2026/02/ARTICLE-05-PART-I-II-NEZO.pdf
Maryland | Cecil | 7, Port Deposit | District | 2401590580 | Noise Limits | 70 | dBA | "Air-conditioning and heat-pump equipment used to cool or heat housing on residential property may not exceed 70 decibels for air-conditioning units and 75 decibels for heat pumps." | 3-1.8 Noise, f. Exceptions, E. | 2019 | https://www.portdeposit.org/_files/ugd/94e3df_060154c3d0264171aad225d951e0f363.pdf
Maryland | Frederick |  | County | 24021 | Definition: Geothermal |  |  | "The following improvements, either new or replacement, to commercial properties qualify as energy efficiency projects or renewable energy projects under the Clean Energy Loan Program: ... (2) Geothermal energy devices" | § 1-8-454 QUALIFYING IMPROVEMENTS AND COSTS | 2016 | https://www.frederickcountymd.gov/DocumentCenter/View/373451/2016---Bill-No-16-17---Establishing-a-Clean-Energy-Loan-Program-for-Commercial-Properties
Maryland | Harford |  | County | 24025 | Definition: Geothermal Heat Pump |  |  | "Nonwater-dependent projects include: ... (5) A small-scale renewable energy system on a pier, including: ... (b) A geothermal energy system and its geothermal heat exchanger or other necessary equipment." | NONWATER-DEPENDENT PROJECT | 2024 | https://ecode360.com/9375535
Maryland | Montgomery | 2 | District | 2403190152 | Definition: Geothermal |  |  | "Geothermal energy device" means a device that: "(1) uses geothermal energy to heat or cool a structure, to provide hot water for use in the structure, or to generate electricity to be used in the structure; and (2) meets safety and performance standards set by a nationally recognized testing laboratory for that kind of device." | 52-18R(a) Definitions | 2009 | https://assets.montgomerycountymd.gov/files/20090313_2-09.pdf
Maryland | Montgomery | 2 | District | 2403190152 | Certification |  |  | An application must "include a certification from the Department of Permitting Services indicating that the device for which the credit is sought: (i) is a solar or geothermal energy device; and (ii) has been properly installed. The Department of Permitting Services must accept a certification by another government agency, including a municipality, that the device has been properly installed." | 52-18R(d) Application | 2009 | https://assets.montgomerycountymd.gov/files/20090313_2-09.pdf
Maryland | Montgomery | 11 | District | 2403190976 | Definition: Geothermal Heat Pump |  |  | "Geothermal energy device means a device that: (1) uses geothermal energy to heat or cool a structure, to provide hot water for use in the structure, or to generate electricity to be used in the structure; and (2) meets safety and performance standards set by a nationally recognized testing laboratory for that kind of device." | Sec. 52-104. Property tax credit — renewable energy. | 2023 | https://codelibrary.amlegal.com/codes/montgomerycounty/latest/montgomeryco_md/0-0-0-152134
Maryland | Montgomery | 11 | District | 2403190976 | Permit |  |  | "An application must ... include a certification from the Department of Permitting Services, indicating that the device for which the credit is sought: (i) is a solar or geothermal energy device; and (ii) has been properly installed." | Sec. 52-104(f) Application. | 2023 | https://codelibrary.amlegal.com/codes/montgomerycounty/latest/montgomeryco_md/0-0-0-152134
Maryland | Montgomery | 11 | District | 2403190976 | Inspection |  |  | "An application must ... include a certification from the Department of Permitting Services, indicating that the device for which the credit is sought ... has been properly installed." Also, "The Department of Permitting Services must accept a certification by another government agency, including a municipality, that the device has been properly installed." | Sec. 52-104(f) Application. | 2023 | https://codelibrary.amlegal.com/codes/montgomerycounty/latest/montgomeryco_md/0-0-0-152134
Maryland | Prince George's |  | County | 24033 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy Device" means an energy conserving device that: (i) uses geothermal energy to heat or cool a structure or to provide hot water for use in the structure; and (ii) meets national safety and performance standards set by a nationally recognized testing laboratory for that kind of device. | Sec. 10-235.06(b)(2) | 2008 | https://www.princegeorgescountymd.gov/sites/default/files/media-document/dcv2184.pdf
Maryland | Talbot | 2, St. Michaels | District | 2404190172 | Permit |  |  | "The Town may issue a building permit or other approval to authorize a non-water dependent project for a small-scale renewable energy system on a pier located on State or private wetlands within the Critical Area if the project..." includes "(d) A closed-loop geothermal heat exchanger under a pier if the geothermal heat exchanger or any associated devices or equipment do not: 1) extend beyond the length, width, or channelward encroachment of the pier; 2) deleteriously alter longshore drift; or 3) cause significant individual or cumulative thermal impacts to aquatic resources." | § 340-29.C. Non-water dependent project for a small-scale renewable energy system on a pier | 2020 | https://dnr.maryland.gov/criticalarea/Documents/06b_StMichaelsZoningOrdinance_Attachment2.pdf
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Definition: Well |  |  | "Well- Any hole or shaft constructed into the ground for the purpose of injecting or extracting water and other fluids, or to monitor groundwater levels and water quality." | SECTION (1) DEFINITIONS | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Definition: Geothermal Heat Pump |  |  | "Groundwater Heat Pump- A refrigeration system which can heat or cool a dwelling which operates by exchanging heat with the groundwater. The groundwater can be supplied by either a closed loop system or an open loop system consisting of a supply and discharge well." | SECTION (1) DEFINITIONS | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Setback - Roads | 10 | feet | For non-potable wells, "The following minimum distances are required: Roadway 10 feet (from edge of road layout, not edge of pavement)." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Setback - Property Lines | 10 | feet | For non-potable wells, "The following minimum distances are required: Property Line 10 feet." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Setback - Wastewater | 50 | feet | For non-potable wells, the table requires setbacks from wastewater infrastructure including "Septic tank 10 feet," "Septic leaching facility 25 feet," and "Septic distribution box 10 feet." The geothermal-specific clause adds: "Inlet and discharge wells used solely to serve open loop heat pumps shall be located not less than 50' from a septic leaching facility." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Setback - Subsurface Drains | 25 | feet | For non-potable wells, the table states: "Subsurface drains 25 feet (but recommend that this distance be maximized, as pollutants frequently travel along the outside of subsurface drainpipes.)" | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Setback - Sewer Lines | 10 | feet | The permit site plan must show the well location relative to "building sewer lines," and the minimum-distance table states: "Building sewer 10 feet." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; A) Well Construction Permit and B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Permit |  |  | "No well shall be installed, altered, or repaired, until a Well Construction Permit has been obtained from the Board of Health." The permit application must include "a site plan showing the proposed location of the well in relation to building foundations, property lines, building sewer lines, subsurface drainage systems, subsurface sewage disposal systems ..." This section applies to non-potable wells, and the ordinance separately defines a "Groundwater Heat Pump" as using closed loop or open loop systems. | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; A) Well Construction Permit | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Licensed Driller |  |  | "No well shall be installed, altered, repaired, replace or abandoned except by a well driller, who is certified by MassDEP pursuant to M.G.L. Chapter 21, Section 20, 310CMR 46.00; and the Brewster Board of Health." Also, "All well drillers doing business in the Town of Brewster shall annually file with the Board of Health a copy of their current well driller registration certificates issued by the MassDEP in accordance with 310 CMR 46.00." | SECTION (2) GENERAL REQUIREMENTS; C) Well Installation, Alteration, Repair and Abandonment | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Certification |  |  | "All well drillers doing business in the Town of Brewster shall annually file with the Board of Health a copy of their current well driller registration certificates issued by the MassDEP in accordance with 310 CMR 46.00." And: "No well shall be installed, altered, repaired, replace or abandoned except by a well driller, who is certified by MassDEP pursuant to M.G.L. Chapter 21, Section 20, 310CMR 46.00; and the Brewster Board of Health." | SECTION (2) GENERAL REQUIREMENTS; B) Registration of Well Drillers and C) Well Installation, Alteration, Repair and Abandonment | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | Town | 2500107980 | Decommissioning |  |  | "Prior to destruction of any well, the well driller must obtain a well destruction permit from the Board of Health." "Any abandoned well shall be filled and sealed with clean puddle clay, neat cement grout, bentonite or concrete grout in such a manner as to prevent it from acting as a channel for pollution to the groundwater." "Within 30 days following the completion of the plugging procedure, the certified well driller who plugged the abandoned well, test hole, or dry or inadequate boring must submit a Well Completion Report to MassDEP with a copy to the Board of Health ... and must submit a Decommissioning Report to the owner, agent and Board of Health." | SECTION (2) GENERAL REQUIREMENTS; E) Well Decommissioning | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Definition: Well |  |  | "Well: any hole or shaft drilled into the ground to inject or withdraw water, other fluids, or gases, monitor soil gasses, monitor groundwater levels or water quality, transfer heat, or provide cathodic protection." | SECTION II: DRINKING WATER, III. DEFINITIONS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Roads | 25 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (b) 25 feet from public or private roadway." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Right of Way | 50 | feet | Section VI lists setbacks including "(c) 15 feet from right of way" and also "(i) 50 feet from any utility right of way." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Property Lines | 10 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (a) 10 feet from the property line." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Wastewater | 50 | feet | Section VI requires setbacks for wells including "(d) 50 feet from building sewer line, septic tank, or distribution box" and "(e) 25 feet from leaching field, catch basin or drywell." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Animal Enclosures | 100 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (f) 100 feet from stable, barnyard, manure storage." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Fuel (below ground) | 250 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (g) 250 feet from an underground fuel storage or pesticide tank." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Water Lines | 10 | feet | "Water supply lines shall be installed at least ten (10) feet from and eighteen (18) inches above any sewer line." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Sewer Lines | 50 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (d) 50 feet from building sewer line, septic tank, or distribution box." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Setback - Water Bodies | 25 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (h) 25 feet from any surface water, including, but not limited to, wetlands." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Maximum Well Depth | 100 | feet | Within the Mandatory Municipal Water Supply Zone, conversion of private drinking water wells for irrigation use may be allowed only if the well "is less than 100 ft. in depth." | SECTION II: DRINKING WATER, XI. Requirements for Wells in the Mandatory Municipal Water Supply Zone | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Permit |  |  | "A Massachusetts Certified Well Driller shall obtain an electronic permit from the Board of Health prior to the commencement of construction of a private well." | SECTION II: DRINKING WATER, IV. WELL CONSTRUCTION PERMIT | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Inspection |  |  | "Each private well shall be located so that it is accessible for repair, maintenance, testing, and inspection." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Licensed Driller |  |  | "no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | SECTION II: DRINKING WATER, IX. WELL CONSTRUCTION REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Certification |  |  | Section IV requires the application to include "the well driller's name and proof of valid Massachusetts certification." Section IX states: "no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | SECTION II: DRINKING WATER, IV. WELL CONSTRUCTION PERMIT; IX. WELL CONSTRUCTION REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Decommissioning |  |  | "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." The owner "shall decommission the well" if specified criteria are met, and "Only certified well drillers may plug abandoned wells, test holes, and borings." Plugging materials and placement are specified, including introduction "at the bottom of the well or boring and placed progressively upward to a level approximately four (4) feet below the ground surface," with the top then filled with concrete and a concrete slab installed. | SECTION II: DRINKING WATER, X. DECOMMISSIONING REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | Town | 2500119295 | Other Prohibitions/Regulations |  |  | "In the Central Area bounded by Glacier Hills Road, Schoolhouse Road, Route 6 and Bike Trail (see attached map) all private wells (potable and non-potable) must be abandoned." | SECTION II: DRINKING WATER, XI. Requirements for Wells in the Mandatory Municipal Water Supply Zone | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Definition: Geothermal Heat Pump |  |  | "Groundwater Heat Pump. A refrigeration system which can heat or cool a dwelling which operates by exchanging heat with the groundwater. The groundwater can be supplied by either a closed loop system or an open loop system consisting of a supply and a discharge well." | § 185-69 Definitions | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Setback - Roads | 10 | feet | For nonpotable wells, including open-loop heat pump wells regulated in the same section, the table states: "Roadway — 10 feet from edge of road layout (not edge of pavement)." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Setback - Right of Way | 50 | feet | For nonpotable wells, the table states: "Utility rights-of way for high voltage transmission lines — 50 feet, but recommend that this distance be maximized." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Setback - Property Lines | 10 | feet | For nonpotable wells, including open-loop heat pump wells regulated in the same section, the table states: "Property Line — 10 feet." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Setback - Wastewater | 50 | feet | The nonpotable well location table requires setbacks of "Septic tank — 10 feet," "Septic leaching facility — 25 feet," and "Septic distribution box — 10 feet." A note specifically for geothermal says: "Inlet and discharge wells used solely to serve open loop heat pumps shall be located not less than 10' from a septic tank" and "Inlet and discharge wells used solely to serve open loop heat pumps shall be located not less than 50' from a septic leaching facility." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Setback - Subsurface Drains | 25 | feet | For nonpotable wells, the table states: "Subsurface drains — 25 feet, but recommend that this distance be maximized, as pollutants frequently travel along the outside of subsurface drainpipes." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Setback - Sewer Lines | 10 | feet | For nonpotable wells, the table states: "Building sewer — 10 feet." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Permit |  |  | For open-loop heat pump wells covered as nonpotable wells: "No well shall be installed, altered, or repaired, until a Well Construction Permit has been obtained from the Board of Health." The application must be submitted by the drilling contractor or agent, and "The Board of Health must approve the location and design of the well, prior to issuance of a Well Construction permit." | § 185-71(A) Well Construction Permit | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Inspection |  |  | The ordinance states: "When the Board of Health deems it necessary, the health agent or other agent of the Board of Health, may be present to witness the taking of a water sample and/or may take the water sample and deliver it to the testing laboratory him/herself." It also requires: "Before approval, every well shall be pump tested to determine yield. The pump test shall include a draw down test at a minimum pumping rate of 5 gallons per minute for one (1) hour." | § 185-72(C)(4) Water Quality; § 185-72(D)(1) Well Yield and Water System Design | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Licensed Driller |  |  | "No well shall be installed, altered, repaired or abandoned except by a well driller, who is registered with the Water Resources Commission, Division of Water Resources, under MGL Ch. 21, Sec. 16 and 31, CMR 3.00 and the Orleans Board of Health." Also, "All well drillers doing business in the Town of Orleans, shall annually file with the Board of Health a copy of their current well driller registration issued by the Commonwealth of Massachusetts Regulations 313 CMR 3.00." | § 185-70 General requirements; § 185-71 Requirements for nonpotable water wells; § 185-72 Requirements for potable water wells | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Certification |  |  | "All well drillers doing business in the Town of Orleans, shall annually file with the Board of Health a copy of their current well driller registration issued by the Commonwealth of Massachusetts Regulations 313 CMR 3.00." | § 185-70 General requirements | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | Town | 2500151440 | Decommissioning |  |  | "Prior to destruction of any well, the well driller must obtain a well destruction permit from the Board of Health." Also, "Any abandoned well shall be filled and sealed with clean puddled clay, neat cement grout, bentonite or concrete grout in such a manner as to prevent it from acting as a channel for pollution to the groundwater." | § 185-70(E) Well Destruction | 2003 | https://ecode360.com/14202077
Massachusetts | Bristol | Easton | Town | 2500520100 | Definition: Well |  |  | "GEO THERMAL WELL — A well or wells drilled vertically in the ground that are water-filled, closed loop of one-inch high-density polyethylene (HDPE) pipe ferries heat between the earth and the house. Pipes descend four-to six-inch-diameter vertical wells... Drillers backfill each hole with bentonite grout... Pumps cycle water through the pipe loop to the heart of the system: the geothermal unit, which acts as furnace and air conditioner." | § 369-2 Definitions | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Roads | 25 | feet | "Each well shall be located... Twenty-five feet from a street layout." | § 369-4 Location and use requirements, E(6) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Property Lines | 25 | feet | "Each well shall be located... Twenty-five feet from a property line." | § 369-4 Location and use requirements, E(5) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Building Foundation | 10 | feet | "Each well shall be located... Ten feet from a dwelling or building;" | § 369-4 Location and use requirements, E(11) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Wastewater | 100 | feet | "Each well shall be located: At a minimum of 100 feet from a subsurface sewage disposal area (including reserve areas);" and "A minimum of 50 feet for irrigation and geothermal wells from sewage disposal and reserve areas. Fifty feet from a septic tank for all wells." | § 369-4 Location and use requirements, E | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Animal Enclosures | 100 | feet | "Each well shall be located... One hundred feet from a Stables, barnyard, Manure storage." | § 369-4 Location and use requirements, E(15) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Fuel (below ground) | 100 | feet | "Each well shall be located... One-hundred feet from underground oil tanks and gasoline tanks, underground oil distribution lines..." | § 369-4 Location and use requirements, E(9) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Subsurface Drains | 25 | feet | "Each well shall be located... Twenty-five feet from subsurface drains;" | § 369-4 Location and use requirements, E(8) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Sewer Lines | 50 | feet | "Each well shall be located... Fifty feet from any sewer main;" | § 369-4 Location and use requirements, E(13) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Pools | 10 | feet | "Each well shall be located... Ten feet from a permanently located swimming pool;" | § 369-4 Location and use requirements, E(12) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Water Bodies | 25 | feet | "Each well shall be located... Twenty-five feet from the normal high water mark of any lake, pond, river, stream, ditch or slough;" | § 369-4 Location and use requirements, E(10) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Setback - Hazardous Materials/Fertilizers | 250 | feet | "Each well shall be located... Two hundred fifty feet for underground pesticide;" | § 369-4 Location and use requirements, E(14) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Inspection |  |  | "Inspections. The Board of Health or its authorized Agent may inspect the installation of the well and may at any stage of construction, require necessary modifications..." Also, "Following review of analytical results, pump tests and all other pertinent information, an inspection will be made by the Board of Health or its agent(s) to verify the well location, construction, operation of the well pump and any required posting." | § 369-3 Well construction permits, F; § 369-9 Well registration, C | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Decommissioning |  |  | "Abandoned Wells... shall be destroyed by removing, plugging or sealing by decommissioning to protect the groundwater." Also, "Only MA Registered Well Drillers may plug abandoned wells... Wells shall be plugged with neat cement grout, sand cement grout, concrete or bentonite grout... applied through a tremie pipe from the bottom of the well upward... casing shall be cut off six inches — 12 inches below existing grade... The remaining depth of casing shall be filled with concrete." | § 369-8 Decommissioning of wells | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | Town | 2500520100 | Open-loop Prohibitions |  |  | "All Geo thermal wells will be closed loop. Open loop wells or these kinds of systems will not be approved..." | § 369-4 Location and use requirements, C | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Westport | Town | 2500577570 | Other Prohibitions/Regulations |  |  | "The open space shall allow walking paths and other passive recreational uses, but shall not be use for the siting of any structure, building, septic system, well (drinking water or geothermal) or utilities or pipes." | 6.5.10 OPEN SPACE REQUIREMENTS | 2023 | https://cms2.revize.com/revize/westportma/Documents/Departments/Building/zoning_by-laws_5.3.23_atm_approved_web_1.pdf?t=202508271350580&t=202508271350580
Massachusetts | Dukes | Chilmark | Town | 2500713800 | Setback - Property Lines | 50 | feet | Section 5.9 states: "Machinery or mechanical units, which are placed outside the footprint of a dwelling, shall be treated as 'structures' and shall be subject to the normal setbacks required by zoning..." Section 6.0 then provides the zoning setbacks: in Districts I, II-A, II-B, III, and VI, each structure and accessory use "shall be set back a minimum of 50 feet from each boundary line of said lot"; District IV requires 25 feet; District V requires 35 feet; and Section 6.1 provides exceptions of 25 feet or 35 feet for certain smaller pre-existing, Homesite Housing, or Youth Lots. | Section 6.0; Section 5.9 - Exterior Mechanical Noise Abatement | 2025 | https://www.chilmarkma.gov/sites/g/files/vyhlif8411/f/uploads/zbl_scan_08112025_searchable_0.pdf
Massachusetts | Dukes | Chilmark | Town | 2500713800 | Noise Limits | 10 | dBA | Section 5.9 applies to "mechanical devices associated with and accessory to residential dwellings, such as, but not exclusively, air conditioners/heat pumps..." and requires such stationary machinery to "be placed in soundproof enclosures or to be so screened and insulated that the perceived sound levels do not rise by more than ten decibels (10 DbA) above the ambient sound level as measured at the property line." | Section 5.9 - Exterior Mechanical Noise Abatement | 2025 | https://www.chilmarkma.gov/sites/g/files/vyhlif8411/f/uploads/zbl_scan_08112025_searchable_0.pdf
Massachusetts | Dukes | Chilmark | Town | 2500713800 | Permit |  |  | "If a swimming pool is heated, applicants are strongly encouraged to use: ... an energy efficient heating system, including on-site solar thermal or a heat pump system." The same subsection states: "A Special Permit is required for a swimming pool or a tennis court from the Zoning Board of Appeals." | Section 4.2A.3(a) - Swimming Pool and/or Tennis Court | 2025 | https://www.chilmarkma.gov/sites/g/files/vyhlif8411/f/uploads/zbl_scan_08112025_searchable_0.pdf
Massachusetts | Essex | Georgetown | Town | 2500925625 | Definition: Well |  |  | "WELL or WATER WELL" means "Any hole or shaft constructed into the ground for the purpose of extracting or injecting water... It shall include wells connected to heat pumps." The same definition section adds "HEAT PUMP WELLS" as: "Consists of a source well and a discharge well which could be one and the same, provided that it is a closed loop system where nothing is added to or taken from the water except heat and no air is in contact with the return water. A heat pump delivers water by way of the source well from an aquifer through a heat exchanger and returns it to the aquifer via the discharge well. The system utilizes the thermal energy stored in groundwater for space heating or cooling." | § 480-3 Definitions |  | https://ecode360.com/6486648
Massachusetts | Essex | Georgetown | Town | 2500925625 | Permit |  |  | "A well permit shall be obtained from the Board of Health prior to the construction of any water well or well system. This includes major rework or repair of existing water wells." The ordinance also requires that "An application for a water well permit must be submitted to the Board of Health" and that "The location, design and operation of the well must be approved by the Board of Health or its agent prior to construction." | § 480-7C Well construction permits |  | https://ecode360.com/6486648
Massachusetts | Essex | Georgetown | Town | 2500925625 | Licensed Driller |  |  | "No person shall engage in the business of constructing wells within the Town of Georgetown unless he is registered with the Water Resources Commission, Division of Water Resources, as required by Water Well Drillers Registration Act (MGL C. 21, § 16)." Also, § 480-3 defines "WELL DRILLER" as a person that constructs a water well, "licensed by Water Resource Commission (§ 480-5)." | § 480-5 Registration of well drillers |  | https://ecode360.com/6486648
Massachusetts | Essex | Middleton | Town | 2500941095 | Definition: Well |  |  | "GROUND SOURCE HEAT PUMP (GSHP) WELL — Any excavation by any method for the purpose of transferring heat to or from the earth for heating and cooling purposes in which the ambient ground temperature (prior to GSHP operations) is 90° Fahrenheit or less." | § 343-3 Definitions | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) SYSTEM — A heating and/or cooling system that transfers heat to or from the earth in which the naturally occurring, ambient ground (prior to GSHP operations) is 90° Fahrenheit or less." | § 343-3 Definitions | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Roads | 25 | feet | "Each private well shall be located at least 25 feet from any property line/road right-of-way." | § 343-6(A)(2) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Property Lines | 25 | feet | "Each private well shall be located at least 25 feet from any property line/road right-of-way." | § 343-6(A)(2) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Building Foundation | 5 | feet | "The center line of a well shall, if extended vertically, clear any projection from an adjacent structure by at least five feet." | § 343-6(A)(2) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Wastewater | 100 | feet | "All wells and/or suction lines shall be located... 50 feet from a septic tank; 100 feet from a leaching field and soil absorption system; and 100 feet from a privy." | § 343-6(A)(4) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Water Lines | 10 | feet | "Water supply lines shall be installed at least 10 feet from and 18 inches above any sewer line." | § 343-6(A)(6) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Sewer Lines | 50 | feet | § 343-6(A)(4): "All wells and/or suction lines shall be located a minimum of 10 feet from a building sewer constructed of durable corrosion-resistant material with watertight joints, or 50 feet from a building sewer constructed of any other type of pipe..." § 343-6(A)(6): "Water supply lines shall be installed at least 10 feet from and 18 inches above any sewer line." | § 343-6(A)(4); § 343-6(A)(6) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Setback - Water Bodies | 25 | feet | "Each private well shall be located at least 25 feet, laterally, from the normal high water mark of any lake, pond, river, stream, ditch, or slough." | § 343-6(A)(3) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Minimum Well Depth | 15 | feet | "Private wells drilled in bedrock shall be grouted from the top of the weathered rock interface to a minimum of 15 feet into competent bedrock." | § 343-9(G)(1) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Permit |  |  | § 343-4(A): "The property owner or his designated representative shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." § 343-6(B)(3) states: "Ground source heat pump wells are subject to the same standards as drinking water wells." | § 343-4 Well construction permit; § 343-6(B)(3) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Inspection |  |  | § 343-6(A)(1): "Each private well shall be accessible for repair, maintenance, testing, and inspection." § 343-7: "a pumping test, witnessed by the Board of Health's representative, shall be conducted" to demonstrate well capacity. | § 343-6(A)(1); § 343-7 | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Licensed Driller |  |  | § 343-4(B)(2) requires a permit application to include "The well driller's name and proof of valid state registration." § 343-9(A) states: "Pursuant to 313 CMR 3.00, no person in the business of drilling shall construct a well unless registered with the Department of Environmental Management/Office of Water Resources." | § 343-4(B)(2); § 343-9(A) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Certification |  |  | § 343-3 defines "REGISTERED WELL DRILLER" as "Any person registered with the Department of Environmental Management/Division of Water Supply Protection to dig or drill wells in the Commonwealth of Massachusetts." § 343-9(A): "no person in the business of drilling shall construct a well unless registered with the Department of Environmental Management/Office of Water Resources." § 343-10(C): "Only registered well drillers may plug abandoned wells, test holes, and borings." | § 343-3 Definitions; § 343-9(A); § 343-10(C) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | Town | 2500941095 | Decommissioning |  |  | § 343-10(A): "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." § 343-10(B): "The owner of the private well shall decommission the well" when listed abandonment conditions occur. § 343-10(C): "Only registered well drillers may plug abandoned wells, test holes, and borings." § 343-10(E): "Abandoned wells or borings shall be completely filled with a grout..." and § 343-10(G): "The plugging materials shall be introduced at the bottom of the well or boring and placed progressively upward..." | § 343-10 Decommissioning requirements | 2008 | https://ecode360.com/10442189
Massachusetts | Franklin | Greenfield | City | 2501127060 | Definition: Geothermal |  |  | "RENEWABLE ENERGY -- The following shall be considered renewable energy: ... • Geothermal ..." | § 200-2.1. Terms and words | 2021 | https://cms5.revize.com/revize/greenfield/Document_Center/Department/Planning%20&%20Development/Zoning_Ordinance.pdf
Massachusetts | Middlesex | Acton | Town | 2501700380 | Definition: Geothermal Heat Pump |  |  | "Geothermal Wells" are referenced in the operative clause: "Notwithstanding the requirements of 9-6.4, the Health Department may grant approval for the installation of Geothermal Wells in public water supply areas..." | Regulation 9-6.4.2 | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Acton | Town | 2501700380 | Permit |  |  | "Notwithstanding the requirements of 9-6.4, the Health Department may grant approval for the installation of Geothermal Wells in public water supply areas when the following conditions have been met:" and "A plan showing the location of the geothermal wells and detailing the system, including piping, heat transfer media and construction, shall be submitted to the Health Division for approval." | Regulation 9-6.4.2(a) | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Acton | Town | 2501700380 | Decommissioning |  |  | "If the geothermal wells not be used for a period of two years, it shall be abandoned and permanently secured by filling the well head with a concrete slurry and by taking all other actions necessary to make the well and area safe from potential accidents and hazards." | Regulation 9-6.4.2(d) | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Acton | Town | 2501700380 | Open-loop Prohibitions |  |  | "All wells for geothermal use shall be artesian or bedrock wells with a closed loop system in the well..." | Regulation 9-6.4.2(a) | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Burlington | Town | 2501709840 | Definition: Well |  |  | "Private Ground Source Heat Pump (Geothermal) Well: Any excavation by any method for the purpose of transferring heat to or from the earth for heating and cooling purposes in which the ambient ground temperature is 90 degrees Fahrenheit or less." | 5.2 Definitions | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | Town | 2501709840 | Setback - Property Lines | 10 | feet | Section 5.6 states: "Private wells must meet the following setback requirements except as otherwise provided below: 10 feet from the property line." Section 5.3.E applies these regulations to "Private Ground Source Heat Pump (Geothermal) Wells" through Sections 5.8-5.12, but Section 5.3.E does not apply Section 5.6 to geothermal wells. | 5.6 Well Location and Operation Requirements | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | Town | 2501709840 | Permit |  |  | Section 5.3.E provides that private geothermal wells are subject to "Article III, Section 5.4 and Section 5.8 through Section 5.12." Section 5.4 states: "The Property Owner and a Massachusetts Certified Well Driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." | 5.3.E Private Ground Source Heat Pump (Geothermal) Wells; 5.4 Well Construction and Operation Permit | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | Town | 2501709840 | Licensed Driller |  |  | Section 5.4 states: "The Property Owner and a Massachusetts Certified Well Driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." The permit application must include "the well driller's name and proof of valid Massachusetts certification." Section 5.9 adds: "Only certified well drillers may plug abandoned wells, test holes, and borings." | 5.4 Well Construction and Operation Permit; 5.9 Decommissioning Requirements | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | Town | 2501709840 | Certification |  |  | Section 5.2 defines "Certified Well Driller" as: "Any person certified with the Massachusetts Department of Environmental Protection Well Driller Program to dig or drill wells in the Commonwealth of Massachusetts." Section 5.4 requires the permit application to include "the well driller's name and proof of valid Massachusetts certification." | 5.2 Definitions; 5.4 Well Construction and Operation Permit | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | Town | 2501709840 | Decommissioning |  |  | Section 5.8 states that the "Guidelines for Ground Source Heat Pump Wells" are "incorporated herein as requirements for private ground source heat pump (geothermal) wells." Section 5.9 further requires: "Abandoned wells, test holes, and boring shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." It also states: "The owner of a private well shall decommission the well" upon listed triggers, including when "the use of the well is to be permanently discontinued" or "the well has been out of service for at least three (3) years." "The Property Owner shall ensure that all abandoned wells and test holes or borings associated with private well installation are properly plugged before work on the site is complete." | 5.8 Additional Requirements; 5.9 Decommissioning Requirements | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Chelmsford | Town | 2501713135 | Permit |  |  | § 201-31.7 states: "Ground source heat pump wells installed in the Town of Chelmsford must comply with all regulations of the Mass DEP as set forth in the 'Guidelines for Ground Source Heat Pump Wells.'" Within this article, § 201-31.1 requires that "A Massachusetts-certified well driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." | § 201-31.7 Geothermal wells (ground source heat pump wells); § 201-31.1 Well construction permit | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | Town | 2501713135 | Licensed Driller |  |  | "A Massachusetts-certified well driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." Also, "Pursuant to 310 CMR 46.02(1), no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | § 201-31.1 Well construction permit; § 201-31.6 Well construction | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | Town | 2501713135 | Certification |  |  | "CERTIFIED WELL DRILLER — Any person certified with the Department of Environmental Protection Well Driller Program to dig or drill wells in the Commonwealth of Massachusetts." Permit applications must include "the well driller's name and proof of valid Massachusetts certification," and "no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | § 201-30.3 Definitions; § 201-31.1 Well construction permit; § 201-31.6 Well construction | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | Town | 2501713135 | Decommissioning |  |  | "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." "The owner of a private well shall decommission the well if" specified criteria are met, including permanent discontinuance, three years out of service, hazard, disrepair, or contamination risk. "The property owner shall ensure that all abandoned wells and test holes or borings associated with the well installation are properly plugged before work at the site is completed. Only certified well drillers may plug abandoned wells, test holes, and borings." | § 201-31.9 Decommissioning | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | Town | 2501713135 | Open-loop Prohibitions |  |  | "Only closed-loop GSHPW systems are approved in Town. All other well types require a variance from the Board." | § 201-31.7 Geothermal wells (ground source heat pump wells) | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Groton | Town | 2501727480 | Definition: Well |  |  | "GEOTHERMAL WELL — Any shaft or hole drilled into the surface of the earth, greater than 20 feet in depth, which is used or intended to be used in connection with coring, or the drilling for, prospecting for, or the production of geothermal resources, hot water, petroleum, natural gas, or other hydrocarbon substances, or shallow extraction wells for heating, agricultural or other purposes, or is used or intended to be used for the subsurface injection into the earth of oilfield waste, gases, water or liquid substances..." | § 330-3 Definitions | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Definition: Geothermal Heat Pump |  |  | "CLOSED-LOOP GEOTHERMAL BOREHOLE — A boring drilled to facilitate the installation of a pipe loop or tubing for a ground source heat pump system whether circulating water, heat transfer fluid or refrigerant using direct exchange." Also: "OPEN-LOOP BOREHOLE — A water well designed to produce source water above land surface to provide heat transfer to a geothermal well." | § 330-3 Definitions | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Driveways | 50 | feet | The minimum-distance table states: "Public or private way, common drive, roadway easement, parking lot — 50" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Roads | 50 | feet | The minimum-distance table states: "Public or private way, common drive, roadway easement, parking lot — 50" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Right of Way | 50 | feet | The minimum-distance table states: "Public or private way, common drive, roadway easement, parking lot — 50" feet. The permit application requirements also require identifying "Utility right-of-way," but that clause does not give a numeric distance. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Property Lines | 50 | feet | The minimum-distance table states: "Property line — 50" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Building Foundation | 10 | feet | The minimum-distance table states: "Slab or foundation — 10" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Wastewater | 100 | feet | The minimum-distance table states: "Leaching facility (310 CMR 15.00) — 100" feet; "Cesspool — 100" feet; "Septic tank — 50" feet; and "Septic expansion area — 100" feet. § 330-12(A)(1) for closed-loop geothermal boreholes states: "Septic tanks — 25" feet and "Septic drain fields — 50" feet. The controlling most restrictive wastewater setback stated is 100 feet. | § 330-6 Well location and use requirements; § 330-12 Geothermal wells | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Public Water | 100 | feet | For closed-loop geothermal boreholes, § 330-12(A)(1) states: "Water wells — 100" feet. | § 330-12 Geothermal wells | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Sewer Lines | 10 | feet | The general well-location table states: "Sewer line — 100" feet. § 330-12(A)(1) separately states for closed-loop geothermal boreholes: "Sewer lines — 10" feet and "House to sewer line connection — 10" feet. The controlling most restrictive stated sewer-line separation in this ordinance is 100 feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Pools | 25 | feet | The minimum-distance table states: "In-ground pool — 25" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Setback - Water Bodies | 100 | feet | The minimum-distance table states: "Any type of surface water/wetland — 100" feet. § 330-12(A)(1) also states for closed-loop geothermal boreholes: "Springs — 100" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Minimum Well Depth | 20 | feet | "GEOTHERMAL WELL — Any shaft or hole drilled into the surface of the earth, greater than 20 feet in depth..." | § 330-3 Definitions | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Permit |  |  | "The application for a permit for the installation of an individual well, geothermal well, irrigation well, monitoring well and test well shall be made by a contractor, appropriately licensed." Also: "The property owner or his/her/their designated representative shall obtain a permit from the Board of Health or its agent prior to the commencement of construction and/or deconstruction of... heating and cooling well, agricultural well, drilled holes, bore holes, or other holes drilled by mechanical means greater than 10 feet..." | § 330-4 Well construction/deconstruction permit | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Licensed Driller |  |  | "All individual wells, geothermal wells, monitoring wells and test wells constructed pursuant to these regulations shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor." | § 330-9 Well construction requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | Town | 2501727480 | Decommissioning |  |  | "A well that is abandoned shall be destroyed to protect the groundwater and to eliminate potential physical hazards. Wells shall be sealed with nonhazardous, impervious materials which shall be permanently in place. All casing materials, pumping equipment, and distribution lines shall be removed. The excavation shall be returned to the current existing grade of the surrounding land." Also: "Abandoned wells, test holes, and borings shall be decommissioned..." and "Only registered well drillers may plug abandoned wells, test holes, and borings." | § 330-10 Deconstruction requirements and irrigation wells | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Definition: Geothermal Heat Pump |  |  | "Any type of well constructed for the purposes of using the ambient temperature of the earth beneath the surface to heat or cool water or other fluids as part of the heating, ventilation, and air conditioning system of a building." | § 155-73H(1) Geothermal wells | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Setback - Property Lines | 50 | feet | Applicants for a Board of Health closed loop geothermal heating system well registration must provide "[a] plan depicting that the system well has a minimum setback distance of 50 feet from any private water supply well or section line or any on-site disposal system ..." | § 155-73H(7)(e) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Setback - Wastewater | 50 | feet | Applicants for a Board of Health closed loop geothermal heating system well registration must provide "[a] plan depicting that the system well has a minimum setback distance of 50 feet from any private water supply well or section line or any on-site disposal system (as defined by 310 CMR 15.002)." | § 155-73H(7)(e) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Setback - Private Water | 50 | feet | Applicants for a Board of Health closed loop geothermal heating system well registration must provide "[a] plan depicting that the system well has a minimum setback distance of 50 feet from any private water supply well ..." | § 155-73H(7)(e) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Permit |  |  | "The property owner or the well driller/digger or his agent shall submit a well construction application, prior to the commencement of construction and/or destruction of a ... geothermal well" (§ 155-72A). Also, "No well shall be constructed, altered or repaired until a well construction permit has been obtained from the Board of Health" (§ 155-71E). For closed-loop geothermal systems, "applicants ... for a Board of Health closed loop geothermal heating system well registration must attach" specified materials, including the MassDEP UIC registration form and registration ID number (§ 155-73H(7)(a)-(b)). | § 155-72 Well construction permit; § 155-73 Well construction | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Inspection |  |  | "All ground source wells installed in the Town of Lexington must be tested for the parameters outlined in the referenced Guidelines" (§ 155-73H(5)). Section § 155-73H(3) also states that installers "must comply with all state and federal regulations applicable to the well being installed ... including but not limited to requirements with respect to reinjection of return water, fluids used in the system, and testing requirements." | § 155-73 Well construction | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Licensed Driller |  |  | "No well shall be installed, altered, repaired, destroyed or abandoned except by a well driller who is registered with the Water Resources Commission, Division of Water Resources" (§ 155-71C). For geothermal wells specifically, the ordinance also requires compliance with the "Massachusetts Well Driller Certification Program (310 CMR 46.00)" (§ 155-73H(1)(d)) and states "the well driller will fully grout the well following piping installation" (§ 155-73H(7)(g)). | § 155-71 General provisions; § 155-73 Well construction | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Certification |  |  | For closed-loop systems, "if not a water only system, the Material Safety Data Sheet (MSDS) for the recirculation fluid to be used in the system must be submitted which indicated that the fluid is non-toxic and non-hazardous food grade propylene glycol." | § 155-73H(7)(c) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Decommissioning |  |  | "Prior to the destruction or abandonment of any well, a well destruction permit must be obtained" (§ 155-78A). "Abandoned wells, test holes and borings shall be decommissioned so as to prevent the well ... from being a channel for pollution into the groundwater" (§ 155-78B). "Only registered well drillers may plug abandoned wells, test holes and borings" (§ 155-78C). "Abandoned wells or borings shall be completely filled with a grout" meeting the stated permeability standard, and a report must be submitted "within 30 days after completion of destruction or abandonment" (§ 155-78D-E). | § 155-78 Well decommission | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | Town | 2501735215 | Other Prohibitions/Regulations |  |  | "No ground source heat pump wells may be used for potable water." | § 155-73H(4) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Natick | Town | 2501743895 | Definition: Geothermal |  |  | "Renewable or Alternative Energy : The following renewable or alternative energy generation activities, products, or technologies: solar (both photovoltaic (PV) and thermal); wind; biomass power conversion or thermal technologies, including R&D related to, or the manufacture of, wood pellets; ultra low emissions high efficiency wood pellet boilers and furnaces; low impact hydro (electric or kinetic); ocean thermal, wave or tidal; geothermal; landfill gas; fuel cells that use renewable energy; advanced biofuels; combined heat and power; electric and hydrogen powered vehicles and associated technologies including advanced batteries and recharging stations." | Section 200 - Definitions | 2025 | https://natickma.gov/DocumentCenter/View/19913/06092025-Addendum-of-2024-Fall-and-2025-Spring-ATM-Zoing-Amendments
Massachusetts | Middlesex | Wakefield | Town | 2501772215 | Definition: Well |  |  | "Well: any hole or shaft drilled into the ground to inject or withdraw water, other fluids, or gases, monitor soil gasses, monitor groundwater levels or water quality, transfer heat, or provide cathodic protection." | III. DEFINITIONS | 2019 | https://www.wakefieldma.gov/DocumentCenter/View/479/Wells-PDF
Massachusetts | Middlesex | Westford | Town | 2501776135 | Definition: Well |  |  | "The word 'WELL', as used in these regulations, shall include any pit, pipe, excavation, casing, drill hole or other source of water to be used for any purpose of supplying potable water, irrigation water, process water, or water for a Ground Source Heat Pump (GSHP) in Westford." | DEFINITIONS | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | Town | 2501776135 | Definition: Geothermal Heat Pump |  |  | "The words 'GSHP WELL' or GROUND SOURCE HEAT PUMP WELL, shall mean any Class V well as defined by 310 CMR 27.03(5) that uses heat transferred to or from the earth to heat and/or cool a structure." | DEFINITIONS | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | Town | 2501776135 | Permit |  |  | "Ground Source Heat Pump Wells installed and operated in the Town of Westford must comply with all regulations of the Mass DEP as set forth in the 'Guidelines for Ground Source Heat Pump Wells'... including but not limited to requirements with respect to reinjection of return water, fluids used in the system, and testing requirements." The ordinance also lists "Massachusetts Groundwater Discharge Permits (314 CMR 5.00)" under "GROUND SOURCE HEAT PUMP WELLS: shall comply with the Mass DEP Regulations." | GROUND SOURCE HEAT PUMP WELLS | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | Town | 2501776135 | Inspection |  |  | "The Board or its agent may require inspection of the work during its progress, including, among other things, the adequacy of the required seal, the pump test, and shall designate the notice required to be given to the Board or its agent that said work is ready for inspection." | CONSTRUCTION, PERMITS, INSPECTIONS, & CERTIFICATES | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | Town | 2501776135 | Licensed Driller |  |  | "Every owner of a company installing wells in Westford shall be required each year to provide the Board with a copy of their well driller's certificate issued by the appropriate governing agency of the State of Massachusetts." Also: "Only certified well drillers may plug abandoned wells, test holes, and borings." | WELL DRILLERS CERTIFICATES & PERMITS / DECOMMISSIONING A WELL | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | Town | 2501776135 | Decommissioning |  |  | "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." "The owner of a private well shall decommission the well if any of the following criteria are met:" including when "the use of the well is to be permanently discontinued" or "the well has been out of service for at least three (3) years." "The property owner shall ensure that that all abandoned wells and test holes or borings associated with the well installation are properly plugged before work at the site is completed." | DECOMMISSIONING A WELL | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Norfolk | Dover | Town | 2502117405 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP WELL — Any excavation by any method for the purpose of transferring heat to or from the earth for heating and cooling purposes. Ground source heat pump wells shall be installed in accordance with MassDEP guidelines; §§ 233-6 through 233-11 of these regulations do not apply to such wells." | § 233-3 Definitions | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | Town | 2502117405 | Permit |  |  | "Before the commencement of construction of a private well, the property owner or his designated representative shall complete the well construction application in full. No work shall commence until the application is approved by the Board or its agent." Also, "A well construction permit shall be required for the installation of any new private well..." | § 233-5 Well construction permit | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | Town | 2502117405 | Inspection |  |  | "The agent shall review the design plans to verify such conformity." | § 233-4 Ground source heat pump wells | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | Town | 2502117405 | Licensed Driller |  |  | § 233-5(A)(2): "The Massachusetts certified well driller's name, address, phone number and proof of valid Massachusetts well driller certification. Only a Massachusetts certified well driller may install a well." § 233-9(P): "Pursuant to 310 CMR 46.00... no person shall engage in the business of well drilling in the Commonwealth." | § 233-5 Well construction permit; § 233-9 General well design and construction parameters | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | Town | 2502117405 | Certification |  |  | "MASSACHUSETTS CERTIFIED WELL DRILLER — Any person or company properly certified by the Commonwealth of Massachusetts pursuant to 310 CMR 46.00, or registered with the Commonwealth pursuant to the predecessor regulations (313 CMR 3.00), to install wells." § 233-5(A)(2) requires "proof of valid Massachusetts well driller certification." § 233-9(P) references "a holder of a certificate in accordance with 310 CMR 46.02, or a registration in accordance with the predecessor regulations, 313 CMR 3.00." | § 233-3 Definitions; § 233-5 Well construction permit; § 233-9 General well design and construction parameters | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | Town | 2502117405 | Decommissioning |  |  | "Abandoned wells, test holes and borings shall be decommissioned so as to prevent the well... from becoming a channel allowing the vertical movement of water and possible contamination." "The property owner shall be responsible for ensuring that all abandoned wells, test holes and borings are properly decommissioned." "Only Massachusetts certified well drillers may decommission wells, test holes and borings." "Abandoned wells, test holes or borings shall be completely filled and plugged with either neat cement grout, sand cement grout, concrete or Bentonite grout." | § 233-12 Decommissioning requirement | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Needham | Town | 2502144105 | Definition: Well |  |  | "Geothermal well : Any well constructed for the location, exploration, monitoring, development, or injection of geothermal resources or the natural heat of the earth, the energy which may be extracted from the natural heat in whatever form found below the surface of the earth as defined." | SECTION 12.3 DEFINITIONS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Definition: Geothermal Heat Pump |  |  | "Open-loop geothermal well : A system which pipes clean ground water directly from a nearby aquifer to an indoor geothermal heat pump. Water leaving the home is expelled through a discharge well which is located a suitable distance from the first." "Closed-loop geothermal well: A ground source heat pump well that uses a closed-loop fluid system to prevent the discharge or escape of its fluid into the subsurface. Closed-loop heat pump wells shall not be used to produce water." "Ground source or geothermal heat pump system : A heating and/or cooling system that transfers heat to or from the earth in which the naturally occurring, ambient ground temperature is 90 degrees Fahrenheit or less." | SECTION 12.3 DEFINITIONS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Roads | 25 | feet | Section 12.12.1 states geothermal wells are governed by these regulations, and Section 12.9.1 provides: "Wells shall be located the following minimum distances from sources of contamination: B. public or private roadways - 25 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Right of Way | 25 | feet | Section 12.12.1 states geothermal wells are governed by these regulations, and Section 12.9.1 provides: "Wells shall be located the following minimum distances from sources of contamination: C. right of way or easements - 25 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Property Lines | 10 | feet | Section 12.12.1 states geothermal wells are governed by these regulations, and Section 12.9.1 provides: "Wells shall be located the following minimum distances from sources of contamination: A. property lines - 10 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Wastewater | 100 | feet | Section 12.9.1 lists wastewater-related setbacks: "E. septic pump or tank - 50 feet *"; "F. privy - 100 feet*"; "G. leaching field (cesspool) or drywell - 100 feet *." Section 12.12.2(E) also provides a geothermal-specific setback: "Geothermal wells shall be located at least 25 feet from potential sources of contamination including, but not limited to septic tanks and field, lagoons...." The most restrictive wastewater setback stated is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Private Water | 50 | feet | Section 12.12.2(D): "Geothermal wells shall be located at least 50 feet from private potable water supply wells." | SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Public Water | 10 | feet | Section 12.12.2(C): "Geothermal wells shall be sited at least 10 feet from surface water bodies, potable water, and sewer lines." | SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Animal Enclosures | 100 | feet | Section 12.9.1: "H. stable, barnyard, manure storage - 100 feet." Section 12.12.2(E) also states: "Geothermal wells shall be located at least 25 feet from potential sources of contamination including, but not limited to ... livestock pens...." The more restrictive stated setback is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Fuel (above ground) | 100 | feet | Section 12.9.1 provides: "I. aboveground fuel storage - 100 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Fuel (below ground) | 100 | feet | Section 12.9.1 provides: "J. underground fuel storage - 100 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Subsurface Drains | 25 | feet | Section 12.9.1 provides: "L. subsurface drains - 25 feet *." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Sewer Lines | 50 | feet | General well setback table at Section 12.9.1: "D. sewer line - 50 feet * (10 feet from a building sewer constructed of durable corrosion resistant material with watertight joints)." Geothermal-specific Section 12.12.2(C) states: "Geothermal wells shall be sited at least 10 feet from surface water bodies, potable water, and sewer lines." The more restrictive stated sewer-line setback is 50 feet in Section 12.9.1. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Water Bodies | 100 | feet | Section 12.9.1 provides: "K. surface water, wetlands - 100 feet **." Section 12.12.2(C) also states: "Geothermal wells shall be sited at least 10 feet from surface water bodies...." The more restrictive stated setback is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Section 12.12.2(E) states: "Geothermal wells shall be located at least 25 feet from potential sources of contamination including, but not limited to ... oil or hazardous materials storage tanks." Section 12.9.1 also provides broader well setbacks including "I. aboveground fuel storage - 100 feet" and "J. underground fuel storage - 100 feet." The most restrictive explicit setback tied to hazardous/oil storage is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Permit |  |  | "12.4.1 Unless otherwise specified, all sections of this regulation apply to open-loop and closed-loop well systems." "Each well permit application will be reviewed and approved by the following before a permit to construct any well will be issued." Section 12.12.2(I): "Any ground source heat pump well system with flows in excess of 15,000 gallons per day must be permitted by the DEP Groundwater Discharge Program (per 314 CMR 5.05)." Section 12.21.1: "Applicants for well permits may be required to obtain plumbing and/or building permits from the Town of Needham Building Department." | SECTION 12.4 WELL CONSTRUCTION PERMIT; SECTION 12.12 GEOTHERMAL WELLS; SECTION 12.21 OTHER PERMITS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Inspection |  |  | Section 12.12.2(L): "The contractor must notify the Water and Sewer Division and the Town Building Commissioner of completion so both Water and Sewer Division and Building Department can conduct a final inspection." Section 12.12.3: "No ground source heat pump well shall be used for its intended purpose until the Public Health Division receives a copy of the final inspection sign-off approval sheets form the Water and Sewer Division and the Building Department along with a copy of the Well Completion Report." | SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Licensed Driller |  |  | Section 12.4.2: "Pursuant to 310 CMR 46.00, no person in the business of digging or drilling shall construct a well unless registered with the Commonwealth of Massachusetts Department of Environmental Management, Office of Water Resources." Section 12.6.1 similarly states: "no person in the business of digging, driving, jetting, drilling or any other method shall construct a well unless registered with the Commonwealth of Massachusetts Department of Environmental Management, Office of Water Resources." Because Section 12.4.1 says "all sections of this regulation apply to open-loop and closed-loop well systems," this drilling registration requirement applies to geothermal wells covered by the regulation. | SECTION 12.4 WELL CONSTRUCTION PERMIT; SECTION 12.6 REGISTRATION REQUIREMENT | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Certification |  |  | "Well completion reports must be submitted for all activities covered under 310 CMR 46.00 including well drilling, decommissioning, Ground Source Heat Pump wells ('geothermal'), repairs, deepening, yield enhancement, pump installation and replacement. ... It should be noted that performing activities under the regulations cited without being certified in Massachusetts is a violation and the violator(s) subject to enforcement action." | SECTION 12.5 WELL COMPLETION REPORT | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | Town | 2502144105 | Decommissioning |  |  | Section 12.5.1 includes geothermal wells in decommissioning reporting: "Well completion reports must be submitted for all activities covered under 310 CMR 46.00 including ... decommissioning, Ground Source Heat Pump wells ('geothermal')...." Section 12.13.1: "A well which has not been used for two consecutive calendar years shall be considered abandoned. The owner of record of such well shall notify the Board of Health in writing that the well is abandoned and shall have a registered well driller seal the well..." Section 12.13.5: "The owner of a private well shall decommission the well if the well meets any of the following criteria..." Section 12.13.6: "Decommissioning must follow Department of Environmental Protection guidelines." | SECTION 12.5 WELL COMPLETION REPORT; SECTION 12.13 ABANDONMENT, or DECOMMISIONING OF WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Definition: Well |  |  | "WELL OR WATER WELL — Any hole or shaft constructed into the ground for the purpose of extracting or injecting water. This definition shall not include wells to dewater excavations or stabilize hillside or earth embankments. It shall include wells connected to heat pumps." | § 784-3 Definitions | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Definition: Geothermal Heat Pump |  |  | "HEAT PUMP WELL — Consists of a source well and a discharge well which could be one in the same, provided that it is a closed loop system where nothing is added to or taken from the water except heat and no air is in contact with the return water. A heat pump delivers water by way of the source well from an aquifer through a heat exchanger and returns it to the aquifer via the discharge well. The system utilizes the thermal energy stored in groundwater for space heating or cooling." | § 784-3 Definitions | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Setback - Property Lines | 50 | feet | "A water well shall also be a minimum of 50 feet from all property lines." | § 784-8B(2) Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Setback - Wastewater | 175 | feet | The table states: "The minimum setback from a leaching area shall be determined by the soil percolation rate and the vertical clearance of the leaching area above the high groundwater (HGW)." Listed distances from leaching area include "175+" feet for certain conditions, with lower alternatives of 151 to 174, 126 to 150, 100 to 125, 150+, and 125+ feet depending on percolation and HGW. The same section also lists "Septic tank — 50" feet and "Distribution box — 100" feet. | § 784-8B(1) Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Setback - Sewer Lines | 50 | feet | The contaminants table lists "Sewer footing drains with cast-iron watertight joints — 50" feet as a minimum lateral distance. | § 784-8B(1) Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Permit |  |  | "A well construction permit shall be obtained from the Board prior to the construction of any water well or well system." "An application for a water well construction permit shall be submitted by the drilling contractor or his agent..." and "The location, design, and operation of the water well must be approved by the Board... prior to construction." | § 784-7C Well construction permits | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Inspection |  |  | "The pumping test shall be performed by a licensed pump or well drilling contractor and in the presence of the Board agent or member; a minimum of five-gallons-a-minute yield shall be deemed acceptable per dwelling unit." | § 784-19 Yield test | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Licensed Driller |  |  | "No person shall engage in the business of constructing wells within the commonwealth unless he is registered with the Water Resources Commission, Division of Water Resources, as required by the Water Well Drillers Registration Act"; § 784-6 also states "a registered well driller shall submit to the Board a report" within 30 days after completion of any water well. | § 784-5 Registration of well drillers | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | Town | 2502154100 | Other Prohibitions/Regulations |  |  | "The construction of a well in a wetland shall be prohibited." | § 784-8D Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Sharon | Town | 2502160785 | Definition: Geothermal Heat Pump |  |  | "HEAT PUMP WELLS Consists of a source well and a discharge well which could be one and the same, provided it is a closed-loop system where nothing is added to or taken from the water except heat and no air is in contact with the return water. A heat pump delivers water by way of the source well from an aquifer through a heat exchanger, and returns it to the aquifer via the discharge well. The system utilizes the thermal energy stored in groundwater for space heating or cooling." | § 300-16.1C Definitions | 2022 | https://ecode360.com/29557412
Massachusetts | Norfolk | Wellesley | Town | 2502174175 | Setback - Yards | 20 | feet | "Heating, ventilation, air conditioning, swimming pool, electric generating, or other noise emitting equipment shall not be located in required setback areas except for Heat Pumps located in Side Yards or Rear Yards which are attached to and do not extend more than two feet from the wall of the building ... or are ground mounted and do not extend more than four feet from the foundation of the building." Tables 1-3 set yard requirements, including "Minimum Side Yard Width" of 20 ft. in all listed districts/tables, with larger values in some Table 3 districts; rear yards range from 10 ft. to 40 ft. | SECTION 5.3. YARD REGULATIONS | 2022 | https://wellesleyma.gov/DocumentCenter/View/12119/Full-Zoning-Bylaw_Version-10-1-2018
Massachusetts | Norfolk | Wellesley | Town | 2502174175 | Setback - Building Foundation | 4 | feet | "Heating, ventilation, air conditioning, swimming pool, electric generating, or other noise emitting equipment shall not be located in required setback areas except for Heat Pumps located in Side Yards or Rear Yards which are attached to and do not extend more than two feet from the wall of the building ... or are ground mounted and do not extend more than four feet from the foundation of the building, including any pad on which the Heat Pump is mounted." | SECTION 5.3. YARD REGULATIONS | 2022 | https://wellesleyma.gov/DocumentCenter/View/12119/Full-Zoning-Bylaw_Version-10-1-2018
Massachusetts | Norfolk | Wellesley | Town | 2502174175 | Screening |  |  | "Plans and installation of sound reduction and/or visual screening may be required if, in the opinion of the Inspector of Buildings abutters may be affected." | SECTION 5.3. YARD REGULATIONS | 2022 | https://wellesleyma.gov/DocumentCenter/View/12119/Full-Zoning-Bylaw_Version-10-1-2018
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Setback - Property Lines | 25 | feet | "All wells shall be located at sufficient distances from potential sources of pollution... The following minimum lateral distances shall apply... (e) Property lines 25 feet." | § 405-98(A)(1)(e) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Setback - Wastewater | 125 | feet | "All wells shall be located at sufficient distances from potential sources of pollution... The following minimum lateral distances shall apply... (a) Subsurface sewage disposal facilities minimum lateral distance 125 feet; (b) Septic tank 50 feet; (c) Distribution box 50 feet." | § 405-98(A)(1)(a)-(c) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Setback - Sewer Lines | 50 | feet | "All wells shall be located at sufficient distances from potential sources of pollution... The following minimum lateral distances shall apply... (d) Sewers 50 feet." | § 405-98(A)(1)(d) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Minimum Well Depth | 40 | feet | "The casing for a driven or drilled well shall have minimum length of 40 feet." | § 405-99(A) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Permit |  |  | "A well construction permit shall be obtained from the Board of Health prior to the construction of any well." "The purpose for which any well is to be used must be indicated in the application permit." § 405-94(A)(3) lists "Heating and/or cooling" as an allowed use of a private well supply. | § 405-95 Permits |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Licensed Driller |  |  | "Construction of wells in Kingston shall be performed only by well drillers who are registered with the Massachusetts Water Resources Commission, Division of Water Resources, as required by 310 CMR 46.00, Certification of Well Drillers and Filing of Well Completion Reports." | § 405-96 Registration for well drillers |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | Town | 2502333220 | Certification |  |  | § 405-95(B): "Permit shall also include the well driller's name and proof of valid state registration under MGL c. 21G, § 20." § 405-96: wells must be performed by drillers "registered with the Massachusetts Water Resources Commission, Division of Water Resources, as required by 310 CMR 46.00, Certification of Well Drillers and Filing of Well Completion Reports." § 405-93 defines "WELL DRILLER" as a person "licensed by the Massachusetts Water Resources Commission to construct wells." | § 405-95(B); § 405-96; § 405-93 |  | https://ecode360.com/37646456
Massachusetts | Worcester | Harvard | Town | 2502728950 | Screening |  |  | "The placement of buildings and structures in an OSC-PRD should: (a) Provide for maximum buffering of buildings and structures to adjoining properties... Such buffering includes, but is not limited to: landscaping, screening materials, natural barriers, fencing, and related measures." | § 125-35E(1)(a) Building and structure placement | 2023 | https://ecode360.com/13697267
Massachusetts | Worcester | Leominster | City | 2502735075 | Definition: Geothermal |  |  | "Energy system, renewable. Any facility or installation such as a windmill, hydroelectric unit, or solar collecting or concentrating array, which is designed and intended to produce energy from natural forces such as wind, water, sunlight, or geothermal heat, or from biomass, for offsite use." | Section 22-4. Definitions | 2013 | https://leominster-ma.gov/DocumentCenter/View/997
Massachusetts | Worcester | Mendon | Town | 2502740255 | Definition: Well |  |  | "Geothermal Well - Ground source heat pump wells used for heating and cooling; further defined by DEP guidance." | Definitions | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Roads | 10 | feet | The setback table in §5.2(1) states: "Public or Private Way, Common Drive Easement ... 10" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Right of Way | 10 | feet | The setback table in §5.2(1) states: "Public or Private Way, Common Drive Easement ... 10" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Property Lines | 10 | feet | The setback table in §5.2(1) states: "Property Line ... 10" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Building Foundation | 25 | feet | The setback table in §5.2(1) states: "Dwelling Unit (Including Overhang) ... 25" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Wastewater | 100 | feet | Section 5.2(1) sets minimum lateral distances of "Leaching Facility (310 CMR 15.00) ...100," "Existing Cesspool ...100," and "Septic Tank ... 50." Section 5.3(6) also states: "Pump suction lines, if used, shall not be closer than 100 feet from the underground sewage leaching facilities or 50 feet from a septic tank (310 CMR 15.03)." | Well Construction Permit Requirements §5.2(1); §5.3(6) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Animal Enclosures | 100 | feet | The setback table in §5.2(1) states: "Stable and Manure Storage Areas ...100" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Fuel (below ground) | 200 | feet | The setback table in §5.2(1) states: "Underground Storage Tank (Outside Dwelling) ...200" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Sewer Lines | 50 | feet | The setback table in §5.2(1) states: "Sewer Line ... 50" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Setback - Water Bodies | 50 | feet | The setback table in §5.2(1) states: "Any Type of Surface Water ... 50" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Permit |  |  | "No private or semipublic water supply shall be installed, altered or repaired until a permit has been obtained from the Board of Health or its agent." Also, "A well construction/destruction permit shall be obtained from the Board prior to the construction/destruction or abandoning of any private well." Geothermal-specific text states: "A Geothermal well or modifications to the existing well are required to meet DEP Geothermal well guidelines." | Requirements for Private Wells and Semi-Public Water Supplies §3.2; Well Construction or Destruction Permits §§4.3-4.4; Well Construction Permit Requirements §5.1(3) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Inspection |  |  | Section 5.3(5) states: "A minimum yield of five gallons per minute (GPM) for four hours is required. When the pump test is performed, a representative of the Board or its agent may observe the initial startup. Following the pump test the well must be shown to recover to within 85% of the pre-pumped static level within 24 hours." | Well Construction Standards §5.3(5) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Licensed Driller |  |  | "No person shall engage in the business of construction or destruction of private wells within the town under these regulations unless registered as a well driller/digger with the DEP, pursuant to 310 CMR 46.00. A copy of the Well Driller’s License must accompany the application for a Well Permit." | Well Construction or Destruction Permits §4.1 | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Certification |  |  | "No person shall engage in the business of construction or destruction of private wells within the town under these regulations unless registered as a well driller/digger with the DEP, pursuant to 310 CMR 46.00. A copy of the Well Driller’s License must accompany the application for a Well Permit." | Well Construction or Destruction Permits §4.1 | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | Town | 2502740255 | Decommissioning |  |  | The Definitions section states: "Abandonment of Water Well - Decommissioning, removal, or sealing of wells in accordance with MGL Chapter 21G Section 20." Section 5.8(2) states: "Any well now or hereafter abandoned or destroyed, including any well deemed to have been abandoned as defined in this regulation shall be brought into compliance with the requirements of this regulation any applicable rules or regulations with respect to abandonment of wells." Section 6.1 requires abandoned wells, test holes, or borings to be either "Sealed with non-hazardous, impervious materials ... with all exposed casing materials, pumping equipment, and distribution lines removed with the excavation returned to the existing grade" or "Sealed with a welded cap so as to prevent surface water or contaminants from entering the well." Section 6.3 adds: "Within 30 days after the destruction of any well, the well driller/digger shall submit to the Board a report" listing destruction details. | Definitions; Well Destruction §§6.1-6.4; Existing Wells §5.8(2) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) WELL – Well constructed for the purpose of transferring heat to or from the earth for heating and cooling purposes. GSHP wells may be Open-loop, closed-loop, or Direct Exchange." | § 201-10.B. Definitions | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Property Lines | 10 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of ... 10-feet from any property line." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Wastewater | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to, septic tanks/fields, lagoons..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Private Water | 50 | feet | "Closed loop and DX wells shall be sited at least 50-feet from any private potable water supply well... If a dual purpose well, then all Primary Potable water setbacks must be met." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Animal Enclosures | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to ... livestock pens..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Fuel (below ground) | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to ... oil ... storage tanks..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Water Bodies | 10 | feet | "Closed loop and DX wells shall be sited at least ... 10-feet from any surface water bodies." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Setback - Hazardous Materials/Fertilizers | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to ... hazardous materials storage tanks..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Permit |  |  | "No well permit shall be issued for an Open Loop system without a DEP Underground Injection Control Registration Number. Closed Loop and Direct Exchange wells also require a UIC registration unless a Ground-Water discharge permit is required." | § 201-10.O. GSHP Wells UIC Registration | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Licensed Driller |  |  | "Pursuant to 313 CMR 3.00, Water Well Diggers and Drillers Registration Regulations, no person in the business of digging or drilling shall construct a well unless registered with the Department of Environmental Management -- Office of Water Resources." | § 201-10.C(1) Well construction | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | Town | 2502746925 | Certification |  |  | "REGISTERED WELL DRILLER -- Any person registered with the Department of Environmental Management/Office of Water Resources to dig or drill wells in the Commonwealth of Massachusetts." | § 201-10.B. Definitions | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Westborough | Town | 2502775015 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat pump systems (GHPs), including Geo-Exchange, earth-coupled, ground-source, or water-source heat pumps, are deemed suitable for compliance." | (2) Sustainable Design, d. 6 Points: Geothermal heat pumps | 2024 | https://www.town.westborough.ma.us/DocumentCenter/View/4428
Massachusetts | Worcester | Westborough | Town | 2502775015 | Permit |  |  | "Geothermal heat pump systems (GHPs), including Geo-Exchange, earth-coupled, ground-source, or water-source heat pumps, are deemed suitable for compliance." "Hybrid GHP systems, which integrate geothermal energy with other non-fossil fuel systems such as Air Source Heat Pumps, are permissible" under the sustainable design point system. | (2) Sustainable Design, d. 6 Points: Geothermal heat pumps | 2024 | https://www.town.westborough.ma.us/DocumentCenter/View/4428
Michigan | Alger |  | County | 26003 | Definition: Well |  |  | "Well" means "An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." The definition expressly includes "A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Alger |  | County | 26003 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and "shall be constructed in accordance with Michigan Water Well Construction and Pump Installation Code, Ground Water Quality Control (R325.1601 et seq.) ... and the Upper Peninsula of Michigan Geothermal Technical Guidance document." | 5-14 Geothermal Wells | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Allegan | Fennville | City | 2600527740 | Definition: Well |  |  | "WELL: As defined in the Michigan Water Well Construction and Pump Installation Code, Part 127, Act 368 of the public Acts of 1978, as amended, and rules; or a permanent or temporary opening in the surface of the earth for the purpose of removing water, or testing water quality, or measuring water characteristics, or measuring liquid recharge, or measuring liquid levels, or oil and gas exploration or production, or waste disposal, or dewatering purposes; or geothermal heat exchange purposes, or a cistern of a depth of 4 feet or more and with a top width of 12 inches or more." | 00.202 DEFINITIONS | 2025 | https://ecode360.com/FE6693/document/753167860.pdf
Michigan | Allegan | Fennville | City | 2600527740 | Permit |  |  | "General-purpose floor drains shall be connected to a public sewer system or an on-site holding tank (not a septic system) in accordance with state, county and municipal requirements (including Industrial Pretreatment criteria), unless a groundwater discharge permit has been obtained from the Michigan Department of Environmental Quality." | Sec. 00.206 CRITERIA FOR REVIEW | 2025 | https://ecode360.com/FE6693/document/753167860.pdf
Michigan |  | Holland | City | 2600538640 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat pump system using a ground source heat exchanger for heating and cooling." | HOLLAND CIVIC CENTER PRELIMINARY ENERGY MODEL SUMMARY - Executive Summary | 2016 | https://ecode360.com/HO3221/document/295996980.pdf
Michigan | Allegan | Otsego | City | 2600561620 | Definition: Well |  |  | "Well means a permanent or temporary opening in the surface of the earth for the purpose of removing water, or testing water quality, or measuring water characteristics, or measuring liquid recharge, or measuring liquid levels, or oil and gas exploration or production, or waste disposal, or dewatering purposes; or geothermal heat exchange purposes, or a cistern of a depth of 4 feet or more and with a top width of 12 inches or more, or as defined in the Michigan Water Well Construction and Pump Installation Code..." | Sec. 59-4. Definitions | 2021 | https://www.cityofotsego.org/wp-content/uploads/2020/12/Groundwater-Protection-Ordinance-166.pdf
Michigan | Allegan | Otsego | City | 2600561620 | Inspection |  |  | The ordinance states the city will "establish legal authority of the city to carry out all inspection, surveillance and monitoring procedures necessary to ensure compliance with this chapter." | Sec. 59-1. Intent and Purpose | 2021 | https://www.cityofotsego.org/wp-content/uploads/2020/12/Groundwater-Protection-Ordinance-166.pdf
Michigan | Allegan | Plainwell | City | 2600564740 | Permit |  |  | "No person shall construct or install a geothermal heat pump system without first obtaining a permit from the city." "An application for a geothermal permit shall be made to the city on city approved forms." "Permits shall be issued to the owner or an agent thereof for the particular parcel of property on which the geothermal heat pump system is to be constructed and/or installs." | Sec. 39-3. GEOTHERMAL HEAT PUMP SYSTEM PERMIT REQUIRED. | 2014 | https://codelibrary.amlegal.com/codes/plainwellmi/latest/plainwell_mi/0-0-0-4687
Michigan | Allegan | Plainwell | City | 2600564740 | Open-loop Prohibitions |  |  | "No permit shall be issued for any open loop geothermal heat pump system per Section 39-8 below." "Open-loop systems existing prior to the date of the adoption of this chapter shall be allowed." | Sec. 39-3. GEOTHERMAL HEAT PUMP SYSTEM PERMIT REQUIRED. | 2014 | https://codelibrary.amlegal.com/codes/plainwellmi/latest/plainwell_mi/0-0-0-4687
Michigan | Arenac |  | County | 26011 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Baraga |  | County | 26013 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Baraga |  | County | 26013 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Baraga |  | County | 26013 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Baraga |  | County | 26013 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gratiot | Alma | City | 2601540 | Permit |  |  | "No permit for the construction or alteration of a building or structure shall be issued or rezoning petition granted for any property on which a well in violation of this Section has been installed or is proposed to be installed." This applies to geothermal wells because Sec. 22-4 expressly addresses "Geothermal Wells: Professionally installed permanent closed loop wells used for heating/cooling residences and small businesses..." as an exception to the general well prohibition. | Sec.22-8. BUILDING AND ZONING PERMITS | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/10354/1067045/pdf
Michigan | Gratiot | Alma | City | 2601540 | Decommissioning |  |  | "Any well existing as of the effective date of this Section the use of which is prohibited by this Section shall be plugged and abandoned." Also, "Any well the use of which is permitted pursuant to Section 22-4 but which is or becomes nonfunctional shall be plugged and abandoned unless the property upon which such well is located is not served by a municipal potable water treatment and distribution system, in which case the well may be replaced or repaired..." For properties later served by municipal water, Sec. 22-4(5)(b) also states "the use of such well shall be discontinued, the well plugged and abandoned." | Sec. 22-5. ABANDONMENT OF PROHIBITED AND NONFUNCTIONAL WELLS | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/10354/1067045/pdf
Michigan | Gratiot | Alma | City | 2601540 | Open-loop Prohibitions |  |  | Sec. 22-3 states: "Except as provided in Section 22-4, no person shall use, install, allow, permit, or contract or provide for the installation or utilization of, a well within the City of Alma." The geothermal exception in Sec. 22-4 is limited to "Geothermal Wells: Professionally installed permanent closed loop wells used for heating/cooling residences and small businesses..." | Sec. 22-3. PROHIBITION; Sec. 22-4. EXCEPTIONS | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/10354/1067045/pdf
Michigan | Benzie |  | County | 26019 | Definition: Well |  |  | 'Well' means a man-made opening in the surface of the earth used for the purpose of removing ground water. Wells, regulated by this Code, include: ... 'd. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formation for heating or air conditioning.' | Section 2.45 WELL | 2023 | https://www.bldhd.org/media/uploads/Environmental%20Health%20Form/bldhd_-_district_sanitary_code_(1-27-2023).pdf
Michigan |  | Niles | City | 2602157760 | Other Prohibitions/Regulations |  |  | "The following uses and actions are prohibited within the Wellhead Protection Overlay District: ... 10. Installation or use of a geothermal well for heating and cooling systems." | Section 326 - Wellhead Protection Area, D. Prohibited Uses within the Wellhead Protection Overlay District | 2025 | https://cms3.revize.com/revize/nilesmi/FINAL%20City%20of%20Niles%20Zoning%20Ordinance%20[EFFECTIVE%208-17-25].pdf
Michigan | Branch | Bronson | City | 2602310860 | Permit |  |  | § 51.14(C)(3)(b): "Any proposed new well installation must be reviewed and approved by EGLE Superfund (or its successor) staff with notice to U.S. EPA prior to well placement, drilling, and construction." § 51.14(C)(5): "a person shall not install a new non-contact well within a restricted or buffer zone unless the requirements in division (C)(3)(b) above are met" and EGLE recommends in writing that use of the non-contact well will not cause specified contamination or vapor-intrusion impacts, the requester submits EGLE's written recommendation to the city, and "the city... may execute a waiver allowing installation and use of the non-contact well upon such terms and conditions that EGLE may identify or require." | § 51.14(C)(3)(b) Certain industrial use wells; § 51.14(C)(5) New, specific non-contact wells | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Branch | Bronson | City | 2602310860 | Inspection |  |  | For waiver conditions on existing and new non-contact wells, the ordinance states: "Such terms and conditions may include, but are not limited to, hydrogeological evaluations including pump tests"; for new wells, conditions may also include "groundwater modeling." | § 51.14(C)(4)(c); § 51.14(C)(5)(c) | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Branch | Bronson | City | 2602310860 | Decommissioning |  |  | § 51.14(C)(3)(b)1: "If the glacial till aquitard unit is not encountered during drilling, then the well is not to be constructed and the borehole must be properly abandoned." § 51.14(C)(3)(b)2: "If the glacial till aquitard unit is less than the ten feet minimum thickness found to be acceptable by EGLE, then the well is not to be constructed and the borehole must be properly abandoned to prevent any cross-contamination between the shallow and lower aquifers." § 51.14(E)(3)(f) also requires a description and schedule for actions "to properly plug per Well Construction Code any existing wells subject to the use prohibition within the proposed restricted or buffer zones." | § 51.14(C)(3)(b)1.-2.; § 51.14(E)(3)(f) | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Branch | Bronson | City | 2602310860 | Other Prohibitions/Regulations |  |  | § 51.14(B)(1): "no person or legal entity shall install or use or allow, permit, or otherwise provide for the installation or use of a well on any property within the restricted zone... Property within the restricted zone shall be serviced only by public water supply." § 51.14(B)(2): within the buffer zone, "no person or legal entity shall install or use... a well... which well draws its water from the shallow aquifer." Also, "The installation and use of water supply wells located within the buffer zone that draw all their water from the lower aquifer are prohibited." For heat-pump-related use specifically, § 51.14(C)(3)(a) states: "any existing well within the restricted or buffer zone shall not be used to produce industrial cooling or process water, or to service heat pumps unless it meets the requirements of division (C)(4) below." | § 51.14(B) Prohibitions; § 51.14(C)(3)(a) Certain industrial use wells | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Cass |  | County | 26027 | Definition: Well |  |  | 'Well - Means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations or removing ground water for any purpose.' The definition further states: 'A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning.' | 3-42 Well | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass |  | County | 26027 | Permit |  |  | Section 9-4(B) expressly states that a 'water supply construction permit will not be required for ... A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning.' Section 9-4(C) adds: 'All Wells within a Restricted Zone must comply with Section 9-16 regulating Groundwater Use Restricted Zones regardless of whether a construction permit is required.' In the West KLA Landfill GRZ appendix, 'All Wells within the GRZ must be approved by EGLE or U.S. EPA, and the Health Department.' | 9-4 Water Supply Construction Permit Required | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass |  | County | 26027 | Inspection |  |  | The appendix states: 'Existing and new wells will be monitored by the RZ Applicant (the KLA Group) to ensure that the concentration of 1,4-dioxane ... remains below one half of its Michigan drinking water criterion.' | West KLA Landfill Groundwater Restricted Zone (GRZ) - Additional Requirements Specific to this GRZ | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass |  | County | 26027 | Decommissioning |  |  | Section 9-16(H) states: 'Any existing Well, the use of which is prohibited by Paragraph (E) and not granted an exception by Paragraph (F) shall be abandoned ... Any non-conforming Well shall be abandoned within 30 days following establishment of the Restricted Zone.' The GRZ appendix also states: 'Potable supply Wells that are replaced are to be properly abandoned in accordance with the Environmental Health Code.' | 9-16(H) Abandonment of Non-Conforming Wells; West KLA Landfill GRZ - Additional Requirements Specific to this GRZ | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass |  | County | 26027 | Other Prohibitions/Regulations |  |  | Section 9-16(E) provides: 'After the effective date of this Amendment, no Well may be installed, utilized, or allowed, permitted, or otherwise provided for on any Affected Premises. The use of any Well on an Affected Premises or the use of groundwater derived from an Affected Premise is prohibited.' Section 9-16(B)(11)(c) defines 'Heat Exchange Well' as 'a well for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning.' Section 9-16(F) creates only limited exceptions, including: 'Agency Approved Heat Exchange Well: If EGLE determines that the use of a Well for loop geothermal heating/cooling ... will not allow for exposure to contamination or cause migration or exacerbation of Contaminated Groundwater ... such use of the Well under terms and conditions specified by EGLE will be allowed.' | 9-16(E) Prohibition of Wells and Groundwater Use Within a Restricted Zone; 9-16(F) Exceptions | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Clare |  | County | 26035 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan |  | Grand Ledge | City | 2603733420 | Permit |  |  | "before construction of a building or structure, the owner... shall submit an application in writing to the appropriate enforcing agency for a building permit"; "The requirements of the code may provide for issuance of construction permits for certain of the systems of a structure"; and "the construction or alteration of a building or structure shall not be commenced until a building permit has been issued." | 125.1510 Sec. 10(1), (6); 125.1511 Sec. 11(1) | 2014 | https://www.cityofgrandledge.com/DocumentCenter/View/454/State-Construction-Code-Act-PDF
Michigan |  | Grand Ledge | City | 2603733420 | Inspection |  |  | "An enforcing agency shall periodically inspect all construction undertaken pursuant to a building permit issued by it" and inspectors "may enter and inspect the premises and construction thereon" to ensure compliance. The enforcing agency must also give "at least 12 hours' notice of the time of any final inspection... of the work covered by the building permit" pursuant to the certificate of use and occupancy application. | 125.1512 Sec. 12(1)-(2); 125.1513 Sec. 13 | 2014 | https://www.cityofgrandledge.com/DocumentCenter/View/454/State-Construction-Code-Act-PDF
Michigan | Delta |  | County | 26041 | Definition: Well |  |  | "Well" means "[a]n opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." The definition expressly includes "[a] heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. Includes both supply and return wells and the vertical boreholes for closed loop systems." | SECTION 6.1 DEFINITIONS | 2009 | https://cms3.revize.com/revize/deltapublichealth/Documents/Department/Environmental%20Health/On%20Site%20Sewage/PHDM%20Sanitary%20Code.pdf
Michigan | Delta |  | County | 26041 | Permit |  |  | "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply ... without first obtaining a water supply construction permit from the department." Because Section 6.1 defines a well to include "[a] heat exchange well ... for heating or air conditioning" and "the vertical boreholes for closed loop systems," this permit requirement applies to geothermal heat exchange wells within that defined term. | SECTION 6.3 PERMITS / 6.3.2 Construction Permits | 2009 | https://cms3.revize.com/revize/deltapublichealth/Documents/Department/Environmental%20Health/On%20Site%20Sewage/PHDM%20Sanitary%20Code.pdf
Michigan | Delta |  | County | 26041 | Inspection |  |  | Section 6.9.1 states: "The department may inspect the water system construction or well drilling process." It also provides: "An inspection of a new or extensively changed water supply system may be required by the department before the system is put into use." Section 6.9.2 adds that "[t]he final approval of a water supply system shall not be granted until ... [a]n on-site inspection has been conducted and the water supply system is found to be in compliance with this regulation, applicable codes, and permit requirements." Because Section 6.1 includes geothermal "heat exchange well[s]" and closed-loop boreholes within 'well,' these inspection provisions can govern geothermal exchange-well construction. | SECTION 6.9 WELL INSPECTION AND APPROVAL / 6.9.1 Inspection and 6.9.2 Approval | 2009 | https://cms3.revize.com/revize/deltapublichealth/Documents/Department/Environmental%20Health/On%20Site%20Sewage/PHDM%20Sanitary%20Code.pdf
Michigan | Eaton | Delta | Charter Township | 2604521520 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy Systems: A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." | Definitions | 2019 | https://www.deltami.gov/defaults/Government/Ordinances/Delta%20Township%20Zoning%20Ordinance-4-19-21.pdf
Michigan | Genesee |  | County | 26049 | Definition: Well |  |  | "Well" means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include, but are not limited to: ... "A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | SECTION 4.01 - DEFINITIONS; SECTION 4.013 - WELL | 1999 | https://www.geneseecountymi.gov/departments/health_department/services/environmental_health/environmental_health_regulations.php
Michigan | Genesee | Swartz Creek | City | 2604977700 | Definition: Well |  |  | "Well means an opening in the surface of the earth for the purpose of removing fresh water through non-mechanical or mechanical means for any purpose other than a public emergency or conducting response actions that are consistent with" specified environmental statutes. | Definitions - K | 2018 | https://cityofswartzcreekmi.gov/images/2018-02-12-Council-Packet.pdf
Michigan | Genesee | Swartz Creek | City | 2604977700 | Permit |  |  | Section 9(G): "Upon review and approval by the MDEQ, geothermal Wells may be used if no impact by plume or influence on plume will occur with use of Well; or an unauthorized discharge may occur." Section 11 adds: "No influential Well may be used or installed without approval by the MDEQ." | SECTION 9. EXCEPTIONS; SECTION 11. INFLUENTIAL WELLS | 2018 | https://cityofswartzcreekmi.gov/images/2018-02-12-Council-Packet.pdf
Michigan | Genesee | Swartz Creek | City | 2604977700 | Decommissioning |  |  | "Any existing Well, the use of which is prohibited by this Ordinance, shall be plugged or abandoned in conformance with all applicable laws, rules, regulations, permit and license requirements... or... in conformance with the protocol developed consistent with the American Standards for Testing and Materials Standard No. D5299-92. Any non-conforming well shall be plugged within 30 days following establishment of the restricted zone." Section 6(C) also requires "abandonment and plugging" of wells on affected premises. | SECTION 8. NON-CONFORMING WELLS | 2018 | https://cityofswartzcreekmi.gov/images/2018-02-12-Council-Packet.pdf
Michigan | Gladwin |  | County | 26051 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Gogebic |  | County | 26053 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gogebic |  | County | 26053 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply ... without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gogebic |  | County | 26053 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gogebic |  | County | 26053 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368"; "The plugging of any well or dry hole on a parcel containing a well that serves the public, or a residence other than that of the owner, shall be plugged by a State of Michigan registered well-drilling contractor"; and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan |  | Traverse City | City | 2605580340 | Permit |  |  | "No person shall install a private well, without first obtaining a permit from the City Director of Public Services." | Section 1044.14(b) - Prohibitions; permits | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/15455/883088/pdf
Michigan |  | Traverse City | City | 2605580340 | Decommissioning |  |  | "A well meeting the above criteria may be used temporarily for water until the City water service is available within 200 feet of the property, at which time the well shall be properly capped and abandoned... The cost of proper abandonment of a well that was temporarily allowed under this section... shall be the owner's responsibility." | Section 1044.14(c) - Temporary use | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/15455/883088/pdf
Michigan |  | Traverse City | City | 2605580340 | Open-loop Prohibitions |  |  | "A private well for an open loop geothermal system shall be prohibited." | Section 1044.14(b) - Prohibitions; permits | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/15455/883088/pdf
Michigan |  | Barton Hills | Village | 2605660 | Definition: Geothermal |  |  | "Geothermal System: A geothermal system pumps liquid from the ground to equipment which heats and cools buildings." | 2:41 - Definitions | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan |  | Barton Hills | Village | 2605660 | Permit |  |  | "A person may install and operate a closed loop geothermal system only in accordance with the requirements of this section. 1. Prior to the start of construction, a permit must be approved by the County of Washtenaw. 2. Prior to the start of construction, a permit must be approved by the Village Board of Trustees upon a finding that the system complies with this section." | 2:43 - Closed Loop Geothermal System Permitted | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan |  | Barton Hills | Village | 2605660 | Inspection |  |  | "The systems shall be tested hydrostatically at one and one half times the maximum system design pressure. The duration of each test shall be not less than 15 minutes. All geothermal systems must be pressure checked to the original standard by a licensed geothermal contractor, every three years from the certification system date. Results from the test shall be submitted to the Board of Trustees. No person shall operate a system if a test reveals that it is likely to leak the heat transfer liquid." | 2:43 - Closed Loop Geothermal System Permitted | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan |  | Barton Hills | Village | 2605660 | Open-loop Prohibitions |  |  | "No person shall install or maintain an open loop geothermal system in the Village." | 2:42 Open Loop Geothermal System Prohibited | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan | Gratiot | Arcada | Township | 2605703260 | Permit |  |  | 'ZONING PERMIT REQUIRED' appears in Article 18 of the Arcada Township Zoning Ordinance, and Section 18.2 establishes that a zoning permit is required under the ordinance. The ordinance also defines 'ZONING PERMIT' as '[t]he written permit issued by the Zoning Administrator indicating that a proposed structure or use of land is in compliance with the requirements of this Ordinance.' | SECTION 18.2 ZONING PERMIT REQUIRED | 2021 | https://arcadami.gov/wp-content/uploads/2024/01/2021.08.11-Arcada-Ordinance-final.pdf
Michigan | Houghton |  | County | 26061 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton |  | County | 26061 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton |  | County | 26061 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton |  | County | 26061 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ionia | Danby | Township | 2606719720 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM - A system that uses a heat pump to extract heat from the earth in a heating mode and/or reject heat into the earth in a cooling mode." | Section 2.08 Definitions - G | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | Township | 2606719720 | Setback - Property Lines | 10 | feet | "All above-ground equipment shall be a minimum of 10 feet from a side and rear lot line." | Section 3.25 D.1 | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | Township | 2606719720 | Permit |  |  | "Closed-loop geothermal energy systems shall only be approved when an applicant demonstrates compliance with this section, and construction shall only commence after approval by the Zoning Administrator and after the issuance of a mechanical permit by the Ionia County Building Official." | Section 3.25 D. Closed-Loop Geothermal Energy System | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | Township | 2606719720 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems are prohibited in Danby Township." | Section 3.25 C. Open-Loop Geothermal Energy Systems | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | Township | 2606719720 | Other Prohibitions/Regulations |  |  | "All components of a closed-loop geothermal energy system, including associated equipment, shall be located outside of easements, unless allowable per the easement restriction, and shall be outside of all public rights-of-way." | Section 3.25 D.2 | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Ionia | City | 2606740860 | Definition: Geothermal Heat Pump |  |  | "It is recognized that residential buildings in the City may be constructed, or be retrofitted with geothermal heat pumps. It is recognized that these climate control systems use substantial amounts of water. It is also recognized that this water, which for the purposes of this chapter shall be identified as sending water..." | 1040.19 GEOTHERMAL HEAT SYSTEMS | 2025 | https://codelibrary.amlegal.com/codes/ionia/latest/ionia_mi/0-0-0-33038
Michigan | Ionia | Ionia | City | 2606740860 | Open-loop Prohibitions |  |  | "Owners of buildings in the City equipped with geothermal heat pump systems must install a closed loop system that will continuously process (heated or cooled) sending water and circulate it through the enclosed or sealed heat pump system, with no discharge of returning water out of the heat pump." Also, "No sending water from a geothermal heat pump system shall be directly or indirectly discharged out of the closed loop system." | 1040.19(b)-(c) GEOTHERMAL HEAT SYSTEMS | 2025 | https://codelibrary.amlegal.com/codes/ionia/latest/ionia_mi/0-0-0-33038
Michigan | Isabella |  | County | 26073 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Definition: Well |  |  | "WELL. Any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed, or otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into an aquifer. WELL does not include... lateral geothermal heat exchange systems less than 20 feet deep..." Also: "GEOTHERMAL BOREHOLE. A hole drilled or bored into the earth into which piping is inserted for use in a geothermal system." | § 52.51(B) Definitions | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A system for heating and/or cooling buildings using the earth's thermal properties in conjunction with electricity." Also defined are system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A geothermal system that consists of the following basic elements: underground loops of piping; heat transfer fluid; a heat pump, and an air distribution system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A geothermal system in which a borehole extends beneath the surface..."; and "OPEN LOOP GEOTHERMAL SYSTEM. A geothermal system in which groundwater is pumped from a well into a heat exchanger located in a surface building..." | § 52.51(B) Definitions | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Maximum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM... A horizontal closed loop geothermal system shall be no more than 20 feet deep." | § 52.51(B) Definitions | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Permit |  |  | "No person shall: (a) Construct or install a geothermal system; (b) Dig, bore, drill, replace, modify, repair, or destroy a well that is, is intended to be, or was part of a geothermal system; or (c) Make any other excavation that may intersect groundwater without first obtaining a permit from the city and, for construction of a well, the Central Michigan Health Department." "A permit is required for any closed loop horizontal and closed loop vertical geothermal system." "All wells must be permitted by the Central Michigan District Health Department..." | § 52.51(C) Permit required; § 52.51(E) Well permits; § 52.51(G) Permit fee | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Inspection |  |  | "Pipes for geothermal system permitted under this section shall be tested hydrostatically at one and one-half times the maximum system design pressure, but not less than 100 psi (689 kPa), for a duration of not less than 15 minutes. All geothermal systems must be pressure checked by a licensed geothermal system contractor every five years from the date of its initial successful test. Results shall be filed with the City Engineer. If the test results show the system fails to meet these requirements, system shutdown and repairs shall be made at the direction of the City Engineer." | § 52.51(J) System testing | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Licensed Driller |  |  | "Boreholes shall be drilled by Michigan registered/licensed water well drillers." | § 52.51(F)(2) Permit requirements | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Certification |  |  | "Boreholes shall be drilled by Michigan registered/licensed water well drillers." "Borehole piping shall be high density polyethylene as specified in International Ground Source Heat Pump Association standards for closed loop heat pumps." | § 52.51(F)(2); § 52.51(F)(4) | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Decommissioning |  |  | "When a permit is revoked, the property owner shall immediately abandon the geothermal system as required by this section." "Abandonment of a geothermal system shall comply with the laws, rules and regulations applicable to abandonment of water supply wells. Heat transfer fluid must be removed by displacement with grout. The top of the borehole must be uncovered and capped with grout." | § 52.51(H)(4); § 52.51(K) | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | City | 2607356020 | Open-loop Prohibitions |  |  | "No permit shall be issued for any open loop geothermal system because such systems are prohibited by division (I) below." "Permits may be issued only for closed loop geothermal systems." "Open loop geothermal systems are prohibited." | § 52.51(C)(2); § 52.51(F)(1); § 52.51(I) | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Jackson | Norvell | Township | 2607559180 | Permit |  |  | "Permits: PRES are permitted in all zoning districts if they are designed to meet all the required regulations and with approval of a zoning permit under Article 16." | Section 8.2(A)(1) | 2026 | https://norvelltwp-mi.gov/wp-content/uploads/2026/03/Zoning-Ordinance-Final-With-Jan-20-2026-Amendment.pdf
Michigan | Jackson | Norvell | Township | 2607559180 | Decommissioning |  |  | "Abandonment: If abandoned, the system must be removed within one (1) year." | Section 8.2(A)(7) | 2026 | https://norvelltwp-mi.gov/wp-content/uploads/2026/03/Zoning-Ordinance-Final-With-Jan-20-2026-Amendment.pdf
Michigan | Jackson | Waterloo | Township | 2607584300 | Definition: Well |  |  | "Well’ means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... f. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 501.6 Well | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Jackson | Waterloo | Township | 2607584300 | Permit |  |  | "No person shall begin construction of a new water supply, or make extensive changes to existing water supplies, without first obtaining a water supply construction permit from the Jackson County Health Department." Because Section 501.6 defines a well to include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning," this permit requirement expressly reaches geothermal heat exchange wells as a type of well/water supply. | Section 507 Water Supply Construction Permit Required | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Jackson | Waterloo | Township | 2607584300 | Inspection |  |  | "The Health Officer shall make inspections of water supplies during and/or after completion of construction as deemed necessary. It shall be the responsibility of the well driller to notify the Health Officer of the dates and times the well will be ready for the required inspections. Well drillers may be required to notify the Health Officer of the dates and times the well will be under construction." Under Section 501.6, wells include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 512 Inspection | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Jackson | Waterloo | Township | 2607584300 | Decommissioning |  |  | "The Health Officer may require the abandonment of a well that is constructed without a permit or is constructed in violation of this code or permit requirements." In addition, "Any abandoned well shall be properly filled and sealed to prevent it from becoming a hazard or serving as a channel for possible contamination of groundwater or the escape of subterranean gases. Procedures to be followed in properly filling and sealing an abandoned water well shall be approved by the Health Officer..." Section 501.6 includes "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning" within the definition of well. | Section 516 Well Abandonment | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Kalamazoo |  | County | 26077 | Definition: Well |  |  | 'Well' means an opening in the surface of the earth for the purpose of removing fresh water for a water supply well, test well, irrigation well, recharge well, industrial well, and heat exchange well. | SECTION 3.92 | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo |  | County | 26077 | Definition: Geothermal Heat Pump |  |  | 'Heat exchange well' means a well for the purpose of utilizing the geothermal properties of earth formations for heating or cooling. | SECTION 3.39 | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo |  | County | 26077 | Permit |  |  | 'Additionally, no person shall construct a heat exchange well, industrial well, irrigation well, recharge well, or test well where the installed pumping equipment produces less than 70 gallons per minute without obtaining a water supply system construction permit from the Department.' | SECTION 14.03: PERMIT FOR WATER SUPPLY SYSTEMS | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo |  | County | 26077 | Inspection |  |  | 'The Department shall inspect all new water supply system installations to determine if the construction complies with the provisions of this Code.' | SECTION 14.10: INSPECTION AND APPROVAL | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo |  | County | 26077 | Other Prohibitions/Regulations |  |  | CHAPTER 24b states: 'Except as provided in CHAPTER 25b of this Code, no person shall install or utilize, or allow, permit, or provide for the installation or utilization of a well in any Restricted Zone. Except as provided in CHAPTER 25b of this Code, no person shall use any groundwater from any well located within a Restricted Zone.' SECTION 25b.06 further states: 'After the establishment of a Restricted Zone under this Code, the Department an individual shall not install a new well to be used for noncontact heating, cooling or processing activities within a Restricted Zone unless all of the following conditions are present...' | CHAPTER 24b; SECTION 25b.06 | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kent |  | County | 26081 | Definition: Well |  |  | "'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states wells include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 2.13 - Well | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent |  | County | 26081 | Permit |  |  | Section 7.0: "No person shall begin construction of a new water supply, or make extensive changes to existing water supplies, without first obtaining a water supply construction permit from the Kent County Health Department." Section 8.0: "If multiple wells of a similar nature are proposed to be constructed for the same project, a single project permit may be issued to cover all of the wells in the project." Section 12.1: "The Health Officer may issue a water supply construction permit..." and "may impose limitations or conditions..." Section 17.0: in emergencies, "a registered well driller may begin extensive changes to or construction of a new water supply without prior notification or without first obtaining a permit," but "must contact the Health Officer on the next regular working day to obtain a permit." | SECTION 7.0 - WATER SUPPLY CONSTRUCTION PERMIT REQUIRED; SECTION 8.0 - PROJECT PERMIT; Section 12.1 - Issuance; Section 17.0 - Emergency Conditions | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent |  | County | 26081 | Inspection |  |  | Section 14.0: "The Health Officer may inspect water supplies during and/or after completion of construction, as determined necessary by the Health Officer." Section 15.0 provides that "A new water supply shall not be placed into service until the construction and installation have been approved by the Health Officer" and requires that "An on-site inspection has been completed by the Health Officer, and the water supply is found to be in compliance with applicable regulations and permit requirements." | SECTION 14.0 - INSPECTION; SECTION 15.0 - APPROVAL | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent |  | County | 26081 | Licensed Driller |  |  | In an emergency, "a registered well driller may begin extensive changes to or construction of a new water supply without prior notification or without first obtaining a permit. However, the well driller must contact the Health Officer on the next regular working day to obtain a permit..." | SECTION 17.0 - EMERGENCY CONDITIONS | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent |  | County | 26081 | Decommissioning |  |  | "The Health Officer may require the proper abandonment of a well that is constructed without a permit or is constructed in violation of these regulations or permit requirements." | SECTION 11.0 - PLUGGING OF WELL | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent | Cedar Springs | City | 2608114200 | Decommissioning |  |  | "Well abandonment. When a well is plugged, formal well abandonment logs must be completed and provided to the city's department of public works, except in cases where wells were abandoned in the past and no well abandonment logs are available." Also, Sec. 14-403(7) states: "Allow the presence of an abandoned well ..." is prohibited, and "A well shall not be considered abandoned if it has been properly closed pursuant to state law." | Sec. 14-404. Requirements and restrictions within the wellhead protection zone. | 2021 | https://cityofcedarsprings.org/wp-content/uploads/2021/11/Cedar-Springs-Code-with-STUL.pdf
Michigan | Kent | Cedar Springs | City | 2608114200 | Other Prohibitions/Regulations |  |  | "Within the WHPZ, no person shall, nor cause or allow another over whom that person has control, to: ... (8) Install or use a geothermal well for heating and cooling systems." | Sec. 14-403. Prohibited activities within the wellhead protection zone. | 2021 | https://cityofcedarsprings.org/wp-content/uploads/2021/11/Cedar-Springs-Code-with-STUL.pdf
Michigan | Kent | Plainfield | Charter Township | 2608164660 | Other Prohibitions/Regulations |  |  | "The following uses and actions are prohibited within the Wellhead Protection Overlay district... K. Installation or use of a geothermal well for heating and cooling systems." | SECTION 27.03 - SPECIFICALLY PROHIBITED USES AND ACTIONS | 2006 | https://www.plainfieldmi.org/DocumentCenter/View/339/Zoning-Ordinance---May-18-2025-PDF
Michigan | Keweenaw |  | County | 26083 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Keweenaw |  | County | 26083 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Keweenaw |  | County | 26083 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Keweenaw |  | County | 26083 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Lapeer | Arcadia | Township | 2608703280 | Definition: Geothermal Heat Pump |  |  | "It is recognized that certain residential structures in the Township are being equipped with geothermal heat pumps. It is further recognized that geothermal heat pumps use water which, if not properly drained, can cause excess wetness or flooding on nearby properties, resulting in undesirable conditions." | Section 1. GEOTHERMAL HEAT PUMPS |  | https://www.arcadiatownship.org/images/Ordinances/ArcadiaTwp-Ord-2200-Geothermal-Drainage.pdf
Michigan | Lapeer | Arcadia | Township | 2608703280 | Other Prohibitions/Regulations |  |  | Section 2 requires owners with geothermal heat pumps to do one of the following: "1 Install a drain system that will contain the water on the owner’s property so as to prevent the drainage of water onto other parcels of land. 2, Install a drain system that will direct any excess water into a lake, stream, spring fed pond, or a public drain under the jurisdiction of the Lapeer County Drain Commissioner. 3. Install a closed loop system that recirculates geothermal heat pump water rather than discharge the water." Section 3 adds: "No drainage from geothermal heat pumps shall be directly or indirectly onto any road right-of-way or road ditch." | Section 2. DRAINAGE; Section 3. ROAD RIGHT-OF-WAY |  | https://www.arcadiatownship.org/images/Ordinances/ArcadiaTwp-Ord-2200-Geothermal-Drainage.pdf
Michigan | Leelanau |  | County | 26089 | Definition: Well |  |  | 'Well' means a man-made opening in the surface of the earth used for the purpose of removing ground water. Wells, regulated by this Code, include: ... 'd. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formation for heating or air conditioning.' | Section 2.45 WELL | 2023 | https://www.bldhd.org/media/uploads/Environmental%20Health%20Form/bldhd_-_district_sanitary_code_(1-27-2023).pdf
Michigan | Luce |  | County | 26095 | Definition: Well |  |  | "Well" means "[a]n opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." It further states wells include "[a] heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Luce |  | County | 26095 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and "shall be constructed in accordance with Michigan Water Well Construction and Pump Installation Code..." | 5-14 Geothermal Wells | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Luce |  | County | 26095 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "[a]n inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." Because 5-14 provides that "Vertical closed-loop geothermal wells shall be permitted as a water well," these water-well inspection provisions apply to those geothermal wells when permitted as water wells. | 5-3.2 Construction Permits; 5-9.1 Inspection | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Luce |  | County | 26095 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." Also, "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac |  | County | 26097 | Definition: Well |  |  | "Well" means "An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." It expressly includes "A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac |  | County | 26097 | Permit |  |  | Section 5-14 states: "Vertical closed-loop geothermal wells shall be permitted as a water well." Section 5-3.2 adds: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells; 5-3.2 Construction Permits | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac |  | County | 26097 | Inspection |  |  | Section 5-3.2(H) states: "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac |  | County | 26097 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "The plugging of any well or dry hole on a parcel containing a well that serves the public, or a residence other than that of the owner, shall be plugged by a State of Michigan registered well-drilling contractor." | 5-16 Well Abandonment and Plugging | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Macomb | Eastpointe | City | 2609924290 | Setback - Property Lines | 5 | feet | 'Accessory uses and structures such as ... heat pumps, and other mechanical equipment ... must be set back a minimum of five feet from the property line.' | Section 7.01(A)(2) Accessory Buildings | 2026 | https://www.eastpointemi.gov/EastpointeZoningOrdinance_Amended%20Through%20March%2016%202026.pdf
Michigan | Monroe |  | County | 26115 | Definition: Well |  |  | "'Well' is defined as an opening in the surface of the earth for the purpose of: obtaining groundwater, monitoring the quality or quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations or removing groundwater for any purpose. Wells as defined in this section shall include: ... (c) A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning;" | 300.10 Well |  | https://www.co.monroe.mi.us/DocumentCenter/View/745/Chapter-3-of-the-Monroe-County-Environmental-PDF
Michigan | Muskegon | Montague | City | 2612155100 | Definition: Well |  |  | "Well means an opening in the surface of the earth for the purpose of removing fresh water through non-mechanical or mechanical means for any purpose other than a public emergency or conducting response actions..." | Sec. 82-142. Definitions. | 2020 | https://cityofmontague.org/wp-content/uploads/2019/12/Chapter_82_UTILITIES_20191216.pdf
Michigan | Muskegon | Montague | City | 2612155100 | Decommissioning |  |  | "Any existing well at the time of the enactment of a restricted zone on any affected parcel within that restricted zone shall be plugged/abandoned... in accordance with applicable laws, regulations and ordinances" unless an exception applies. Sec. 82-148 adds that the owner "shall immediately take steps" to comply for domestic use water within 365 days from notice and that "Any existing well in violation of this division shall then be plugged or abandoned in conformance with applicable legal requirements." Sec. 82-149 states "any well in violation of this division shall be immediately taken out of service and lawfully abandoned in compliance with applicable legal requirements." | Sec. 82-145. Prohibition.; Sec. 82-148. Enforcement.; Sec. 82-149. Penalty. | 2020 | https://cityofmontague.org/wp-content/uploads/2019/12/Chapter_82_UTILITIES_20191216.pdf
Michigan | Muskegon | Montague | City | 2612155100 | Other Prohibitions/Regulations |  |  | "Except as provided in section 82-146 no person shall install or utilize, or allow, permit, or provide for the installation or utilization of a well on any affected parcel; or use any groundwater from an affected parcel." This applies within the restricted zone established by Sec. 82-143. | Sec. 82-145. Prohibition. | 2020 | https://cityofmontague.org/wp-content/uploads/2019/12/Chapter_82_UTILITIES_20191216.pdf
Michigan | Oakland | Farmington | City | 2612527380 | Permit |  |  | "Any owner or owner's authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical ... system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." The mechanical residential fee table also specifically lists geothermal entries: "Geothermal: Plans Required"; "Heat Pump $50.00"; "Plan Review if Required Minimum $50.00". | SECTION 8 - MECHANICAL FEES | 2019 | https://www.farmgov.com/media/1uipszhv/1072019-_191007.pdf
Michigan | Oakland | Farmington | City | 2612527380 | Inspection |  |  | The mechanical residential fee table expressly includes geothermal inspection/test items: "Geothermal: Plans Required"; "Manifold Test - Underground $75.00"; and a general mechanical "Observable / Re-Inspection $50.00." | SECTION 8 - MECHANICAL FEES | 2019 | https://www.farmgov.com/media/1uipszhv/1072019-_191007.pdf
Michigan | Oakland | Ferndale | City | 2612527880 | Definition: Geothermal |  |  | "Geothermal Energy. A closed loop system that uses buried high-density polyethylene (HDPE) plastic piping installed in drilled and grouted boreholes that conductively exchanges thermal (heat) energy with the ground via circulating water or a water/antifreeze mixture through the piping system." | Article 20. Glossary – Definitions G-H | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Oakland | Ferndale | City | 2612527880 | Setback - Property Lines | 10 | feet | For "Ground-Source Heat Pump Systems (either vertical or horizontal loops)," the code states: "Allowed in all yards, however, the setback for private system ground loops must be a minimum of 10-feet from all lot lines." It also states: "The setback for groundloops within a networked system that are adjacent to a co-participating lot (that is also served by the networked GSHP system) can be setback a maximum of 5-feet." | Section 3.04 Accessory Structures: Distributed Energy Systems | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Oakland | Ferndale | City | 2612527880 | Permit |  |  | In the 'Distributed Energy Resource (DER) Uses' table under 'Heat Pump Systems (HPS),' "Ground-Source (Single Lot)" is listed as "S" in R-1 and R-2, while "Networked Ground-Source" is listed as "P" in all districts and "Ground-Source (Single Lot)" is "-" in CBD. | Section 2.05 Schedule of Permitted Uses | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Oakland | Ferndale | City | 2612527880 | Other Prohibitions/Regulations |  |  | In the 'Distributed Energy Resource (DER) Uses' table under 'Heat Pump Systems (HPS),' "Ground-Source (Single Lot)" is marked "-" in the CBD district, and the code states in Section 1.04(B): "Any use not expressly permitted within the Schedule of Permitted Uses is prohibited." | Section 2.05 Schedule of Permitted Uses | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Ontonagon |  | County | 26131 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ontonagon |  | County | 26131 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ontonagon |  | County | 26131 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ontonagon |  | County | 26131 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Osceola |  | County | 26133 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Roscommon | Gerrish | Township | 2614331960 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Roscommon | Roscommon | Township | 2614369560 | Permit |  |  | "Any building moved into Roscommon Township shall conform to this Ordinance and require a Land Use Permit from the Zoning Administrator." | SECTION 1.4 REGULATED STRUCTURES AND USES | 2025 | https://roscommontownshipmi.gov/wp-content/uploads/2025/09/Zoning-Ordinance-86-Rev-July-2025.pdf
Michigan | Saginaw | Buena Vista | Charter Township | 2614511560 | Noise Limits | 50 | dBA | 'Sound emitted by any source is considered a noise disturbance when its average A-weighted sound level exceeds the limit set forth for the receiving zoning district... Residential Districts 7:00 a.m. to 10:00 p.m. 55 dB(A); 10:00 p.m. to 7:00 a.m. 50 dB(A). Non-Residential Districts 7:00 a.m. to 6:00 p.m. 62 dB(A); 6:00 p.m. to 7:00 a.m. 55 dB(A).' | Section 509(C)(3) | 2026 | https://www.bvct.org/2300112%20-%20Adopted%20Zoning%20Ordinance%20Bueva%20Vista%20Township%20Eff%203-25-26.pdf?t=202604070758250
Michigan | St. Clair | East China | Township | 2614723820 | Setback - Yards | 3 | feet | "A central air-conditioning condenser unit, heat pump, or any other noise-producing mechanical system components which are typically required to be located on the exterior of the house shall be located within three feet of the main building within the rear yard, and clear of side yard setbacks." | § 480-61(P)(1) Heating and/or cooling units located outside of single-family homes | 2023 | https://ecode360.com/9688304
Michigan | St. Clair | East China | Township | 2614723820 | Setback - Building Foundation | 3 | feet | "A central air-conditioning condenser unit, heat pump, or any other noise-producing mechanical system components which are typically required to be located on the exterior of the house shall be located within three feet of the main building within the rear yard, and clear of side yard setbacks." | § 480-61(P)(1) Heating and/or cooling units located outside of single-family homes | 2023 | https://ecode360.com/9688304
Michigan | St. Clair | East China | Township | 2614723820 | Permit |  |  | "Administrative review and approval of a plot plan by the Building Official ... is required before a building permit may be issued for ... (b) Accessory structures and uses in any zoning district." | § 480-72(A)(1)(b) Site plan review | 2023 | https://ecode360.com/9688304
Michigan | Schoolcraft |  | County | 26153 | Definition: Well |  |  | "Well" means "An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." It expressly includes "A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Schoolcraft |  | County | 26153 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and shall be constructed in accordance with listed state code and guidance documents. | 5-14 Geothermal Wells | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Schoolcraft |  | County | 26153 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9.1 Inspection | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Schoolcraft |  | County | 26153 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." Also, "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Shiawassee |  | County | 26155 | Definition: Well |  |  | "Well means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... f) A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 400.13 - WELL | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee |  | County | 26155 | Permit |  |  | "No person shall begin construction of a new water supply, or make extensive changes to existing water supplies, without first obtaining a Water Supply Construction Permit from the Shiawassee County Health Department." Section 400.13 defines a well to include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | SECTION 450 - WATER SUPPLY CONSTRUCTION PERMIT REQUIRED | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee |  | County | 26155 | Inspection |  |  | Section 493: "The Health Officer may make inspections of water supplies during and/or after completion of construction as deemed necessary." Section 494(a): "A new water supply shall not be approved by the Health Officer until ... An on-site inspection has been completed by the Health Officer, and the water supply is found to be in compliance with applicable code and permit requirements." | SECTION 493 - INSPECTION; SECTION 494 - APPROVAL | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee |  | County | 26155 | Licensed Driller |  |  | "...when the well driller is involved with repair work and it is deemed necessary to begin construction immediately on a new well, a registered well driller may begin extensive changes to or construction of a new water supply without notification or permit." | SECTION 496 - EMERGENCY CONDITIONS | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee |  | County | 26155 | Certification |  |  | "...a registered well driller may begin extensive changes to or construction of a new water supply without notification or permit." | SECTION 496 - EMERGENCY CONDITIONS | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Washtenaw | Pittsfield | Charter Township | 2616164560 | Permit |  |  | The ordinance states generally that a person who intends "to erect, install, enlarge, alter, repair, remove, convert, or replace any ... mechanical ... system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." It then creates a geothermal-specific exemption under mechanical permits: "Mechanical permits shall not be required for any of the following: ... When installing geothermal vertical closed loops under the supervision of a mechanical contractor licensed in HVAC as long as the company meets both of the following: - Has obtained a certificate of registration as a well drilling contractor - Has installed the geothermal vertical closed loops in accordance with the department of environmental quality's best practices regarding geothermal heat pump closed loops." | Required Permits / Work Exempt from Permits |  | https://www.pittsfield-mi.gov/152/Required-Permits
Michigan | Washtenaw | Pittsfield | Charter Township | 2616164560 | Certification |  |  | For the geothermal mechanical-permit exemption, the company must have "obtained a certificate of registration as a well drilling contractor" and must install the loops "under the supervision of a mechanical contractor licensed in HVAC." | Work Exempt from Permits |  | https://www.pittsfield-mi.gov/152/Required-Permits
Michigan | Wayne | Wyandotte | City | 2616388900 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. All the pipes, valves, headers, and other equipment and material, required for the purpose of constructing a vertical heat exchanger (VHE), or ground source heat pump loop system, installed in the city right-of- way for the purpose of providing a renewable source of energy for heating and cooling systems in residential, commercial and industrial buildings." Also: "PRIVATE GEOTHERMAL SYSTEM. All the pipes, valves, headers and other equipment and material, required for the purpose of constructing a vertical heat exchanger (VHE), or ground source heat pump loop system, installed on private property for the purpose of providing a renewable source of energy for heating and cooling systems in residential, commercial and industrial buildings." | § 180.002 DEFINITIONS. | 2010 | https://codelibrary.amlegal.com/codes/wyandotte/latest/wyandotte_mi/0-0-0-11451
Michigan | Wayne | Wyandotte | City | 2616388900 | Permit |  |  | "A plumbing permit shall be required prior to the installation, alteration or modification of vertical heat exchangers and ground source heat pump loop systems." "(A) The permit shall be secured from the City Engineer." "(B) No alterations or additions shall be made to an existing vertical heat exchanger or ground source heat pump loop system after installation and inspection without first notifying the City Engineer and securing a permit thereof." "(C) Division (A) above shall not apply to repair work of valves and fittings." | § 180.020 PERMIT REQUIRED. | 2010 | https://codelibrary.amlegal.com/codes/wyandotte/latest/wyandotte_mi/0-0-0-11451
Michigan | Van Buren | Decatur | Village | 2621040 | Permit |  |  | "Before any connection is made to any water main, application for a permit must be made in writing by the owner of the premises to be served, or by his, her or their authorized representative at the office of the Village Clerk." This applies to geothermal-related premises only where Section 3.1(e) allows a private well to be maintained on premises connected to the System if "the premises maintains a closed geothermal heating system and the private well is an integral part of said system." | Section 3.2(a) Permit Application | 2020 | https://cms5.revize.com/revize/decatur/Document_Center/Forms/Ordinances/Ordinance-2020-001-Water-System.pdf
Michigan | Kalkaska | Kalkaska | Village | 2642260 | Definition: Well |  |  | "'Well' means any opening in the surface of the earth for the purpose of removing fresh water or a test well, recharge well, waste disposal well, or a well-used temporarily for dewatering purposes during construction... and also including all of the following: ... (3) 'Heat Exchange Well' means a well for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | §51.66(2)(e) Definitions | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | Village | 2642260 | Permit |  |  | "No permit for construction or alteration of a building or structure, nor any permit for any zoning approval, shall be issued for any improvement on an affected parcel which has, or proposes, a water supply from a well in violation of this Ordinance." | §51.66(10) Building and Zoning Permits | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | Village | 2642260 | Inspection |  |  | "The Village Manager or other authorized Village representative may enter the lands upon which any well subject to this Ordinance is situated or proposed, for the purposes of inspecting those lands and well and for maintaining compliance with the provisions of this Ordinance." | §51.66(11) Enforcement | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | Village | 2642260 | Decommissioning |  |  | §51.66(6): "Any existing well at the time of the enactment of a restricted zone on any affected parcel within that restricted zone shall be plugged at the expense of the applicant for that particular restricted zone... unless such existing well falls within one of the exceptions listed in Section 7." §51.66(8): "Any existing well, the use of which is prohibited by Section 6 or is otherwise an abandoned water well, shall be plugged in conformance with all applicable laws, rules, regulations, permit and license requirements, orders and directives of any governmental entity or agency of competent jurisdiction." | §51.66(6) Wells and Groundwater Use Prohibition; §51.66(8) Plugging of Non-Conforming Wells | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | Village | 2642260 | Closed-loop Prohibitions |  |  | "Heat Exchange Well - Vertical Closed Loop Geothermal. The Village of Kalkaska shall not allow the use of a vertical closed loop geothermal well within a restricted zone unless an exception to the restrictions is granted." | §51.66(7)(6) Exceptions to Prohibition of Well Use | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Minnesota | Anoka | Andover | City | 2700301486 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEM: An energy transfer of generating system such as ground source heat pump, wind or solar energy system." | 9-14-2: DEFINITIONS | 2024 | https://www.andovermn.gov/DocumentCenter/View/256/Title-9---Building-Regulations-PDF-
Minnesota | Anoka | Andover | City | 2700301486 | Permit |  |  | "Water-fed Heat Extractors and Air Conditioning Equipment may be installed only in accordance with the city, county, state and federal law." | 9-2-1: WATER-FED HEAT EXTRACTORS AND AIR CONDITIONING EQUIPMENT | 2024 | https://www.andovermn.gov/DocumentCenter/View/256/Title-9---Building-Regulations-PDF-
Minnesota | Anoka | Nowthen | City | 2700347536 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." The ordinance also defines related GHP types: "Closed loop ground source heat pump system: A system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." "Open loop ground source heat pump system: A system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." "Horizontal ground source heat pump system: A closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." "Vertical ground source heat pump system: A closed loop ground source heat pump system where the loops or coils are installed vertically in one or more borings below the land surface." | 11-2-2: TERMS | 2025 | https://www.cityofnowthen.gov/media/196
Minnesota |  | Royalton | City | 2700956176 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system means a system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." Also: "Closed loop ground source heat pump system means a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface." "Open loop ground source heat pump system means a system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | 18.03 - Definitions | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least eight feet from interior side lot lines and at least ten feet from rear lot lines." | 18.04(b)(2) - Setbacks | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Setback - Yards | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least eight feet from interior side lot lines and at least ten feet from rear lot lines." Also, "Above-ground equipment associated with ground source heat pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable zoning district." | 18.04(b)(2) - Setbacks | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Maximum Well Depth | 20 | feet | "Horizontal ground source heat pump system means a closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." | 18.03 - Definitions | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Permit |  |  | "A building permit and interim conditional use permit, if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." | 18.04(e) - Permits | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of Ordinance 47 Sec. 9." | 18.04(b)(5) - Screening | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code and the Minnesota Department of Health." | 18.04(c) - Safety | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... (1) The heat pump and any external mechanical equipment shall be removed. (2) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted. (3) Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 18.04(d) - Abandonment | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in section 18.03 are permitted. Open loop ground source heat pump systems are not permitted." | 18.04(b)(1) - System requirements | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | City | 2700956176 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the City of Royalton are not permitted." | 18.04(b)(1) - System requirements | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Sartell | City | 2700958612 | Permit |  |  | "Geothermal system. 1. Permitted accessory use in all zoning districts on the condition it meets the requirements of this Section and other provisions of the Code." | 10-8-17: GEOTHERMAL, SOLAR, AND WIND ENERGY CONVERSION SYSTEMS; A. Geothermal system. |  | https://cms5.revize.com/revize/sartell/TITLE%2010%20ZONING%20REGULATIONS%20RV%202024.pdf
Minnesota | Carver |  | County | 27019 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | § 152.010 DEFINITIONS. | 2024 | https://codelibrary.amlegal.com/codes/carvercounty/latest/carverco_mn/0-0-0-3098
Minnesota | Carver | Hamburg | City | 2701926666 | Permit |  |  | The ordinance allows geothermal only as an accessory use in listed districts: "Solar collection and geo-thermal heating and cooling systems used in conjunction with permitted uses" are permitted accessory uses in the A-1, R-1, R-2, B, and I districts. It also states: "Uses not specifically identified in this ordinance as a permitted use, a conditional use, an interim use or accessory use shall be prohibited." Separately, "It shall be unlawful to use any structure or land for any purpose requiring a conditional use permit in the zoning district in which the property is located without first obtaining a conditional use permit from the city." | SECTION C. ADMINISTRATION AND ENFORCEMENT, Subdivision 6. Conditional Use Permit; SECTION D. GENERAL PROVISIONS, Subdivision 1; SECTION E, Subdivisions 3-7 | 2009 | http://www.cityofhamburgmn.com/Forms/Ordinance%20Number%20133%20(Zoning).pdf
Minnesota | Carver | Hamburg | City | 2701926666 | Other Prohibitions/Regulations |  |  | "Uses not specifically identified in this ordinance as a permitted use, a conditional use, an interim use or accessory use shall be prohibited." Geothermal is expressly listed only as an accessory use: "Solar collection and geo-thermal heating and cooling systems used in conjunction with permitted uses." | SECTION D. GENERAL PROVISIONS, Subdivision 1. Uses Not Provided for Within a Zoning District | 2009 | http://www.cityofhamburgmn.com/Forms/Ordinance%20Number%20133%20(Zoning).pdf
Minnesota | Carver | Mayer | City | 2701941138 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | Section 152.003 - Definitions | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM (GSHPS). A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site." | Section 152.003 - Definitions | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Setback - Property Lines | 10 | feet | "All components of Ground Source Heat Pump Systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | Section 152.102(B)(3) - Location | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Setback - Yards | 10 | feet | "Ground Source Heat Pump Systems shall only be located in the rear yard as defined by the City of Mayer zoning ordinance." Also, "All components of Ground Source Heat Pump Systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | Section 152.102(B)(3) - Location | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Permit |  |  | "A building permit shall be obtained for any Ground Source Heat Pump System prior to installation." Also, "Borings for Ground Source Heat Pump System where the pipes or coils are installed vertically below the land shall also be subject to approval by the Minnesota Department of health." | Section 152.102(B)(8) - Building Permit | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Screening |  |  | "Ground Source Heat Pump Systems installed for use in a commercial, industrial or institutional uses are considered mechanical equipment and shall be screened in accordance with the requirements of the City's zoning ordinance, if required. Ground source heat pumps installed for residential use shall be exempt from the screening requirement." | Section 152.102(B)(4) - Screening | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Certification |  |  | "The Ground Source heat Pump System shall be certified by Underwriters Laboratories, inc., and comply with the requirements of the international building code." | Section 152.102(B)(6) - Certification | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Decommissioning |  |  | "Any Ground Source Heat Pump System which is inoperable for twelve (12) successive months shall be deemed to be abandoned and shall be deemed a public nuisance. The owner shall remove the abandoned system at their expense after obtaining a demolition permit." Further: "The heat pump and any external or aboveground mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid, which is to be captured and disposed of in accordance with state and federal regulations"; and "The top of the pipe, coil or boring shall be uncovered and sealed." | Section 152.102(B)(7) - Abandonment | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Open-loop Prohibitions |  |  | "All Ground Source heat Pump Systems shall be closed loop systems that circulate heat transfer fluids as allowed by this section through pipes or coils buried beneath the land surface." The ordinance also defines "OPEN LOOP GROUND SOURCE HEAT PUMP SYSTEM" separately, but the operative rule requires all GHP systems to be closed loop. | Section 152.102(B)(2) - System Requirements | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | City | 2701941138 | Other Prohibitions/Regulations |  |  | "Ground Source Heat Pump Systems in public water bodies or water bodies owned or managed by the City of Mayer shall be prohibited except for stormwater ponds managed by the City of Mayer and when accessory to a City of Mayer facility." | Section 152.102(B)(1)(b) - Accessory Use | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | New Germany | City | 2701945556 | Permit |  |  | Accessory uses in multiple districts expressly include "Solar collection and geo-thermal heating and cooling systems used in conjunction with permitted uses" in the A - Agricultural District, R-1 Single Family Residential District, R-2 Multiple Family Residential District, B - Business/Commercial District, and I - Industrial District. In the PUD District, "All permitted uses and accessory uses of the R-1 Single Family Residential District and R-2 Multiple Family Residential District are allowed" in residential areas, and "All permitted uses and accessory uses of the B - Business/Commercial District" and "I- Industrial District" are allowed in commercial and industrial areas of the PUD District. | CHAPTER VIII, Section 2 (Zoning District Regulations) | 2011 | http://cityofnewgermany.com/wp-content/uploads/2018/04/Ordinance-100-final.pdf
Minnesota | Ramsey | Arden Hills | City | 2702026 | Definition: Geothermal |  |  | "Geothermal energy - Hot water or steam extracted from geothermal reservoirs in the earth's crust. Water or steam extracted from geothermal reservoirs can be used for geothermal heat pumps, water heating, or electricity generation." | Exhibit V - Definitions |  | https://codelibrary.amlegal.com/codes/ardenhills/latest/ardenhills_mn/0-0-0-14021
Minnesota | Ramsey | Arden Hills | City | 2702026 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump - A heat pump in which the refrigerant exchanges heat (in a heat exchanger) with a fluid circulating through an earth connection medium (ground or ground water). The fluid is contained in a variety of loop (pipe) configurations depending on the temperature of the ground and the ground area available. Loops may be installed horizontally or vertically in the ground or submersed in a body of water." | Exhibit V - Definitions |  | https://codelibrary.amlegal.com/codes/ardenhills/latest/ardenhills_mn/0-0-0-14021
Minnesota | Chisago | Chisago City | City | 2702511350 | Definition: Geothermal |  |  | "Geothermal Energy. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | 6.12 C. Geothermal Energy Sources and Systems, 1. Definitions | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | City | 2702511350 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Ground Source Heat Pump System. A system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." Also: "Ground Source Heat Pump System (GSHPS). A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site." | 6.12 C. Geothermal Energy Sources and Systems, 1. Definitions | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | City | 2702511350 | Permit |  |  | "A building permit is required with all new installation of a Ground Source Heat Pump System." | 6.12 C. Geothermal Energy Sources and Systems, 1. Permits and Applications | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | City | 2702511350 | Decommissioning |  |  | "A GSHPS that is allowed to remain in a nonfunctional or inoperative state for a period of twelve (12) consecutive months, and which is not brought in operation within the time specified by the city after notification to the owner or operator of the GSHPS, shall be presumed abandoned and may be declared a public nuisance subject to removal at the expense of the operator." | 6.12 C. Geothermal Energy Sources and Systems, 5. Abandonment | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | City | 2702511350 | Open-loop Prohibitions |  |  | "Only closed loop GSHPS utilizing Minnesota Department of Health approved heat transfer fluids are permitted." | 6.12 C. Geothermal Energy Sources and Systems, 3. Design and Placement | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | City | 2702511350 | Other Prohibitions/Regulations |  |  | "GSHPS are prohibited on surface waters, except for stormwater ponds where they are permitted." | 6.12 C. Geothermal Energy Sources and Systems, 3. Design and Placement | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Clay | Barnesville | City | 2702703574 | Permit |  |  | "The city requires that all geothermal heating systems be registered." "Property owners are required to register their systems by providing the City Administrator with all state-approved permits prior to installation." "Before installing geothermal heating systems, residents are required to obtain a city building permit." | § 151.122 CITY REQUIREMENTS. | 2023 | https://codelibrary.amlegal.com/codes/barnesvillemn/latest/barnesville_mn/0-0-0-5453
Minnesota | Clay | Barnesville | City | 2702703574 | Inspection |  |  | "city officials may, upon reasonable notice to the owner, enter upon any property within the city... for purposes of inspecting geothermal facilities, or monitoring the operational characteristics of such facilities" and "The city shall provide affected property owners or occupants with reasonable prior notice... Such inspections or monitoring shall be conducted in accordance with applicable city and state procedures for inspections." | § 151.123 CITY INSPECTION AND MONITORING OF GEOTHERMAL FACILITIES. | 2023 | https://codelibrary.amlegal.com/codes/barnesvillemn/latest/barnesville_mn/0-0-0-5453
Minnesota | Clay | Dilworth | City | 2702715976 | Permit |  |  | "Any person, including the city, desiring to construct, install or alter a geothermal heating system within the city shall first apply for a geothermal heating system permit at the City Hall on forms provided for that purpose. No person shall commence construction or alteration of a geothermal heating system prior to the owner of a proposed geothermal heating system receiving a permit." | § 54.07 APPLICATION FOR GEOTHERMAL HEATING SYSTEM PERMIT | 2009 | https://codelibrary.amlegal.com/codes/dilworthmn/latest/dilworth_mn/0-0-0-1245
Minnesota | Dakota | Lakeville | City | 2703735180 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems shall be set back a minimum of five feet (5') from interior side lot lines and ten feet (10') from rear lot lines." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: C. Location | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Setback - Yards | 10 | feet | "Ground source heat pump systems shall only be located in the rear yard as defined by this title." "All components of ground source heat pump systems shall be set back a minimum of five feet (5') from interior side lot lines and ten feet (10') from rear lot lines." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: C. Location | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation." "Borings for ground source heat pump systems where the pipes or coils are installed vertically below the land shall also be subject to approval by the Minnesota department of health." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: G. Building Permit | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Screening |  |  | "Ground source heat pump systems shall be screened in accordance with the requirements of section 11-21-13 of this title." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: D. Screening | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Certification |  |  | "The ground source heat pump system shall be certified by Underwriters Laboratories, Inc., and comply to the requirements of the international building code." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: E. Certification | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Decommissioning |  |  | "Any ground source heat pump system which is inoperable for twelve (12) successive months shall be deemed to be abandoned and shall be deemed a public nuisance. The owner shall remove the abandoned system at their expense after obtaining a demolition permit" including: "The heat pump and any external or aboveground mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid, which is to be captured and disposed of in accordance with state and federal regulations"; and "The top of the pipe, coil or boring shall be uncovered and sealed." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: F. Abandonment | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed loop systems that circulate heat transfer fluids as allowed by this section through pipes or coils buried beneath the land surface." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: B. System Requirements | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | City | 2703735180 | Other Prohibitions/Regulations |  |  | "Ground source heat systems in public water bodies or water bodies owned or managed by the city of Lakeville shall be prohibited except when accessory to a city of Lakeville facility." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: A. Accessory Use | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | § 151.33(A) Definitions | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, boring and loops shall be set back at least five feet from interior side lot lines and at least ten feet from rear lot lines." | § 151.33(B)(b)(ii) Setbacks | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Permit |  |  | "A building permit and a conditional use permit if required shall be obtained for any ground source heat pump prior to installation. Borings for vertical systems are subject to approve from the MN Dept. of Public Health." In addition, "no alternative energy system shall be located, constructed, erected, moved, reconstructed, extended, enlarged or structurally altered within the City until a permit for the system has been issued by the City" and "a zoning permit must be obtained from the city prior to the construction of any system." | § 151.33(B)(e) Permits; § 151.33(E) Permits for Alternative Energy Systems | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and in order to suppress noise and hide from public view materials and designs matching those used for the structure will be incorporated into a plan design. Where miscellaneous exterior equipment cannot be fully hidden with matching building materials, landscaping may be used as additional screening. Screening remains subject to the requirements of the applicable zoning district." | § 151.33(B)(b)(v) Screening | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirement of the State Building Code and the Minnesota Department of Health." | § 151.33(B)(c) Safety | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed" and "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable state and federal regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 151.33(B)(d) Abandonment | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | City | 2704535450 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids are permitted. One loop ground source heat pump systems are not permitted." | § 151.33(B)(b)(i) System Requirements | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota |  | Pine Island | City | 2704951136 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | SEC. 11.73, Subd. 4.C. Location | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Setback - Yards | 10 | feet | "Ground source heat pump systems shall only be located in the rear yard as defined by this chapter." Also, "All components of ground source heat pump systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | SEC. 11.73, Subd. 4.C. Location | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation." The ordinance also states: "Borings for ground source heat pump systems where the pipes or coils are installed vertically below the land shall also be subject to approval by the Minnesota Department of Health." | SEC. 11.73, Subd. 4.G. Building Permit | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Screening |  |  | "Ground source heat pump systems shall be screened in accordance with the requirements of Section 11.70, Subdivision 7 of this Chapter." | SEC. 11.73, Subd. 4.D. Screening | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Certification |  |  | "The ground source heat pump system shall be certified by Underwriters Laboratories, Inc., and comply to the requirements of the international building code." | SEC. 11.73, Subd. 4.E. Certification | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Decommissioning |  |  | "Any ground source heat pump system which is inoperable for 12 successive months shall be deemed to be abandoned and shall be deemed a public nuisance. The owner shall remove the abandoned system at their expense after obtaining a demolition permit" including: "The heat pump and any external or aboveground mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid, which is to be captured and disposed of in accordance with state and federal regulations"; and "The top of the pipe, coil or boring shall be uncovered and sealed." | SEC. 11.73, Subd. 4.F. Abandonment | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed loop systems that circulate heat transfer fluids as allowed by this subdivision through pipes or coils buried beneath the land surface." | SEC. 11.73, Subd. 4.B. System Requirements | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | City | 2704951136 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems shall only be located in the rear yard as defined by this chapter." Also: "Ground source heat pump systems shall not encroach upon drainage and utility easements." | SEC. 11.73, Subd. 4.C. Location | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Definition: Geothermal |  |  | "Geothermal Project: Ground source heat pump systems which use the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. Systems include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; a heat pump unit that processes heat for use or disperses heat for cooling and an air distribution system. This includes open and closed loop as well as horizontal and vertical ground source heat pump systems" | Section 28, Subd. 2. Definitions | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Ground Source Heat Pump System: A system which circulates a heat transfer fluid through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." "Open Loop Ground Source Heat Pump System: A system using groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a body of water or into an injection well." "Horizontal Ground Source Heat Pump System: A closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." "Vertical Ground Source Heat Pump System: A closed loop ground source heat pump system where the loops or coils are installed vertically in one or more borings below the land surface." | Section 28, Subd. 2. Definitions | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Permit |  |  | "Within all zoning districts, no structure or land shall be used for a ground source heat pump system except by Conditional Use Permit (CUP) issued in accordance with Section 22, Subdivision 10." Also: "A permit from the MN Department of Health must be obtained prior to boring and installing a vertical ground source heat pump system." | Section 28, Subd. 4. Conditional Uses; Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Inspection |  |  | "A listing or schedule of when and what improvements, subject to inspection and approval by the City Engineer shall be required..." "A provision requiring all improvements to be inspected by the City Engineer during construction at the expense of the Subdivider." "SUBD. 4. INSPECTION. All required improvements shall be inspected by the City Engineer during construction at the expense of the subdivider." | Section 5, Subd. 1. Developer's Agreement; Section 5, Subd. 4. Inspection | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Certification |  |  | "All systems must be certified by Underwriters Laboratories, Inc. (UL)." Also: "All ground source heat pump systems shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the MN State Building Code." | Section 28, Subd. 4. Conditional Uses; Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained from the City Building Official. The heat pump and any external mechanical equipment shall be removed. Pipes or coils below ground shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid must be captured and disposed of in accordance with applicable MN Pollution Control agency regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | Section 28, Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Open-loop Prohibitions |  |  | "Open loop ground source heat pump systems are prohibited; only closed loop ground source heat pump systems utilizing heat transfer fluid are allowed as a conditional use." Also: "Only closed loop ground source heat pump systems utilizing heat transfer fluids are permitted. Open loop ground source heat pump systems are prohibited." | Section 28, Subd. 3. Prohibited Uses; Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | City | 2704972328 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in public waters are also prohibited." | Section 28, Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Hennepin | Brooklyn Park | City | 2705307966 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils, or plates; fluid that absorbs and transfers heat; and a heat pump unit the processes heat for use or disperses heat for cooling; and an air distribution system." | §152.107 DEFINITIONS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | City | 2705307966 | Setback - Property Lines | 10 | feet | §152.1001(C)(2)(a): "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least 5 feet from interior side lot lines and at least 10 feet from rear lot lines." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | City | 2705307966 | Permit |  |  | §152.1001(C)(4): upon abandonment, "The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | City | 2705307966 | Screening |  |  | §152.1001(C)(3): "Ground source heat pumps are considered mechanical equipment subject to screening requirements of §152.1023." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | City | 2705307966 | Decommissioning |  |  | §152.1001(C)(4): "If the ground source heat pump remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | City | 2705307966 | Open-loop Prohibitions |  |  | §152.1001(C)(1): "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in §152.107 are permitted. Open loop ground source heat pump systems are not permitted." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Corcoran | City | 2705313168 | Permit |  |  | "Mechanical (Residential) $75.00 per unit + State Surcharge Fee ($1.00) (Furnace, AC or Gas line) ... The following qualify as a 'unit' Furnace, AC, Air Exchange, In-floor heat, Boiler, Geothermal System, Ground System Heat Pump, Garage Heater, etc." | 2023 CITY OF CORCORAN BUILDING PERMIT AND RELATED FEES SCHEDULE – OVER THE COUNTER PERMITS | 2023 | https://cdnsm5-hosted.civiclive.com/UserFiles/Servers/Server_15543680/File/Our%20Community/City%20Code/Proposed%20Ordinances/Ordinance%202023-XXX%20Rental%20and%20Property%20Maintenance%20Code%20Draft%20Version%205.pdf
Minnesota | Hennepin | Corcoran | City | 2705313168 | Inspection |  |  | The fee schedule lists explicit inspection requirements/fees, including: "Inspection outside normal business hours; minimum two hour charge $90.00 per hr.," "Re-inspection Fee $45.00 per hr.," "Inspections for which no fee is specifically indicated $60.00 per hr.," and "Site Inspection Fee RESIDENTIAL $45.00 ea. COMMERCIAL $80.00 ea." | 2023 CITY OF CORCORAN BUILDING PERMIT AND RELATED FEES SCHEDULE – OTHER INSPECTIONS AND FEES | 2023 | https://cdnsm5-hosted.civiclive.com/UserFiles/Servers/Server_15543680/File/Our%20Community/City%20Code/Proposed%20Ordinances/Ordinance%202023-XXX%20Rental%20and%20Property%20Maintenance%20Code%20Draft%20Version%205.pdf
Minnesota | Hennepin | Medina | City | 2705341480 | Setback - Property Lines | 10 | feet | "No portions of the geothermal system shall be permitted to be located within or below drainage and utility easements or within 10 feet of any property line." | Section 828.09.2. Geothermal Systems, Subd. 2 | 2023 | https://www.medinamn.gov/files/assets/city/v/1/admin/documents/city-code-book/may-2025-changes/828.pdf
Minnesota | Hennepin | Medina | City | 2705341480 | Other Prohibitions/Regulations |  |  | "Geothermal systems shall not be permitted within or under wetlands." | Section 828.09.2. Geothermal Systems, Subd. 3 | 2023 | https://www.medinamn.gov/files/assets/city/v/1/admin/documents/city-code-book/may-2025-changes/828.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump systems" are regulated in Sec. 42-76(b), which establishes standards for this system type as an alternative energy system. | Sec. 42-76(b) | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Setback - Property Lines | 10 | feet | "Except as otherwise allowed for systems within public waters (by conditional use permit), all components of ground source heat pump systems including pumps, borings and loops shall be set back at least ten feet from all lines..." | Sec. 42-76(b)(2)b.1 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Setback - Water Bodies | 25 | feet | "Except as otherwise allowed for systems within public waters (by conditional use permit), all components of ground source heat pump systems including pumps, borings and loops shall be set back at least ten feet from all lines and 25 feet from the ordinary high water level of any public water body." | Sec. 42-76(b)(2)b.1 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Noise Limits | 55 | dBA | "Audible noise from ground source heat pump systems shall not exceed 55 dB(A) when measured from the outside of the nearest residence, business, school, hospital, religious institution, or other inhabited structure." | Sec. 42-76(b)(2)d | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation." Also, "Borings for vertical systems are subject to approval by the state department of public health." | Sec. 42-76(b)(4) | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Inspection |  |  | "Ground source heat pump systems shall be subject to inspection by the city's building official every three years and at the property owner's expense in accordance with the city's fee schedule." | Sec. 42-76(b)(4)c | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the screening requirements of section 42-64(j) of this chapter." | Sec. 42-76(b)(2)e | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | Sec. 42-76(b)(2)f | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The property owner shall remove the abandoned system and restore vegetation upon the site at his/her expense after a demolition permit has been obtained..." Subsection (a): "The heat pump and any external mechanical equipment shall be removed." Subsection (b): "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring (where it connects to mechanical equipment) shall be capped in a secure manner." | Sec. 42-76(b)(3) | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in article 1, division 2 are permitted. Open loop ground source heat pump systems are prohibited." | Sec. 42-76(b)(2)a.1 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | City | 2705362014 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems located within public waters are prohibited." | Sec. 42-76(b)(2)a.2 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Wayzata | City | 2705368818 | Permit |  |  | "105 Work exempt from permit. Permits shall not be required for the following:" followed by a list of exempt work items that does not include ground-source heat pump systems. The code scope states in 1346.0101 that "This code shall regulate the design, installation, maintenance, alteration, and inspection of mechanical systems... utilized to provide control of environmental conditions within buildings," which encompasses mechanical GHP systems under this code. | 1346.0105 SECTION 105 WORK EXEMPT FROM PERMIT |  | https://www.wayzata.org/DocumentCenter/View/209/Minnesota-Mechanical-Fuel-Gas-Code-PDF
Minnesota | Hennepin | Wayzata | City | 2705368818 | Inspection |  |  | "106 Required inspections. The building official, upon notification from the permit holder or the permit holder’s agent, shall make the following inspections..." including "Underground inspection shall be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place" and "Final inspection shall be made upon completion of the mechanical system. Exception: Ground-source heat pump loop systems tested in accordance with this code shall be permitted to be backfilled prior to inspection." | 1346.0106 SECTION 106 REQUIRED INSPECTIONS |  | https://www.wayzata.org/DocumentCenter/View/209/Minnesota-Mechanical-Fuel-Gas-Code-PDF
Minnesota | Hubbard |  | County | 27057 | Definition: Geothermal Heat Pump |  |  | "Geothermal energy system. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." | Section 111. Definitions as Used in this Ordinance | 2024 | https://www.co.hubbard.mn.us/uploads/dm/16109/County_Ordinance_Number_17_Shoreland.pdf
Minnesota | Hubbard |  | County | 27057 | Permit |  |  | "Installation of geothermal energy systems shall be allowed per the following requirements. No additional permitting shall be required if a current dwelling permit is in place and the following standards are met:" and "If a current dwelling permit is in place, no additional permit shall be required." | Section 512. Geothermal Energy Systems | 2024 | https://www.co.hubbard.mn.us/uploads/dm/16109/County_Ordinance_Number_17_Shoreland.pdf
Minnesota | Hubbard |  | County | 27057 | Other Prohibitions/Regulations |  |  | Section 512 requires that for geothermal systems, "All parts of the system (except for a water discharge pipe on an open loop geothermal energy system) must be located behind the required structure setback from the ordinary high water mark." It further allows parts "in the area between the ordinary high water mark and structure setback" only when "the installation of the system parts complies with Section 902" and "the structure serviced by the system is a legal nonconformity in terms of its ordinary high water mark structure setback." | Section 512. Geothermal Energy Systems | 2024 | https://www.co.hubbard.mn.us/uploads/dm/16109/County_Ordinance_Number_17_Shoreland.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump System. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | 1501.018.C. Definitions | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet (5') from interior side lot lines..." | 1501.018.D.2.b. Setbacks | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Setback - Yards | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet (5') from interior side lot lines and at least ten feet (10') from rear lot lines." Also: "Above-ground equipment associated with ground source heat pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable zoning district." | 1501.018.D.2.b. Setbacks | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Permit |  |  | "Those permits as required, and a conditional use permit if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." Also, in 1501.018.I.2: "no alternative energy system shall be located, constructed, erected, moved, reconstructed, extended, enlarged or structurally altered within the City until a permit for the system ('system permit') has been issued by the City." In 1501.018.I.3: "a zoning certificate must be obtained from the City prior to the construction of any system." In 1501.018.I.4: "a building permit must be obtained from the City prior to the construction of any system when construction activity is of such a nature that a building permit is required." | 1501.018.D. Ground Source Heat Pump Systems | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and in order to suppress noise and hide from public view materials and designs matching those used for the structure will be incorporated into a plan design. Where miscellaneous exterior equipment cannot be fully hidden with matching building materials, landscaping may be used as additional screening. Screening remains subject to the requirements of the applicable zoning district." | 1501.018.D.2.e. Screening | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | 1501.018.D.3. Safety | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained" and "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable state and federal regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | 1501.018.D.4. Abandonment | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | City | 2708571086 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in Section 1501.018.C., are permitted. Open loop ground source heat pump systems are not permitted." | 1501.018.D.2.a.I. System requirements | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Definition: Well |  |  | "CLOSED LOOP GROUND SOURCE GEOTHERMAL SYSTEM. A system that circulates a heat transfer fluid, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water whereby the temperature of the surrounding earth or water is transferred to the structure at the ground surface." "HORIZONTAL GEOTHERMAL SYSTEM. A closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." "VERTICAL GEOTHERMAL SYSTEM. A closed loop ground source heat pump system where the loops or coils are installed vertically in one or more borings below the land surface." | § 154.003 DEFINITIONS | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A system that uses the relatively constant temperature of the stored energy of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. Also called a ground source heat pump system." | § 154.003 DEFINITIONS | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet from side, front and rear lot lines." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; ii. Setbacks | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval by the Minnesota Department of Public Health." Also under water-based systems: "Ground source heat pump systems in public waters may be permitted as a conditional use..." subject to DNR approval, owner/association consent, and "demonstrated compliance with applicable city permit requirements." | (I) Alternative energy systems; 1. Ground source heat pump systems; (e) Permits | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Inspection |  |  | "All wiring, installation of pipes, grading and all other installations and construction shall be subject to inspection." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; iii. Construction | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements for the applicable zoning district." Related screening requirement: "Building utility services and structures such as meters, transformers, refuse containers, including dumpsters, ancillary equipment and the like shall be either located inside the principal building, inside an accessory building, or, where outside be entirely screened from off-site views." Also, for rooftop equipment: "All rooftop equipment, with the exception of solar and wind equipment, shall be screened from view from adjacent streets and public rights-of-way." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; vi. Screening | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the State Building Code." | (I) Alternative energy systems; 1. Ground source heat pump systems; (c) Certification | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained..." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | (I) Alternative energy systems; 1. Ground source heat pump systems; (d) Abandonment | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in this section are permitted. Open loop ground source heat pump systems are not permitted." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; i. System requirements | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | City | 2712347221 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the city are not permitted." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; i. System requirements | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | St. Louis | Duluth | City | 2713717000 | Definition: Geothermal Heat Pump |  |  | "Accessory solar or geothermal power equipment. Accessory uses and structures that are clearly subordinate in size and use to the primary use and structure on the property, and that are used to reduce energy consumption or to generate energy from non-fossil fuel and non-carbon dioxide emitting sources on the property. These structures and uses may include but are not limited to the following, and may be located at ground level or above or below ground unless specifically limited in this Chapter, provided that they meet all other applicable requirements of this Chapter: solar photovoltaic modules, solar thermal hot water collectors, solar arrays; and geothermal heat pumps, earth tubes, or downhole heat exchangers." | 50-41.1 Definitions: A | 2025 | https://duluthmn.gov/media/xgicauxa/udc-2025.pdf
Minnesota | Scott | Elko New Market | City | 2713918662 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet (5') from interior side lot lines and at least ten feet (10') from rear lot lines." | 11-14-2(B)(1)(a) Setbacks | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | City | 2713918662 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval by the Minnesota department of public health." | 11-14-2(D) Permits | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | City | 2713918662 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the screening requirements of section 11-5-4 of this title." | 11-14-2(B)(3) Screening | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | City | 2713918662 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the state building code." | 11-14-2(B)(4) Safety | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | City | 2713918662 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained..." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted"; and "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 11-14-2(C) Abandonment | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | City | 2713918662 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in section 11-2-2 of this title are permitted. Open loop ground source heat pump systems are not permitted." | 11-14-2(B)(1)(a) System Requirements | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | City | 2713918662 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the city of Elko New Market are not permitted." | 11-14-2(B)(1)(c) System Requirements | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Jordan | City | 2713932174 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least 5 feet from interior side lot lines and at least 10 feet from rear lot lines." | § 154.392(B)(2)(a) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | City | 2713932174 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval by the Minnesota Department of Public Health." | § 154.392(D) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | City | 2713932174 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and shall be screened from view to the extent possible without impacting their function." | § 154.392(B)(5) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | City | 2713932174 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the State Building Code." | § 154.392(B)(6) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | City | 2713932174 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of 1 year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... (1) The heat pump and any external mechanical equipment shall be removed. (2) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted. (3) Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | § 154.392(C) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | City | 2713932174 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in this section are permitted. Open loop ground source heat pump systems are not permitted." | § 154.392(B)(1)(a) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | City | 2713932174 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the City of Jordan are not permitted." | § 154.392(B)(1)(c) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Washington | Dellwood | City | 2715616 | Definition: Geothermal Heat Pump |  |  | "Geo-thermal heating systems, also known as watered heating systems and air conditioning units..." | 96.01 GEO-THERMAL HEATING SYSTEMS, WATER FED HEAT EXTRACTORS AND WATER FED AIR CONDITIONING UNITS | 2015 | https://www.dellwood.us/wp-content/uploads/2024/01/Dellwood-Code-Book-2023.pdf
Minnesota | Washington | Dellwood | City | 2715616 | Permit |  |  | "No person shall erect, construct, or alter any geo-thermal or water fed heating system, in the City of Dellwood without first securing a building permit therefore and paying the permit fee as established by the Council from time to time." Also, the permit application "shall include a description of the system clearly showing that the system employs a closed loop recirculating water system with property equipment to prevent discharge of any water in the ordinary use of the system." | 96.02 PERMIT REQUIRED | 2015 | https://www.dellwood.us/wp-content/uploads/2024/01/Dellwood-Code-Book-2023.pdf
Minnesota | Washington | Dellwood | City | 2715616 | Open-loop Prohibitions |  |  | "Geo-thermal heating systems, also known as watered heating systems and air conditioning units are prohibited, except those systems which are constructed and installed with a closed, recirculating ground loop water system..." and "No system shall be permitted which allows discharge of water onto the surface, or into a seepage pit/drainfield system, or into any natural or artificial drainage- ways." | 96.01 GEO-THERMAL HEATING SYSTEMS, WATER FED HEAT EXTRACTORS AND WATER FED AIR CONDITIONING UNITS | 2015 | https://www.dellwood.us/wp-content/uploads/2024/01/Dellwood-Code-Book-2023.pdf
Minnesota | Washington | Newport | City | 2716345790 | Definition: Geothermal Heat Pump |  |  | "Heat pump system, ground source means a heat pump system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | Sec. 36-16. Terms defined. | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Setback - Property Lines | 20 | feet | "All air conditioning units excluding window units shall be located a minimum of 20 feet from all lot lines, but not within the front yard." | Sec. 36-422(j) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Setback - Yards | 20 | feet | For ground source heat pump systems, "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet from interior side lot lines and at least ten feet from rear lot lines." Separately, "All air conditioning units excluding window units shall be located a minimum of 20 feet from all lot lines, but not within the front yard." | Sec. 36-424(b)(2)b.1; Sec. 36-422(j) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Permit |  |  | "A building permit and interim conditional use permit, if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the state department of public health." | Sec. 36-424(b)(5) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of division 3 of this article." Division 3 states: "All utility equipment, such as heating and ventilating equipment, meters and other devices shall be completely screened from eye-level view of adjacent properties and streets. Equipment shall be screened with a screen wall, berm, or landscaping if located on the ground. If on the roof, the equipment shall be screened with a parapet or screen wall of materials compatible with the principal structure..." | Sec. 36-424(b)(2)e.; Sec. 36-448(f) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the state building code." | Sec. 36-424(b)(3) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... The heat pump and any external mechanical equipment shall be removed. Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations... Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | Sec. 36-424(b)(4) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids, as defined in section 36-16, are permitted. Open loop ground source heat pump systems are not permitted." | Sec. 36-424(b)(2)a.1. | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | City | 2716345790 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the city are not permitted." | Sec. 36-424(b)(2)a.3. | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | 401.17.C. Definitions; Alternative Energy Systems Related/Ground Source Heat Pumps (Geothermal Heating) | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five (5) feet from interior side lot lines and at least ten (10) feet from rear lot lines." | 401.17.G.2.b. Setbacks | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Permit |  |  | "Permits. A building permit and a conditional use permit, if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." Also, "Ground source heat pump systems in public waters may be permitted as a conditional use in accordance with Section 401.17.D and Section 401.03 of this Ordinance, subject to approval from the Minnesota Department of Natural Resources and subject to written consent of all property owners and/or approval by an association in accordance with its adopted bylaws." | 401.17.G. Ground Source Heat Pumps (Geothermal Heating) | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of Section 401.15.E.10.c." | 401.17.G.2.e. Screening | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | 401.17.G. Safety | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one (1) year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted"; "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 401.17.G. Abandonment | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in Section 401.17.C.4 of this Ordinance are permitted. Open loop ground source heat pump systems are not permitted." | 401.17.G.2.a. System Requirements | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | City | 2716347914 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the City of Oak Park Heights are not permitted." | 401.17.G.2.a. System Requirements | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Winona |  | County | 27169 | Permit |  |  | "A Land Disturbance Permit, located in Chapter 6 is required for the following situations when installing a Geothermal Energy System: a. When there is to be excavation or filling of land that would deprive an adjoining property owner of lateral support. b. When there is to be excavation of earthen material of more than one thousand (1,000) cubic yards, for the installation of a geothermal heat pump system. 1. When there is to be excavation of earthen material, for the installation of a geothermal heat pump system located within Shoreland, Floodplain, or on steep slopes as described in Chapter 11." | 12.4.1 Land Disturbance Permit | 2011 | https://www.winonacounty.gov/DocumentCenter/View/580/WCZO-Amendment---Renewable-Energy---Approved-June-28-2011-PDF
Minnesota | Winona | St. Charles | City | 2716956788 | Setback - Yards | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet from interior side lot lines and at least ten feet from rear lot lines." Also, "Above-ground equipment associated with ground source heat pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable zoning district." | § 152.76(B)(2)(a)-(b) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | City | 2716956788 | Permit |  |  | "Those permits as required, and a conditional use permit if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." | § 152.76(E) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | City | 2716956788 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and in order to suppress noise and hide from public view materials and designs matching those used for the structure will be incorporated into a plan design. Where miscellaneous exterior equipment cannot be fully hidden with matching building materials, landscaping may be used as additional screening. Screening remains subject to the requirements of the applicable zoning district." | § 152.76(B)(5) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | City | 2716956788 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | § 152.76(C) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | City | 2716956788 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable state and federal regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 152.76(D) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | City | 2716956788 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in § 152.75 (C) are permitted. Open loop ground source heat pump systems are not permitted." | § 152.76(B)(1)(a) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Missouri | St. Charles | O'Fallon | City | 2954074 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL OR GROUND-SOURCE HEAT-PUMP SYSTEM. A system for heating and/or cooling buildings using the earth's thermal properties in conjunction with electricity. This system may include open and closed loop systems." | Section 400.910 Definitions | 2025 | https://ecode360.com/43322073
Missouri | St. Charles | O'Fallon | City | 2954074 | Permit |  |  | Section 400.920(C): "It shall be unlawful for any renewable energy system to be constructed, erected, and/or installed without a building permit." Section 400.920(D): "Geothermal energy systems ... may be approved by the Planning and Development Department in accordance with this Article by the issuance of a building permit." Section 400.955(A): "A completed building permit with all the applicable electrical and mechanical engineering information and drawings." | Section 400.920 General Provisions; Section 400.955 Application Requirements For Geothermal Systems | 2025 | https://ecode360.com/43322073
Missouri | St. Charles | O'Fallon | City | 2954074 | Decommissioning |  |  | "Any system that is out of service for a continuous period of twelve (12) months will be considered abandoned and must be removed within ninety (90) days. If such system is not removed within ninety (90) days, the City may remove such system at the owner's expense after giving the owner notice and an opportunity to be heard with respect to removal." | Section 400.990 Abandonment | 2025 | https://ecode360.com/43322073
Missouri | St. Charles | O'Fallon | City | 2954074 | Other Prohibitions/Regulations |  |  | Section 400.950(A): "Setback Requirements. Drilling and trenching for geothermal heat pump systems shall be prohibited on any easement." | Section 400.950 Geothermal Systems | 2025 | https://ecode360.com/43322073
Missouri | Phelps | Rolla | City | 2962912 | Permit |  |  | Section 35-189(a) states: "Private wells may be utilized for closed loop heat pump systems... A construction permit and an operation permit as provided in Sections 35-185 and 35-186 of this Code are required." Section 35-185(a) adds: "Before commencement of drilling, installation, or construction... the owner... shall first obtain a written construction permit signed by the General Manager of the Rolla Municipal Utilities." Section 35-186(a) provides that after completion, "the Rolla Municipal Utilities shall issue an operation permit." | Section 35-189 Private Wells For Heat Pumps; Section 35-185 Construction Permit Required Prior To Commencement Of Drilling, Installation, Or Construction; Application; Fee; Inspection Provisions; Section 35-186 Permit For Operation Of Private Well Or Water Supply | 2017 | https://ecode360.com/42770538
Missouri | Phelps | Rolla | City | 2962912 | Inspection |  |  | Section 35-185(b) states: "Prior to completion of the private well or water supply, the Rolla Municipal Utilities shall be allowed to inspect the work at any stage of the drilling, installation, or construction" and the permit holder must notify the utility "before any underground portions are covered" and "when the work is ready for final inspection." It further provides: "The inspection shall be made within sixty (60) hours... of the receipt of notice." Section 35-186(a) says the operation permit is issued after completion "to the satisfaction of the Rolla Municipal Utilities," and Section 35-186(b) adds: "Rolla Municipal Utilities, at its discretion, shall perform yearly inspections of the installation to verify compliance with applicable ordinances." | Section 35-185 Construction Permit Required Prior To Commencement Of Drilling, Installation, Or Construction; Application; Fee; Inspection Provisions; Section 35-186 Permit For Operation Of Private Well Or Water Supply | 2017 | https://ecode360.com/42770538
Missouri | Phelps | Rolla | City | 2962912 | Decommissioning |  |  | Section 35-183 requires owners "to plug any existing private wells in accordance with 10 CSR 23-3.110" and provides that when the grandfather clause no longer applies, "the private well shall be properly plugged as stipulated herein." | Section 35-183 Plugging Of Existing Wells And Connection To Public Water Supply | 2017 | https://ecode360.com/42770538
Missouri | Phelps | Rolla | City | 2962912 | Open-loop Prohibitions |  |  | Section 35-189(b) states: "Private wells shall not be permitted for any type of open loop heat pump system, as defined and discussed in 10 CSR 23-5 in the Missouri, Code of State Regulations." | Section 35-189 Private Wells For Heat Pumps | 2017 | https://ecode360.com/42770538
Missouri | Ste. Genevieve | Ste. Genevieve | City | 2964180 | Permit |  |  | "It is unlawful for any person, without first obtaining a construction permit, to: Install, alter or modify any electrical, plumbing or mechanical system of a building where the cost is in excess of five hundred dollars ($500.00)." Ground-source heat pump work is explicitly within the mechanical/plumbing/electrical system context, and the same section states: "Application for such permit shall be made to the Clerk and shall be accompanied by plans and specifications in duplicate..." and "No permit shall be issued until after approval of plans." | Section 500.190 Construction Permits | 2025 | https://ecode360.com/27816792
Missouri | Ste. Genevieve | Ste. Genevieve | City | 2964180 | Inspection |  |  | Section 500.190(E) provides: "The Building Inspector shall make or cause to be made such inspections as are necessary to see to the enforcement of the provisions of this Article and to make any tests or examinations of materials or methods to be used for the purpose of seeing that they comply with the provisions of this Article." | Section 500.190 Construction Permits | 2025 | https://ecode360.com/27816792
Missouri |  | University City | City | 2975220 | Permit |  |  | "Type of Permit Fee ... Geothermal system (per system) $90.00." This appears within the Mechanical Code permit fee schedule, which states: "The fee charged for each mechanical permit shall be as scheduled below." | Section 500.080, 106.5.2 Fee schedule | 2013 | https://www.ucitymo.org/documentcenter/view/14300
Missouri |  | University City | City | 2975220 | Inspection |  |  | Mechanical Code: "In addition to the inspections normally provided, the Code Official shall require that additional inspections or reinspections be conducted due to non-compliance with Code requirements or due to work which is not ready for inspection or not accessible for inspection at the time of a scheduled inspection." Also, "All third-party inspections shall be in accordance with Section 110.4.90 of the Building Code of University City." Building Code Section 110.4.90 provides: "All third-party inspections, qualifications, and reliability must be preapproved by the Building Official." | Section 500.080, 107.90 Extra inspections; Section 500.020, 110.4.90 Third-party inspections | 2013 | https://www.ucitymo.org/documentcenter/view/14300
Montana | Flathead | Flathead | Reservation | 3002991118 | Definition: Well |  |  | "Heating/Cooling Exchange Well" means a Well for the purpose and with the attributes set forth in Section 2-2-119(1) of this Ordinance. | 1-1-104(30) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | Reservation | 3002991118 | Permit |  |  | "Before appropriating water for a use described in this subsection (1), approval of the Engineer is required." Also, "An applicant must file a completed application form and obtain approval from the Engineer before drilling any Well(s) ... and putting water to use pursuant to this Section." Once approved, "the Engineer shall issue an authorization to develop the Appropriation Right for a Heating/Cooling Exchange Well." | 2-2-119(1)-(5) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | Reservation | 3002991118 | Inspection |  |  | For completed appropriations, "The Office of the Engineer shall review the certified statement and may then inspect the Appropriation, and if it determines that the Appropriation has been completed in substantial accordance with the Appropriation Right or Change in Use authorization, it shall issue" the final document. Staff analysis of applications may also include "field inspection by Staff." | 2-2-114; 2-2-107(2)(c) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | Reservation | 3002991118 | Decommissioning |  |  | "If an Appropriation Right for a Heating/Cooling Exchange Well is revoked by the Board ... or is determined to be abandoned ... or is voluntarily abandoned, the Appropriator shall, within 180 days of the revocation or voluntary abandonment, follow the well abandonment procedures, standards, and rules adopted by the board of water well contractors pursuant to 37-43-202, MCA ... for any Well associated with the revoked or abandoned Appropriation Right for a Heating/Cooling Exchange Well." | 2-2-119(7) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | Reservation | 3002991118 | Other Prohibitions/Regulations |  |  | "Aquifer Injection and Injection Wells are not allowed except when used exclusively for Heating/Cooling Exchange Wells." | 1-1-111(3) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Lake |  | County | 30047 | Permit |  |  | Section 3-1(A): "No person(s) may proceed with any construction work, landscape modification, or maintenance which alters or disturbs the lakeshore protection zone... until she/he has obtained and has physical possession of a valid 'Lakeshore Construction Permit' issued by the governing body." Section 3-4(A): "Any work, including maintenance, which will temporarily or permanently alter, diminish, or increase the course, current or cross-sectional area of the lakeshore protection zone must first be secured by a permit from the governing body before any work is commenced." | Section 3-1 General Requirements; Section 3-4 Work for Which a Permit is Required | 2024 | https://www.lakemt.gov/DocumentCenter/View/2951/Lake-County-Lakeshore-Protection-Regulations-amended-8-2024-pdf
Montana | Lake |  | County | 30047 | Inspection |  |  | Section 3-2(A): "the governing body, the planning board, or the planning staff may conduct investigations, examinations and site evaluations... to observe and monitor construction, and/or to evaluate completed projects for compliance with approved plans." Section 5-2(N): "The applicant or his/her authorized agent shall notify the planning staff when an approved project is completed. The planning staff will then be able to initiate onsite evaluation of the project in order to assure that the project is compliant with approved plans, 'Conditions of Approval', and 'Lake County Lakeshore Protection Regulations'." | Section 3-2 Permission to Enter; Section 5-2(N) | 2024 | https://www.lakemt.gov/DocumentCenter/View/2951/Lake-County-Lakeshore-Protection-Regulations-amended-8-2024-pdf
Montana | Lake |  | County | 30047 | Other Prohibitions/Regulations |  |  | Section 5-3(N)(2)(a): "No geothermal system shall be located within the lakeshore protection zone." Section 5-3(N)(2)(b): "Geothermal heating systems that make use of the lake are prohibited." | Section 5-3(N) Geothermal Heating Systems | 2024 | https://www.lakemt.gov/DocumentCenter/View/2951/Lake-County-Lakeshore-Protection-Regulations-amended-8-2024-pdf
Montana | Lewis and Clark |  | County | 30049 | Permit |  |  | "Renewable Energy Facilities" are listed as conditional uses in RR and SR. RR §704 states: "The following uses are permitted, upon approval of a Conditional Use Permit (CUP) by the Board of Adjustment (BOA), in accordance with Section 14, of these Regulations ... 704.40 Renewable Energy Facilities." SR §804 likewise states: "The following uses are permitted, upon approval of a Conditional Use Permit (CUP) by the Board ... 804.42 Renewable Energy Facilities." Section 3 defines "Renewable Energy Facility" as "A site, together with its accessory facilities, where energy is generated using renewable resources. Such sites may include but are not limited to solar farms, wind turbines, or geothermal facilities." | SECTION 7 Rural Residential Mixed-Use District (RR) / SECTION 8 Suburban Residential Mixed-Use District (SR) | 2022 | https://www.lccountymt.gov/files/assets/county/v/1/government/commission-bocc/documents/resolutions/2022/resolution_2022-113.pdf
Montana | Sanders |  | County | 30089 | Definition: Well |  |  | "(K) Wells: an excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed and includes any related system(s) of pumps, pipes, controls, reservoirs, or mechanical devices used for the purpose(s) of: location, diversion, artificial recharge, acquisition of groundwater or for any other similar purpose. (1) 'Well' includes, but is not limited to: ... (b) Heat exchange well: well used for extracting or injecting groundwater for heating or air conditioning purposes." | 2. Definitions and Acronyms | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders |  | County | 30089 | Setback - Wastewater | 100 | feet | Table 1 lists horizontal setback distances for well uses. For "Heat Exchange" wells, the setback to "Absorption Systems" is "100" feet. Section 4(C) states that where there is no Certificate of Subdivision Approval, "the location of the well(s) must conform to the minimum setback requirements shown in Table 1." | 4. SITING REQUIREMENTS / Table 1. Horizontal setback distances in feet* | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders |  | County | 30089 | Permit |  |  | "(A) Permit Required. A person may not construct a well within Sanders County without first obtaining a permit from the Department." The application "must include" a site plan showing, among other things, "the proposed well," "existing and proposed sewage facilities," "existing and proposed buildings," "property lines and easements," and nearby "floodplain or surface water within 100' of proposed well location." A permit expires if the well "is not installed, inspected and approved by the Department within one year after issuance." | 1. PERMITS AND APPLICATIONS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders |  | County | 30089 | Inspection |  |  | "(B) Prior to being used, all wells require a final inspection of the well location by the Department unless specific permission has been granted by the Department." "(C) When final approval is withheld ... A re-inspection must be made to confirm the deficiencies have been corrected and the system is in compliance with the regulations." "(D) The applicant or licensed well driller must notify the Department that a well is ready for inspection within two (2) business days of completion of the well." | 5. INSPECTIONS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders |  | County | 30089 | Licensed Driller |  |  | Section 5 repeatedly assigns duties to a "licensed well driller," including: "The applicant or licensed well driller must notify the Department upon correction of any and all deficiencies" and "The applicant or licensed well driller must notify the Department that a well is ready for inspection within two (2) business days of completion of the well." | 5. INSPECTIONS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders |  | County | 30089 | Other Prohibitions/Regulations |  |  | "(E) Drilling of a well is prohibited if the well isolation zone, as defined in 76-4-102, encroaches onto adjacent private property without the authorization of the private property owner." | 4. SITING REQUIREMENTS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Nebraska | Adams |  | County | 31001 | Definition: Well |  |  | "GROUND WATER HEAT PUMP WELL shall mean a well constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well constructed for the purpose of installing the underground closed loop pipe necessary to re-circulate heat transfer fluid. a. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. b. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definition of Terms | 2010 | https://adamscountyne.gov/images/PDFS/PlanningZoning/AdamsCoZoning%20Regs%20-%202010%20final.pdf
Nebraska | Adams | Hastings | City | 3100121415 | Definition: Well |  |  | "Water Well. Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, obtaining hydrogeologic information, or extracting water from or injecting water into the underground water reservoir." | 32-601(19). Definitions. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Adams | Hastings | City | 3100121415 | Definition: Geothermal Heat Pump |  |  | "Geothermal Water Source Heat Pump System. The installation, operation, or use of any well, device, piping, or other apparatus for the purpose of utilizing the geothermal properties of groundwater, whereby water passes through a heat exchanger to provide heating or cooling from the geothermal properties of the groundwater, and the spent water is discharged to the surface or subsurface. This system is sometimes referred to as a 'pump and dump' system." | 32-601(9). Definitions. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Adams | Hastings | City | 3100121415 | Permit |  |  | Section 32-615.01 states: "Geothermal Water Source Heat Pump Systems may be installed and operated within the City of Hastings, and its two mile extraterritorial jurisdiction, subject to permitting and other applicable requirements of the Hastings City Code." Section 32-616 requires a "well permit for a domestic water well or a nonpotable water well within the City of Hastings or its two mile extraterritorial jurisdictional area" and lists required application information including "the depth of the proposed well" and "an accurate diagram showing the location of the proposed well in respect to the boundaries of the property, the nearest street, road, or highway intersection, and any on site septic or waste disposal system." | 32-615.01. Geothermal water source heat pump systems.; 32-616. Permitting of water wells; application for well permit. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Adams | Hastings | City | 3100121415 | Other Prohibitions/Regulations |  |  | Section 32-615.01 provides that geothermal water source heat pump systems "may be installed and operated" but adds: "In no event shall the spent water from any Geothermal Water Source Heat Pump System be directed or allowed to enter into or onto any publicly maintained street right of way, road right of way, ditch, storm sewer system, or sanitary sewer system." It also requires that discharge "shall be dedicated to a beneficial use" and "shall not include chemical additives for cleaning or descaling." | 32-615.01. Geothermal water source heat pump systems. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Antelope |  | County | 31003 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2018 | https://antelopecounty.nebraska.gov/sites/default/files/doc/Antelope%20County%20Zoning%20Regs_adopted%20041018.pdf
Nebraska | Antelope |  | County | 31003 | Permit |  |  | "No building, structure, or land ... shall hereafter be used or occupied and no building or structure or part thereof shall hereafter be erected, constructed, reconstructed, moved, or structurally altered, except in conformity with the provisions of this Resolution ... and except after receiving a zoning permit from the Antelope County Zoning Administrator." | Section 3.08 Scope of Regulations | 2018 | https://antelopecounty.nebraska.gov/sites/default/files/doc/Antelope%20County%20Zoning%20Regs_adopted%20041018.pdf
Nebraska | Hall | Alda | Village | 3100625 | Setback - Public Water | 1000 | feet | Section 3-124 provides: "Under no circumstances shall the Alda Village Board approve any permit to drill or operate any of the below described facilities within the indicated number of feet from the Village of Alda water wells:" The table lists "All water wells, including, but not limited to, domestic supply wells, irrigation wells, stock wells, sandpoint wells, and heat pump wells — 1,000 feet." | Section 3, Chapter 3, Article 1, Section 3-124 | 2001 | https://dwee.nebraska.gov/sites/default/files/publications/ATTLGRBL.pdf
Nebraska | Hall | Alda | Village | 3100625 | Permit |  |  | Section 3-122 states: "it shall be unlawful for any person, corporation or other legal entity to drill and/or operate any of the following facilities ... without first having obtained a permit from the Alda Village Board of Trustees," including "heat pump wells." Section 3-123 adds that the owner "must complete and submit an application" to the Village Clerk, and the Village Board of Trustees "shall approve or deny such permit." | Section 1 / Section 2, Chapter 3, Article 1, Sections 3-122 and 3-123 | 2001 | https://dwee.nebraska.gov/sites/default/files/publications/ATTLGRBL.pdf
Nebraska | Hall | Alda | Village | 3100625 | Other Prohibitions/Regulations |  |  | Section 3-124 states: "Under no circumstances shall the Alda Village Board approve any permit to drill or operate" listed facilities within the stated distances from municipal wells. The table includes "heat pump wells" with a prohibited distance of "1,000 feet" from the Village of Alda water wells. | Section 3, Chapter 3, Article 1, Section 3-124 | 2001 | https://dwee.nebraska.gov/sites/default/files/publications/ATTLGRBL.pdf
Nebraska | Butler | David City | City | 3102312315 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth, as an integral part of the HVAC system of a principal structure." It further defines system types: "Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground"; "Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid"; "Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer"; and "Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions | 2025 | https://www.davidcityne.com/vimages/shared/vnews/stories/62a09a9a6c318/David_City%20Zoning_Ordinance_1504%20Redacted.pdf
Nebraska | Cass | Weeping Water | City | 3102593383 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a F or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions | 2023 | https://www.weepingwater.org/documents/216/Weeping_Water_Zoning_and_Subdivision_Regulations_FINAL_DRAFT_8.29.23.pdf
Nebraska | Gage | Beatrice | City | 3103390 | Permit |  |  | Sec. 26-189: "Repair of a water well shall not commence before a repair permit has been issued by the city to the owner of the land on which such well is located... In the case of emergency repairs, such repairs may be made without first obtaining the repair permit; provided, however, said permit shall be obtained within ten (10) calendar days subsequent to such emergency repair." Sec. 26-190: "If such applicant's well is found to be in compliance with the 'Water Well Regulations and Standards of the City of Beatrice' and its ordinances, a permit shall then be issued." | Sec. 26-189. Repair of water well; permit required.; Sec. 26-190. Permit for water well; application; fees. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Gage | Beatrice | City | 3103390 | Inspection |  |  | "Within sixty (60) calendar days following the repair of the water well, the owner shall be required to have the well inspected by the community development director." | Sec. 26-189. Repair of water well; permit required. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Gage | Beatrice | City | 3103390 | Decommissioning |  |  | "Whenever a person shall abandon or destroy a water well, such person shall first contact the community development director for the purpose of inspection of such abandonment or destruction process from its inception. All abandoned water wells shall be properly abandoned or destroyed in accordance with applicable regulations and standards on file within the city clerk's office." | Sec. 26-191. Abandoned water well. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Gage | Beatrice | City | 3103390 | Other Prohibitions/Regulations |  |  | "Discharge, recharge, or reinjection wells are prohibited except for the disposal of water where only the temperature of the water has been altered, provided that the maximum water temperature shall not exceed ninety (90) degrees Fahrenheit. It shall be deemed a violation of this section to reinject or inject any chemically altered water or hazardous substance of any kind into or above the groundwater aquifer." | Sec. 26-188. Use of water well; when permitted. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Furnas | Beaver City | City | 3103495 | Definition: Geothermal Heat Pump |  |  | "Any well utilizing geothermal properties of the ground shall meet the following guidelines..." | § 52.47 GEOTHERMAL WELLS | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Furnas | Beaver City | City | 3103495 | Setback - Public Water | 1000 | feet | § 52.46(A) states: "It shall be unlawful to place, maintain, construct or replace any of the following facilities or structures... within the indicated number of feet from the city's public water supply wells." The table lists "Water well — 1,000 feet." | § 52.46 DESIGNATED DISTANCE FROM MUNICIPAL WATER SOURCES; PROHIBITED | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Furnas | Beaver City | City | 3103495 | Setback - Sewer Lines | 50 | feet | § 52.46(A) provides that listed facilities may not be placed within specified distances from the city's public water supply wells; the table includes "Sanitary sewer line — 50 feet." | § 52.46 DESIGNATED DISTANCE FROM MUNICIPAL WATER SOURCES; PROHIBITED | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Furnas | Beaver City | City | 3103495 | Permit |  |  | "It shall be unlawful for any person, corporation or other legal entity to drill and/or operate any of the following facilities within the corporate limits or zoning jurisdiction of the city without first having obtained the proper permit from the City Council: potable water well; any other well, including heat pumps..." Subsection (B) adds: "In order to obtain a permit to drill and/or operate any of the facilities listed above, the owner of the property on which the proposed facility is to be located must make application to the City Council... After reviewing said application, the Council must approve or deny such permit." | § 52.45 PERMIT REQUIRED | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Cuming |  | County | 31039 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2020 | https://cumingcountyne.gov/wp-content/uploads/2021/06/2-Zoning-Regulations-Resolution-20200201-February-26-2020.pdf
Nebraska | Dawson |  | County | 31047 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2019 | https://cms8.revize.com/revize/dawnsoncounty/Dawson%20County%20Zoning.pdf
Nebraska | Dawson | Gothenburg | City | 3104791169 | Permit |  |  | The ordinance lists geothermal as a special-use category in multiple districts: "Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources..." may be used "if a special permit for the use has been obtained" in the AG, AG-1, R-1, R-2, R-3, R-4, C-1, C-2, I-1, and I-2 districts. | § 152.018(D)(12); § 152.019(D)(5); § 152.020(D)(6); § 152.021(D)(10); § 152.022(D)(9); § 152.023(D)(8); § 152.024(D)(6); § 152.025(D)(6); § 152.026(D)(7); § 152.027(D)(7) | 2009 | https://ci.gothenburg.ne.us/pdf/Zoning.pdf
Nebraska | Dodge | North Bend | City | 3105334720 | Definition: Well |  |  | "GEOTHERMAL WELL OR CLOSED LOOP HEAT PUMP WELL. A well constructed for the purpose of installing the underground closed loop necessary to circulate fluid from a closed loop heat pump system." | § 172.002 DEFINITIONS | 2015 | https://www.northbendne.com/_files/ugd/fce8b2_80e4f1b66eb14ed7ac1f49af4438726b.pdf
Nebraska | Dodge | North Bend | City | 3105334720 | Setback - Public Water | 1000 | feet | "Under no circumstances shall the City Council approve any permit to drill or operate any of the below described facilities within the indicated number of feet from the City of North Bend Municipal water wells: ... Any other well within 1,000 feet." The chapter also defines "GEOTHERMAL WELL OR CLOSED LOOP HEAT PUMP WELL" in § 172.002, making that well type an in-scope well category. | § 172.024 DRILLING OR INSTALLATION OF OTHER FACILITIES WITHIN DESIGNATED DISTANCE PROHIBITED | 2015 | https://www.northbendne.com/_files/ugd/fce8b2_80e4f1b66eb14ed7ac1f49af4438726b.pdf
Nebraska | Dodge | North Bend | City | 3105334720 | Permit |  |  | § 172.022(B) states it is unlawful to "drill and/or operate" listed facilities "without having first obtained the proper permit from the governing body of the city;" and § 172.023 provides: "In order to obtain a permit to drill and/or operate any of the facilities listed in § 172.022, the owner of the property... must make application on the proper form..." The same chapter separately defines "GEOTHERMAL WELL OR CLOSED LOOP HEAT PUMP WELL" in § 172.002. | § 172.022 WELLS; § 172.023 PROCEDURE TO OBTAIN PERMIT | 2015 | https://www.northbendne.com/_files/ugd/fce8b2_80e4f1b66eb14ed7ac1f49af4438726b.pdf
Nebraska | Lincoln | Brady | Village | 3106085 | Other Prohibitions/Regulations |  |  | "It shall be unlawful for any person, firm, partnership, corporation or school district to establish or cause to be established any water well for the purpose of extracting water or injecting water within the corporate limits of the municipality; provided, such wells shall be permitted use in operating water to air heat pumps or heat exchangers." | § 52.24 PRIVATE WELLS |  | https://codelibrary.amlegal.com/codes/bradyne/latest/brady_ne/0-0-0-1189
Nebraska | Franklin | Franklin | City | 3106117530 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2019 | https://cdn.prod.website-files.com/616efa093e9c59154f8da1d1/61797bbe7e24c9625d52571f_Franklin%20Zoning%20and%20Subdivision%20Regulations.pdf
Nebraska | Furnas |  | County | 31065 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G |  | https://furnascounty.ne.gov/wp-content/uploads/sites/47/2025/06/zoning_regulations.pdf
Nebraska | Greeley |  | County | 31077 | Permit |  |  | The zoning text expressly allows geothermal only as a special use in multiple districts: "Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources in conformance with 'Net Metering' per Nebraska State Statutes 70-201to 205, as amended." This appears in AG-1 §5.15, AG-2 §5.25, RC §5.35, C §5.44, and I §5.54, each stating such uses may occur "if a special permit for such use has been obtained in accordance with Article 6." Article 6 states: "The County Board may authorize by special permit after public hearing, any of the buildings or uses designated in this resolution as permitted special uses." | 5.15 PERMITTED SPECIAL USES; 5.25 PERMITTED SPECIAL USES; 5.35 PERMITTED SPECIAL USES; 5.44 PERMITTED SPECIAL USES; 5.54 PERMITTED SPECIAL USES; Article 6 - SPECIAL USE PERMIT | 2015 | https://greeleycounty.ne.gov/wp-content/uploads/sites/34/2025/06/zoning_regulations.pdf
Nebraska | Hall | Grand Island | City | 3107919595 | Definition: Geothermal Heat Pump |  |  | "Geothermal water source heat pump systems" are the systems governed by this section; subsection A states that such systems "may be installed and operated within the City of Grand Island" and regulates "any discharge of the spent water from any such system." | 40-17 Geothermal Water Source Heat Pump Systems | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hall | Grand Island | City | 3107919595 | Permit |  |  | "It shall be unlawful for any person... to install a well to be used for geothermal heat transfer purposes... without obtaining a permit for said well." Subsection A also states systems are allowed "subject to permitting and other applicable requirements of the Grand Island City Code." | 40-17(D) Prohibited Acts | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hall | Grand Island | City | 3107919595 | Open-loop Prohibitions |  |  | "New open-loop systems are prohibited in the City of Grand Island and its two (2) mile jurisdictional boundary." The ordinance adds that previously installed open-loop systems are exempt only "until the system requires overhaul and/or replacement." | 40-17(B) | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hall | Grand Island | City | 3107919595 | Other Prohibitions/Regulations |  |  | "It shall be unlawful to connect or discharge any water from said well... to the city stormwater conveyance system without first obtaining a permit for the connection." Subsection A further provides: "In no event shall the spent water from any geothermal water source heat pump system be directed toward or allowed to enter into or onto any publicly maintained street right of way, road right of way, ditch, storm sewer system, or sanitary sewer system." | 40-17(D)(3) | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hamilton |  | County | 31081 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 37. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 38. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 39. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 40. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2019 | https://hamiltoncountyne.gov/wp-content/uploads/2021/07/hamilton-county-zoning-current.pdf
Nebraska | Holt |  | County | 31089 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDWEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." |  | 2025 | https://holtcounty.nebraska.gov/sites/default/files/doc/Holt%20Co%20Zoning%20Update%20Final.pdf
Nebraska | Jefferson |  | County | 31095 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions | 2026 | https://jeffersoncounty.nebraska.gov/sites/default/files/doc/Redacted%20Jefferson%20Co%20NE%20Zoning%20Regs%202026.pdf
Nebraska | Kearney |  | County | 31099 | Permit |  |  | Geothermal is allowed only through district use permissions: in AG-1, RC, AGR, and R-1 it is listed as an accessory use; in C and R-M it is listed under uses requiring a special use permit; in FS it appears under special uses. Examples: 'Alternative energy systems utilizing biomass, geothermal, hydropower, solar energy systems less than 25 kW and/or wind sources...' (Secs. 5.13, 5.23, 5.33, 5.43, 5.62, 5.83); 'A building or premises may be used for the following purposes ... if a special use permit for such use has been obtained in accordance with Article 6' including geothermal in C and FS districts (Secs. 5.54, 5.73). Article 6.1 states the County or Village 'may authorize by special permit after public hearing' designated special uses, and 6.2 states applications are filed with the Clerk and heard by the Planning Commission and County or Village Board before becoming effective. | Article 6; Sections 5.14, 5.24, 5.34, 5.44, 5.54, 5.64, 5.73, 5.83 | 2020 | https://kearneycounty.ne.gov/wp-content/uploads/sites/41/2025/12/zoning_regulations.pdf
Nebraska | Keith | Ogallala | City | 3110192218 | Setback - Public Water | 1000 | feet | "The minimum distance separating the municipal water supply wells of the city from potential sources of contamination shall be as follows: (1) One thousand feet: All water wells, including but not limited to, domestic supply wells, irrigation wells, stock wells, and heat pump wells." | § 52.075 ENCROACHMENT OF POTENTIAL SOURCES OF CONTAMINATION | 2018 | https://www.ogallala-ne.gov/your_government/municipal_code/docs/MunicipalCode_191008_250325.pdf
Nebraska | Keith | Ogallala | City | 3110192218 | Permit |  |  | "Any person who intends to construct a potential source of contamination or enlarge an existing potential source of contamination shall file a written application for a permit with the City Manager. The City Manager may approve a permit which conforms to the distance requirements of this section; provided, however, if the City Manager determines that the proposed construction poses a risk of contaminating a municipal water supply well, the City Manager shall deny the permit." | § 52.075 ENCROACHMENT OF POTENTIAL SOURCES OF CONTAMINATION | 2018 | https://www.ogallala-ne.gov/your_government/municipal_code/docs/MunicipalCode_191008_250325.pdf
Nebraska | Lincoln |  | County | 31111 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground... 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. a. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. b. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions - G |  | https://lincolncountyne.gov/wp-content/uploads/2015/06/zonereg.pdf
Nebraska | Madison | Norfolk | City | 3111992133 | Definition: Well |  |  | "Water Well shall mean any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, obtaining hydrogeologic information, or extracting water from the underground water reservoir." | Water Well shall mean | 2021 | https://bloximages.newyork1.vip.townnews.com/norfolkdailynews.com/content/tncms/assets/v3/editorial/8/d0/8d0d11e2-96e3-11eb-9478-779ac98dea93/606c6ee3ebdf8.pdf.pdf
Nebraska | Nance |  | County | 31125 | Permit |  |  | AG and RC list 'Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources in conformance with "Net Metering" per Nebraska State Statutes §70-2001 to §70-2005' as permitted accessory uses. AGR, HC, and I list the same 'Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources in conformance with "Net Metering" per Nebraska State Statutes §70-2001 to §70-2005' as 'PERMITTED CONDITIONAL USES.' Article 8 provides that 'a conditional permit for such use has been obtained in accordance with Article 8 of these regulations' and that 'After receiving an application and fee... the County Board of Supervisors, after recommendation of the Planning and Zoning Commission, may authorize a conditional use permitted in a zoning district.' | ARTICLE 12: AG GENERAL AGRICULTURAL DISTRICT, Section 2. PERMITTED ACCESSORY USES AND STRUCTURES; ARTICLE 13: RC RURAL CONSERVATION DISTRICT, Section 2. PERMITTED ACCESSORY USES AND STRUCTURES; ARTICLE 14: AGR AGRICULTURAL RESIDENTIAL DISTRICT, Section 3. PERMITTED CONDITIONAL USES; ARTICLE 15: HC HIGHWAY COMMERCIAL DISTRICT, Section 3. PERMITTED CONDITIONAL USES; ARTICLE 16: I INDUSTRIAL DISTRICT, Section 3. PERMITTED CONDITIONAL USES; ARTICLE 8, Section 2. Conditional Uses | 2023 | https://nancecountyne.gov/wp-content/uploads/sites/40/2025/06/Nance-County-Nebraska-Zoning-Regulations.pdf
Nebraska | Thayer | Deshler | City | 3112840 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2024 | https://www.deshlernebraska.com/wp-content/uploads/2024/05/Deshler-NE-Zoning-Ord-2024-rv1-redacted-for-posting.pdf
Nebraska | Phelps |  | County | 31137 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2022 | https://phelpscounty.ne.gov/pdfs/zoning/Phelps%20County%20Final%20Draft%20Zoning%20112622.pdf
Nebraska | Pierce | Plainview | City | 3113992378 | Setback - Public Water | 1000 | feet | § 3-137 provides: "Under no circumstances shall the Plainview City Council approve any permit to drill or operate any of the above-described facilities within the below-referenced number of feet from the City of Plainview Municipal water wells:" including "Potable Water Well 1,000 feet" and "Any Other Well 1,000 feet." Read with § 3-135, closed-loop systems used for heating and cooling are the only new wells allowed and "shall be subject to setbacks and permits as otherwise set forth in this code." | § 3-137 DRILLING OR INSTALLATION OF OTHER FACILITIES WITHIN DESIGNATED DISTANCE FROM MUNICIPAL WATER SOURCES; PROHIBITED | 1996 | https://codelibrary.amlegal.com/codes/plainviewne/latest/plainview_ne/0-0-0-1291
Nebraska | Pierce | Plainview | City | 3113992378 | Permit |  |  | § 3-135 states: "On or after November 21, 2002, no new water wells of any type shall be drilled or operated within the corporate limits, with the exception of closed loop systems used for heating and cooling. Closed loop systems shall be subject to setbacks and permits as otherwise set forth in this code." § 3-136 adds: "In order to obtain a permit to drill and/or operate any of the facilities listed in section 3-135, the owner of property on which the proposed facility is to be located, must make application on the proper form provided by the Governing Body of the City of Plainview... the Plainview City Council must approve or deny said permit." | § 3-135 DRILLING AND OPERATION OF WELLS, AND OTHER UNDERGROUND FACILITIES OR CONTAMINATING FACILITIES UNLAWFUL; § 3-136 WELLS AND OTHER FACILITIES; PROCEDURE TO OBTAIN PERMIT | 1996 | https://codelibrary.amlegal.com/codes/plainviewne/latest/plainview_ne/0-0-0-1291
Nebraska | Red Willow | McCook | City | 3114591882 | Permit |  |  | "All fences constructed in the City of McCook shall comply with the provision of this section and obtain a building permit." | Section 2102. Fences, Walls, Hedges | 2017 | https://www.cityofmccook.com/276/Zoning-Ordinance-PDF
Nebraska | Saunders | Wahoo | City | 3115550965 | Permit |  |  | "If a Building Permit for the construction of a residence is issued by the City of Wahoo for an undeveloped lot in any of the Areas, a domestic potable water well may be installed only if permitted by the Board of Public Works of the City of Wahoo." | § 5.22.06(3) Water, Potable and Non-Potable | 2005 | https://www.wahoo.ne.us/vimages/shared/vnews/stories/50364172e06a0/wahoozoning%20regulations%20to%208-20-2014.pdf
Nebraska | Saunders | Wahoo | City | 3115550965 | Other Prohibitions/Regulations |  |  | "Any existing water wells which are being used for a well-to-well ground source heat pump system will be allowed to remain in service until said system is not permitted by the State of Nebraska, said water to be used for non-potable purposes only." | § 5.22.06(3)(d) Water, Potable and Non-Potable | 2005 | https://www.wahoo.ne.us/vimages/shared/vnews/stories/50364172e06a0/wahoozoning%20regulations%20to%208-20-2014.pdf
Nebraska | Seward |  | County | 31159 | Definition: Geothermal Heat Pump |  |  | "GROUND WATER HEAT PUMP WELL shall mean a well constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground... 2. Closed Loop Heat Pump well shall mean a well constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. a. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. b. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | 2.03.208 GROUND WATER HEAT PUMP WELL | 2007 | https://sewardcountyne.gov/wp-content/uploads/sites/50/2025/09/Zoning-Regulations.pdf
Nebraska | Seward |  | County | 31159 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be a closed loop system." | 4.13.03 Specific Conditions Required | 2007 | https://sewardcountyne.gov/wp-content/uploads/sites/50/2025/09/Zoning-Regulations.pdf
Nebraska | Stanton |  | County | 31167 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2025 | https://stantoncounty.nebraska.gov/sites/default/files/doc/Zoning%20Regulations%20-%20amended%20June%202025.pdf
Nebraska | Stanton | SBE | Precinct | 3116792862 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. ... 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2023 | https://stantoncounty.nebraska.gov/sites/default/files/doc/2017%20Zoning%20Regulations%20approved%20nov%202017%20-%20amended%202023.pdf
Nebraska | Stanton | SBE | Precinct | 3116792862 | Permit |  |  | "No building, structure, or land ... shall hereafter be used or occupied and no building or structure or part thereof shall hereafter be erected, constructed, reconstructed, moved, or structurally altered, except in conformity with the provisions of this Resolution ... and except after receiving a zoning permit from the Stanton County Zoning Administrator..." Also: "Any structure over 64 square feet in size shall require a permit from the Stanton County Zoning Office." | ARTICLE 3: GENERAL REGULATIONS, Section 3.07 Scope of Regulations | 2023 | https://stantoncounty.nebraska.gov/sites/default/files/doc/2017%20Zoning%20Regulations%20approved%20nov%202017%20-%20amended%202023.pdf
Nebraska | Thayer |  | County | 31169 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2025 | https://thayercountyne.gov/wp-content/uploads/2025/06/Thayer-County-Zoning-Regulation-signed-2025-Redacted-Version-1.pdf
Nebraska | Washington |  | County | 31177 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G |  | http://www.co.washington.ne.us/media/draftplan/Washington_County_Zoning_Regulations_draft.pdf
Nebraska | Clay | Harvard | City | 3121345 | Setback - Public Water | 100 | feet | "Systems utilizing the geothermal properties of the ground for water wells... (F) Must be located no closer than 100 feet to the city's drinking water source." | § 52.56 GEOTHERMAL SYSTEMS | 2002 | https://codelibrary.amlegal.com/codes/harvardne/latest/harvard_ne/0-0-0-1779
Nebraska | Clay | Harvard | City | 3121345 | Open-loop Prohibitions |  |  | "Systems utilizing the geothermal properties of the ground for water wells: (A) Must be a closed loop system." | § 52.56 GEOTHERMAL SYSTEMS | 2002 | https://codelibrary.amlegal.com/codes/harvardne/latest/harvard_ne/0-0-0-1779
Nebraska | Platte | Humphrey | City | 3123480 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 12. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 13. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 14. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 15. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2019 | https://www.cityofhumphrey.com/vimages/shared/vnews/stories/5cbdbfcf3869e/Humphrey%20Zoning_070318.pdf
Nebraska | Sherman | Rockville | Village | 3142075 | Definition: Well |  |  | "WATER WELL. Any excavation that is drilled, corralled, bored, washed, dug, driven, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal property of the ground or extracting water from or injecting water into the underground water. WATER WELL shall not include any excavation made for obtaining or prospecting for oils, natural gas, minerals, or products mined or quarried or inserting media to repressure oil or natural gas bearing formation." | § 51.23 WATER WELLS. (A) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Sherman | Rockville | Village | 3142075 | Setback - Public Water | 1000 | feet | "It shall be unlawful to place, maintain, construct, or replace any of the following structures or conduct any of the following activities within the distance specified below from any existing village water well, water storage tanks, or existing underground water mains." The table lists "Water well — 1,000 feet." | § 51.23 WATER WELLS. (C)(1) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Sherman | Rockville | Village | 3142075 | Setback - Water Lines | 500 | feet | "It shall be unlawful to place, maintain, construct, or replace any of the following structures or conduct any of the following activities within the distance specified below from any existing village water well, water storage tanks, or existing underground water mains." The table lists "Village water main — 500 feet." | § 51.23 WATER WELLS. (C)(1) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Sherman | Rockville | Village | 3142075 | Permit |  |  | "The construction of a water well, within the corporate limits or within one mile of the corporate limits of the village, shall not be started unless a permit approved by the Village Board has been obtained." Also, for closer placement approved under division (E), "No installation shall be made without the approval of both the Village Board and Department of Health of the state." | § 51.23 WATER WELLS. (D) and (E)(2) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Lincoln | Sutherland | Village | 3147920 | Setback - Public Water | 1000 | feet | The table of minimum distances from municipal water supply wells lists: "All water wells, including, but not limited to, domestic supply wells, irrigation wells, stock wells and heat pump wells — 1,000" feet. | § 53.26 MUNICIPAL WATER SUPPLY PROTECTION | 2013 | https://codelibrary.amlegal.com/codes/sutherlandne/latest/sutherland_ne/0-0-0-1754
Nebraska | Lincoln | Sutherland | Village | 3147920 | Permit |  |  | "Any person who intends to construct a potential source of contamination or enlarge an existing potential source of contamination shall file a written application for a permit with the Board of Trustees." The Board "may approve a permit which conforms to the distance requirements of this section" and "shall deny the permit" if the proposed construction poses a contamination risk to a municipal water supply well. | § 53.26(C) MUNICIPAL WATER SUPPLY PROTECTION | 2013 | https://codelibrary.amlegal.com/codes/sutherlandne/latest/sutherland_ne/0-0-0-1754
Nebraska | Lancaster | Waverly | City | 3151770 | Definition: Well |  |  | "For purposes of this Article, 'water well' shall mean any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground or extracting water from or injecting water into the underground water reservoir." | § 51.39 WELL - HEAD PROTECTION: DEFINITIONS | 2021 | https://www.citywaverly.com/vimages/shared/vnews/stories/620ea640e9a25/Wavelry%20Municipal%20Code.pdf
Nebraska | Lancaster | Waverly | City | 3151770 | Setback - Public Water | 500 | feet | Section 51.40 states: "It shall be unlawful to place, maintain, construct, or replace any of the following structures or conduct any of the following activities within the distance specified below from existing Municipal water well:" The table lists "Closed-Loop Food Grade Heat Pump" at "500" "Feet" ("150" meters). | § 51.40 WELL - HEAD PROTECTION: PLACEMENT, MAINTENANCE AND CONSTRUCTION; PROHIBITIONS | 2021 | https://www.citywaverly.com/vimages/shared/vnews/stories/620ea640e9a25/Wavelry%20Municipal%20Code.pdf
Nebraska | Lancaster | Waverly | City | 3151770 | Permit |  |  | "Any well that penetrates the aquifer for purposes of extracting water or injecting water or any other substance, or for purposes of testing or monitoring ground water must have a permit issued by the City. Ground source heat pumps with closed loop systems used for heating and cooling of facilities are exempt from the permit requirement." | § 51.28 MANDATORY HOOKUP | 2021 | https://www.citywaverly.com/vimages/shared/vnews/stories/620ea640e9a25/Wavelry%20Municipal%20Code.pdf
Nevada | Clark |  | County | 32003 | Other Prohibitions/Regulations |  |  | The AEO key states: "4800* Renewable energy facilities (ex. Solar and geothermal facilities as well as wind turbines) shall delineate methods of mitigating possible plumes." | §30.02.26C, Airport Environs Overlay (AEO) | 2024 | https://www.clarkcountynv.gov/assets/documents/government/departments/comprehensive_planning_department/library/title-30-eff-11-20-24.pdf
Nevada | Elko |  | County | 32007 | Permit |  |  | Section 3-1-5(H) states: "Solar, Hydronics and Geothermal Code Fees: All editions of the Uniform Plumbing Code, present and future, are hereby amended and modified as follows: Table 104.5 - Solar, Hydronics and Geothermal Code Fees, the following is added: System fee schedule (note: the following do not include permit issuing fee) shall be set by resolution adopted by the Elko County commission." Section 3-1-1(I) also adopts "The 2018 Uniform Solar, Hydronics and Geothermal Code." | 3-1-5: RESTRICTIONS / 3-1-1: CODES ADOPTED | 2021 | https://codelibrary.amlegal.com/codes/elkocountynv/latest/elkocounty_nv/0-0-0-779
Nevada | Lyon |  | County | 32019 | Permit |  |  | 'Geothermal direct use wells for commercial or industrial space heating, food dehydration, or other similar such uses shall be subject to the standards listed in this chapter and Nevada Revised Statutes 534A.' | 15.336.08: GEOTHERMAL GENERATING SYSTEMS, F. Geothermal Direct Use Wells | 2025 | https://codelibrary.amlegal.com/codes/lyoncountynv/latest/lyoncounty_nv/0-0-0-8734
Nevada | Washoe | Reno North | City | 3203194703 | Definition: Geothermal Heat Pump |  |  | "Rebates for Solar/Renewable Technologies. (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno North | City | 3203194703 | Permit |  |  | "City Facilitation of Market Mechanisms in the Buildings Sector - Various city policies to facilitate the purchase of energy efficient appliances and the purchase of solar/renewable technologies ... Policies could include ... Rebates for Solar/Renewable Technologies, (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southeast | City | 3203194709 | Definition: Geothermal Heat Pump |  |  | "Rebates for Solar/Renewable Technologies. (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southeast | City | 3203194709 | Permit |  |  | "City Facilitation of Market Mechanisms in the Buildings Sector - Various city policies to facilitate the purchase of energy efficient appliances and the purchase of solar/renewable technologies ... Policies could include ... Rebates for Solar/Renewable Technologies, (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southwest | City | 3203194712 | Definition: Geothermal Heat Pump |  |  | "Rebates for Solar/Renewable Technologies. (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southwest | City | 3203194712 | Permit |  |  | "City Facilitation of Market Mechanisms in the Buildings Sector - Various city policies to facilitate the purchase of energy efficient appliances and the purchase of solar/renewable technologies ... Policies could include ... Rebates for Solar/Renewable Technologies, (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
New Hampshire | Belknap | Alton | Town | 3300101060 | Permit |  |  | "If water is discharged back into the bedrock well for geothermal applications, then the applicant must demonstrate that the discharge water is not contaminated and is in compliance with the standards and requirements of the New Hampshire Department of Environmental Services." | 5.12 SURFACE WATERS | 2012 | https://alton.nh.gov/wp-content/uploads/2026/01/Site-Plan-Review-Regulations.pdf
New Hampshire | Belknap | Alton | Town | 3300101060 | Screening |  |  | "Air conditioners, heat pumps, compressors, generators, fans, and other devices which produce noise shall be so located and screened as to meet the above noise standard, and so not to be visually offensive to adjacent property owners or as seen from public streets. Each site plan shall indicate the location of all such devices and include a brief description of how this standard will be met." | 5.17 NOISE | 2012 | https://alton.nh.gov/wp-content/uploads/2026/01/Site-Plan-Review-Regulations.pdf
New Hampshire | Cheshire | Keene | City | 3300539300 | Definition: Geothermal |  |  | "Geothermal heating and cooling systems (e.g. groundwater wells and subsurface heat exchange installations)" are listed as permitted uses in the Surface Water Protection Overlay District without a surface water protection conditional use permit. | Section 11.5 PERMITTED USES | 2025 | https://keenenh.gov/wp-content/uploads/2026/01/Land-Development-Code_Amended-November-2025.pdf
New Hampshire | Coos | Carroll | Town | 3300710100 | Definition: Geothermal Heat Pump |  |  | "Accessory Use - A use customarily incidental and subordinate to the principal building or use and located on the same lot with such principal building or lot. The following examples are considered accessory uses, but are not limited to, antennas, swimming pools, satellite dishes, garages, barns, storage sheds, storage of a registered camper or recreational vehicle, and renewable energy facilities for on-site use including wind, solar and geothermal." | Section 202. Definitions | 2024 | https://carrollnh.org/wp-content/uploads/2024/07/2024-Zoning-Ordinance.pdf
New Hampshire | Coos | Carroll | Town | 3300710100 | Setback - Yards | 20 | feet | Section 202 defines setback/yard applicability for accessory geothermal use: "renewable energy facilities for on-site use including wind, solar and geothermal. All accessory uses must follow zoning set-back requirements." The ordinance defines "Yard - That portion of a lot formed by the required setback which may not be occupied by a building or other structure." District yard setbacks include RES 1: "SIDE SETBACK: 20 Feet"; RES 2 residential: "SIDE SETBACK: 20 Feet"; R-B: "SIDE SETBACK: 20 Feet"; RU: "SIDE SETBACK: 30 feet." | Section 202. Definitions; Section 403.2 Residential: RES 1; Section 403.3 Residential: RES 2; Section 403.4 Residential - Business: R-B; Section 403.6 Rural: RU | 2024 | https://carrollnh.org/wp-content/uploads/2024/07/2024-Zoning-Ordinance.pdf
New Hampshire | Grafton | Lisbon | Town | 3300942020 | Definition: Geothermal |  |  | "1.28 Renewable Energy Facility : A facility for the generation of solar, wind or geothermal energy." | ARTICLE I DEFINITIONS §1.28 | 2023 | https://www.lisbon.nh.gov/DocumentCenter/View/344/Zoning-Ordinances-Regulations-2023-PDF
New Hampshire | Grafton | Waterville Valley | Town | 3300979380 | Permit |  |  | "Small wind, solar or geothermal energy systems designed primarily to supply energy for on-site use" are listed as accessory uses ("a") in all districts shown in the use table. Article VIII states: "Permit Required - After passage of this Ordinance, it shall be unlawful to change the nature or extent of the use of any building or lot, erect and use any building, sign or other structure, or alter any existing sign or the size of any building or other structure, or relocate any building or other structure in any district without first obtaining a permit from the Selectmen or their agent." | Article IV - Uses | 2026 | https://www.watervillevalleynh.gov/planning-board/files/zoning-ordinance-2026-updated
New Hampshire | Merrimack | Bradford | Town | 3301306980 | Permit |  |  | Within the SWOD Buffer, "Conditional Uses" include "p. Geothermal heating and cooling systems, including but not limited to related groundwater wells and subsurface heat exchange installations." The ordinance further states: "An application for a CUP will be considered at a public hearing" and "Completed Conditional Use Permit Applications will include" specified materials. | Article XI SURFACE WATER PROTECTION OVERLAY DISTRICT (SWOD), D. Uses / E. Conditional Use Permit Requirements | 2025 | https://bradfordnh.gov/uploads/2025-bradford-zoning-ordinance.pdf
New Hampshire | Merrimack | Bradford | Town | 3301306980 | Inspection |  |  | During construction on parcels including land within the SWOD Buffer, "the boundaries of the SWOD Buffer areas will be marked on the site with stakes and flagging along the buffer perimeter. Such markings will remain in place until all construction is complete and has been inspected and approved." | Article XI SURFACE WATER PROTECTION OVERLAY DISTRICT (SWOD), D. Uses | 2025 | https://bradfordnh.gov/uploads/2025-bradford-zoning-ordinance.pdf
New Hampshire | Rockingham | Rye | Town | 3301566180 | Definition: Geothermal |  |  | "RENEWAL ENERGY SYSTEMS: Renewal energy systems include solar systems, small wind energy systems, geothermal systems and hydro systems. (added 9-20-2022)" | § 202-1.14. Definitions | 2022 | https://www.ryenh.gov/DocumentCenter/View/5460
New Jersey | Atlantic | Linwood | City | 3400140530 | Definition: Geothermal |  |  | "RENEWABLE ENERGY SYSTEM — Any structure or installation, such as a small wind energy system, solar- collecting array, or geothermal system, which is designed and intended to produce energy from natural forces such as wind, sunlight or geothermal heat." | § 273-4 Definitions | 2021 | https://ecode360.com/14620824
New Jersey | Atlantic | Linwood | City | 3400140530 | Permit |  |  | "A zoning permit shall be required for the installation of a renewable energy system." Also, "An owner shall submit an application to the Zoning Officer for a permit for a renewable energy system." | § 273-6A; § 273-8A | 2021 | https://ecode360.com/14620824
New Jersey | Atlantic | Linwood | City | 3400140530 | Inspection |  |  | "The Zoning Officer may enter any property for which a permit has been issued under this chapter to conduct inspections to determine whether the conditions stated in the permit have been met." | § 273-10B | 2021 | https://ecode360.com/14620824
New Jersey | Atlantic | Linwood | City | 3400140530 | Decommissioning |  |  | "A renewable energy system that is out of service for a continuous twelve-month period will be deemed abandoned." If abandoned, "the owner of the renewable energy system shall remove the system at the owner's sole expense within three months after the owner receives the notice of abandonment." | § 273-7 | 2021 | https://ecode360.com/14620824
New Jersey | Bergen | River Vale | Township | 3400363690 | Permit |  |  | The ordinance expressly includes geothermal-type systems in the permit fee schedule: Plumbing Subcode fees, § 90-4A(3)(b)[23]: "Heating and cooling equipment such as ground source, heat pump systems, heat pumps, solar thermal systems but not limited to these systems: $125 each." Mechanical subcode fees, § 90-4A(5)(b): "Replacement of heating and cooling equip such as ground source, heat pump systems, heat pumps solar: $150." Also, § 90-4A states: "The fee for a construction or zoning permit shall be the sum of the subcode fees listed... and shall be paid before the permit is issued." | § 90-4 Fees | 2024 | https://ecode360.com/11325645
New Jersey | Burlington | Mount Laurel | Township | 3400549020 | Permit |  |  | "The fee for the installation of a geothermal system shall be $81.00." | § 66-3 Fees, (2) Plumbing Subcode Fees, a.13 | 2021 | https://cms7files.revize.com/mountlaurel/Document%20Center/Department/Municipal%20Clerk's%20Office/Upcoming%20Ordinances/O5.21.pdf
New Jersey | Cape May | Middle | Township | 3400945810 | Definition: Geothermal |  |  | "Any structure or installation, such as a wind turbine, solar collecting array, or geothermal system, which is designed and intended to produce energy from natural forces, such as wind, sunlight or geothermal heat." | § 250-629B. Definition | 2018 | https://ecode360.com/9072391
New Jersey | Cape May | Middle | Township | 3400945810 | Setback - Building Foundation | 10 | feet | "The minimum separation distance required between any structures associated with the renewable energy system and any other structures or buildings on site is 10 feet." Section § 250-629B defines a renewable energy system to include "a ... geothermal system." | § 250-629C(3) | 2018 | https://ecode360.com/9072391
New Jersey | Cape May | Middle | Township | 3400945810 | Permit |  |  | "Permit. A zoning permit and construction permit shall be required for the installation of a renewable energy system." Section § 250-629B defines a renewable energy system to include "a ... geothermal system." | § 250-629E(2) Permit requirements | 2018 | https://ecode360.com/9072391
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Definition: Well |  |  | "CLOSED LOOP GEOTHERMAL WELL. A well or borehole drilled or a shallow trench installed in the earth, wherein a series of pipes is installed into the opening and connected to a heat exchange system in the dwelling. The pipes form a 'closed loop' (hence the name) and are filled with a heat transfer fluid. The fluid is circulated through the piping from the opening into the heat exchanger and back. The system functions in the same manner as the open looped system, except there is no pumping of groundwater." | § 153-21 Definitions | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Setback - Wastewater | 50 | feet | For vertical closed loop geothermal wells, the separation table requires "Septic leaching fields — 50 feet" and "Septic tank — 25 feet." For horizontal closed loop geothermal systems, the table requires "Septic leaching fields — 25 feet" and "Septic tank — 25 feet." | § 153-39B(1)(a) and § 153-39C(1) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Setback - Private Water | 100 | feet | For vertical closed loop geothermal wells, the separation table requires "On-site or off-site water supply well(s) — 100 feet." Horizontal systems require "On-site or off-site water supply well(s) — 50 feet." | § 153-39B(1)(a) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Setback - Public Water | 500 | feet | For both vertical and horizontal closed loop geothermal systems, the separation tables require "Public water supply well or future well site — 500 feet." | § 153-39B(1)(a) and § 153-39C(1) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Setback - Hazardous Materials/Fertilizers | 500 | feet | For both vertical and horizontal closed loop geothermal systems, the separation tables require "Known groundwater plume of contamination (as mapped by a governmental agency) — 500 feet." | § 153-39B(1)(a) and § 153-39C(1) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Permit |  |  | "No person shall locate, construct or alter any geothermal well within the Township of Kingwood until a permit for the location, construction or alteration of such well has been issued by the administrative authority." Also, "Compliance with all state permitting requirements is a prerequisite to the issuance of a Kingwood Township geothermal well construction permit." | § 153-38 Geothermal well construction permit | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Inspection |  |  | "All closed loop systems must be hydrostatically pressure tested at not less than 1 1/2 times working pressure for two hours." Also, "The heat exchanger installer shall certify that the installed system meets pressure test and heat exchange fluid requirements." | § 153-39B(4) and § 153-39B(6) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Certification |  |  | "At the completion of the geothermal system construction, the applicant shall submit an as-built survey with GPS coordinates for each well, one geologic/well log and well completion certificates. The heat exchanger installer shall certify that the installed system meets pressure test and heat exchange fluid requirements." | § 153-39B(6) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | Township | 3401937065 | Decommissioning |  |  | "All geothermal wells shall be abandoned in accordance with the latest and most applicable NJDEP requirements. Records of decommissioning/abandonment shall be submitted to the Township and administrative authority. Any wells/borings that are drilled and not used for a geothermal installation must be abandoned immediately as per NJDEP requirements." Also, "Any geothermal well not in normal operation for a period of 24 months or more shall be considered inactive and shall be abandoned. The tubing in such wells must be flushed with clean water until all of the ground heat exchanger circulating fluids have been flushed out." | § 153-39D | 2022 | https://ecode360.com/10106816
New Jersey | Mercer | Ewing | Township | 3402122185 | Inspection |  |  | The ordinance expressly sets fees for geothermal inspections: "[5] Geothermal inspections: [a] Residential: $50. [b] Commercial: $100." It also establishes related inspection categories generally under administrative fees, including "Off hour inspections" and "Expedited inspections," but the geothermal-specific inspection requirement is the quoted geothermal inspection fee. | § 172-25A(2) Plumbing subcode fees; § 172-25A(5) Administrative Fees | 2023 | https://ecode360.com/EW1628/document/744062108.pdf
New Jersey | Mercer | Lawrence | Township | 3402139510 | Permit |  |  | "The fee for plan review of a building for compliance under the alternate systems and nondepletable energy source provisions of the energy subcode shall be $240.00 for one- and two-family residences ... and for all other structures as per Ordinance No. 1893-06 For GeoThermal Heating/Cooling Systems." | CERTIFICATES AND OTHER PERMITS | 2009 | https://www.lawrencetwp.com/media/Departments/Construction/Construction%20Permit%20Fees.pdf
New Jersey | Monmouth | Bradley Beach | Borough | 3402506970 | Permit |  |  | "The fee for the installation of a geo-thermal system shall be $75." | § 160-3(B)(2)(n) | 2026 | https://ecode360.com/7043039
New Jersey | Monmouth | Howell | Township | 3402533300 | Permit |  |  | The Electrical Subcode fee schedule expressly includes geothermal equipment under electrical permit fee calculations: 'Electrical devices (This includes transformers and generators and P V devices)' with fee brackets by kW, and the average ratings table lists 'Geothermal: range from 3.8 KW to 19.2KW, plus heat pump 2.6 KW to 7.4KW.' | § 139-86, Article XXXVI Uniform Construction Code Fees, C. Electrical Subcode fees, (2)(b) Electrical devices | 2011 | http://nj-howelltownship.civicplus.com/AgendaCenter/ViewFile/Item/18?fileID=81
New Jersey | Monmouth | Sea Girt | Borough | 3402566330 | Screening |  |  | "All exterior mechanical equipment, including units for heat, ventilation, air- conditioning, pool pumps and accessories, heat pumps, other than individual air-conditioners to serve a building property shall be located in the rear yard and/or on the top story of either the principal or accessory buildings, either inside or outside." If installed on the buildings, "they shall not be visible from the front or side street or from ground level of immediately adjacent properties and shall be located behind a solid non-transparent physical buffer such as a parapet wall or solid short fence so as to dampen noise effects on neighboring properties." | § 17-5.4 Mechanical Equipment | 2026 | https://ecode360.com/36181331
New Jersey | Monmouth | Wall | Township | 3402576460 | Permit |  |  | "No person shall drill, construct, install or redesignate the use of any well until a permit shall have been issued by the Board of Health." | § 222-54-10. Permit required. | 2018 | https://www.wallnj.gov/DocumentCenter/View/4184/Ordinance-19-2018-Well-Regulation
New Jersey | Monmouth | Wall | Township | 3402576460 | Inspection |  |  | "The Wall Township Health Department shall have access and entry to any property upon which there is located a well or individual sewage disposal system for the purpose of inspecting and/or testing the same." | § 222-54-8. Right of entry. | 2018 | https://www.wallnj.gov/DocumentCenter/View/4184/Ordinance-19-2018-Well-Regulation
New Jersey | Morris | Morris | Township | 3402748090 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM — A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." | § 95-34.4B Definitions | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | Township | 3402748090 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM, CLOSED-LOOP — A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." Also: "OPEN-LOOP GEOTHERMAL SYSTEM — A type of geothermal system that utilizes a water-supply well and a water pump to deliver groundwater to a water-source heat pump." | § 95-34.4B Definitions | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | Township | 3402748090 | Setback - Right of Way | 25 | feet | "Geothermal systems shall not encroach on public drainage, utility roadway or trail easements of any nature." Also: "All geothermal systems shall be located a minimum distance of 25 feet from any property line." | § 95-34.4E(4) and (5) | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | Township | 3402748090 | Setback - Property Lines | 25 | feet | "All geothermal systems shall be located a minimum distance of 25 feet from any property line." | § 95-34.4E(5) | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | Township | 3402748090 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems are prohibited." | § 95-34.4E(2) | 2020 | https://ecode360.com/10355002
New Jersey | Passaic | Bloomingdale | Borough | 3403106340 | Permit |  |  | The construction permit fee schedule includes a specific geothermal entry: "Installation or removal of Geothermic or Photovoltaic systems — $30 per $1,000." The section also states: "The fee for a construction permit shall be the sum of the subcode fees listed in the Fee Schedule hereunder, and shall be paid before the permit is issued." | § 11-1.2 Fees | 2024 | https://ecode360.com/36000989
New Jersey | Salem |  | County | 34033 | Definition: Well |  |  | "Closed loop geothermal well" means a well or a borehole drilled to a specific depth either singly or in a series wherein a continuous closed loop of pipe is inserted from one well to another for the purpose of noncontact thermal energy transfer from a fluid in the loop to or from the earth. "Open loop geothermal well" means a well designed and installed specifically for use of the earth as a source for heat extraction/rejection. | 7:9D1.5 Definitions | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Definition: Geothermal Heat Pump |  |  | "Closed loop geothermal well" means a well or a borehole drilled to a specific depth either singly or in a series wherein a continuous closed loop of pipe is inserted from one well to another for the purpose of noncontact thermal energy transfer from a fluid in the loop to or from the earth. "Open loop geothermal well" means a well designed and installed specifically for use of the earth as a source for heat extraction/rejection. | 7:9D1.5 Definitions | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Setback - Building Foundation | 5 | feet | "All new Category 1 and Category 2 wells shall be located at least five feet horizontally from a building or any portion thereof, except for a pumphouse." Open loop geothermal wells are listed as Category 2 wells in 7:9D2.1(a)2. | 7:9D2.7 Minimum distance requirements | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Setback - Fuel (above ground) | 25 | feet | "All Category 2 wells shall be located no less than 25 feet from a fuel storage tank." Open loop geothermal wells are included in Category 2 under 7:9D2.1(a)2. | 7:9D2.7 Minimum distance requirements | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Minimum Well Depth | 50 | feet | For potable water supply wells in unconsolidated formations, "All well casing shall be no less than four inches in inner diameter and no less than 50 feet in depth." Open-loop geothermal wells are Category 2, but the 50-foot minimum depth in this section applies explicitly to potable Category 1 wells, not all geothermal wells. | 7:9D2.3 Specific requirements for the construction of Category 1 and Category 2 wells | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Permit |  |  | "the owner or authorized agent ... and the New Jersey licensed well driller of the proper class shall sign and obtain a valid New Jersey well permit from the Department prior to drilling, constructing, installing, physically altering, or redesignating the use of any well." Also, "A licensed well driller may obtain a sitewide permit when installing ... closedloop geothermal well systems," and "A State well permit shall be required prior to the construction of all wells as described in N.J.A.C.7:9D2." | 7:9D1.11 Well permits | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Inspection |  |  | The Department may, as a permit condition, require the driller to "Provide advanced notice of drilling in order to allow for the inspection of the well site by authorized representatives and/or provide for the taking of geophysical logs, geologic or water samples as necessary." Also, "Original State well permits or copies thereof shall be available onsite at all times for inspection by any authorized local and/or State representative." | 7:9D1.11 Well permits | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Licensed Driller |  |  | "No person shall drill, construct, install, repair, replace, modify, stimulate or decommission any well ... without possessing a valid New Jersey well driller's license of the proper class unless that activity is performed under the direct and immediate onsite supervision of a New Jersey licensed well driller of the proper class." Also, "No person shall conduct any operation involving the drilling ... of any well ... without the immediate onsite supervision of a licensed well driller of the proper class," and "A New Jersey licensed well driller shall be onsite and directly supervise each well drilling operation, and there shall be one licensed well driller of the proper class on site for each well drilling rig on site." | 7:9D1.6 General provisions; 7:9D2.2 General construction requirements for all wells | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Certification |  |  | For applicants lacking the required New Jersey experience, the rule requires "evidence that he or she is in possession of a valid National Ground Water Association Certification (NGWA) in the appropriate well drilling category" for journeyman/journeyman (Class B) applicants and similarly for monitoring well drilling applicants. | 7:9D1.8 Application and licensing examination procedures and requirements for well driller licenses of the proper class and pump installer licenses | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Decommissioning |  |  | "Unsuitable or nonproductive wells that cannot be used for their intended purpose shall be decommissioned in accordance with N.J.A.C. 7:9D3. These include, but are not limited to, wells which are abandoned during construction, are contaminated, exhibit a loss of supply or are damaged." Also, "When the drilling of a borehole for any well is temporarily suspended and the rig moves away from the drilling site, the borehole shall be considered abandoned and subject to the decommissioning requirements in N.J.A.C.7:9D3." In addition, activities performed without an individual permit under 7:9D1.11(g) must result in any well being "decommissioned in accordance with N.J.A.C.7:9D3." | 7:9D2.2 General construction requirements for all wells; 7:9D1.11 Well permits | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem |  | County | 34033 | Other Prohibitions/Regulations |  |  | For dewatering wells, "The screening of a dewatering well in more than one aquifer is prohibited." | 7:9D2.5 Requirements for the installation of Category 4 wells | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Somerset | Branchburg | Township | 3403507180 | Definition: Geothermal Heat Pump |  |  | "On or after the connection date, a nonpotable well may be installed, maintained, or used for geothermal heating and cooling purposes only." | § BH3A-5A RESTRICTIONS ON NONPOTABLE WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | Township | 3403507180 | Permit |  |  | "Any well installed, maintained or used for geothermal hearing and cooling purposes must be registered with the State of New Jersey as a nonpotable well." | § BH3A-5A(b) RESTRICTIONS ON NONPOTABLE WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | Township | 3403507180 | Inspection |  |  | "Every well closed and sealed shall be approved by the Township Health Department." | § BH3A-6 CLOSING AND SEALING OF WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | Township | 3403507180 | Decommissioning |  |  | "Not later than the Mandatory Connection Date, all private wells within a Ground Water Impact Area shall be closed and sealed by the owner in accordance with State regulations." | § BH3A-6 CLOSING AND SEALING OF WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | Township | 3403507180 | Other Prohibitions/Regulations |  |  | "On and after the Mandatory Connection Date, there shall be no well installations of any type within a Ground Water Impact Area. Wells used solely for groundwater monitoring, and owned or controlled by the New Jersey Department of Environmental Protection, are permitted." | § BH3A-7 FUTURE WELL INSTALLATIONS PROHIBITED | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Bridgewater | Township | 3403507720 | Permit |  |  | "geothermal facilities, as an accessory use only, are permitted in all zones when wholly provided within a principal structure. Board review is not required if the geothermal facility is located within a principal structure." Also: "All renewable energy facilities require approval from the Zoning Officer and construction office prior to receiving a building permit. Applications for an energy facility shall include information demonstrating compliance with the provisions of this ordinance." | Section 126-335(B)(6) and (9) | 2012 | https://ecode360.com/BR0606/document/753042732.pdf
New Jersey | Sussex | Sparta | Township | 3403769690 | Definition: Well |  |  | "CLOSED LOOP GEOTHERMAL WELL - Shall mean a well into which a continuous closed loop of pipe is inserted for the purpose of non-contact thermal energy transfer from a fluid in the loop to or from the earth." | 19-3.4. Definitions | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | Township | 3403769690 | Permit |  |  | "No person shall locate, construct or alter any geothermal well system until a permit for the location, construction or alteration of geothermal well system shall have been issued by the Sussex County Health Department." Also, "All proposed geothermal systems will require a permit application, and must include a list of equipment to be served and system design drawings." | 19-1.4(c); 19-11.3(a) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | Township | 3403769690 | Certification |  |  | "Geothermal wells shall be constructed or altered by a duly licensed New Jersey geothermal well installation contractor who is licensed as set forth pursuant to N.J.A.C. 7:9D-1.7 and 1.8 and in complete conformance with the Township standards in effect at the time." | 19-11.1(a) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | Township | 3403769690 | Decommissioning |  |  | "After connection to the Township's water utility system, each property owner shall seal their well(s) in compliance with Sussex County Health Department regulations and with the requirements of the Department of Environmental Protection, Division of Water Resources, and in accordance with the standard specifications for sealing abandoned wells which have been adopted by that agency. All wells must be closed by a New Jersey licensed well driller." | 19-6.10 | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | Township | 3403769690 | Open-loop Prohibitions |  |  | "Only Closed Loop Geothermal Well systems are allowed to be installed within Sparta Township. Open loop geothermal well systems are prohibited." | 19-11.2(a) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | Township | 3403769690 | Other Prohibitions/Regulations |  |  | "Cross connections between a private geothermal well system and public water supply systems are strictly prohibited." | 19-11.2(b) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Union | Clark | Township | 3403913150 | Permit |  |  | Chapter 122 establishes permit fees that apply to items requiring permits, including a geothermal-specific electrical fee entry: under Electrical § 122-2B(9)(j), 'Geothermal, kw range of 3.8 to 19.2; heat pump, 2.6 kw to 7.4 kw: $40.' The chapter also states in § 122-2G(1)(a): 'Any item required to have a permit not listed in fees: All subcodes: $125.' | § 122-2 Fees; G. Minimum fee | 2025 | https://ecode360.com/13977161
New Jersey | Union | Rahway | City | 3403961530 | Permit |  |  | "Plan review. The fee for plan review shall be 25% of the amount to be charged for the construction permit..." and "For complete installation, replacement or conversion of heating ventilation/air-conditioning equipment, boilers and furnaces: $75." The chapter also lists electrical fees and includes an average field rating entry for "Geothermal: kw range of 3.8 to 19.2; and heat pump, 2.6 to 7.4 kw." | § 177-3 Fees | 2026 | https://ecode360.com/9583051
New Mexico | Eddy | Carlsbad | City | 3512150 | Definition: Geothermal Heat Pump |  |  | "Geothermal energy system. A geothermal energy collection and conversion device that produces electricity or other form of energy primarily used for heating/cooling." | SEC. 56-31. DEFINITIONS. | 2017 | https://irp.cdn-website.com/f12fb9e8/files/uploaded/Chapter-56-Zoning-Ordinance-2017.pdf
New York | Broome | Binghamton | Town | 3600706618 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY - Thermal energy generated and stored in the Earth" | SECTION III. DEFINITIONS | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Definition: Geothermal Heat Pump |  |  | "There are several types of geothermal systems, also known as 'ground source heating pumps'. They include closed loop, open loop, and direct exchange systems and are distinguished by the type of ground heat exchange (GHX) installed in the earth for heat transfer." | Part IV, A. Permitting Geothermal Systems | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal energy systems shall be located a minimum distance of 25 feet from any property line." | Part IV, B.4(b) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Building Foundation | 10 | feet | "All geothermal energy systems shall be located a minimum distance of... Ten feet from any building foundation." | Part IV, B.4(d)(ii) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Wastewater | 100 | feet | "All geothermal energy systems shall be located a minimum distance of... Seventy-five feet from any sewage disposal structure, such as a septic tank or cesspool or leaching field, except a supply well in an open loop system shall be a minimum of one hundred feet from such sewage disposal structure." | Part IV, B.4(d)(v) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Public Water | 100 | feet | "All geothermal energy systems shall be located a minimum distance of... One hundred feet from potable water wells" | Part IV, B.4(d)(vi) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Fuel (below ground) | 25 | feet | "All geothermal energy systems shall be located a minimum distance of... Twenty-five feet from any potential source of contamination, such as underground fuel tanks, except a supply well in an open loop system shall be a minimum of 50 feet from such potential source of contamination." | Part IV, B.4(d)(iii) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Water Lines | 10 | feet | "All geothermal energy systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | Part IV, B.4(d)(i) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Sewer Lines | 10 | feet | "All geothermal energy systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | Part IV, B.4(d)(i) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Setback - Water Bodies | 100 | feet | Permitted geothermal systems must be those that are "not proposed to be located within" a "Freshwater wetland or within 100 feet landward of the aforementioned" and a "Regulated freshwater surface water body." | Part IV, A.5(f)(ii)-(iii) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Maximum Well Depth | 20 | feet | "All horizontal closed-loop systems shall be no more than 20 feet deep." This depth limit is repeated in the setbacks section: "All horizontal closed-loop systems shall be no more than 20 feet deep." | Part IV, B.2(b)(v); B.4(a) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Permit |  |  | "Geothermal energy systems shall be permitted, installed, and erected within the Town pursuant to a building permit... no building permit shall be issued to construct a geothermal energy system until all other applicable permits have been secured." Also, "All permit applications shall be submitted to the Code Enforcement Officer on forms it provides." | Part IV, A.4; Part IV, B.1 | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Inspection |  |  | The ordinance requires "on or before final inspection, certification by the design engineer and/or installer that the geothermal system was installed as designed" and states that "The individual piping loops and circuits, and fully constructed piping network for all geothermal systems shall be pressure tested for integrity of original material and joints prior to backfill." | Part IV, B.1(d); B.2(a)(i)1 | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Certification |  |  | Permit applications must include "Certification by the design engineer and/or installer that the geothermal system complies with all applicable regulations" and, before final inspection, "certification by the design engineer and/or installer that the geothermal system was installed as designed." Applications also require "an engineering analysis... certified by a licensed professional engineer." For closed-loop systems, "Closed loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer," and borefields over 50 tons "must be designed by an IGSHPA certified geothermal designer." For open loop systems, contractors "must be registered with the NYSDEC." For DX systems, contractors must show they "completed a DX system installers training course and are certified by an applicable equipment and material manufacturer." | Part IV, B.1(c)-(d), (f); B.2(b)(i)-(ii); B.2(c)(i); B.2(d)(i) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned... The owner shall remove the abandoned system at his/her expense... after obtaining a demolition permit." "Closed loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends." "Open loop wells shall be decommissioned per NYSDEC requirements." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout..." and "Water body geothermal systems shall be completely removed from the bottom of the body of water." | Part IV, B.5 | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | Town | 3600706618 | Other Prohibitions/Regulations |  |  | Permitted geothermal systems must be those that are "not proposed to be located within" specified sensitive areas, including "Freshwater wetland or within 100 feet landward," "Regulated freshwater surface water body," "Coastal erosion hazard areas," "Historic... resources," "Identified wellhead protection areas and aquifer protection districts," and "Lake Protection Overlay District." The ordinance also states: "Discharge of water from open loop systems into storm or sanitary sewer systems shall be prohibited, except upon written approval..."; "Discharge of water from open loop systems into a waterway or freshwater wetland is not allowed unless approved..."; and "The use of open loop systems within identified wellhead protection areas is prohibited." | Part IV, A.5(f); B.2(c)(vii)1-2, (x) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Clinton | Plattsburgh | Town | 3601958585 | Screening |  |  | Section 5.2 G.1: "At-grade electrical transformers and HVAC equipment shall be screened from public view by a solid visual barrier." Section 5.2 G.2: "To the maximum extent practical, all roof-mounted and ground-mounted mechanical equipment shall be screened from view or isolated so as not to be visible from any public right-of-way or residential district within 150 feet of the subject lot... Roof screens, when used, shall be coordinated with the building to maintain a unified appearance." Section 5.14 D.6.a-b: "All off-street loading, service, dumpster or mechanical equipment areas shall be located in the rear or side of the building and screened from view from the public right-of-way... Dumpster areas and mechanical equipment shall be screened from view by a wall of landscaping or screening walls on at least three sides which is equal or more in height to the equipment being screened." Section 5.14 D.8.b: "Mechanical equipment such as HVAC heating and cooling installed on rooftops shall be fully screened from view from adjacent public right of ways, properties and pedestrian walkways with the use of parapets or sloped parapet roof designs." Section 5.14 E.1.d(1): "Rooftop mechanical equipment... should be screened so as to not be visible from public view from adjoining roadways. Screening should consist of architecturally compatible materials, parapets, sloped roof form or walls that are at least as high as the equipment being screened." | Section 5.2 G. Mechanical equipment; Section 5.14 D.6 Equipment Screening; Section 5.14 D.8.b Roof-Mounted Mechanical Equipment; Section 5.14 E.1.d Specialty equipment |  | https://www.townofplattsburghny.gov/wp-content/uploads/2026/04/2026-Zoning-Ordinance.pdf
New York | Dutchess | Rhinebeck | Town | 3602761357 | Permit |  |  | "All other uses and activities that are permitted in the applicable underlying zoning district shall be permitted in the aquifer protection area, provided that a special use permit is issued by the Planning Board..." and "Each application submitted to the Town for the establishment of a use or the development of land and/or buildings and structures within the aquifer protection area shall include identification of any necessary federal, state or county permits, copies of all such permit applications and copies of all related correspondence between the applicant and the permitting agency or agencies." Also, for open-loop geothermal wells: "Open-loop geothermal wells shall be in compliance with the New York State DEC's requirements governing injection wells and/or the United States EPA's Class V well injection program requirements found in 40 CFR Part 146, Underground Injection Control Program: Criteria and Standards." | § 125-54(D)(2) and § 125-54(D)(3) | 2019 | https://ecode360.com/14083825
New York | Dutchess | Rhinebeck | Town | 3602761357 | Decommissioning |  |  | "Any well that is abandoned, meaning that its use has been permanently discontinued, or which is in a state of disrepair such that it cannot be used for its intended purpose or for observation purposes, shall be sealed in accordance with the requirements of the Dutchess County Department of Health." | § 125-54(D)(1)(q) | 2019 | https://ecode360.com/14083825
New York | Jefferson | Henderson | Town | 3604534055 | Definition: Geothermal Heat Pump |  |  | "The following are accessory uses and structures that are permitted in all zoning districts and to any lot size without the need of review by the planning board: ... wells for heat pumps ..." | SCEDULE II Permitted Principal, Permitted Accessory & Special Uses | 2019 | https://www.townofhendersonny.org/uploads/6/0/3/1/60311435/zoning_laws_2020.pdf
New York | Jefferson | Le Ray | Town | 3604542015 | Setback - Yards | 10 | feet | "All components of geothermal energy systems, including pumps, borings and loops, shall be set back at least five feet from side lot lines and at least 10 feet from rear lot lines." | § 158-128B(1) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Setback - Building Foundation | 10 | feet | "All borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off site." | § 158-128B(2) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Noise Limits | 50 | dBA | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less." | § 158-128B(5) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Permit |  |  | "A building permit shall be obtained from the Jefferson County Fire Prevention and Building Codes Department for any geothermal energy system prior to installation." "Borings for vertical systems are subject to any and all required approvals and permits from the NYSDEC Division of Waters the New York State Department of Health." | § 158-128E Permits | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less." "In addition to screening for noise control, geothermal energy systems are considered mechanical equipment and are subject to screening by landscaping, fencing or other methods to enhance the view." | § 158-128B(5) and (6) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Certification |  |  | "Geothermal energy systems shall be certified by Underwriters' Laboratories, Inc., and shall meet the requirements of the New York State Building Code as adopted by the Town of LeRay." | § 158-128C Standards and certifications | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance." "Upon notice to the owner by the Zoning Enforcement Officer, within 180 days the owner shall remove the abandoned system at his/her expense..." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." "Geothermal energy systems shall be completely removed from the bottom of any water body." | § 158-128D Abandonment | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems utilizing heat transfer fluids as defined in Article I are permitted. Open-loop geothermal energy systems are not permitted." | § 158-128A(1) Applicability | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | Town | 3604542015 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems in water bodies owned or managed by the Town of LeRay are not permitted." | § 158-128A(3) Applicability | 2021 | https://ecode360.com/29145485
New York | Jefferson | Watertown | Town | 3604578619 | Other Prohibitions/Regulations |  |  | "Equipment, piping, and all other devices shall not be located in any easement or right-of-way." | Sec. 310-56 Geothermal Energy Systems | 2023 | https://www.watertown-ny.gov/media/PlanningZoning/Zoning%20Ordinance/2023%20Feb%20FINAL_Full%20Ordinance_small.pdf
New York | Jefferson | Wilna | Town | 3604582348 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEMS Are a system of ground-source heat pumps that can also be designed as direct exchange systems, which circulate a refrigerant through a copper pipe instead of a typical ground loop. Direct exchange systems are highly efficient at heat extraction and rejection." | ARTICLE III DEFINITIONS | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Setback - Property Lines | 10 | feet | "All components of geothermal energy systems, including pumps, borings and loops, shall be set back at least five feet from side lot lines and at least 10 feet from rear lot lines." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Setback - Building Foundation | 10 | feet | "All borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off site." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Noise Limits | 50 | dBA | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Permit |  |  | "A building permit shall be obtained from the Town of Wilna Code Enforcement Officer." Also, "Borings for vertical systems are subject to any and all required approvals and permits from the NYSDEC Division of Water and the New York State Department of Health." | Section 740 Energy Systems, A. Geothermal energy systems, 5. Permits | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts." Also, "In addition to screening for noise control, geothermal energy systems are considered mechanical equipment and are subject to screening by landscaping, fencing or other methods to enhance the view." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Certification |  |  | "Geothermal energy systems shall be certified by Underwriters' Laboratories, Inc., and shall meet the requirements of the New York State Building Code as adopted by the Town of Wilna." | Section 740 Energy Systems, A. Geothermal energy systems, 3. Standards and certifications | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance." "Upon notice to the owner by the Zoning Enforcement Officer, within 180 days the owner shall remove the abandoned system at his/her expense after a hearing by the Wilna Town Board." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." "Geothermal energy systems shall be completely removed from the bottom of any water body." | Section 740 Energy Systems, A. Geothermal energy systems, 4. Abandonment | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems utilizing heat transfer fluids as defined in Article I arc permitted. Open-loop geothermal energy systems are not permitted." | Section 740 Energy Systems, A. Geothermal energy systems, 1. Applicability | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | Town | 3604582348 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems in water bodies owned or managed by the Town of Wilna are not permitted." | Section 740 Energy Systems, A. Geothermal energy systems, 1. Applicability | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Lewis | Croghan | Town | 3604919081 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL CLOSED-LOOP SYSTEM: Closed-loop systems use a ground loop (typically made of polyethylene or PVC piping) that circulates water or antifreeze to exchange heat with the ground or a groundwater source..."; "GEOTHERMAL ENERGY SYSTEMS: Are a system of ground-source heat pumps that can also be designed as direct exchange systems, which circulate a refrigerant through a copper pipe instead of a typical ground loop."; "GEOTHERMAL OPEN-LOOP SYSTEM: Open-loop systems circulate water for heat extraction and rejection directly from local groundwater sources." | ARTICLE III. DEFINITIONS | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Setback - Property Lines | 10 | feet | "All components of geothermal energy systems, including pumps, borings and loops, shall be set back at least five feet from side lot lines and at least 10 feet from rear lot lines." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Setback - Building Foundation | 10 | feet | "All borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off site." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Noise Limits | 50 | dBA | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Permit |  |  | "A building permit shall be obtained from the Lewis County Code Enforcement Officer."; "Borings for vertical systems are subject to any and all required approvals and permits from the NYSDEC Division of Water and the New York State Department of Health." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts."; "In addition to screening for noise control, geothermal energy systems are considered mechanical equipment and are subject to screening by landscaping, fencing or other methods to enhance the view." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Certification |  |  | "Geothermal energy systems shall be certified by Underwriters' Laboratories, Inc., and shall meet the requirements of the New York State Building Code as adopted by the Town of Croghan." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance." "Upon notice to the owner by the Zoning Enforcement Officer, within 180 days the owner shall remove the abandoned system at his/her expense after a hearing by the Croghan Town Board" including: "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted"; and "Geothermal energy systems shall be completely removed from the bottom of any water body." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems utilizing heat transfer fluids as defined in Article XII are permitted. Open-loop geothermal energy systems are not permitted." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | Town | 3604919081 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems in water bodies owned or managed by the Town of Croghan are not permitted unless municipally owned/operated." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Monroe | Penfield | Town | 3605557144 | Definition: Geothermal |  |  | "GEOTHERMAL, HEAT TRANSFER FLUID — Nontoxic, food-grade or United States Pharmacopeia (USP)-grade fluids of potable water or aqueous solution of propylene glycol not to exceed 25% by weight." | Section 3. Amendment to Section 250-2.2 Terms Defined | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — A system that harnesses the relatively constant temperature of the earth or a body of water to provide space heating and/or cooling. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | Section 3. Amendment to Section 250-2.2 Terms Defined | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Setback - Building Foundation | 10 | feet | "All vertical borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off-site." | D. Geothermal Energy Systems (GES) - General Requirements | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Maximum Well Depth | 150 | feet | "All vertical boring shall be limited to a depth of 150 feet from the surface elevation." | D. Geothermal Energy Systems (GES) - General Requirements | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Permit |  |  | "Borings for vertical systems are subject to any and all required approvals and permits from the NYS Department of Environmental Conservation, NYS Department of Health, and any other applicable state or federal agencies." Also, "When a GES is included as part of a proposed development that requires a site plan or the GES' area of disturbance triggers site plan approval set forth in 250, Planning Board review and approval shall be required." | D. Geothermal Energy Systems (GES) - Additional Permitting Required | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels..." Also, "GES equipment outside of structures should be located and/or screened in a way that minimizes views of the equipment." | D. Geothermal Energy Systems (GES) - General Requirements; Site Plan Application Required | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Decommissioning |  |  | "If a GES remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and the following decommissioning actions are required. [1] The heat pump and any external mechanical equipment shall be removed. [2] Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil, or boring shall be uncovered and grouted. [3] All GES components shall be completely removed from any water body." | D. Geothermal Energy Systems (GES) - Abandonment | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | Town | 3605557144 | Open-loop Prohibitions |  |  | "Only Closed-loop GES that utilize heat transfer fluids as defined in 250-2.2 are permitted. Open-loop GES, as defined in 250-2.2, are not permitted." | D. Geothermal Energy Systems (GES) - Applicability | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Perinton | Town | 3605557221 | Setback - Property Lines | 5 | feet | "All ground-mounted exterior mechanical devices, such as air conditioners, heat pumps, and generators, must be located in a side or rear yard, no closer than five feet from a property line." | § 208-14M(2)(a) | 2024 | https://ecode360.com/6741309
New York | Monroe | Perinton | Town | 3605557221 | Screening |  |  | "All ground-mounted exterior mechanical devices, such as commercial refuse containers, ventilating and air-conditioning units (except window and wall units), shall be enclosed and/or screened." | § 208-14M(1)(a) | 2024 | https://ecode360.com/6741309
New York | Monroe | Pittsford | Town | 3605558365 | Definition: Geothermal Heat Pump |  |  | "Geothermal system for heating and or cooling. Subject to § 185-113C(4)." | § 185-113A(19) Accessory uses and structures |  | https://ecode360.com/48538733
New York | Monroe | Pittsford | Town | 3605558365 | Setback - Property Lines | 10 | feet | "All accessory uses and structures shall follow the primary structure minimum setback requirements of the zoning district in which it is located, with the following exceptions: ... (c) Geothermal systems must maintain a minimum setback of 10 feet from all property lines." | § 185-113C(4)(c) Size and location restrictions |  | https://ecode360.com/48538733
New York | Niagara | Royalton | Town | 3606364034 | Definition: Geothermal Heat Pump |  |  | "ALTERNATE ENERGY SYSTEMS: Structures, equipment, devices or construction techniques used for the production of heat, light, cooling, electricity or other forms of energy on a site and may be attached to or separate from the principal structure. Current examples include windmills, solar collectors, solar greenhouses, heat pumps or other related devices. For the purposes of this Local Law, this definition shall apply to individual residences or businesses; commercial generating plants are excluded." | Section 210 Definitions | 2008 | https://www.niagaracountybusiness.com/file-library/100219/town_royalton_zoning_ordinance.pdf
New York | Oneida | Utica | City | 3606576540 | Inspection |  |  | "The systems shall be tested hydrostatically at 1 1/2 times the maximum system design pressure, but not less than 100 psi. The duration of each test shall not be less than 15 minutes. All geothermal systems must be pressure checked to the original standard by a licensed geothermal contractor every three years from the certification system date. Results from the test shall be submitted to the Building Department. No person shall operate a system if a test reveals that it is likely to leak the heat transfer liquid." | Sec. 2-29-350(c)(2) Geothermal energy systems | 2024 | https://ecode360.com/14017100
New York | Oneida | Utica | City | 3606576540 | Certification |  |  | "Applicant shall submit a certificate of compliance demonstrating that the proposed system has been tested and approved by Underwriters Laboratories (UL) or other approved independent testing agency." | Sec. 2-29-350(c)(1) Geothermal energy systems | 2024 | https://ecode360.com/14017100
New York | Oneida | Utica | City | 3606576540 | Open-loop Prohibitions |  |  | "Open loop geothermal systems. No person shall install or maintain an open loop geothermal system within the City." | Sec. 2-29-350 Geothermal energy systems | 2024 | https://ecode360.com/14017100
New York | Orleans | Yates | Town | 3607383448 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEMS: Structures, equipment, devices or construction techniques used for the production of heat, light, cooling, electricity or other forms of energy on site and may be attached to or separate from the principal structure. Current examples include windmills, solar collectors and solar greenhouses, heat pumps, or other related devices. For the purposes of this Local Law, this definition shall apply to individual residences and businesses. Commercial generating plants, the prime function of which is selling energy, are excluded." | SECTION 210 DEFINITIONS | 2016 | https://www.townofyates.org/Forms/Yates%20Zoning%20Book%20Revised.pdf
New York | Orleans | Yates | Town | 3607383448 | Permit |  |  | "No building or structure shall be erected, enlarged, structurally altered or moved, no new use shall be established, and no building permit shall be granted pursuant to the Codes of New York State, until a zoning permit therefore has been issued by the Zoning Officer." | SECTION 300 PERMITS REQUIRED | 2016 | https://www.townofyates.org/Forms/Yates%20Zoning%20Book%20Revised.pdf
New York | Orleans | Yates | Town | 3607383448 | Inspection |  |  | "The applicant shall notify the Zoning Enforcement Officer when the structure or use is ready for final inspection. The Zoning Enforcement Officer shall then make a final inspection. If satisfied that the regulations pertaining to the project have been complied with and that the project has been completed as specified on the approved application, the Zoning Enforcement Officer shall issue a certificate of Zoning Compliance granting permission to occupy or use the structure." | SECTION 306 CERTIFICATE OF ZONING COMPLIANCE | 2016 | https://www.townofyates.org/Forms/Yates%20Zoning%20Book%20Revised.pdf
New York | Saratoga | Ballston | Town | 3609104220 | Definition: Geothermal |  |  | "There are several types of Geothermal Systems, also known as Ground Source Heat Pumps. They include Closed Loop, Open Loop, and Direct Exchange systems and are distinguished by the type of Ground Heat Exchanger (GHX) installed in the earth for heat transfer." | § 57-1(B) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Definition: Geothermal Heat Pump |  |  | "There are several types of Geothermal Systems, also known as Ground Source Heat Pumps. They include Closed Loop, Open Loop, and Direct Exchange systems and are distinguished by the type of Ground Heat Exchanger (GHX) installed in the earth for heat transfer." | § 57-1(B) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Property Lines | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Property line" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Building Foundation | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Building foundation" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Wastewater | 75 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Sewage disposal structure, e.g., septic tank, cesspool" requires: Closed Loop and DX Systems: "25"; Open Loop Supply Well <45 gpm: "50"; Open Loop Supply Well >45 gpm: "75"; Open Loop Return Well <45 gpm: "25"; Open Loop Return Well >45 gpm: "50." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Private Water | 100 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Private water supply well" requires: Closed Loop and DX Systems: "25"; Open Loop Supply Well <45 gpm: "25"; Open Loop Supply Well >45 gpm: "50"; Open Loop Return Well <45 gpm: "50"; Open Loop Return Well >45 gpm: "100." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Public Water | 200 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Public water supply well" requires: Closed Loop and DX Systems: "100"; Open Loop Supply Well <45 gpm: "100"; Open Loop Supply Well >45 gpm: "100"; Open Loop Return Well <45 gpm: "200"; Open Loop Return Well >45 gpm: "200." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Water Lines | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "On-site utility, sewage and water line, lined catch basin" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Sewer Lines | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "On-site utility, sewage and water line, lined catch basin" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Setback - Hazardous Materials/Fertilizers | 50 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Potential source of contamination, e.g. underground petroleum storage tank, chemical use and waste storage area, etc." requires: Closed Loop and DX Systems: "25"; Open Loop Supply Well <45 gpm: "25"; Open Loop Supply Well >45 gpm: "50"; Open Loop Return Well <45 gpm: "25"; Open Loop Return Well >45 gpm: "25." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Minimum Well Depth | 20 | feet | "An open loop system where the depth to groundwater is at least 20 feet below the surface." | § 57-2(B)(3) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Permit |  |  | "Geothermal systems may be permitted, installed, and erected pursuant to a building permit" and "Permit applications shall be submitted to the Building Department on forms it provides." | § 57-2(A); § 57-3(A) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Inspection |  |  | "The individual piping loops, circuits, and fully constructed piping network for all Geothermal Systems shall be pressure tested for integrity of original material and joints prior to backfill in accordance with the manufacturer's instructions and the governing standards or guidelines." | § 57-3(A)(2)(a)[1] | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Licensed Driller |  |  | "Open Loop system contractors must be registered by NYSDEC for drilling and installing wells and installing and start-up of submersible pumps." | § 57-3(A)(2)(c)(1) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Certification |  |  | "Certification of (1) through (5) above must be performed by a licensed Professional Engineer." "Closed Loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques." "Closed Loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA Certified Geothermal Designer in good standing with IGSHPA." "DX system contractors shall demonstrate they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | § 57-3(A)(1)(a)[6]; § 57-3(A)(2)(b)(1)-(2); § 57-3(A)(2)(d)(1) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Decommissioning |  |  | "If the Geothermal System remains nonfunctional or inoperative for a continuous period of one year, the Building Inspector may require that the buried ground heat exchanger be taken out of service by the property owner." "Closed Loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends. If the heat transfer fluid contains regulated materials (e.g., antifreeze, biocides, or corrosion inhibitors), the heat transfer fluid shall be contained and disposed of in accordance with applicable regulations." "Open Loop wells shall be decommissioned per NYSDEC requirements." | § 57-3(C) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | Town | 3609104220 | Other Prohibitions/Regulations |  |  | Geothermal systems eligible for a building permit must satisfy the criterion that the system "Is not proposed to be located within the following areas of potential sensitivity:" "100-year flood hazard zones considered V or AE zone on the FEMA Flood Maps," "Tidal or freshwater wetland," "Regulated tidal or freshwater surface water body," and "Coastal erosion hazard area." | § 57-2(B)(7); § 57-2(C) | 2025 | https://ecode360.com/49590886
New York | Seneca | Fayette | Town | 3609925505 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEMS: Structures, equipment, devices, or construction techniques used for the production of heat, light, cooling, electricity, or other forms of energy on site and may be attached to or separate from the principal structure. Current examples include wind turbines, solar collectors and solar greenhouses, heat pumps, wind-powered air compressors, or other related devices." | SECTION 210 DEFINITIONS | 2018 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B95110B70-ABD5-4ECC-BD43-A56D00C37638%7D
New York | Seneca | Fayette | Town | 3609925505 | Permit |  |  | "No building or structure shall be erected, enlarged, structurally altered or moved, no new use shall be established, and no building permit shall be issued ... until a land use permit therefore has been issued by the Land Use Officer. No alterations to an existing building shall be made without a land use permit, unless pursuant to the New York State Uniform Fire Prevention and Building Code such alterations do not require a building permit." | SECTION 301 PERMITS REQUIRED | 2018 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B95110B70-ABD5-4ECC-BD43-A56D00C37638%7D
New York | Seneca | Fayette | Town | 3609925505 | Inspection |  |  | "The applicant shall notify the Land Use Officer when the structure and/or land use is ready for final inspection. The Land Use Officer shall then make a final inspection. If satisfied that the standards, conditions and regulations pertaining to the project have been complied with ... the Land Use Officer shall issue a certificate of compliance..." | SECTION 307 CERTIFICATE OF COMPLIANCE | 2018 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B95110B70-ABD5-4ECC-BD43-A56D00C37638%7D
New York | Suffolk | Brookhaven | Town | 3610310000 | Definition: Geothermal Heat Pump |  |  | "There are several types of geothermal systems, also known as 'ground source heating pumps,' typically used on Long Island for space heating and cooling. They include closed loop, open loop, and direct exchange systems and are distinguished by the type of ground heat exchange (GHX) installed in the earth for heat transfer." | § 85-808B | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 25 feet from any property line." | § 85-810D(2) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Setback - Building Foundation | 10 | feet | "All geothermal systems shall be located a minimum distance of... Ten feet from any building foundation." | § 85-810D(4)(b) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Setback - Wastewater | 75 | feet | "All geothermal systems shall be located a minimum distance of... Fifty feet from any sewage disposal structure, such as a septic tank or cesspool or leaching field, except a supply well in an open loop system shall be a minimum of 75 feet from such sewage disposal structure." | § 85-810D(4)(e) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Setback - Fuel (below ground) | 25 | feet | "All geothermal systems shall be located a minimum distance of... Twenty-five feet from any potential source of contamination, such as underground fuel tanks, except a supply well in an open loop system shall be a minimum of 50 feet from such potential source of contamination." | § 85-810D(4)(c) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Setback - Water Lines | 10 | feet | "All geothermal systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | § 85-810D(4)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Setback - Sewer Lines | 10 | feet | "All geothermal systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | § 85-810D(4)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Maximum Well Depth | 20 | feet | "All horizontal closed-loop systems shall be no more than 20 feet deep." The same limit is repeated in setbacks: "All horizontal closed-loop systems shall be no more than 20 feet deep." | § 85-810B(2)(f); § 85-810D(1) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Permit |  |  | "Geothermal energy systems shall be permitted, installed, and erected within the Town pursuant to a building permit so long as they meet the provisions of this article and all applicable sections of the Town Code. Further, no building permit shall be issued to construct a geothermal energy system until all other applicable permits have been secured." Also, "Geothermal energy systems shall be constructed pursuant to a building permit so long as the geothermal energy system meets the criteria set forth in § 85-810, subject to obtaining all other necessary approvals." | § 85-808E; § 85-809A | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Inspection |  |  | "Subsequent to installation and on or before final inspection, certification by the design engineer and/or installer that the geothermal system was installed as designed..." and "The individual piping loops and circuits, and fully constructed piping network for all geothermal systems shall be pressure tested for integrity of original material and joints prior to backfill..." | § 85-810A(4); § 85-810B(1)(a)[1] | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Licensed Driller |  |  | "Open loop system contractors must be registered with the NYSDEC for drilling and installing wells and installing and start-up of submersible pumps..." | § 85-810B(3)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Certification |  |  | "Closed loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques..."; "Closed loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA certified geothermal designer in good standing with the IGSHPA."; "DX system contractors shall demonstrate that they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | § 85-810B(2)(a); § 85-810B(2)(b); § 85-810B(4)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned... The owner shall remove the abandoned system at his/her expense... after obtaining a demolition permit." "Closed loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends." "Open loop wells shall be decommissioned per NYSDEC requirements." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid..." | § 85-811 | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | Town | 3610310000 | Open-loop Prohibitions |  |  | "The use of open loop systems within identified wellhead protection areas is prohibited." | § 85-810B(3)(j) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Shelter Island | Town | 3610366839 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A geothermal system uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings. It shall include both open-loop geothermal and closed-loop geothermal systems." | § 74-4 Definitions | 2009 | https://ecode360.com/13841397
New York | Suffolk | Shelter Island | Town | 3610366839 | Decommissioning |  |  | "Any person... who installs such a geothermal system in violation of this prohibition shall immediately remove the system and be liable for a penalty of $1,000 per day until such system is removed." | § 74-6 Penalties for offenses | 2009 | https://ecode360.com/13841397
New York | Suffolk | Shelter Island | Town | 3610366839 | Closed-loop Prohibitions |  |  | "The installation of a geothermal system is prohibited in the Town of Shelter Island." Section 74-4 defines "GEOTHERMAL SYSTEM" to "include both open-loop geothermal and closed-loop geothermal systems." | § 74-5 Installation prohibited | 2009 | https://ecode360.com/13841397
New York | Suffolk | Shelter Island | Town | 3610366839 | Open-loop Prohibitions |  |  | "The installation of a geothermal system is prohibited in the Town of Shelter Island." Section 74-4 defines "GEOTHERMAL SYSTEM" to "include both open-loop geothermal and closed-loop geothermal systems." | § 74-5 Installation prohibited | 2009 | https://ecode360.com/13841397
New York | Suffolk | Smithtown | Town | 3610368000 | Definition: Geothermal Heat Pump |  |  | "There are several types of geothermal systems, also known as 'ground source heat pumps,' typically used on Long Island for space heating and cooling. They include: closed loop, open loop, and direct exchange systems and are distinguished by the type of ground heat exchanger (GHX) installed in the earth for heat transfer." | § 112-1.4A(2) | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Property Lines | 10 | feet | The setbacks table lists "Property line" with a separation distance of 10 feet across the geothermal system categories shown. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Building Foundation | 10 | feet | The setbacks table lists "Building foundation" with a separation distance of 10 feet for the geothermal system categories shown. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Wastewater | 75 | feet | The setbacks table includes "Sewage disposal structure, e.g., septic tank, cesspool" with values of 25 feet for several system categories, 50 feet for one >45 gpm category, and 75 feet for an open-loop category. It also includes "Stormwater recharge structure, e.g., leach field, unlined catch basin" with values up to 50 feet. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Private Water | 100 | feet | The setbacks table lists "Private water supply well" with distances of 25 feet for closed loop and DX systems, 50 feet for some open-loop categories, and 100 feet for the most restrictive open-loop category (>45 gpm return well). | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Public Water | 200 | feet | The setbacks table lists "Public water supply well" with distances of 100 feet for closed loop and DX systems and for some open-loop categories, and 200 feet for the more restrictive open-loop categories (>45 gpm). | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Water Lines | 10 | feet | The setbacks table lists "On-site utility, sewage and water line, lined catch basin" with a separation distance of 10 feet across all shown geothermal system categories. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Sewer Lines | 10 | feet | The setbacks table lists "On-site utility, sewage and water line, lined catch basin" with a separation distance of 10 feet across all shown geothermal system categories. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Setback - Hazardous Materials/Fertilizers | 50 | feet | The setbacks table lists "Potential source of contamination; e.g., underground petroleum storage tank, chemical use and waste storage area, etc." with values of 25 feet in several categories and 50 feet in some open-loop categories. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Permit |  |  | "Geothermal systems may be permitted, installed, and erected pursuant to a building permit" and "Permit applications shall be submitted to the Building Department on forms it provides" with required materials including a plot plan, engineer/installer certifications, and for open loop systems a one-line electrical diagram. | § 112-1.4B(1); § 112-1.4C(1)(a) | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Inspection |  |  | "The individual piping loops, circuits, and fully constructed piping network for all geothermal systems shall be pressure tested for integrity of original material and joints prior to backfill in accordance with the manufacturer’s instructions and the governing standards or guidelines." | § 112-1.4C(1)(b)[1][a] | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Licensed Driller |  |  | "Open loop system contractors must be registered by NYSDEC for drilling and installing wells and installing and start-up of submersible pumps." | § 112-1.4C(1)(b)[3][a] | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Certification |  |  | "Certification of Subsection C(1)(a)[1] through [5] above must be performed by a licensed professional engineer." "Closed loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques." "Closed loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA certified geothermal designer in good standing with IGSHPA." "DX system contractors shall demonstrate they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | § 112-1.4C(1)(a)[6]; § 112-1.4C(1)(b)[2]-[4] | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the Chief Building Inspector may require that the buried ground heat exchanger be taken out of service by the property owner." "Closed loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends." "Open loop wells shall be decommissioned per NYSDEC requirements." | § 112-1.4C(3) | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | Town | 3610368000 | Other Prohibitions/Regulations |  |  | "Discharge of water from open loop systems into storm or sanitary sewer systems shall be prohibited, except upon written approval by the SCDHS, NYSDEC, or other authority having jurisdiction." "Discharge of water from open loop systems into a waterway or tidal or freshwater wetland is not allowed unless approved by applicable federal, state, and local authorities." | § 112-1.4C(1)(b)[3][g][i]-[ii] | 2026 | https://ecode360.com/15097677
New York | Sullivan | Cochecton | Town | 3610516661 | Definition: Geothermal Heat Pump |  |  | "Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. A geothermal energy system consists of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump." | § 240-25 Renewable energy systems, B. Special definitions | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | Town | 3610516661 | Setback - Property Lines | 5 | feet | "Renewable energy systems are not permitted within 10 feet of any property line or 35 feet of the front lot line, except for underground systems, which may extend to within five feet of a property line..." Geothermal systems are included within renewable energy systems, and underground systems receive the specific 5-foot property-line setback. | § 240-25 Renewable energy systems, C(4) Setbacks | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | Town | 3610516661 | Setback - Yards | 35 | feet | "Renewable energy systems are not permitted within 10 feet of any property line or 35 feet of the front lot line, except for underground systems, which may extend to within five feet of a property line..." | § 240-25 Renewable energy systems, C(4) Setbacks | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | Town | 3610516661 | Permit |  |  | "Building permits shall be required for all renewable energy system installations as defined herein." | § 240-25 Renewable energy systems, C(6) Permit requirements | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | Town | 3610516661 | Inspection |  |  | "All renewable energy systems must be inspected and approved by a qualified third-party electrical inspector approved by the Town of Cochecton and, if connected to the local electric utility transmission grid, approved by the appropriate utility." | § 240-25 Renewable energy systems, C(2) Qualified installations | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | Town | 3610516661 | Other Prohibitions/Regulations |  |  | "No part of any such system shall be located within public rights-of-way." "...no portion of a geothermal system shall be located within a stream or the Upper Delaware River." "Vertical or deep-bore geothermal systems are not permitted within [designated water well protection] zones." | § 240-25 Renewable energy systems, D(1)-(2) Geothermal energy system standards | 2018 | https://ecode360.com/26992708
New York | Sullivan | Lumberland | Town | 3610543786 | Setback - Roads | 10 | feet | "All components of a closed-loop ground-source heat pump system, including pumps, borings and loops, shall be set back at least five feet from interior side lot lines and at least 10 feet from front and rear lot lines." Read together with § 250-38B(4): aboveground equipment "shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way." | § 250-38B(3) Location of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | Town | 3610543786 | Setback - Property Lines | 10 | feet | "All components of a closed-loop ground-source heat pump system, including pumps, borings and loops, shall be set back at least five feet from interior side lot lines and at least 10 feet from front and rear lot lines." | § 250-38B(3) Location of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | Town | 3610543786 | Setback - Yards | 10 | feet | "All components of a closed-loop ground-source heat pump system, including pumps, borings and loops, shall be set back at least five feet from interior side lot lines and at least 10 feet from front and rear lot lines." In addition, "Aboveground equipment associated with a closed-loop ground-source heat pump system shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way..." | § 250-38B(3)-(4) Location of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | Town | 3610543786 | Permit |  |  | "Closed-loop ground-source heat pump systems using a nontoxic and food-grade fluid as a heat transfer fluid are permitted in all districts. Installation of a closed-loop ground-source heat pump system requires a building permit." | § 250-38A(1) Site plan approval required | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | Town | 3610543786 | Decommissioning |  |  | "If a closed-loop ground-source heat pump system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove such system..." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed"; "Pipes and coils below the land surface shall be filled with grout to displace the heat transfer fluid..."; and "Pond and similar ground-source heat pump systems shall be completely removed from the body of water." | § 250-38C Abandonment and removal of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | Town | 3610543786 | Open-loop Prohibitions |  |  | "Open-loop ground-source heat pump systems... are prohibited in every district within the Town." | § 250-38A(2) Site plan approval required | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | Town | 3610543786 | Other Prohibitions/Regulations |  |  | "...closed-loop ground-source heat pump systems utilizing a heat transfer fluid that is not a nontoxic and food- grade liquid are prohibited in every district within the Town." | § 250-38A(2) Site plan approval required | 2016 | https://ecode360.com/26934437
New York | Ulster | Denning | Town | 3611120247 | Other Prohibitions/Regulations |  |  | "Restrictions: Geothermal Systems are permitted as long as it does not interfere with the groundwater aquifer and does not affect or contaminate the groundwater of surrounding properties." | §510 - GEOTHERMAL SYSTEMS | 2019 | https://www.denningny.gov/wp-content/uploads/2023/05/TOD-ZONING-LAW-2019.pdf
New York | Ulster | Rochester | Town | 3611163011 | Definition: Geothermal Heat Pump |  |  | "Green energy/energy conservation/passive house development. ... The Planning Board shall certify the development incorporates sufficient energy conservation measures such as, but not limited to: LEED net zero construction, geothermal (ground source heat pump) or passive solar heating, and natural habitat preservation." | § 140-10. Lot development standards, B.3 Density Bonus | 2024 | https://ecode360.com/RO1435/laws/LF2209768.pdf
New York | Ulster | Woodstock | Town | 3611183052 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP GEOTHERMAL SYSTEM. A geothermal system that continuously circulates water or a mixture of water and nontoxic, food-grade antifreeze through buried or submerged plastic pipes and passes the fluid through a heat exchange system. The loop is filled just once and the same water mixture is used again and again." "OPEN LOOP GEOTHERMAL SYSTEM. A geothermal system that withdraws water from an extraction well or body of water, passes the water through a heat exchange system, and discharges the temperature-altered water either into the ground in a discharge or return well or to the ground surface or into surface water." | § 260-40.a(F) Definitions | 2023 | https://woodstockny.gov/application/files/6917/6624/6982/Zoning_Edits_Accepted_October_3rd_2023.pdf
New York | Ulster | Woodstock | Town | 3611183052 | Open-loop Prohibitions |  |  | The ordinance states that in the WDWP-O District, "the following uses and activities are specifically prohibited," including "Open loop geothermal systems." | § 260-40.a(D) Permitted and prohibited uses and activities in the Water District Wellhead Protection (WDWP-O) Overlay District | 2023 | https://woodstockny.gov/application/files/6917/6624/6982/Zoning_Edits_Accepted_October_3rd_2023.pdf
New York | Westchester | Peekskill | City | 3611956979 | Definition: Geothermal Heat Pump |  |  | "A Closed Loop system uses buried high-density polyethylene (HDPE) plastic piping installed in drilled and grouted boreholes that conductively exchanges thermal (heat) energy with the ground via circulating water or a water/antifreeze mixture through the piping system." "A Direct Exchange system uses buried copper tubing that conductively exchanges heat energy with the ground via circulating a refrigerant through the tubing." Also: "There are two types of Geothermal Systems, also known as Ground Source Heat Pumps, permitted to be used in the City of Peekskill, for space heating and cooling. They include: Closed Loop, and Direct Exchange systems and are distinguished by the type of Ground Heat Exchanger (GHX) installed in the earth for heat transfer." | Geothermal Systems, 1. Definitions / 2 |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Property Lines | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "Property Line — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Building Foundation | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "Building Foundation — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Wastewater | 25 | feet | Table entries for "Closed Loop and DX Systems" state: "Sewage Disposal Structure, e.g. septic tank, cesspool — 25*" and "Storm water Recharge Structure, e.g., leach field, unlined catch basin — 25." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Private Water | 25 | feet | Table entry for "Closed Loop and DX Systems" states: "Private water supply well — 25." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Public Water | 100 | feet | Table entry for "Closed Loop and DX Systems" states: "Public water supply well — 100*." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Water Lines | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "On-Site Utility, Sewage and Water Line, Lined Catch Basin — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Sewer Lines | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "On-Site Utility, Sewage and Water Line, Lined Catch Basin — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Setback - Hazardous Materials/Fertilizers | 25 | feet | Table entry for "Closed Loop and DX Systems" states: "Potential Source of contamination, e.g. Underground Petroleum Storage Tank, Chemical Use and Waste Storage Area, etc. — 25." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Permit |  |  | The ordinance provides: "Geothermal Systems may be permitted, installed, and erected pursuant to a building permit and subject to the project meeting all other requirements including compliance with applicable plumbing, electrical and mechanical codes." It further states: "Permitted Geothermal Systems eligible to receive a building permit are those that are of a system listed above and comply with the applicable General Requirements" and that permit applications "shall be submitted to the Building Department on forms it provides." | Geothermal Systems, 5.A-B; General Requirements, 1 |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Inspection |  |  | The ordinance states: "The individual piping loops, circuits, and fully constructed piping network for all Geothermal Systems shall be pressure tested for integrity of original material and joints prior to backfill in accordance with the manufacturer's instructions and the governing standards or guidelines." | 2. Design Standards and Guidelines, 2.A.a |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Certification |  |  | The ordinance requires specific credentials: "Certification of (a) through (d) above must be performed by a licensed Professional Engineer." It also states, "Closed Loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques, whichever is used." For larger systems, "Closed Loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA Certified Geothermal Designer in good standing with IGSHPA." For DX systems, "DX system contractors shall demonstrate they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | General Requirements, 1.A.e; 3.A; 3.B; 4.A |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | City | 3611956979 | Decommissioning |  |  | "If the Geothermal System remains nonfunctional or inoperative for a continuous period of one year, the Building Director may require that the buried ground heat exchanger be taken out of service by the property owner." Also: "Closed Loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends. If the heat transfer fluid contains regulated materials (e.g., antifreeze, biocides, or corrosion inhibitors), the heat transfer fluid shall be contained and disposed of in accordance with applicable regulations." | 6. Decommissioning |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Wyoming | Sheldon | Town | 3612166773 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEMS: Structures, equipment, devices or construction techniques used for the production of heat, light, cooling, electricity or other forms of energy on site and may be attached to or separate from the principal structure. Current examples include windmills, solar collectors and solar greenhouses, heat pumps, or other related devices. For the purposes of this Local Law, this definition shall apply to individual residences, farms and businesses." | Section 2010 Definitions | 2016 | https://www.sheldonzoning.com/resources/files/Current_Sheldon_Zoning_Law_complete.pdf
New York | Wyoming | Sheldon | Town | 3612166773 | Permit |  |  | "No use or structure shall be established, erected, demolished nor land developed until a Zoning Permit has been issued by the Zoning Officer... A Building Permit may also be required pursuant to the NYS Uniform Fire Prevention and Building Code." Section 3010 adds that "A zoning permit for a permitted use... may be issued by the Zoning Officer" and Section 3020 requires zoning permit applications with sketch maps/site plans showing "existing and proposed buildings," "water and sewage disposal systems," "parking areas and driveway location," and other site information. | Section 3000 Permits Required | 2016 | https://www.sheldonzoning.com/resources/files/Current_Sheldon_Zoning_Law_complete.pdf
New York | Wyoming | Sheldon | Town | 3612166773 | Inspection |  |  | "Within fifteen (15) days of the receipt of this letter, the Zoning Officer shall conduct a final inspection of the premises to determine whether the new use complies with the requirements of this Local Law." A Certificate of Compliance is issued only if the Zoning Officer determines the building or use complies; otherwise violations must be corrected first. | Section 3050 Certificate of Compliance | 2016 | https://www.sheldonzoning.com/resources/files/Current_Sheldon_Zoning_Law_complete.pdf
New York |  | New York | City | 3651000 | Definition: Geothermal |  |  | § 3-125(a): 'Geothermal system. The term "geothermal system" means a geothermal system as defined in section one of local law number 32 for the year 2013.' | § 3-125(a) | 2023 | https://codelibrary.amlegal.com/codes/newyorkcity/latest/NYCadmin/0-0-0-503
New York |  | New York | City | 3651000 | Definition: Geothermal Heat Pump |  |  | § 3-125.1(a): 'Geothermal exchange system. The term "geothermal exchange system" means a system owned by the city that is used to exchange heat between the earth and two or more buildings for the purpose of providing heating, cooling or hot water to two or more buildings. The term "geothermal exchange system" may also include a waste heat system.' § 3-128(a): 'For purposes of this section, the term "geothermal system" means a system used to exchange geothermal energy between the earth and one or more buildings to provide heating or cooling.' | § 3-125.1(a) Definitions; § 3-128(a) | 2023 | https://codelibrary.amlegal.com/codes/newyorkcity/latest/NYCadmin/0-0-0-503
North Carolina | Guilford |  | County | 37081 | Definition: Well |  |  | "Geothermal borehole" means "any hole in the earth which is drilled for the purpose of installing piping for heating and air conditioning systems through which water, antifreeze, water mixtures, Freon, or other media are circulated to exchange heat with the earth for the purpose of heating or cooling, or both." | Chapter 1 Definitions (33) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Definition: Geothermal |  |  | The rules define geothermal heating/cooling uses through specific geothermal terms: "Geothermal Aqueous Closed-Loop Wells" are wells with closed-loop pipe circulating potable water or water with approved additives "for heating and cooling purposes"; "Geothermal Direct Expansion Closed-Loop Wells" are wells with closed-loop pipe that circulates refrigerant gas "for heating and cooling purposes"; and "Geothermal Heating/Cooling Water Return Well" means "a well that reinjects groundwater used to provide heating or cooling for structures." | Chapter 1 Definitions (32), (34), (35) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop Geothermal Injection Well System" means "a system of continuous piping, part of which is installed in the subsurface via vertical or angled borings, through which moves a fluid that does not exit the piping, and which is used to transfer heat energy between the subsurface and the fluid in association with a heating and cooling system." Also, "Geothermal Heating/Cooling Water Return Well" means "a well that reinjects groundwater used to provide heating or cooling for structures." | Chapter 1 Definitions (16) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Setback - Building Foundation | 15 | feet | For a "Closed Loop Geothermal Injection Well System" the minimum horizontal separation from "Building perimeters, including any attached structures" is "15 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Setback - Wastewater | 50 | feet | For closed-loop geothermal injection wells, the minimum horizontal separation includes: "Septic systems including septic tank, drainfield, waste application area, and drainfield repair area ... 50 feet" and "Land-based or subsurface waste storage or disposal systems ... 50 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Setback - Fuel (above ground) | 50 | feet | The ordinance requires a 50-foot separation from "Above ground or underground storage tanks which contain petroleum fuels used for heating equipment, boilers, or furnaces, with the exception of tanks used solely for storage of propane, natural gas, or liquefied petroleum gas." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Setback - Fuel (below ground) | 100 | feet | For closed-loop geothermal injection wells, "Chemical or petroleum fuel underground storage tank systems regulated under 15A NCAC 02N with secondary containment" must be separated by "50 feet," and those "without secondary containment" by "100 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Setback - Sewer Lines | 25 | feet | For a closed-loop geothermal injection well, separation distances include "Industrial or municipal sewage or liquid waste collection or transmission sewer mains ... 15 feet," "Water-tight sewer lateral lines from a residence or other non-public system ... 15 feet," and "Other industrial or municipal sewage or liquid-waste collection or transfer facilities ... 25 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Permit |  |  | "It shall be unlawful for any person to construct, repair, or perform ground source heat pump well contractor activities in Guilford County without first obtaining a ground source heat pump well permit from the Guilford County Health Director or their designee." The permit "shall be valid for 12 months from date of issuance." The property owner must also submit DEQ forms before construction, including for "Geothermal Heating/Cooling Water Return Wells" an "APPLICATION FOR A PERMIT TO CONSTRUCT OR OPERATE INJECTION WELL(S)" and for a "Closed Loop Geothermal Injection Well System" a "NOTIFICATION OF INTENT TO CONSTRUCT OR OPERATE INJECTION WELLS." | Chapter 5 Section II Ground Source Heat Pump Well Permits | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Licensed Driller |  |  | Chapter 5 states: "Only Certified Well Contractors shall perform well contractor activities." Chapter 1 Section III(B) adds: "No person shall perform, manage, or supervise any well contractor activity without being certified according to the well contractor certification requirements of 15A NCAC 27." | Chapter 5 Section II(H); Chapter 1 Section III(B) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford |  | County | 37081 | Certification |  |  | "Certified Well Contractor" means "a person certified as a well contractor with the State of North Carolina in accordance with 15A NCAC 27 (North Carolina Well Contractor Certification Commission Rules)." Section III(B) states: "No person shall perform, manage, or supervise any well contractor activity without being certified according to the well contractor certification requirements of 15A NCAC 27." | Chapter 1 Definitions (14); Chapter 1 Section III(B) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Montgomery |  | County | 37123 | Permit |  |  | The fee schedule lists under "E. Heating & Air Conditioning Permits" the item "4. Geothermal System — $100.00." | FY2022 BUDGET ORDINANCE — BUILDING INSPECTIONS, E. Heating & Air Conditioning Permits | 2021 | https://nmcdn.io/e186d21f8c7946a19faed23c3da2f0da/9938771685204d8ea2bbc1353c6b7aed/files/departments/finance/budget-information/fy22-bud-ord-signed.pdf
North Carolina | Orange |  | County | 37135 | Definition: Well |  |  | "'Closed loop geothermal heat exchange injection well' or 'geothermal well' means an excavation that is drilled into which a sealed pipe loop is inserted through which fluid or gas is recirculated for the sole purpose of a vertical closed loop geothermal heat exchange system." | Section I.B.14 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Definition: Geothermal Heat Pump |  |  | "'Closed loop geothermal heat exchange system' means a system of continuous piping, part of which is installed in the subsurface, through which moves a fluid or gas that does not exit the piping, and which is used to transfer heat energy to and from the fluid or gas." | Section I.B.15 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Setback - Building Foundation | 15 | feet | For "closed loop geothermal wells that are fully grouted with an approved grout," setbacks measured "from any portion of the borehole to the potential source of contamination" include: "Building perimeters, including any attached structures — 15 ft." | Section III.C.4 table | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Setback - Wastewater | 50 | feet | For "closed loop geothermal wells that are fully grouted with an approved grout," setbacks include: "Septic tanks and drainfields, including drainfield repair areas — 50 ft." and "Land-based or subsurface waste storage or disposal systems — 50 ft." | Section III.C.4 table | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Setback - Sewer Lines | 25 | feet | For "closed loop geothermal wells that are fully grouted with an approved grout," setbacks include: "Sewer lines constructed to water main standards — 15 ft." and "Sewer lines not constructed to water main standards — 25 ft." | Section III.C.4 table | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Permit |  |  | Section I.C: "A property owner or the property owner's agent shall submit an application for a permit to construct, repair, or to abandon a well to Orange County Health Department." For geothermal-specific applications, "An application for a closed-loop geothermal well shall also include: a. The type of recirculation fluid or gas, and any additives to be used... b. A detailed site plan showing the locations of the well or wells and the horizontal piping routes... c. A detailed profile diagram showing the components of the geothermal well system... d. Any current or pending restrictions regarding groundwater use..." Section I.D further states permit validity and administration for well permits. | Section I.C; Section I.D | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Inspection |  |  | Section III.C.9: "Prior to the initiation of the grouting process, the OCHD will verify that the locations of all geothermal wells meet all applicable setbacks. The OCHD may conduct intermittent inspections of the grouting process thereafter, and shall ensure by visual inspection that each well is grouted to within one foot of land surface." Section I.E adds: "The grouting of any well shall not commence before a representative of the Health Department has inspected the annular space around the well." Section I.F requires notice "so that a final inspection can be conducted." | Section III.C.9; Section I.E; Section I.F | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Licensed Driller |  |  | "Geothermal well construction standards, installation standards and contractor certification procedures adopted by the International Ground Source Heat Pump Association (IGSHPA) are hereby enacted by reference." | Section III.C.1 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Screening |  |  | "When closed loop geothermal heat exchange injection wells are terminated below the ground surface, either: a. Each well shall have a permanent monument at grade level directly above each well... or b. The perimeter corners of each well field shall be marked at ground surface with a permanent monument..." | Section III.C.11 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Certification |  |  | "Geothermal well construction standards, installation standards and contractor certification procedures adopted by the International Ground Source Heat Pump Association (IGSHPA) are hereby enacted by reference." | Section III.C.1 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange |  | County | 37135 | Decommissioning |  |  | "Any well that acts as a source or channel of contamination shall be repaired or permanently abandoned within 30 days of receipt of notice from the OCHD." Also, "All wells shall be permanently abandoned in which the casing has not been installed or from which the casing has been removed, prior to removing drilling equipment from the site." | Section IV.B | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Union |  | County | 37179 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. Geothermal energy systems consists of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump. This includes vertical closed loop, horizontal closed loop and water body closed loop systems." | Article 105 ¦ Definitions, Terms Beginning with “G” | 2015 | https://files.nc.gov/ncdeq/Environmental%20Management%20Commission/EMC%20Meetings/2017/3-May2017/AG17-23/AttachmentE_17-23_UC_EIS-AppE_CD-1.pdf
North Dakota | Cass | Horace | City | 3801738900 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY. A source of energy generated from solar, water, geothermal, or similar sources, which is capable of providing energy and utility provisions to a permitted use." | Section 4-2.2 Definitions A | 2024 | https://cms7files.revize.com/cityofhoracend/Horace1.pdf
North Dakota | Cass | Oxbow | City | 3801760480 | Permit |  |  | "Geothermal energy systems are allowed for a private home, group of homes, or as an alternative energy solution to be shared by the entire neighborhood and/or commercial properties. Any geothermal energy system must be guaranteed parts and labor for a minimum of ten (10) years by the vendor." | 6.14. ALTERNATIVE ENERGY SYSTEMS | 2015 | https://oxbownd.com/documents/546/Oxbow_Land_Development_Code.pdf
Ohio | Hamilton | Amberley | Village | 3901672 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEMS (GES). A system that extracts heat from the earth by an open or closed system. An open system typically utilizes a well that is drilled to extract ambient tepid water, whereby the system extracts the heat and returns the water to the earth through the well. A closed system is normally a network of pipe or tubing that circulates water to transfer the heat from the earth to the liquid within the closed loop, whereby the system extracts the hear and recycles the liquid to repeat the cycle." | § 158.02 DEFINITIONS. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | Village | 3901672 | Setback - Right of Way | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | Village | 3901672 | Setback - Property Lines | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | Village | 3901672 | Setback - Yards | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way. Geothermal energy systems located underground may be permitted in the front yard." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | Village | 3901672 | Setback - Water Lines | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | Village | 3901672 | Setback - Sewer Lines | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | Village | 3901672 | Permit |  |  | § 158.06: "The installation of any alternative energy system, or the replacement or alteration of more than 50% of an existing alternative energy system, shall require a permit from the village to be considered and administered by the Board of Zoning Appeals." § 158.07: "The owner of the property upon which an alternative energy system is installed shall ensure that the design, installation, and maintenance of such systems comply with all applicable regulations ... as well as obtain all required permits and approvals from the village." Because "alternative energy system" is defined to include geothermal, these permit requirements apply to geothermal energy systems. | § 158.06 PERMIT REQUIRED.; § 158.07 COMPLIANCE. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio |  | Fairfield | City | 3901725970 | Definition: Well |  |  | "Geothermal Well. This term, as it applies to Source Water Protection, refers to well(s) that have been drilled to access and utilize heat sources from within the earth." | 1157.10 Source Water Protection Program Definitions | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio |  | Fairfield | City | 3901725970 | Permit |  |  | "All new wells and boreholes must be registered by the well or borehole owner with the Public Utilities Director no later than 15 days prior to installation of the well or borehole." | 1157.06.G.2 Wells or Boreholes - Installation and Maintenance | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio |  | Fairfield | City | 3901725970 | Licensed Driller |  |  | "All new wells or boreholes must be installed by a State-recognized well driller." | 1157.06.G.2 Wells or Boreholes - Installation and Maintenance | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio |  | Fairfield | City | 3901725970 | Decommissioning |  |  | "All wells or boreholes which are not maintained for production, standby, or observation purposes are to be permanently sealed according to the State of Ohio Technical Guidance Manual for Sealing Abandoned and Unsealed Wells or Boreholes... The Facility Operator must notify the Public Utilities Director no later than 15 days prior to abandonment of the well or borehole and all paperwork associated with the well or borehole abandonment process must be filed with the Ohio Department of Natural Resources and the City of Fairfield Development Services Department." | 1157.06.G.3 Abandonment of Wells or Boreholes | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio | Cuyahoga | Bay Village | City | 3903504416 | Permit |  |  | Under the building permit fee schedule for "D Heating and Air Conditioning," the ordinance lists "(6) Solar Heat/Geothermal System" with permit fees of "C. Residential $125.00" and "D. Commercial $250.00." | 1305.02 FEES FOR BUILDING PERMITS | 2014 | https://www.cityofbayvillage.gov/DocumentCenter/View/564/Ordinances-14-60-thru-14-64---First-Reading-5-19-14-Second-Reading-6-2-14-Adopted-6914-PDF
Ohio | Cuyahoga | Berea | City | 3903505690 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP GROUND SOURCE HEAT PUMP SYSTEM. A system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." "GEOTHERMAL ENERGY SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. Also referred to as a ' ground source heat pump. '" "OPEN LOOP GROUND SOURCE HEAT PUMP SYSTEM. A system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | CHAPTER 400 Definitions |  | https://cityofberea.org/DocumentCenter/View/3647/Exhibit-A-Definitions-current
Ohio | Cuyahoga | Cleveland Heights | City | 3903516014 | Setback - Yards | 10 | feet | Residential districts: Schedule 1121.12(a) lists 'Freestanding air conditioning machinery, emergency generator, above-ground components of geothermal energy systems, and other similar equipment' as permitted in 'Rear and side, except not in required minimum side yard (see Section 1121.08)' with side lot line setback 'AA-10 & A&B-5.' Multiple-family districts: Schedule 1123.12(a) lists 'Freestanding air conditioning machinery, above-ground components of geothermal energy systems, emergency generator and other similar equipment' and states '(a) Shall maintain the same minimum yard requirement as for a principal use set forth in Section 1123.07.' Section 1123.07 requires side yards of 15 feet abutting MF, C or S districts and up to 25 feet abutting AA, A or B districts. | Schedule 1121.12(a) / Schedule 1123.12(a) | 2023 | https://www.clevelandheights.gov/DocumentCenter/View/14834
Ohio | Cuyahoga | Cleveland Heights | City | 3903516014 | Screening |  |  | For residential districts, Schedule 1121.12(a) applies to 'Freestanding air conditioning machinery, emergency generator, above-ground components of geothermal energy systems, and other similar equipment' and requires 'standard screening, see note (m).' Note (m) states: 'Standard screening means a fence, masonry wall or evergreen hedge which is eighty percent (80%) or more solid and either six (6) feet high or a height adequate to screen the view from a person six (6) feet tall standing on a public street or on adjacent property.' | Schedule 1121.12(a), Note (m) | 2023 | https://www.clevelandheights.gov/DocumentCenter/View/14834
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Definition: Geothermal Heat Pump |  |  | "The installation and construction of a geothermal energy system, referred to as a ground source heat pump system..." | 1155.08 GEOTHERMAL ENERGY SYSTEM STANDARDS | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Roads | 10 | feet | The setback chart requires 10 feet from "Dedicated public right-of-way and all property lines" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Property Lines | 10 | feet | The setback chart requires 10 feet from "Dedicated public right-of-way and all property lines" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Building Foundation | 10 | feet | The setback chart requires 10 feet from "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Wastewater | 25 | feet | The setback chart requires 25 feet from "Septic tanks, aerobic tanks, or holding tanks," 25 feet from "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields," 25 feet from "Sewage seepage pits and cesspools," and 25 feet from "Spray irrigation sites, sewage sludge, and septage disposal sites." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Animal Enclosures | 25 | feet | The setback chart requires 25 feet from "Farm silos, barnyards, privies, and fuel tanks" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Fuel (above ground) | 25 | feet | The setback chart requires 25 feet from "Farm silos, barnyards, privies, and fuel tanks" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Water Lines | 15 | feet | The setback chart requires 15 feet from "Existing water and forced sewer buried utilities and/or utility trenches" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Sewer Lines | 15 | feet | The setback chart requires 10 feet from "Gravity sewer lines and drains carrying domestic sewage or industrial waste" and 15 feet from "Existing water and forced sewer buried utilities and/or utility trenches" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Water Bodies | 15 | feet | The setback chart requires 15 feet from "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The setback chart requires 300 feet from a "Preparation area or storage area of hazardous spray materials, fertilizers of chemicals, or salt piles" and states "150 feet if borehole is cased and grouted inside and out." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Permit |  |  | "A building permit and shall be obtained for any ground source heat pump system prior to installation or usage." | 1155.08(i) Building Permit Required | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the Ohio State Basic Building Code." | 1155.08(g) Safety | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of three hundred sixty five days, the system shall be deemed to be abandoned... The owner shall remove the abandoned system at their expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid... The top of the pipe, coil or boring shall be uncovered and grouted"; "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 1155.08(h) System Abandonment | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | City | 3903549644 | Open-loop Prohibitions |  |  | "Open loop ground source heat pump systems are not permitted." | 1155.08(c) System Requirements | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Oakwood | Village | 3903557750 | Permit |  |  | Section 3 states: "Fees shall be charged for the examination of plans, permits to proceed and for the inspection of all types of construction, installation demolition, removal or alteration work performed on all types of property within the Municipality in accordance with schedules adopted from time to time by Council and on file in the Building Department." Exhibit A lists a residential HVAC permit category for "SOLAR OR GEOTHERMAL" with a fee of "150.00." Exhibit B lists a commercial HVAC permit category for "SOLAR OR GEOTHERMAL" with a fee of "250.00." | SECTION 3; EXHIBIT A; EXHIBIT B | 2025 | https://www.oakwoodvillageoh.com/wp-content/uploads/2025/06/2025-28_Building_Department_Fees.pdf
Ohio | Cuyahoga | Pepper Pike | City | 3903561686 | Permit |  |  | Section 1446.23 states: "The fee for a permit for HVAC work shall be as follows:" and includes line item "(8) GEO Thermal Systems ¦ $100.00." | 1446.23 HVAC MECHANICAL PERMIT FEE | 2011 | https://codelibrary.amlegal.com/codes/pepperpike/latest/pepperpike_oh/0-0-0-47077
Ohio | Franklin | Grandview Heights | City | 3904931304 | Permit |  |  | "(g) (1) Prior to the commencement of any heating or ventilation installation, an application for heating or ventilation permit shall be made at the Department of Building and Zoning, and a heating or ventilation permit shall be secured from the Director." Also, under "REFRIGERATION; HEAT PUMPS PERMIT FEES," the ordinance states: "(b) (1) The fee for heat pumps shall be as follows: (Based on cooling BTU/hr.) Up to and including 5 tons $75.00; Each additional 5 tons or fraction thereof 5.00," and "(4) The fee for replacement of refrigeration and/or heat pump system shall be per the above schedule." | 1325.01 PERMITS REQUIRED | 2026 | https://www.grandviewheights.gov/DocumentCenter/View/11129/02092026-Regular-Council-Packet
Ohio | Franklin | Grandview Heights | City | 3904931304 | Inspection |  |  | "All work for which a permit is required shall be subject to inspection by the Director of Building and Zoning." "No part of the work shall be made inaccessible for inspection until it has been inspected, tested and approved." "There shall be a final inspection and approval on all buildings and mechanical equipment governed by this Code, when completed and ready for occupancy and use." Section 1325.09 adds: "The Director of Building and Zoning upon notification from the permit holder or his agent shall make the following inspections..." including a "Final Inspection." | 1325.05 INSPECTION REQUIRED; 1325.07 APPROVALS REQUIRED; 1325.09 TYPES OF INSPECTIONS | 2026 | https://www.grandviewheights.gov/DocumentCenter/View/11129/02092026-Regular-Council-Packet
Ohio | Franklin | Plain | Township | 3904962974 | Screening |  |  | "Any residence or building using well water as a source of heating or cooling (groundwater heat pump) shall cease to use the well water for heating or cooling if the water level in surrounding or nearby wells is depleted or reduced to the point that those wells must be deepened." | Section 409.02 | 2020 | https://plaintownship.org/wp-content/uploads/2023/01/Plain-Township-Zoning-Resolution-1.pdf
Ohio | Franklin | Westerville | City | 3904983342 | Setback - Property Lines | 5 | feet | "Setbacks. All underground piping and other geothermal appurtenances shall be no closer than five feet to any property line." | 1176.07(b)(3) | 2011 | https://codelibrary.amlegal.com/codes/westerville/latest/westerville_oh/0-0-0-18600
Ohio | Franklin | Westerville | City | 3904983342 | Decommissioning |  |  | "All alternative energy systems and related components shall be properly maintained and kept in operation. Any alternative energy system that remains nonfunctional or inoperative for a continuous period of 120 days shall be deemed to be abandoned and shall constitute a public nuisance... The owner shall be notified of the violation and shall be responsible for the removal of the abandoned system and all associated structures and equipment within 60 days. Removal of an alternative energy system shall require approval of the Chief Building Official." | 1176.1 | 2011 | https://codelibrary.amlegal.com/codes/westerville/latest/westerville_oh/0-0-0-18600
Ohio | Franklin | Westerville | City | 3904983342 | Open-loop Prohibitions |  |  | "All geothermal energy systems must be closed loop systems. Open loop systems are not permitted." | 1176.07(b)(1) | 2011 | https://codelibrary.amlegal.com/codes/westerville/latest/westerville_oh/0-0-0-18600
Ohio | Geauga | Bainbridge | Township | 3905503590 | Open-loop Prohibitions |  |  | Section 177.01(bb) lists as a prohibited use: "Open loop geothermal heating systems." | 177.01 PROHIBITED USES SPECIFIED. | 2024 | https://bainbridgetwp.com/wp-content/uploads/sites/4/2024/03/Zoning-Resolution-Effective-3-27-2024-Z-2023-2.pdf
Ohio | Geauga | Russell | Township | 3905569232 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating System - Any heating or cooling system which uses ground water or the earth as a heat source or heat sink." | Section 2.1 Words and Terms Defined | 2025 | https://russelltownship.us/includes/uploads/Photo_Zoning/Russell_Township_Zoning_Resolution_v2_1.pdf
Ohio | Geauga | Russell | Township | 3905569232 | Permit |  |  | "No geothermal heating system shall be installed within the Township without obtaining a zoning certificate from the Zoning Inspector. The applicant shall supply the Zoning Inspector with a list of specifications describing the type of system utilized, the name and address of the installer, and the specific equipment and systems to be utilized to ensure compliance with the requirements and regulations of the Township's Zoning Resolution." | Section 4.12 Geothermal Heating Systems | 2025 | https://russelltownship.us/includes/uploads/Photo_Zoning/Russell_Township_Zoning_Resolution_v2_1.pdf
Ohio | Geauga | Russell | Township | 3905569232 | Open-loop Prohibitions |  |  | "All geothermal systems permitted in the Township shall be installed and maintained as closed loop systems." The section further defines closed loop systems as designed "to prohibit the discharge of water, chemicals or hazardous substances on the surface of the ground, into the ground or into ground water." | Section 4.12 Geothermal Heating Systems | 2025 | https://russelltownship.us/includes/uploads/Photo_Zoning/Russell_Township_Zoning_Resolution_v2_1.pdf
Ohio | Geauga | South Russell | Village | 3905573684 | Permit |  |  | "No water well being utilized in a geothermal heating unit, as defined in Section 1030.04 shall be drilled in the Village unless prior to such drilling a permit has been secured from the Building Inspector of the Village." Also, "Permits to drill for groundwater source heat pumps, geothermal heating units and other such systems will be denied in areas where inadequate domestic supplies exist at the time application is made for such permit." | 1030.01 PERMIT REQUIRED. | 1986 | https://codelibrary.amlegal.com/codes/southrussell/latest/southrussell_oh/0-0-0-33528
Ohio | Geauga | South Russell | Village | 3905573684 | Decommissioning |  |  | "The water well shall be constructed, operated, maintained and abandoned in compliance with the Ohio Administrative Code, Chapter 3745-9, and as may hereinafter be amended, together with the requirements of the County Health Department or such other governmental agency having jurisdiction." | 1030.04 OPERATION REQUIREMENTS. | 1986 | https://codelibrary.amlegal.com/codes/southrussell/latest/southrussell_oh/0-0-0-33528
Ohio | Geauga | South Russell | Village | 3905573684 | Other Prohibitions/Regulations |  |  | "No geothermal heating unit or similar device shall use, as its source of water, a central water system or the appurtenances to such central water system within the Village." | 1030.04 OPERATION REQUIREMENTS. | 1986 | https://codelibrary.amlegal.com/codes/southrussell/latest/southrussell_oh/0-0-0-33528
Ohio | Greene | Xenia | City | 3905786772 | Inspection |  |  | Table P14.1 lists under Mechanical Permits: 'Geothermal trench/pressure test ¦ $125 per inspection.' Table P14.2 likewise lists under Mechanical Permits: 'Geothermal trench/pressure test ¦ $90 per inspection.' | Table P14.1 G.1 - Chapter 1402: Ohio Building Code; Table P14.2 G.2 - Chapter 1404: Residential Code | 2024 | https://files-backend.assets.thrillshare.com/documents/asset/uploaded_file/4479/Xeniacity/bef52d06-1cda-441a-92e3-30e1ec2781ab/Ord_2023-38_Amending_XCO_Part_Ten_Title_Four_U.pdf?disposition=inline
Ohio | Hamilton | Mariemont | Village | 3906147600 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP SYSTEMS. A geothermal heat pump system which relies on the contained circulation of geothermal fluids through an underground loop of pipes. The loops act as a subsurface heat exchanger, which transports the heat to or from the ground. The loop of pipe is installed either vertically in borings or horizontally in trenches." "OPEN LOOP SYSTEMS. A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring or surface water. The source for heat, groundwater is moved from the ground to a heat pump. The water is then transferred to a discharge area, typically a surface water body, storm or sanitary sewer system, or recharge well." | § 151.141 DEFINITIONS. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Setback - Property Lines | 3 | feet | "Geothermal installations are allowed in a side or rear yard with the following provisions: (1) Well locations must be setback three feet from all side or rear property lines." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Setback - Yards | 3 | feet | "Geothermal installations are not allowed in any front yard." "Geothermal installations are allowed in a side or rear yard with the following provisions: (1) Well locations must be setback three feet from all side or rear property lines." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Setback - Water Lines | 10 | feet | "Geothermal installations are allowed in a side or rear yard with the following provisions: ... (2) A minimum of ten feet from any public utilities (electrical, gas, water, sewer)." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Setback - Sewer Lines | 10 | feet | "Geothermal installations are allowed in a side or rear yard with the following provisions: ... (2) A minimum of ten feet from any public utilities (electrical, gas, water, sewer)." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Permit |  |  | "All applications for a geothermal heating system permit shall be accompanied by an application fee, which shall be non-refundable, and such fee will be according to a fee schedule established by village resolution. Engineering and other professional fees incurred in the review of the permit application shall be paid by the applicant." Also, § 151.142(A) states: "No person shall install a geothermal system in any zoning district in the village without compliance with the provisions of this chapter..." | § 151.145 FEES. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Inspection |  |  | "Any leakage of the geothermal fluid requires the system to be shut down immediately until successful repairs are completed and inspected." "Officials may, upon notice to the applicant, enter upon any property within the village for purposes of inspecting geothermal systems or monitoring the operational characteristics of such facilities." | § 151.146 MAINTENANCE AND ABANDONMENT. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Decommissioning |  |  | "The applicant shall notify the municipality within 30 days of the abandonment of any geothermal heating system." "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... The heat pump and any external mechanical equipment shall be removed. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe/coil shall be properly capped." | § 151.146 MAINTENANCE AND ABANDONMENT. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | Village | 3906147600 | Open-loop Prohibitions |  |  | "Open loop systems shall be prohibited." | § 151.144 DESIGN AND PERFORMANCE STANDARDS. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Springdale | City | 3906174104 | Setback - Property Lines | 7 | feet | "Any wall bracket or ground supported air conditioning, heat pump, or electric generator unit shall not project into or be located in a front yard, but such unit may be located in a side yard if it is no closer than seven feet to the side lot line..." and "Units may be located in the rear yard if they are not less than seven feet from a rear or side lot line." | 153.252(F)(1) Air Conditioning, Heat Pump, and Fixed Electric Generator Equipment | 2020 | https://cms2.revize.com/revize/springdaleoh/Documents/Department/Development%20Regulations/Zoning%20Code/756.pdf
Ohio | Hamilton | Springdale | City | 3906174104 | Setback - Yards | 7 | feet | "Any wall bracket or ground supported air conditioning, heat pump, or electric generator unit shall not project into or be located in a front yard, but such unit may be located in a side yard if it is no closer than seven feet to the side lot line..." and "Units may be located in the rear yard if they are not less than seven feet from a rear or side lot line." | 153.252(F)(1) Air Conditioning, Heat Pump, and Fixed Electric Generator Equipment | 2020 | https://cms2.revize.com/revize/springdaleoh/Documents/Department/Development%20Regulations/Zoning%20Code/756.pdf
Ohio | Hamilton | Springdale | City | 3906174104 | Screening |  |  | "...if the unit is ground mounted, is screened from view from the front lot line. Such screening shall consist of landscaping, fencing, or other type of structure. In all cases, screening shall be consistent with the aesthetics and design of the residence and neighborhood." | 153.252(F)(1) Air Conditioning, Heat Pump, and Fixed Electric Generator Equipment | 2020 | https://cms2.revize.com/revize/springdaleoh/Documents/Department/Development%20Regulations/Zoning%20Code/756.pdf
Ohio | Hamilton | Wyoming | City | 3906186730 | Open-loop Prohibitions |  |  | "No person, firm, partnership, or corporation shall install an open loop geothermal system in the City of Wyoming." | 959.03 OPEN LOOP GEOTHERMAL SYSTEMS PROHIBITED. | 2024 | https://codelibrary.amlegal.com/codes/wyoming/latest/wyoming_oh/0-0-0-35754
Ohio | Huron | Willard | City | 3907785232 | Setback - Water Lines | 10 | feet | "No service line shall be installed closer than ten feet horizontally or eighteen inches vertically to any sewer." | § 5. TERMS AND CHARGES FOR INSTALLATION OF TAPS AND SERVICE CONNECTIONS | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | City | 3907785232 | Setback - Sewer Lines | 10 | feet | "No service line shall be installed closer than ten feet horizontally or eighteen inches vertically to any sewer." | § 5. TERMS AND CHARGES FOR INSTALLATION OF TAPS AND SERVICE CONNECTIONS | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | City | 3907785232 | Permit |  |  | "Plans for the installation of backflow prevention devices for the purpose of containment must be submitted to the City for review and approval." Also: "Plans for new installations and improvements to existing facilities should be evaluated prior to construction to determine the degree of hazard to the potable water system." | PART VI § 3. WATER SYSTEM | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | City | 3907785232 | Inspection |  |  | For geothermal systems, "An approved backflow prevention assembly shall be installed on each service line to a consumer's water system serving any of the following systems... (8) Geothermal heating systems or chemically treated heating systems." The ordinance then requires: "Double check valve assemblies... [and] reduced pressure principle assemblies... shall be inspected and tested for tightness at the time of installation and at least every twelve months thereafter." It also states inspections, tests, and overhauls "shall be performed by a licensed plumber who is qualified and certified to inspect, test and overhaul backflow prevention devices." | PART VI § 10. INSPECTION AND MAINTENANCE | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | City | 3907785232 | Certification |  |  | To inspect, test, and overhaul required backflow prevention assemblies, "The individual must possess a current valid backflow tester certification from the Ohio Department of Commerce, Division of Industrial Compliance." | PART VI § 11. APPROVAL TO INSPECT, TEST, AND OVERHAUL BACKFLOW PREVENTION ASSEMBLIES | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Lake | Kirtland | City | 3908540642 | Definition: Geothermal |  |  | "Geothermal Energy System" means "an energy system that derives its heat energy from the earth." | § 1468.02 DEFINITIONS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | City | 3908540642 | Definition: Geothermal Heat Pump |  |  | "Geothermal systems (also known as a ground source heat pump system)". | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | City | 3908540642 | Setback - Right of Way | 10 | feet | "Piping and geothermal fields shall have a minimum setback from property lines and public right-of ways of ten feet." | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | City | 3908540642 | Setback - Property Lines | 10 | feet | "Piping and geothermal fields shall have a minimum setback from property lines and public right-of ways of ten feet." | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | City | 3908540642 | Permit |  |  | "A zoning permit and building permit shall be obtained for any alternative energy system prior to installation or usage." Section 1468.03(d) separately states: "Alternative energy systems, except for geothermal, as provided in § 1468.06(a)(1) and (2), shall be permitted, as a conditional use..." | § 1468.03 ADMINISTRATION. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | City | 3908540642 | Inspection |  |  | "The Administrator may enter onto any property for which a zoning permit has been issued under this chapter to conduct an inspection to determine whether the conditions stated in the permit have been met." | § 1468.03 ADMINISTRATION. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | City | 3908540642 | Screening |  |  | "Piping and geothermal fields are permitted in front lots or under parking areas so long as they are buried and not visible in the final site and landscaping plan." | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lorain | Oberlin | City | 3909357834 | Permit |  |  | The fee schedule expressly establishes geothermal-specific heating permits: "Geothermal System (New) $200.00," "Geothermal Unit (Replace) $150.00," and "Geothermal Loop System (Replace) $75.00." The ordinance also states a general enforcement provision: "Penalty for starting work without first obtaining required Permit or Required Contractor Registration ... Permit Fee/Registration PLUS 300%." | Heating Permits | 2014 | https://www.cityofoberlin.com/wp-content/uploads/2017/05/ORD_14-19.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Setback - Roads | 70 | feet | Article 4.15(D)(1): "All loops must maintain the following setbacks: 1. Front Yard – 70 feet from road right-of-way." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Setback - Property Lines | 15 | feet | Article 4.15(D)(2): "Side yard – 15 feet from property line." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Setback - Yards | 15 | feet | Article 4.15(D): "All loops must maintain the following setbacks:" including "2. Side yard – 15 feet from property line" and "3. Rear yard – 15 feet from property line." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Setback - Wastewater | 15 | feet | Article 4.15(D)(4): "15 feet on either side of any water line and/or septic system." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Setback - Water Lines | 15 | feet | Article 4.15(D)(4): "15 feet on either side of any water line and/or septic system." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Minimum Well Depth | 5 | feet | Article 4.15(F): "Horizontal loops must have a minimum of a one (1) acre lot and must be installed at least five (5) feet deep." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Permit |  |  | "Closed Loop Geothermal Technologies are permitted in all districts with proper permitting." Also, Article 4.10 requires for a zoning permit: "A completed detailed plot plan depicting the structure or pond to be built, its measurements and the measurements to the four property lines. Plan to include existing structures, if any, and layout of septic systems and geothermal lines. (Effective 10/09)" and Article 4.15(B) states: "A diagram of location of all loop construction must be provided on the site layout and attached to the permit application." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Licensed Driller |  |  | Article 4.15(F): "Vertical loops must be have a minimum of one half (1/2) acre lot and must be installed by a certified well driller." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Open-loop Prohibitions |  |  | "Open Loop Geothermal Technologies are not permitted in any district." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | Township | 3909361532 | Other Prohibitions/Regulations |  |  | Article 4.15(E): "Loops may not be connected to any well water supply or home water supply." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Medina |  | County | 39103 | Inspection |  |  | Section 3.14 applies to backflow prevention and states: 'The MCSE may inspect the water use practices within the consumer's premises to determine compliance with the requirements of these Rules and Regulations.' It also requires that 'inspections, tests, and overhauls of backflow prevention devices shall be made at the expense of the water consumer' and for reduced pressure principle backflow prevention devices and double check valve assemblies they 'shall be inspected and tested for tightness at the time of installation and at least every twelve (12) months thereafter.' | Section 3.14 G. Inspections; Section 3.14 L. Inspection and Maintenance | 2013 | https://sanitaryengineer.co.medina.oh.us/downloads/rulesandregs.pdf
Ohio | Montgomery | Clayton | City | 3911315644 | Permit |  |  | The ordinance and attached agreement establish permit requirements and fees for geothermal work, including a listed fee item for "Geothermal trench/pressure test" ($75.00 in the residential fee schedule; $100.00 in the OBC-covered fee list). The agreement also states NIC shall "Prepare permits (Certificates of Plan Approval) and certificates of occupancy/completion when the installed work complies with all applicable building code regulations, ordinances, and statutes" and "Examine plans and specifications for proposed work" under the applicable codes. | Clayton Proposed Fee Schedule / Agreement § 2(a), (e) | 2022 | https://www.clayton.oh.us/DocumentCenter/View/5523/O-11-22-35
Ohio | Montgomery | Clayton | City | 3911315644 | Inspection |  |  | The agreement requires inspections: NIC "shall exercise enforcement authority for inspections and make inspections on behalf of Clayton"; "Inspections shall be performed on a daily basis during regular business hours"; and NIC shall "Perform job inspections of all work described on the application and plans, including the installation of equipment." The fee schedule also expressly lists "Geothermal trench/pressure test," plus fees for "Re-Inspection" and "Out of Normal Hours Inspection." | Agreement § 1; § 2(d); Clayton Proposed Fee Schedule | 2022 | https://www.clayton.oh.us/DocumentCenter/View/5523/O-11-22-35
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Definition: Geothermal |  |  | "Geothermal Heating and Cooling System" - "A mechanical system for space heating or cooling that relies on the transfer of thermal energy between the earth, including ground water, and a heat transfer fluid and consists of a heat pump, a heat exchange well or loop, and a heat distribution network." | 947.01(d) Geothermal Definitions | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop System" - "A low-temperature geothermal heating and cooling system that circulates a heat transfer fluid, usually water with an antifreeze additive, through a loop or multiple loops of piping installed below the ground surface or within a surface water body." "Open-Loop System" - "A geothermal heating and cooling system that withdraws water from an extraction well or body of water, passes the water through a heat exchange system, and discharges the temperature-altered water either into the ground in a discharge or return well or to the ground surface or into surface water." | 947.01(d) Geothermal Definitions | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Permit |  |  | "Before installing, drilling or otherwise constructing a geothermal heating and cooling system within the City of New Philadelphia, Ohio, an application shall be submitted to the New Philadelphia City Health Department for a permit for the drilling and/or construction of such geothermal heating and cooling system... All such permits shall remain in force for one year from the date of submittal to the City of New Philadelphia." | 947.05 Regulation of Geothermal Heating/Cooling Systems | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Inspection |  |  | Section 947.05(f) states: "The requirements of Section 947.03 shall apply to any and all geothermal heating and cooling system wells constructed, maintained or abandoned within the City." Section 947.03(d)(1) then provides: "All sources of water supply other than the municipal water system shall henceforth be subject to inspection and approval by the New Philadelphia City Health Department and/or the Water Department Superintendent." In addition, for certified testing of required backflow assemblies, 945.04(b)(6) states: "it shall be the duty of the customer user at any premises where backflow prevention assemblies are installed to have certified inspections and operational tests made at least once per year." | 947.03(d)(1); 947.08(g) Water Withdrawal Regulations as applied by 947.05(f) | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Certification |  |  | "No person shall engage in the work or business of installing of geothermal systems within the City of New Philadelphia without first obtaining a license from the City." "the Director of Public Service shall issue a Geothermal Heating and Cooling Installer's License for a period of one year expiring December 31 of the year of registration." "At the time of application, the applicant shall enter into a bond payable to the City of New Philadelphia of five thousand dollars ($5,000)..." | 947.06 Bonding/Registration of Geothermal Installers | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Decommissioning |  |  | "The application fee for the abandonment/de-commissioning of a geothermal heating and cooling system shall be fifty dollars ($50.00)." Section 947.05(f) adds: "The requirements of Section 947.03 shall apply to any and all geothermal heating and cooling system wells constructed, maintained or abandoned within the City." Section 947.03(d)(4) requires that "Abandonment shall be in accordance with OAC 3745-9-10," and 947.03(d)(6) requires for abandoned wells: "a copy of the abandonment report required by Ohio R.C. 1521.05(C) shall be submitted to this office within (30) days of the completion of the abandonment process." | 947.05(e)-(f); 947.03(d)(4),(6) | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | City | 3915755216 | Other Prohibitions/Regulations |  |  | "No geothermal heating and cooling system or part thereof shall be drilled or otherwise constructed in the current five year time of travel zone or within one-half mile from the center of the municipal water well field." | 947.05(b) Regulation of Geothermal Heating/Cooling Systems | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Wood | Northwood | City | 3917357190 | Noise Limits | 10 | dBA | "Noise from any renewable energy system shall be limited to no more than ten (10) decibels above the original ambient sound level beyond the property line, considering both daytime and night measurements pursuant to measurement with a sound decibel meter." The chapter also states: "Other types of renewable energy systems such as, geothermal energy, hydrogen, biomass or other similar technologies shall meet the minimum requirements of this chapter and the respective zoning district." | 1251.04 DEVELOPMENT STANDARDS | 2023 | https://cms9files1.revize.com/northwoodoh/ORD%202022-45.pdf
Ohio | Wood | Northwood | City | 3917357190 | Permit |  |  | "All renewable energy systems shall require a zoning permit." The same section also states: "Other types of renewable energy systems such as, geothermal energy, hydrogen, biomass or other similar technologies shall meet the minimum requirements of this chapter and the respective zoning district." | 1251.04 DEVELOPMENT STANDARDS | 2023 | https://cms9files1.revize.com/northwoodoh/ORD%202022-45.pdf
Ohio | Wood | Northwood | City | 3917357190 | Decommissioning |  |  | "Any renewable energy system, including related equipment, that becomes inoperable shall be repaired or removed at the owner's expense within one (1) year of the date the system became inoperable." | 1251.05 INOPERABLE RENEWABLE ENERGY SYSTEMS | 2023 | https://cms9files1.revize.com/northwoodoh/ORD%202022-45.pdf
Ohio |  | Dublin | City | 3922694 | Definition: Geothermal |  |  | "Equipment for the collection of solar, wind or geothermal energy or its conversion to electrical energy or heat for use on the same property or for incidental sale to a utility when that equipment is accessory to a permitted or approved conditional principal use of the property." | Chapter 153.002 - Definitions, (18)(b): RENEWABLE ENERGY EQUIPMENT OR ALTERNATIVE ENERGY EQUIPMENT |  | https://dublinohiousa.gov/dev/dev/wp-content/uploads/2021/10/C5_Dublin-Zoning-Code-Regs.pdf
Ohio |  | Dublin | City | 3922694 | Setback - Yards | 5 | feet | "Ground-mounted equipment for the collection of geothermal energy is permitted only to the rear of and within five feet of the principal structure." Similar rear-yard placement language also appears in Chapter 153.172 - Architectural Review - Uses: "The collection of geothermal energy is permitted only to the rear of and within five feet of the principal structure." | Chapter 153.059 - Bridge Street District - Uses, (j) Renewable energy equipment |  | https://dublinohiousa.gov/dev/dev/wp-content/uploads/2021/10/C5_Dublin-Zoning-Code-Regs.pdf
Ohio |  | Dublin | City | 3922694 | Screening |  |  | "Ground-mounted equipment for the collection of geothermal energy is permitted only to the side or rear of the principal structure, and equipment must be adequately screened." Additional geothermal-specific concealment language appears in Chapter 153.059(j)(4): "Ground-mounted renewable energy equipment shall be sited to minimize view from the public right-of-way and adjacent properties, and shall be camouflaged to the extent that the equipment can function normally," and Chapter 153.172(j)(2)(c): "Ground-mounted renewable energy equipment shall be sited to minimize view from the public right-of-way and surrounding properties and shall be camouflaged to the extent that the equipment can function normally." | Chapter 153.038 - EAZ Innovation Districts - District Uses, (C)(31)(a) |  | https://dublinohiousa.gov/dev/dev/wp-content/uploads/2021/10/C5_Dublin-Zoning-Code-Regs.pdf
Ohio | Butler | Oxford | City | 3959234 | Permit |  |  | The fee ordinance expressly lists geothermal-specific permit/inspection line items under the Building Official schedules: residential includes "Geothermal trench/pressure test 75.00" and commercial includes "Geothermal Trench/Pressure Test 100.00 per inspection." | C) INSPECTIONS (Building Official) |  | https://www.cityofoxford.org/Documents/%20Government/%20City%20Charter%20and%20Codified%20Ordinances/Fee%20Ordinances/2023%20Fee%20Ordinance.pdf?t=202603230833000
Ohio | Butler | Oxford | City | 3959234 | Inspection |  |  | Under Building Official inspection fees, the ordinance includes geothermal-specific inspection items: residential "Geothermal trench/pressure test 75.00" and commercial "Geothermal Trench/Pressure Test 100.00 per inspection." | C) INSPECTIONS (Building Official) |  | https://www.cityofoxford.org/Documents/%20Government/%20City%20Charter%20and%20Codified%20Ordinances/Fee%20Ordinances/2023%20Fee%20Ordinance.pdf?t=202603230833000
Ohio | Paulding | Paulding | Village | 3961252 | Permit |  |  | "Any person, firm, group or corporation, either owner or agent who tampers with or attempts to use facilities provided by the village without first obtaining the necessary permits and approvals is in violation of the rules and regulations." | § 52.22 GENERAL CONDITIONS | 2020 | https://codelibrary.amlegal.com/codes/pauldingoh/latest/paulding_oh/0-0-0-1968
Ohio | Lucas | Swanton | Village | 3975896 | Definition: Geothermal |  |  | "Geothermal System : Any energy system where thermal transfer is extracted from heat stored in the earth and designed to deliver a heating and cooling resource to any building/structure." | SECTION 2 DEFINITIONS | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | Village | 3975896 | Setback - Property Lines | 10 | feet | "A geothermal system shall be located at least ten (10) feet from adjacent property lines and from the foundation of any building/structure." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | Village | 3975896 | Setback - Building Foundation | 10 | feet | "A geothermal system shall be located at least ten (10) feet from adjacent property lines and from the foundation of any building/structure." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | Village | 3975896 | Setback - Wastewater | 25 | feet | "A geothermal system shall be located at least twenty-five (25) feet from leach fields and any potable water source." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | Village | 3975896 | Setback - Public Water | 25 | feet | "A geothermal system shall be located at least twenty-five (25) feet from leach fields and any potable water source." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | Village | 3975896 | Permit |  |  | "Before installation of geothermal system, a zoning permit must be obtained; the following requirement must be met to obtain a zoning permit for the installation of a geothermal system: 1. Site plan: A detailed site plan shall be required in accordance with the requirements of Section 9.17." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | Village | 3975896 | Open-loop Prohibitions |  |  | "All geothermal systems must have a closed loop technologies. Open loop systems are not permitted." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Champaign | Urbana | City | 3979072 | Definition: Geothermal Heat Pump |  |  | "A CLOSED-LOOP SYSTEM IS DEFINED AS A PIPE AND HEAT EXCHANGER NETWORK SEALED FROM ITS SURROUNDING ENVIRONMENT." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Setback - Property Lines | 5 | feet | "THE LOCATION OF ALL UNITS AND PIPING LOOPS SHALL BE A MINIMUM OF FIVE FEET (5') FROM ALL SIDE AND REAR PROPERTY LINES..." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Setback - Building Foundation | 5 | feet | "ALL BURIED GEOTHERMAL PIPES IN SYSTEMS CONTAINING ANTIFREEZE PASSING PARALLEL WITHIN 5 FEET OF ANY WALL, STRUCTURE OR WATER PIPE SHALL BE INSULATED WITH R2 MINIMMUM CLOSED CELL INSULATION." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Setback - Private Water | 25 | feet | "AN OVERALL ISOLATION RADIUS OF ... 25’ AWAY FROM ANY PRIVATE WATER SUPPLY WELLS SHALL BE MAINTAINED." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Setback - Public Water | 300 | feet | "AN OVERALL ISOLATION RADIUS OF 300’ AWAY FROM ANY PUBLIC WATER SUPPLY WELLS... SHALL BE MAINTAINED." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Setback - Water Lines | 2 | feet | "THERE SHALL BE A 2’ MINIMUM SEPARATION BETWEEN SUPPLY/RETURN LINES AND WATER/SEWER LINES." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Setback - Sewer Lines | 2 | feet | "THERE SHALL BE A 2’ MINIMUM SEPARATION BETWEEN SUPPLY/RETURN LINES AND WATER/SEWER LINES." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Permit |  |  | "A NOMINAL PERMIT FEE WILL BE CHARGED FOR ANY GEOTHERMAL INSTALLATION WITHIN THE CITY OF URBANA." | PERMITTING AND INSPECTION | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Inspection |  |  | "THE FEE COVERS AN INITIAL INSPECTION (BEFORE THE LOOP INSTALLATION WHILE THE PRESSURE TESTING IS BEING PERFORMED) AND A FINAL INSPECTION (TO MAKE SURE GROUTING AND BACKFILLING PROCEDURES ARE FOLLOWED) BY THE CITY ENGINEERING DEPARTMENT." | PERMITTING AND INSPECTION | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Certification |  |  | "ALL GEOTHERMAL SYSTEM INSTALLERS SHALL BE IGSHPA (INTERNATIONAL GROUND SOURCE HEAT PUMP ASSOCIATION) CERTIFIED." | 2. INSTALLER CERTIFICATION | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | City | 3979072 | Open-loop Prohibitions |  |  | "ONLY GEOTHERMAL CLOSED-LOOP SYSTEMS SHALL BE INSTALLED... NO OPEN-LOOP SYSTEMS WILL BE PERMITTED." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Arizona | Navajo |  | County | 4017 | Permit |  |  | "Any underground injection, except into a well authorized by rule or authorized by permit under the Arizona UIC program, is prohibited. The construction of any well required to have a permit is prohibited until the permit has been issued." Also, "Unless an underground injection well is authorized by rule under R18-9-I650, all injection activities including construction of an injection well are prohibited until the owner or operator is authorized by permit." Class V wells expressly include "Air conditioning return flow wells used to return to the supply aquifer the water used for heating or cooling in a heat pump." | R18-9-B607. Prohibition of Unauthorized Injection; R18-9-C616. Individual Permits; Application for Individual Permits | 2022 | https://www.navajocountyaz.gov/DocumentCenter/View/533/18-09_(15-2)_130pgs.pdf
Arizona | Navajo |  | County | 4017 | Inspection |  |  | "One of the following methods must be used to evaluate the absence of significant leaks... 1. Following an initial pressure test... 2. Pressure test with liquid or gas..." and "One of the following methods must be used to determine the absence of significant fluid movement... 1. The results of a temperature or noise log..." | R18-9-B613. Mechanical Integrity | 2022 | https://www.navajocountyaz.gov/DocumentCenter/View/533/18-09_(15-2)_130pgs.pdf
Arizona | Navajo |  | County | 4017 | Decommissioning |  |  | For Class V wells, "Prior to abandoning a Class V well, the owner or operator shall close the well in a manner that prevents the movement of fluid containing any contaminant into an USDW..." and "The owner or operator shall dispose of or otherwise manage any soil, gravel, sludge, liquids, or other materials removed from or adjacent to the well in accordance with all applicable Federal, State, and local regulations and requirements." Permit applicants must also submit "A plugging and abandonment plan that meets the requirements of R18-9-B614 and is acceptable to the Director." | R18-9-B614. Plugging and Abandoning Class I, II, III, IV, and V Wells; R18-9-C616. Individual Permits; Application for Individual Permits | 2022 | https://www.navajocountyaz.gov/DocumentCenter/View/533/18-09_(15-2)_130pgs.pdf
Oklahoma | Tulsa | Tulsa | City | 4075000 | Definition: Geothermal Heat Pump |  |  | “Geothermal Heat Exchange System Equipment that exchanges thermal energy between the ground (or a water source) and a building. This includes vertical closed loop, horizontal closed loop, water body closed loop system and open loop systems. Also known as ground source heat pumps and geothermal heat pumps.” | Section 95.100 ¦ Terms Beginning with “G” | 2025 | http://tulsaplanning.org/plans/TulsaZoningCode.pdf
Oklahoma | Tulsa | Tulsa | City | 4075000 | Permit |  |  | “Unless otherwise expressly allowed by this zoning code or state law, any violation of a provision of this zoning code—including any of the following—are subject to the remedies and penalties provided for in this zoning code. 85.020-D To engage in the use of a building, structure or land, the use or installation of a sign, or any other activity requiring one or more permits or approvals under this zoning code without obtaining such required permits or approvals.” | Section 85.020 ¦ Violations | 2025 | http://tulsaplanning.org/plans/TulsaZoningCode.pdf
Oklahoma | Tulsa | Tulsa | City | 4075000 | Other Prohibitions/Regulations |  |  | “Underground equipment, piping and devices may not be located in any public easement or right-of-way.” | Section 45.080-B ¦ Location | 2025 | http://tulsaplanning.org/plans/TulsaZoningCode.pdf
Oregon |  | Adams | City | 4100350 | Definition: Geothermal |  |  | "Geothermal Area - Means any parcel of land that is or reasonably appears to be underlain by geothermal resources. (ORS 522.005.)" "Geothermal Resources - The natural heat of the earth, the energy, in whatever form, below the surface of the earth, present in, resulting from, or created by, or which may be extracted from, the natural heat, and all minerals in solution or other products obtained from naturally heated fluids, brines, associated gases and steam, in whatever form, found below the surface of the earth..." | Chapter 1.3 Definitions | 2003 | http://www.cityofadamsoregon.com/uploads/3/1/2/3/3123389/development_code.pdf
Oregon | Deschutes |  | County | 41017 | Permit |  |  | "11(20) High-temperature geothermal wells and small-scale geothermal energy facilities" requires application materials, and states: "For drilling applications..." specified narratives and diagrams must be provided; "When approved by the Planning Director, applications for prospect wells... may satisfy the information requirements... by submission of a copy of the applicant's prospect well permit application to the Oregon Department of Geology & Mineral Industries." It also states, "Applicants may redrill or otherwise reenter the same well-bore of any well for which a conditional use permit has already been issued as long as all conditions of the use permit continue to be met." | Section 9. Section 8.050, Specific Use Standards, subsection (20) | 1985 | https://g3mtx8smp2.execute-api.us-east-2.amazonaws.com/v1/6254/chapter_12/12.23.pdf
Oregon | Deschutes |  | County | 41017 | Decommissioning |  |  | "Site abandonment and restoration. When a well or facility is permanently abandoned; the applicant shall remove all equipment, structures, and other related material within 180 days from the date operations cease. Thereafter the applicant shall regrade the area of operations so as to match original land contours as closely as practical, and shall revegetate the area in accordance with Subsection 21 of 8.050(B)." | Section 9. Section 8.050, Specific Use Standards, subsection (20)(B) | 1985 | https://g3mtx8smp2.execute-api.us-east-2.amazonaws.com/v1/6254/chapter_12/12.23.pdf
Oregon | Douglas |  | County | 41019 | Definition: Geothermal |  |  | "GEOTHERMAL RESOURCES: The natural underground reservoirs of heat that may be exploited for the production of heat energy, including but not limited to all minerals obtained from naturally or artificially injected fluid, brine or associated gas and steam in any form whatsoever, but excluding oil, hydrocarbon gas and other hydrocarbon substances and hot waters of less than 250 degrees Fahrenheit and bottom hold temperature." | SECTION 1.090 Definitions | 2012 | https://www.douglascountyor.gov/DocumentCenter/View/2899/2012-Chapter-1-PDF
Oregon | Jackson | Ashland | City | 4103050 | Noise Limits | 45 | dBA | Section 9.08.170(E)(3)(a) states: "No person shall operate a commercial or residential heat pump, air-conditioning unit, or similar mechanical device if noise levels from its operation exceed forty-five (45) dBA from the closest property line of a residential property on an adjacent parcel of land characterized as a noise sensitive area." Section 9.08.170(E)(3)(b) adds a separate limit for older units: "No person shall operate a commercial or residential heat pump, air-conditioning unit, or similar mechanical device that was installed prior to 1981 if noise levels from its operation exceed fifty (50) dBA..." | 9.08.170 Unnecessary Noise | 2017 | https://ashland.municipal.codes/AMC/9.08.280
Oregon | Josephine |  | County | 41033 | Setback - Property Lines | 5 | feet | Section 84.080 states: "Any new wells drilled after the effective date of this code shall not be located within 5 feet of a property line. Furthermore, all wells shall meet the location requirements of OAR, Chapter 690, Division 210." | 84.080 - NEW WELLS | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Josephine |  | County | 41033 | Permit |  |  | Section 84.020.J states: "A water well permit shall be obtained prior to the commencement of any work for each of the following: 1. Construction of any well; 2. Alteration of any well; 3. Abandonment of any well." The same article expressly includes geothermal-related use by exempting "Down-hole heat exchange" in Section 84.020.I.4. | 84.020 - APPLICATION | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Josephine |  | County | 41033 | Certification |  |  | Section 84.050 provides: "The certified pump tester shall submit a preliminary report..."; "the certified pump tester shall attempt to notify all property owners..."; and under "CERTIFICATION AND RESPONSIBILITY": "A major or minor pump test is to be conducted by a firm, or individual, who has been certified by the Water Resources Department to have the necessary equipment and knowledge required to conduct the test." | 84.050 - TEST OBJECTIVE | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Josephine |  | County | 41033 | Decommissioning |  |  | Section 84.050 states: "Any substandard well on a lot or parcel proposed for development, must be properly abandoned or repaired as required by the Oregon Administrative Rules (OAR), Chapter 690, Division 200 to 235, for well construction, maintenance, and abandonment." Section 84.070.A adds that if water quality standards are not met, "the well must be properly constructed in accordance with OAR, Chapter 690 Division 210 and 215, or abandoned in accordance with OAR, Chapter 690 Division 220." Section 84.020.J also requires a permit for "Abandonment of any well." | 84.050 - TEST OBJECTIVE; 84.070 - WATER QUALITY OR QUANTITY TEST | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Multnomah |  | County | 41051 | Permit |  |  | "For the purposes of this section, the expiration provisions in (a) and (b) shall also apply to all other Type II or III decisions associated with approval of the residential development, such as SEC or GHP permits." | § 39.1185 EXPIRATION OF TYPE II OR TYPE III DECISIONS |  | https://multnomah.granicus.com/MetaViewer.php?view_id=3&clip_id=2566&meta_id=162614
Oregon | Multnomah |  | County | 41051 | Inspection |  |  | "Inspection and enforcement. The director may take steps to ensure compliance with the requirements of Part 6, Geologic Hazards permit requirements, and Large Fill permit requirements any permit listed in subsection (A) and 39.6235, including but not limited to, inspections, peer review of engineering analysis (at the applicant's expense), post construction certification of the work... If inspection by county staff reveals erosive conditions which exceed those prescribed by the permit, work may be stopped until appropriate correction measures are completed." | § 39.6210 PERMITS REQUIRED |  | https://multnomah.granicus.com/MetaViewer.php?view_id=3&clip_id=2566&meta_id=162614
Oregon | Polk | Dallas | City | 4117700 | Permit |  |  | "A building permit shall not be issued until the Planning Official has issued a Land Use Review approval in accordance with the provisions of Chapter 4.2, or has otherwise found that such review is not required. The Planning Official may determine that this Code requires other permits or approvals in lieu of or before Land Use Review approval may be granted." | 1.2.080 Building Permit And Certificate Of Occupancy | 2026 | https://dallasor.municipalcodeonline.com/book?type=development#name%3DARTICLE_1_GENERAL_PROVISIONS
Oregon | Multnomah | Gresham | City | 4131250 | Definition: Geothermal |  |  | "Geothermal energy is generated from heat stored in the earth." | 2.381.4 Geothermal Energy | 2013 | https://www.greshamoregon.gov/globalassets/government/city-codes-and-policies/comprehensive-plan/comprehensive-plan---volume-1---section-2.000.pdf
Oregon | Multnomah | Gresham | City | 4131250 | Definition: Geothermal Heat Pump |  |  | "Low Temperature Geothermal: This approach utilizes the relatively constant and mild temperatures naturally found at shallow depths in the soil and groundwater throughout the year. The ground-source heat pump transfers heat stored in the earth or in groundwater into a building during the winter and transfers heat out of a building and into the ground during the summer." Also: "A ground-source heat pump has two main parts: - Either a closed-loop or open-loop system in the ground where the heat transfer occurs with the soil or groundwater." | 2.381.4 Geothermal Energy | 2013 | https://www.greshamoregon.gov/globalassets/government/city-codes-and-policies/comprehensive-plan/comprehensive-plan---volume-1---section-2.000.pdf
Oregon | Klamath | Klamath Falls | City | 4139700 | Definition: Well |  |  | "Well. Any artificial opening or artificially altered natural opening, however made, by which geothermal fluids or ground water flows under natural pressure or is artificially withdrawn, or is used to operate a heat exchanger within the well, provided that this definition shall not include a natural spring." | 8.254 DEFINITIONS | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | City | 4139700 | Permit |  |  | "Any person, including the City, desiring to construct, install, or alter a well within the City shall first apply for a Well Permit at the Geothermal Data Center... No person shall commence construction or alteration of a well prior to the owner of a proposed well receiving a Well Permit." | 8.268 APPLICATION FOR WELL PERMIT | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | City | 4139700 | Inspection |  |  | Section 8.282: "Upon completion of any well construction or alteration, but prior to regular use, the owner shall promptly notify the Geothermal Data Center to request a well completion inspection and written report thereof..." Section 8.296: "City officials may, upon reasonable notice to the owner, enter upon any property within the City for purposes of inspecting wells and/or geothermal facilities, or monitoring the operational characteristics of such wells and/or facilities..." | 8.282 COMPLETION INSPECTION; 8.296 CITY INSPECTION AND MONITORING OF WELLS AND GEOTHERMAL FACILITIES | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | City | 4139700 | Decommissioning |  |  | Section 8.264(2): the City Manager shall offer technical assistance "during the conversion or abandonment of such discharging wells or facilities." Section 8.298: when a well is wasteful or defective, the City Manager shall notify the owner and "require said owner to repair or adjust the well within 60 days; a well continuing a wasteful or defective operation after expiration of the 60 days shall be prosecuted as a violation of this Ordinance." | 8.264 PRE-ORDINANCE SURFACE DISCHARGE ELIMINATION; 8.298 WASTEFUL OR DEFECTIVE WELLS | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | City | 4139700 | Other Prohibitions/Regulations |  |  | "No well constructed or altered after the effective date of this Ordinance shall be operated or altered in such a manner as to cause thermal ground water to be discharged onto the surface of the ground or into any public ditch or drainage facility. Construction and routine maintenance of wells shall be exempt from said prohibition..." | 8.284 POST-ORDINANCE SURFACE DISCHARGES | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Arizona |  | Dewey-Humboldt | Town | 419145 | Permit |  |  | "Mechanical permits. A mechanical permit shall not be required for the following:" followed by exempt items such as "A portable heating appliance," "A portable cooling unit," and certain minor equipment work. Ground-source heat pump systems are not listed among the mechanical permit exemptions, while the code elsewhere states in Section 105.8 that persons performing installation or repair of "mechanical" systems to which the code applies must comply with the code. | § 150.01 Administrative Code, Section 105.2 — Work exempt from permit | 2021 | https://codelibrary.amlegal.com/codes/deweyhumboldt/latest/deweyhum_az/0-0-0-11034
Arizona |  | Dewey-Humboldt | Town | 419145 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to slab grade inspection, or at the time of rough-in inspection prior to insulation." The section adds: "Exception: Back-filling of ground-source heat pump loop systems tested in accordance with Sections M2105.1 of the 2018 International Residential Code and 1208.1. of the 2018 International Mechanical Code prior to inspection shall be permitted." | § 150.01 Administrative Code, Section 110.2.6 — Plumbing, mechanical, gas and electrical systems inspection | 2021 | https://codelibrary.amlegal.com/codes/deweyhumboldt/latest/deweyhum_az/0-0-0-11034
Pennsylvania | Adams | Franklin | Township | 4200127320 | Definition: Well |  |  | "Well — Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or monitoring of groundwater. This includes but is not limited to test wells, test borings, monitoring wells, geothermal wells, domestic wells, irrigation wells, or commercial wells." | Section 201: Definitions | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Definition: Geothermal |  |  | "Geothermal — A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." | Section 201: Definitions | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop Geothermal — A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere. The heat transfer fluid is potable or beneficial reuse water and may have approved antifreeze added." Also: "Open-Loop Geothermal — A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump. The discharge water from the water-source heat pump may be returned to the subsurface through a recharge well or infiltration bed, or may be discharged into a pond, lake, or stream. A spring may also be the source of the ground water supply." | Section 201: Definitions | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Roads | 10 | feet | Table 1 requires a minimum setback from "Dedicated public right-of-way" of "10" for "Boreholes (ft)." Section 102 states the ordinance applies to "vertical closed-loop geothermal wells and/or boreholes." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Building Foundation | 10 | feet | Table 1 requires a minimum setback from "Building foundations (except for buildings enclosing water wells, water well pumps, and/or any other source of pollution as approved)" of "10" for "Boreholes (ft)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Wastewater | 25 | feet | For boreholes, Table 1 sets setbacks of "25" ft from "Septic tanks, aerobic tanks or holding tanks"; "25" ft from "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields"; "25" ft from "Sewage seepage pits, cesspools"; and "25" ft from "Domestic spray irrigation sites, sewage sludge and septage disposal sites." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Animal Enclosures | 25 | feet | Table 1 lists "Farm silos, barnyards, privies and fuel tanks" with a borehole setback of "25" ft. | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Fuel (above ground) | 25 | feet | Table 1 lists "Farm silos, barnyards, privies and fuel tanks" with a borehole setback of "25" ft. | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Water Lines | 15 | feet | Table 1 states for "Existing water and forced sewer buried utilities and/or utility trenches" that boreholes must be "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench centerline." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Sewer Lines | 10 | feet | Table 1 lists "Public or on lot gravity sewer lines and drains carrying domestic sewage or industrial waste" with a minimum setback of "10 or according to easement" for "Boreholes (ft)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Water Bodies | 25 | feet | Table 1 requires a minimum setback from "Lakes, ponds, streams or other surface waters" of "25" for "Boreholes (ft)." Section 102 includes "vertical closed-loop geothermal wells and/or boreholes" within the ordinance scope. | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table 1 lists "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" with a minimum setback of "100" for "Boreholes (ft)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Permit |  |  | Section 300 states: "No person, firm, or corporation shall make a penetration of soil and, or rock that is augered, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed that is regulated by this Ordinance until a Drilling Permit has been issued." Section 102 makes the ordinance applicable to "vertical closed-loop geothermal wells and/or boreholes." Section 400.C.1 adds that work may begin only "after the Drilling Permit has been issued and the Code Enforcement Officer has conducted the preliminary inspection of the site." | Section 300: Well Drilling Permit Required; Section 400: Drilling Permits | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Inspection |  |  | Section 400.C.1 requires that work may begin only after "the Code Enforcement Officer has conducted the preliminary inspection of the site." Section 401.D states: "A preliminary/pre-construction inspection shall be conducted at the site before any well or borehole drilling is commenced." At that inspection, the officer determines "Compliance with setback distances as found in Table 1 of Section 302.C." Section 401.E also provides: "Code Enforcement Officer reserves the right to inspect the site at any time to determine if the well is in compliance with the Drilling Permit, the standards within this ordinance, and to observe the implementation of any of the standards listed in the Adams County Construction Standards and Material Specifications for Wells & Geothermal Systems." | Section 400.C.1; Section 401: Inspection/Reviews | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Decommissioning |  |  | "Existing wells that are being replaced that are not grouted with approved grout or do not have a sanitary well cap shall be decommissioned or mitigated in accordance with the Adams County Construction Standards and Material Specifications for Wells & Geothermal Systems." | Section 305: Well Abandonment | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | Township | 4200127320 | Open-loop Prohibitions |  |  | "Geothermal wells shall only be constructed as part of Closed-Loop Geothermal systems. Open-Loop Geothermal systems are prohibited." | Section 301: Geothermal Wells | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Definition: Well |  |  | "Well - Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or monitoring of groundwater. This includes but is not limited to test wells, test borings, monitoring wells, geothermal wells, domestic wells irrigation wells, or commercial wells." | Section 201: Definitions | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Definition: Geothermal Heat Pump |  |  | "Geothermal - A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." "Closed-Loop Geothermal - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." "Open-Loop Geothermal - A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump." | Section 201: Definitions | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Roads | 10 | feet | For boreholes, Table 1 requires 10 ft from "Dedicated public right-of-way." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Building Foundation | 10 | feet | For boreholes, Table 1 requires 10 ft from "Building foundations (except for buildings enclosing water wells, water well pumps, and/or any other source of pollution as approved)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Wastewater | 25 | feet | For boreholes, Table 1 requires 25 ft from "Septic tanks, aerobic tanks or holding tanks," 25 ft from "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields," 25 ft from "Sewage seepage pits, cesspools," and 25 ft from "Domestic spray irrigation sites, sewage sludge and septage disposal sites." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Animal Enclosures | 25 | feet | For boreholes, Table 1 requires 25 ft from "Farm silos, barnyards, privies and fuel tanks." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Fuel (above ground) | 25 | feet | For boreholes, Table 1 requires 25 ft from "Farm silos, barnyards, privies and fuel tanks." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Water Lines | 15 | feet | For boreholes, Table 1 requires setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench centerline." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Sewer Lines | 15 | feet | Table 1 requires boreholes to be set back from "Public or on lot gravity sewer lines and drains carrying domestic sewage or industrial waste" by "10 or according to easement" and from "Existing water and forced sewer buried utilities and/or utility trenches" by "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench centerline." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Water Bodies | 25 | feet | For boreholes, Table 1 requires a 25 ft setback from "Lakes, ponds, streams or other surface waters." Section 102 states the ordinance applies to "vertical closed-loop geothermal wells and/or boreholes." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Setback - Hazardous Materials/Fertilizers | 100 | feet | For boreholes, Table 1 requires 100 ft from "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Permit |  |  | Section 300 states: "No person, firm, or corporation shall make a penetration of soil and, or rock that is augered, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed that is regulated by this Ordinance until a Drilling Permit has been issued." Section 102 makes the ordinance applicable to "vertical closed-loop geothermal wells and/or boreholes." Section 400.C.1 adds: "The applicant may initiate work ... after the Drilling Permit has been issued and the Zoning Officer has conducted the preliminary inspection of the site." | Section 300: Well Drilling Permit Required; Section 400: Drilling Permits | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Inspection |  |  | Section 402.A provides: "The Zoning Officer shall conduct all inspections required by this Ordinance." Section 402.D states: "A preliminary/pre-construction inspection shall be conducted at the site before any well or borehole drilling is commenced." Section 402.E states: "A final inspection shall be conducted at the site upon the completion of the well drilling and other related processes." Section 400.C.1 also requires work to begin only after "the Zoning Officer has conducted the preliminary inspection of the site." | Section 402: Inspection / Reviews | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Decommissioning |  |  | Section 305 states: "Existing wells that are being replaced that are not grouted with approved grout or do not have a sanitary well cap shall be decommissioned or mitigated in accordance with the Adams County Construction Standards and Material Specifications for Wells & Geothermal Systems." | Section 305: Well Abandonment | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | Township | 4200132200 | Open-loop Prohibitions |  |  | Section 301.B states: "Geothermal wells shall only be constructed as part of Closed-Loop Geothermal systems. Open-Loop Geothermal systems are prohibited." | Section 301: Geothermal Wells | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop - a geothermal heat exchanger that circulates a nontoxic antifreeze heat transfer fluid through a loop or multiple loops of polyethylene piping installed below the ground surface or within a surface water body." | SECTION 8 - GEOTHERMAL WELLS - Geothermal Heat Pump Systems (GHPS), A. DEFINITION | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Driveways | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Property lines, driveways, all right-of- ways, easements" at "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Right of Way | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Property lines, driveways, all right-of- ways, easements" at "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Property Lines | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Property lines, driveways, all right-of- ways, easements" at "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Building Foundation | 20 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Principal structure/dwelling" at "20 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Wastewater | 100 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists wastewater-related setbacks including "Subsurface sewage absorption areas elevated sand mounds, cesspools, sewage seepage pits" - "100 feet"; "Spray irrigation site perimeter, sewage sludge and seepage disposal sites" - "100 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, privies, holding tanks" - "50 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Fuel (above ground) | 150 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Surface or subsurface containers or tanks of greater than 1000 gallons used for storage of materials that cannot be properly renovated by passage through soil... includ[ing] gasoline and all other petroleum products" at "150 feet," and also lists smaller tanks at 30 feet. | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Sewer Lines | 50 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Sewer drains, public sewer laterals" at "50 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Water Bodies | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" at a "MINIMUM DISTANCE" of "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Setback - Hazardous Materials/Fertilizers | 150 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles" at "150 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Permit |  |  | Section 106 provides: "No construction, drilling, or digging for any well/water supply for the production of water for any purposes shall commence unless the property owner... has obtained a well permit." Section 8.B.2 adds that for closed-loop boreholes, "Any proposed deviation from the isolation distances prescribed in section 104 must be approved in writing by the Township, or his designee, with reasons stated for such deviation." | SECTION 106 - REGISTRATION; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Inspection |  |  | Section 8.B.3(d): "Pressure testing is required with water at 100 psi for 30 minutes with no leaks observed." Section 107 states that upon a permit application, the Township representative shall "perform an inspection of the premises on which the well is to be constructed." | SECTION 8 - GEOTHERMAL WELLS - B.3. CONSTRUCTION; SECTION 107 - INSPECTION | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Certification |  |  | Section 8.B.3(b): "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." Section 5.B also states water testing must be conducted "by a certified laboratory." | SECTION 8 - GEOTHERMAL WELLS - B.3. CONSTRUCTION; SECTION 5 WELL CERTIFICATION, B. Water Quality | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Decommissioning |  |  | "Wells, cisterns and water storage tanks, which are no longer in use, shall be removed, filled or otherwise maintained in a condition such as to prevent access... and to effectively prevent pollution of groundwater. Abandoned wells or wells with no future planned use... shall be tremie grouted from the bottom up in one continuous operation using cement with five percent (5%) bentonite grout or other DEP-approved method." | SECTION 7 - ABANDONED WATER SUPPLIES | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | Township | 4200134424 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be allowed in Highland Township." | SECTION 8 - GEOTHERMAL WELLS - Geothermal Heat Pump Systems (GHPS), B.1. ALLOWED SYSTEMS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Definition: Well |  |  | The ordinance defines "Heat exchange well" as "a well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | §26-104.I(1) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Definition: Geothermal Heat Pump |  |  | The ordinance defines geothermal heat pump system types: "Closed-loop–a geothermal heat exchanger that circulates a nontoxic antifreeze heat transfer fluid through a loop or multiple loops of polyethylene piping installed below the ground surface or within a surface water body"; "Direct exchange–a type of closed-loop heat exchanger that uses loops of copper tubing installed in pits, trenches or vertical borings in the earth, through which a refrigerant is circulated"; and "Open-loop–a geothermal heat exchanger that withdraws groundwater from a supply well, passes the groundwater through a heat pump, and discharges the temperature-altered water back either to the ground in a discharge (return) well or to the ground surface or into surface water." | §26-104.I(1) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Right of Way | 10 | feet | For closed-loop boreholes, the ordinance requires under miscellaneous sources: "Property lines, all right-of-ways, easements. 10 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Property Lines | 10 | feet | For closed-loop boreholes, the ordinance requires under miscellaneous sources: "Property lines, all right-of-ways, easements. 10 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Wastewater | 100 | feet | For closed-loop boreholes, the ordinance requires minimum isolation distances from sewage-related sources: "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits. 100 feet"; "Spray irrigation site perimeter, sewage sludge and seepage disposal sites. 50 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks. 50 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Fuel (above ground) | 300 | feet | For closed-loop boreholes, the ordinance states: "Surface or subsurface containers or tanks of greater than 1000 gal. used for storage of materials that cannot be properly renovated by passage through soil. This includes, but is not limited to, gasoline and all other petroleum products. ... 300 feet" and "...containers or tanks of 1000 gal. or less... This includes, but is not limited to, gasoline and all other petroleum products... 100 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Sewer Lines | 5 | feet | For closed-loop boreholes, the ordinance lists under sewage-related sources: "Sewer drains, public sewer laterals. 5 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Water Bodies | 50 | feet | For closed-loop boreholes, the ordinance states: "Minimum isolation distances from the proposed Closed-Loop Borehole... Delineated wetlands, flood plains, lakes, ponds, or other surface waters. 50 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop boreholes, the ordinance requires: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles. 300 feet"; and "Surface or subsurface containers or tanks of greater than 1000 gal. used for storage of materials that cannot be properly renovated by passage through soil... 300 feet." It also lists "Identified NPL Site (Superfund Sites) plume area. 300 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Permit |  |  | For closed-loop systems, the ordinance provides: "Closed-Loop Geothermal Boreholes shall be permitted in accordance with paragraph .I(3). Each borehole must be permitted using a single application. A fee shall be charged for each borehole." | §26-104.I(2)(c)1) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Inspection |  |  | The ordinance states: "The Inspection Officer or designated Township employee shall be responsible for insuring that the borehole is drilled in the permitted location" and also requires "Pressure testing ... with water at 100 psi for 30 minutes with no leaks observed. Evidence of testing from the installer must be provided to the Township." | §26-104.I(2)(b)2); §26-104.I(2)(b)7) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Certification |  |  | The ordinance states: "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer. The well contractor shall be responsible for insuring that the pipe loop is installed in accordance with the specifications of the ground source heat pump system manufacturer, the International Ground Source Heat Pump Association, National Groundwater Association, the pipe manufacturer..." | §26-104.I(2)(b)4) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | Township | 4200163616 | Decommissioning |  |  | The ordinance provides: "Wells, springs, cisterns and water storage tanks, which are no longer in use, shall be removed, filled or otherwise maintained..." and specifically, "Abandoned wells shall be tremie grouted from the bottom up in one continuous operation using cement with 5 percent bentonite grout or other DEP-approved method." It also states: "The Township shall also be given the opportunity to conduct an inspection at the time of abandonment of a well/water supply." | §26-104.G; §26-108.3 | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Allegheny | Brentwood | Borough | 4200308416 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 210-9 Definitions | 2026 | https://ecode360.com/29424067
Pennsylvania | Allegheny | Brentwood | Borough | 4200308416 | Minimum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM ... A horizontal closed loop system shall be no more than 20 feet deep." | § 210-9 Definitions | 2026 | https://ecode360.com/29424067
Pennsylvania | Allegheny | Heidelberg | Borough | 4200333592 | Setback - Property Lines | 10 | feet | "Geothermal energy facilities shall meet the accessory structure setbacks that may apply in the zoning district within which the facility is constructed, and where no such setback is specified, the facility shall be no closer than 10 feet from any property line." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | Heidelberg | Borough | 4200333592 | Permit |  |  | "Accessory geothermal energy facilities shall be permitted by conditional use in the M - Manufacturing Zoning District." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | Heidelberg | Borough | 4200333592 | Screening |  |  | "Required landscape buffering may be modified so that tall tree species may be replaced with lower-growing tree species where the required tree species may interfere with the functioning of the geothermal energy facility..." and "Secure perimeter fencing shall be installed around the geothermal energy facility... The fence shall be supplemented with screening material which creates a visual barrier that is at least 80% opaque." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | Heidelberg | Borough | 4200333592 | Certification |  |  | "A design certification by a certified engineer shall be required, consisting of the proposed foundation design and analysis of soil conditions." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | O'Hara | Township | 4200356384 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY FACILITY - A generating facility capable of capturing and converting hydrothermal energy into hydronic or electrical energy sources." | Section 72-2.1 Strict Construction | 2020 | https://www.ohara.pa.us/sites/g/files/vyhlif6181/f/uploads/zoning_ord_1361.pdf
Pennsylvania | Allegheny | O'Hara | Township | 4200356384 | Setback - Property Lines | 20 | feet | Geothermal accessory-use clauses state: "Geothermal energy facilities shall meet the accessory structure setbacks that may apply in the zoning district within which the facility is constructed and where no such setback is specified, the facility shall be no closer than (10) ten feet from any property line." Separately, the district yard tables set accessory-structure setbacks: CD districts: "Permitted accessory structures shall be located no closer than twenty feet (20') to the side or rear property line" (Section 72-8.7); C district: "Permitted accessory structures shall be located no closer than twenty feet (20') to the side or rear property line" (Section 72-9.5); SM district: "Permitted accessory structures shall be located no closer than twenty feet (20') to the side or rear property line" (Section 72-10.6). | Sections 72-8.7, 72-9.5, and 72-10.6 | 2020 | https://www.ohara.pa.us/sites/g/files/vyhlif6181/f/uploads/zoning_ord_1361.pdf
Pennsylvania | Allegheny | O'Hara | Township | 4200356384 | Permit |  |  | District permit sections provide: "A Zoning/Building permit shall be required prior to the erection, construction or alteration of any structure proposed in relation to those uses enumerated in this Article." Geothermal Energy Facility is enumerated as a permitted accessory use and/or conditional use in the listed district articles. Section 72-1.2 also states: "No building or structure shall be used, located, erected, constructed, altered, enlarged or moved... except in full compliance with all of the provisions of this Ordinance and after the lawful issuance of all permits and certificates required by this Ordinance." | Sections 72-4.8, 72-5.8, 72-6.8, 72-7.8, 72-8.9, 72-9.7, 72-10.8, and Section 72-1.2 | 2020 | https://www.ohara.pa.us/sites/g/files/vyhlif6181/f/uploads/zoning_ord_1361.pdf
Pennsylvania | Allegheny | Pine | Township | 4200360272 | Permit |  |  | "Non-contaminated HVAC condensation and water from geothermal systems" are authorized discharges only under Section 801.C, and Section 801.B states that non-stormwater discharges are prohibited "except ... discharges authorized under a state or federal permit." | Section 801. Prohibited Discharges and Connections | 2018 | https://ecode360.com/PI1032/laws/LF1059482.pdf
Pennsylvania | Allegheny | Plum | Borough | 4200361536 | Definition: Geothermal |  |  | 'RENEWABLE ENERGY SOURCE - Any method, process or substance whose supply is rejuvenated through natural processes and, subject to those natural processes, remains relatively constant, including, but not limited to, biomass conversion, geothermal energy, solar and wind energy and hydroelectric energy and excluding those sources of energy used in the fission and fusion processes.' | RENEWABLE ENERGY SOURCE | 2018 | https://www.plumboro.com/sites/g/files/vyhlif3686/f/pages/plum_zoning_ordinance.pdf
Pennsylvania |  | Adamstown | Borough | 4200364 | Definition: Well |  |  | "GEOTHERMAL BOREHOLE. A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 320-7 Terms defined. | 2026 | https://ecode360.com/31736387
Pennsylvania |  | Adamstown | Borough | 4200364 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy-generating system that uses the earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also defined are system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system... The pipes form a closed loop and are filled with a heat transfer fluid"; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A borehole that extends beneath the surface. Pipes are installed with U-bends at the bottom of the borehole. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes"; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM. Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | § 320-7 Terms defined. | 2026 | https://ecode360.com/31736387
Pennsylvania | Allegheny | Swissvale | Borough | 4200375816 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES – A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 202: Definitions | 2017 | https://swissvaleborough.com/DocumentCenter/View/101/Swissvale-Zoning-Ordinance-2017-PDF
Pennsylvania | Allegheny | Swissvale | Borough | 4200375816 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM – An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM – A mechanism for heat exchange which consists of the following basic elements: underground loops of piping; heat transfer fluid; a heat pump; an air distribution system... The pipes form a closed loop and are filled with a heat transfer fluid..." and "OPEN LOOP GEOTHERMAL SYSTEM – Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | Section 202: Definitions | 2017 | https://swissvaleborough.com/DocumentCenter/View/101/Swissvale-Zoning-Ordinance-2017-PDF
Pennsylvania | Allegheny | Swissvale | Borough | 4200375816 | Maximum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM ... A horizontal closed loop system shall be no more than twenty (20) feet deep." | Section 202: Definitions | 2017 | https://swissvaleborough.com/DocumentCenter/View/101/Swissvale-Zoning-Ordinance-2017-PDF
Pennsylvania | Allegheny | Wilkinsburg | Borough | 4200385188 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES. A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Allegheny | Wilkinsburg | Borough | 4200385188 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy-generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Allegheny | Wilkinsburg | Borough | 4200385188 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A mechanism for heat exchange which consists of the following basic elements: underground loops of piping; heat transfer fluid; a heat pump; an air distribution system. An opening is made in the earth. A series of pipes is installed into the opening and connected to a heat exchange system in the building. The pipes form a closed loop and are filled with a heat transfer fluid. The fluid is circulated through the piping from the opening into the heat exchanger and back. The system functions in the same manner as the open loop system except there is no pumping of groundwater." "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A borehole that extends beneath the surface. Pipes are installed with U-bends at the bottom of the borehole. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." "OPEN LOOP GEOTHERMAL SYSTEM. Water is pumped from a water well or other water source into a heat exchanger located in a surface building. The water drawn from the Earth is then pumped back into the ground through a different well or in some cases the same well, also known as 'reinjection.' Alternatively, the groundwater could be discharged to a surface water body also known as a 'pump and dump.' In the heating mode, cooler water is returned to the Earth, and in the cooling mode, warmer water is returned to the surface water body or well." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Allegheny | Wilkinsburg | Borough | 4200385188 | Maximum Well Depth | 20 | feet | In the definition of "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM," the ordinance states: "A horizontal closed loop system shall be no more than 20 feet deep." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Lancaster | Akron | Borough | 4200540 | Setback - Right of Way | 25 | feet | "All systems shall be set back a minimum of twenty-five (25) feet from any property line or right-of-way line and a minimum of one hundred (100) feet from any potable water supply wells." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | Borough | 4200540 | Setback - Property Lines | 25 | feet | "All systems shall be set back a minimum of twenty-five (25) feet from any property line or right-of-way line and a minimum of one hundred (100) feet from any potable water supply wells." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | Borough | 4200540 | Setback - Public Water | 100 | feet | "All systems shall be set back a minimum of twenty-five (25) feet from any property line or right-of-way line and a minimum of one hundred (100) feet from any potable water supply wells." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | Borough | 4200540 | Permit |  |  | "Manufacturer specifications shall be submitted as part of any building or zoning application." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | Borough | 4200540 | Open-loop Prohibitions |  |  | "Geothermal heat pumps are permitted in all zoning districts as an accessory use under the following conditions: 1. Open-loop systems shall not be permitted." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | §27-202. Definitions | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system..."; "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a water-supply well, or other source, and a pump to deliver groundwater to a heat exchanger." | §27-202. Definitions | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, Geothermal Energy Systems shall be set back a minimum distance of twenty-five (25) feet from any property line." | §27-1630.A.(3)(e) Setback Requirements | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Setback - Wastewater | 100 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 100 feet from on-lot sewage disposal systems." | §27-1630.A.(3)(e) Setback Requirements | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Maximum Well Depth | 20 | feet | "All closed horizontal loop systems shall be no more than twenty (20) feet deep." | §27-1630.A.(3)(f) Closed-loop Geothermal Systems | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Permit |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to all applicable industry standards... The manufacturer specifications shall be submitted as part of the application. A zoning permit and building permit, under the PA Uniform Construction Code, shall be required." | §27-1630.A.(3)(a) Design and Permitting | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Decommissioning |  |  | "If the Geothermal Energy System is ever abandoned or enters into a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the Geothermal Energy System within six (6) months from the date the system enters such a state." "Any earth disturbance as a result of the removal or permanent sealing of the Geothermal Energy System shall be graded and reseeded." | §27-1630.A.(3)(h)-(i) | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | Township | 4201156672 | Other Prohibitions/Regulations |  |  | "Only the following types of Geothermal Energy Systems shall be permitted: i. Closed horizontal loop; ii. Closed vertical loop; and, iii. Open horizontal loop systems relying upon injection wells or watercourses." "Extraction of water from surface waters shall be prohibited." "Discharge of water from open-loop systems into sanitary sewer systems shall be prohibited." "Discharge of water from open-loop systems into storm sewers, and onto roads, shall be prohibited." "Discharge of water from open-loop systems into a watercourse shall be prohibited." | §27-1630.A.(3)(b), §27-1630.A.(3)(g)(i)-(ii) | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Reading | City | 4201163624 | Setback - Roads | 1.1 | structure-height-multiplier | "All alternative energy systems and/or any appurtenant structures shall be set back from all public roads a distance of not less than 1.1 times the alternative energy system's height... to the right-of-way line of all public roads." | § 600-1012 D(5) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | City | 4201163624 | Permit |  |  | "No alternative energy system shall be located, modified or constructed within the City of Reading unless a permit has been issued to the facility owner in accordance with the provisions of this section of the Zoning Ordinance." The same installation rule is repeated in § 600-1012 J(1)(a). Geothermal heat pumps are included as alternative energy systems in § 600-1012 B. | § 600-1012 D(6); J(1)(a) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | City | 4201163624 | Certification |  |  | "For alternative energy system categories in which installer certification exists, a certified installer shall be required for more complex installations, nonresidential installations, or if recommended by the manufacturer." | § 600-1012 J(1)(b) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | City | 4201163624 | Decommissioning |  |  | "The facility owner or operator shall, at his/her expense, completely remove any alternative energy system within 12 months after the end of its useful life." The system "will be presumed to be at the end of its useful life if no energy is generated for a continuous period of 12 months." If the owner fails to remove it, "the City may take such measures as necessary to complete removal ... at the expense of the facility owner and operator." | § 600-1012 J(5)(a)-(b) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | City | 4201163624 | Other Prohibitions/Regulations |  |  | "The geothermal heat pump may not be in contact with an aquifer or be sited within any aquifer's recharge zone." | § 600-1012 F(2)(c) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 10 feet from any property line." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Noise Limits | 50 | dBA | § 27-620 states: "No continuous noise in excess of the following limits shall be permitted at the property line of the site on which the noise sources originates," including "R-1 and R-2 Residential Zoning Districts ... 50 dBA" for "8:00 p.m. to 6:00 a.m." It also lists other limits: R-1/R-2 "55 dBA" daytime; R-3 "60 dBA" daytime and "55 dBA" nighttime; Commercial/L-C/Industrial "60 dBA" daytime and "55 dBA" nighttime. § 27-624 makes geothermal heating systems a permitted accessory use and subjects them to Borough requirements: "The design and installation of geothermal systems ... shall ... comply with ... all other applicable federal, state and Borough requirements." | § 27-620 Environmental Performance Standards for Nonresidential Uses; § 27-624 Alternative Energy Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Maximum Well Depth | 40 | feet | Under "For closed-loop systems, the following shall apply": "All horizontal closed-loop systems shall be no more than 40 feet deep." The same section repeats under "Height and Setback Restrictions": "All horizontal closed-loop systems shall be no more than 40 feet deep." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Permit |  |  | The abandonment provision states: "The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained... The heat pump and any external mechanical equipment shall be removed. Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | Borough | 4201170248 | Open-loop Prohibitions |  |  | Under geothermal heating systems: "Only the following types of geothermal energy systems shall be permitted: Closed horizontal loop. Closed vertical loop. Open-loop systems are not permitted within the Borough." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Spring | Township | 4201172824 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, ACCESSORY - a sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes, but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop." | Section 202. Definitions | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | Township | 4201172824 | Minimum Well Depth | 20 | feet | "All wells serving geothermal heating and/or cooling systems shall be equipped with watertight and durable casing pipe. The casing shall be carried to a minimum depth of 20 feet and grouted in place." Also, "Boreholes must be grouted from a minimum depth of 20 feet below grade to the ground surface with an approved grout." | Section 327(C)(5)(e)-(f) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | Township | 4201172824 | Certification |  |  | "Geothermal energy systems shall conform to the applicable industry standards including those of the American National Standards Institute (ANSI). Applicants shall submit certificates of compliance demonstrating that the system has been tested and approved by Underwriters Laboratories (UL) or other approved independent testing agency." | Section 327(C)(5)(c) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | Township | 4201172824 | Open-loop Prohibitions |  |  | "No person shall install an open loop geothermal system. It shall be permissible to operate an open loop geothermal system provided that such unit was legally installed on the property prior to the enactment of this Ordinance". | Section 327(C)(5)(b) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | Township | 4201172824 | Other Prohibitions/Regulations |  |  | "Equipment, piping and devices shall not be located within any easement or right-of-way." | Section 327(C)(5)(d)(2) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | West Reading | Borough | 4201183928 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of 10 feet from any property line." | § 455-168 Alternative energy systems, D(2)(b) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | Borough | 4201183928 | Maximum Well Depth | 40 | feet | "All horizontal closed-loop systems shall be no more than 40 feet deep." The same limit is repeated under height and setback restrictions: "All horizontal closed-loop systems shall be no more than 40 feet deep." | § 455-168 Alternative energy systems, D(1)(d)[2] and D(2)(a) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | Borough | 4201183928 | Permit |  |  | "Geothermal heating systems shall be permitted as an accessory use in all zoning districts and shall be subject to the following regulations"; for multi-property systems, "there shall be documentation provided to the Borough showing that the parties are in agreement to the removal of the system." The abandonment section also states: "The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained." | § 455-168 Alternative energy systems, D. Geothermal heating systems | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | Borough | 4201183928 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | § 455-168 Alternative energy systems, D(1)(c) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | Borough | 4201183928 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." Removal must include: "The heat pump and any external mechanical equipment shall be removed" and "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 455-168 Alternative energy systems, D(3) Abandonment | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | Borough | 4201183928 | Open-loop Prohibitions |  |  | "Open-loop systems are not permitted within the Borough." | § 455-168 Alternative energy systems, D(1)(b) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | Wyomissing | Borough | 4201186880 | Permit |  |  | "3.10 Mechanical Permits (new or replacement heaters, furnaces, boilers, H20 heaters, fuel burning appliances, a/c units, exhaust systems, and geothermal/solar-thermal mechanical systems)" and "Miscellaneous Mechanical Fee... $150.00 PA $4.50." | 3.10 Mechanical Permits | 2025 | https://wyomissingboro.org/DocumentCenter/View/523
Pennsylvania | Bucks |  | County | 42017 | Definition: Well |  |  | "Geothermal well - Any well or borehole in the ground constructed for the purpose of extracting heat from or transferring heat to the ground or groundwater. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes." | SECTION ONE - GENERAL PROVISIONS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump Equipment - Any components of a heating or cooling system in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | SECTION ONE - GENERAL PROVISIONS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Driveways | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. The note adds: "Closed loop geothermal systems and monitoring wells do not have to meet isolation distance for driveways." | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Right of Way | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Property Lines | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Building Foundation | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Wastewater | 50 | feet | The isolation distance table requires setbacks from wastewater-related sources, including "Community spray irrigation sites, sewage sludge and septage disposal sites" at "100*" feet; "All sewage absorption areas including cesspools and seepage pits" at "100*" feet; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks" at "50*" feet. Note: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." This yields 50 feet from the 100* wastewater sources for closed-loop systems, which is the most restrictive closed-loop wastewater setback stated. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Private Water | 50 | feet | Section 8.2(a): "To prevent thermal degradation, the withdraw and return wells must be a minimum of 50 feet apart." | SECTION EIGHT - GEOTHERMAL WELLS, 8.2 Open-Loop Geothermal HVAC Systems | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Animal Enclosures | 100 | feet | The isolation distance table lists "Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure" at "200*" feet, and notes: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Sewer Lines | 25 | feet | The isolation distance table includes sewer-line setbacks: "Gravity sewer lines and drains carrying domestic sewage or industrial waste (unless item 9 applies)" at "50*" feet; "Gravity sewer lines and drains using cast iron pipe with watertight lead caulked or neoprene gasketed joints, or Schedule 40 polyvinyl chloride (PVC) pipe with solvent welded joints" at "10" feet; "Sewer lines and drains carrying domestic sewage or industrial waste under pressure constructed of welded steel pipe or concrete encased pipe" at "10" feet; and "Sewer lines and drains carrying domestic sewage or industrial waste under pressure using material other than items in #10" at "50*" feet. Note: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." This makes the controlling most restrictive closed-loop sewer-line setback 25 feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Pools | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Water Bodies | 25 | feet | The isolation distance table lists "Delineated wetlands or 100-year floodplain" at "25" feet, with note: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." Because this row is not marked with an asterisk, the 25-foot isolation distance remains applicable. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Setback - Hazardous Materials/Fertilizers | 150 | feet | The isolation distance table sets "Commercial preparation area or storage area of hazardous spray materials, fertilizers, or chemicals; salt piles" at "300*" feet. The note provides: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Permit |  |  | Section 3.1(a): "It shall be unlawful to install a new well or geothermal borehole or modify an existing well without an approved well permit and submission of appropriate fees." Section 3.1(c): "The BCDH must field verify the location of the proposed wells and all applicable isolation distances as outlined in Section 4 of these regulations." Section 8.1(b): "The proposed system design must be submitted and approved by the Department prior to installation. Isolation distances according to Section 4.1 must be confirmed." Section 8.2(d): "The person requesting a geothermal permit from the Department is required to submit proof of an NPDES permit or exemption with any application." | SECTION THREE - APPLICATION TO CONSTRUCT OR MODIFY; SECTION EIGHT - GEOTHERMAL WELLS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Inspection |  |  | Section 6.2(b): "A BCDH representative is to be on site to observe the grouting of the well or borehole and any other inspections deemed necessary." Section 6.5(a): "A BCDH representative is to be on site to observe grouting of the well or borehole and any other inspection during the well construction deemed necessary." Section 6.5(b): "A BCDH representative is to be on-site to observe a 30-minute pressure test as specified in section 8.3." | SECTION SIX - INSPECTION | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Licensed Driller |  |  | Section 7.1(a): "Only well drillers with a PA DCNR license shall be permitted to construct drinking water wells, geothermal wells, test wells and monitoring wells. Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation." Section 8.2(b): "Only PA DCNR approved well drillers using PA DCNR approved well drilling rigs shall drill the withdraw and return flow wells for this type of system." | SECTION SEVEN - WELL DRILLERS; SECTION EIGHT - GEOTHERMAL WELLS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Screening |  |  | Section 8.3(c)(2): "Trench System - A minimum of 6 inches of sand or screenings is to be added to the bottom of the trench to prevent the loop piping from rubbing on stones." | SECTION EIGHT - GEOTHERMAL WELLS, 8.3 Closed-Loop Geothermal Systems | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Certification |  |  | Definition of Well Driller: "A person who is licensed by the state of Pennsylvania to drill wells, or in the case of geothermal wells has IGSHPA certification." Section 7.1(a): "Only well drillers with a PA DCNR license shall be permitted to construct ... geothermal wells ... Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation." Section 8.1(a): "Installation must be by a PA DCNR approved well driller or IGSHPA accredited geothermal system installer." Section 8.3(a)-(b): "Installation must be by a PA DCNR approved well driller or IGSHPA accredited geothermal system installer" and "The system design shall be made by an IGSHPA accredited person or firm or an engineering firm familiar with loading and heat transfer requirements..." | SECTION ONE - GENERAL PROVISIONS; SECTION SEVEN - WELL DRILLERS; SECTION EIGHT - GEOTHERMAL WELLS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks |  | County | 42017 | Decommissioning |  |  | Section 12.1(a)-(d): "A well permit must be obtained prior to abandoning all wells." "Only a PA DCNR licensed well driller is permitted to abandon a well." "Abandonment procedures shall be subject to the BCDH inspection." "Well abandonment procedures must minimally comply with the specifications referenced in the PA DEP/DCNR Water Well Abandonment Guidelines." Section 12.2(a): "The borehole must be cleared of obstructions prior to abandonment. Pumps, pipes, wiring, and air lines must be removed if possible... If the casing cannot be removed, it should be cut below the land surface." | SECTION TWELVE - WELL ABANDONMENT | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | Doylestown | Borough | 4201719784 | Definition: Well |  |  | "GEOTHERMAL WELL — Any well or borehole in the ground constructed for the purpose of extracting heat from or transferring heat to the ground or groundwater. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes." | § 202 Definitions | 2011 | https://ecode360.com/16053299
Pennsylvania | Bucks | Doylestown | Borough | 4201719784 | Permit |  |  | "it shall be unlawful for any person to locate, drill or have drilled any ... geothermal well ... or to alter an existing ... geothermal well ... until a permit for such location, drilling, installation or alteration shall have been issued by the Borough Manager of the Borough of Doylestown." | § 203 Permits | 2011 | https://ecode360.com/16053299
Pennsylvania | Bucks | Doylestown | Borough | 4201719784 | Licensed Driller |  |  | "All wells drilled within the Borough of Doylestown must be drilled by a well driller licensed by the Commonwealth of Pennsylvania." | § 204 Application and Forms | 2011 | https://ecode360.com/16053299
Pennsylvania | Bucks | Dublin | Borough | 4201720104 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM - a system that uses a heat pump to extract heat from the earth in heating mode and/ or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, a ground source heat pump system (GSHP) and a GeoExchange® system." | Section 1; Section 3-103. Definitions | 2025 | https://ecode360.com/DU3825/laws/LF2318336.pdf
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Definition: Geothermal Heat Pump |  |  | "GROUND-SOURCE HEAT PUMP SYSTEM (Also known as 'geothermal energy system') — A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; an approved fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air-distribution system. Open-loop ground-source heat pump systems are not permitted in East Rockhill Township." | § 13-403 Definitions | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Setback - Right of Way | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines and rights-of-way." | § 13-406(C)(3) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Setback - Property Lines | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines and rights-of-way." | § 13-406(C)(3) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Setback - Building Foundation | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (4) Twenty-five feet from existing or proposed structures." | § 13-406(C)(4) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Setback - Wastewater | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (2) Twenty-five feet from any existing or proposed individual or community on-lot sewage disposal system, including any primary or alternate drainfield sites." | § 13-406(C)(2) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Setback - Private Water | 100 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (1) One hundred feet from any existing or proposed drinking water wells." | § 13-406(C)(1) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Minimum Well Depth | 2.5 | feet | "The depth of the tubing or heat transfer element must be at least 30 inches below the surface of the ground." | § 13-406(J) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Permit |  |  | "No person shall: (1) construct or install a GSHP; (2) dig, bore, drill, replace, modify, repair and/or destroy a well that is, is intended to be, or was part of a GSHP; or (3) make any other excavation that may intersect groundwater without first applying for and obtaining the appropriate permit from the Township and paying the requisite permit fee in full. A permit is required for any GSHP within East Rockhill Township." It also states: "Application for a permit for the drilling of a well and/or the installation and/or construction of a GSHP shall be made to the Township Code Enforcement Officer." | § 13-406(A) Geothermal Energy Systems | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Inspection |  |  | Section E requires "A written plan ... provide for the operation and periodic inspection of the GSHP system." Section I requires prior to activation "written documentation of the GSHP system testing and certification." Section L states: "The owner of the GSHP shall submit an annual inspection report certifying the integrity of the system." In addition, § 13-409 provides: "The Building Inspector and/or Code Enforcement Officer, or other designated Township representative, shall require the proper maintenance and use of all alternative energy systems and will inspect every alternative energy system for which a permit is required within 10 days after work is completed on the alternative energy system." | § 13-406(E), § 13-406(I), § 13-406(L), § 13-409 | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Licensed Driller |  |  | "GSHP well drilling shall only be undertaken by a Pennsylvania-licensed well driller." | § 13-406(G) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Certification |  |  | Section D(1) states: "All joints shall be sealed by heat fusion or IGSHPA-certified process." Section I(4) requires prior to activation: "Written documentation of the GSHP system testing and certification." | § 13-406(D)(1); § 13-406(I)(4) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Decommissioning |  |  | § 13-406(E)(2) requires "A system closure plan for use in the event of the discontinuance of the use of the GSHP system." More generally, § 13-408 states: "If an alternative energy system remains nonfunctional or inoperative for a continuous period of six months, the system shall be deemed to be abandoned and constitute a public nuisance and shall thereafter be removed by the property owner." It further requires: "The alternative energy system owner, at his/her sole expense, shall complete decommissioning of the system within six months after the end of the useful life of the system, or within six months of damage which prevents the system from operating in a safe manner at full capacity or according to industry standards." "The owner shall remove the abandoned and/or decommissioned system after a demolition or other requisite permit has been obtained from the Township. Removal includes the entire structure, including foundations to below natural grade, external mechanical equipment and transmission equipment." | § 13-406(E)(2); § 13-408 | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Open-loop Prohibitions |  |  | "Closed-loop systems are permitted within East Rockhill Township with the appropriate permit. Open-loop systems are not permitted in East Rockhill Township." Section A repeats: "Only closed-loop systems are permitted within East Rockhill Township. No open-loop system shall be permitted within East Rockhill Township." | § 13-406 Geothermal Energy Systems | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | Township | 4201721760 | Other Prohibitions/Regulations |  |  | "Ground-source heat pump systems shall not encroach on public drainage and/or stormwater, utility, roadway or trail easements." | § 13-406(K) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | Lower Southampton | Township | 4201745112 | Permit |  |  | The fee schedule expressly lists a geothermal-specific permit charge under plumbing permits: "4. Well installation ... c) Geothermal unit (each) $150.00" and also states generally, "PERMIT FEES MAY BE DOUBLED FOR FAILURE TO PULL PERMITS." | PART 3 - PLUMBING PERMITS | 2024 | https://lowersouthamptontownship.org/wp-content/uploads/2024/04/2024-LSTWP-Fee-Schedule-April-10-revised.pdf
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY. A renewable source of energy generated from solar, water, wind, geothermal, or similar sources, which is capable of providing energy and utility provisions to a permitted use." | § 500-202, Specific terms | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." Also: "GROUND SOURCE HEAT PUMP. A geothermal heat pump that uses the earth itself as a heat source and heat sink. It is coupled to the ground by means of a closed-loop heat exchanger installed horizontally or vertically underground." | § 500-202, Specific terms | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Right of Way | 10 | feet | Table 1 states: "Dedicated public right-of-way and property lines — 10 feet." Section 500-2903.C.9 provides that wells and boreholes regulated by the ordinance must use the minimum isolation distances listed in Table 1. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Property Lines | 10 | feet | Table 1 states: "Dedicated public right-of-way and property lines — 10 feet." Section 500-2903.C.9 provides that wells and boreholes regulated by the ordinance must use the minimum isolation distances listed in Table 1. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Building Foundation | 10 | feet | Table 1 states: "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved) — 10 feet." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Wastewater | 50 | feet | Table 1 includes multiple wastewater setbacks: "Septic tanks, aerobic tanks, or holding tanks — 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields — 50 feet"; "Sewage seepage pits and cesspools — 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites — 25 feet." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Animal Enclosures | 25 | feet | Table 1 states: "Farm silos, barnyards, privies, and fuel tanks — 25 feet." Section 500-2903.C.9 applies Table 1 to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Fuel (above ground) | 25 | feet | Table 1 states: "Farm silos, barnyards, privies, and fuel tanks — 25 feet." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Water Lines | 15 | feet | Table 1 states: "Existing water and forced sewer buried utilities and/or utility trenches — 15 feet or outside easement." Section 500-2903.C.9 applies these Table 1 isolation distances to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Sewer Lines | 15 | feet | Table 1 states: "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 15 feet or according to easement." It also states: "Existing water and forced sewer buried utilities and/or utility trenches — 15 feet or outside easement." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Water Bodies | 25 | feet | Table 1 states: "Delineated wetlands, flood plains, lakes, ponds, or other surface waters — 25 feet." Section 500-2903.C.9 makes Table 1's minimum isolation distances applicable to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table 1 states: "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles — 300 feet; 150 feet (if borehole is cased and grouted inside and out)." Section 500-2903.C.9 applies Table 1 to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Noise Limits | 55 | dBA | "Audible sound from any alternative and/or emerging energy facility shall not exceed 55 dBA, as measured at the applicant's property line. Middletown Township has the right to inspect, measure, and record sound levels at the applicant's expense." | § 500-2903.G.1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." Also: "No alternative or emerging energy facility shall be located, modified, or constructed within Middletown Township unless a permit has been issued to the landowner in accordance with the provisions of this Section." | § 500-2903.C; § 500-2906.A | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Inspection |  |  | § 500-2907.B: "The landowner shall consult with a qualified inspector every 12 months to determine if the alternative and emerging energy facility is operating in accordance with the specifications of the manufacturer. A copy of the report shall be submitted to Middletown Township, and Middletown Township shall have the right to inspect." § 500-2910.B: "Middletown Township reserves the right to inspect an alternative or emerging energy system, at any time, if the system appears inoperable, or constitutes a danger to life or property." § 500-2903.G.1: "Middletown Township has the right to inspect, measure, and record sound levels at the applicant's expense." | § 500-2907.B; § 500-2910.B; § 500-2903.G.1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well. In all cases, the well drilling rig must also be approved by the Pennsylvania Department of Environmental Protection." | § 500-2903.C.7 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well." | § 500-2903.C.7 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Decommissioning |  |  | § 500-2903.C.6 states: "The geothermal system must be installed, maintained, and decommissioned in conformance with the IGSHPA Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards..." Section 500-2909 further provides: "The landowner or energy facility operator shall, at its expense, complete decommissioning of the alternative or emerging energy facility within 12 months after the end of the useful life of the alternative and emerging system" and "All disturbed earth shall be restored, graded, and reseeded." | § 500-2903.C.6; § 500-2909 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | Township | 4201749120 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems are prohibited." | § 500-2903.C.3 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Milford | Township | 4201749384 | Permit |  |  | "Geothermal wells shall be allowed in open space where approved by the Board of Supervisors." | Section 251 - Open Space | 2019 | https://milfordtownship.org/wp-content/uploads/2020/05/ord_174_AMU-Amendment.pdf
Pennsylvania | Bucks | Newtown | Borough | 4201754184 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Geothermal System. A heating and/or cooling system that utilizes the earth's thermal energy to heat and/or cool a building through the use of a series of underground pipes." | Part 6 - Building Permits, H. Closed Loop Geothermal System | 2022 | https://www.boroughofnewtown.com/media/2023%20Fee%20Schedule.pdf
Pennsylvania | Bucks | Newtown | Borough | 4201754184 | Permit |  |  | Part 6 states building permit fees apply, and "all fees referenced within this part shall be doubled if the project is started without the applicable permits and/or approvals." The fee schedule specifically lists "Closed Loop Geothermal System" with "Fee is $350." Part 1.E also states: "The applicant assumes all risks for any actions taken by the applicant prior to the issuance of an appropriate permit for which an application has been made." | Part 6 - Building Permits; Part 1 - General Provisions; Part 6 - Building Permits, H. Closed Loop Geothermal System | 2022 | https://www.boroughofnewtown.com/media/2023%20Fee%20Schedule.pdf
Pennsylvania | Bucks | Nockamixon | Township | 4201754576 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM (also known as 'GEOTHERMAL ENERGY SYSTEM') A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; an approved fluid that absorbs and transfers heat; a heat pump unit that processes heat for use or disperses heat for cooling; and an air-distribution system. Open-loop ground source heat pump systems are not permitted in Nockamixon Township." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Nockamixon | Township | 4201754576 | Maximum Well Depth | 20 | feet | "HORIZONTAL GROUND SOURCE HEAT PUMP SYSTEM A closed-loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Nockamixon | Township | 4201754576 | Certification |  |  | "HEAT TRANSFER FLUID A Township-approved nontoxic and food-grade fluid..." and the closed-loop definition states: "A system that circulates an approved heat transfer fluid through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Nockamixon | Township | 4201754576 | Open-loop Prohibitions |  |  | The ordinance expressly states in the GHP definition and again in the open-loop definition: "Open-loop ground source heat pump systems are not permitted in Nockamixon Township." The open-loop definition further describes such a system as one that "uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Definition: Well |  |  | 'Geothermal well - Any well or borehole in the ground constructed for the purpose of extracting heat from or transferring heat to the ground or groundwater. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes.' | SECTION TWO - DEFINITIONS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Definition: Geothermal Heat Pump |  |  | 'Open-Loop Geo-Thermal System-These systems draw groundwater from a source well, to a heat exchanger, and then discharge the water via injection wells or return flow wells.' Also: 'Ground Source Heat Pump Equipment Any components of a heating or cooling system in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems.' | SECTION TWO - DEFINITIONS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Setback - Wastewater | 100 | feet | Section 4.1 requires minimum isolation distances. The table lists wastewater-related sources including 'Community spray irrigation sites, sewage sludge and septage disposal sites' and 'Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits, single family spray irrigation system, etc.' at 100 feet, and 'Septic tanks, aerobic tanks, sewage pump tanks, holding tanks.' at 50 feet. The note states: 'Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above.' The application form likewise notes: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Setback - Animal Enclosures | 100 | feet | The Section 4.1 isolation-distance table includes 'Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure.' The application-form table gives this distance as 200 feet and notes: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Setback - Sewer Lines | 50 | feet | The Section 4.1 table lists 'Gravity sewer lines and drains carrying domestic sewage or industrial waste (unless item 9 applies)' and 'Sewer lines and drains carrying domestic sewage or industrial waste under pressure (except welded steel pipe or concrete encased pipe).' The application-form table gives these distances as 50 feet, with a narrower 10-foot case for specified gravity sewage lines using certain pipe materials. The note states: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Setback - Water Bodies | 12.5 | feet | Section 4.1 states: 'For all wells, minimum isolation distances shall be maintained...' The table lists 'Delineated wetlands or 100-year floodplain' at 25 feet, and the note provides: 'Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above.' The application form separately states: 'Note: Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *' for starred items only, but in the adopted regulations table the wetland/floodplain row is listed among isolation distances for all wells at 25 feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Setback - Hazardous Materials/Fertilizers | 150 | feet | Section 4.1's table includes 'Commercial preparation area or storage area of hazardous spray materials, fertilizers or chemicals; salt piles.' The application-form table gives this isolation distance as 300 feet and notes: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Minimum Well Depth | 30 | feet | Section 4.2(a) states: 'The casing shall be carried to a minimum depth of (30) feet and (5) feet into hard bedrock or other impervious strata, whichever is deeper, and grouted in place.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / 4.2 Casing | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Permit |  |  | Section 7.1(b): 'The proposed system design must be submitted and approved by the Department prior to installation. Isolation distances according to Section 4.1 must be confirmed.' Section 7.3(b): 'The proposed system design must be submitted to and approved by the Department prior to construction.' Section 7.2(d): 'The person requesting a geothermal permit from the Department is required to submit proof of an NPDES permit or exemption with any application.' | SECTION SEVEN GEO-THERMAL WELLS / SECTION THREE - APPLICATION TO CONSTRUCT OR MODIFY | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Inspection |  |  | Section 5.2(a): 'A BCDH representative is to be on site to observe the installation of the well casing,' Section 5.2(b): 'A BCDH representative is to be on-site to observe the grouting of the well and any other inspection during the well construction.' Section 7.3(c): 'Prior to construction, a site meeting with the Department will be required to layout the proposed design under actual field conditions.' Also, 'The system must be pressure tested prior to backfilling or grouting but after flushing the pipe to remove debris.' | SECTION FIVE - INSPECTION / SECTION SEVEN GEO-THERMAL WELLS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Licensed Driller |  |  | Section 6.1(a): 'Only well drillers with a PA DCNR license shall be permitted to construct individual residential water supply wells. Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation.' Section 7.2(b): 'Only PA DCNR approved well drillers using PA DCNR approved well drilling rigs shall drill the withdraw and return flow wells for this type of system.' | SECTION SIX - WELL DRILLERS / SECTION SEVEN GEO-THERMAL WELLS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Certification |  |  | The ordinance specifies concrete credentials: 'Well Driller - A person who is licensed by the state of Pennsylvania to drill wells, or in the case of geo-thermal wells has IGSHPA certification.' Section 6.1(a): 'Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation.' Section 7.1(a): 'Installation must be by a PA DCNR approved well driller or a IGSHPA accredited geothermal system installer.' Section 7.3(b): 'The system design shall be made by a IGSHPA accredited person or firm or an engineering firm familiar with loading and heat transfer requirements for the site specific proposed HVAC system.' | SECTION TWO - DEFINITIONS / SECTION SIX - WELL DRILLERS / SECTION SEVEN GEO-THERMAL WELLS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Decommissioning |  |  | The Northampton Township form states: 'In event this well is abandoned, owner will assume responsibility for plugging or sealing it in a manner satisfactory to the Township.' Section Eleven provides: 'A permit must be obtained prior to abandoning all wells.' 'Abandonment procedures shall be subject to the BCDH inspection.' 'Well abandonment procedures must minimally comply with the specifications referenced in the PA DEP/DCNR Water Well Abandonment Guidelines.' 'A copy of the PA DEP/DCNR Water Well Abandonment Form shall be submitted to the BCDH within ten days of abandonment.' | GENERAL CONDITIONS / SECTION ELEVEN - WELL ABANDONMENT | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | Township | 4201754688 | Other Prohibitions/Regulations |  |  | Section 7.2(f): 'Under no circumstances may additives of any kind be placed in this type of geothermal system to enhance heat transfer or reduce freezing points of the circulating water.' Section 7.3(c) also states: 'Copper piping is not acceptable for heat transfer use.' | SECTION SEVEN GEO-THERMAL WELLS / 7.2 Open-Loop Geo-thermal HVAC Systems | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Plumstead | Township | 4201761616 | Noise Limits | 28 | dBA | "Measurements can also be taken with approved equipment in weighted terms, with limits as shown below..." Table: "dBA ¦ 46 ¦ 56." The section also states: "The sound level of any operation... shall not exceed the levels designated below." | § 27-2310 Noise | 2026 | https://ecode360.com/14150522
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Definition: Well |  |  | "Boring/Borehole. A penetration of soil and/or rock that is augured, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed which is generally cylindrical in shape and whose diameter is generally smaller than its depth of penetration." | §27-3202. Definitions | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Definition: Geothermal |  |  | "Alternative Energy. A renewable source of energy generated from solar, water, wind, geothermal, or other renewable sources, which is capable of providing energy and utility provisions to a permitted use." | §27-3202. Definitions | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Definition: Geothermal Heat Pump |  |  | "Geothermal System. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earthsource heat pump system, and a GeoExchange system." Also: "Ground Source Heat Pump. A geothermal heat pump that uses the earth itself as a heat source and heat sink. It is coupled to the ground by means of a closedloop heat exchanger installed horizontally or vertically underground." | §27-3202. Definitions | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Right of Way | 15 | feet | Table I states: "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." The ordinance also states, "Geothermal systems shall not encroach on public drainage, utility roadway or trail easements of any nature." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance or twenty five Feet (25) feet from any property line." Table I also lists "Dedicated public right-of-way and property lines — at least 10 feet," but the more restrictive stated property-line setback is 25 feet. | §27-3204.3.K | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Building Foundation | 10 | feet | Table I lists: "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved) — at least 10 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Wastewater | 50 | feet | Table I lists multiple wastewater-related setbacks: "Septic tanks, aerobic tanks, or holding tanks — at least 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields — 25-50 feet"; "Sewage seepage pits and cesspools — at least 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites — at least 25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Animal Enclosures | 25 | feet | Table I lists: "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Fuel (above ground) | 25 | feet | Table I lists: "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Water Lines | 15 | feet | Table I lists: "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Sewer Lines | 15 | feet | Table I lists: "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 5-'15 feet or according to easement" and "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Water Bodies | 25 | feet | Table I lists: "Delineated wetlands, flood plains, lakes, ponds, or other surface waters — 10-25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table I lists: "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles — 300 feet 100-150 feet (if borehole is cased and grouted inside and out)." It also lists "Any other source or potential source of pollution — at least 300 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Noise Limits | 55 | dBA | "Audible sound from any alternative and/or emerging energy facility shall not exceed 55 dBA, as measured at the applicant's property line." | §27-3204.7.A | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Maximum Well Depth | 15 | feet | "All horizontal closed loop systems shall be no more than 15 feet deep." | §27-3204.3.I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." Also, "No alternative or emerging energy facility shall be located, modified, or constructed within Solebury Township unless a permit has been issued to the landowner in accordance with the provisions of this Section." | §27-3204.3.B; §27-3206.1 | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well drilier, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well. In all cases, the well drilling rig must also be approved by Pennsylvania Department of Environmental Protection." | §27-3204.3.M | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well drilier, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well." | §27-3204.3.M | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Decommissioning |  |  | "The geothermal system must be installed, maintained, and decommissioned in standards conforming to IGSHPA Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards..." Also, "If a geothermal system remains nonfunctional or inoperative for a continuous period of one (1) year (or longer timeframe where approved by the Township), the system/well piping should be drained of all heat transfer fluids and all well heads should be temporarily sealed and secured with a locking water-tight cap unless the well is otherwise abandoned/sealed in accordance with BCDH/Township regulations." Chapter-wide decommissioning also states: "The landowner or energy facility operator shall, at its expense, complete decommissioning of the alternative or emerging energy facility within 12 months after the end of the useful life..." and "All disturbed earth shall be restored, graded, and reseeded." | §27-3204.3.G; §27-3204.3.T; §27-3209.1-4 | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | Township | 4201771752 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems shall be prohibited." | §27-3204.3.C | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Definition: Geothermal Heat Pump |  |  | "Accessory Geothermal Heat Pump. A ground-integrated facility to provide heating and cooling to structures on a lot." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Roads | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "At least 10 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Right of Way | 15 | feet | Table 1 requires setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "At least 15 feet or outside easement." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Property Lines | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "At least 10 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Building Foundation | 10 | feet | Table 1 requires setback from "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" of "At least 10 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Wastewater | 50 | feet | Table 1 requires setbacks from wastewater-related features including "Septic tanks, aerobic tanks, or holding tanks" at "At least 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields" at "25-50 feet"; "Sewage seepage pits and cesspools" at "At least 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites" at "At least 25 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Animal Enclosures | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "At least 25 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Fuel (above ground) | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "At least 25 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Water Lines | 15 | feet | Table 1 requires setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "At least 15 feet or outside easement." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Sewer Lines | 15 | feet | Table 1 lists "Gravity sewer lines and drains carrying domestic sewage or industrial waste" at "5-15 feet or according to easement" and "Existing water and forced sewer buried utilities and/or utility trenches" at "At least 15 feet or outside easement." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Water Bodies | 25 | feet | Table 1 lists setbacks for geothermal boreholes/supply/return wells from "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" at "10-25 feet" and from an "Identified NPL Site (Superfund) plume area" at "At least 300 feet." The ordinance also includes "Any other source or potential source of pollution" at "At least 100 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table 1 requires setback from "Preparation area of storage area of hazardous spray materials, fertilizers of chemicals, or salt piles" of "300 feet; 100-150 feet (if borehole is cased and grouted inside and out)." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Permit |  |  | "It shall be unlawful to install a new geothermal subsurface facility (wells, horizontal or sub-aqueous tubing emplacements) or modify an existing subsurface facility without a valid permit." "Prior to constructing a new geothermal facility or modifying an existing system; property owner shall file all appropriate applications with Springfield Township, Bucks County, or other regulating agency and pay all applicable fees." "If the geothermal facility construction is not completed in two years of the permit issuance date, the approval to construct shall expire." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Inspection |  |  | "Springfield Township must field verify the location of the proposed geothermal installations and all applicable isolation distances." "The IGSHPA recommendation that the heat exchanger be isolated and tested to 150 percent of design pressure or 300 percent of system operating pressure shall be followed. No leaks shall occur within a 30-minute period." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Licensed Driller |  |  | "Only a PA DEP-licensed well driller or an International Ground Source Heat Pump Association (IGSHPA)-accredited geothermal system installer shall conduct trench excavation or drilling of a geothermal well. In all cases, the well drilling rig must also be approved by PA DEP." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Certification |  |  | "Only a PA DEP-licensed well driller or an International Ground Source Heat Pump Association (IGSHPA)-accredited geothermal system installer shall conduct trench excavation or drilling of a geothermal well." "The standing column well geothermal system... shall be installed by a geothermal well installation contractor who is certified in the proper installation methods as specified by the manufacturer." "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer..." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Decommissioning |  |  | "In the event of the proposed discontinuance of the use of the ground source heat pump system, a system closure plan will be prepared and submitted to Springfield Township for its approval." "A geothermal system shall be abandoned in a manner acceptable to Springfield Township and shall comply with the laws, rules, and regulations applicable to the abandonment of water wells. Any and all heat transfer fluid must be removed by displacement with grout in a manner acceptable to Springfield Township. The top of the borehole must be uncovered and capped with grout in a manner acceptable to Springfield Township." | (16) H-16 Accessory Geothermal Heat Pump; (i)-(j) | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | Township | 4201773016 | Open-loop Prohibitions |  |  | "Only closed loop systems or standing column well systems are allowed. Open loop systems with separate supply and reinjection wells or surface discharge sites are prohibited." | (16) H-16 Accessory Geothermal Heat Pump; (h) Geothermal Heat Pump Regulations | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Tinicum | Township | 4201776784 | Definition: Geothermal Heat Pump |  |  | "Geothermal system, closed loop: An energy system that circulates water or a water solution through the earth to use and extract heat without drawing groundwater and discharging the water or solution into an aquifer or aquitard." "Geothermal system, open loop: An energy system that circulates water or a water solution through the earth to use and extract heat by drawing groundwater into the system and/ or discharging the water or solution into an aquifer or aquitard." | SECTION 1. Section 809.03 | 2025 | https://tinicumtownship.org/wp-content/uploads/2025/04/272-Ordinance-Closed-Loop-signed-adopted.pdf
Pennsylvania | Bucks | Tinicum | Township | 4201776784 | Permit |  |  | "A Well Permit Application for a closed loop geothermal system shall follow the procedures contained in Subsection C. above." Also, "No Well Permit shall be issued for an open loop geothermal system." | SECTION 2. Section 809.12(E)(1)-(2) | 2025 | https://tinicumtownship.org/wp-content/uploads/2025/04/272-Ordinance-Closed-Loop-signed-adopted.pdf
Pennsylvania | Bucks | Tinicum | Township | 4201776784 | Open-loop Prohibitions |  |  | "Open loop geothermal systems are not permitted anywhere within Tinicum Township. No Well Permit shall be issued for an open loop geothermal system." | SECTION 2. Section 809.12(E)(2) | 2025 | https://tinicumtownship.org/wp-content/uploads/2025/04/272-Ordinance-Closed-Loop-signed-adopted.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Definition: Well |  |  | "GEOTHERMAL WELL - a well installed for the purpose of heating or cooling a facility. These shall include wells drilled as supply and/or return wells for open-loop systems, or closed-loop geothermal boreholes." | §302. Definitions | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP EQUIPMENT - any components of a heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | §302. Definitions | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Roads | 10 | feet | For closed-loop geothermal boreholes, §305.3.A table lists under miscellaneous: "Dedicated road right-of-way — 10 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Right of Way | 5 | feet | For closed-loop geothermal boreholes, §305.3.A table lists under miscellaneous: "Property lines, rights-of-way, easements — 5 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Property Lines | 5 | feet | For closed-loop geothermal boreholes, §305.3.A table lists under miscellaneous: "Property lines, rights-of-way, easements — 5 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Wastewater | 50 | feet | For closed-loop geothermal boreholes, §305.3.A table requires: "Surface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits — 50 feet" and "Spray irrigation site perimeter, sewage sludge and seepage disposal sites — 50 feet"; also "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks — 25 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Fuel (above ground) | 300 | feet | For closed-loop geothermal boreholes, §305.3.A table states: "Surface or subsurface containers or tanks of greater than 1,000 gal. used for storage of materials which cannot be properly renovated by passage through soil. This includes, but is not limited to, gasoline and all other petroleum products. (If borehole is cased and grouted inside and out) — 300 feet (150 feet)" and "Surface or subsurface containers or tanks of 1,000 gal. or less ... including ... gasoline and all other petroleum products ... — 30 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Sewer Lines | 5 | feet | For closed-loop geothermal boreholes, §305.3.A table lists "Sewer drains, public sewer laterals — 5 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Water Bodies | 10 | feet | For closed-loop geothermal boreholes, §305.3.A table states minimum isolation distances to pollution sources, including "Delineated wetlands, floodplains, lakes, ponds or other surface waters — 10 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop geothermal boreholes, §305.3.A table requires setbacks from chemical-related sources: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles. (If borehole is cased and grouted inside and out) — 300 feet (150 feet)." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Minimum Well Depth | 40 | feet | §305.2.A provides that open-loop geothermal delivery and return wells "must meet all Authority isolation distance requirements listed in this Part." §303.2.A states: "The source of supply shall be from a water bearing formation drawn not less than forty (40) feet from the ground surface." | §303. Drilled Water Supply Wells; §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Permit |  |  | §305.3.C states: "Closed-loop geothermal boreholes shall be permitted in accordance with §310. Each borehole must be permitted using a single application. A separate fee will be charged for each borehole." §310.2 provides: "It shall be unlawful for any person to locate, drill or have drilled any well ... until a permit ... shall have been issued by the Authority." §310.3.B states: "No monitoring well, test well, or geothermal well shall be used until it has received written approval for use from the Authority." | §305. Geothermal Wells; §310. Permit Procedure | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Licensed Driller |  |  | §305.1 states: "Licenses Only Pennsylvania-licensed well drillers shall install wells within Warminster Township." §302 also defines "GEOTHERMAL WELL INSTALLATION CONTRACTOR" as an individual responsible for drilling geothermal boreholes who "is licensed as a well contractor and geothermal well installation contractor by the Department." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Certification |  |  | §302 defines "GEOTHERMAL WELL INSTALLATION CONTRACTOR" as an individual responsible for geothermal borehole drilling who "is licensed as a well contractor and geothermal well installation contractor by the Department." §305.3.B.3 states: "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | §302. Definitions; §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | Township | 4201780952 | Decommissioning |  |  | §312.1 states: "Whenever a public water supply or another well replaces an existing well, it shall be the responsibility of the property owner to have the existing well properly abandoned by a licensed well contractor in accordance with §307 Abandonment of Wells... No well may exist in a decommissioned state." §312.2 adds: "All wells that are to be abandoned, or wells that are removed from use or a useable status such as decommissioned wells or any well that meets the definition of an abandoned well according to §302. shall be abandoned according to the requirements of §307." §307 requires one of the listed abandonment methods to be used and that a sealing report be filed with the Authority. | §307. Abandonment of Wells; §312. Water Source Replacements | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warrington | Township | 4201781048 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY — Energy generated due to variations in the subsurface temperature of soil, and/or use of hot springs, ground- or surface water temperature gradients. There are two basic types of geothermal systems, closed loop, and open loop. Closed-loop systems that take advantage of soil temperature gradients can be either horizontal or vertical and utilize piping buried at different depths in the earth's soil. Open-loop systems utilize either ground (well) or surface (lake/stream) water as the heat exchange medium, taking advantage of water temperature gradients in the earth or in bodies of surface water. Open-loop systems are strictly prohibited in Warrington Township." | § 370-202. Definitions of terms | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | Township | 4201781048 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY FACILITY — A passive or mechanical energy generation facility, whose main purpose is to convert geothermal energy into thermal energy to a permitted use. Such facilities may use closed loop piping, heat exchangers, and mechanical infrastructure and related appurtenant facilities." | § 370-202. Definitions of terms | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | Township | 4201781048 | Permit |  |  | § 370-1003.C(1): "Geothermal energy systems are permitted provided that a permit is obtained, and such facilities are limited to heating and cooling of buildings and located on a lot with a permitted use in accordance with the applicable provisions of this Ordinance." § 370-1005.A: "No alternative or emerging energy facility shall be located, modified or constructed within Warrington Township unless a permit has been issued to the landowner in accordance with the provisions of this section of this Article. Geothermal energy systems are exempt from the permit application process, but not exempt from the special exception application process." | § 370-1003.C(1) and § 370-1005.A | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | Township | 4201781048 | Open-loop Prohibitions |  |  | In the geothermal definition, the ordinance states: "Open-loop systems are strictly prohibited in Warrington Township." | § 370-202. Definitions of terms | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | Township | 4201781048 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems are permitted provided that a permit is obtained, and such facilities are limited to heating and cooling of buildings and located on a lot with a permitted use in accordance with the applicable provisions of this Ordinance." | § 370-1003.C(1) | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System. A system that uses a heat pump to extract heat from the earth in heating and / or reject heat into the earth in cooling mode. It may also be referred to a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." | Section 195-16.1(10) G(10) Geothermal Energy System | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Roads | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "at least 10 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Property Lines | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "at least 10 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Building Foundation | 10 | feet | Table 1 requires setback from "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" of "at least 10 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Wastewater | 50 | feet | Table 1 includes multiple wastewater-related setbacks: "Septic tanks, aerobic tanks, or holding tanks" — "at least 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields" — "at least 50 feet"; "Sewage seepage pits and cesspools" — "at least 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites" — "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Animal Enclosures | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Fuel (above ground) | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Water Lines | 15 | feet | Table 1 lists "Existing water and forced sewer buried utilities and/or utility trenches" with a required setback of "at least 15 feet or outside easement." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Sewer Lines | 15 | feet | Table 1 requires setback from "Gravity sewer lines and drains carrying domestic sewage or industrial waste" of "at least 15 feet or according to easement." It also lists "Existing water and forced sewer buried utilities and/or utility trenches" at "at least 15 feet or outside easement." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Water Bodies | 25 | feet | Table 1 requires geothermal boreholes/wells to be setback from "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" by "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table 1 lists "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" with a setback of "at least 300 feet" and "at least 150 feet (if borehole is cased and grouted inside and out)." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without all necessary permits, including but not limited to, zoning permits, and grading permits. Permit applications shall be accompanied by a site plan, prepared, signed, and sealed by a qualified professional licensed in the Commonwealth of Pennsylvania, which identifies property lines, lot area, location of existing natural and manmade features, location of the proposed closed-loop geothermal system, bore holes, ownership information for adjoining properties, and setback measurements from property lines, street lines, and occupied buildings." | Section 195-16.1(10) G(10)(1) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Inspection |  |  | "The landowner shall consult with a qualified inspector when requested by the Township to determine if the geothermal system is operating in accordance with the specifications of the manufacturer. A copy of the report shall be submitted to the Township and the Township shall have the right to inspect." Also, "An independent and certified professional engineer may be retained by the Township to inspect the decommissioning of the geothermal system. All such inspection fees shall be paid by the applicant or landowner." | Section 195-16.1(10) G(10) Maintenance; Decommissioning | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall drill a geothermal well. In all cases, the well drilling rig must also be approved by Pennsylvania Department of Environmental Protection." | Section 195-16.1(10) G(10) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall drill a geothermal well." | Section 195-16.1(10) G(10) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Decommissioning |  |  | "The landowner or Geothermal Energy System operator shall, at its expense, complete decommissioning of the geothermal system within 12 months after the end of the useful life. The geothermal system will presume to be at the end of its useful life if no energy is generated for a continuous period of 12 months. The removal of the above-ground geothermal system components shall be completed within 6 months of decommissioning. All disturbed earth shall be restored, graded, and reseeded. The landowner shall secure a permit to decommission the Geothermal Energy System... If the landowner or facility operator fails to complete decommissioning during the prescribed period of 12 months, the Township may take such measures as necessary to complete decommissioning..." | Section 195-16.1(10) G(10) Decommissioning | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | Township | 4201781144 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems (geothermal systems which expel the water after it leaves the structure) are prohibited." | Section 195-16.1(10) G(10)(2) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Wrightstown | Township | 4201786624 | Permit |  |  | The fee schedule states: "In the event construction is started without the required zoning and building permit(s), permit fees will be doubled." It also lists a geothermal-specific permit item under "TANK PERMITS": "Geothermal $200 Plus Inspection Fees." | BUILDING, ZONING, & ELECTRICAL PERMITS / TANK PERMITS | 2026 | https://www.wrightstownpa.org/media/2291/2026-fee-schedule-final.pdf
Pennsylvania | Bucks | Wrightstown | Township | 4201786624 | Inspection |  |  | The schedule provides: "Residential and Commercial Building and Fire Code Inspection Fees- $100 per inspection," "A reinspection required as a result of incomplete or improper work will be invoiced to the permit holder at an additional charge of $100 per inspection," and under "TANK PERMITS" lists "Geothermal $200 Plus Inspection Fees." | BUILDING, ZONING, & ELECTRICAL PERMITS / TANK PERMITS | 2026 | https://www.wrightstownpa.org/media/2291/2026-fee-schedule-final.pdf
Pennsylvania | Cambria | Adams | Township | 4202100308 | Definition: Geothermal |  |  | "Renewable energy sources," "Any method, process or substance whose supply is rejuvenated through natural processes and, subject to those natural processes, remains relatively constant, including, but not limited to, bio-mass conversion, geothermal energy, solar and wind energy and hydroelectric energy and excluding those sources of energy used in the fission and fusion processes." | SECTION 202 Definitions | 2007 | https://cambriaplanning.org/wp-content/uploads/2015/03/adamstownnshipzoningcomplete.pdf
Pennsylvania | Centre | Ferguson | Township | 4202725624 | Definition: Well |  |  | "A bored, drilled, driven, or dug well for the emplacement of fluids into the ground (except open loop geothermal heat pump systems)." |  | 2024 | https://ecode360.com/36116571
Pennsylvania | Centre | Ferguson | Township | 4202725624 | Definition: Geothermal Heat Pump |  |  | "A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump. The discharge water from the water-source heat pump may be returned to the subsurface through a recharge well or infiltration bed, or may be discharged into a pond, lake, or stream. A spring may also be the source of the ground water supply." |  | 2024 | https://ecode360.com/36116571
Pennsylvania | Centre | Ferguson | Township | 4202725624 | Maximum Well Depth | 20 | feet | "A borehole which is constructed to receive heat exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20 feet below grade as the subsurface conditions warrant." |  | 2024 | https://ecode360.com/36116571
Pennsylvania | Centre | Halfmoon | Township | 4202731992 | Definition: Well |  |  | "VERTICAL CLOSED-LOOP BOREHOLE. A borehole which is constructed to receive heat-exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20 feet below grade as the subsurface conditions warrant." "DECOMMISSIONED VERTICAL CLOSED-LOOP BOREHOLE. A vertical closed-loop borehole whose original purpose and use have been permanently discontinued or which is in such a state of disrepair that its original purpose cannot be reasonably achieved." | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Centre | Halfmoon | Township | 4202731992 | Definition: Geothermal |  |  | "CLOSED-LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere. The heat transfer fluid is potable or beneficial reuse water and may have approved antifreeze added." "DIRECT-EXCHANGE (DX) GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system where the heat pump refrigerant is circulated through metal piping installed in vertical, inclined, or horizontal boreholes." "OPEN-LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver groundwater to a water-source heat pump." "STANDING-COLUMN GEOTHERMAL SYSTEM. A type of open-loop geothermal heating and/or cooling system that circulates groundwater from a water well through a water-source heat pump and returns the discharge water ... to the same water well it was pumped from." | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Centre | Halfmoon | Township | 4202731992 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEATING AND/OR COOLING SYSTEM. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a 'geothermal heat pump system,' a 'ground-coupled heat pump system,' an 'earth-source heat pump system,' and a 'GeoExchange system.'" | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Centre | Halfmoon | Township | 4202731992 | Minimum Well Depth | 20 | feet | "VERTICAL CLOSED-LOOP BOREHOLE. A borehole which is constructed to receive heat-exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20 feet below grade as the subsurface conditions warrant." | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Chester |  | County | 42029 | Definition: Well |  |  | "Geothermal Well": "A vertical well or borehole constructed to facilitate the installation of, or connection to, equipment used for the purpose of heating or cooling a facility. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes." | 501.4.23 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump Equipment": "Any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | 501.4.25 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Right of Way | 10 | feet | For closed-loop geothermal boreholes, the Miscellaneous table requires "10 feet" from "Property lines, all right-of-ways, easements." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Property Lines | 10 | feet | For closed-loop geothermal boreholes, the Miscellaneous table requires "10 feet" from "Property lines, all right-of-ways, easements." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Wastewater | 50 | feet | For closed-loop geothermal boreholes, the table requires "50 feet" from "Subsurface sewage absorption areas elevated sand mounds, ... seepage pits, cesspools, sewage" and "50 feet" from "Spray irrigation site perimeter, sewage sludge and septage disposal sites"; and "25 feet" from "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Fuel (above ground) | 300 | feet | For closed-loop geothermal boreholes, the Chemical Related table requires "300 feet" from "Surface or subsurface containers or tanks of greater than 1,000 gallons used for storage of materials that cannot be properly renovated by passage through soil ... including ... gasoline and all other petroleum products," and "30 feet" from similar containers or tanks of "1,000 gallons or less." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Sewer Lines | 5 | feet | For closed-loop geothermal boreholes, the table requires a minimum isolation distance of "5 feet" from "Sewer drains, public sewer laterals." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Water Bodies | 10 | feet | For closed-loop geothermal boreholes, the table requires a minimum isolation distance of "10 feet" from "Delineated wetlands, flood plains lakes, ponds or other surface waters." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop geothermal boreholes, the Chemical Related table requires "300 feet" from "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals; salt piles" and "300 feet" from "Surface or subsurface containers or tanks of greater than 1,000 gallons used for storage of materials that cannot be properly renovated by passage through soil ... including ... gasoline and all other petroleum products." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Permit |  |  | 501.7.1.1: "All ... geothermal wells ... require a permit." 501.7.1.2: "Geothermal wells are required to be permitted." 501.14.3.1.1: "Open-loop geothermal delivery wells and return each require a separate permit." 501.14.3.2.1.1: "Closed-loop geothermal boreholes shall be permitted in accordance with §501.7." 501.14.3.2.1.2: "All Closed-loop geothermal boreholes that are part of the project may be included on a single application, and a single permit for the project will be issued. A master plot plan showing the numbered location of each borehole must be included." | 501.7.1.1; 501.7.1.2; 501.14.3.1.1; 501.14.3.2.1.1-501.14.3.2.1.2 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Inspection |  |  | "A site inspection may be conducted by the Department at any time during the construction process." | 501.7.8.1.2 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Licensed Driller |  |  | 501.6.1: "The Department shall license all well contractors, geothermal well installation contractors, or pump installation contractors. Geothermal Well Installation Contractors must also be licensed by Department as a well contractor." 501.7.1.3: "All ... geothermal wells ... shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor who is licensed as set forth in this Section." 501.4.24: "Geothermal Well Installation Contractor" is an individual "responsible for the drilling of boreholes used for the purpose of geothermal heating or cooling of a facility" and "shall be licensed as a Well Contractor and a Geothermal Well Installation Contractor by the Department." | 501.6.1; 501.7.1.3; 501.4.24 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Decommissioning |  |  | 501.17.1: "All wells considered to be abandoned shall be filled and sealed by licensed well contractor licensed by the Department in accordance with the procedures for decommissioning listed in this section." The Department "must be notified in writing within thirty (30) days" when a well meets abandoned-well criteria, and "Written notification and proper documentation of decommissioning shall be submitted to the Department on the Well Decommissioning Form within thirty (30) days." 501.16.1-501.16.2 further state that wells replaced or removed from use, including abandoned wells, "shall be decommissioned according to the requirements of §501.17." | 501.17.1; 501.16.1-501.16.2 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester |  | County | 42029 | Other Prohibitions/Regulations |  |  | 501.15.1: "No new ... geothermal well ... may be permitted, and no new ... geothermal well ... may be constructed, within the delineated Plume Area of a contaminated site unless the United States Environmental Protection Agency (US EPA) or the PA DEP agree and provide written documentation that installation of the well will not have any impact on the Plume or remediation effort." 501.14.3.2.3.2.1: "Boreholes must be vertical and may not be drilled at any angle. Only vertical closed-loop geothermal boreholes require a permit. Horizontal geothermal loop installations do not require a permit." 501.14.3.1.5: "Open-loop geothermal wells systems must include a return well and may not discharge directly or indirectly into surface waters." | 501.15.1; 501.14.3.2.3.2.1; 501.14.3.1.5 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Definition: Geothermal Heat Pump |  |  | The ordinance uses the term in operative text as: "geothermal systems and related boreholes for geothermal heat pump systems." | § 27-2303 General Provisions, Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Setback - Property Lines | 10 | feet | "Minimum Setbacks. Geothermal boreholes and wells shall be set back in accordance with the following: (4) A minimum of 10 feet from any property line." | § 27-2303(D)(4) | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Setback - Wastewater | 50 | feet | "Minimum Setbacks. Geothermal boreholes and wells shall be set back in accordance with the following: (1) A minimum of 50 feet from on-lot sewage disposal systems, or spray irrigation site perimeter." | § 27-2303(D)(1) | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Setback - Water Bodies | 10 | feet | "Minimum Setbacks. Geothermal boreholes and wells shall be set back in accordance with the following: (2) A minimum of 10 feet from surface waters, floodplains or wetlands." | § 27-2303(D)(2) | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Permit |  |  | "Permit Required. No person shall install, construct or otherwise implement a new alternative energy system within the Township without first obtaining the required permit(s) from the Township. No person shall modify any existing alternative energy system in the Township without first obtaining a permit from the Township." For geothermal specifically: "A zoning permit and building permit, under the Pennsylvania Uniform Construction Code, shall be required." | § 27-2303 General Provisions; Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Decommissioning |  |  | "The geothermal system shall be installed, maintained, and decommissioned in conformance with standards established by the IGSHPA Closed-loop/Geothermal Heat Pump Systems Design and Installation Standards, as same may be amended from time to time." | § 27-2303 General Provisions, Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | Township | 4202912744 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be permitted in the Township." | § 27-2303 General Provisions, Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | East Bradford | Township | 4202920824 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the earth’s thermal properties, in conjunction with electricity, to provide for the heating and cooling of Buildings." | SECTION 115-201. DEFINITIONS OF TERMS |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Bradford | Township | 4202920824 | Permit |  |  | "No person shall repair, modify, install, construct, or otherwise implement any Alternative Energy System(s) within the Township, without first obtaining all applicable permits from the Township." "A zoning permit and all other applicable permits shall be obtained prior to installation of any Alternative Energy System." For geothermal specifically: "An approved Chester County Health Department permit shall be included with the permit application submitted to the Township. If the total land disturbance is in excess of one (1) acre, an approved Chester County Conservation District and/or NPDES permit may also be required as part of the permit application." | SECTION 115-1703. ALTERNATIVE ENERGY; B. Applicability; C. General requirements for all Alternative Energy Systems; F. Geothermal Energy Systems |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Bradford | Township | 4202920824 | Certification |  |  | "The design, installation and operation of Geothermal Energy Systems shall be permitted in conformance with all applicable regulations under Section 501 of the Chester County Health Department Rules and Regulations and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | SECTION 115-1703(F)(2) |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Bradford | Township | 4202920824 | Decommissioning |  |  | General alternative energy systems: "The property owner shall be responsible to remove or properly restore any Alternative Energy System when determined to be a safety hazard by the Township or other regulatory authority." "If any Alternative Energy System is ever removed, any earth disturbance as a result of the removal of the any Alternative Energy System shall be graded and reseeded to the satisfaction of the Township." Geothermal-specific: "where the use of any Geothermal Energy System is abandoned, the property owner shall be responsible to cap and seal the in-ground portion(s) of the system. The property owner may further be required to evacuate (pump out) the fluid(s) in the system and to fill the borehole(s) with bentonite or an acceptable alternative." | SECTION 115-1703(C)(10)-(11); SECTION 115-1703(F)(4) |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Caln | Township | 4202920920 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: An energy-generating system utilizing the earth's thermal properties to meet all or part of the heating requirements of the on-site user. Specific terms include: ... CLOSED-LOOP GEOTHERMAL SYSTEM A type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, nontoxic heat transfer fluid; a heat pump; and an air distribution system; intended to utilize the earth's constant temperature for improved heat pump efficiency. ... OPEN-LOOP GEOTHERMAL SYSTEM A type of geothermal heating and/or cooling system that utilizes a water-supply well, or other sources, and a pump to deliver groundwater to a heat exchanger." | § 225-3 Definitions and word usage | 2026 | https://ecode360.com/10740718
Pennsylvania | Chester | East Caln | Township | 4202920920 | Open-loop Prohibitions |  |  | "OPEN-LOOP GEOTHERMAL SYSTEM ... The discharge water from the heat exchanger may be returned to the subsurface through a recharge well or infiltration bed or may be discharged into a pond, lake, or stream. [PROHIBITED]" | § 225-3 Definitions and word usage | 2026 | https://ecode360.com/10740718
Pennsylvania | Chester | East Marlborough | Township | 4202921480 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM An energy generating system that uses the earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | SECTION 202. DEFINITIONS OF TERMS | 2019 | https://www.eastmarlborough.org/wp-content/uploads/2019-zoning-ordinance.pdf
Pennsylvania | Chester | East Vincent | Township | 4202922000 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy generating system that uses the earth's thermal properties, in conjunction with electricity, to provide for the heating and cooling of buildings." | SECTION 27-1925.B. Definitions | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | East Vincent | Township | 4202922000 | Permit |  |  | "A zoning permit and all other applicable permits shall be required prior to installation of any renewable energy system." For geothermal specifically: "An approved Chester County Health Department permit shall be submitted as part of the permit application. Based on its proposed overall land disturbance, an approved Chester County Conservation District permit may also be required as part of the permit application." Also, "Any application for a geothermal energy system shall include a erosion and sedimentation control plan in accordance with the East Vincent Township Subdivision and Land Development Ordinance." | SECTION 27-1925.C.1; SECTION 27-1925.G.1; SECTION 27-1925.G.3 | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | East Vincent | Township | 4202922000 | Certification |  |  | "The design, installation and operation of geothermal energy systems shall be permitted in conformance with all applicable regulations under Section 501 of the Chester County Health Department Rules and Regulations and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | SECTION 27-1925.G.2 | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | East Vincent | Township | 4202922000 | Decommissioning |  |  | "If the geothermal energy system enters into a state of disrepair, it shall be the responsibility of the property owner to properly maintain the geothermal energy system or to decommission the system within six (6) months from the date the system enters such a state or immediately in any case determined to be a safety hazard." "Where the use of any geothermal energy system is abandoned, it shall be the responsibility of the property owner to cap and seal the in-ground portion(s) of the system. The property owner may further be required to evacuate (pump out) the fluid(s) in the system and to fill the borehole(s) with bentonite or an acceptable alternative." "If a geothermal energy system is ever removed, any earth disturbance as a result of its removal shall be in accordance with an approved erosion and sediment control plan and fully graded and reseeded to the satisfaction of the Township." | SECTION 27-1925.G.5-6 | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | Franklin | Township | 4202927376 | Definition: Well |  |  | "WELL — Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or artificial recharge of groundwater or for the installation of ground source heat pump equipment. This includes, but is not limited to, test wells, test borings, geothermal and monitoring wells, in addition to wells to be utilized as individual or semipublic or public water supplies." | § 26-117 Definitions | 2009 | https://ecode360.com/30847013
Pennsylvania | Chester | Franklin | Township | 4202927376 | Permit |  |  | § 26-102 states: "This Part shall apply to all wells to be drilled..." and "This Part shall further apply to the reconstruction, major repair and other changes to existing wells." § 26-112 states: "Geothermal well systems shall meet all standards as outlined in Chester County Health Departments Rules and Regulations, § 501.14.3." | § 26-102 Applicability; § 26-112 Geothermal Wells | 2009 | https://ecode360.com/30847013
Pennsylvania | Chester | Franklin | Township | 4202927376 | Licensed Driller |  |  | "WELL DRILLER — Any water well contractor licensed by the Commonwealth of Pennsylvania, his employees or representatives in responsible charge of drilling or otherwise constructing a well." | § 26-117 Definitions | 2009 | https://ecode360.com/30847013
Pennsylvania | Chester | Kennett | Township | 4202939344 | Definition: Well |  |  | "BOREHOLES - A penetration of soil and/or rock that is augured, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed which is generally cylindrical in shape and whose diameter is generally smaller than its depth of penetration. Used in closed vertical loop geothermal systems." | Section 2, Chapter 240, § 240-201, Definition of Terms | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | Section 2, Chapter 240, § 240-201, Definition of Terms | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, non-toxic heat transfer fluid; a heat pump; and an air distribution system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere..."; "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a water-supply well, or other source, and a pump to deliver groundwater to a heat exchanger." | Section 2, Chapter 240, § 240-201, Definition of Terms | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, Geothermal Energy Systems shall be set back a minimum distance of twenty-five (25) feet from any property line." | § 240-1943.A, Setback requirements | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Setback - Wastewater | 100 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 100 feet from on-lot sewage disposal systems." | § 240-1943.A, Setback requirements | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Setback - Public Water | 200 | feet | "The return well shall be located a minimum distance of two hundred (200) feet from wells on adjacent properties." | § 240-1943.A.10(c)(ii), Underground injection of water | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Permit |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards... and shall comply with the Township Building Code and with all other applicable Township requirements. A zoning permit and building permit, consistent with the PA Uniform Construction Code, shall be required. Applicable manufacturer specifications shall be submitted as part of the application for any permit." For open-loop systems, "Prior to the issuance of any permit for the installation of an open-loop Geothermal Energy System, the Township shall receive a report of the yield of the supply and recharge of the groundwater system..." | § 240-1943.A.2, Design and permitting | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Decommissioning |  |  | "If the Geothermal Energy System is ever abandoned or enters into a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the Geothermal Energy System within six (6) months from the date the system enters such a state." "Any earth disturbance as a result of the removal or permanent sealing of the Geothermal Energy System shall be graded and reseeded." | § 240-1943.A.11-.12, Abandonment or disrepair; Decommissioning | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | Township | 4202939344 | Other Prohibitions/Regulations |  |  | "Extraction of water from surface waters shall be prohibited." "Discharge of water from open-loop systems into sanitary sewer systems shall be prohibited." "Discharge of water from open-loop systems into storm sewers, and onto roads, shall be prohibited." "Discharge of water from open-loop systems into a watercourse shall be prohibited." | § 240-1943.A.10(a)-(b), Open-loop Geothermal Energy Systems | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Penn | Township | 4202958808 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: An energy generating system that uses the earth's thermal properties in conjunction with electricity to provide heating and cooling of buildings." | SECTION 201. DEFINITION OF TERMS | 2019 | https://www.penntownship.us/sites/g/files/vyhlif1061/f/uploads/penn_township_zoning_ordinances_adopted_2019.pdf
Pennsylvania | Chester | Pocopson | Township | 4202961800 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." The ordinance also defines system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system..."; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system..." | § 250-6 Definitions and word usage | 2026 | https://ecode360.com/6537874
Pennsylvania | Chester | Thornbury | Township | 4202976568 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM An energy generating system that uses the Earth's thermal properties, in conjunction with electricity, to provide for the heating and cooling of buildings." | § 155-1619B Definitions |  | https://ecode360.com/36852550
Pennsylvania | Chester | Thornbury | Township | 4202976568 | Permit |  |  | "A zoning permit and all other applicable permits shall be required prior to installation of any renewable energy system." For geothermal systems specifically: "An approved Chester County Health Department permit shall be submitted as part of the permit application. Based on its proposed overall land disturbance, an approved Chester County Conservation District permit may also be required as part of the permit application." Also, "Any application for a geothermal energy system shall include a stormwater management plan as required under Chapter 116." | § 155-1619C(1); § 155-1619F(1); § 155-1619F(3) |  | https://ecode360.com/36852550
Pennsylvania | Chester | Thornbury | Township | 4202976568 | Certification |  |  | "The design, installation and operation of geothermal energy systems shall be permitted in conformance with all applicable regulations under Section 501 of the Chester County Health Department Rules and Regulations and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | § 155-1619F(2) |  | https://ecode360.com/36852550
Pennsylvania | Chester | Thornbury | Township | 4202976568 | Decommissioning |  |  | "If the geothermal energy system enters into a state of disrepair, it shall be the responsibility of the property owner to properly maintain the geothermal energy system or to decommission the system within six months from the date the system enters such a state or immediately in any case determined to be a safety hazard." "Where the use of any geothermal energy system is abandoned, it shall be the responsibility of the property owner to cap and seal the in-ground portion(s) of the system. The property owner may further be required to evacuate (pump out) the fluid(s) in the system and to fill the borehole(s) with bentonite or an acceptable alternative." "If a geothermal energy system is ever removed, any earth disturbance as a result of its removal shall be in accordance with an approved erosion and sediment control plan and fully graded and reseeded to the satisfaction of the Township." | § 155-1619F(5); § 155-1619F(6) |  | https://ecode360.com/36852550
Pennsylvania | Chester | Upper Uwchlan | Township | 4202979352 | Definition: Geothermal Heat Pump |  |  | § 77-8B-C-D regulates "Geothermal systems" and requires that they "shall be closed-loop systems" and use approved heat-transfer fluids, indicating the term refers to geothermal heating/cooling exchange systems governed by this section. | § 77-8 Geothermal systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | Township | 4202979352 | Permit |  |  | § 77-4A: "All systems including modifications to existing systems must obtain permits under the Township Building Code and Pennsylvania Uniform Construction Code in effect at the time of application and construction." § 77-8E: "In-ground bed/tank systems require a Township grading permit." | § 77-4 Compliance with other codes and standards required; § 77-8 Geothermal systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | Township | 4202979352 | Decommissioning |  |  | § 77-9A: "The alternative energy system owner shall, at its sole expense, complete decommissioning of the system within 12 months after the end of the useful life of the system, or after 12 months of nonuse..." § 77-9A(1): "Decommissioning of a geothermal system shall include purging the system of the working fluid and disposing of the fluid in accordance with guidelines issued by the Pennsylvania Department of Environmental Protection." § 77-9A(2): "The geothermal in-ground fluid system and boreholes shall be backfilled with bentonite clay or equivalent material." | § 77-9 Decommissioning of systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | Township | 4202979352 | Open-loop Prohibitions |  |  | § 77-8C: "Geothermal systems shall be closed-loop systems." | § 77-8 Geothermal systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | Township | 4202979352 | Other Prohibitions/Regulations |  |  | § 77-3C(1): "Geothermal systems are specifically prohibited in the following areas: (1) C-1 Village District and historical districts designated by the Board of Supervisors in the Zoning Ordinance." | § 77-3 Permitted and prohibited district uses | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | West Goshen | Township | 4202983080 | Setback - Property Lines | 10 | feet | "All wells drilled for closed loop geothermal energy systems shall be set back ... a minimum of 10 feet from property lines. All wells drilled for open loop geothermal energy systems shall be set back ... a minimum of 10 feet from property lines." | §84-57.16(A)(3) | 2025 | https://www.westgoshen.org/DocumentCenter/View/1809/Ordinance-No-1-2025---Zoning-Ordinance-Amendment-Geothermal-Wells
Pennsylvania | Chester | West Goshen | Township | 4202983080 | Setback - Building Foundation | 30 | feet | "All wells drilled for closed loop geothermal energy systems shall be set back a minimum of 10 feet from any building foundation... All wells drilled for open loop geothermal energy systems shall be set back a minimum of 30 feet from any building foundation..." | §84-57.16(A)(3) | 2025 | https://www.westgoshen.org/DocumentCenter/View/1809/Ordinance-No-1-2025---Zoning-Ordinance-Amendment-Geothermal-Wells
Pennsylvania | Chester | West Goshen | Township | 4202983080 | Permit |  |  | "Prior to the installation of a geothermal energy system, the property owner shall provide a copy of the permit issued by Chester County and obtain a zoning permit pursuant to this chapter and a grading permit pursuant to Chapter 69 of the West Goshen Township Code." | §84-57.16(A)(2) and §84-57.16(B)(2) | 2025 | https://www.westgoshen.org/DocumentCenter/View/1809/Ordinance-No-1-2025---Zoning-Ordinance-Amendment-Geothermal-Wells
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES - A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 112 Definitions | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | Section 112 Definitions | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Setback - Roads | 20 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than ... twenty feet (20') from any property lines and street rights-of-way." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Setback - Property Lines | 20 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than ... twenty feet (20') from any property lines and street rights-of-way." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Setback - Wastewater | 25 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than ... twenty-five feet (25') from any existing or planned on-lot sewage disposal systems..." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Setback - Private Water | 100 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than one hundred feet (100') from any existing or planned drinking water wells that serve one principal use." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | Township | 4202983464 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be permitted." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Nantmeal | Township | 4202983664 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY. A source of energy generated from solar, water, wind, geothermal or similar sources which is capable of providing energy and utility provisions to a permitted use." | § 215-7 Specific terms; ALTERNATIVE AND EMERGING ENERGY FACILITIES; A. ALTERNATIVE ENERGY | 2026 | https://ecode360.com/35800116
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | §202. Definitions | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM, CLOSED HORIZONTAL LOOP - A type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, nontoxic heat transfer fluid; a heat pump; and an air distribution system..." and "GEOTHERMAL SYSTEM, CLOSED VERTICAL LOOP - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." | §202. Definitions | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal systems shall be set back a minimum distance of 10 feet from any property line." | §1230(g) Setback requirements | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Setback - Wastewater | 25 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 25 feet from on-lot sewage disposal systems or potable wells." | §1230(g)(1) Potential pollution sources | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Setback - Public Water | 25 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 25 feet from on-lot sewage disposal systems or potable wells." | §1230(g)(1) Potential pollution sources | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application. A zoning permit and building permit, under the Pennsylvania Uniform Construction Code, shall be required." Also: "A geothermal energy system shall be permitted by right in all zoning districts as an accessory use." | §1230. Geothermal Energy Systems | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Inspection |  |  | "Geothermal heating and/or cooling system vertical heat exchange boreholes containing loop pipes shall be tremie grouted... West Sadsbury Township shall be notified prior to grouting activities. At the discretion of the Township, the Township or its representative may perform inspections of the borehole grouting." Also, "For geothermal projects proposed in Zone 2, the project shall be reviewed and requires approval by the Township Engineer and the Township's Professional Geologist as part of the permit process." And: "In Zone 2, no drilling or grouting shall be performed without inspections by the Township Engineer or the Township's Professional Geologist. A twenty-four-hour notice is required prior to starting the project, and to schedule inspections." | §1230(h)(2), (4), (5) | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Screening |  |  | "All or any mechanical equipment (appurtenances) associated with and necessary for the operation of the geothermal energy system shall comply with all accessory setbacks for the district in which the system is installed." | §1230(f) Appurtenances | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to all applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | §1230(b) Design and permitting | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Decommissioning |  |  | "The agreement shall include that if the geothermal energy system is abandoned or is in a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the geothermal energy system within six months from the date the system enters such a state." Also: "Any earth disturbance as a result of the removal or permanent sealing of the geothermal energy system shall be graded and reseeded." | §1230(i)-(j) Abandonment or disrepair; Decommissioning | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Open-loop Prohibitions |  |  | "Only the following types of geothermal energy systems shall be permitted: (1) Closed horizontal loop; (2) Closed vertical loop." In addition, "Within Zone 2 of the designated wellhead protection area, geothermal systems are limited to closed-loop systems as defined within this section." | §1230(c) Permitted types; §1230(d) Wellhead protection areas | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | Township | 4202983968 | Other Prohibitions/Regulations |  |  | "All geothermal energy systems... shall be prohibited from construction and use within Zone 1 of the designated wellhead protection areas." | §1230(d) Wellhead protection areas | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | Westtown | Township | 4202984104 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the Earth's thermal properties, in conjunction with electricity, to provide for the heating and cooling of buildings." Also defined are system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM — A type of geothermal heating and/or cooling system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM — A type of geothermal heating and/or cooling system..."; and "OPEN-LOOP GEOTHERMAL SYSTEM — A type of geothermal heating and/or cooling system..." | § 170-201 Definitions | 2026 | https://ecode360.com/12396648
Pennsylvania | Chester | West Vincent | Township | 4202984160 | Setback - Wastewater | 100 | feet | "Any recharge well must be located at least 100 feet from any subsurface septic or sewage disposal system." | § 390-145B(1)(e) | 2024 | https://ecode360.com/32402746
Pennsylvania | Chester | West Vincent | Township | 4202984160 | Permit |  |  | "No geothermal heat pump shall be installed or used without a building permit first being issued by the Township." | § 390-145B(1)(a) | 2024 | https://ecode360.com/32402746
Pennsylvania | Chester | West Vincent | Township | 4202984160 | Other Prohibitions/Regulations |  |  | "The discharge or effluent from a geothermal heat pump system must be returned to the groundwater through a recharge well and the system so maintained that there is no outflow to the surface of the ground or any surface waters." | § 390-145B(1)(d) | 2024 | https://ecode360.com/32402746
Pennsylvania | Chester | Willistown | Township | 4202985352 | Inspection |  |  | "Upon presentation of proper credentials, duly authorized representatives of the Township may enter at reasonable times upon any property within the Township to inspect the implementation, condition, or operation and maintenance of the stormwater controls or BMPs... Inspections, including but not limited to a final inspection, of all constructed BMPs, conveyances, or other stormwater facilities and related improvements may be conducted to confirm compliance with this article and with the final approved SWM site plan prior to the issuance of any occupancy permit, use permit, or other form of final approval of the project by the Township." Also, "The landowner or the owner's designee shall inspect SWM BMPs, facilities and/or structures installed under this article" at stated frequencies, with written inspection reports. | § 73-45 Right of entry; § 73-43 Operation and maintenance responsibilities | 2026 | https://ecode360.com/11712374
Pennsylvania | Cumberland | Camp Hill | Borough | 4204111000 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY SYSTEM: Any one (1) or more method and facility used in the conversion, storage, and distribution including electrical infrastructure, transmission lines, and other appurtenant Structures and facilities of renewable energy sources, including but not limited to sunlight, wind, rain, tides, and geothermal heat." | § 202. Definitions | 2023 | https://cms8.revize.com/revize/camphillborough/Departments/Code%20Enforcement-Zoning/2023%20Zoning%20Ordinance/2023%20ZONING%20ORDINANCE%202023-04.pdf
Pennsylvania | Cumberland | Dickinson | Township | 4204119144 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | § 205-12 Definitions | 2020 | https://ecode360.com/36501835
Pennsylvania | Cumberland | Monroe | Township | 4204150472 | Permit |  |  | "Green Energy Projects - Green energy projects, including the installation of solar panels, wind energy systems or geothermal heating, are subject to a 25% permit fee discount, but in no case will the overall permit fee be reduced below $150." The resolution also establishes building permit categories and fees for "Residential Building Permit Review and Inspections," "Commercial Building Permit Review," and related inspections under Monroe Township's administration and enforcement of the Pennsylvania Uniform Construction Code. | Fee Schedule item 1 / note 1 | 2012 | https://cms6.revize.com/revize/monroetwppa/RESOLUTIONS/2012/2012-06.pdf
Pennsylvania | Cumberland | Silver Spring | Township | 4204170792 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM - A well or wells installed for the purpose of heating or cooling. The system can be either closed or open loop." | SECTION 203 SPECIFIC TERMS | 2022 | https://www.sstwp.org/Documents/Departments/Community%20Development/Permit%20Forms%20Applications/Silver%20Spring%20SLDO%20Adopted%20March%202022%20-%20Formatted%20with%20signature%20page%20(1)_202205181140007159.pdf?t=202507211024550
Pennsylvania | Cumberland | South Middleton | Township | 4204172336 | Definition: Geothermal Heat Pump |  |  | 'Abandonment of Well - An abandoned or unused well may be defined as one or more of the following: ... (vii.) An inactive geothermal groundwater heat exchange system.' | 1404(4)(a) - Definitions | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Cumberland | South Middleton | Township | 4204172336 | Permit |  |  | For geothermal exchange systems in Zone 2: 'a. No such systems shall be permitted within 200 feet of the WHPA Zone 1 boundary. b. Submittal of evidence that 1) the landowner is aware that only food-based antifreeze may be used in piping, 2) professionally designed & installed piping will be encased to prevent leakage, & 3) the recommendations in DEP's Ground Source Heat Pump Manual for protecting water quality will be utilized.' For abandoned geothermal systems treated as abandoned wells: 'A zoning permit demonstrating planned compliance with DEP's water well abandonment guidelines shall be required prior to the sealing of a well.' | Table 1404(7) Use 19; Table 1404(7) Use 27 | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Cumberland | South Middleton | Township | 4204172336 | Decommissioning |  |  | Definition: 'Abandonment of Well - An abandoned or unused well may be defined as ... (vii.) An inactive geothermal groundwater heat exchange system.' Operative rule in Table 1404(7) Use 27: 'a. Wells shall be sealed within 30 days of abandonment b. A zoning permit demonstrating planned compliance with DEP's water well abandonment guidelines shall be required prior to the sealing of a well. c. Certification by a licensed well driller, professional engineer or registered professional geologist of the sealing of the well consistent with DEP guidelines shall be required.' | 1404(4)(a); Table 1404(7) Use 27 - Abandonment of Wells | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Cumberland | South Middleton | Township | 4204172336 | Other Prohibitions/Regulations |  |  | Table 1404(7) lists '19. Geothermal Exchange Systems (groundwater & ground loop)' as 'Not Permitted' in Zone 1 of the Wellhead Protection Area. | Table 1404(7) Use 19 - Geothermal Exchange Systems (groundwater & ground loop) | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Definition: Well |  |  | "Geothermal Boreholes: A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Definition: Geothermal |  |  | "Geothermal: Of, relating to, or utilizing the heat of the earth's interior." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System: An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Setback - Property Lines | 25 | feet | "All parts of the geothermal system shall be located a minimum distance of twenty-five (25) feet from any property line." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Setback - Public Water | 25 | feet | "All parts of the geothermal system shall be located a minimum distance of twenty-five (25) from any on-lot wells." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Maximum Well Depth | 20 | feet | "Closed Horizontal Loop Geothermal System ... A horizontal closed loop system shall be no more than twenty (20) feet deep." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design and installation comply with applicable industry standards." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | Township | 4204349040 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in the Township." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum of 25 feet from all property lines, except as otherwise specified." | § 27-1102, Subsection 24.E(3)(c) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 27-1102, Subsection 24.E(3)(d) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Setback - Private Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 27-1102, Subsection 24.E(3)(d) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Maximum Well Depth | 20 | feet | "A horizontal closed-loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 27-1102, Subsection 24.E(3)(a) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Permit |  |  | "Required Permit. The design and installation of geothermal energy systems shall conform to applicable industry standards and the UCC. At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 27-1102, Subsection 24.E(4) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Certification |  |  | "At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 27-1102, Subsection 24.E(4) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Decommissioning |  |  | General decommissioning rules state: "Except for geothermal systems, the alternative energy system owner shall, at its expense, complete decommissioning of the system within 12 months after the end of the useful life of the system, or after 12 months of nonuse." For geothermal specifically: "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his or her expense after a demolition permit has been obtained," and "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 27-1102, Subsection 24.C(1); § 27-1102, Subsection 24.E(5) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | Township | 4204379216 | Open-loop Prohibitions |  |  | "Closed-loop geothermal energy systems are permitted in all zoning districts as an accessory use to a principal use of the site. Open-loop geothermal energy systems are prohibited within the Township." | § 27-1102, Subsection 24.E(1) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Delaware |  | County | 42045 | Definition: Well |  |  | "Well": Any vertical excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or artificial recharge of groundwater or for the installation of ground source heat pump equipment. This includes but is not limited to test wells, test borings, geothermal and monitoring wells, in addition to wells to be utilized as individual or semi-public or public water supplies. | 501.4.46 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Definition: Geothermal |  |  | "Geothermal Well": A vertical well or borehole constructed to facilitate the installation of, or connection to, equipment used for the purpose of heating or cooling a facility. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes. | 501.4.23 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump Equipment": Any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems. | 501.4.25 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Right of Way | 10 | feet | For closed-loop geothermal boreholes, the table states: "Property lines, all right-of-ways, easements — 10 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Property Lines | 10 | feet | For closed-loop geothermal boreholes, the table states: "Property lines, all right-of-ways, easements — 10 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Wastewater | 50 | feet | For closed-loop geothermal boreholes, the table states: "Subsurface sewage absorption areas elevated sand mounds, cesspools, sewage seepage pits — 50 feet" and "Spray irrigation site perimeter, sewage sludge and septage disposal sites — 50 feet"; also "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks — 25 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Fuel (above ground) | 300 | feet | For closed-loop geothermal boreholes, the table states: "Surface or subsurface containers or tanks of greater than 1,000 gallons used for storage of materials that cannot be properly renovated by passage through soil. This includes, but is not limited to, gasoline and all other petroleum products. — 300 feet" and "... 1,000 gallons or less ... gasoline and all other petroleum products ... — 30 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Sewer Lines | 5 | feet | For closed-loop geothermal boreholes, the table states: "Sewer drains, public sewer laterals — 5 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Water Bodies | 10 | feet | For closed-loop geothermal boreholes, the table states: "Delineated wetlands, flood plains lakes, ponds or other surface waters — 10 feet" and "Rainwater pits and rain gardens — 10 feet" and "Storm drains, retention basins storm water stabilization ponds — 10 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop geothermal boreholes, the table states: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles — 300 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Permit |  |  | 501.7.1.1: "All ... geothermal wells ... require a permit..." 501.7.1.2: "Geothermal wells are required to be permitted." 501.14.3.1.1: "Open-loop geothermal delivery wells and return each require a separate permit." 501.14.3.2.1.1: "Closed-loop geothermal boreholes shall be permitted in accordance with §501.7." | 501.7.1.1; 501.7.1.2; 501.14.3.1.1; 501.14.3.2.1.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Inspection |  |  | "A site inspection may be conducted by the Department at any time during the construction process." | 501.7.8.1.2 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Licensed Driller |  |  | 501.6.1: "The Department shall license all well contractors, geothermal well installation contractors, or pump installation contractors. Geothermal Well Installation Contractors must also be licensed by Department as a well contractor." 501.7.1.3: "All ... geothermal wells ... shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor..." 501.4.24: "Geothermal Well Installation Contractor" is the individual "responsible for the drilling of boreholes used for the purpose of geothermal heating or cooling of a facility" and "shall be licensed as a Well Contractor and a Geothermal Well Installation Contractor by the Department." | 501.6.1; 501.7.1.3; 501.4.24 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Decommissioning |  |  | 501.17.1: "All wells considered to be abandoned shall be filled and sealed by licensed well contractor licensed by the Department... Written notification and proper documentation of decommissioning shall be submitted to the Department on the Well Decommissioning Form within thirty (30) days..." 501.17.6: "Concrete, cement grout, bentonite or sealing clay shall be used as primary sealing materials and shall be placed from bottom to top by a method that will prevent segregation or dilution of materials." | 501.17.1; 501.17.6 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware |  | County | 42045 | Other Prohibitions/Regulations |  |  | 501.15.1: "No new ... geothermal well may be permitted, and no new ... geothermal well may be constructed, within the delineated Plume Area of a contaminated site unless the United States Environmental Protection Agency (US EPA) or the PA DEP agree and provide written documentation that installation of the well will not have any impact on the Plume or remediation effort." 501.14.3.2.3.2.1: "Boreholes must be vertical and may not be drilled at any angle. Only vertical closed-loop geothermal boreholes require a permit. Horizontal geothermal loop installations do not require a permit." | 501.15.1; 501.14.3.2.3.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | Aston | Township | 4204503336 | Permit |  |  | "Alternative energy sources, which include but are not limited to ground source heat pumps (geothermal), solar energy systems, and wind energy systems are permitted in all districts by conditional use only." Also, "The alternative energy system shall require a Building Permit and any other associated permits..." | 1292.27 ALTERNATIVE ENERGY SOURCES | 2012 | https://astontownship.net/download/ordinances/Aston%20Township%20Zoning%20Ordinance%202011.pdf
Pennsylvania | Delaware | Aston | Township | 4204503336 | Decommissioning |  |  | "If an alternative energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." | 1292.27 ALTERNATIVE ENERGY SOURCES | 2012 | https://astontownship.net/download/ordinances/Aston%20Township%20Zoning%20Ordinance%202011.pdf
Pennsylvania | Delaware | Brookhaven | Borough | 4204509080 | Permit |  |  | "Fees for installation of gas appliances (' 1484.03): ... (d) Solar systems and geothermal systems: $50." | § 208.06(N)(3)(d) - Fees for installation of gas appliances | 2013 | https://brookhavenboro.com/wp-content/uploads/2019/11/Administrative-Code.pdf
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Definition: Well |  |  | "GEOTHERMAL WELL — A well(s) installed for the purpose of heating and/or cooling the dwelling or building on a property (see 'closed-loop geothermal borehole')." | § 365-168A |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Definition: Geothermal Heat Pump |  |  | "GROUND-SOURCE HEAT PUMP — A ground-source heat pump, which shall include, but not be limited to, any components of a heating and/or cooling system (including supply wells) installed in a closed-loop geothermal borehole and used for heating and/or cooling of a building or dwelling using a heat transfer fluid or direct exchange system." | § 365-168A |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Right of Way | 10 | feet | The setback table lists "Rights-of-way and easements — 10" as a minimum isolation distance for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Property Lines | 40 | feet | The table sets minimum isolation distances from "Property lines of properties served by public sewers — 10" and from "Property lines of properties served by on-lot septic systems — 40" for closed-loop geothermal boreholes. | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Building Foundation | 10 | feet | The setback table requires a minimum isolation distance of "Building foundations — 10" for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Wastewater | 50 | feet | The setback table for "closed-loop geothermal boreholes" requires minimum isolation distances of "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits — 50" and "Septic tanks, aerobic tanks, sewage pump tanks and holding tanks — 25." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Fuel (above ground) | 30 | feet | The table lists "Exterior surface or subsurface containers or tanks used for storage of materials that cannot be properly disposed of by passage through soil; this includes, but is not limited to, gasoline and all other petroleum products, and propane — 30" for closed-loop geothermal boreholes. | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Sewer Lines | 10 | feet | The table lists "Sewer drains and public sewer laterals — 10" as a minimum isolation distance for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Water Bodies | 50 | feet | The setback table states: "Delineated wetlands, floodplains, lakes, ponds or other surface waters — 50" minimum isolation distance for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The table requires separation from "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals or salt piles ... 300 (150)" for closed-loop geothermal boreholes, with "300" generally and "(150)" "[i]f borehole is cased and grouted inside and out." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Permit |  |  | "No person shall install, construct, drill or excavate to facilitate the construction or installation of a ground-source heat pump for use as a heating and/or cooling system for a residential or commercial building within the Township without first obtaining a ground-source heat pump permit from the Township. No person shall drill or excavate to repair or modify or to facilitate the repair or modification of a ground-source heat pump system in the Township without first obtaining a ground-source heat pump permit." | § 365-168D(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Inspection |  |  | "Prior to commencing any work under any permit, the property shall be staked to accurately identify the approved location of each proposed geothermal borehole. The Township shall inspect the property and shall sign off on each location prior to any drilling or installation." The contractor must also provide before activation: "Written documentation verifying the ground-source heat pump system has been successfully pressure tested and it is ready for use and operation." | § 365-168E(1), (7)(d) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Decommissioning |  |  | "In the event of the discontinuance of the use of the ground-source heat pump system, a system closure plan shall be prepared and submitted to the Township for approval." | § 365-168F |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Open-loop Prohibitions |  |  | The ordinance states: "All ground-source heat pump systems shall be closed-loop systems" and under prohibited uses, "No open-loop systems shall be permitted." | § 365-168B(3), (4)(a) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | Township | 4204522584 | Other Prohibitions/Regulations |  |  | Under prohibited uses, the ordinance states: "Class V wells (as defined by U.S. EPA) are prohibited" and "A ground-source heat pump system shall not be connected in any way to any sanitary sewage disposal or stormwater system." | § 365-168B(4)(b), (c) |  | https://ecode360.com/34067174
Pennsylvania | Erie | Edinboro | Borough | 4204922608 | Definition: Geothermal Heat Pump |  |  | "OPEN LOOP — A geothermal heat pump system that withdraws water from a well or surface water supply, passes it through a heat exchanger, and discharges the water to a surface water body, storm or sanitary sewer system, or recharge well." Also: "CLOSED LOOP SYSTEMS — Systems which rely on the contained circulation of fluids through an underground pipe circuit" and "DIRECT EXPANSION or DX — A system which circulates refrigerant in a closed underground loop." | § 13-401 Definitions | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | Borough | 4204922608 | Permit |  |  | "No person, partnership, corporation or other entity shall... install, construct, drill or excavate to facilitate the construction or installation of ground source heat pump for use as a heating and/or cooling system for any residential, commercial or industrial structures without first obtaining a building permit." | § 13-402 General Provisions | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | Borough | 4204922608 | Inspection |  |  | "Prior to backfilling, in-ground joints shall be pressure tested to 500 psi for a minimum of 15 minutes, with no pressure loss. Should any buried portion fail, refrigeration shall be recaptured, and the loop shall be repaired or abandoned." | § 13-405 Installation of Direct Expansion (DX) Systems | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | Borough | 4204922608 | Decommissioning |  |  | "Whenever a ground source heat pump system is permanently removed from service, and the pipes are not removed from the ground, the outside loop pipes shall be filled with materials meeting specifications for grout." | § 13-407 Provisions for the Decommissioning of Ground Source Heat Pump Systems | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | Borough | 4204922608 | Open-loop Prohibitions |  |  | "Shall not be permitted." | § 13-403 Installation of Open Loop Systems | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | Borough | 4204922608 | Other Prohibitions/Regulations |  |  | "In specific areas of the Home Rule Borough of Edinboro where, as determined by the Borough of Edinboro Engineer, local geological conditions, including but not limited to karst or permafrost, do not meet the requirements for installation and/or efficient operation of geothermal heat pump systems, the Borough Engineer may prohibit the installation of one or more types of geothermal heat pump systems." | § 13-402 General Provisions | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | North East | Borough | 4204954952 | Definition: Geothermal |  |  | "RENEWABLE ENERGY SOURCE: Any method, process or substance whose supply is rejuvenated through natural processes and, subject to those natural processes, remains relatively constant including, but not limited to, biomass conversion, geothermal energy, solar and wind energy, and hydroelectric energy..." | Sec. 201 General Definitions | 2011 | https://www.northeastborough.com/wp-content/uploads/2020/02/ZoningOrdinance.pdf
Pennsylvania | Erie | North East | Borough | 4204954952 | Permit |  |  | Sec. 507 states: "This use may be permitted in all districts as a special exception use, if approved by the Zoning Hearing Board." Sec. 405 lists "Renewable Energy Source (D) (Sec.705)" as "S" in R-A, R-B, C-1, and M-1 districts. | Sec. 507 Renewable Energy Source; Sec. 405 Permitted Use and Special Exception Use Table | 2011 | https://www.northeastborough.com/wp-content/uploads/2020/02/ZoningOrdinance.pdf
Pennsylvania | Erie | North East | Borough | 4204954952 | Inspection |  |  | "Applications, Zoning Certificates, Building Permits, and Inspection. He/she shall receive applications for zoning certificates and building permits and make all inspection in accordance with the provisions of this Zoning Ordinance." Also: "The Zoning Officer may examine or cause to be examined all structures and/or land for which an application has been filed for zoning certificates, and he/she may conduct such inspections from time to time during and at completion of the work for which a zoning certificate has been issued." | Sec. 602 Duties of the Zoning Officer | 2011 | https://www.northeastborough.com/wp-content/uploads/2020/02/ZoningOrdinance.pdf
Pennsylvania | Erie | Summit | Township | 4204975208 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM: Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the open-loop or closed-loop circulation of a geothermal fluid vertically, or the location, acquisition or artificial recharge of groundwater." | Section 202 – Specific Terms | 2025 | https://summittownship.com/wp-content/uploads/2026/01/2021-02-Summit-Township-Zoning-Ordinance-Amended-2025-12-20-BLANK-LAST-PAGE.pdf
Pennsylvania | Franklin | Greene | Township | 4205530944 | Definition: Well |  |  | "GEOTHERMAL WELL — A well installed for the purpose of heating or cooling a facility. This shall include wells drilled as supply and return wells for an open loop system, or closed loop geothermal boreholes." | § 101-4 Definitions | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP EQUIPMENT — Any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed loop applications using heat transfer fluid or direct exchange systems." | § 101-4 Definitions | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Driveways | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (11) Property lines, driveways, rights-of-way or easements: 10 feet." | § 101-14(E)(11) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Right of Way | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (11) Property lines, driveways, rights-of-way or easements: 10 feet." | § 101-14(E)(11) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Property Lines | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (11) Property lines, driveways, rights-of-way or easements: 10 feet." | § 101-14(E)(11) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Wastewater | 100 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (4) Subsurface sewage absorption areas, elevated sand mounds, seepage pits, cesspools or other on-lot sewage disposal systems: 100 feet. (5) Spray irrigation perimeter, sewage sludge or septage disposal sites: 100 feet. (6) Septic tanks, aerobic tanks, sewage pumps or holding tanks: 50 feet." | § 101-14(E)(4)-(6) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Fuel (above ground) | 300 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (9) Surface or subsurface containers or tanks of greater than 1,000 gallons' capacity used for storage of materials that cannot be properly renovated by passage through soil. This includes gasoline, diesel fuel and other petroleum products: 300 feet (can be reduced to 150 feet if the borehole is cased and grouted inside and out). (10) Surface or subsurface containers or tanks of 1,000 gallons or less used for storage of materials like heating oil or other petroleum products: 30 feet." | § 101-14(E)(9)-(10) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Fuel (below ground) | 300 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (9) Surface or subsurface containers or tanks of greater than 1,000 gallons' capacity used for storage of materials that cannot be properly renovated by passage through soil. This includes gasoline, diesel fuel and other petroleum products: 300 feet (can be reduced to 150 feet if the borehole is cased and grouted inside and out). (10) Surface or subsurface containers or tanks of 1,000 gallons or less used for storage of materials like heating oil or other petroleum products: 30 feet." | § 101-14(E)(9)-(10) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Sewer Lines | 5 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (7) Sanitary sewer lines, drains or laterals: five feet." | § 101-14(E)(7) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Water Bodies | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (1) Delineated wetlands, floodplains, lakes, ponds, streams or other surface waters: 10 feet." | § 101-14(E)(1) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Setback - Hazardous Materials/Fertilizers | 300 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (8) Preparation or storage area of hazardous spray materials, fertilizers, chemicals or salt piles: 300 feet (can be reduced to 150 feet if the borehole is cased and grouted inside and out)." | § 101-14(E)(8) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Permit |  |  | § 101-7(A)(1): "Any installation, repair or modification requires a permit from the Township." § 101-14(H): "The geothermal well installation contractor shall be responsible for insuring that the borehole is drilled in the permitted location..." | § 101-7 Permit procedures; § 101-14 Geothermal wells | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Licensed Driller |  |  | § 101-7(A)(1): "All individual and semipublic water supplies shall be constructed by a duly licensed well or pump installation contractor." § 101-14(H): "The geothermal well installation contractor shall be responsible for insuring that the borehole is drilled in the permitted location..." | § 101-7 Permit procedures; § 101-14 Geothermal wells | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Certification |  |  | § 101-14(J): "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | § 101-14 Geothermal wells | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | Township | 4205530944 | Decommissioning |  |  | "Whenever an existing well is replaced, the property owner shall be responsible for the decommissioning of the existing well by a licensed contractor. No well shall exist in an abandoned state." | § 101-14(O) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Washington | Township | 4205581240 | Definition: Well |  |  | "Geothermal Well - Any excavation that is drilled, cored, bored, washed, driven, dug, jetted or otherwise constructed when the intended use of such excavation is for the circulation of a geothermal fluid vertically, or the location, acquisition or artificial recharge of groundwater. (Includes open and closed loop vertical systems)" | Section 165-2. Definitions and Terms. | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating System - A geothermal heat pump system which relies on the contained circulation of geothermal fluids to obtain and to utilize geothermal resources." Also: "Closed Loop Systems - A geothermal heat pump system which relies on the contained circulation of geothermal fluids through an underground loop of pipes." "Open Loop System - A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring or surface water." | Section 165-2. Definitions and Terms. | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Driveways | 10 | feet | Table in §165-13(B): "Property lines, driveways, and private roads — 10" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Right of Way | 20 | feet | Table in §165-13(B): "Dedicated public right of ways — 20" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Property Lines | 10 | feet | Table in §165-13(B): "Property lines, driveways, and private roads — 10" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Building Foundation | 30 | feet | Table in §165-13(B): "Building foundations (except for buildings enclosing water wells and/or water well pumps) — 30" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Wastewater | 100 | feet | Table in §165-13(B): "Septic tanks, aerobic tanks or holding tanks — 50" feet; "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields — 100" feet; "Sewage seepage pits, cesspools — 100" feet; "Spray irrigation sites, sewage sludge and septage disposal sites — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Animal Enclosures | 100 | feet | Table in §165-13(B): "Farm silos, barnyards, privies and fuel tanks — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Fuel (above ground) | 100 | feet | Table in §165-13(B): "Farm silos, barnyards, privies and fuel tanks — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Sewer Lines | 50 | feet | Table in §165-13(B): "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 50" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Water Bodies | 25 | feet | §165-13(A): "Geothermal wells shall not be sited in floodplains." Table in §165-13(B): "Lakes, ponds, streams or other surface waters — 25" feet; "Rainwater pits, ditches — 25" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table in §165-13(B): "Preparation areas or storage areas of hazardous spray materials, fertilizers or chemicals, salt piles — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Permit |  |  | §165-7: "Any persons desiring to construct, install, or alter a Geothermal Heating System within the Township shall first apply for a Geothermal Heating System permit... No Person shall commence construction or Alteration of a Geothermal Heating System prior to the Owner... receiving a permit." §165-11(A): "Before any drilling or site preparation begins, the well driller shall apply for a Well Permit from the Township." §165-11(E): "No Geothermal Well shall be put into service without receiving a Geothermal Well permit and meeting the requirements of this Chapter." §165-8(C): "All applicants for a Geothermal Heating System permit shall also obtain a building permit as per the UCC..." | Section 165-7. Application for Geothermal Heating System Permit / Section 165-11. Wells for Geothermal Systems - Procedures. | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Inspection |  |  | §165-15: "The following inspections shall be required by the Township and Authority: A. Site inspection before any work is done... B. Inspection of the installed loop (pressure test). C. Inspection of grouting. D. Inspection of the completely installed system before operations commence and upon commencement of operations. E. Periodic inspections no less than once every three years. F. Inspection if geothermal system or well is abandoned." §165-11(B): "During the well drilling and construction process, the Township or Authority may enter the premises to determine if the well is being installed according to the requirements of this Chapter." §165-16(B): "Abandonment procedures shall be subject to Township inspection." | Section 165-15. Inspection / Section 165-11(B) / Section 165-16(B) | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Licensed Driller |  |  | §165-12: "All Geothermal Heating Systems and wells installed for the purposes of heating and cooling a facility must adhere to the International Ground Source Heat Pump Association's (IGSHPA) Design & Installation Standards and the installer(s) and well driller(s) must be certified by the IGSHPA." §165-12(A)(1): "All geothermal wells in the Township shall be constructed in accordance with PA Act 610 (Water Well Drillers License Act)." §165-16(A): "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller..." | Section 165-12. Geothermal Well Construction Requirements / A. Construction by Licensed Driller | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Certification |  |  | §165-12: "All Geothermal Heating Systems and wells installed for the purposes of heating and cooling a facility must adhere to the International Ground Source Heat Pump Association's (IGSHPA) Design & Installation Standards and the installer(s) and well driller(s) must be certified by the IGSHPA." | Section 165-12. Geothermal Well Construction Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Decommissioning |  |  | §165-16(A): "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment form shall be submitted to the Township within thirty (30) days of abandonment." §165-16(B): "Abandonment procedures shall be subject to Township inspection." | Section 165-16. Well Abandonment | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Closed-loop Prohibitions |  |  | §165-6(A)(1): "All Geothermal Heating Systems shall be prohibited within Zone 1 of the Wellhead Protection District." | Section 165-6. Post Chapter Geothermal Heating Systems | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Open-loop Prohibitions |  |  | §165-6(A)(1): "All Geothermal Heating Systems shall be prohibited within Zone 1 of the Wellhead Protection District." Also: "Open Loop Systems shall be prohibited within Zone 2 of the Wellhead Protection District." | Section 165-6. Post Chapter Geothermal Heating Systems | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | Township | 4205581240 | Other Prohibitions/Regulations |  |  | §165-6(A)(1): "All Geothermal Heating Systems shall be prohibited within Zone 1 of the Wellhead Protection District." | Section 165-6. Post Chapter Geothermal Heating Systems | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Definition: Well |  |  | "Heat Exchange Well- a well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | SECTION 105 - DESIGN STANDARDS, A. DEFINITIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop - a geothermal heat exchanger that circulates a nontoxic antifreeze heat transfer fluid through a loop or multiple loops of polyethylene piping installed below the ground surface or within a surface water body." "Open-Loop - a geothermal heat exchanger that withdraws groundwater from a supply well, passes the groundwater through a heat pump, and discharges the temperature-altered water back to the ground in a discharge (return) well." "Direct Exchange - a type of closed-loop heat exchanger that uses loops of copper tubing installed in pits, trenches or vertical borings in the earth, through which a refrigerant is circulated." | SECTION 105 - DESIGN STANDARDS, A. DEFINITIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Driveways | 10 | feet | Minimum isolation distance for "Driveways" is "10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Right of Way | 10 | feet | Minimum isolation distance for "Property lines, all right-of-ways, easements" is "10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Property Lines | 10 | feet | Minimum isolation distance for "Property lines, all right-of-ways, easements" is "10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Building Foundation | 20 | feet | Minimum isolation distance for "Dwellings and structures" is "20 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Wastewater | 100 | feet | Minimum isolation distances include: "Subsurface sewage absorption areas, elevated sandmounds, cesspools, sewage seepage pits. 100 feet"; "Spray irrigation site perimeter, sewage sludge, and seepage disposal site. 100 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks. 50 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Private Water | 50 | feet | Minimum isolation distance for "Potable Water Well" is listed as "Hand Dug Well 50 feet" and "Drilled/Cased Well 25 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Animal Enclosures | 100 | feet | Minimum isolation distance for "Farm structures (silos, barnyards, manure pit, etc.)" is "100 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Fuel (above ground) | 300 | feet | Minimum isolation distance for "Surface or subsurface containers or tanks greater than 1000 gal. used for storage of materials that cannot be properly renovated by passage through soil. This includes, but not limited to, gasoline and all other petroleum products" is "300 feet (150 feet)." The table also lists tanks "of 1000 gal. or less... For example, the type of tanks frequently used in homes using oil for heating purposes. 50 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Sewer Lines | 50 | feet | Minimum isolation distances include "Private Sewer Drains 50 feet" and "Public sewer laterals. 10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Water Bodies | 50 | feet | Minimum isolation distance for "Delineated wetlands, flood plains, lakes, ponds or other surface waters" is "50 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Minimum isolation distance for "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles" is "300 feet (150 feet)" when borehole casing and grouting conditions apply. The table also lists "Identified NPL site (Superfund Sites) plume area. 300 feet (or as regulated by PA DEP)." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Minimum Well Depth | 15 | feet | "If the closed-loop borehole penetrates bedrock it must be grouted from a depth of fifteen feet (15') into the bedrock to the top of the borehole." | SECTION 105(B)(2)(e) | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Permit |  |  | SECTION 103: "No construction, drilling, digging, reconstruction, major repair or other change of or for any geothermal well shall commence unless the property owner, or his/her duly authorized agent, shall apply for and receive a permit..." SECTION 105(B)(3)(a): "Each borehole must be permitted using a single application. A fee will be charged for each borehole." SECTION 110: permits remain effective for "one (1) year" with a one-time written extension request allowed, "limited to thirty (30) days." | SECTION 103 - PERMITS; SECTION 105(B)(3) - PERMITTING; SECTION 110 - EFFECTIVE DATE OF PERMIT | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Inspection |  |  | SECTION 105(B)(2)(b): "The Inspection Officer or designated Township employee shall inspect to determine that the borehole is drilled in the permitted location." SECTION 106: "Upon receipt of an application for a well permit, the Township... shall within seven (7) business days, perform an inspection of the premises on which the well is to be constructed." SECTION 109: "The applicant shall be responsible for costs associated with inspection of work under this ordinance." | SECTION 105(B)(2)(b); SECTION 106 - INSPECTION; SECTION 109 | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Licensed Driller |  |  | The geothermal well permit application must include: "Name and license number of well driller." | SECTION 103 - PERMITS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Certification |  |  | "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer... in accordance with the specifications of the ground source heat pump system manufacturer, the pipe manufacturer, the International Ground Source Heat Pump Association (IGSHPA) and the National Ground Water Association." | SECTION 105(B)(2)(c) | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | Township | 4206127416 | Open-loop Prohibitions |  |  | "OPEN-LOOP' GEOTHERMAL SYSTEMS ARE PROHIBITED WITHIN THE TOWNSHIP." | SECTION 105(C)(1) | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Indiana | Indiana | Borough | 4206336816 | Definition: Geothermal Heat Pump |  |  | Figure 400.1 lists "Geothermal Energy System" as an "ACCESSORY USES" category in the Table of Permissible Uses. | §460-405 Figure 400.1 – Table of Permissible Uses |  | https://ecode360.com/IN2678/document/753169213.pdf
Pennsylvania | Juniata | Port Royal | Borough | 4206762304 | Permit |  |  | "Private wells shall be permitted within the Borough solely for the purpose of supplying underground water to a closed loop geothermal heat system servicing that particular structure and for providing solely nonpotable water for non-household consumption." | §26-209. Miscellaneous Provisions | 2010 | https://portroyalborough.org/ordinances/
Pennsylvania | Juniata | Port Royal | Borough | 4206762304 | Inspection |  |  | "Before activating such system, inspection, and approval of the system must be obtained from the Borough." | §26-209. Miscellaneous Provisions | 2010 | https://portroyalborough.org/ordinances/
Pennsylvania | Juniata | Port Royal | Borough | 4206762304 | Other Prohibitions/Regulations |  |  | "Private wells shall be permitted within the Borough solely for the purpose of supplying underground water to a closed loop geothermal heat system servicing that particular structure and for providing solely nonpotable water for non-household consumption." "Further, no water from the geothermal well shall be used for domestic water consumption." | §26-209. Miscellaneous Provisions | 2010 | https://portroyalborough.org/ordinances/
Pennsylvania | Lancaster | Clay | Township | 4207113960 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of ten (10) feet from any property line." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | Township | 4207113960 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | Township | 4207113960 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | Township | 4207113960 | Open-loop Prohibitions |  |  | "Only closed loop geothermal energy systems shall be permitted." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | Township | 4207113960 | Other Prohibitions/Regulations |  |  | "For all closed loop geothermal systems relying upon circulating fluids, only nontoxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Definition: Well |  |  | "GEOTHERMAL BOREHOLE. A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 301.5 Alternative Energy Sources - Definitions | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy generating system that uses the earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also defines system types including: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; and an air distribution system"; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A borehole that extends beneath the surface..."; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM. Water is pumped from a water well or other water source into a heat exchanger..." | Section 301.5 Alternative Energy Sources - Definitions | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Setback - Right of Way | 25 | feet | "Geothermal systems shall not encroach on public drainage, utility, roadway or trail easements of any nature." Also, "Above-ground equipment associated with geothermal pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum distance of twenty-five (25) feet from any property line, unless documentation in the form of a written agreement with the adjoining property owner(s) is provided." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum distance of... twenty-five (25) feet from any existing septic system." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum distance of one hundred (100) feet from existing potable water wells..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Permit |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards... The manufacturer specifications shall be submitted as part of the application." Also, under abandonment: "The owner shall remove the abandoned system at their expense after a demolition permit has been obtained..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Decommissioning |  |  | "Abandonment. If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... a. The heat pump and any external mechanical equipment shall be removed. b. Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | Township | 4207115824 | Open-loop Prohibitions |  |  | "Only closed loop geothermal energy systems shall be permitted. Open-loop geothermal energy systems are prohibited within the Township." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum of 25 feet from all property lines, except as otherwise specified." | § 200-55.1(D)(3)(c) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 200-55.1(D)(3)(d) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 200-55.1(D)(3)(d) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Maximum Well Depth | 20 | feet | "A horizontal closed-loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 200-55.1(D)(3)(a) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Permit |  |  | "The design and installation of geothermal energy systems shall conform to applicable industry standards and the UCC. At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 200-55.1(D)(4) Required permit | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Certification |  |  | "At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 200-55.1(D)(4) Required permit | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his or her expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 200-55.1(D)(5) Decommissioning | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | Borough | 4207118888 | Open-loop Prohibitions |  |  | "Closed-loop geothermal energy systems are allowed in all zoning districts as an accessory use to a principal use of the site. Open-loop geothermal energy systems are prohibited within the Borough." | § 200-55.1(D)(1) Zoning districts allowed | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Drumore | Township | 4207120032 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY - A source of energy generated from solar, wind, or geothermal sources, which is capable of providing basic utility provisions to a permitted use." | Section 112 Definitions | 2015 | https://www.drumoretownship.org/DocumentCenter/View/50/Article-1-Background-Provisions
Pennsylvania | Lancaster | Earl | Township | 4207120688 | Setback - Property Lines | 10 | feet | "All parts of the geothermal system shall be located a minimum distance of 10 feet from any property line." | § 27-1414.A(3) | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | Earl | Township | 4207120688 | Permit |  |  | "The following alternative energy systems are approved by right and require a zoning permit. These alternative energy systems are also subject to approval pursuant to the Township's building code, as may be applicable:" "Closed loop geothermal systems shall be permitted in all zoning districts upon approval of a zoning and building permit..." | § 27-1414.A. Alternative Energy Systems Permitted by Right | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | Earl | Township | 4207120688 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the ANSI, the IGSHPA, ASTM, the ARI, or other similar certifying organizations... The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design complies with, and the installation shall comply with, applicable industry standards." | § 27-1414.A(1) | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | Earl | Township | 4207120688 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in Earl Township." | § 27-1414.A. Alternative Energy Systems Permitted by Right | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | East Cocalico | Township | 4207120984 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system. [Added 6-19-2014 by Ord. No. 2014-05]" | § 220-11 Definitions and word usage | 2018 | https://ecode360.com/10746660
Pennsylvania | Lancaster | East Cocalico | Township | 4207120984 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature. [Added 6-19-2014 by Ord. No. 2014-05]" | § 220-11 Definitions and word usage | 2018 | https://ecode360.com/10746660
Pennsylvania | Lancaster | East Donegal | Township | 4207121032 | Definition: Geothermal Heat Pump |  |  | 'Geothermal Energy System, Closed-Loop'. A type of geothermal heating and/or cooling system, not designed or used for the generation of power, that utilizes various devices and equipment in which the heat transfer fluid (potable water) is not exposed to the atmosphere. The heat transfer fluid may contain an approved antifreeze solution. 'Closed-Loop Geothermal System, Horizontal'. A mechanism for heat exchange which consists of various devices and equipment installed horizontally in the earth and are connected to the heat exchange system of the building in which the heat transfer fluid is circulated through the piping. 'Closed-Loop Geothermal System, Vertical': A mechanism for heat exchange which consists of various devices and equipment installed vertically in the earth and are connected to the heat exchange system of the building in which the heat transfer fluid is circulated through the piping. | Section 201 - Terms Defined | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | Township | 4207121032 | Permit |  |  | 'Accessory alternative energy systems shall be permitted by right in all zoning districts, subject to the following conditions:' Section 602.4.C.1 states: 'Geothermal energy systems are permitted in any zoning district.' | Section 602.4 - Alternative Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | Township | 4207121032 | Screening |  |  | Section 602.4.C.5 states: 'Any associated above-ground appurtenances shall comply with all accessory use setback requirements of a zoning district.' Read together with Section 605, projections may include 'HVAC and other utility appurtenances.' | Section 602.4 - Alternative Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | Township | 4207121032 | Open-loop Prohibitions |  |  | Section 602.4.C.2 states: 'Only "closed-loop" geothermal energy systems are permitted. "Open-loop" geothermal energy systems are prohibited.' | Section 602.4.C - Geothermal Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | Township | 4207121032 | Other Prohibitions/Regulations |  |  | Section 602.4.C.4 states: 'Geothermal energy systems shall not encroach into any utility, roadway or other recorded easement.' | Section 602.4.C - Geothermal Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Drumore | Township | 4207121040 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." [Added 1-12-2012 by Ord. No. 1-2012] | § 120-6. Definitions | 2020 | https://eastdrumoretownship.org/wp-content/uploads/2022/04/ED-Zoning-Ordinance-2021-1.pdf?ref=writing.strisker.com
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Definition: Well |  |  | "Geothermal Boreholes - A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 202. DEFINITIONS | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also defined are system types: "Closed Horizontal Loop Geothermal System - A mechanism for heat exchange which consists of ... underground loops of piping; heat fluid; a heat pump; an air distribution system... The pipes form a closed loop and are filled with a heat transfer fluid" and "Open Loop Geothermal System - Water is pumped from a water well or other water source into a heat exchanger located in a surface building." | Section 202. DEFINITIONS | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Setback - Property Lines | 10 | feet | "All parts of the geothermal system shall be located a minimum distance of ten (10) feet from any property line." | Section 2205.BBB.1.c Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Maximum Well Depth | 20 | feet | "Closed Horizontal Loop Geothermal System ... A horizontal closed loop system shall be no more than twenty (20) feet deep." | Section 202. DEFINITIONS | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Permit |  |  | Section 2304 states: "No building or structure shall be erected, constructed, reconstructed, structurally altered, or moved, and no land or building changed in use or any new use commenced until a zoning permit has been secured from the Zoning Officer." For geothermal applications, Section 2205.BBB.1 requires application materials: "The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design complies with and the installation shall comply with applicable industry standards." | Section 2304; Section 2305; Section 2205.BBB.1 | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the ANSI, the IGSHPA, ASTM, the ARI, or other similar certifying organizations, and shall comply with the Building Code and with all other applicable Township requirements." | Section 2205.BBB.1.a Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in the Township." | Section 2205.BBB.1 Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | Township | 4207121072 | Other Prohibitions/Regulations |  |  | "In all closed loop geothermal systems relying upon circulating fluids, only nontoxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | Section 2205.BBB.1.b Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Lampeter | Township | 4207121344 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump: An energy system utilized for heating and cooling purposes through a series of heat-exchanging pipes or tubes integrated into the ground, groundwater or surface water with a heat-exchanging media that flows through a closed loop system. A pump forces either water or air through the system where it either gains or loses temperature before it circulates back to the heat pump." | Section 2020: Definitions of Specific Terms | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | Township | 4207121344 | Setback - Roads | 15 | feet | For geothermal heat pumps, "All geothermal heat pumps and appurtenant structures and/or facilities associated with their operation shall be setback from all property lines a distance of not less than the normal setback requirements for accessory buildings/structures in that zoning district or at least fifteen (15) feet from all property lines and all street right of way lines, whichever is larger." | Section 23050.1.C.1.e | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | Township | 4207121344 | Setback - Property Lines | 15 | feet | For geothermal heat pumps, "All geothermal heat pumps and appurtenant structures and/or facilities associated with their operation shall be setback from all property lines a distance of not less than the normal setback requirements for accessory buildings/structures in that zoning district or at least fifteen (15) feet from all property lines and all street right of way lines, whichever is larger." | Section 23050.1.C.1.e | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | Township | 4207121344 | Setback - Yards | 15 | feet | For geothermal heat pumps, "No visible appurtenant structures and/or facilities associated with the operation of a geothermal heat pump shall be permitted in the front yard of the lot on which it is located and shall be a minimum of fifteen (15) feet to the rear of the front face of the principal building." | Section 23050.1.C.1.f | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | Township | 4207121344 | Open-loop Prohibitions |  |  | "Geothermal heat pumps designed with an open loop system shall be prohibited." | Section 23050.1.C.1.h | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | Section 114 Definitions | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Setback - Property Lines | 10 | feet | "All parts of the geothermal system shall be located a minimum distance of ten (10) feet from any property line..." | Section 461.4 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Setback - Wastewater | 100 | feet | "All parts of the geothermal system shall be located a minimum distance of ten (10) feet from any property line, fifty (50) feet from any septic tank, and one hundred (100) feet from any septic leaching system." | Section 461.4 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Setback - Private Water | 25 | feet | "All parts of the geothermal system shall be located a minimum distance of twenty-five (25) feet from any on-lot wells." | Section 461.5 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design complies with, and the installation shall comply, with applicable industry standards." | Section 461.2 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Screening |  |  | "Above ground equipment associated with geothermal pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable Zone." | Section 461.6 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Certification |  |  | "The design and installation of Geothermal Systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the ANSI, the IGSHPA, ASTM, the ARI, or other similar certifying organizations, and shall comply with the Building Code and with all other applicable Township requirements." | Section 461.2 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | Township | 4207122336 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in the Township." | Section 461 Geothermal Energy Systems | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Elizabethtown | Borough | 4207123016 | Permit |  |  | "In addition to all other requirements to obtain a zoning permit, the application shall state the kind of system to be installed; the name, address and telephone number of the proposed installer; and the plot plan of the lot, indicating the size of lot and location of the geothermal boreholes for heat pump systems." Also: "No person shall (1) construct or install a geothermal system; (2) dig, bore, drill, replace, modify, repair or destroy a well that is intended to be or was part of a geothermal system; or (3) make any other excavation that may intersect groundwater without first obtaining a permit from the Borough." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | Borough | 4207123016 | Inspection |  |  | "Said site shall be available for inspection prior to completion." Also under System Testing: "All geothermal systems installed under the provisions of this Section must be tested." "The system shall be tested hydrostatically at 1 1/2 times the maximum system design pressure but not less than 200 psi." "The duration of each test shall be not less than 15 minutes." "All geothermal systems must be pressure checked to the original standard by a geothermal contractor licensed in the Commonwealth of Pennsylvania once every three years from the system's certification date. Results of the test shall be submitted to the Borough's Building Code Inspector." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | Borough | 4207123016 | Licensed Driller |  |  | "All boreholes shall be drilled by Pennsylvania registered/licensed water well drillers." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | Borough | 4207123016 | Certification |  |  | "All boreholes shall be drilled by Pennsylvania registered/licensed water well drillers." "The contractor shall provide data sheets indicating that the grout meets the requirements of NSF/ANSI Standard 60, Drinking Water Treatment Chemicals — Health Effects." "All geothermal systems must be pressure checked to the original standard by a geothermal contractor licensed in the Commonwealth of Pennsylvania once every three years from the system's certification date." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | Borough | 4207123016 | Decommissioning |  |  | "System Abandonment. Heat transfer fluid must be removed by displacement with grout. The top of the borehole must be uncovered and capped with grout." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | Borough | 4207123016 | Open-loop Prohibitions |  |  | "Open Loop Geothermal System Prohibited. No person shall install or maintain an open loop system within the Borough." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Lititz | Borough | 4207143816 | Other Prohibitions/Regulations |  |  | 'The following discharges are authorized unless they are determined to be significant contributors to pollution ... Non-contaminated HVAC condensation and water from geothermal systems.' Section 801.F adds: 'In the event that the Borough or DEP determines that any of the discharges identified in Section 801.E above significantly contribute to pollution of the waters of this Commonwealth, the Borough or DEP will notify the responsible person(s) to cease the discharge.' | Section 801.E | 2019 | https://www.lititzborough.org/1303/Stormwater-Management-Ordinance
Pennsylvania | Lancaster | Manheim | Borough | 4207146888 | Permit |  |  | "it will be necessary for any property owner owning property within Manheim Borough to obtain a permit from the Borough Building Code Official prior to installation of any type of geothermal boreholes for heat pump systems on said land within the Borough." The application "shall state the kind of system to be installed, the name, address and telephone number of the proposed installer, the plot plan of the lot indicating the size of lot and location of the geothermal boreholes for heat pump systems." | § 132-1 Permit required. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | Borough | 4207146888 | Inspection |  |  | "Said site shall be available for inspection prior to completion." | § 132-1 Permit required. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | Borough | 4207146888 | Certification |  |  | "Pipes must be heat fused and the joints water pressure tested, with a minimum test pressure of 200 pounds per square inch, by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | § 132-5 Regulations. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | Borough | 4207146888 | Decommissioning |  |  | "All bore holes must be backfilled (preferably with bentonite), capped and sealed." | § 132-5 Regulations. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | Borough | 4207146888 | Open-loop Prohibitions |  |  | "Types of geothermal boreholes for heat pump systems not permitted to be installed within the Borough is the open loop system." | § 132-4 Not permitted. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | Borough | 4207146888 | Other Prohibitions/Regulations |  |  | "Closed loop (vertical). May only be installed on lots where the Codes Compliance Officer determines that the lot is too small for a closed loop (horizontal) system or in cases in which rock hinders the excavation and/or installation process." | § 132-3 Permitted types. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | Township | 4207146896 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM (GEOTHERMAL HEAT PUMPS) - An energygenerating system that uses a heat pump in conjunction with the earth's thermal properties to heat and cool buildings. Such systems may be categorized as or include: A. BOREHOLES - A hole drilled or bored into the earth into which piping is inserted for use in a closed-vertical-loop geothermal system. B. CLOSED-LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump and a water source heat pump in which the heat transfer fluid is not exposed to the atmosphere. The heat transfer fluid is potable or beneficial reuse water and may have approved antifreeze added. C. OPEN-LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a water pump to deliver water from a well or other source to a heat exchanger. The discharge water from the heat exchanger may be returned to the subsurface through an injection or recharge well or infiltration bed or may be discharged into a pond, lake or stream." | SECTION 503. DEFINITIONS | 2023 | https://www.manheimtownship.org/DocumentCenter/View/7917/8ARTICLE-5---Definitions
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, CLOSED LOOP A type of geothermal heating or cooling system, not designed or used for the generation of power, that utilized a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere..." and "GEOTHERMAL ENERGY SYSTEM, OPEN LOOP A type of geothermal heating or cooling system that utilizes a water-supply well and water pump to deliver ground water to a water-source heat pump." | § 270-32. Definitions | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum of 25 feet from all property lines, except as otherwise specified." | § 270-63.D(14)(d)[3](c) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 270-63.D(14)(d)[3](d) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells..." | § 270-63.D(14)(d)[3](d) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Maximum Well Depth | 20 | feet | "A closed horizontal loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 270-63.D(14)(d)[3](a) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Permit |  |  | WP District: "Any geothermal exchange system shall only be permitted if the applicant provides written evidence that the system will comply with the DEP Ground Source Heat Pump Manual as it pertains to protection of water quality." Also, "Construction and Permit. The design and installation of geothermal energy systems shall conform to applicable industry standards and the UCC. At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 270-49.E(4); § 270-63.D(14)(d)[4] | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Decommissioning |  |  | "If the geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his/her expense after a demolition permit has been obtained... (i) The heat pump and any external mechanical equipment shall be removed; and (ii) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with the applicable regulations. The top of the pipe, coil, or boring shall be uncovered and grouted." | § 270-63.D(14)(d)[5] | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Open-loop Prohibitions |  |  | "Closed-loop geothermal energy systems are allowed in all zoning districts as an accessory use to a principal use of the site. Open-loop geothermal energy systems are prohibited within the Borough." | § 270-63.D(14)(d)[1] | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | Borough | 4207151656 | Other Prohibitions/Regulations |  |  | Within the WP Wellhead Protection District, the following uses are prohibited: "Underground injection wells." | § 270-49.E(3)(f) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mountville | Borough | 4207152016 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY SYSTEM — Any one or more method and facilities used in the conversion, storage, and distribution including electrical infrastructure, transmission lines, and other appurtenant structures and facilities of renewable energy sources, including but not limited to sunlight, wind, rain, tides, and geothermal heat." | § 202 Definitions | 2019 | https://ecode360.com/42252150
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Definition: Well |  |  | "GEOTHERMAL WELL - a drilled hole used in connection with a geothermal system." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 1. Definitions | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP GEOTHERMAL SYSTEM - a geothermal system in which the same liquid is continuously running through piping in a closed circuit, and during its operation, no new liquid is introduced to the system or used liquid discharged from the system." "OPEN LOOP GEOTHERMAL SYSTEM - a geothermal system in which liquid is run through piping after being drawn from a source and is then discharged to that source or an alternate location." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 1. Definitions | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Setback - Roads | 25 | feet | "No well shall be permitted within 25 feet of a cartway." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Setback - Property Lines | 25 | feet | "A geothermal well shall be set back at least 25 feet from all lot lines." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Setback - Wastewater | 100 | feet | "No geothermal well shall be located within 100 feet of any existing drinking water wells or any planned drinking water wells, or 100 feet of any septic system." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Setback - Public Water | 100 | feet | "No geothermal well shall be located within 100 feet of any existing drinking water wells or any planned drinking water wells..." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Permit |  |  | "No person shall (1) construct or install a geothermal system, (2) dig, bore, drill, replace, modify, repair, and/or destroy a well that is, is intended to be, or was part of a geothermal system, or (3) make any other excavation that may intersect groundwater without first obtaining a permit from the Borough. A permit is required for any geothermal system within New Holland Borough." The ordinance also requires that "No permit for such a well shall be issued until the plans, specifications, and site plans have been approved by the Borough for compliance with this Part." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 2. Permits | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Decommissioning |  |  | "A geothermal system shall be abandoned in a manner acceptable to the Borough and shall comply with the laws, rules, and regulations applicable to the abandonment of water wells. Any and all heat transfer fluids must be removed by displacement with grout in a manner acceptable to the Borough. The top of the borehole must be uncovered and capped with grout in a manner acceptable to the Borough." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | Borough | 4207153696 | Open-loop Prohibitions |  |  | "No person shall construct or install an Open Loop Geothermal System." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 2. Permits | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY PRODUCTION FACILITIES - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from natural sources (e.g. solar panels, wind turbines, hydro turbines, geo-thermal exchangers, and similar technologies.)" | Section 112 Specific Words and Phrases | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of twenty five feet (25) feet from any property line." | Section 404.1.3 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Setback - Private Water | 200 | feet | For open loop systems with underground injection, "The return well shall be located a minimum distance of two hundred (200) feet from wells on adjacent properties" and "The return well shall be located a minimum distance of one hundred (100) feet from the on-site well." | Section 404.1.5.2(F)-(I) | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Maximum Well Depth | 20 | feet | "Horizontal closed loop systems shall be no more than twenty (20) feet deep." | Section 404.1.4.2 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." Also, Section 400.2 states for permitted uses: "these standards must be satisfied prior to approval of any application for a land development (when applicable) or a zoning permit." Section 200.3.1, 201.3.1, 202.3.1, 203.3.1, 204.3.1, and 418.6.1 list "Alternative energy production facilities (Geothermal Systems...)" as accessory uses "subject to the requirements of Section 404." | Section 404.1 Geothermal Systems | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Licensed Driller |  |  | "Vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | Section 454.21.3 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Open-loop Prohibitions |  |  | "Discharge of water from open loop systems into sanitary sewer systems shall be prohibited, except upon approval by the sanitary sewage system provider." "Discharge of water from open loop systems into storm sewers shall not be permitted." "The use of open loop systems within identified well head protection areas is prohibited." | Section 404.1.5.2(A)-(B),(L) | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | Township | 4207162832 | Other Prohibitions/Regulations |  |  | "Only the following types of geothermal energy systems shall be permitted: ... Closed horizontal loop; ... Closed vertical loop; and ... Open horizontal loop systems relying upon injection wells or water courses." | Section 404.1.2 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, CLOSED-LOOP — A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." "GEOTHERMAL ENERGY SYSTEM, OPEN-LOOP — A type of geothermal heating or cooling system that utilizes a water-supply well and a water pump to deliver groundwater to a water-source heat pump." | § 217-2 Definitions and word usage | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Setback - Right of Way | 10 | feet | Aboveground equipment associated with geothermal pumps "shall meet all minimum accessory structure setbacks required for the zoning district" and "shall not be installed in ... the yard of a corner lot adjacent to a public right-of-way." | § 217-3C(6) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Setback - Property Lines | 10 | feet | "Geothermal energy systems shall be located a minimum of 10 feet from all property lines, except as otherwise specified." | § 217-3C(3) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Setback - Yards | 10 | feet | "Aboveground equipment associated with geothermal pumps shall not be installed in the front yard of any lot or the yard of a corner lot adjacent to a public right-of-way and shall meet all minimum accessory structure setbacks required for the zoning district." | § 217-3C(6) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Setback - Wastewater | 100 | feet | "Geothermal energy systems shall be located a minimum of 50 feet from treatment tanks, dosing tanks, lift pump tanks, filter tanks and chlorine contact/storage tanks of an on-lot sewage disposal system. Geothermal energy systems shall be located a minimum of 100 feet from the absorption area of an on-lot sewage disposal system. Geothermal energy systems shall be located a minimum of 100 feet from the perimeter of any spray field of an on-lot sewage disposal system." | § 217-3C(5) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells." | § 217-3C(4) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Maximum Well Depth | 20 | feet | "A horizontal closed-loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 217-3C(1) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Permit |  |  | "Any person seeking to install a geothermal energy system shall apply for and obtain a permit from the Borough prior to commencing installation." The applicant must file information demonstrating compliance and pay the Borough fee. The ordinance also requires submission of "manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 217-3D | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Inspection |  |  | "Any person installing a geothermal energy system shall obtain all inspections required by the UCC. The Construction Code Official shall have the authority to inspect for compliance with all requirements of this chapter as well as compliance with all requirements of the UCC." | § 217-3E | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed" and "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 217-3F | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | Borough | 4207163064 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems are permitted within the Borough. Open-loop geothermal energy systems are prohibited within the Borough." | § 217-3A | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES – A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 202.A.142.c | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY SYSTEM – A system or facility used in the conversion, storage, and distribution of renewable energy sources, including electrical infrastructure, transmission lines, and other appurtenant structures and facilities. For purposes of this Zoning Ordinance, this term includes but not limited to renewable energy sources such as sunlight, wind, rain, tides, and geothermal heat facilities." | Section 202.A.23 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL TERMS & PHRASES ... when used in Article 5 ... relating to the 'Geothermal Energy Systems' (§ 502.A.) shall have the meaning given to them..." including: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM – A mechanism for heat exchange ... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM – A borehole that extends beneath the surface. Pipes are installed with U-bends at the bottom of the borehole..."; "GEOTHERMAL ENERGY SYSTEM – An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings."; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM – Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | Section 202.A.142 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | Section 502.A.4.b | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Permit |  |  | Section 502.A.1 states: "The manufacturer specifications shall be submitted as part of the application." Section 502 governs accessory alternative energy systems, including geothermal energy systems, so geothermal applications must include manufacturer specifications as part of the approval application. | Section 502.A.1; Section 902 (referenced) | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | Section 502.A.1 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | Township | 4207163440 | Other Prohibitions/Regulations |  |  | Section 502.A.2 states: "Only the following types of geothermal energy systems shall be permitted: a. Closed horizontal loop; b. Closed vertical loop; and c. Open horizontal loop systems relying upon injection wells or water courses." Section 502.A.5.b.(6) further states: "The use of open loop systems within identified well head protection areas is prohibited." | Section 502.A.2; Section 502.A.6 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM – an energy generating system that uses the Earth’s thermal properties in conjunction with a power source such as electricity to provide greater efficiency in the heating and cooling of buildings." | §104. Definitions | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of twenty five feet (25) feet from any property line." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Permit |  |  | "In addition to all other requirements to obtain a zoning permit, the applicant shall state the kind of system to be installed; the name, address and telephone number of the proposed installer; and the plot plan of the lot, indicating the size of the lot and the location of the geothermal boreholes for the heat pump system." Also: "Nor shall any person dig, bore, drill, replace, modify or destroy a well that is intended to be or was part of a geothermal system nor make any other excavation that may intersect groundwater without first obtaining a permit from the Borough." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Inspection |  |  | "Said site shall be available for inspection prior to completion." Also: "All geothermal systems installed under the provisions of this Section shall be tested hydrostatically at one and one half times the maximum system design pressure, but not less than 200 psi. The duration of each test shall be not less than 15 minutes." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Licensed Driller |  |  | "All bore holes shall be drilled by a Pennsylvania registered and licensed water well driller." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Certification |  |  | "All bore holes shall be drilled by a Pennsylvania registered and licensed water well driller." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a permit has been obtained... (1) The heat pump and any external mechanical equipment shall be removed and (2) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Open-loop Prohibitions |  |  | "Open loop geothermal systems are prohibited. No person shall install, maintain or operate an open loop system within the Borough." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | Borough | 4207176400 | Other Prohibitions/Regulations |  |  | "The only type of geothermal boreholes permitted to be drilled within the Borough are: (1) Air to air; (2) Closed loop horizontal; and (3) Closed loop vertical." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | SECTION 113 SPECIFIC WORDS AND PHRASES | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Setback - Property Lines | 20 | feet | "No geothermal system sub-surface loops and related geothermal boreholes shall be located closer than... twenty feet (20') from any and any property lines." | SECTION 405.T.4 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Setback - Wastewater | 25 | feet | "No geothermal system sub-surface loops and related geothermal boreholes shall be located closer than... twenty-five feet (25’) from any existing or planned on-lot sewage disposal systems..." | SECTION 405.T.4 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Setback - Public Water | 100 | feet | "No geothermal system sub-surface loops and related geothermal boreholes shall be located closer than one hundred feet (100’) from any existing or planned drinking water wells..." | SECTION 405.T.4 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Permit |  |  | "Within every Zone, alternative energy systems are permitted accessory uses by right" and "Any physical modification to an existing alternative energy system that materially alters the size, type and quantity of the facilities shall require a zoning permit"; also "In addition to those materials required in Section 901.B. of this Ordinance for a zoning permit, applicants for alternative energy systems shall be required to submit..." Section 405.T governs geothermal systems as part of these alternative energy systems. | SECTION 405 ALTERNATIVE ENERGY SYSTEMS | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Inspection |  |  | "With respect to each geothermal system well installation, the Pennsylvania-licensed well driller and/ or system installer shall provide to the Township, before activation of the system, copies of... Written documentation of the geothermal system testing and certification." | SECTION 405.T.7.D | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | SECTION 405.T.3 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Certification |  |  | "Prior to installation, all installation specifications and drawings for the geothermal system must be certified by a registered engineer within the Commonwealth of PA as conforming to the installation standards of the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations." | SECTION 405.T.2 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Decommissioning |  |  | "The applicant shall maintain the geothermal system in a safe condition and good repair at all times. Whenever a geothermal system endangers the public safety, the Zoning Officer shall give written notice to the owner... that such geothermal system shall be made safe or removed. The disposal of geothermal systems shall comply with all applicable Township, county, state, and federal regulations" and "In the event of the proposed discontinuance of the use of the geothermal system, a system closure plan will be prepared and submitted to the Township for its approval by the landowner prior to the conveyance by the landowner of the land to any third party." | SECTION 405.T.6 and 405.T.7.E.2 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | Township | 4207179080 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be permitted." | SECTION 405.T The following provisions shall specifically apply to geothermal systems | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Warwick | Township | 4207181168 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM" means "[a]n energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 340-10 Definitions | 2026 | https://ecode360.com/11671453
Pennsylvania | Lancaster | Warwick | Township | 4207181168 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM" means "[a] type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, nontoxic heat transfer fluid; a heat pump; and an air distribution system." "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM" means "[a] type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM" means "[a] type of geothermal heating and/or cooling system that utilizes a water-supply well, or other source, and a pump to deliver groundwater to a heat exchanger." | § 340-10 Definitions | 2026 | https://ecode360.com/11671453
Pennsylvania | Lancaster | West Cocalico | Township | 4207182728 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, CLOSED-LOOP" is defined as "A type of geothermal heating or cooling system, not designed or used for the generation of power, that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." It further states: "The heat transfer fluid is potable water and may have approved antifreeze added." "GEOTHERMAL ENERGY SYSTEM, OPEN LOOP" is defined as "A type of geothermal heating or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump. The discharge water from the water-source heat pump may be returned to the subsurface through a recharge well or infiltration bed or may be discharged into a pond, lake or stream. A spring may also be the source of the ground water supply." | GEOTHERMAL ENERGY SYSTEM, CLOSED-LOOP / GEOTHERMAL ENERGY SYSTEM, OPEN LOOP | 2024 | https://ecode360.com/37307777
Pennsylvania | Lancaster | West Hempfield | Township | 4207183152 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES" means "A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 201.2 Terms defined. GEOTHERMAL TERMS [Added 8-3-2010 by Ord. No. 4-10] | 2020 | https://ecode360.com/32127028
Pennsylvania | Lancaster | West Hempfield | Township | 4207183152 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM" means "An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." The same geothermal terms section also defines system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM" as "A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system" and "OPEN LOOP GEOTHERMAL SYSTEM" as a system where "Water is pumped from a water well or other water source into a heat exchanger located in a surface building." | § 201.2 Terms defined. GEOTHERMAL TERMS [Added 8-3-2010 by Ord. No. 4-10] | 2020 | https://ecode360.com/32127028
Pennsylvania | Lancaster | West Hempfield | Township | 4207183152 | Maximum Well Depth | 20 | feet | The definition of "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM" states: "A horizontal closed loop system shall be no more than 20 feet deep." | § 201.2 Terms defined. GEOTHERMAL TERMS [Added 8-3-2010 by Ord. No. 4-10] | 2020 | https://ecode360.com/32127028
Pennsylvania | Lebanon | North Cornwall | Township | 4207554928 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | SECTION 113 - SPECIFIC WORDS AND PHRASES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | Township | 4207554928 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | SECTION 113 - SPECIFIC WORDS AND PHRASES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | Township | 4207554928 | Setback - Private Water | 20 | feet | "No geothermal system sub-surface loops will be located closer than twenty (20) feet from any existing or planned drinking water wells." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | Township | 4207554928 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | Township | 4207554928 | Certification |  |  | "The geothermal system shall conform to the International Ground Source Heat Pump Association (IGSHPA) installation standards, as same may be amended and updated from time." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | Township | 4207554928 | Open-loop Prohibitions |  |  | "The following provisions shall specifically apply to geothermal systems: a. Only closed loop geothermal systems shall be permitted." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | South Londonderry | Township | 4207572296 | Setback - Private Water | 20 | feet | 'No geothermal system sub-surface loops will be located closer than twenty (20) feet from any existing or planned drinking water wells.' | Section 404.F | 2024 | https://www.southlondonderry.org/uploads/6/1/2/6/61268441/slt_2024_zoning_ordinance_final.pdf
Pennsylvania | Lebanon | South Londonderry | Township | 4207572296 | Open-loop Prohibitions |  |  | 'The following provisions shall specifically apply to geothermal systems: Only closed loop geothermal systems shall be permitted.' | Section 404.F | 2024 | https://www.southlondonderry.org/uploads/6/1/2/6/61268441/slt_2024_zoning_ordinance_final.pdf
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Definition: Well |  |  | "GEOTHERMAL WELL — Any excavation that is drilled, cored, bored, washed, driven, dug, jetted or otherwise constructed where the intended use of such excavation is for the circulation of geothermal fluid vertically, or the location, requisition or artificial recharge of groundwater. (includes open- and closed-loop vertical systems)." | § 12-102 Definitions | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Definition: Geothermal |  |  | "GEOTHERMAL HEAT — Heat derived from geothermal resources, or heat derived from groundwater." Also: "GEOTHERMAL FLUID — Any fluid transporting or capable of transporting geothermal heat." | § 12-102 Definitions | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEATING SYSTEM — A geothermal heat pump system which relies on the contained circulation of geothermal fluids to obtain and to utilize geothermal resources." Also: "CLOSED-LOOP SYSTEMS — Geothermal heat pump system which relies on the contained circulation of geothermal fluids through any underground loop of pipes..." and "OPEN-LOOP SYSTEM — A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring, or surface water." | § 12-102 Definitions | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Permit |  |  | § 12-107: "Any persons desiring to construct, install, or alter a geothermal heating system within the Township shall first apply for a geothermal heating system permit... No person shall commence construction or alteration of a geothermal heating system prior to... applying for and receiving a permit." § 12-106: "All open-loop geothermal heating systems are permitted, provided they are reviewed and approved by the Township prior to construction" and "Vertical closed-loop systems shall be permitted, provided they are reviewed and approved by the Township prior to construction." § 12-111: "Before any drilling or site preparation begins the well driller shall apply for a well permit from the Township" and "No geothermal well shall be put into service without receiving a geothermal well permit..." | §§ 12-106, 12-107, 12-111 | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Inspection |  |  | § 12-115: "The following inspections shall be required by the Township: Site inspection before any work is done... Inspection of the installed loop (pressure test); Inspection of grouting; Inspection of the completely installed system before operations commence and upon commencement of operations; Periodic inspections no less than once every three years; Inspection if geothermal system or well is abandoned..." § 12-116: "Abandonment procedures shall be subject to Township inspection." § 12-117 authorizes Township entry "for purposes of inspecting geothermal facilities or monitoring the operational characteristics of such facilities..." | §§ 12-115, 12-116, 12-117 | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Licensed Driller |  |  | § 12-112(A)(1): "All geothermal wells in the Township shall be constructed in accordance with Pennsylvania Act 610 (Water Well Drillers License Act)." § 12-116: "All abandoned wells must be filled and sealed by a PA/DCNR licensed water well driller..." § 12-111(A): "Before any drilling or site preparation begins the well driller shall apply for a well permit from the Township." | §§ 12-111, 12-112, 12-116 | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Certification |  |  | "All geothermal heating systems and wells installed for the purposes of heating and/or, cooling a facility must adhere to the International Ground Source Heat Pump Associations (IGSHPA) design and installation standards, and the installer(s) and well driller(s) must be certified by the IGSHPA." | § 12-112 Geothermal Well Construction Requirements | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | Township | 4207583312 | Decommissioning |  |  | "All abandoned wells must be filled and sealed by a PA/DCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR water well abandonment form shall be submitted to the Township within 30 days of abandonment. Abandonment procedures shall be subject to Township inspection." | § 12-116 Well Abandonment | 2025 | https://ecode360.com/30862575
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Setback - Right of Way | 20 | feet | Table 27-4.H.a states: "Dedicated public Right-of-Way — 20" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, underground geothermal systems shall be located a minimum distance of 10 feet from any Lot Line." | §27-412 Accessory Uses, 2.I.(3)(b) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Setback - Wastewater | 100 | feet | Table 27-4.H.a states: "Septic tanks, aerobic tanks or holding tanks — 50" feet and "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields — 100" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Setback - Sewer Lines | 50 | feet | Table 27-4.H.a states: "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 50" feet; and for "Existing water and forced sewer buried utilities and/or utility trenches" the system must be "Outside existing Easement or, if no Easement exists, no less than 50 feet from the utility or trench center line." | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Setback - Water Bodies | 50 | feet | Table 27-4.H.a states: "Lakes, ponds, streams, or other surface waters — 50" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table 27-4.H.a states: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles — 100" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Permit |  |  | "The owner shall remove the abandoned system at their expense after a demolition Permit has been obtained..." | §27-412 Accessory Uses, 2.I.(5) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Certification |  |  | "The installer must have at least one representative who is certified by the International Ground Source Heat Pump Association (IGSHPA)." | §27-412 Accessory Uses, 2.I.(1) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition Permit has been obtained..." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations"; and "All abandoned wells shall be reported to PA DCNR on its forms and a copy provided to the municipality." | §27-412 Accessory Uses, 2.I.(5) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | Borough | 4207723584 | Open-loop Prohibitions |  |  | "Open-Loop Geothermal Energy Systems and any system not meeting the definition of a Closed-Horizontal-Loop Geothermal Energy System or closed-vertical-loop geothermal energy system are prohibited in the Borough." | §27-412 Accessory Uses, 2.I. Geothermal Energy Systems | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Fountain Hill | Borough | 4207727008 | Permit |  |  | The fee schedule lists: "GENERATOR (backup power) OR GEOTHERMAL SYSTEMS: - $ 200.00 plan submission, Building, Mechanical and Electrical Only." The resolution also states under surcharge rates: "FAILURE TO OBTAIN A PERMIT BEFORE WORK BEGINS" and "ALL PERMIT FEES DOUBLED." | Uniform Construction Code Building Permit Fee Schedule / GENERATOR (backup power) OR GEOTHERMAL SYSTEMS | 2022 | https://www.fountainhill.org/wp-content/uploads/2022/03/Current-Fee-Schedule.pdf
Pennsylvania | Lehigh | Fountain Hill | Borough | 4207727008 | Inspection |  |  | The resolution states: "Please call 610-867-5124 for any costs not included on these sheets or with any questions. TO SCHEDULE INSPECTIONS REQUIRE 48 HOURS NOTICE." It also includes geothermal systems under the building permit schedule as "Building, Mechanical and Electrical Only," and separately provides "RESIDENTIAL BUILDING INSPECTIONS (when not included in above pricing): $ 75.00 per hour as well as failed inspections." | Uniform Construction Code Building Permit Fee Schedule / MISCELLANEOUS FEES; note on scheduling inspections | 2022 | https://www.fountainhill.org/wp-content/uploads/2022/03/Current-Fee-Schedule.pdf
Pennsylvania | Lehigh | South Whitehall | Township | 4207772632 | Definition: Geothermal Heat Pump |  |  | "GEOEXCHANGE ENERGY SYSTEM, OPEN LOOP — A geoexchange energy system which extracts surface or ground water into a heat pump, and discharges water back into the ground through a different well." | § 350-05 Definition of terms | 2019 | https://ecode360.com/48196093
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Setback - Private Water | 20 | feet | "No geothermal system sub-surface loops will be located closer than twenty feet (20') from any existing drinking water wells or any planned drinking water wells;" | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Permit |  |  | "Prior to installation, all installation specifications and drawings for the geothermal system must be approved by the Township's geotechnical consultant as conforming to the International Ground Source Heat Pump Association (IGSHPA) installation standards..." | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Inspection |  |  | Before activation, the driller and/or installer must provide "written documentation of the geothermal system testing and certification"; for closed-loop systems, "System leak testing shall be 150 percent higher than operating pressure." | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller;" | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Certification |  |  | "Prior to installation, all installation specifications and drawings for the geothermal system must be approved by the Township's geotechnical consultant as conforming to the International Ground Source Heat Pump Association (IGSHPA) installation standards..." and before activation the driller and/or installer must provide "written documentation of the geothermal system testing and certification." | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Decommissioning |  |  | "In the event of the proposed discontinuance of the use of the geothermal system, a system closure plan will be prepared and submitted to the Township for its approval by the landowner prior to the conveyance by the landowner of the land to any third party." | Section 404.H.e.2 | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Open-loop Prohibitions |  |  | "Every geothermal system to be installed or constructed in areas of the Township underlain by carbonate bedrock, as depicted on the Natural and Cultural Features Map as Carbonate Geology, and Floodplain Zones, Riparian Buffers, Wetlands and Buffers, and PNDI sites regulated by Section 515 of this Ordinance must be a 'closed-loop' system." | Section 404.H.f | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | Township | 4207779288 | Other Prohibitions/Regulations |  |  | "No geothermal system shall be connected in any way to any facilities for sanitary sewer or stormwater management." | Section 404.H.g | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Luzerne | Hazleton | City | 4207933408 | Screening |  |  | "All mechanical, electrical, communication, and service equipment, including satellite dishes, air conditioning units, large vents and vent pipes, heat pumps and mechanical equipment, and other appurtenances shall be concealed by or integrated within the roof form or screened from view at ground level of nearby streets by parapets, walls, fences, landscaping, or other approved means." | SECTION 505. DOWNTOWN OVERLAY DISTRICT, s. Screening | 2020 | https://hazletoncity.org/images/Hazleton_2020_Draft_Zoning_Ordinance.pdf
Pennsylvania | Mercer | Springfield | Township | 4208573080 | Definition: Well |  |  | "Abandonment of Well – An abandoned or unused well may be defined as one of the following: ... 6. An inactive geothermal groundwater heat exchange system." | Section 602.2 Special Definitions | 2018 | http://www.springfield-mercer.org/images/_4-2018_Zoning_Ordinance_-_October_2,_2018.pdf
Pennsylvania | Monroe | Paradise | Township | 4208957856 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP Any geothermal, earth-coupled, geoexchange, water-coupled, groundwater, ground-coupled, closed-loop, coiled, open, or water source heat pump system used for heating and/or cooling which utilizes groundwater extracted from a well." | § 1-16 Defined terms | 2026 | https://ecode360.com/38606445
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Right of Way | 25 | feet | The geothermal setback table lists "Dedicated public right-of-way and property lines — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Property Lines | 25 | feet | The geothermal setback table lists "Dedicated public right-of-way and property lines — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Building Foundation | 25 | feet | The geothermal setback table lists "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved) — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Wastewater | 100 | feet | The geothermal setback table requires: "Septic tanks, aerobic tanks, or holding tanks — at least 100 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields — 100 feet"; "Sewage seepage pits and cesspools — at least 100 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites — at least 100 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Animal Enclosures | 25 | feet | The geothermal setback table lists "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Fuel (above ground) | 25 | feet | The geothermal setback table lists "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Water Lines | 15 | feet | The geothermal setback table requires separation from "Existing water and forced sewer buried utilities and/or utility trenches" of "at least 15 feet or outside easement." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Sewer Lines | 15 | feet | The geothermal setback table lists "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 5-15 feet or according to easement" and "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The geothermal setback table requires wells and boreholes to be separated from "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" by "300 feet 100-150 feet (if borehole is cased and grouted inside and out)." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." | § 470-31.F(3) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well." | § 470-31.F(6) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well. In all cases, the well drilling rig must also be approved by Pennsylvania Department of Environmental Protection." | § 470-31.F(6) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Decommissioning |  |  | The ordinance requires the geothermal system to be "installed, maintained, and decommissioned in standards conforming to International Ground Source Heat Pump Association (IGSHPA) Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards" and further states: "If the geothermal energy system is ever abandoned or enters into a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the geothermal energy system within 12 months from the date the system enters such a state. Any earth disturbance as a result of the removal or permanent sealing of the geothermal energy system shall be graded, reseeded and revegetated with native species to its pre-disturbance condition." | § 470-31.F(5), § 470-31.F(13) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | Township | 4208961728 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems are prohibited." | § 470-31.F(2) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) - Any system of mechanical and electrical facilities designed for the purpose of withdrawing heat from, or discharging heat to the ground, groundwater or surface waters." | ARTICLE II: Chapter 27, Part 2, Section 202 (Definitions) | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Setback - Roads | 10 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 10 feet from any property line or public road right-of-way line." | ARTICLE I, Section 508, Paragraph 1, H.2.a | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 10 feet from any property line or public road right-of-way line." | ARTICLE I, Section 508, Paragraph 1, H.2.a | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Permit |  |  | Inspection subsection: "Applicable plan review and inspection fees shall be paid at the time of application for a building permit." Abandonment subsection: "The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." | ARTICLE I, Section 508, Paragraph 1, H.4.a; H.6 | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Inspection |  |  | "The Township Building Code Inspector or his or her designee shall observe the pressure testing." "The Township Building Code Inspector or his or her designee shall observe grouting of the vertical boreholes for the GSHP system wells." "The GSHP system installer shall contact the Township Building Code Inspector or his or her designee a minimum of 48 hours in advance to inspect grouting and to verify pressure testing." | ARTICLE I, Section 508, Paragraph 1, H.4.b-d | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Licensed Driller |  |  | "GSHP system well drilling shall only be undertaken by a Pennsylvania licensed well driller." | ARTICLE I, Section 508, Paragraph 1, H.1.c | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Decommissioning |  |  | Operation and maintenance: "A GSHP system closure plan in the event of the discontinuation of the use of the geothermal system." Abandonment: "If the GSHP system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." Further, "The heat pump and any external mechanical equipment shall be removed." "All abandoned wells shall be filled and sealed according to the PADEP/DCNR Water Well Abandonment Guidelines." "Pipes or coils below the land surface shall be filled and capped in accordance with IGSHPA standards." | ARTICLE I, Section 508, Paragraph 1, H.5.b.2; H.6 | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | Township | 4208974880 | Open-loop Prohibitions |  |  | "Only closed horizontal loop or closed vertical loop GSHP systems are permitted. Open-loop GSHP systems are not permitted." | ARTICLE I, Section 508, Paragraph 1, H.1.a | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Montgomery |  | County | 42091 | Definition: Well |  |  | "GEOTHERMAL WELL - A well installed for the purpose of extracting water for heating or cooling." | Section 17-4 Definitions |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Definition: Geothermal Heat Pump |  |  | "CLOSED-LOOP GEOTHERMAL WELL SYSTEM - A heat pump system using groundwater, surface water, or sub-surface as the heating/cooling source which continuously circulates a heat transferring liquid through sealed pipe and a heat exchanger. The internal liquid is not consumed from or discharged into the environment." "OPEN-LOOP GEOTHERMAL WELL SYSTEM- A heat pump system using groundwater or surface water as the heat/cooling source, circulated through the heat exchanger and returned to the environment via a separate discharge point." | Section 17-4 Definitions |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Setback - Wastewater | 100 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." Wastewater-related entries include: "Community spray irrigation site: 100 feet"; "Sewage sludge and septage disposal sites" under the same 100-foot line; "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits, single family spray irrigation system, etc." at "100 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks" at "50 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Setback - Animal Enclosures | 200 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure" at "200 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Setback - Sewer Lines | 50 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Gravity sewer lines and drains carrying domestic sewage or industrial waste" at "50 feet," with a narrower exception of "10 feet" for specified pipe materials, and "Sewer lines and drains carrying domestic sewage or industrial waste under pressure" at "50 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Setback - Water Bodies | 13 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Delineated wetlands or floodplains" at "25 feet." Applying the ordinance's express closed-loop rule yields a minimum closed-loop distance of one half that listed amount. | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Setback - Hazardous Materials/Fertilizers | 300 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Commercial preparation area or storage area of hazardous spray materials, fertilizers or chemicals; salt piles" at "300 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Permit |  |  | "It shall be unlawful to install or modify an individual water supply well, irrigation well or geothermal well without first obtaining a permit from MCHD." | Section 17-5 GENERAL |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Inspection |  |  | "Prior to geothermal well construction, a site meeting with MCHD will be required to layout the proposed design under actual field conditions. Any changes required based on the field design must be addressed by the designing firm before construction begins." | Section 17-6 Inspection procedure for geothermal well system |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Licensed Driller |  |  | "All permit-required wells shall be constructed by a PADCNR-licensed water well driller or an IGSHPA accredited geothermal system installer, if applicable." | Section 17-5 GENERAL |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Certification |  |  | "All permit-required wells shall be constructed by a PADCNR-licensed water well driller or an IGSHPA accredited geothermal system installer, if applicable." | Section 17-5 GENERAL |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery |  | County | 42091 | Decommissioning |  |  | "All abandoned wells must be filled and sealed according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment form shall be submitted to MCHD within thirty (30) days of abandonment." "If applicant/homeowner chooses not to abandon the well, a nonabandonment declaration must be signed and submitted to MCHD within thirty (30) days." | Section 17-8 Abandoned Wells |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Definition: Well |  |  | "GEOTHERMAL WELL. A well(s) installed for the purpose of heating and/or cooling the dwelling or building on a property." | § 680-210 Definitions | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Definition: Geothermal Heat Pump |  |  | "CLOSED-LOOP GEOTHERMAL HEATING/COOLING SYSTEM. A closed or sealed system designed to heat and/or cool a dwelling or building which circulates water, heat transfer fluid or refrigerant through underground loops. The loops are installed either in closed-loop boreholes or horizontally in trenches or ponds and exchange heat with the ground." "GEOTHERMAL HEATING/COOLING SYSTEM. A mechanism for heat exchange which consists of the following basic elements: underground loops of piping, heat transfer fluid, a heat pump, and air distribution system." "OPEN-LOOP GEOTHERMAL HEATING/COOLING SYSTEM. An open or unsealed system designed to heat and/or cool a building which uses a ground water supply well to extract groundwater which is passed through a heat pump and into any discharge well or other area." | § 680-210 Definitions | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Setback - Right of Way | 10 | feet | Under "Isolation distances," the minimum setback from "Property lines and all rights-of-way and easements" is "10" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Setback - Property Lines | 10 | feet | Under "Isolation distances," the minimum setback from "Property lines and all rights-of-way and easements" is "10" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Setback - Wastewater | 50 | feet | Under "Isolation distances," closed-loop geothermal boreholes must be at least "50" feet from "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits" and at least "25" feet from "Septic tanks, aerobic tanks, sewage pump tanks and holding tanks." | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Setback - Fuel (above ground) | 300 | feet | Under "Isolation distances," the minimum setback from "Surface or subsurface containers or tanks of greater than 1,000 gal. used for storage of materials that cannot be properly disposed of by passage through the soil. This includes, but is not limited to, gasoline and all other petroleum products" is "300" feet; the table also shows "(If borehole is grouted and cased inside and out) (150)." The table further requires "30" feet from "Surface or subsurface containers or tanks of less than 1,000 gal.... For example, the type of tank used in homes for storing oil for heating purposes." | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Setback - Water Bodies | 10 | feet | Under "Isolation distances," closed-loop geothermal boreholes must observe minimum setbacks from "Delineated wetlands, floodplains, lakes, ponds, or other surface waters" of "10" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Setback - Hazardous Materials/Fertilizers | 5 | feet | Under "Isolation distances," the minimum setback from a "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" is "5" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Permit |  |  | "Geothermal heating/cooling system equipment shall be permitted as an accessory use in any zoning district upon receipt of a permit from the Zoning Officer." "No person shall install, construct, drill, or excavate to facilitate the construction or installation of a geothermal heating/cooling system for use as a heating and/or cooling system for a structure, residential or nonresidential within the Borough without first obtaining a geothermal heating/cooling system permit from the Borough. No person shall drill or excavate to repair or modify or to facilitate the repair or modification of a ground source heat pump system in the Borough without first obtaining a ground source heat pump permit." | § 680-213A | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Inspection |  |  | "All applicants for ground source heat pump permits shall pay all fees for application and inspection as established by resolution by Borough Council, from time to time." | § 680-213A(2) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Certification |  |  | "The pipe loop is to be installed by a geothermal well installation contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." The contractor must also provide before activation "Written documentation of the geothermal heating/cooling system testing and certification." | § 680-213C(10) and § 680-213C(12)(d) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Decommissioning |  |  | "In the event of the proposed discontinuance of the geothermal heating/cooling system, a system closure plan will be prepared and submitted to the Borough for its removal." "If a geothermal heating/cooling system is inoperable for six consecutive months, the owner shall be notified. Within three months of receiving the notice, the owner shall either restore the system to operating condition or remove it, at the owner's expense. The heat transfer fluid must be removed by a displacement with grout. The top of the borehole must be uncovered and capped with grout." | § 680-213C(13)(e) and (f) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Open-loop Prohibitions |  |  | "Closed-loop systems. All geothermal heating/cooling systems shall be closed-loop systems. No open-loop systems shall be permitted." | § 680-213C(1) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | Borough | 4209115192 | Other Prohibitions/Regulations |  |  | "All geothermal heating/cooling systems in areas underlain by carbonate bedrock must be vertical loop systems." | § 680-213C(7) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Roads | 10 | feet | The table requires a setback from "Dedicated public right-of-way and property lines" of "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Right of Way | 15 | feet | The table requires a setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "15 feet or outside easement." It also lists "Dedicated public right-of-way" at "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Property Lines | 10 | feet | The table requires a setback from "Dedicated public right-of-way and property lines" of "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Building Foundation | 10 | feet | The table requires a setback from "Building foundations (except buildings enclosing water wells and/or water well pumps)" of "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Wastewater | 100 | feet | The table lists wastewater-related setbacks including: "Community spray irrigation site sewage sludge and septage disposal site" at "50 feet" closed-loop and "100 feet" standing-column; "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits, single-family spray irrigation system, etc." at "50 feet" closed-loop and "100 feet" standing-column; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks" at "25 feet" closed-loop and "50 feet" standing-column. | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Animal Enclosures | 200 | feet | The table requires setbacks from "Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure" of "100 feet" for closed-loop systems and "200 feet" for standing-column well systems. | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Water Lines | 15 | feet | The table requires a setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "15 feet or outside easement." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Sewer Lines | 50 | feet | The table sets isolation distances from "Gravity sewer lines and drains carrying domestic sewage or industrial waste" at "25 feet" closed-loop and "50 feet" standing-column. It also lists "Gravity sewer lines and drains using cast-iron pipe with watertight lead-caulked or neoprene-gasketed joints, or Schedule 40 PVC pipe with solvent-welded joints" at "5 feet" and "10 feet," and "Sewer lines and drains carrying domestic sewage or industrial waste under pressure" at "25 feet" and "50 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Water Bodies | 25 | feet | The isolation-distance table requires separation from "Delineated wetlands, floodplains, lakes, ponds, streams, or other surface waters" of "12.5 feet" for "Closed-Loop Systems" and "25 feet" for "Standing-Column Well Systems." Footnote: "These amounts are the minimum isolation distances required by Montgomery County Health Department (MCHD) Code § 17-7." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The table requires setbacks from "Commercial preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles" of "150 feet" for closed-loop systems and "300 feet" for standing-column well systems. | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." "Prior to constructing a new geothermal well or modifying an existing geothermal well, the property owner shall file all appropriate applications with the municipality, county, or other regulating agency and pay all applicable fees." "The Borough shall approve or deny the application within 15 working days of receipt of a complete application and the appropriate fee." | § 95-165 Renewable energy systems, C.(1) Permitting |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Inspection |  |  | "The Borough shall field verify the location of the proposed geothermal well(s) and all applicable isolation distances." "Abandonment procedures may be subject to MCHD inspection." | § 95-165 Renewable energy systems, C.(1)(d) and C.(5)(d) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Licensed Driller |  |  | "All wells shall be constructed by a Pennsylvania Department of Conservation and Natural Resources (DCNR) licensed water well driller or an International Ground Source Heat Pump Association (IGSHPA) accredited geothermal system installer." | § 95-165 Renewable energy systems, C.(2)(b) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Certification |  |  | "All wells shall be constructed by a Pennsylvania Department of Conservation and Natural Resources (DCNR) licensed water well driller or an International Ground Source Heat Pump Association (IGSHPA) accredited geothermal system installer." "The geothermal system shall be designed and installed in conformance with IGSHPA Heat Pump Systems Design and Installation Standards..." | § 95-165 Renewable energy systems, C.(2)(b) and C.(4)(a) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Decommissioning |  |  | "All abandoned wells shall be filled and sealed according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment Form shall be submitted to MCHD within 30 days of abandonment." "Any and all heat transfer fluid shall be removed by displacement with grout. The top of the borehole shall be uncovered and capped with grout in a manner acceptable to the Borough and MCHD." "If the applicant/homeowner chooses not to abandon the well, a nonabandonment declaration shall be signed and submitted to MCHD within 30 days." | § 95-165 Renewable energy systems, C.(5) Decommissioning requirements |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal well systems or standing-column geothermal well systems are allowed." "Open-loop geothermal well systems, except for standing-column geothermal well systems, are prohibited. Separate supply and reinjection wells are prohibited." | § 95-165 Renewable energy systems, C.(2)(c)-(d) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | Borough | 4209121200 | Other Prohibitions/Regulations |  |  | "Separate supply and reinjection wells are prohibited." | § 95-165 Renewable energy systems, C.(2)(d) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | Lower Frederick | Township | 4209144912 | Permit |  |  | The fee schedule expressly includes geothermal permits: "Building, Plumbing, Electrical and Mechanical Permits" with a "Zoning permit (when building, plumbing, electrical and/or mechanical permits are needed) $50.00"; "MECHANICAL PERMIT FEES: a. Residential* $100.00; b. Non-Residential* $150.00"; and under zoning permits, "i. Wind turbine, solar panel, geo-thermal installations $300.00." | 1. APPLICATION/PLAN REVIEW FEES / 1. MECHANICAL PERMIT FEES / 8. ZONING PERMIT FEES | 2023 | https://lowerfrederick.org/wp-content/uploads/2023/04/2023-Fee-Schedule_adopted-2023.4.04.pdf
Pennsylvania | Montgomery | Lower Frederick | Township | 4209144912 | Inspection |  |  | The ordinance imposes inspection-related requirements/fees for geothermal installations through general permit administration: "Re-inspections (will be assessed on a per inspection basis) $75.00" appears under building, plumbing, electrical, mechanical, and zoning fees; mechanical fees also state "*Additional inspections based on plan review at a cost of $75.00 per inspection"; and the failure-to-comply section refers to "any required permit(s) or inspections" and allows the Township to require "approved proof of compliance, such as soil compaction testing, electrical certifications, compressed air testing of pipes, or other similar testing deemed necessary and deemed acceptable to the Township." | 1. APPLICATION/PLAN REVIEW FEES / 8. ZONING PERMIT FEES / 24. FAILURE TO COMPLY FEES | 2023 | https://lowerfrederick.org/wp-content/uploads/2023/04/2023-Fee-Schedule_adopted-2023.4.04.pdf
Pennsylvania | Montgomery | Lower Moreland | Township | 4209145008 | Permit |  |  | "The applicant shall demonstrate compliance with all applicable regulations of Chapter 17 of the Montgomery County Public Health Code relating to Individual Water Supply, Irrigation Well, and Geothermal Well System Regulations." | ARTICLE 5(b) Geothermal Wells | 2020 | https://www.lowermoreland.org/UserFiles/Servers/Server_15465051/File/Solar%20Panels%20Requirements.pdf
Pennsylvania | Montgomery | Lower Moreland | Township | 4209145008 | Open-loop Prohibitions |  |  | "Open loop geothermal well systems, except for standing column well systems, shall be prohibited." | ARTICLE 5(b)[3] | 2020 | https://www.lowermoreland.org/UserFiles/Servers/Server_15465051/File/Solar%20Panels%20Requirements.pdf
Pennsylvania | Montgomery | Lower Moreland | Township | 4209145008 | Other Prohibitions/Regulations |  |  | "Separate supply and reinjection wells shall be prohibited." | ARTICLE 5(b)[3] | 2020 | https://www.lowermoreland.org/UserFiles/Servers/Server_15465051/File/Solar%20Panels%20Requirements.pdf
Pennsylvania | Montgomery | Lower Salford | Township | 4209145096 | Permit |  |  | The fee schedule lists a specific geothermal permit category under zoning: "Well Permit ... (2) Geothermal Well $325.00 (Each)." It also states generally for this section: "All Fees referenced within this section shall be doubled if the project is started without the applicable Permits and/or Approvals." | A. BUILDING AND ZONING PERMITS, 6. ZONING, (e) Well Permit | 2025 | https://lowersalfordtownship.org/media/2466/01-january-6-2025-reorganization-packet.pdf
Pennsylvania | Montgomery | Narberth | Borough | 4209152664 | Permit |  |  | "No building shall be constructed or altered in the Borough nor the use of any building changed nor vacant land occupied until the Zoning Officer has determined plans to be in conformity with the provisions of this chapter." Also, "The Zoning Officer shall issue no permit unless it conforms to all applicable ordinances, statutes and regulations." | § 500-803 Permits | 2023 | https://ecode360.com/34355883
Pennsylvania | Montgomery | Narberth | Borough | 4209152664 | Inspection |  |  | "No permit shall be considered as complete or permanently effective until the Zoning Officer has noted on the permit that the work has been inspected and approved as being in conformity with the provisions of this chapter." | § 500-803 Permits | 2023 | https://ecode360.com/34355883
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM - An energy system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." | § 340-10 Terminology | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Right of Way | 10 | feet | Under "Minimum Setbacks": "Property lines and right-of-way lines: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Property Lines | 10 | feet | Under "Minimum Setbacks": "Property lines and right-of-way lines: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Building Foundation | 10 | feet | Under "Minimum Setbacks": "Building foundations: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Wastewater | 25 | feet | Under "Minimum Setbacks": "Subsurface sewage disposal or storage systems: 25'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Water Lines | 15 | feet | Under "Minimum Setbacks": "Domestic water lines or sanitary force mains: 15'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Sewer Lines | 10 | feet | Under "Minimum Setbacks": "Gravity sanitary sewer lines: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Water Bodies | 10 | feet | Under "Minimum Setbacks": "Delineated wetlands, floodplains, surface waters: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Under "Minimum Setbacks": "Hazardous materials storage: 300'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Permit |  |  | Under "Permitting": "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." "Prior to constructing a new geothermal well or modifying an existing geothermal well, the property owner shall file all appropriate applications with the Borough, county, or other regulating agency and pay all applicable fees." "If geothermal well construction is not completed within three (3) years of the permit issuance date, the approval to construct shall expire." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Licensed Driller |  |  | "Only an PA DCNR-licensed well driller or a geothermal system installer accredited by the International Ground Source Heat Pump Association (IGSHPA) shall conduct the drilling of a geothermal well. The well drilling rig must also be approved by PA DCNR." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Certification |  |  | "Only an PA DCNR-licensed well driller or a geothermal system installer accredited by the International Ground Source Heat Pump Association (IGSHPA) shall conduct the drilling of a geothermal well." Also, "The pipe loop is to be installed by a geothermal well installation contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Decommissioning |  |  | "The geothermal system must be installed, maintained, and decommissioned in accordance with IGSHPA Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards, latest version." Also under "Abandonment": "A geothermal system shall be abandoned in a manner acceptable to the Borough and shall comply with the laws, rules, and regulations applicable to the abandonment of water wells." "Any and all heat transfer fluid must be removed by displacement with grout in a manner acceptable to the Borough." "The top of the borehole must be uncovered and capped with grout in a manner acceptable to the Borough." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | Borough | 4209177304 | Closed-loop Prohibitions |  |  | "Closed loop systems are prohibited." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Upper Dublin | Township | 4209179008 | Definition: Well |  |  | "GEOTHERMAL BOREHOLE or BOREHOLE — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 255-260. Definitions. | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | Township | 4209179008 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An alternative energy system serving as a mechanism for heat exchange that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings ... Geothermal heat pumps come in two basic configurations: closed loop and open loop systems." | § 255-260. Definitions. | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | Township | 4209179008 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than 20 feet deep." | § 255-262(B)(5) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | Township | 4209179008 | Permit |  |  | "Open loop geothermal energy systems are prohibited with the exception of standing column well geothermal systems in which water is circulated from and back to the same borehole, in which case such open loop geothermal energy system may be permitted with conditional use approval in all zoning districts subject to demonstration by the applicant for conditional use approval that the proposed site for the standing column well geothermal system has the requisite geological and groundwater properties for the proper functioning of the system." | § 255-262(B)(2) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | Township | 4209179008 | Decommissioning |  |  | "If a geothermal energy system remains unserviceable for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove or seal the system within six months of abandonment after a demolition permit has been obtained..." "Any aboveground mechanical equipment, wiring, piping, coils, and other components shall be removed." "Underground pipes or coils should be removed and the resulting void space filled, or if abandoned in place, underground pipes and coils shall be filled with grout to displace the heat transfer fluid. The top of any pipe, coil or boring shall be uncovered and grouted." "Heat transfer fluid shall be captured and disposed of in accordance with applicable regulations." "When a geothermal energy system is removed, any disturbed earth as a result of the removal of the system shall be restored, graded and reseeded." | § 255-262(D)(1)-(2) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | Township | 4209179008 | Open-loop Prohibitions |  |  | "Open loop geothermal energy systems are prohibited with the exception of standing column well geothermal systems in which water is circulated from and back to the same borehole, in which case such open loop geothermal energy system may be permitted with conditional use approval..." | § 255-262(B)(2) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Definition: Well |  |  | "Vertical Closed-Loop Borehole. A borehole which is constructed to receive heat-exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20' below grade as the subsurface conditions warrant." | SECTION ONE. Article II, § 201 - Terms Defined | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating and/ or Cooling System. A system that uses a heat pump to extract heat from the earth in heating mode and/ or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, and earth-source heat pump system and a Geo Exchange system." Also: "Ground-Coupled Heat Pump. A geothermal heat pump that uses the earth itself as a heat source and heat sink. It is coupled to the ground by means of a closedloop heat exchanger installed horizontally or vertically underground." | SECTION ONE. Article II, § 201 - Terms Defined | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Roads | 10 | feet | Setback table: "Dedicated public right-of-way" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Right of Way | 10 | feet | Setback table: "Property lines and all rights-of-way and easements" — "10" feet. Also: "Existing water and forced sewer buried utilities and/or utility trenches" — "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench." | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Property Lines | 10 | feet | Setback table: "Property lines and all rights-of-way and easements" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Building Foundation | 10 | feet | Setback table: "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Wastewater | 25 | feet | Setback table includes: "Septic tanks, aerobic tanks or holding tanks" — "25" feet; "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields" — "25" feet; "Sewage seepage pits, cesspools" — "25" feet; "Spray irrigation sites, sewage sludge and septage disposal sites" — "25" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Animal Enclosures | 25 | feet | Setback table: "Farm silos, barnyards, privies and fuel tanks" — "25" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Fuel (above ground) | 300 | feet | Setback table includes: "Farm silos, barnyards, privies and fuel tanks" — "25" feet; and "Surface or subsurface containers or tanks of greater than 1000 gallons used for storage of materials that cannot be properly disposed of by passage through soil. This includes, but is not limited to gasoline and all other petroleum products (if borehole is cased and grouted inside and out)" — "300" feet; plus "Surface or subsurface containers of tanks of 1000 gallons or less ... including ... gasoline and all other petroleum products ..." — "30" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Subsurface Drains | 10 | feet | Setback table: "Rainwater pits, ditches" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Water Lines | 15 | feet | Setback table: "Existing water and forced sewer buried utilities and/or utility trenches" — "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench." | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Sewer Lines | 15 | feet | Setback table: "Gravity sewer lines and drains carrying domestic sewage or industrial waste" — "10 or according to easement." Also: "Existing water and forced sewer buried utilities and/or utility trenches" — "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench." | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Water Bodies | 25 | feet | Setback table: "Lakes, ponds, streams or other surface waters" — "25" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Setback table: "Preparation area or storage area of hazardous spray materials, fertilizers of chemicals, salt piles" — "100" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Permit |  |  | "Closed-Loop geothermal systems shall be permitted as an accessory use in any zoning district, upon receipt of a permit from the zoning officer and compliance with the requirements of this ordinance." Also: "An applicant who seeks to install a closed-loop geothermal system shall submit an application for a zoning permit." | SECTION FOUR. Article IV, § 467 - Geothermal Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Decommissioning |  |  | "The geothermal heating and/or cooling system must be installed, maintained and decommissioned utilizing standards conforming to the International Ground Source Heat Pump Association (IGSHPA) Closed-Loop/Geothermal Heat Pump System Design and Installation Standards, 2010 edition..." Also: "In the event of the proposed discontinuance of the use of the ground source heat pump system or geothermal system, a system closure plan will be prepared and submitted to the Township for its approval. At a minimum, any and all heat transfer fluid must be removed by displacement with grout in a manner acceptable to the Township engineer. The top of the borehole must be uncovered and capped with grout in a manner acceptable to the Township." | SECTION FOUR. Article IV, § 467.D-F - Geothermal Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Open-loop Prohibitions |  |  | "Due to the serious potential for adverse environmental impact, any open-loop geothermal systems ... are prohibited in West Pottsgrove Township." | SECTION FOUR. Article IV, § 467.B - Prohibited Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | Township | 4209183912 | Other Prohibitions/Regulations |  |  | "Due to the serious potential for adverse environmental impact, any ... direct exchange (DX) geothermal systems are prohibited in West Pottsgrove Township." | SECTION FOUR. Article IV, § 467.B - Prohibited Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Northampton | East Allen | Township | 4209520736 | Permit |  |  | "Monitoring, agricultural, and geothermal wells not used to supply water for human consumption do not require permits under this section." | § 250-39.3 Regulations governing the construction and closure of individual water supply wells | 2016 | https://ecode360.com/12791288
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (sometimes referred to as 'GSHP') Any system of mechanical and electrical facilities designed for the purpose of withdrawing heat from, or discharge heat to, the ground, groundwater, or surface waters." | § 90-3 Definitions | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Setback - Right of Way | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines, rights-of-way." | § 90-5B(3) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Setback - Property Lines | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines, rights-of-way." | § 90-5B(3) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Setback - Building Foundation | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (4) Twenty-five feet from existing or proposed structures." | § 90-5B(4) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Setback - Wastewater | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (2) Twenty-five feet from any existing or proposed individual or community on-lot sewage disposal system, including any primary or alternate drainfield sites." | § 90-5B(2) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Setback - Private Water | 100 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (1) One hundred feet from any existing or proposed drinking water wells." | § 90-5B(1) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Minimum Well Depth | 2.5 | feet | "The depth of the tubing or heat transfer element must be at least 30 inches below the surface of the ground." | § 90-7D | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Permit |  |  | "No person shall install, construct, modify, drill, or excavate to facilitate any construction/installation and/or modification of a GSHP for use as a heating and/or cooling system for any building or structure without first obtaining from the Township a permit allowing for the construction or modification of a GSHP." Also, "A permit under the provision of this chapter shall be required prior to any person: (a) Construction or modifying a GSHP; (b) Drilling or redrilling any vertical GSHP; and (c) Decommissioning or abandoning an existing GSHP." | § 90-4 Construction permits | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Inspection |  |  | "Piping shall be flushed and pressure-tested before vertical borings are sealed or before horizontal trenches are backfilled. The Township Code Enforcement Officer or his or her designee shall observe pressure testing;" "The Township Code Enforcement Officer, or his or her designee, shall observe grouting of the vertical boreholes for the GSHP wells;" and "GSHP system installer shall contact the Township Code Enforcement Officer, or his or her designee, a minimum of 24 hours in advance to inspect grouting pond piping and to verify pressure testing." | § 90-8 Inspections | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Licensed Driller |  |  | "GSHP well drilling shall only be undertaken by a Pennsylvania licensed well driller." | § 90-6A(1) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Certification |  |  | "All joints shall be sealed by heat fusion or IGSHPA certified process;" and prior to activation, the driller and/or installer shall provide "Written documentation of the GSHP system testing and certification." | § 90-5C(2); § 90-6B(4) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Decommissioning |  |  | The ordinance requires permit application "[w]here a person proposes to construct, modify, or decommission a GSHP," and states that a permit is required prior to "(c) Decommissioning or abandoning an existing GSHP." It also requires "A system closure plan for use in the event of the discontinuance of the use of the GSHP system." | § 90-4B(1), (2); § 90-5D(2) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | Township | 4209532432 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed-loop systems. (1) Open-loop GSHP systems shall not be permitted." | § 90-5 GSHP system standards | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Lower Mount Bethel | Township | 4209545016 | Setback - Wastewater | 20 | feet | "No portion of a geothermal energy system shall be constructed within 20 feet of a water supply well, a sewage disposal facility or a carbonate geologic feature..." | § 27-1202(D) Isolation Distances | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | Township | 4209545016 | Setback - Public Water | 20 | feet | "No portion of a geothermal energy system shall be constructed within 20 feet of a water supply well, a sewage disposal facility or a carbonate geologic feature..." | § 27-1202(D) Isolation Distances | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | Township | 4209545016 | Permit |  |  | "A zoning permit and building permit pursuant to the PA Uniform Construction Code, shall be required prior to installation of any geothermal energy system. Applicable manufacturer specifications and any PA Department of Environmental Protection (PA DEP) or Northampton County Health Department correspondence shall be submitted to Lower Mount Bethel Township as part of the application for any permit." | § 27-1202(B) Permitting | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | Township | 4209545016 | Certification |  |  | "The design, installation and operation of geothermal energy systems shall be permitted in conformance with all applicable regulation under PA DEP and the PA Uniform Construction Code... and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations... Such conformance shall be certified by the installer of the system on a form adopted by resolution of the Board of Supervisors from time to time." | § 27-1202(C) Design | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | Township | 4209545016 | Decommissioning |  |  | "If the geothermal energy system enters into a state of disrepair, it shall be the responsibility of the property owner to properly maintain the geothermal energy system or to decommission the system within six months from the date the system enters such a state or immediately in any case determined to be a safety hazard." "Where the use of any geothermal energy system is abandoned, it shall be the responsibility of the property owner to evacuate (pump out) the fluid(s) in the system, to fill the borehole(s) with bentonite or an equivalent alternative acceptable to the Township, and to conform to any applicable PA DEP well abandonment guidelines within 90 days from the date the system is abandoned or immediately in any case determined to be a safety hazard." "Any earth disturbance as a result of decommissioning or removal of any geothermal energy system shall be graded and reseeded." | § 27-1202(G)-(H) Disrepair; Abandonment and Decommissioning | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | Township | 4209545016 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems shall not be permitted." | § 27-1202(A) Permitted Use | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (also shown as GSHP) Any system of mechanical and electrical facilities designed for the purpose of withdrawing heat from, or discharging heat to the ground, groundwater or surface waters." | § 94-3 Definitions | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Setback - Right of Way | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) 25 feet from property lines, rights-of-way." | § 94-5(B)(3) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Setback - Property Lines | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) 25 feet from property lines, rights-of-way." | § 94-5(B)(3) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Setback - Building Foundation | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (4) 25 feet from existing or proposed structures." | § 94-5(B)(4) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Setback - Wastewater | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (2) 25 feet from any existing or proposed individual or community on-lot sewage disposal system including any primary or alternate drainfield sites." | § 94-5(B)(2) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Setback - Private Water | 100 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (1) 100 feet from any existing or proposed drinking water wells." | § 94-5(B)(1) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Minimum Well Depth | 2.5 | feet | For horizontal closed-loop systems, "The depth of the tubing or heat transfer element must be at least 30 inches below the surface of the ground." | § 94-7(D) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Permit |  |  | "No person shall install, construct, modify, drill, or excavate to facilitate the construction/installation and modification of a GSHP for use as a heating and/or cooling system for any building or structure without first obtaining from the Township a permit allowing for the construction of a GSHP." Also, "A permit under the provision of this chapter shall be required prior to any person: (a) Constructing or modifying a GSHP. (b) Drilling or redrilling any vertical GSHP. (c) Decommissioning or abandoning an existing GSHP." | § 94-4 Construction permits | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Inspection |  |  | "Piping shall be flushed and pressure tested before vertical borings are sealed or before horizontal trenches are backfilled. The Township Code Enforcement Officer or his or her designee shall observe pressure testing." Also, "The Township Code Engineer, or his or her designee, shall observe grouting of the vertical boreholes for the GSHP wells." And, "GSHP system installer shall contact the Township Engineer, or his or her designee, a minimum of 24 hours in advance to inspect grouting pond piping and to verify pressure testing." | § 94-8 Inspections | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Licensed Driller |  |  | "GSHP well drilling shall only be undertaken by a Pennsylvania licensed well driller." | § 94-6(A)(1) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Certification |  |  | "GSHP systems shall be designed and constructed in accordance with the International Ground Source Heat Pump Association (hereafter IGSHPA) Installation Standards..."; "All joints shall be sealed by heat fusion or IGSHPA certified process"; and prior to activation, the driller and/or installer must provide "Written documentation of the GSHP system testing and certification." | § 94-5(A)(2); § 94-5(C)(1); § 94-6(B)(4) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Decommissioning |  |  | The permit application applies where a person proposes to "construct, modify, or decommission a GSHP," and "A permit under the provision of this chapter shall be required prior to any person: ... (c) Decommissioning or abandoning an existing GSHP." The ordinance also requires "A system closure plan for use in the event of the discontinuance of the use of the GSHP system." | § 94-4(B)(1); § 94-4(B)(2)(c); § 94-5(D)(2) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed-loop systems. Open-loop GSHP systems shall not be permitted." | § 94-5 Standards for GSHP systems | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | Township | 4209545104 | Other Prohibitions/Regulations |  |  | "GSHP systems to be designed and constructed in the Township's Watershed Protection or Carbonate Geology Districts shall be horizontal closed-loop systems. Outside the Watershed Protection or Carbonate Geology Districts, either vertical or horizontal closed-loop GSHP systems may be used." | § 94-5 Standards for GSHP systems | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Williams | Township | 4209585256 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM (CLOSED LOOP) Any heating and/or cooling system that utilizes the earth's thermal energy to heat and/or cool a building through the use of a series of underground pipes in which the same liquid is circulated through piping in a continuous configuration such that no new liquid is introduced to the system or used liquid discharged from the system." "GEOTHERMAL SYSTEMS (OPEN LOOP) Any heating and/or cooling system that utilizes the earth's thermal energy to heat and/or cool a building through the use of a series of underground pipes in which the same liquid is circulated through piping in a continuous configuration after being drawn from a source and is then discharged to that source or an alternate location." | § 27-201 Definitions; Terms Defined | 2025 | https://ecode360.com/31570532
Pennsylvania | Perry | Marysville | Borough | 4209947968 | Definition: Well |  |  | "GEOTHERMAL WELL - a well installed for the purpose of heating or cooling a facility. These shall include wells drilled as closed-loop geothermal boreholes." | § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | Borough | 4209947968 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP EQUIPMENT - any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | Borough | 4209947968 | Permit |  |  | "The installation, repair, or alteration of any well... requires a permit prior to the beginning of the installation... Geothermal wells are required to be permitted." § 23-101 also states the Chapter is intended "to require a permit for the construction of a well... and the drilling of boreholes used for the installation of ground source heat pump equipment." | § 23-301. General. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | Borough | 4209947968 | Licensed Driller |  |  | § 23-301(2): "All private or public water supplies and geothermal wells, monitoring wells and test wells constructed pursuant to this Chapter shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor who is licensed as set forth in this Chapter." § 23-201 defines "GEOTHERMAL WELL INSTALLATION CONTRACTOR" as an individual "responsible for the drilling of boreholes used for the purpose of geothermal heating or cooling of a facility" and states that this individual "is licensed as a well contractor and/or a geothermal well installation contractor." | § 23-301. General.; § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | Borough | 4209947968 | Decommissioning |  |  | "BACKFILLING - the process of sealing a borehole for the purpose of decommissioning a well or enclosing the closed-loop of a ground source heat pump equipment system." Also, "DECOMMISSIONING - the process of properly filling and sealing a well, in accordance with this Chapter." | § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Washington | Charleroi | Borough | 4212512704 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 338-202 Definitions |  | https://ecode360.com/32070838
Pennsylvania | Washington | Charleroi | Borough | 4212512704 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 338-202 Definitions |  | https://ecode360.com/32070838
Pennsylvania | Washington | Charleroi | Borough | 4212512704 | Minimum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM ... A horizontal closed loop system shall be no more than 20 feet deep." | § 338-202 Definitions |  | https://ecode360.com/32070838
Pennsylvania | Westmoreland | Washington | Township | 4212981336 | Inspection |  |  | Section 403(D): "The filing of an application for either preliminary or final approval shall constitute authorization for the Washington Township Board of Supervisors, Planning Commission, Municipal Authority of Washington Township, Sewage Enforcement Officer, Solicitor and Engineer or their agents or representatives as they may designate to make such on-site inspections, before, during and after construction, as may be required to effectively administer this Ordinance." Section 407(C)-(D): "Inspections of Improvements shall be made by the Township Engineer or his assigned agent." The contractor "shall contact the Township engineer before backfilling any storm sewer, retaining wall foundation, culvert, inlet or manhole; before spreading sub-base or applying base course to any street, or before covering any other structures that are part of the Improvements included under the bond. The engineer shall inspect the work... The engineer shall reinspect the work..." Section 407(F): after completion, the Township engineer must "make a final inspection of all Improvements covered by the bond." | Section 403 — Application Procedures for Development Other Than Minor Subdivisions; Section 407 — Construction of Improvements | 2017 | https://www.washingtontownship.com/_files/ugd/241b02_2a8ec24dd39b46e089251cce31eeabcc.pdf
Pennsylvania | Wyoming | Falls | Township | 4213125128 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump -Any geothermal, earth-coupled, geo-exchange, water-coupled, groundwater, ground-coupled, closed-loop, coiled, open, or water source heat pump system used for heating and/or cooling which utilizes groundwater extracted from a well." | §707.12 Definitions | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | Wyoming | Falls | Township | 4213125128 | Setback - Wastewater | 100 | feet | "Horizontal closed loop ground source heat pumps must be a minimum of twenty-five (25) feet from any existing or permitted on-lot sewage disposal system. Vertical closed loop ground source heat pumps must be a minimum of one hundred (100) feet from any existing or permitted on-lot sewage disposal system, unless the entire borehole around the annulus of the loop is grouted with bentonite slurry." | §707.8(I)(2)-(3) Ground Source Heat Pumps | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | Wyoming | Falls | Township | 4213125128 | Permit |  |  | "Applicants for open loop ground source heat pumps that discharge to the surface must either obtain a National Pollutant Discharge Elimination System (NPDES) permit from the Pennsylvania Department of Environmental Protection, or demonstrate that such permit is not required." | §707.8(I)(6) Ground Source Heat Pumps | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | Wyoming | Falls | Township | 4213125128 | Other Prohibitions/Regulations |  |  | "Closed loop ground source heat pumps that treat extracted water in any way, or involve circulation of toxic refrigerants below the surface, are prohibited. Water treatment associated with open loop ground source heat pumps is prohibited." | §707.8(I)(4)-(5) Ground Source Heat Pumps | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | York | Carroll | Township | 4213311432 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEMS. A geothermal heat pump (GHP) or ground source heat pump (GSHP) is a central heating and/or cooling system that transfers heat to or from the ground." | § 450-112 Definitions | 2023 | https://ecode360.com/37602037
Pennsylvania | York | Fawn | Township | 4213325408 | Definition: Geothermal |  |  | "GEOTHERMAL HEAT -Heat derived from geothermal resources, or heat derived from groundwater." "GEOTHERMAL FLUID -Any fluid transporting or capable of transporting geothermal heat." | Section 2. Definitions | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP SYSTEMS -A geothermal heat pump system which relies on the contained circulation of geothermal fluids through an underground loop of pipes. The loops act as a subsurface heat exchanger, which transports the heat to or from the ground." "GEOTHERMAL HEATING SYSTEM -A geothermal heat pump system which relies on the contained circulation of geothermal fluids to obtain and to utilize geothermal resources." "OPEN LOOP SYSTEMS -A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring or surface water." | Section 2. Definitions | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Driveways | 10 | feet | Section 13 table: "Driveways — 10 ft." Section 18 table: "Driveways — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Right of Way | 10 | feet | Section 13 table: "Property lines and right-of-way easements — 10 ft." Section 18 table: "Property lines and right-of-way easements — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Property Lines | 10 | feet | Section 13 table: "Property lines and right-of-way easements — 10 ft." Section 18 table: "Property lines and right-of-way easements — 10 ft." Section 23 exemption applies only to agricultural adaptations and states the installation is "a minimum of 200 feet from property boundaries." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements; Section 23. Exemption | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Building Foundation | 20 | feet | Section 13 table for wells: "Building foundations — 20 ft." Section 18 table for horizontal systems: "Building foundations — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Wastewater | 50 | feet | Section 13 table: "Septic tanks - active — 50 ft." and "Septic drain fields, seepage pits, privies, or cesspools - 50 ft." Section 18 table: "Septic tanks - active — 10 ft." and "Septic drain fields, seepage pits, privies, or cesspools - 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Sewer Lines | 25 | feet | Section 13 table: "On-lot sewage system line — 25 ft." Section 18 table: "On-lot sewage system line — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Pools | 25 | feet | Section 13 table: "Swimming pools — 25 ft." Section 18 table: "Swimming pools — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Setback - Water Bodies | 25 | feet | Section 13 table: "Lakes, ponds, or surface water — 25 ft." and "Storm water retention/detention ponds berm (measured from top to bottom) — 25 ft." Section 18 table: "Lakes, ponds, or surface water — 20 ft." and "Storm water retention/detention ponds berm (measured from top to bottom) — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Maximum Well Depth | 800 | feet | "The depth of any well shall not exceed 800 ft." | Section 12. Well Construction Requirements, a. Construction by Licensed Driller | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Permit |  |  | Section 7: "Any persons desiring to construct, install, or alter a Geothermal Heating System within the Township shall first apply for a Geothermal Heating System permit at the Township Office... No Person shall commence construction or alteration of a Geothermal Heating System prior to the Owner of a proposed Geothermal Heating System receiving a permit." Section 11: "No geothermal well shall be installed without receiving a well permit... Before any drilling or site preparation begins, the well driller shall apply for a Well Permit from the Township Well Officer." Section 17: "Prior to any on lot excavation or installation of the horizontal closed loop system a permit for same shall be secured from the permit officer." | Section 7, Application for Geothermal Heating System Permit; Section 11. Geothermal Wells for Closed Loop, Vertical Systems — Requirements/ Procedures; Section 17. Closed Loop, Horizontal Installation — Requirements/Procedures | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Inspection |  |  | Section 15: "The following inspections shall be required by the Township: a. Site inspection before any work is done, showing the location of proposed work. b. Inspection of grouting. c. Inspection of the completely installed system before operations commence and upon commencement of operations. d. Inspection if geothermal system or well is abandoned." Section 11(b): "During the well drilling and construction process, the Township Well Officer may enter the premises to determine if the well is being installed according to the requirements of the Township." Section 20: Township officials may enter property "for purposes of inspecting geothermal facilities, or monitoring the operational characteristics of such facilities." | Section 15. Inspection; Section 11. Geothermal Wells for Closed Loop, Vertical Systems — Requirements/ Procedures; Section 20. Township Monitoring of Geothermal Facilities | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Licensed Driller |  |  | Section 12(a)(1): "All geothermal wells in the Township shall be constructed in accordance with PA Act 610 (Water Well Drillers License Act)." Section 16: "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller..." | Section 12. Well Construction Requirements, a. Construction by Licensed Driller; Section 16. Well Abandonment | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Certification |  |  | Section 12(a)(1): "All geothermal wells in the Township shall be constructed in accordance with PA Act 610 (Water Well Drillers License Act)." Section 16: "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines." | Section 12. Well Construction Requirements, a. Construction by Licensed Driller; Section 16. Well Abandonment | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Decommissioning |  |  | "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment form shall be submitted to the Township within thirty (30) days of abandonment. Abandonment procedures shall be subject to Township inspection and shall follow PADEP guidelines." | Section 16. Well Abandonment | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | Township | 4213325408 | Other Prohibitions/Regulations |  |  | "No Geothermal Heating System constructed or altered after the effective date of this Ordinance shall be operated or altered in such a manner as to cause Geothermal Fluids or Thermal Groundwater to be discharged onto the surface of the ground or into any public ditch or drainage facility." | Section 19. Surface Discharges | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Right of Way | 20 | feet | The isolation distance table requires 20 feet from "Dedicated public right-of-way." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, underground geothermal systems shall be located a minimum distance of 10 feet from any property line." | § 490-25M(3)(b) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Wastewater | 100 | feet | The isolation distance table requires 50 feet from "Septic tanks, aerobic tanks or holding tanks"; 100 feet from "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields"; 100 feet from "Sewage seepage pits, cesspools"; and 25 feet from "Spray irrigation sites, sewage sludge and septage disposal sites." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Animal Enclosures | 50 | feet | The isolation distance table requires 50 feet from "Farm silos, barnyards, privies and fuel tanks." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Fuel (above ground) | 50 | feet | The isolation distance table requires 50 feet from "Farm silos, barnyards, privies and fuel tanks." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Water Lines | 50 | feet | The isolation distance table requires geothermal wells/boreholes to be "Outside existing easement or, if no easement exists, no less than 50 feet from the utility or trench center line" for "Existing water and forced sewer buried utilities and/or utility trenches." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Sewer Lines | 50 | feet | The isolation distance table requires "50 or according to easement" from "Gravity sewer lines and drains carrying domestic sewage or industrial waste." It also requires geothermal wells/boreholes to be "Outside existing easement or, if no easement exists, no less than 50 feet from the utility or trench center line" for "Existing water and forced sewer buried utilities and/or utility trenches." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Water Bodies | 50 | feet | The isolation distance table requires 50 feet from "Lakes, ponds, streams or other surface waters." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Setback - Hazardous Materials/Fertilizers | 100 | feet | The isolation distance table requires 100 feet from "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Minimum Well Depth | 50 | feet | "Geothermal heating and/or cooling system vertical heat exchange boreholes containing loop pipes may be filled with approved grout or bridging or fill materials from their total depth up to a minimum depth of 50 feet below grade. These vertical heat exchange boreholes must be filled with only approved grout from a minimum depth of 50 feet below grade up to the ground surface." | § 490-25M(5)(a) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Permit |  |  | "The construction documents submitted with the application for a permit shall be accompanied by a site plan..." | § 490-25M(4) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Inspection |  |  | "All materials and construction practices shall conform to the requirements stated in Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards, such as, but not limited to, standards for pressure testing, heat transfer fluids, etc." | § 490-25M(5)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Certification |  |  | "The installer must have at least one representative who is certified by IGSHPA." | § 490-25M(1) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his/her expense after a demolition permit has been obtained..." Subsection (a) requires removal of "The heat pump and any external mechanical equipment"; Subsection (b) requires below-grade pipes or coils to "be filled with grout to displace the heat transfer fluid" and the fluid to "be captured and disposed of in accordance with applicable regulations"; Subsection (c) requires reporting abandoned wells to DCNR and providing a copy to the municipality. | § 490-25M(6) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | Township | 4213333728 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems and any system not meeting the definition of a closed-horizontal-loop geothermal energy system or closed-vertical-loop geothermal energy system are prohibited in the Township." | § 490-25M | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 211-6C Definitions | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 211-6D Definitions | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM — A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system..." "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM — A borehole that extends beneath the surface. Pipes are installed... The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM — Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | § 211-6A-B, E Definitions | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Setback - Public Water | 200 | feet | "The return well shall be located a minimum distance of 200 feet from wells on adjacent properties." | § 211-3E(2)(e)[2] Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than 20 feet deep." Also repeated in § 211-6A: "A horizontal closed loop system shall be no more than 20 feet deep." | § 211-3D(2) Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." | § 211-3 Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Inspection |  |  | "Installation requirements for extraction wells shall be the same as those for potable water wells, with respect to those regulations designed to prevent aquifer contamination (grouting, etc.), or in conformance with IGSHPA standards, as determined by the Borough Engineer." | § 211-3E(1)(b) Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Certification |  |  | "Discharge of water from open loop systems into a watercourse shall require certification by a licensed professional engineer registered by the Commonwealth of Pennsylvania that the design of the watercourse is such that the watercourse can be expected to retain its capacity to meet the needs of the geothermal system over the lifetime of the system and of any other water discharges for which it is used." | § 211-3E(2)(c) Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | Borough | 4213352056 | Other Prohibitions/Regulations |  |  | "Only the following types of geothermal energy systems shall be permitted: (1) Closed horizontal loop; (2) Closed vertical loop; and (3) Open horizontal loop systems relying upon injection wells or watercourses." | § 211-3B Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Springettsbury | Township | 4213372992 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 325-209 Definitions | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy-generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 325-209 Definitions | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Setback - Private Water | 100 | feet | "No geothermal energy system shall be located within 100 feet of any existing drinking water wells or any planned drinking water wells." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Maximum Well Depth | 20 | feet | In the definition of "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM," the ordinance states: "A horizontal closed loop system shall be no more than 20 feet deep." | § 325-209 Definitions | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Permit |  |  | "No person shall install, construct, drill or excavate to facilitate the construction or installation of a geothermal energy system for use as a heating and/or cooling system for a structure without first obtaining a geothermal energy system permit from the Township. No person shall drill or excavate to repair or modify or to facilitate the repair or modification of a geothermal energy system in the Township without first obtaining a zoning permit." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Licensed Driller |  |  | "The vertical geothermal energy well (or wells) installation shall be made only by a Pennsylvania-licensed well driller." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Certification |  |  | Before activation, the driller and/or installer must provide the Township "[w]ritten documentation of the geothermal energy system testing and certification." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Decommissioning |  |  | The required written operation plan must provide that "[i]n the event of the proposed discontinuance of the use of the geothermal energy system, a system closure plan will be prepared and submitted to the Township for its approval." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Open-loop Prohibitions |  |  | "All geothermal energy systems shall be closed systems. No open loop ground-source heat pump systems shall be permitted." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | Township | 4213372992 | Other Prohibitions/Regulations |  |  | "All geothermal energy systems in areas underlain by carbonate bedrock must be vertical loop systems. Outside the carbonate bedrock areas, either vertical or horizontal closed loop geothermal energy system may be used..." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
South Carolina | Lancaster |  | County | 45057 | Permit |  |  | "Geothermal heat exchange systems are permitted as an accessory use in all zoning districts." | 5.11.2 GEOTHERMAL ENERGY SYSTEMS [ALL DISTRICTS] | 2021 | https://www.lancastercountysc.gov/DocumentCenter/View/380/Chapter-5---Use-Regulations-PDF
South Carolina | Chesterfield | Cheraw | Town | 4513600 | Setback - Yards | 3 | feet | "Heat pumps or air conditioning units outside principal or accessory structures shall be placed no closer than three feet (3) from any side or rear property line." | 8-5.6 Heat pumps or air conditioning units outside principal or accessory structures | 2025 | https://cms8.revize.com/revize/cherawsc/Document_Center/Government/Zoning/2020%20ZO%20Updated%20to%202025.pdf
South Carolina | Florence | Florence | City | 4525810 | Definition: Geothermal |  |  | "Renewable energy systems include photovoltaic arrays (solar electric panels), solar water heaters, and geothermal heating and cooling systems." | Sec. 3-8.1.6 Renewable Energy Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | City | 4525810 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating and Cooling System means a system of pipes used to heat and cool buildings by exchanging heat with the ground. There are four types of systems: A. Vertical loop systems use pipes that are oriented vertically by insertion into a bore hole that extends deep into the ground. B. Horizontal loop systems use pipes that are oriented horizontally, installed in trenches that are typically five or more feet deep. C. Lake loop systems use pipes that extend into waterbodies, where they exchange heat with the water instead of the ground. D. Open loop systems extract groundwater and then discharge it into a drainage ditch or waterbody." | Division 7-25.2 Definitions / Geothermal Heating and Cooling System | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | City | 4525810 | Setback - Property Lines | 2 | feet | "Closed loop systems (horizontal loop systems and vertical loop systems) are permitted, provided that the loops are set back at least two feet from property lines and outside of utility easements." | Sec. 3-8.1.6(E) Geothermal Heating and Cooling Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | City | 4525810 | Permit |  |  | "Systems approved pursuant to this Section shall not generate power as a commercial enterprise." Also, "Community Geothermal Facility. A facility that serves more than an individual home or business shall be permitted in any district if a subdivision or portion of a subdivision: Has land in common ownership where certain components of the system are located; and Has a homeowners' association to maintain any off-site components." | Sec. 3-8.1.6 Renewable Energy Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | City | 4525810 | Open-loop Prohibitions |  |  | "Open loop systems are not permitted." | Sec. 3-8.1.6(E) Geothermal Heating and Cooling Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | City | 4525810 | Other Prohibitions/Regulations |  |  | "Lake loop systems are permitted if the water body is entirely within the property lines of the parcel proposed for development." | Sec. 3-8.1.6(E) Geothermal Heating and Cooling Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Charleston | Mount Pleasant | Town | 4548535 | Other Prohibitions/Regulations |  |  | § 51.115(E): "Discharge from ground water source heat pump prohibited. No discharge shall be allowed from a ground water source heat pump." | § 51.115 RESTRICTED DISCHARGES | 2016 | https://codelibrary.amlegal.com/codes/mtpleasantsc/latest/mpleasant_sc/0-0-0-114011
South Carolina |  | Sullivan's Island | Town | 4570090 | Permit |  |  | "It shall be unlawful to erect, construct, improve, alter or repair any building, sign or other structure or any part thereof or alter any parcel of land in preparation of such erection, construction, improvement or repair without first having obtained from the Building Inspector a written permit for such erection, construction, improvement, alteration or repair, pursuant to the provisions of this subchapter." | § 150.35 REQUIRED. | 2020 | https://codelibrary.amlegal.com/codes/sullivansislandsc/latest/sullivansisland_sc/0-0-0-3258
South Dakota | Lincoln | Harrisburg | City | 4608327260 | Permit |  |  | "Any person who commences work on a mechanical system before obtaining the necessary permits shall be subject to a Late Application Fee..." Also, in CHAPTER 9.05 - EXISTING BUILDING CODE, 105.1 Required: "Any owner or authorized agent who intends to... install, add, alter, remove, convert, or replace any... mechanical... system, the installation of which is regulated by this code... shall first make application to the Building Official and obtain the required permit." | CHAPTER 9.06 - MECHANICAL AND FUEL GAS CODE, 106.5.1 Work commencing before permit issuance | 2020 | https://www.harrisburgsd.gov/DocumentCenter/View/212/Harrisburg-SD-Codified-Municipal-Ordinances-Updated-June-30-2020-PDF
South Dakota | Lincoln | Harrisburg | City | 4608327260 | Inspection |  |  | "The mechanical inspector, upon notification from the permit holder or the permit holder's agent, shall make the following inspections... 1. Underground inspection... after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place... 2. Rough-in inspection... prior to the installation of wall or ceiling membranes. 3. Final inspection shall be made upon completion of the mechanical system. Exception: Ground-source heat pump loop systems tested in accordance with Section 1208.1.1 shall be permitted to be backfilled prior to inspection." | CHAPTER 9.06 - MECHANICAL AND FUEL GAS CODE, 107.2 Required inspections and testing | 2020 | https://www.harrisburgsd.gov/DocumentCenter/View/212/Harrisburg-SD-Codified-Municipal-Ordinances-Updated-June-30-2020-PDF
South Dakota | Union | Elk Point | City | 4612718620 | Permit |  |  | "Any person who commences work on a mechanical system before obtaining the necessary permits shall be subject to a Late Application Fee..." and "An owner, authorized agent, or contractor who desires to erect, install, enlarge, alter, repair, remove, convert, or replace an installation regulated by this code... shall first make application to the Building Official and obtain the required permit for the work." | CHAPTER 9.05 - MECHANICAL AND FUEL GAS CODES, 106.5.1 Work commencing before permit issuance | 2022 | https://files.frontdeskgworks.com/city/1912/media/elkpointmunicipalordinances.docx
South Dakota | Union | Elk Point | City | 4612718620 | Inspection |  |  | "The mechanical inspector... shall make the following inspections... 1. Underground inspection... 2. Rough-in inspection... 3. Final inspection shall be made upon completion of the mechanical system. Exception: Ground-source heat pump loop systems tested in accordance with Section 1208.1.1 shall be permitted to be backfilled prior to inspection." | CHAPTER 9.05 - MECHANICAL AND FUEL GAS CODES, 107.2 Required inspections and testing | 2022 | https://files.frontdeskgworks.com/city/1912/media/elkpointmunicipalordinances.docx
Arizona | Cochise | Sierra Vista | City | 466820 | Permit |  |  | "Application for construction, installation, and use of alternative energy systems will follow the normal building permit process." Section 151.06.003(B) states the contemplated systems include "geothermal systems." | Section 151.06.003 Alternative Energy Systems | 2026 | https://codelibrary.amlegal.com/codes/sierravista/latest/sierravistaUDO/0-0-0-1386
Tennessee | Shelby |  | County | 47157 | Definition: Well |  |  | "Geothermal Well: A well constructed for the primary purpose of adding or removing British Thermal Units (Btu) from groundwater for heating or cooling purposes." | Section 3.20 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby |  | County | 47157 | Definition: Geothermal Heat Pump |  |  | "Groundwater Heat Pump: Any mechanical device used for heating or cooling, which adds removes British Thermal Units (Btu) from groundwater." | Section 3.22 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby |  | County | 47157 | Permit |  |  | Section 4.02(A): "A permit shall be obtained from the Department prior to beginning the installation, modification, repair, or abandonment of a water well or any other type of well..." Section 4.02(C): "If a well application is approved by the Department, the well driller shall [be] issued a permit. Receipt of the permit shall constitute permission to begin well construction..." Section 11(B)(1): "Any person requesting a permit to construct a water well for use in an underground heat pump system... shall limit such discharges by taking conservation steps established by the Department." Section 11(D): "The design of such heat pump systems, shall be approved by the applicable code, and the owner shall have a valid mechanical permit." | Section 4.02; Section 11 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby |  | County | 47157 | Inspection |  |  | Section 4.04(F): "It shall be the duty of the well driller to notify the Department when construction of a well is to begin and when the work is completed so that proper inspections may be made during and after construction..." Section 8(A): "During the construction, modification, repair, or abandonment of any well the Department may conduct such periodic inspections as it deems necessary to insure conformity with applicable standards." | Section 4.04(F); Section 8 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby |  | County | 47157 | Licensed Driller |  |  | Section 1.02(A): "all such activities which are contracted for shall be carried by those persons having a valid Tennessee License for Water Well Drillers..." Section 11(D): "All residential, commercial and industrial heat pump systems, shall be horizontal closed loop system with no discharge." | Section 1.02(A); Section 11(D) |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby |  | County | 47157 | Decommissioning |  |  | Section 9.01(A): "All abandoned wells shall be filled with Portland cement grout, a high solids bentonite grout, or a Portland cement grout and bentonite combination..." Section 9.01(B): "The owner shall submit a plan to fill at the owners expense any abandoned or condemned well within thirty (30) days after receipt of notice..." Section 9.01(C): "All abandoned wells shall be filled only by a person having a valid license from the Tennessee Department of Environment and Conservation, or be an engineer or geologist registered with the State of Tennessee." Section 9.03(B): "All wells shall be filled with the required sealing or fill material from the bottom of the well up..." and Section 9.03(C): "The grout shall be pumped into the well through a tremmie pipe in one continuous operation." | Section 9.01; Section 9.03 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby |  | County | 47157 | Other Prohibitions/Regulations |  |  | "Non-aqueous heat pump systems shall be prohibited." | Section 11(E) |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Texas | Tarrant | Arlington | City | 4804000 | Definition: Geothermal Heat Pump |  |  | "Geoexchange System A system comprised of a central pump that transfers heat to or from the ground by passing fluid through underground coils in the ground or in body of surface water for the purpose of preconditioning air used in building heating or cooling." | 12.3.5. ACCESSORY USES AND STRUCTURES B. Alternative Energy System c. Geoexchange System | 2025 | https://www.arlingtontx.gov/files/assets/city/v/5/city-secretary/documents/city-code-of-ordinances/unified-development-code-chapter.pdf
Texas |  | Benbrook | City | 4807552 | Setback - Property Lines | 5 | feet | "Placement: No portion of a closed-loop system may be constructed within five feet (5') of a property line or within a dedicated easement without obtaining written permission from the City and/or all franchised utilities." | 17.84.130.C.1.b | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas |  | Benbrook | City | 4807552 | Permit |  |  | "Building Permit Required: A building permit must be obtained prior to the construction or installation of a closed-loop geothermal heat pump system." The ordinance also lists required application contents, including permit fee, survey and legal description, plan view layout, electrical line drawing, and standard installation drawings. | 17.84.130.C.1.c | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas |  | Benbrook | City | 4807552 | Decommissioning |  |  | "Abandoned: If a closed-loop geothermal heat pump system has been abandoned meaning not in operation for a period of six (6) months or is defective or is deemed to be unsafe by the Building Official, the closed-loop geothermal heat pump system shall be required to be repaired by the owner to meet federal, state and local safety standards, or be removed by the property owner within the time period allowed by the Building Official in accordance with federal, state and local regulations. If the owner fails to remove or repair the defective or abandoned closed-loop geothermal heat pump system, the City may pursue legal action to the system removed at the owner's expense." | 17.84.130.C.2.d | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas |  | Benbrook | City | 4807552 | Open-loop Prohibitions |  |  | "Open-loop systems shall be prohibited." | 17.84.130.C.1.a | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas | Nueces | Corpus Christi | City | 4817000 | Definition: Geothermal Heat Pump |  |  | "Essential domestic activity" ... "does not include ... non-closed system geothermal heating/cooling systems." | Rule 1.1 Definitions | 2025 | https://www.corpuschristitx.gov/media/k4rg0ztp/2025gmp_withappendices_final.pdf
Texas |  | Lake Worth | City | 4841056 | Setback - Property Lines | 5 | feet | "Placement. No portion of a closed-loop system may be constructed within five feet (5 ft.) of a property line or within a dedicated easement without obtaining written permission from the city and/or all franchised utilities." | § 14.06.021(d)(1)(B) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | City | 4841056 | Permit |  |  | "Building permit required. A building permit must be obtained prior to the construction or installation of a closed-loop geothermal heat pump system." The ordinance also lists required application contents, including "a survey and legal description," "a plan view layout," "electrical plan required," and "standard installation drawings of the closed loop geothermal installation." | § 14.06.021(d)(1)(C) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | City | 4841056 | Certification |  |  | "Any closed-loop geothermal heat pump system must be installed according to the manufacturer's recommendations and under the seal of a professional engineer registered in the State of Texas." | § 14.06.021(d)(2) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | City | 4841056 | Decommissioning |  |  | "Abandoned. If a closed-loop geothermal heat pump system has been abandoned meaning not in operation for a period of six (6) months or is defective or is deemed to be unsafe by the city manager and/or designee, the closed-loop geothermal heat pump system shall be required to be repaired by the owner to meet federal, state and local safety standards, or be removed by the property owner within the time period allowed by the city manager and/or designee in accordance with federal, state and local regulations. If the owner fails to remove or repair the defective or abandoned closed-loop geothermal heat pump system, the city may pursue legal action to [have] the system removed at the owner's expense." | § 14.06.021(d)(2)(D) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | City | 4841056 | Open-loop Prohibitions |  |  | "Open-loop systems shall be prohibited." | § 14.06.021(d)(1)(A) | 2019 | https://ecode360.com/40375001
Texas | Atascosa | Pleasanton | City | 4858280 | Permit |  |  | § 52.02.2(C): "It shall be unlawful for any person to reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled beat exchange system... without first applying for and securing a permit from the Public Works Department." § 52.04 repeats the same requirement for repair or closure work. § 52.05 adds: "Every application for a permit for the drilling, construction, repair, or plugging of a well or the construction, repair, or plugging of a well for the purpose of an earth-coupled heat exchange system, shall be considered incomplete unless all information requested by the Public Works Department application form has been provided." | § 52.02.2 PERMIT FOR NEW WELL REQUIRED; § 52.04 PERMIT FOR REPAIR OR CLOSURE OF EXISTING WELL REQUIRED; § 52.05 APPLICATION FOR PERMIT; INFORMATION REQUIRED | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | City | 4858280 | Inspection |  |  | § 52.06(A): "It shall be the duty of the Public Works Director to consider every permit application submitted under this chapter, to inspect the property where any well will be drilled, sunk, dug, or bored..." § 52.06(B) states: "Divisions (A)(2), (3) and (4) of this section do not apply to injection wells for the purpose of an earth-coupled heat exchange system." | § 52.06 INSPECTION BEFORE ISSUANCE OF PERMIT | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | City | 4858280 | Decommissioning |  |  | § 52.02.2(C): "It shall be unlawful for any person to reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled beat exchange system... without first applying for and securing a permit from the Public Works Department." § 52.04 likewise provides that no person may "reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled beat exchange system" without first securing a permit. | § 52.02.2 PERMIT FOR NEW WELL REQUIRED; § 52.04 PERMIT FOR REPAIR OR CLOSURE OF EXISTING WELL REQUIRED | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | City | 4858280 | Open-loop Prohibitions |  |  | § 52.02(C): "An open system, geothermal well that draws water from an aquifer and is circulated through the heat exchange system or geothermal wells which inject water into an aquifer will not be permitted within the limits of the city." | § 52.02 PROHIBITED ACTIVITIES | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | City | 4858280 | Other Prohibitions/Regulations |  |  | § 52.02(A): "It shall be unlawful for anyone to drill, maintain, or otherwise construct or have constructed... injection wells for the purpose of a earth-coupled heat exchange system, within the city or the Public Works Department service area." § 52.02(B): "To preserve the water quality of the aquifer, the construction of any bore hole, injection well for the purpose of an earth-coupled heat exchange system, or water well for the purpose of an earth-coupled heat exchange system located over the Carrizo-Wilcox Aquifer Recharge Zone and Transition Zone shall be prohibited." | § 52.02 PROHIBITED ACTIVITIES | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas |  | San Antonio | City | 4865000 | Permit |  |  | "It shall be unlawful for anyone to drill, maintain, or otherwise construct or have constructed... injection wells for the purpose of a earth-coupled heat exchange system, within the City of San Antonio or SAWS Water Quality Division." Section 34-567(b) adds: "All drilling or construction of... injection wells for the purpose of an earth-coupled heat exchange system, shall be done in strict compliance with the terms of the well drilling permit, the SAWS Water Well Permitting Procedures, and 30 TAC, Chapter 238." Section 34-568 further states: "It shall be unlawful for any person to reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled heat exchange system... without first applying for and securing a permit from the SAWS Water Quality Division." | Sec. 34-567. Permit for drilling new well required. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | City | 4865000 | Inspection |  |  | "It shall be the duty of the SAWS Water Quality Division to consider every permit application submitted under this division, to inspect the property where any well will be drilled, sunk, dug, or bored..." Section 34-573(c) also refers to "any water well that was constructed without a permit and associated inspections." | Sec. 34-570. Inspection before issuance of permit. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | City | 4865000 | Decommissioning |  |  | Section 34-568 makes a permit mandatory to "plug a well or injection well for the purpose of earth-coupled heat exchange system." Section 34-574(c) states: "Every abandoned well shall be filled and plugged in accordance with all applicable TNRCC regulations and SAWS Water Well Permitting Procedures..." Section 34-573(d) authorizes SAWS to order an owner "to plug this well in such a manner as prescribed by the SAWS Board" when the well is contaminating or defective. | Sec. 34-568. Permit for repair or closure of existing well required.; Sec. 34-574. Abandoned Wells. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | City | 4865000 | Open-loop Prohibitions |  |  | Section 34-567(e) states: "An open system, geothermal well that draws water from an aquifer and is circulated through the heat exchange system or geothermal wells which inject water into an aquifer will not be permitted within the limits of the City of San Antonio and within SAWS Water Quality Division." | Sec. 34-567. Permit for drilling new well required. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | City | 4865000 | Other Prohibitions/Regulations |  |  | Section 34-567(d) states: "To preserve the water quality of the aquifer, the construction of any bore hole, injection well for the purpose of an earth-coupled heat exchange system, or water well for the purpose of an earth-coupled heat exchange system located over the Edwards Aquifer Recharge Zone and Transition Zone shall be prohibited." | Sec. 34-567. Permit for drilling new well required. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Utah | Millard |  | County | 49027 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System (Major). A system or facility using the thermal energy resources of the Earth (geothermal energy) to provide mechanical or electrical power or heating or cooling systems for commercial purposes which may or may not be located on the same site as the Geothermal Energy System (Major)." Also, "Geothermal Energy System (Minor). A system or facility using the thermal energy resources of the Earth (geothermal energy) to provide mechanical or electrical power or heating or cooling systems for private, non- commercial purposes for use on the same site as the Geothermal Energy System (Minor)." | APPENDIX A TABLE OF USES AND ACCOMPANYING USE DEFINITIONS | 2014 | https://millardcounty.gov/wp-content/uploads/public-notices/2014/PC_-_CODIFICATION_CORRECTIONS_PC_Public_Hearing_02052014__Z-2014-002.pdf
Utah | Millard |  | County | 49027 | Other Prohibitions/Regulations |  |  | The Table of Uses states: "X = Use Prohibited in the Zoning District (Zone)." It further states: "A Use that is not identified in the Table of Uses is determined to be a Prohibited Use in Millard County." For "Geothermal Energy System (Minor)," the table shows "X" in the "TC" zoning district. For "Geothermal Energy System (Major)," the table shows "C-2" in "RF" and "X" in "AG-20," "AG," "AI," "R1," "TC," "HC," "LI," and "HI." | APPENDIX A TABLE OF USES AND ACCOMPANYING USE DEFINITIONS | 2014 | https://millardcounty.gov/wp-content/uploads/public-notices/2014/PC_-_CODIFICATION_CORRECTIONS_PC_Public_Hearing_02052014__Z-2014-002.pdf
Utah |  | Millcreek | City | 4950150 | Screening |  |  | "HVAC systems, utility meters, and overhead powerlines/utilities -shall be screened from view from a pedestrian perspective from the adjacent street." | 19.44.060 SUBDIVISION OF ATTACHED DWELLING UNITS | 2018 | https://www.millcreekut.gov/AgendaCenter/ViewFile/Item/75?fileID=485
Utah |  | Murray | City | 4953230 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) SYSTEM: Means a central heating and/or cooling system that pumps heat to or from the ground. It uses the earth as a heat source in the winter or a heat sink in the summer. These systems reduce operational costs of heating and cooling by taking advantage of moderate ground temperatures. GSHP as used in this chapter includes, but is not limited to, any such systems commonly referred to as Geothermal Wells, Geothermal Heat Pump Wells, Geothermal Heat Pumps, Closed-loop Heating/Cooling Exchange Wells, and Heat Exchange Units." | 13.30.030: DEFINITIONS | 2021 | https://www.murray.utah.gov/DocumentCenter/View/12337
Utah |  | Murray | City | 4953230 | Other Prohibitions/Regulations |  |  | "The City restricts GSHP wells drilled in Source Protection Zones 1 through 4 as follows: 1. GSHP wells of any depth are prohibited in Zones 1 and 2. 2. GSHP wells less than 30' are restricted in zones 3 and 4." | 13.30.070(C) Ground Source Heat Pump wells | 2021 | https://www.murray.utah.gov/DocumentCenter/View/12337
Vermont | Windsor | Woodstock | Town | 5002785975 | Noise Limits | 55 | dBA | 'Generators, heat pumps, and or air condition units or compressors when placed outdoors shall not require a permit if they comply with the following: ... D. Shall not exceed 55 decibels as measured 3 (three) feet from the unit.' | SECTION 533 GENERATORS/HEAT PUMPS/AC | 2020 | https://www.townofwoodstock.org/fileadmin/files/Archive/2020/10/TOWN-Zoning-Regulations-searchable-1.pdf
Vermont | Windsor | Woodstock | Town | 5002785975 | Permit |  |  | 'Generators, heat pumps, and or air condition units or compressors when placed outdoors shall not require a permit if they comply with the following...' and 'F. An exception may be granted in special circumstances with a Conditional use Approval; G. If placed within the Design Review District, a Design Review permit is required.' | SECTION 533 GENERATORS/HEAT PUMPS/AC | 2020 | https://www.townofwoodstock.org/fileadmin/files/Archive/2020/10/TOWN-Zoning-Regulations-searchable-1.pdf
Vermont | Windsor | Woodstock | Town | 5002785975 | Screening |  |  | 'Generators, heat pumps, and or air condition units or compressors when placed outdoors shall not require a permit if they comply with the following: ... C. Shall be screened from public view.' | SECTION 533 GENERATORS/HEAT PUMPS/AC | 2020 | https://www.townofwoodstock.org/fileadmin/files/Archive/2020/10/TOWN-Zoning-Regulations-searchable-1.pdf
Virginia | Northampton |  | County | 51131 | Other Prohibitions/Regulations |  |  | The ordinance treats "Geothermal heating facilities" as a special use in the IL district and as a special use in the IG district: Section 17-3(f) lists "Geothermal heating facilities" under "Special Uses and Structures," while Section 18-3(o) likewise lists "Geothermal heating facilities" under "Special Uses and Structures." In those districts, only principal permitted uses are allowed by right under Sections 17-2 and 18-2, so geothermal heating facilities are not permitted by right there. | Section 17-2 and Section 17-3; Section 18-2 and Section 18-3 | 1992 | https://cdnsm5-hosted.civiclive.com/UserFiles/Servers/Server_14877142/File/Government/Departments_Elected%20Offices/Planning,%20Permiting%20&%20Enforcement/ordinance%201983%20zoning.pdf
Washington | Garfield |  | County | 53023 | Definition: Geothermal Heat Pump |  |  | "Alternative Energy System (Geothermal)" means "Equipment that transfer thermal energy to and/or from the ground for purposes of heating and/or cooling a building. An alternative energy system (geothermal) consists of a closed-loop system of pipes filled with liquid, a heat exchanger and a heat pump." | 1.01.030 Definitions | 2022 | https://www.garfieldcountywa.gov/media/5741
Washington | Garfield |  | County | 53023 | Permit |  |  | The land use matrix lists "Alternative energy facility" as "C-3" in the Agricultural zone and "C" in Agricultural Transition, Commercial, and Industrial zones; Mountain Cabin is "X." The ordinance states: "Allowed (A) means that the land use is allowed outright. Conditional Use (C) means that the land use may be allowed if it is granted approval pursuant to Chapter 1.05." Footnote C-3 adds: "RENEWABLE ENERGY FACILITIES ON AGRICULTURAL LANDS ARE EXEMPT FROM THE ONE ACRE CONVERSION OF AG LAND RULE, HOWEVER, APPLICANTS FOR THESE TYPES OF CONDITIONAL USES SHALL DEMONSTRATE EFFORTS TO FIRST UTILIZE NON-PRODUCTIVE LANDS WITH POOR SOILS THAT ARE NOT OTHERWISE SUITABLE FOR AGRICULTURAL PURPOSES." | 1.03.030 Permitted land uses / Land Use Matrix and C-1, C-2, C-3 footnotes | 2022 | https://www.garfieldcountywa.gov/media/5741
Washington | Garfield |  | County | 53023 | Other Prohibitions/Regulations |  |  | The land use matrix lists "Alternative energy facility" as "X" in the Mountain Cabin zone. The matrix legend states: "A - ALLOWED C - CONDITIONAL USE ... X - NOT ALLOWED." | 1.03.030 Permitted land uses / Land Use Matrix | 2022 | https://www.garfieldcountywa.gov/media/5741
Washington | Grant |  | County | 53025 | Definition: Geothermal Heat Pump |  |  | Table IV footnote 4 defines 'Closed geothermal loop' as: 'A network of underground piping carrying fluid under pressure used to heat and cool a structure.' | Section 5. Amends WAC 246-272A-0210 Location | 2025 | https://www.granthealth.org/DocumentCenter/View/853
Washington |  | Shoreline | City | 5363960 | Permit |  |  | "Air-to-water heat pump manufacturers shall report the hourly heating output or heating efficiency with and without defrost operation at 32°F ... The hourly heating output or heating efficiency with and without defrost operation shall be documented on the mechanical permit drawings." | Section C403.3.2 | 2021 | http://cosweb.ci.shoreline.wa.us/uploads/attachments/cck/council/staffreports/2021/staffreport111521-9a.pdf
Wisconsin |  | New Auburn | Village | 5500556350 | Setback - Property Lines | 4 | feet | "Air-conditioning equipment and heat pumps... shall be located at least four feet from side and rear property lines." | § 350-63. Other accessory uses, B. Air-conditioning equipment and heat pumps | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | New Auburn | Village | 5500556350 | Setback - Yards | 4 | feet | "Air-conditioning equipment and heat pumps... shall not be located forward the front faces of the principal building and shall be located at least four feet from side and rear property lines." | § 350-63. Other accessory uses, B. Air-conditioning equipment and heat pumps | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | New Auburn | Village | 5500556350 | Noise Limits | 65 | dBA | "No operation or activity shall transmit any noise exceeding 75 dBA from 7:00 a.m. to 10:00 p.m. and 65 dBA from 10:00 p.m. to 7:00 a.m. beyond the property line." | § 350-80. Noise | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | New Auburn | Village | 5500556350 | Screening |  |  | "Any object that has potential for safety, or attractive nuisance problems must, at the discretion of the Zoning Administrator, be security fenced." | § 350-63. Other accessory uses, B. Air-conditioning equipment and heat pumps | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin | Brown | Allouez | Village | 5500901150 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM (GEOTHERMAL HEAT EXCHANGE). Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. Geothermal energy systems consist of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump. This includes vertical closed loop, horizontal closed loop and water body closed loop systems." | 475-159 TERMS BEGINNING WITH 'G' |  | https://www.villageofallouezwi.gov/wp-content/uploads/2020/07/Allouez-Zoning-Ordinance-Fradt.pdf
Wisconsin | Brown | Allouez | Village | 5500901150 | Permit |  |  | "To engage in the use of a building or land or any other activity requiring one or more permits or approvals under this zoning ordinance without obtaining such required permits or approvals" is unlawful, and "To engage in the use of a building or land or any other activity requiring one or more permits or approvals under this zoning ordinance in any way inconsistent with any such permit or approval" is also a violation. | 475-141 VIOLATIONS |  | https://www.villageofallouezwi.gov/wp-content/uploads/2020/07/Allouez-Zoning-Ordinance-Fradt.pdf
Wisconsin | Brown | Allouez | Village | 5500901150 | Other Prohibitions/Regulations |  |  | "No portion of a geothermal energy system may be located within a stream or stream buffer." | 475-78 F. Geothermal Energy Systems |  | https://www.villageofallouezwi.gov/wp-content/uploads/2020/07/Allouez-Zoning-Ordinance-Fradt.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Setback - Property Lines | 25 | feet | Section 315-91(C)(3)(c) provides: "Above ground equipment shall comply with the setback requirements of the respective zoning district." Section 315-91(C)(3)(e) adds: "Geothermal energy systems shall conform to all setbacks requirements for Accessory Structures." Accessory-structure side/rear lot-line setbacks vary by district, including R-1 side/rear 8 ft.; R-2 side/rear 8 ft.; R-3 side/rear 5 ft.; R-4 side/rear 10 ft.; RD-1 side/rear 10 ft.; B-1 rear 25 ft.; B-2 side/rear 10 ft.; I-1 rear 25 ft.; I-2 rear 25 ft. | 315-91 Alternative Energy Systems, C(3)(c)-(e); district setback tables | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Setback - Wastewater | 75 | feet | "Geothermal energy systems shall conform to all setbacks requirements for Accessory Structures and shall: 1. Be setback a minimum of 75 feet between a vertical geothermal energy system and a personal onsite wastewater treatment system. 2. Be setback a minimum of 25 feet between a horizontal geothermal energy system and a personal onsite wastewater treatment system." | 315-91 Alternative Energy Systems, C(3)(e)1-2 | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Setback - Private Water | 75 | feet | "...except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 315-91 Alternative Energy Systems, C(3)(e)3 | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Setback - Public Water | 200 | feet | "Geothermal energy systems shall... Not be located closer than 200 feet to a well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 315-91 Alternative Energy Systems, C(3)(e)3 | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Permit |  |  | Section 315-9(D): "No structure, land, water, or air shall hereafter be used, and no structure or part thereof shall hereafter be located, erected, moved, reconstructed, extended, enlarged, converted, or structurally altered without a zoning permit..." Section 315-91(C)(2)(b) states the purpose is to "Oversee the permitting of geothermal systems." | 315-9 Interpretation; 315-91 Alternative Energy Systems, C. Geothermal Energy Systems | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Certification |  |  | "A geothermal energy system shall conform to applicable industry standards including those of ANSI. Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by UL or other approved independent testing agency." | 315-91 Alternative Energy Systems, C(3)(b) | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | Village | 5500919700 | Other Prohibitions/Regulations |  |  | "Equipment, piping and devices shall not be located in any easement or right-of-way." | 315-91 Alternative Energy Systems, C(3)(d) | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Wastewater | 1000 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Wastewater-related distances include: "Two hundred feet between a well field and ... private onsite wastewater treatment system (POWTS) treatment tank or holding tank component and associated piping"; "Four hundred feet between a well field and a POWTS dispersal component with a design capacity of less than 12,000 gallons per day"; and "One thousand feet between a well field and ... agricultural, industrial, commercial or municipal waste water treatment plant treatment units, lagoons, or storage structures; ... or POWTS dispersal component with a design capacity of 12,000 gallons per day or more." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Public Water | 1200 | feet | Section 13-1-30(f) subjects "Geothermal wells, systems or heat exchange drilling" to the "separation distances in Section (h)." Section (h) says: "The following separation distances as specified in s. NR 811.12(5)(d), Wis. Adm. Code, shall be maintained within the Wellhead protection overlay district." The largest listed distance is "Twelve hundred feet between a well field and any solid waste storage..." while other listed distances from the municipal well/well field include 10 feet, 50 feet, 200 feet, 300 feet, 400 feet, 600 feet, and 1,000 feet. | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Fuel (above ground) | 1200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Relevant above-ground fuel tank distances include: "Ten feet between a well and an emergency or standby power system ... that has a double wall above ground storage tank"; "Two hundred feet between a well field and ... one or two family residential heating fuel oil underground storage tank or above ground storage tank"; "Three hundred feet between a well field and any farm above ground storage tank..."; "Six hundred feet between a well field and any ... above ground storage tank system with double wall, or single wall tank with secondary containment and under a canopy..."; and "Twelve hundred feet between a well field and ... any single wall farm ... above ground storage tank or other single wall ... above ground storage tank..." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Fuel (below ground) | 1200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Underground fuel tank distances include: "Two hundred feet between a well field and ... one or two family residential heating fuel oil underground storage tank..."; "Three hundred feet between a well field and any farm underground storage tank system or other underground storage tank system with double wall and with electronic interstitial monitoring..."; "Six hundred feet between a well field and any farm underground storage tank system or other underground storage tank system with double wall and with electronic interstitial monitoring..."; and "Twelve hundred feet between a well field and ... any single wall farm underground storage tank or single wall farm above ground storage tank or other single wall underground storage tank..." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Sewer Lines | 200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Section (h)(2) states: "Fifty feet between a well and a storm sewer main or a sanitary sewer main where the sanitary sewer main is constructed of water main class materials and joints." Section (h)(3) states: "Two hundred feet between a well field and any sanitary sewer main not constructed of water main class materials..." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Water Bodies | 400 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Section (h)(6) requires "Four hundred feet between a well field and ... a storm water retention or detention pond." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Setback - Hazardous Materials/Fertilizers | 1200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Hazardous-material related distances include: "Three hundred feet between a well field and any ... underground storage tank system ... These requirements apply to tanks containing ... hazardous substances"; "Three hundred feet between a well field and ... above ground storage tank system ... These requirements apply to tanks containing ... hazardous substances"; "Six hundred feet between a well field and any ... underground storage tank system ... [and] above ground storage tank system ... These requirements apply to tanks containing ... hazardous substances"; and "Twelve hundred feet between a well field and ... any single wall ... underground storage tank or above ground storage tank ... These requirements apply to tanks containing ... hazardous substances; and bulk pesticide or fertilizer handling or storage facilities." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Permit |  |  | In the Wellhead Protection Overlay District, "Geothermal wells, systems or heat exchange drilling, along with any associated piping and/or ground loop component installations" are listed as conditional uses. Section 13-1-30(f) states these uses "may be conditionally permitted ... in accordance with Title 13, Chapter 1 Article D Conditional Uses and subject to the separation distances in Section (h) Separation Distances." Article D then requires "Application for conditional use permits" and Village Board approval before the permit is issued. | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT; (f) Conditional Uses; ARTICLE D Conditional Uses |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Inspection |  |  | Section 13-1-30(h)(2), which applies because geothermal wells/systems are subject to Section (h), requires testing of certain sewer infrastructure: "Gravity sanitary sewers shall be successfully air pressure tested in place. The air pressure test shall meet or exceed the requirements of the 4 psi low pressure air test... Force mains shall be successfully pressure tested with water to meet the AWWA C600 pressure and leakage testing requirements for one hour at 125% of the pump shut-off head." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | Village | 5502328450 | Other Prohibitions/Regulations |  |  | The overlay ordinance states that certain uses are prohibited in the Wellhead Protection Overlay District, but "Geothermal wells, systems or heat exchange drilling, along with any associated piping and/or ground loop component installations" are instead listed in Section 13-1-30(f) as uses that "may be conditionally permitted ... subject to the separation distances in Section (h) Separation Distances." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (g) Prohibited Uses |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin |  | Belleville | Village | 5502506300 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as 'ground source heat pumps,' along with any associated piping and/or ground loop component installations." | § 615-18.1.F(5) | 2017 | https://assets.parkingreform.org/assets/52b52ef6-63ed-40fb-96c7-e77e66fdf1cf/belleville-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | Belleville | Village | 5502506300 | Permit |  |  | In the Groundwater Protection Overlay District, "Geothermal wells, also known as 'ground source heat pumps,' along with any associated piping and/or ground loop component installations" are listed as "Conditional uses." Section 615-20.A states that the Zoning Administrator may issue "a conditional use permit" only "after review, public hearing, and approval by the Plan Commission." | § 615-18.1.F(5); Article IV; § 615-20.A | 2017 | https://assets.parkingreform.org/assets/52b52ef6-63ed-40fb-96c7-e77e66fdf1cf/belleville-wisconsin-united-states-attachment.pdf?download
Wisconsin | Dane | DeForest | Village | 5502519350 | Permit |  |  | Within the WP Wellhead Protection Overlay District, "Geothermal wells, systems, or heat exchange drilling, along with any associated piping and/or ground loop component installations" are listed as "conditional uses." The ordinance further provides that "No application for a conditional use permit shall be placed on any agenda for action... unless the Zoning Administrator has determined that a complete application has been submitted." | §15.155(5) CONDITIONAL USES; §15.16(3) APPLICATION, PROCEDURES, AND CRITERIA | 2026 | https://www.deforestwi.gov/DocumentCenter/View/86/Chapter-15-Zoning-Code-PDF
Wisconsin | Dane | Maple Bluff | Village | 5502548750 | Definition: Geothermal |  |  | "Such energy generating equipment includes solar, wind, and geothermal energy systems that convert energy from the sun, wind, or earth into usable thermal, mechanical, chemical, or electrical energy, where such energy system is accessory to the principal use of the parcel, and primarily supplies energy to such principal use." | § 225-3-5 C. Small exterior communication or energy system | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dane | Maple Bluff | Village | 5502548750 | Permit |  |  | "Prior to installation or expansion, shall be subject to Building Board approval per § 225-8-5 ... Following such approval, a building permit shall also be required." Also, for geothermal systems, "All activities, materials, structures, and products associated with the installation and maintenance of the system shall comply with applicable state-approved standards and drilling permit procedures..." | § 225-3-5 C(2) and C(10)(d) | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dane | Maple Bluff | Village | 5502548750 | Certification |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of the system shall comply with applicable state-approved standards and drilling permit procedures and shall meet the certification standards established by the IGSHPA or other professional geothermal system accreditation association recognized by the State of Wisconsin." | § 225-3-5 C(10)(d) | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dane | Maple Bluff | Village | 5502548750 | Other Prohibitions/Regulations |  |  | For open loop geothermal systems, "Such systems may not be installed directly in a navigable body of water." | § 225-3-5 C(10)(e) | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dodge | Mayville | City | 5502750200 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | § 430-48.1 GWP Groundwater Protection Overlay District, Conditional uses | 2023 | https://ecode360.com/9525348
Wisconsin | Dodge | Mayville | City | 5502750200 | Permit |  |  | "The following uses may be conditionally permitted in the Wellhead Protection Area under § 430-49, Conditional uses, and subject to the separation distances in Subsection H, Separation distances. ... Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | § 430-48.1 GWP Groundwater Protection Overlay District, Conditional uses | 2023 | https://ecode360.com/9525348
Wisconsin | Dunn | Wheeler | Village | 5503386575 | Permit |  |  | "The following uses may be conditionally permitted in the Wellhead protection overlay district in accordance with Article E Conditional Uses and subject to the separation distances in Section (h) Separation Distances. ... (5) Geothermal wells, systems or heat exchange drilling, along with any associated piping and/or ground loop component installations." | Sec. 13-1-53 WP Wellhead Protection Overlay District; Conditional Uses | 2025 | https://villageofwheelerwi.com/wp-content/uploads/2025/12/well-head-protection-plan20251210_18043137.pdf
Wisconsin | Iowa | Barneveld | Village | 5504775 | Permit |  |  | "The following uses may be conditionally permitted in the Wellhead protection overlay district in accordance with Chapter 280 Article IV Conditional Uses and subject to the separation distances in Section (J) Separation Distances. ... 5) Geothermal wells, systems or heat exchange drilling, along with any associated piping and/ or ground loop component installations." | H. Conditional Uses | 2025 | https://ecode360.com/BA3856/laws/LF2493855.pdf
Wisconsin | Juneau | New Lisbon | City | 5505756900 | Definition: Geothermal Heat Pump |  |  | Conditional uses in the Groundwater Protection Overlay District include: "Geothermal wells, also known as ground source heat pump, along with any associated piping and/or ground loop component installations." | § 520-25.1 Groundwater Protection Overlay District | 2018 | https://ecode360.com/15204104
Wisconsin | Juneau | New Lisbon | City | 5505756900 | Permit |  |  | The ordinance states: "The following uses may be conditionally permitted in the Groundwater Protection Overlay District... Geothermal wells, also known as ground source heat pump, along with any associated piping and/or ground loop component installations." It further states these uses are "governed by the conditional use provisions in Article V of this chapter." | § 520-25.1 Groundwater Protection Overlay District | 2018 | https://ecode360.com/15204104
Wisconsin | Manitowoc | Reedsville | Village | 5507166875 | Permit |  |  | Table 3 lists "Geothermal equipment for private use not associated with a public or private utility" as an accessory use and marks it "Yes" under the conditional-use reference column; Section 8-12-4(A)(1) states: "A conditional use permit shall be required for the establishment of each use listed as a conditional use in Table 1 of this Chapter." | Table 3 - Table of Allowed Accessory Uses; 8-12-4: CONDITIONAL USE PERMITS | 2026 | https://storage.googleapis.com/juniper-media-library/506/2026/03/Ordinance%202026-01%20Amending%20Title%208.pdf
Wisconsin | Marathon | Rothschild | Village | 5507369725 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." | § 590-32 C(2)(d) | 2026 | https://ecode360.com/15464803
Wisconsin | Marathon | Rothschild | Village | 5507369725 | Permit |  |  | In the Wellhead Protection Overlay District, "Only the following uses may be conditionally permitted... (d) Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." Section E adds that "The Village shall permit conditional uses in the Groundwater Protection Overlay Districts" subject to application, referral, review, and hearing procedures. | § 590-32 C(2)(d); § 590-32 E | 2026 | https://ecode360.com/15464803
Wisconsin | Marathon | Schofield | City | 5507372150 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." | § 55-673(c)(2)(d) Conditional Uses | 2016 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/14110/801091/pdf
Wisconsin | Marathon | Schofield | City | 5507372150 | Permit |  |  | Geothermal wells/ground source heat pumps are listed as a conditional use: "Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." The ordinance then states: "The City shall permit conditional uses in the Groundwater Protection Overlay District subject to" the application, review, hearing, and standards in § 55-673(e). | § 55-673(c)(2)(d); § 55-673(e) Administration of Conditional Use Permits | 2016 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/14110/801091/pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Definition: Geothermal Heat Pump |  |  | "A Geothermal Energy System (GES) is a central heating and/or cooling system that uses the moderate temperatures of subsurface ground or a body of water to assist with the heating or cooling of a building or a building’s water. A GES requires an underground heat exchanger, in the form of a network of underground or underwater pipes or tubes filled with a liquid medium (refrigerant, water mixed with anti-freeze, or water). The liquid medium within the heat exchanger is transferred between a structure and the heat exchanger via pumps. In an Open Loop GES, ground or surface water is continuously drawn from an outside source through the heat exchanger pipes and discharged after use. In a Closed Loop GES, the system is designed so that heat exchanger fluid does not come in direct contact with soils, groundwater, or surface water." | Section 94.4.09(19) Geothermal Energy System (GES) | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Setback - Roads | 10 | feet | "Underground GES pipes or tubes shall be set back a minimum of 10 feet from any lot line, public right-of-way, buried utility line, utility easement, and permanently protected natural resource area." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 2 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Setback - Right of Way | 10 | feet | "Underground GES pipes or tubes shall be set back a minimum of 10 feet from any lot line, public right-of-way, buried utility line, utility easement, and permanently protected natural resource area." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 2 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Setback - Property Lines | 10 | feet | "Underground GES pipes or tubes shall be set back a minimum of 10 feet from any lot line, public right-of-way, buried utility line, utility easement, and permanently protected natural resource area." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 2 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Permit |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable State-approved standards and drilling permit procedures..." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 5 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Certification |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable State-approved standards and drilling permit procedures and shall meet the certification standards established by the IGSHPA or other professional geothermal system accreditation association recognized by the State of Wisconsin." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 5 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | Town | 5507386050 | Other Prohibitions/Regulations |  |  | "GESs may not be installed directly in a navigable body of water..." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 6 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Oneida | Rhinelander | City | 5508567200 | Definition: Geothermal Heat Pump |  |  | "A geothermal energy system (GES) is a central heating and/or cooling system that uses the moderate temperatures of subsurface ground or a body of water to assist with the heating or cooling of a building or a building's water. A GES requires an underground heat exchanger, in the form of a network of underground or underwater pipes or tubes filled with a liquid medium (refrigerant, water mixed with antifreeze, or water). The liquid medium within the heat exchanger is transferred between a structure and the heat exchanger via pumps. In an open loop GES, ground or surface water is continuously drawn from an outside source through the heat exchanger pipes and discharged after use. In a closed loop GES, the system is designed so that heat exchanger fluid does not come in direct contact with soils, groundwater, or surface water." | 5.07.4.09(13) Geothermal energy system (GES) | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Oneida | Rhinelander | City | 5508567200 | Permit |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable state-approved standards and drilling permit procedures..." | 5.07.4.09(13) Performance standards | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Oneida | Rhinelander | City | 5508567200 | Certification |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable state-approved standards and drilling permit procedures and shall meet the certification standards established by the IGSHPA or other professional geothermal system accreditation association recognized by the State of Wisconsin." | 5.07.4.09(13) Performance standards | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Oneida | Rhinelander | City | 5508567200 | Other Prohibitions/Regulations |  |  | "GESs may not be installed directly in a navigable body of water..." | 5.07.4.09(13) Performance standards | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Outagamie | Buchanan | Town | 5508710750 | Permit |  |  | Table 525-32-1 lists "Geothermal equipment for private use not associated with a public or private utility" and the "Is Permit Required?" column states "Yes." | Table 525-32-1: Accessory Uses, Buildings and Structures | 2024 | https://d3n9y02raazwpg.cloudfront.net/buchanan/fe958e2f-c4fa-11ee-8fe8-0050569183fa-301dd9fd-e864-4fb1-8bf5-0961d018c857-1710285886.pdf
Wisconsin | Racine | Wind Point | Village | 5510187700 | Definition: Geothermal |  |  | "Geothermal Energy System. A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems." | Sec. 36-301. Definitions | 2024 | https://cms3.revize.com/revize/windpoint/Documents/Government/Agenda%20and%20Minutes/Plan%20Commission/2024/Plan%20Commission%20Agenda%20&%20Meeting%20Packet%2001.04.2024.pdf
Wisconsin | Racine | Wind Point | Village | 5510187700 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System, Horizontal. A geothermal energy system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth." "Geothermal Energy System, Vertical. A geothermal energy system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth." | Sec. 36-301. Definitions | 2024 | https://cms3.revize.com/revize/windpoint/Documents/Government/Agenda%20and%20Minutes/Plan%20Commission/2024/Plan%20Commission%20Agenda%20&%20Meeting%20Packet%2001.04.2024.pdf
Wisconsin | Sauk | Merrimac | Town | 5511151350 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | §185-21A(6)(e) Conditional Uses |  | https://merrimacwi.gov/vertical/sites/%7BCBEFE108-6CEC-4014-B024-0697DD562493%7D/uploads/Proposed_WHPP_ORD_185-21A_as_Posted.pdf
Wisconsin | Sauk | Merrimac | Town | 5511151350 | Permit |  |  | "The following uses may be conditionally permitted under Chapter 185 Zoning, Article IV Conditional Uses, in the Wellhead Protection Area Overlay District... (e) Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | §185-21A(6) Conditional Uses |  | https://merrimacwi.gov/vertical/sites/%7BCBEFE108-6CEC-4014-B024-0697DD562493%7D/uploads/Proposed_WHPP_ORD_185-21A_as_Posted.pdf
Wisconsin | Sauk | North Freedom | Village | 5511158025 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | 3.11(f)(5) Conditional Uses | 1996 | https://storage.googleapis.com/juniper-media-library/239/2026/01/CHAPTER%2016%20ZONING.pdf
Wisconsin | Sauk | North Freedom | Village | 5511158025 | Permit |  |  | In the Groundwater Protection Overlay District, "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations" are listed under "Conditional Uses." Section 4.1 states: "The Village Plan Committee may authorize the Village Board to issue a zoning permit for conditional uses after review and a public hearing." Section 4.2 requires applications for zoning permits for conditional uses, and Section 4.4 states the Plan Committee reviews and approves, approves with conditions, or rejects the application. | 3.11(f) Conditional Uses; 4.1 PERMITS; 4.2 APPLICATION; 4.4 REVIEW AND APPROVAL | 1996 | https://storage.googleapis.com/juniper-media-library/239/2026/01/CHAPTER%2016%20ZONING.pdf
Wisconsin | Sauk | North Freedom | Village | 5511158025 | Inspection |  |  | "The Village Board will act as the administrator and enforcement officer for the provisions of this Ordinance. Their duties shall be to interpret and administer this Ordinance and to issue, after on-site inspection, all permits required by this Ordinance." Also, "any trustee may enter at any reasonable time onto any public or private lands or waters to make a zoning inspection." | 2.3 ZONING ADMINISTRATOR DESIGNATED | 1996 | https://storage.googleapis.com/juniper-media-library/239/2026/01/CHAPTER%2016%20ZONING.pdf
Wisconsin | Sawyer | Spider Lake | Town | 5511375450 | Permit |  |  | "a Conditional Use Permit is required for the construction, installation or modification of alternative or renewable energy systems. These systems include, but are not limited to: solar systems, wind energy systems, geothermal units, and energy producing digester systems." | Section 6.11(A) Purpose and Intent | 2019 | https://storage.googleapis.com/juniper-media-library/534/2026/03/2019_FINAL_Ord_17-88_land_use_ordinance-1.pdf
Wisconsin | Sawyer | Spider Lake | Town | 5511375450 | Inspection |  |  | "For the purpose of issuance of necessary permits and inspections, all alternative energy systems are deemed to be structures. As a condition of the issuance of the Conditional Use Permit for an alternative or renewable energy system, the permit holder shall allow access to the site by the Zoning Administrator." | Section 6.11(C)(1) General | 2019 | https://storage.googleapis.com/juniper-media-library/534/2026/03/2019_FINAL_Ord_17-88_land_use_ordinance-1.pdf
Wisconsin | Sawyer | Spider Lake | Town | 5511375450 | Decommissioning |  |  | An applicant for an alternative or renewable energy system must provide "[a] description of the decommissioning process and the cost of decommissioning or removal of the system." | Section 6.11(B) Conditional Use | 2019 | https://storage.googleapis.com/juniper-media-library/534/2026/03/2019_FINAL_Ord_17-88_land_use_ordinance-1.pdf
Wisconsin | Shawano |  | County | 55115 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump (land use): Electrically powered systems that tap the stored energy of the earth. These systems use the earth's relatively constant temperature to provide heating, cooling, and hot water for homes and commercial buildings. In the FP district, each Ground Source Heat Pump must also meet the standards set forth in Section X.9.03(14) for Agricultural Structures." | X.9.03(140) Ground Source Heat Pump (land use) | 2019 | https://www.co.shawano.wi.us/i_shawano/pu/6-3-19_zoning_ordinance.pdf
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems." | 17.120 Application of Definitions, B. Definitions | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Setback - Property Lines | 10 | feet | 17.52 C.3.c requires: "Above ground equipment shall comply with the setback requirements of the respective zoning district." The referenced district standards are generally "Side and rear yard setbacks -10-feet or the height of the building or structure, whichever is greater" in AG-1, adopted by reference in AG-2, AG-3, R-1, C-1, IN-1, and M-1; R-2 uses the AG-1 standards except for street setback wording. | 17.30 AG-1 Large Parcel General Agricultural District; 17.31 AG-2 Animal Intensive Agricultural District; 17.32 AG-3 Smaller Parcel General Agricultural District; 17.33 R-1 Small Lot Residential District; 17.34 R-2 Large Lot Residential District; 17.35 C-1 Commercial District; 17.37 IN-1 Institutional District; 17.38 M-1 Manufacturing District; 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Setback - Wastewater | 75 | feet | 17.52 C.3.e provides: "Geothermal energy systems shall conform to all setbacks requirements for accessory structures and shall: (1) Be setback a minimum of 75 feet between a vertical geothermal energy system and a personal onsite wastewater treatment system. (2) Be setback a minimum of 25 feet between a horizontal geothermal energy system and a personal onsite wastewater treatment system." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Setback - Private Water | 75 | feet | 17.52 C.3.e(3) states geothermal systems shall "Not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Setback - Public Water | 200 | feet | 17.52 C.3.e(3) states geothermal systems shall "Not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Permit |  |  | The ordinance makes geothermal systems a conditional use in several districts: "Geothermal energy systems" are listed under "Conditional Uses" in R-1, R-2, and C-1. It also states in 17.52 C.1.b that the purpose is to "Oversee the permitting of geothermal systems." Separately, 17.100.B provides: "A Building Permit shall be required for the construction or alteration of any building or structure..." and 17.100.A states the Building Permit verifies conformity with applicable law. | 17.33 R-1 Small Lot Residential District; 17.34 R-2 Large Lot Residential District; 17.35 C-1 Commercial District; 17.52 C. Geothermal Energy Systems; 17.100 Building Permits | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | Town | 5511753375 | Certification |  |  | 17.52 C.3.b states: "A geothermal energy system shall conform to applicable industry standards including those of ANSI. Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by UL or other approved independent testing agency." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Taylor | Little Black | Town | 5511944900 | Permit |  |  | "The owner of any building or structure in the town... who constructs, installs... any building or structure within the Town shall seek and obtain from the Zoning Administrator a Zoning Permit prior to commencing... any construction, installation... of any building." Section 5.4.B adds: "A Zoning Permit shall be issued if and only if it has been satisfactorily determined... that the use of land and buildings set forth in the zoning permit application is consistent and in compliance with this ordinance." For conditional uses, Section 9.2.B requires "a copy of all federal, state, and county permits necessary for the proposed use." | Section 5.2 / 5.4 / 9.2 | 2018 | https://www.townoflittleblack.com/townoflittleblack/Ordinances%20and%20Permits/90%20Zoning/ZONING%20CODE%20OF%20LITTLE%20BLACK%202017-2-15%20.pdf
Wisconsin | Taylor | Little Black | Town | 5511944900 | Inspection |  |  | "Upon completion of a project for which a zoning permit is required, the owner shall notify the Zoning Administrator and request an inspection to determine completion and compliance with this Ordinance. The inspection must be made before a zoning certificate of compliance may be issued." | Section 5.4.F | 2018 | https://www.townoflittleblack.com/townoflittleblack/Ordinances%20and%20Permits/90%20Zoning/ZONING%20CODE%20OF%20LITTLE%20BLACK%202017-2-15%20.pdf
Wisconsin | Taylor | Little Black | Town | 5511944900 | Open-loop Prohibitions |  |  | Residential District purpose clause states: "Residential normal water usage is acceptable with the exception of open loop geothermal." Separately, Section 12.5.R prohibits "Any use requiring continuous pumping of a groundwater well." | Section 12.1 / 12.5.R | 2018 | https://www.townoflittleblack.com/townoflittleblack/Ordinances%20and%20Permits/90%20Zoning/ZONING%20CODE%20OF%20LITTLE%20BLACK%202017-2-15%20.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Definition: Geothermal |  |  | 'Geothermal Energy System. A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems.' Also: 'Geothermal Energy System, Horizontal. A geothermal energy system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth.' 'Geothermal Energy System, Vertical. A geothermal energy system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth.' | 17.13.01(B)(21)-(23) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Setback - Yards | 25 | feet | Section 17.7.03(C)(4) requires: 'Above ground equipment shall comply with the setback requirements of the respective zoning district.' Section 17.7.03(C)(6) adds: 'Geothermal energy systems shall conform to all setbacks requirements for accessory structures.' The accessory-structure yard rule in Section 17.6.02(E) states such structures 'shall not be closer than 25 feet to a rear lot line (unless a greater setback is required by the applicable zoning district).' | 17.7.03(C)(4), 17.7.03(C)(6), 17.6.02(E) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Setback - Wastewater | 75 | feet | Section 17.7.03(C)(6)(a): 'Be setback a minimum of 75 feet from a personal onsite wastewater treatment system.' | 17.7.03(C)(6)(a) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Setback - Private Water | 75 | feet | Section 17.7.03(C)(6)(b) creates an exception for private wells: geothermal systems may be closer than 200 feet 'when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system.' | 17.7.03(C)(6)(b) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Setback - Public Water | 200 | feet | Section 17.7.03(C)(6)(b): geothermal systems shall 'Not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system.' | 17.7.03(C)(6)(b) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Permit |  |  | Section 17.2.03 states: 'Applications for a Building Permit shall be made in duplicate to the Zoning Administrator...' and the permit application must include site and use information, with the permit 'granted or denied in writing by the Building Inspector and issued by the Zoning Administrator within 30 days.' Section 17.12.01 adds that 'all persons, firms, or corporations performing work in the Town of Polk for which this Chapter requires the application for a permit... shall pay a fee.' Geothermal systems are regulated in Chapter 17.7.03 as accessory systems under this chapter. | 17.2.03 BUILDING AND ZONING PERMIT; 17.12.01 FEES | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Inspection |  |  | Section 17.2.02(B) provides: 'The Duty of the Zoning Administrator or his designee, shall be to investigate all complaints, give notice of violations, and enforce the provisions of Chapter 17. The Zoning Administrator and his designee, may enter at any reasonable time onto any public or private lands or waters to make a Zoning Inspection.' | 17.2.02 COMPLIANCE | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | Town | 5513163875 | Other Prohibitions/Regulations |  |  | Section 17.7.03(C)(5) states: 'Equipment, piping and devices shall not be located in any easement or right-of-way.' | 17.7.03(C)(5) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | West Bend | Town | 5513185375 | Setback - Wastewater | 75 | feet | "Geothermal energy systems shall conform to all setbacks requirements for Accessory Structures and shall: (1) Be setback a minimum of 75 feet between a vertical geothermal energy system and a personal onsite wastewater treatment system. (2) Be setback a minimum of 25 feet between a horizontal geothermal energy system and a personal onsite wastewater treatment system." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | Town | 5513185375 | Setback - Private Water | 75 | feet | "[Geothermal systems shall] not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | Town | 5513185375 | Setback - Public Water | 200 | feet | "[Geothermal systems shall] not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | Town | 5513185375 | Permit |  |  | "A geothermal energy system shall require a Conditional Use permit in all zoning districts." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | Town | 5513185375 | Certification |  |  | "A geothermal energy system shall conform to applicable industry standards including those of ANSI. Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by UL or other approved independent testing agency." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Winnebago | Winchester | Town | 5513987650 | Definition: Geothermal |  |  | "Geothermal Energy System. A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems." "Geothermal Energy System, Horizontal. A geothermal energy system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth." "Geothermal Energy System, Vertical. A geothermal energy system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth." | 17.300 Definitions(115)-(117) | 2024 | https://townofwinchesterwi.gov/wp-content/uploads/2024/07/Chapter-17-Zoning-Ordinance-Approved-07-15-2024.pdf
Wisconsin | Winnebago | Wolf River | Town | 5513988475 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY: Energy fueled in ways that do not use up natural resources or harm the environment such as solar, wind, and geothermal". | CHAPTER A DEFINITIONS, SECTION 1.01 DEFINITIONS | 2015 | https://townofwolfrivercom-old.townweb.com/wp-content/uploads/2016/05/Town-Zoning-Ordinance.pdf
Wisconsin | Winnebago | Wolf River | Town | 5513988475 | Permit |  |  | Section 1.03(2): "after the effective date of this Ordinance, no structure, land or water shall be developed, and no structure or part thereof shall be located, erected, moved, reconstructed, enlarged, extended, converted or structurally altered without a Zoning/Building Permit and without full compliance with this Ordinance." Section 1.13: "No heat pumps that discharge water shall be installed in any facility in the Town of Wolf River unless and until the proposed installation is reviewed by the Planning and Zoning Committee... If the Planning and Zoning Committee is satisfied that such conditions are met... the heat pump installation may proceed, and the Zoning Administrator shall note the location of such installation." Section 1.21(3): "A Zoning/Building Permit shall be granted or denied in writing by the Zoning Administrator within thirty (30) days after filing of the application." | SECTION 1.03 GENERAL PROVISIONS; SECTION 1.13 HEAT PUMPS; SECTION 1.21 ZONING / BUILDING PERMITS | 2015 | https://townofwolfrivercom-old.townweb.com/wp-content/uploads/2016/05/Town-Zoning-Ordinance.pdf
California | Calaveras |  | County | 6009 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat exchange well" means "any uncased artificial excavation, constructed by any method, that uses the heat exchange capacity of the earth for heating and cooling, in which excavation the ambient ground temperature is thirty (30) degrees Celsius (eighty-six (86) degrees Fahrenheit) or less, and which excavation uses a closed loop, fluid system to prevent the discharge or escape of its fluid into surrounding aquifers or other geologic formations. Geothermal heat exchange wells include ground source heat pump wells." | 8.20.030 Definitions | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Roads | 30 | feet | Setback table: "Adjacent Road Easement where no specified right of way is identified — 30*." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Right of Way | 30 | feet | Setback table: "On-site Road Easement where no specified right of way is identified — 30**" and "Utility Easement — 10." The controlling most restrictive right-of-way/easement setback stated is 30 feet. | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Property Lines | 50 | feet | Setback table: "Property line of parcels that are less than five (5) acres in area — 10" and "Property line of parcels that are five (5) acres or more in area — 50." Because the chapter regulates "geothermal heat exchange wells," the controlling most restrictive property-line setback in this ordinance is 50 feet. | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Building Foundation | 10 | feet | Setback table: "Permanent structure — 10." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Wastewater | 150 | feet | Setback table: "Subsurface sewage leach field or other sewage dispersal area — 100"; "Watertight septic tank — 100"; "Seepage pit or cesspool (The use of cesspools is prohibited.) — 150." The controlling most restrictive wastewater setback is 150 feet. | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Animal Enclosures | 100 | feet | Setback table: "Animal enclosures — 100." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Fuel (below ground) | 150 | feet | Setback table: "Underground storage tank (petroleum products, e.g., gasoline and diesel) — 150." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Sewer Lines | 50 | feet | Setback table: "Any sewer line (e.g., sanitary, industrial, main or lateral or combined storm water drain) — 50." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Setback - Water Bodies | 25 | feet | Setback table: "Surface Water (e.g., ponds, lakes, reservoirs, streams, brooks, flood plains and seasonal drainage channels) — 25." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Minimum Well Depth | 20 | feet | Table under 8.20.390(F): "MINIMUM DEPTH OF SEAL BELOW GROUND SURFACE" lists "Vertical geothermal exchange wells — 20." Section 8.20.390(D) also states that if a well is approved within twenty-five (25) feet of a water course, "the annular seal must extend below the bed of the water way for the applicable depth or at least ten (10) feet into an impervious, bedrock layer, whichever is deeper." | 8.20.390 Annular seal | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Permit |  |  | "No person ... shall commence to dig, bore or drill a new well or to deepen, seal, perforate, re-perforate, abandon or destroy, or otherwise commence work on a well in Calaveras County without first having received a permit to do such work." The chapter purpose expressly includes "geothermal heat exchange wells," so this enacted well-permit requirement applies to geothermal heat exchange wells covered by the chapter. | 8.20.050 Permit required | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Inspection |  |  | "The Director, at a minimum, shall conduct the following prescribed inspections: 1. Initial well site inspection; 2. Annular seal inspection; 3. Final well inspection, and 4. Well destruction inspections when required." Also: "Prior to sealing the annular space, the well contractor shall notify the Director and schedule an inspection of the sealing process... No annular seal shall be installed until permission to proceed is given by the Director." | 8.20.590 Inspections | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Licensed Driller |  |  | "No person shall undertake to dig, bore or drill any well, including but not limited to ... geothermal heat exchange well ... unless the person responsible for that construction, alteration, destruction, or abandonment possesses a C-57 Water Well Drilling Contractor license." | 8.20.040 License required | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Certification |  |  | 8.20.040(A): "No person shall undertake to dig, bore or drill any well, including but not limited to ... geothermal heat exchange well ... unless the person responsible for that construction, alteration, destruction, or abandonment possesses a C-57 Water Well Drilling Contractor license." 8.20.030(12): "'C-57 licensed Water Well Drilling Contractor' means any person or company licensed under authority of the State Contractors License Law..." | 8.20.040 License required; 8.20.030 Definitions | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras |  | County | 6009 | Decommissioning |  |  | 8.20.540: "When a well no longer functions as originally designed... or is found or declared to be abandoned, it must be destroyed by a well contractor, under a well permit issued by the Director." 8.20.550 sets destruction requirements, including: "The well shall be filled... from the bottom of the well to a level that is no deeper than twenty-five (25) feet below the ground surface" and "At least twenty (20) feet of sealing material... shall be placed on top of the fill material." | 8.20.540 Mandatory destruction of wells; 8.20.550 Sealing requirements for the destruction of wells | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Lake |  | County | 6033 | Maximum Well Depth | 3000 | feet | "The drilling of new geothermal direct use well(s) shall not exceed three thousand (3,000) feet in depth. Wells exceeding two thousand (2,000) feet in depth shall require a major use permit." | (p) Geo-direct use well project | 2020 | https://www.lakecountyca.gov/DocumentCenter/View/12781/Article-27---Uses-Generally-Permitted-PDF
California | Lake |  | County | 6033 | Permit |  |  | "Wells exceeding two thousand (2,000) feet in depth shall require a major use permit." "Geothermal direct use wells proposed in conjunction with a project requiring a use permit or specific plan of development approval shall be processed with the larger project." "Geothermal direct use wells with over one thousand (1,000) feet of new road construction or located within five hundred (500) feet of a dwelling or three hundred (300) feet of a lake, perennial or seasonal creek shall require a major use permit." "A geothermal direct use well project with three (3) or more wells shall require a major use permit." "Only geothermal direct use wells utilizing downhole heat exchangers may be processed by a minor use permit. All geothermal direct use wells which remove geothermal fluids from the well bore shall require a major use permit." | (p) Geo-direct use well project | 2020 | https://www.lakecountyca.gov/DocumentCenter/View/12781/Article-27---Uses-Generally-Permitted-PDF
California | Lassen |  | County | 6035 | Permit |  |  | The ordinance establishes explicit geothermal permitting under Water Well Management: "Application: Monitoring, Test or Boring, Geothermal Well/Heat Exchange — 170.00 — Per well. Does not include permit to construct or construction inspection" and "Permit to Construct: Geothermal Well/Heat Exchange — 335.00 — Per well." It also includes related permit administration entries: "Permit Extension — 170.00 — Prior to expiration. Per permit," "Reinstatement of Expired Permit — 254.00 — Per permit," and "Drilling without a Permit or Inspection of Unpermitted Well — 254.00 — In addition to application, permit and inspection fees." | 3.18.120 Environmental health fees; s) Water Well Management | 2024 | https://ecode360.com/LA4955/laws/LF2151481.pdf
California | Lassen |  | County | 6035 | Inspection |  |  | The ordinance expressly provides for geothermal-related inspections by fee schedule reference: "Application: Monitoring, Test or Boring, Geothermal Well/Heat Exchange — 170.00 — Per well. Does not include permit to construct or construction inspection" and "Drilling without a Permit or Inspection of Unpermitted Well — 254.00 — In addition to application, permit and inspection fees." | 3.18.120 Environmental health fees; s) Water Well Management | 2024 | https://ecode360.com/LA4955/laws/LF2151481.pdf
California | Riverside |  | County | 6065 | Definition: Well |  |  | "Geothermal Heat Exchange Well" shall mean any uncased excavation by any method for the purpose of using the heat exchange capacity of the earth for heating and cooling and in which the ambient ground temperature is 86° Fahrenheit (30° Celsius) or less and which uses a closed loop fluid system to prevent the discharge or escape of its fluid into the surrounding aquifers or geologic formations. Geothermal Heat Exchange Wells are also know[n] as ground source heat pump wells (California Water Code 13713). Such wells or boreholes are not intended to produce water or steam. | Section 2.L | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside |  | County | 6065 | Permit |  |  | Section 3.A: "No person or entity... shall dig, drill, bore, drive, reconstruct or destroy... (4) geothermal heat exchange well, without first filing a written application to do so with the Department, and receiving and retaining a valid permit as provided herein." Section 3.D: "An application for a permit to construct a... geothermal heat exchange well shall be submitted to the Department on a form and in a manner prescribed by the Department." | Section 3.A; Section 3.D | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside |  | County | 6065 | Inspection |  |  | Section 13 requires inspections for certain wells and destruction activities: "A well inspection shall be requested of the Department at least two (2) working days in advance" of specified activities, including "For well and boring destruction: a. During the actual sealing of the well, b. Immediately after all well destruction work has been completed." Section 13.C adds: "If the enforcement agency fails to appear at the well site within 30 minutes of the scheduled time designated for sealing, the well may be sealed without the presence of the enforcement agency." | Section 13 | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside |  | County | 6065 | Certification |  |  | Section 3.D.2 requires permit applications to include "The C-57 license number and signature of the person responsible for constructing the well." Section 9 states: "No persons shall engage in any activity listed in Section 3. of this ordinance unless he is... in compliance with the Provisions herein and possesses a valid C57 license in accordance with the California Contractor's State License Law... or possesses a license appropriate to the activity to be engaged in." | Section 3.D.2; Section 9 | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside |  | County | 6065 | Decommissioning |  |  | Section 10 states that standards for "abandonment, or destruction of wells" are those in incorporated state bulletins. Section 22 provides: "If after thirty (30) days of abandonment, the owner has not declared to the Department a proposed reuse of the well per Section 24... and the well has been found by the Department to be a hazard... the Department shall direct the owner to destroy the well, in accordance with Section 10. of this ordinance." It further states: "Upon removal of the pump, the casing shall be provided with a threaded or equivalently secured watertight cap. The well shall be maintained so that it will not be a hazard to public health and safety until such time as it is properly destroyed." Section 24 allows an owner to file a "Declaration of Proposed Reuse" and seek an exemption from destruction requirements. | Section 10; Section 22; Section 24 | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | San Diego |  | County | 6073 | Definition: Well |  |  | "WELL. Any artificial excavation constructed by any method for the purpose of extracting water from or injecting water into the underground, for providing cathodic protection or electrical grounding of equipment, for making tests or observations of ground water conditions, for using the heat exchange capacity of the earth for heating and cooling, or for any other similar purpose. Wells shall include, but shall not be limited to, community water supply wells, individual domestic wells, commercial wells, industrial wells, agricultural wells, monitoring wells and salt water (hydraulic) barrier wells, as defined herein, geothermal heat exchange wells and other wells whose regulation is necessary to accomplish the purposes of this chapter." | SEC. 67.402. DEFINITIONS AS USED IN THIS CHAPTER. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Diego |  | County | 6073 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT EXCHANGE WELL. Any uncased artificial excavation, by any method, that uses the heat exchange capacity of the earth for heating and cooling, in which excavation the ambient ground temperature is 30 degrees Celsius (86 degrees Fahrenheit) or less, and which excavation uses a closed loop fluid system to prevent the discharge or escape of its fluid into surrounding aquifers or other geologic formations. Geothermal heat exchange wells include ground source heat pump wells. Such wells or boreholes are not intended to produce water or steam." | SEC. 67.402. DEFINITIONS AS USED IN THIS CHAPTER. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Diego |  | County | 6073 | Permit |  |  | "Applications for permits shall be made to the Director" and must include "a plot plan showing the location of the well and related piping" with listed surrounding features, "the proposed minimum and the proposed maximum depth of the well," "the proposed use of the well," and other specified information. "Each application shall be accompanied by a fee..." and "Permits may also include any other condition or requirement found by the Director to be necessary to accomplish the purposes of this Chapter." Section 67.423a separately provides: "Standards for the construction, repair, reconstruction or destruction of geothermal heat exchange wells shall be as set forth in the Geothermal Heat Exchange Well Draft Well Standards..." | SEC. 67.441. PERMITS. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Diego |  | County | 6073 | Inspection |  |  | "The permittee shall notify the Director in writing upon completion of the work and submit a copy of the well drilling log... A final inspection of the work shall be made by the Director unless such inspection is waived by him, and no permittee shall be deemed to have complied with this Chapter or his permit until such inspection has been performed or waived." | SEC. 67.441. PERMITS. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Mateo |  | County | 6081 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat exchange well" means any artificial excavation by any method for the purpose of using the heat exchange capacity of the earth for heating and/or cooling and in which the ambient ground temperature is 86 degrees Fahrenheit or less and which uses a closed loop fluid system to prevent the discharge or escape of its fluid into the surrounding aquifers or geologic formations. Geothermal heat exchange wells are also known as ground source heat pump wells. Such wells or boreholes are not intended to produce water or steam. | 4.68.020(i) Definitions | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo |  | County | 6081 | Permit |  |  | "No Person shall dig, bore, deepen, reperforate, excavate, construct, reconstruct, inactivate, convert, destroy or repair any water well, geothermal heat exchange well or cathodic protection well, without first having applied for and obtained a Permit for such activity from the County Health Officer pursuant to the provisions of this chapter. A Permit granted pursuant to this chapter is valid only for the proposed activity listed on the Permit application and solely for the site specified therein." | 4.68.080 Permit for the construction, destruction, inactivation, repair or conversion of a water well, geothermal heat exchange well or cathodic protection well | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo |  | County | 6081 | Inspection |  |  | Section 4.68.070 provides that "Permit fees shall be charged for each Permit to cover the cost of inspection and enforcement pursuant to this chapter." Section 4.68.090 requires a geothermal well permit to "be kept available for inspection at the well site during the course of and until completion" of the work. Section 4.68.280 states: "As a condition for the issuance of a Permit under this chapter, the permittee shall allow the County Health Officer or an authorized representative to enter the property where the well is located, upon reasonable notice ... to investigate, examine and test the well and well site." | 4.68.070 Fees; 4.68.090 Placement of Permit on job site; 4.68.280 Right of inspection | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo |  | County | 6081 | Licensed Driller |  |  | "Any construction, reconstruction, repair, destruction or conversion of a water well, geothermal heat exchange or cathodic protection well shall be undertaken by a well-driller who possesses a C-57 Water Well Contractor's License as provided by state licensing law." | 4.68.040 Well-driller | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo |  | County | 6081 | Certification |  |  | "Any construction, reconstruction, repair, destruction or conversion of a water well, geothermal heat exchange or cathodic protection well shall be undertaken by a well-driller who possesses a C-57 Water Well Contractor's License as provided by state licensing law." | 4.68.040 Well-driller | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo |  | County | 6081 | Decommissioning |  |  | Section 4.68.050 requires: "Upon completion of the construction, destruction or conversion of the well, the site shall be restored as near as possible to its original condition, and appropriate erosion control measures shall be implemented. Site restoration is the responsibility of the property owner and must be implemented within 60 days of the completion of the well, and not more than a year from the date of the Permit issuance." Section 4.68.410 states: "It is unlawful to maintain an abandoned well. Any Person owning property upon which an abandoned well is located shall obtain a Permit to destroy or inactivate the well." | 4.68.050 Mitigation of disturbance at well site; 4.68.410 Abandoned wells | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | Sonoma |  | County | 6097 | Definition: Geothermal Heat Pump |  |  | "Accessory renewable energy system: An on-site renewable energy system, including but not limited to wind, bioenergy, solar, low-temperature geothermal heating systems, geothermal heat pump systems, and fuel cells and combinations thereof, where the energy generated is used primarily to meet the energy demands of the lawful use on the property where the system is located." | Section 26-02-140, Definitions | 2013 | https://sonomacounty.gov/administrative-support-and-fiscal-services/county-administrators-office/ordinance-6046
California |  | Emeryville | City | 622594 | Definition: Geothermal Heat Pump |  |  | "ELECTRIC HEATING APPLIANCE. A device that produces heat energy to create a warm environment by the application of electric power to resistance elements, refrigerant compressors, or dissimilar material junctions, as defined in the California Mechanical Code." | Section 202: Definitions | 2022 | https://www.emeryville.org/files/assets/city/v/1/development/documents/building-permits/repealing-and-replacing-buidling-regulations.pdf
California |  | Emeryville | City | 622594 | Permit |  |  | Where combustion equipment is allowed, "the construction drawings shall indicate electrical infrastructure and physical space accommodating the future installation of an electrical heating appliance ... as certified by a registered design professional or licensed electrical contractor." The ordinance also states that all-electric requirements apply to "new construction buildings and qualifying alteration projects" under Sections 4.106.5 and 5.106. | Section 5.106.13.2 Requirements for combustion equipment; Section 4.106.5.2 Requirements for combustion equipment | 2022 | https://www.emeryville.org/files/assets/city/v/1/development/documents/building-permits/repealing-and-replacing-buidling-regulations.pdf
California |  | Huntington Beach | City | 636000 | Permit |  |  | "the Uniform Solar, Hydronics and Geothermal Code... 2021 Edition" is adopted by reference, and the chapter states it is adopted "for the purpose of protecting public health and safety by prescribing minimum standards for the use, design and installation of solar energy systems; by requiring a permit and inspection for installation, alteration and replacement of said equipment." It further states: "From the date on which this chapter takes effect, the provisions thereof shall be controlling within the corporate limits of the City of Huntington Beach." | § 17.60.010 Adoption. | 2025 | https://ecode360.com/43801882
California |  | Huntington Beach | City | 636000 | Inspection |  |  | "the Uniform Solar, Hydronics and Geothermal Code... 2021 Edition" is adopted by reference, and the chapter states it is adopted "for the purpose of protecting public health and safety by prescribing minimum standards for the use, design and installation of solar energy systems; by requiring a permit and inspection for installation, alteration and replacement of said equipment." It further states: "From the date on which this chapter takes effect, the provisions thereof shall be controlling within the corporate limits of the City of Huntington Beach." | § 17.60.010 Adoption. | 2025 | https://ecode360.com/43801882
California |  | Palo Alto | City | 655282 | Inspection |  |  | 'Alterations which install new or replacement heat pumps shall meet the applicable requirements of subsections i, ii, iii, and v.' Subsection ii requires that minimum airflow rate be 'confirmed through field verification and diagnostic testing' and refrigerant charge be verified by either: 'The installer and rater shall perform the standard charge verification procedure as specified in Reference Residential Appendix Section RA3.2.2' or 'The ECC-Rater shall verify the charge using RA3.2.2 and RA3.3.' Subsection iii similarly requires weigh-in charging 'as verified by an ECC-Rater according to the procedures specified in Reference Residential Appendix RA3.2.3.2.' | 16.17.140 Section 150.2(b)1.F | 2025 | https://www.paloalto.gov/files/assets/public/v/1/development-services/building-division/adoptive-ordinances/2025-edition/urgent_ord_5665-cenc-1.pdf
California |  | Piedmont | City | 656938 | Noise Limits | 50 | dBA | 'Machines and other devices located on the exterior of structures which generate sounds perceptible outside the perimeters of the lot on which they are located must be installed with sound transmission control measures to adequately minimize or eliminate the transmission of the sound to a level not to exceed 50 decibels, A-weighted, at the nearest property line to the source.' The section adds that it 'includes, but is not limited to, pool and spa filter systems, air conditioning units, heat pumps, generators, and exterior mounted blowers for exhaust systems.' | 8.02.020 CC. Appendix BG, Section BG105 - Mechanically Generated Noise Sources | 2026 | https://piedmont.ca.gov/common/pages/GetFile.ashx?key=r0lBARG3
California |  | Piedmont | City | 656938 | Permit |  |  | For qualifying single-family additions or alterations, the ordinance states: 'An alteration of or addition to a single family building, with a stated project value of $35,000 or more, is required to submit documentation that one item from the following list of Energy Efficiency and Electrification measures is included in the scope of work...' The list includes: '*Replace fuel gas furnace with an electric heat pump system meeting the Requirements of the 2025 California Energy Code Section 150.2(b)C...' and another measure may be implemented if it 'is submitted with the application for a building permit.' | 8.02.070 E. Section 150.2(d) - Single Family Additions or Alterations | 2026 | https://piedmont.ca.gov/common/pages/GetFile.ashx?key=r0lBARG3
California | San Bernardino | San Bernardino | City | 665000 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL FACILITY. Any space or process, heating or cooling apparatus or system used to pump, convey or transport geothermal resources or thermal ground water, including, but not limited to, ground water heat pumps, fluid heat exchangers, well and circulating pumps, pipelines, valves, fittings or controls." | § 13.20.115 GEOTHERMAL FACILITY. | 1983 | https://codelibrary.amlegal.com/codes/sanbernardinoca/latest/sanbernardino_ca/0-0-0-14939
California | Santa Cruz | Santa Cruz | City | 669112 | Permit |  |  | "The chief building official shall charge and receive such fees for services, inspections, and permits relating to any work subject to this chapter..." Section 3 states: "This ordinance shall take effect and be in full force thirty (30) days after final adoption." | 18.15.050 PERMIT FEES | 2023 | https://www.santacruzca.gov/files/assets/city/v/1/pl/documents/green-building-program/ordinance-202312-energy-reach-code.pdf
California | Santa Cruz | Santa Cruz | City | 669112 | Inspection |  |  | "The chief building official shall charge and receive such fees for services, inspections, and permits relating to any work subject to this chapter..." | 18.15.050 PERMIT FEES | 2023 | https://www.santacruzca.gov/files/assets/city/v/1/pl/documents/green-building-program/ordinance-202312-energy-reach-code.pdf
California |  | South Gate | City | 673080 | Permit |  |  | "9.13.010 Adoption by Reference to the Uniform Solar, Hydronics and Geothermal Code. Except as provided herein, the 2024 Edition of the Uniform Solar, Hydronics and Geothermal Code ... is hereby adopted by reference as though fully set forth herein"; and "The Building Official shall not issue a permit pursuant to the Building Code unless he or she determines an applicant and a property owner have first complied with all regulations in Title 9, and with all other provisions of the South Gate Municipal Code ... that pertain to the work and/or installations for which a permit is sought." | Section 13, 9.13.010 Adoption by Reference to the Uniform Solar, Hydronics and Geothermal Code; Section 2, [A]105.8 Permit Issuance - Additional Prerequisites | 2026 | https://ecode360.com/SO4650/laws/LF2686687.pdf
California |  | South Gate | City | 673080 | Inspection |  |  | "The final inspection shall be made after all work required by the building permit is completed. All work and installations that are authorized by the building permit shall not become lawful until a permit holder has obtained a final inspection approval from the Building and Safety Division, which shall be in writing." Also, "Construction, work, or installations occurring in connection with a permit that do not remain visible and accessible for an inspection ... are unlawful" and noncompliant work is subject to a correction notice "following an inspection." | Section 2, 110.3.12 Final inspection; [A]110.7 Concealed and/or Inaccessible Construction; [A]110.8 Corrections | 2026 | https://ecode360.com/SO4650/laws/LF2686687.pdf
California | Lassen | Susanville | City | 677364 | Definition: Well |  |  | "Well" means "any artificial opening or artificially altered natural opening, however made, by which geothermal fluids or thermal groundwater is sought or through which geothermal fluids or thermal groundwater flows under natural pressure or is artificially withdrawn, or is used to operate a heat exchanger within the well, provided that this definition shall not include a natural spring." | § 13.12.030 Definitions |  | https://ecode360.com/44217318
California | Lassen | Susanville | City | 677364 | Definition: Geothermal Heat Pump |  |  | "Geothermal facility" means "any space or process heating or cooling apparatus or system used to pump, convey or transport geothermal resources or thermal groundwater, including, but not limited to, groundwater heat pumps, fluid heat exchangers, well and circulating pumps, pipelines, valves, fittings or controls." | § 13.12.030 Definitions |  | https://ecode360.com/44217318
California |  | Wildomar | City | 685446 | Definition: Well |  |  | "Geothermal heat exchange well" means "any uncased excavation by any method for the purpose of using the heat exchange capacity of the earth for heating and cooling and in which the ambient ground temperature is 86° Fahrenheit (30° Celsius) or less and which uses a closed loop fluid system to prevent the discharge or escape of its fluid into the surrounding aquifers or geologic formations. Geothermal heat exchange wells are also known as ground source heat pump wells (California Water Code Section 13713). Such wells or boreholes are not intended to produce water or steam." | § 13.20.020 Definitions | 2008 | https://ecode360.com/43471046
California |  | Wildomar | City | 685446 | Permit |  |  | "No person or entity... shall dig, drill, bore, drive, reconstruct or destroy... (4) geothermal heat exchange well, without first filing a written application to do so with the Department, and receiving and retaining a valid permit as provided in this chapter." The section also states: "An application for a permit to construct a... geothermal heat exchange well shall be submitted to the Department" and lists required application contents. | § 13.20.030 Permit requirements | 2008 | https://ecode360.com/43471046
California |  | Wildomar | City | 685446 | Inspection |  |  | "A well inspection shall be requested of the Department at least two working days in advance of" specified activities, including for "all wells" any "special inspection" required by permit and for "well and boring destruction" both "[d]uring the actual sealing of the well" and "[i]mmediately after all well destruction work has been completed." | § 13.20.130 Required inspection of wells | 2008 | https://ecode360.com/43471046
California |  | Wildomar | City | 685446 | Certification |  |  | The geothermal permit application must include "[t]he C-57 license number and signature of the person responsible for constructing the well." Separately, "No persons shall engage in any activity listed in Section 13.20.030 unless he or she... possesses a valid C-57 license in accordance with the California Contractor's State License Law... or possesses a license appropriate to the activity to be engaged in." | § 13.20.030 Permit requirements; § 13.20.090 Licensing and registration of water well drillers and contractors | 2008 | https://ecode360.com/43471046
California |  | Wildomar | City | 685446 | Decommissioning |  |  | "If after 30 days of abandonment, the owner has not declared to the Department a proposed reuse of the well... and the well has been found by the Department to be a hazard... the Department shall direct the owner to destroy the well, in accordance with Section 13.20.100." Also, "Upon removal of the pump, the casing shall be provided with a threaded or equivalently secured watertight cap. The well shall be maintained so that it will not be a hazard to public health and safety until such time as it is properly destroyed." In addition, "As a condition of a construction or reconstruction permit, any abandoned wells on the property shall be destroyed in accordance with standards provided in this chapter." | § 13.20.220 Well abandonment; § 13.20.030(E) | 2008 | https://ecode360.com/43471046
Colorado | Boulder |  | County | 8013 | Definition: Geothermal Heat Pump |  |  | 'Renewable Energy Systems' means: 'Any renewable energy systems which meet the intent of the required on-site renewable energy offset required by other Sections of this code, including solar thermal systems, solar photovoltaic electric systems, geothermal heating systems, wood and pellet burning stoves, boilers, or furnaces, small scale wind generation systems, and other similar systems.' | N1101.3.1 Definitions | 2013 | https://bouldercounty.gov/wp-content/uploads/2017/03/buildsmart-code-2012.pdf
Colorado | Larimer |  | County | 8069 | Permit |  |  | "Any owner or owner's authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any electrical, gas, mechanical or plumbing system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." | R105.1 Required | 2022 | https://www.larimer.org/sites/default/files/uploads/2022/2021_irc_amendments_final_1.pdf
Colorado | Larimer |  | County | 8069 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to or concurrent with framing inspection. Exception: Backfilling of ground-source heat pump loop systems tested in accordance with Section M2105.28 prior to inspection shall be permitted." | R109.1.2 Plumbing, mechanical, gas and electrical systems inspection | 2022 | https://www.larimer.org/sites/default/files/uploads/2022/2021_irc_amendments_final_1.pdf
Colorado | Pitkin |  | County | 8097 | Permit |  |  | "Compliance with this section will be documented via the free Public Domain tool 'Pitkin County REMP Calculation Sheet' in the most current version at the time of permit application." Also, exterior energy uses "may be installed only if the supplemental energy meets the requirements of Appendix A. This applies to all installations for which an application for a permit or renewal of an existing permit is filed or is by law required to be filed with or without an associated Building Permit." | APPENDIX A: Section 101.1 Scope / Section 101.1.2 Exterior Energy Uses | 2024 | https://pitkincounty.com/DocumentCenter/View/32667/boccord0042024
Colorado | Pitkin |  | County | 8097 | Inspection |  |  | "Each ground source heat pump system shall be tested and balanced and commissioned in accordance with C408." | APPENDIX A: Section 106 Ground Source Heat Pump (GSHP) | 2024 | https://pitkincounty.com/DocumentCenter/View/32667/boccord0042024
Colorado | Pitkin |  | County | 8097 | Certification |  |  | "The design engineer shall certify in writing that it meets or exceeds the design coefficient of performance (COP) as specified in the 'Pitkin County REMP Calculation Sheet'. The ground loop system must be designed by a CGD (Certified Geo Exchange Designer certified by the Association of Energy Engineers) or a Professional Engineer licensed in the State of Colorado or an IGSHPA (International Ground Source Heat Pump Association) certified designer. The mechanical system must be installed by a certified IGSHPA contractor." | APPENDIX A: Section 106 Ground Source Heat Pump (GSHP) | 2024 | https://pitkincounty.com/DocumentCenter/View/32667/boccord0042024
Colorado |  | Carbondale | Town | 812045 | Definition: Geothermal |  |  | Table C409.1.2.3.1 lists "Geothermal energy" as an energy source with a threshold of "> 1,000,000 Btu/h (300 kW) heating" for required measurement devices. | Table C409.1.2.3.1 ENERGY SOURCE THRESHOLDS | 2025 | https://carbondalegov.community.diligentoneplatform.com/document/c1af4225-b3f7-4809-a65b-210bd4c9d9d3/
Colorado | Montezuma | Dolores | Town | 820770 | Definition: Well |  |  | "Geothermal boreholes: A hole drilled or bored into the earth into which piping is inserted for use a closed vertical loop geothermal system." | Section 2.6. - General definitions | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." Also defined are "Ground source heat pump system, closed loop," "Ground source heat pump system, horizontal," "Ground source heat pump system, open loop," and "Ground source heat pump system, vertical." | Section 2.6. - General definitions | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems including pumps, borings, and loops shall be setback at least five feet from all property lines." | Section 4.5.G.1.c(3)(i) - Setbacks | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Setback - Public Water | 25 | feet | "All parts of the heat pump system shall be located a minimum distance of 25 feet from any on-lot or adjacent lot wells." | Section 4.5.G.1.c(3)(iii) - Setbacks | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Maximum Well Depth | 20 | feet | "Depth: All horizontal closed loop systems shall be installed to no more than 20 feet in depth." | Section 4.5.G.1.c(2) - Generally Applicable Standards | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Permit |  |  | "Detailed plans of a vertical system shall be reviewed and approved by the zoning administrator prior to installation." | Section 4.5.G.1.b(2) - Installation of Vertical Systems | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Screening |  |  | "Ground source heat pump systems are considered mechanical equipment and are subject to mechanical screening requirements of the zoning district." | Section 4.5.G.1.c(4) - Screening | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Certification |  |  | "Vertical systems may only be installed by a geothermal installer or vertical closed loop (VCL) driller accredited by the International Ground Source Heat Pump Association (IGSHPA) or installer with an equivalent accreditation or certification from a nationally recognized organization, as determined by the zoning administrator." | Section 4.5.G.1.b(1) - Installation of Vertical Systems | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The property owner shall shut down the system as follows: (1) The heat pump and any external mechanical equipment shall be removed. (2) Pipes or coils beneath the land surface shall be drained and filled with grout. The top of the pipe, coil, or boring shall be uncovered and grouted." | Section 4.5.G.1.d - Abandonment | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | Town | 820770 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids are permitted. Open loop ground source heat systems are prohibited." | Section 4.5.G.1.c(1)(i) - Generally Applicable Standards | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Garfield | Glenwood Springs | City | 830780 | Screening |  |  | "Ground-mounted mechanical equipment" may "encroach five feet into required side and rear yards provided no element is located closer than two feet from any property line and the equipment complies with screening standards in 070.40.050(f), Screening, Fences, and Walls." | 070.20.190 Measurements and Exceptions (d) Building Height; Table 20.20: Authorized Exceptions to Setback Standards | 2022 | https://www.cogs.us/DocumentCenter/View/3490/New-Development-Code-Adopted-August-2-2018
Colorado | Gunnison | Gunnison | City | 833640 | Definition: Geothermal Heat Pump |  |  | "Geothermal heating and cooling systems are systems that use buried pipes to exchange heat with the ground, cooling buildings in the summer and warming them in the winter." | OTHER USE STANDARDS § C.2. Geothermal Heating and Cooling Systems | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | City | 833640 | Setback - Property Lines | 5 | feet | "Closed loop systems (horizontal loop systems and vertical loop systems) are permitted, provided that the loops are contained entirely within the lot and are setback five feet from property lines." | OTHER USE STANDARDS § C.2.a | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | City | 833640 | Permit |  |  | "Such manifest shall be located at the system and available for inspection and testing by the Public Works Director or designee to ensure the safety of the City's water well systems." | OTHER USE STANDARDS § C.2.e | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | City | 833640 | Inspection |  |  | "Such manifest shall be located at the system and available for inspection and testing by the Public Works Director or designee to ensure the safety of the City's water well systems." | OTHER USE STANDARDS § C.2.e | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | City | 833640 | Open-loop Prohibitions |  |  | "Open loop systems are prohibited. (Ordinance #8, Series 2021)" | OTHER USE STANDARDS § C.2.f | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Archuleta | Pagosa Springs | Town | 856860 | Definition: Geothermal |  |  | "GEOTHERMAL WATER means the means raw geothermal water produced by the Two Wells." and "GEOTHERMALLY HEATED WATER means non-potable fresh water that is heated in a heat exchanger using water directly from geothermal wells and delivered to Customers." | Section 1-02 DEFINITIONS |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | Town | 856860 | Definition: Geothermal Heat Pump |  |  | "GH SYSTEM means the geothermal heating system which is owned and operated by the Town, consisting of all Facilities, improvements and appurtenances, associated with providing raw Geothermal Water or geothermally heated non-potable fresh water for heating purposes." Also: "GEOTHERMAL SERVICE means the ability of a Customer to receive Geothermal Water or Geothermally Heated Water to a Customer Tap for Customer Uses pursuant to these Regulations." | Section 1-02 DEFINITIONS |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | Town | 856860 | Permit |  |  | "Any Customer desiring to contract to receive Geothermal Water or Geothermally Heated Water for Customer Uses may apply for a Geothermal Water Tap with the Geothermal Department." The Director "shall approve or deny said application within thirty (30) days." Also, "It shall be a violation of these regulations for any person to construct or cause the construction of a Service Line or Tap-in without approval of the Department." | Section 1-03 SERVICE CONNECTION PROCEDURES; Section 1-03 G. Violations |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | Town | 856860 | Inspection |  |  | "Upon completion of the permitted Customer Tap, and prior to covering the Tap-in and any in-ground Facilities, the Customer shall promptly notify the Department to request a service connection inspection." "Upon inspection by the Geothermal Department, Customers may be required to perform additional work... if... the initial Tap-in work and Customer Facilities fail to comply..." "All requests for inspection must be made to the Department at least twenty-four (24) hours in advance." If a customer connects without the Department "first inspecting and approving the construction and Tap-in," the customer must excavate and disconnect so "a proper inspection can be made." | Section 1-03 F. Service Connection Standards and Inspections; Section 1-03 H. Inspection; Section 1-03 I. Failure to Apply or Inspect |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | Town | 856860 | Other Prohibitions/Regulations |  |  | "Glycol circulated in Pex piping shall be used in all sidewalk, driveway and parking area heating systems. Such systems shall include a heat exchanger and closed loop system..." | Section 1-03.2 Heating of Sidewalks/Driveways/Parking Areas |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado |  | Ridgway | Town | 864200 | Permit |  |  | The ordinance imposes permit requirements on mechanical work that would encompass heat pump installation: IMC amendment §106.5.1 states, "Any person who commences any work on a building, structure, electrical, gas, mechanical or plumbing system before obtaining the necessary permits shall be subject to a fee..." and IMC amendment §106.5.2 provides, "The fees for mechanical work, or alterations requiring a permit, shall be derived using Appendix ABL of 202418 International Residential Code." Parallel permit language appears in IRC §R108.6 and IBC §109.2 for work on "mechanical" systems. | Exhibit B, 6-1-3(CD)(3); 6-1-3(CD)(4); 6-1-3(B)(8); 6-1-3(A)(10) | 2026 | https://townofridgway.colorado.gov/sites/g/files/lrnvjt1246/files/documents/Ordinance-No.-03-2026.pdf
Colorado |  | Ridgway | Town | 864200 | Inspection |  |  | IBC amendment §110.5 reads: "It shall be the duty of the holder of the building permit or their duly authorized agent to notify the Building Official when work is ready for inspection. It shall be the duty of the permit holder to provide access to and means for inspections of such work that are required by this code. Inspection requests shall be made a minimum of forty-eight (48) twenty-four hours in advance." In addition, §6-1-2(B) authorizes entry "to inspect or enforce the provisions of this Section and any of the codes adopted herein by reference." | Exhibit B, 6-1-3(A)(156); 6-1-2(B) | 2026 | https://townofridgway.colorado.gov/sites/g/files/lrnvjt1246/files/documents/Ordinance-No.-03-2026.pdf
Colorado |  | Superior | Town | 875640 | Permit |  |  | "Applicable permit fees for the installation of a renewable energy source system, such as solar electric, wind or geothermal, shall be exempt from Town permit fees." | Sec. 18-14-90. - Permit fee. | 2022 | https://townofsuperior.granicus.com/MetaViewer.php?view_id=4&clip_id=2058&meta_id=98287
Connecticut | Capitol | Coventry | Town | 911017800 | Definition: Geothermal |  |  | "Passive Geothermal : A dwelling specifically designed to use natural and architectural components to collect and store the heat of the earth's interior without using any external mechanical power." | Section 2.02 Definitions | 2026 | https://www.coventry-ct.gov/DocumentCenter/View/9347/FINAL-3-28-25-ZONING-REGULATIONS
Connecticut | Capitol | East Windsor | Town | 911024800 | Screening |  |  | "All parking areas not contained within structures shall be appropriately screened and landscaped." | 802.17 PARKING AND ACCESS DRIVES | 2025 | https://portal.ct.gov/-/media/csc/1_dockets-medialibrary/1_media_do500_600/do547/applicantsubmissions/application/2-town-of-east-windsor-zoning-regulations.pdf?rev=590dadec2f244e76b43acc59a0a6f738&hash=8CC873552D0629FDC31B646F4DCE3008
Connecticut | Capitol | Granby | Town | 911032640 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: An energy system that utilizes the production of energy from underneath the earth's surface to generate heating and cooling for buildings through the use of ground source heat pumps and underground closed loop piping systems." | Section 1.4 Definitions | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | Town | 911032640 | Setback - Property Lines | 10 | feet | "All system components, including pumps, borings, tanks, and loops shall be setback at least 10 feet from all property lines." | Section 8.29.2.2 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | Town | 911032640 | Permit |  |  | Section 8.29.2.6 states: "A plot plan showing the proposed system, system specifications, and other information as required by the Building Official, shall be submitted with the Building Permit." Section 10.2.1.1 further provides: "It shall be unlawful to commence, for any purpose, the construction or alteration of any building or excavation for any building or structure or to commence any use of land or buildings until the application and plans thereof shall have been approved by the Building Official and a written permit shall have been issued by the Building Official." | Section 8.29.2.6; Section 10.2.1.1 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | Town | 911032640 | Screening |  |  | "Above-ground equipment is considered mechanical equipment and is subject to mechanical screening requirements of the zoning district." | Section 8.29.2.4 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | Town | 911032640 | Decommissioning |  |  | "All unused systems shall be removed within twelve (12) months of cessation of operations." | Section 8.29.2.5 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | West Hartford | Town | 911082590 | Definition: Geothermal Heat Pump |  |  | "A mechanism for using ground source heat pumps for heating and/or cooling a building which consists of a length of closed underground piping (which may be installed horizontally or vertically) containing heat transfer fluid; a heat exchange mechanism; and an air distribution system. This definition is expressly intended to exclude any form of open loop geothermal system." | § 177-37.3 Alternative energy systems — Definitions | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | West Hartford | Town | 911082590 | Maximum Well Depth | 20 | feet | "Horizontal closed loop systems shall be no more than 20 feet deep." | § 177-37.3 Alternative energy systems — Closed loop geothermal systems | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | West Hartford | Town | 911082590 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." | § 177-37.3 Alternative energy systems — Closed loop geothermal systems | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | West Hartford | Town | 911082590 | Open-loop Prohibitions |  |  | "Open loop geothermal systems are prohibited in all zones." | § 177-37.3 Alternative energy systems — Prohibited equipment | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | Windsor | Town | 911087000 | Permit |  |  | "No geothermal system shall be installed or modified without first obtaining a Building Permit." Also, "Geothermal systems utilizing surface waters, wells, or trenches in an area regulated by the Floodplain Ordinance or the Inland Wetlands and Watercourses Commission (IWWC) shall not be installed without a Floodplain Permit or an Inland Wetlands and Watercourses Permit, respectively." | Section 14.1 - Geothermal Energy Facilities, General Requirements | 2022 | https://www.windsorct.gov/DocumentCenter/View/1374/Latest-Annotated-Zoning-Regulations-11-09-22-PDF
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System. An energy system that utilizes the production of energy from underneath the Earth’s surface to generate heating and cooling for buildings through the use of ground source heat pumps and underground closed loop piping systems." | Section 2.2 Defined Terms | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Permit |  |  | Section 5.1.B.2 states geothermal systems are allowed and that permitting applies as follows: "Permitted without a Zoning Permit... b. All Closed-Loop Geothermal Energy Systems in all zones." Section 5.1.B.5 adds: "An approval under this Section does not relieve any person of the requirement to obtain other necessary permit approvals if applicable," including wetland, floodplain, or other regulated activities. | Section 5.1.B.2-5 Renewable Energy System Structures | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Inspection |  |  | No geothermal-specific inspection, witness, pressure test, flow test, or final approval inspection requirement is stated in the provided text. | Section 5.1.B Renewable Energy System Structures | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Screening |  |  | The ordinance allows the Town to require submittals including "an A-2 Survey and project narrative showing detailed information, including maps, plans sheets, or dimensioned sketches, showing the proposed location, including setbacks from property lines, adjacent roadways and sight line studies, distances from structures on neighboring properties, and height." | Section 5.1.B.8 Requirements for All Systems | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards." | Section 5.1.B.11 Requirements for Geothermal Energy Systems | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Decommissioning |  |  | No abandonment, plugging, sealing, removal, or restoration requirement for geothermal systems is stated in the provided text. | Section 5.1.B Renewable Energy System Structures | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | Town | 913018080 | Other Prohibitions/Regulations |  |  | "Only non-toxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | Section 5.1.B.11 Requirements for Geothermal Energy Systems | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Old Saybrook | Town | 913057320 | Permit |  |  | "Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs." Also, "Any person conducting regulated activities that are within the authority of the Commissioner must submit an application or obtain a permit or exemption from the Commissioner prior to engaging in the activity." The definition of "regulated aquifer activity" includes "wastewater discharges to ground water... except discharges from... (iii) a heat pump system" when permitted by the Commissioner. | SECTION 9 Permit Requirements | 2021 | https://www.oldsaybrookct.gov/DocumentCenter/View/977/Aquifer-Protection-Area-Regulations-PDF
Connecticut | Lower Connecticut River Valley | Old Saybrook | Town | 913057320 | Inspection |  |  | "The Agency or its agent may make regular inspections, except at private residences, at reasonable hours, of all regulated activities for which permits or registrations have been issued by these regulations." | SECTION 14 Enforcement | 2021 | https://www.oldsaybrookct.gov/DocumentCenter/View/977/Aquifer-Protection-Area-Regulations-PDF
Connecticut | Naugatuck Valley | Oxford | Town | 914058300 | Permit |  |  | The ordinance includes a heat-pump-specific permit carve-out within the definition of regulated activity: wastewater discharges to groundwater are regulated, except for discharges from a "Heat pump system" that "have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes." It also states generally that "All regulated activities are prohibited in aquifer protection areas, except" a regulated activity that "has received a permit issued pursuant to §22a-354i-8 ... or Section 9 of the APA Regulations." | SECTION 2. DEFINITIONS; SECTION 4. PROHIBITED AND REGULATED ACTIVITIES; SECTION 9. PERMIT REQUIREMENTS | 2010 | https://www.oxford-ct.gov/DocumentCenter/View/329/town_of_oxford_apa_regulations_approved_010908_lsrevised2_18_10
Connecticut | Naugatuck Valley | Oxford | Town | 914058300 | Other Prohibitions/Regulations |  |  | "All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (B) of this section." In the definitions, regulated activities include "Wastewater discharges to ground water other than domestic sewage and stormwater," except for certain permitted systems including a "Heat pump system" that has received a permit from the Commissioner. | SECTION 4. PROHIBITED AND REGULATED ACTIVITIES | 2010 | https://www.oxford-ct.gov/DocumentCenter/View/329/town_of_oxford_apa_regulations_approved_010908_lsrevised2_18_10
Connecticut | Naugatuck Valley | Watertown | Town | 914080490 | Permit |  |  | "Groundwater heat pumps supplying heating and cooling for other than a detached single-family residence" are "only permitted in the APOZ subject to Special Permit approval in accordance with Section 8.4 and Site Plan approval in accordance with Section 8.3," and such systems are allowed only if "restricted to closed-loop types." | Section 4.1.E.22 - Aquifer Protection Overlay Zone, Special Permit Uses | 2024 | https://www.watertownct.org/Documents/Government/Agendas%20and%20Minutes/Planning%20and%20Zoning%20Commission/2026/Minutes/Watertown%20ZR%20-%20Adopted%20-%20Effective%20123024%20CL2.pdf?t=202604100051420
Connecticut | Naugatuck Valley | Watertown | Town | 914080490 | Screening |  |  | Business districts: "Building mechanical equipment located outside the principal structure, including radio and television reception equipment, provided that such equipment shall be properly screened." Industrial districts: "Building mechanical equipment located outside the structure provided that such equipment shall be properly screened." ARH overlay: "Mechanical equipment and refuse containers shall be screened from view on at least three sides and to the satisfaction of the Commission on all sides." DRD overlay: "Mechanical equipment and refuse containers shall be screened from view on at least three sides and to the satisfaction of the Commission on all sides." | Section 2.3 Accessory Uses and Structures; Section 3.3 Accessory Uses And Structures; Section 4.3.F.54; Section 4.5.E.107 | 2024 | https://www.watertownct.org/Documents/Government/Agendas%20and%20Minutes/Planning%20and%20Zoning%20Commission/2026/Minutes/Watertown%20ZR%20-%20Adopted%20-%20Effective%20123024%20CL2.pdf?t=202604100051420
Connecticut | Naugatuck Valley | Watertown | Town | 914080490 | Open-loop Prohibitions |  |  | In the APOZ, "Groundwater heat pumps supplying heating and cooling for other than a detached single-family residence" are allowed only if "restricted to closed-loop types." | Section 4.1.E.22 - Aquifer Protection Overlay Zone, Special Permit Uses | 2024 | https://www.watertownct.org/Documents/Government/Agendas%20and%20Minutes/Planning%20and%20Zoning%20Commission/2026/Minutes/Watertown%20ZR%20-%20Adopted%20-%20Effective%20123024%20CL2.pdf?t=202604100051420
Connecticut | Northeastern Connecticut | Plainfield | Town | 915059980 | Permit |  |  | Section 4(a) states: "All regulated activities are prohibited in aquifer protection areas, except as specified in Subsection (b) of this Section." Section 4(b)(2) then provides that a regulated activity is not prohibited if it "has received a permit issued pursuant to §22a‐354i‐8 of the Regulations of Connecticut State Agencies or Section 9 of the APA Regulations." In the definition of "Regulated activity," Section 2(a)(35)(F) includes "wastewater discharges to ground water other than domestic sewage and stormwater, except for discharges from the following that have received a permit from the Commissioner pursuant to §22a‐430 of the Connecticut General Statutes: ... (iii) heat pump system." | SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2012 | https://www.plainfieldct.org/Document%20Center/Department/Planning%20&%20Zoning/Regulations%20&%20Ordinances/aquiferprotectionregs.pdf?t=202104021433310
Connecticut | Northeastern Connecticut | Plainfield | Town | 915059980 | Inspection |  |  | Section 12(a)(5)(A)(iv) requires "a record‐keeping system" for hazardous materials and states that "such record‐keeping system shall be maintained at the subject facility and shall be made available thereat for inspection during normal business hours by the Commissioner and the municipal aquifer protection agency." Section 12(a)(5)(C) likewise states that "the materials management plan shall be maintained at the subject facility and shall be made available thereat for inspection during normal business hours by the Commissioner and the municipal aquifer protection agency." | SECTION 12. Best Management Practices | 2012 | https://www.plainfieldct.org/Document%20Center/Department/Planning%20&%20Zoning/Regulations%20&%20Ordinances/aquiferprotectionregs.pdf?t=202104021433310
Connecticut | South Central Connecticut | Bethany | Town | 917004580 | Permit |  |  | "Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs." Also, "The Agency shall process permit applications for those registrants that have registered pursuant to section 8 of the APA Regulations..." and under the definition of regulated activity, wastewater discharges from a "heat pump system" are listed as a regulated activity exception only when they "have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes." | SECTION 9. Permit Requirements | 2022 | https://bethanyct.gov/filestorage/216/228/288/3270/TOWN-OF-BETHANY-ZONING-REGULATIONS-EFFECTIVE-_October_10%2C_2022.pdf
Connecticut | South Central Connecticut | Bethany | Town | 917004580 | Inspection |  |  | "The Agency may impose reasonable conditions or limitations on any permit issued under this section to assure protection of the ground water, including, but not limited to... ground water monitoring." Also, materials management plan records "shall be made available thereat for inspection during normal business hours by the Commissioner and the municipal aquifer protection agency." | SECTION 14. Enforcement / SECTION 9. Permit Requirements | 2022 | https://bethanyct.gov/filestorage/216/228/288/3270/TOWN-OF-BETHANY-ZONING-REGULATIONS-EFFECTIVE-_October_10%2C_2022.pdf
Connecticut | South Central Connecticut | Bethany | Town | 917004580 | Other Prohibitions/Regulations |  |  | "All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section." The ordinance definition of "regulated activity" includes wastewater discharges to groundwater, except for discharges from certain systems, including a "heat pump system," that "have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes." | SECTION 4. Prohibited and Regulated Activities | 2022 | https://bethanyct.gov/filestorage/216/228/288/3270/TOWN-OF-BETHANY-ZONING-REGULATIONS-EFFECTIVE-_October_10%2C_2022.pdf
Connecticut | South Central Connecticut | Wallingford | Town | 917078740 | Permit |  |  | "Regulated Activity" includes "wastewater discharges to ground water other than domestic sewage and stormwater, except for discharges from the following that have received a permit issued by the Commissioner pursuant to Section 22a-430 of the Connecticut General Statutes: ... (iii) heat pump system." Section 4 states: "All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section," and subsection (b) allows "a regulated activity which has received a permit issued pursuant to §22a-354i-8 ... or Section 9 of the APA Regulations." Section 9(a) provides: "Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs." | SECTION 2. Definitions; SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2009 | https://www.wallingfordct.gov/customer-content/www/CMS/files//PZAPARegs41615.pdf
Connecticut | Southeastern Connecticut | East Lyme | Town | 918023400 | Permit |  |  | Section 2(a)(35)(F) includes as a regulated activity 'wastewater discharges to ground water other than domestic sewage and storm water, except for discharges from the following that have received a permit from the Commissioner pursuant to §22a-430 of the Connecticut General Statutes: ... (iii) heat pump system ...'. Section 4(a) states: 'All regulated activities are prohibited in aquifer protection areas, except as specified in Subsection (b) of this Section.' Section 4(b)(2) allows 'A regulated activity which has received a permit issued pursuant to §22a-354i-8 of the Regulations of Connecticut State Agencies or Section 9 of the APA Regulations.' Section 9(a) states: 'Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs.' | SECTION 2. Definitions; SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2012 | https://eltownhall.com/wp-content/uploads/Aquifer-Protection-Regulations-effective-December-14-2012.pdf
Connecticut | Southeastern Connecticut | Windham | Town | 918086790 | Inspection |  |  | "the Formal Application under these Regulations shall constitute authorization for the Commission to enter upon the property to obtain additional information or to inspect proposed improvements" and "The Commission may perform an official Site Inspection prior to or during the statutory review period." | Section 4.1.15; Section 4.3.4 | 2014 | https://windhamct.gov/DocumentCenter/View/1768/Subdivision-Regulations-Effective-August-9-2014
Connecticut | Western Connecticut | Greenwich | Town | 919033620 | Permit |  |  | Site plan applications must include "[t]wo copies of a brief narrative addressing ... (B) The potential and use of renewable energy systems, as well as highly energy efficient equipment such as air and ground source heat pumps, hot water heat pumps and fuel cells." | Sec. 6-14(c)(22) | 2023 | https://www.greenwichct.gov/DocumentCenter/View/37847/2023-Building-Zone-Regulations
Connecticut | Western Connecticut | Ridgefield | Town | 919063970 | Definition: Geothermal Heat Pump |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards." | Section 7.16.H - Requirements for Geothermal Energy Systems | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Ridgefield | Town | 919063970 | Permit |  |  | "Permitted (without a Zoning Permit): ... b. All closed-loop geothermal energy systems in all zones." | Section 7.16.D - Permits Required | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Ridgefield | Town | 919063970 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards." | Section 7.16.H - Requirements for Geothermal Energy Systems | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Ridgefield | Town | 919063970 | Open-loop Prohibitions |  |  | Section 7.16.D permits only "All closed-loop geothermal energy systems in all zones" without a zoning permit, and Section 7.16.H regulates "All closed-loop geothermal systems" and requires that "Only non-toxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | Section 7.16.D and 7.16.H | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Sherman | Town | 919068310 | Definition: Geothermal |  |  | "Energy Efficient Designed Dwellings — Dwellings which have been designed to harness wind, sun, and/or geothermal heat sources to provide primary or supplemental energy to such dwelling." | SECTION 610. DEFINITIONS | 2026 | https://municipal-documents.s3.amazonaws.com/uploads/sherman-ct/planning-zoning/documents/regulations/154750/ZONING%20REGULATIONS%20Last%20amended%20May%201%202026.pdf
Connecticut | Western Connecticut | Sherman | Town | 919068310 | Definition: Geothermal Heat Pump |  |  | "Energy Efficient Structures — Wind powered generators, solar panel arrays, geothermal wells and pumps, and other structures which are designed and used to provide primary or supplemental energy as an accessory to a permitted principal use: does not include energy production facilities as a principal use." | SECTION 610. DEFINITIONS | 2026 | https://municipal-documents.s3.amazonaws.com/uploads/sherman-ct/planning-zoning/documents/regulations/154750/ZONING%20REGULATIONS%20Last%20amended%20May%201%202026.pdf
Connecticut | Western Connecticut | Wilton | Town | 919086370 | Permit |  |  | 'Groundwater heat pumps supplying heating and cooling for other than a detached single-family residence' are 'permitted subject to Special Permit and Site Plan approvals in accordance with 29-10 and 29-11,' provided 'such systems shall be designed to treat, if necessary, and return discharged water to the groundwater.' | Section 29-9.D.4.c Special Permit Uses | 2019 | https://www.wiltonct.gov/sites/g/files/vyhlif10026/f/uploads/zoning_regs_revised_jun_25_2019_updated_app_b_0.pdf
Connecticut | Naugatuck Valley | Naugatuck | Borough | 949880 | Permit |  |  | Section 4(a) states: 'All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section.' Section 4(b)(2) then provides an exception for 'a regulated activity which has received a permit issued pursuant to §22a-354i-8 of the Regulations of Connecticut State Agencies or section 9 of the APA Regulations.' In the definition of 'Regulated activity,' Section 2(a)(35)(F) includes 'wastewater discharges to ground water other than domestic sewage and storm water, except for discharges from the following that have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes: ... (iii) heat pump system ...' | SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2006 | https://www.naugatuck-ct.gov/filestorage/166/237/239/Final_Aquifer_Protection_Regulations.pdf
Connecticut | Naugatuck Valley | Naugatuck | Borough | 949880 | Other Prohibitions/Regulations |  |  | Section 4(a) provides: 'All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section.' Section 2(a)(35)(F) defines one regulated activity as 'wastewater discharges to ground water other than domestic sewage and storm water,' while carving out only specified discharges that 'have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes,' including '(iii) heat pump system.' | SECTION 4. Prohibited and Regulated Activities | 2006 | https://www.naugatuck-ct.gov/filestorage/166/237/239/Final_Aquifer_Protection_Regulations.pdf

## State-Level
State | County Subdivision FIPS Code | Feature | Value | Units | Summary | Section | Ordinance Year | Source URL
Massachusetts | 25000 | Definition: Geothermal Heat Pump |  |  | Closed-Loop GSHP System - A GSHO system that utilizes closed-loop well Closed-loop well - A GSHP well that uses a closed-loop fluid system to prevent the discharge or escape of its fluid into the subsurface. Closed-loop heat pump wells shall not be used to produce. Direct exchange (DX) well - A GSHP well that circulates a refrigerant through a closed-loop fluid/vapor system to prevent the discharge or escape of its fluid into the subsurface. DX wells shall not be used to produce water. Direct exchange GSHP systems are also commonly referred to as direct expansion systems. |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts | 25000 | Setback - Property Lines | 10 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts | 25000 | Setback - Private Water | 10 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts | 25000 | Setback - Sewer Lines | 10 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts | 25000 | Setback - Hazardous Materials/Fertilizers | 25 | feet | existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks. |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts | 25000 | Maximum Well Depth | 20 | feet |  |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Massachusetts | 25000 | Licensed Driller |  |  | Must be Mass DEP certified well driller |  | 2013 | https://www.mass.gov/doc/guidelines-for-ground-source-heat-pump-wells/download
Michigan | 26000 | Definition: Geothermal Heat Pump |  |  | Geothermal Heat Pump System - a mechanical device, also known as a ground source heat pump or geoexchange system, which uses the geothermal exchange properties and the relatively constant temperature of earth formations for heating or cooling a building space. A GHPS consists of three parts: 1) heat pump unit, 2) heat exchanger, and 3) heating/cooling distribution system (e.g., duct work). |  | 2013 | https://www.michigan.gov/-/media/Project/Websites/egle/Documents/Programs/DWEHD/Water-Well-Construction/Geothermal-Heat-Pump-Systems.pdf?rev=9af2da6143b84b5a9ca8278362dd67cb
Missouri | 29000 | Setback - Animal Enclosures | 100 | feet |  |  | 2024 | https://www.sos.mo.gov/cmsimages/adrules/csr/current/10csr/10c23-5.pdf
Missouri | 29000 | Setback - Hazardous Materials/Fertilizers | 300 | feet |  |  | 2024 | https://www.sos.mo.gov/cmsimages/adrules/csr/current/10csr/10c23-5.pdf
Missouri | 29000 | Maximum Well Depth | 500 | feet |  |  | 2024 | https://www.sos.mo.gov/cmsimages/adrules/csr/current/10csr/10c23-5.pdf
Montana | 30000 | Definition: Geothermal Heat Pump |  |  | Closed-Loop System – Horizontal Horizontal ground source heat pump installation is generally most cost-effective for residential installations, particularly for new construction where sufficient land is available. It requires trenches at least four feet deep. The most common layouts either use two pipes, one buried at six feet, and the other at four feet, or two pipes placed side-by-side at five feet in the ground in a two-foot wide trench. The method of looping pipe allows more pipe in a shorter trench, which cuts down on installation costs and makes horizontal installation possible in areas it would not be with conventional horizontal applications. Closed-Loop System – Vertical Vertical systems are often used for large commercial buildings and schools because the land area required for horizontal loops would be prohibitive. Vertical loops are also used where the soil is too shallow for trenching, and they minimize the disturbance to existing landscaping. For a vertical system, holes approximately four inches in diameter are drilled about 20 feet apart and 100 to 400 feet deep. Into these holes go two pipes that are connected at the bottom with a U-bend to form a loop. The vertical loops are connected with horizontal pipe, placed in trenches, and connected to the heat pump in the building. Closed-Loop System – Pond/Lake If your site has an adequate water body, this may be the lowest cost option. A supply line pipe is run underground from the building to the water and coiled into circles at least eight feet under the surface to prevent freezing. The coils should only be placed in a water source that meets minimum volume, depth, and quality criteria. Open-Loop System An open-loop system uses a well or surface water body such as a pond or lake as the heat exchange fluid that circulates directly through the ground source heat pump system. Once the water has circulated through the system, it returns to the ground through the well, a recharge well, or surface discharge. This option is only practical where there is an adequate supply of relatively clean water, and all regulations regarding ground water discharge are met. |  |  | https://deq.mt.gov/files/Energy/EnergizeMT/Renewables/Geothermal%20Pub/5%20HeatPumps.pdf
New Hampshire | 33000 | Setback - Public Water | 50 | feet | Fifty feet from a well used for potable water supply |  | 2017 | https://www.law.cornell.edu/regulations/new-hampshire/N-H-Admin-Code-SS-We-602.37
New Hampshire | 33000 | Setback - Hazardous Materials/Fertilizers | 25 | feet | Twenty five feet from a septic tank or effluent disposal area |  | 2017 | https://www.law.cornell.edu/regulations/new-hampshire/N-H-Admin-Code-SS-We-602.37
North Carolina | 37000 | Definition: Geothermal Heat Pump |  |  | Geothermal Direct Expansion Closed-Loop Wells" means wells used to house a subsurface system of closed-loop pipe that circulates refrigerant gas for heating and cooling purposes. |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Building Foundation | 15 | feet |  |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Wastewater | 50 | feet | Septic systems, including drainfield, waste application area, and repair area |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Fuel (above ground) | 50 | feet | Above ground or underground storage tanks that contain petroleum fuels used for heating equipment, boilers, or furnaces, except for tanks used solely for storage of propane, natural gas, or liquefied petroleum gas |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Fuel (below ground) | 50 | feet | Chemical or petroleum fuel underground storage tank systems regulated under 15A NCAC 02N with secondary containment |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Fuel (below ground) | 100 | feet | Chemical or petroleum fuel underground storage tank systems regulated under 15A NCAC 02N without secondary containment |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Subsurface Drains | 50 | feet | Land-based or subsurface waste storage or disposal systems |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Sewer Lines | 15 | feet | Water-tight sewer lateral lines from a residence or other non-public system to a sewer main or other wastewater disposal system |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
North Carolina | 37000 | Setback - Sewer Lines | 25 | feet | Other industrial or municipal sewage or liquid waste collection or transmission sewer mains |  | 2019 | https://www.law.cornell.edu/regulations/north-carolina/15A-N-C-Admin-Code-02C-0223
Oklahoma | 40000 | Setback - Public Water | 10 | feet | A vertical heat exchange well shall be located on a site so that surface water will not pool or pond around or within ten (10) feet of the heat exchange well location |  | 2008 | https://regulations.justia.com/states/oklahoma/title-785/chapter-35/subchapter-7/section-785-35-7-1-1/
Tennessee | 47000 | Definition: Well |  |  | "Geothermal well" means a hole drilled into the earth, by boring or otherwise, greater than twenty feet in depth constructed for the primary purpose of adding or removing British Thermal Units (BTU) from the earth for heating or cooling. This is also referred to as a closed loop geothermal borehole. |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.17
Tennessee | 47000 | Setback - Wastewater | 10 | feet | house to septic tank connection |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee | 47000 | Setback - Wastewater | 100 | feet |  |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee | 47000 | Setback - Private Water | 100 | feet |  |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee | 47000 | Setback - Sewer Lines | 10 | feet | house to sewer line connection |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee | 47000 | Setback - Sewer Lines | 25 | feet | septic tank |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Tennessee | 47000 | Setback - Sewer Lines | 10 | feet | Applies only to locations of Closed Loop Geothermal Boreholes |  | 2015 | https://www.law.cornell.edu/regulations/tennessee/Tenn-Comp-R-Regs-0400-45-09-.01
Texas | 48000 | Licensed Driller |  |  | Closed-loop geothermal wells must be drilled and completed by a water well driller licensed in Texas. |  | 2023 | https://www.rrc.texas.gov/oil-and-gas/applications-and-permits/injection-storage-permits/geothermal/
Utah | 49000 | Licensed Driller |  |  | Must be drilled by a licensed driller and the owner or applicant must have an approved application for that specific purpose |  | 2022 | https://www.law.cornell.edu/regulations/utah/Utah-Admin-Code-R655-4-12

## County-Level
This data was collected with the help of generative AI. The Large Language Models used for this effort make mistakes. Always validate the data for critical use cases.
State | County | County Subdivision FIPS Code | Feature | Value | Units | Summary | Section | Ordinance Year | Source URL
District Of Columbia | District of Columbia | 11001 | Definition: Geothermal |  |  | "geothermal energy: heat extracted from the Earth's interior and used to produce electricity or mechanical power or provide thermal energy for heating buildings or processes. Geothermal energy does not include systems such as heat pumps that use energy independent of the geothermal source to raise the temperature of the extracted heat." | 3.2 Definitions | 2020 | https://dob.dc.gov/sites/default/files/dc/sites/dob/publication/attachments/2017%20DC%20Energy%20Code.pdf
Florida | Alachua | 12001 | Definition: Geothermal |  |  | "Renewable Energy (see also Alternative Energy): Systems that generate energy from non-fossil fuel resources that are locally harvested, collected or concentrated in such a way as to not deplete nor imperil the resource base from which they are derived... (e.g. solar photovoltaic panels or solar thermal systems, geothermal energy for heating or cooling of structures, biomass, biodiesel, cellulosic ethanol, wind turbines, methane production via anaerobic digestion from organic materials and discarded foodstuffs)" | ATTACHMENT 'B' - ENERGY ELEMENT DEFINITIONS | 2011 | https://growth-management.alachuacounty.us/formsdocs/Ordinance_11_01.pdf
Florida | Lee | 12071 | Definition: Well |  |  | "GEOTHERMAL WELLS -means a combination of a supply well and an injection well installed to utilize the natural thermal characteristics of groundwater for heating and cooling. Groundwater withdrawn by geothermal wells does not typically result in changes in water quality or consumptive use (i.e., the same quality and quantity of water withdrawn from the supply well is returned to the same aquifer through the injection well)." | SECTION FIVE: DEFINITIONS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee | 12071 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL CLOSED LOOP SYSTEMS -means a system that uses water and an antifreeze solution circulated through a closed-loop system of pipes buried in the earth commonly referred to as a loop field. The solution acts as a medium for heat transfer. These loops are heat fused at the joints and pressurized. (The loop field is what sets these systems apart from conventional heating and cooling equipment.)" | SECTION FIVE: DEFINITIONS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee | 12071 | Permit |  |  | Section 9.1(1): "A valid permit issued by the DNR is required to drill, construct, repair, rehabilitate, plug, enlarge or deepen any well..." Appendix A specifically lists permit application requirements for "Geo-Thermal Supply and Injection Well (single family, replacement)" and "Geo-Thermal Supply and Injection Well (commercial, farm, replacement)," including "A properly completed State of Florida Water Well Application," site plan materials, and for single-family: "Copy of exemption from SFWMD; Copy of exemption from DEP"; for commercial/farm: "Florida Department of Environmental Protection ('FDEP') injection well permit; WUP Number and copy of WUP; Copy of exemption from SFWMD; Copy of exemption from DEP." | SECTION NINE: PERMITS; APPENDIX "A" SECTION I PERMITS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee | 12071 | Inspection |  |  | Section 12.2(1): "The DNR or appropriate state agency will conduct inspection of well construction, alterations, and plugging." Section 12.2(2): "It is the Contractor's responsibility to advise the DNR of the date(s) and time(s) when construction will begin, when various portions of the work will be completed..." Section 13.10: "The DNR must be notified by the Contractor at least twenty-four (24) hours prior to plugging the replacement well, so that an inspector can be present during plugging operation." | SECTION TWELVE: DRILLING INSPECTORS AND INSPECTIONS; SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee | 12071 | Licensed Driller |  |  | Section 13.1(2): "Only licensed State of Florida Water Well contractors are authorized to drill, construct, repair, rehabilitate, plug, enlarge, or deepen wells." Appendix A, "Geo-Thermal Supply and Injection Well" permit requirements: "A valid State of Florida water well contractor license." | SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES; APPENDIX "A" SECTION I PERMITS | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee | 12071 | Decommissioning |  |  | Section 13.8(1): "Generally, a well may be plugged provided: It is filled from bottom to the land surface with an appropriate grouting material... and work done in accordance with the requirements of the DNR and the SFWMD." Section 13.9(1): "Prior to plugging any well, a permit must be obtained from the DNR." Section 13.10: "The Contractor shall ensure that the existing well is plugged from bottom to the land surface with approved grouting material and in accordance with the requirements of this Ordinance within 2 weeks following completion of installation of the replacement well." | SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | Lee | 12071 | Other Prohibitions/Regulations |  |  | Section 13.12 states for "GEOTHERMAL CLOSED LOOP HOLES" that "Holes may not exceed the Water-Table Aquifer... The open hole or any installed pipe may not exceed the first confining unit below the Water Table aquifer." | SECTION THIRTEEN: CONSTRUCTION OF WELLS, BORINGS AND SHAFT HOLES | 2023 | https://www.leegov.com/bocc/Ordinances/23-14.pdf
Florida | St. Lucie | 12111 | Permit |  |  | "Unless expressly exempt by statute or this rule, all wells must be permitted prior to construction, repair or abandonment." "Unless expressly exempted by statute or District rule, a permit must be obtained from the District or delegated agency prior to the construction, repair or abandonment of any water well within the District's jurisdiction." Also, "a permit shall be required before beginning construction or repair of any water well within such area." | 40E-3.040 Scope of Part I; 40E-3.041 Permits Required; 62-532.400 Permit for Water Well Construction or Repair | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie | 12111 | Inspection |  |  | The agreement states the HEALTH DEPARTMENT "shall review, evaluate and make final inspections and disposition of permit applications for the construction, repair and abandonment of all water wells." Rule 40E-3.461 adds: "The District or delegated agency is authorized to inspect any well or abandoned well within its jurisdiction... Inspections shall be done as necessary to insure conformity with applicable standards." Rule 62-532.510 similarly provides inspections "as is necessary to ensure conformity with applicable standards." | III. SCOPE OF DELEGATION; 40E-3.461 Inspection; 62-532.510 Water Well Inspections | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie | 12111 | Licensed Driller |  |  | "Unless expressly exempt by statute or this rule, all wells must be permitted prior to construction, repair or abandonment and must be constructed, repaired or abandoned by a licensed water well contractor." "The work shall be performed by a licensed water well contractor." Also, "It is unlawful for any person to... Construct, repair, or abandon a water well, or operate drilling equipment for such purpose, unless employed by or under the supervision of a licensed water well contractor." | 40E-3.040 Scope of Part I; 40E-3.531 Abandoned Well Plugging; 62-531.450 Unlawful Acts, Grounds for Disciplinary Actions, and Penalties | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie | 12111 | Certification |  |  | "Water Well Contractor means an individual who is responsible for the location, construction, repair, or abandonment of a water well and who is licensed under Chapter 62-531, F.A.C., to engage in the business of construction, repair, or abandonment of water wells." Rule 40E-3.036 incorporates "Chapter 62-531, F.A.C., Well Contractor Licensing Requirements." | 40E-3.021(30) Definitions; 40E-3.036 Rules and Publications Incorporated by Reference; 62-531.200(11) Definitions Used in Water Well Contractor Rules | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Florida | St. Lucie | 12111 | Decommissioning |  |  | "All abandoned wells shall be plugged by filling them from bottom to top with grout within a time specified by the District. The work shall be performed by a licensed water well contractor." "The owner of the property... shall be responsible for ensuring that all abandoned wells on the property are properly plugged." Also, "All abandoned wells shall be filled and sealed in accordance with Rule 62-532.500(4), F.A.C." and "All abandoned wells shall be plugged by filling them from bottom to top with neat cement grout or bentonite and capped with a minimum of one foot of neat cement grout." | 40E-3.531 Abandoned Well Plugging; 62-532.440 Abandonment of Water Wells; 62-532.500(4) Plugging | 2005 | https://www.sfwmd.gov/sites/default/files/documents/stlucie_well_delegation_amend_20050511.pdf
Idaho | Elmore | 16039 | Maximum Well Depth | 18 | feet | In Wellhead Protection Zones II and III, "Injection well is a prohibited use except for the following: a. Deep well injection (below eighteen (18°) feet in depth): (1) Geothermal heat; or (2) Heat pump return; or (3) Cooling water return." The ordinance also distinguishes "Shallow well injection only (less than eighteen (18°) feet in depth)" for other listed uses. | Section 6-25-5(C)-(D): Allowed Uses and Notice Requirements by Zone |  | http://elmorecounty.org/wp-content/uploads/2018/11/chapter-25-wellhead-protection.pdf
Idaho | Elmore | 16039 | Other Prohibitions/Regulations |  |  | Within Wellhead Protection Zone IA, permitted uses are limited to "Necessary public water supply wellhead equipment including, wellhead facility buildings, water storage tanks, disinfections equipment, disinfections chemical storage and landscaping as required by this Title. All other uses shall be prohibited." | Section 6-25-5(A): Wellhead Protection Zone IA |  | http://elmorecounty.org/wp-content/uploads/2018/11/chapter-25-wellhead-protection.pdf
Idaho | Minidoka | 16067 | Other Prohibitions/Regulations |  |  | Zone IB: 'Injection well is a prohibited use except for the following: a. Closed systems or as approved by IDEQ.' Zone II: 'Injection well is a prohibited use except for the following: a. Deep well injection (below 18 feet in depth): (1) Geothermal heat; or (2) Heat pump return; or (3) Cooling water return; b. Shallow well injection only (less than 18 feet in depth)...' Zone III: 'Injection wells except for the following: a. Deep well injection (below 18 feet in depth): (1) Geothermal heat; or (2) Heat pump return; or (3) Cooling water return...'. | 8-15-5: ALLOWED USES AND NOTICE REQUIREMENTS BY ZONE | 2016 | https://codelibrary.amlegal.com/codes/minidokaco_id/latest/minidokaco_id/0-0-0-3538
Idaho | Twin Falls | 16083 | Minimum Well Depth | 18 | feet | 'District 2 ... Injection wells except for the following: a. Deep well injection (eighteen (18) feet or deeper in depth) of one or more of the following types: i. Geothermal heat, ii. Heat pump return, or iii. Cooling water return.' The same deep-well exception also appears in 'District 3.' | 8-7E-3: PROHIBITED USES |  | https://twinfallscounty.org/wp-content/uploads/TFCO-ZONE-CODE-2022.pdf
Idaho | Twin Falls | 16083 | Other Prohibitions/Regulations |  |  | 'District 2: The following uses or conditions are prohibited within Wellhead Protection Overlay District 2: ... Injection wells except for the following: a. Deep well injection (eighteen (18) feet or deeper in depth) of one or more of the following types: i. Geothermal heat, ii. Heat pump return, or iii. Cooling water return ...' and 'District 3: The following uses or conditions are prohibited within Wellhead Protection Overlay District 3: 1. Injection wells except for the following: a. Deep well injection (eighteen (18) feet or deeper in depth) of one or more of the following types: i. Geothermal heat, ii. Heat pump return, or iii. Cooling water return ...' | 8-7E-3: PROHIBITED USES |  | https://twinfallscounty.org/wp-content/uploads/TFCO-ZONE-CODE-2022.pdf
Illinois | Clinton | 17027 | Definition: Well |  |  | "Closed Loop Well means a sealed, watertight loop of pipe buried outside of a building foundation intended to recirculate a liquid solution through a heat exchanger but is limited to the construction of the bore hole, piping in the bore hole, heat exchange fluid, and the grouting of the bore hole and does not include the piping and appurtenances used in any other capacity. 'Closed Loop Well' does not include any horizontal closed loop well systems where grouting is not necessary by law or standard industry practice." | Section 18-3-1 - Definitions | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Definition: Geothermal Heat Pump |  |  | "Geothermal Closed Loop System means the entire system containing the horizontal closed loop well or wells, the vertical closed loop well or wells, and the horizontal header piping." | Section 18-4-1 - Definitions | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Building Foundation | 5 | feet | The setback table requires separation from "Pits, Crawl Spaces or Basements" of "5" feet for closed-loop wells. Section 18-3-7 also requires permit applications to show locations and distances to potential contamination sources, and the table provides the controlling numeric lateral distance. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Wastewater | 150 | feet | The setback table lists wastewater-related separations for closed-loop wells, including: "Cess Pools 150"; "Leaching Pit 25"; "Pit Privy 25"; "Subsurface Seepage Pipe/Tile From Private Sewage Systems 25"; and "Septic Tank 25" for USP food grade propylene glycol closed-loop wells, with larger distances for other authorized coolants in some cases. The controlling most restrictive wastewater setback shown is "Cess Pools 150." | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Private Water | 25 | feet | "When USP food grade propylene glycol is used as the geothermal coolant, the minimum setback of a closed loop well from a water well shall be twenty-five (25) feet." The setback table likewise lists "Existing Private Water Well ... 25" feet for USP food grade propylene glycol closed-loop wells. | Section 18-4-5 - Setback Distances | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Animal Enclosures | 25 | feet | The setback table requires closed-loop wells to be set back from "Barnyard or Animal Confinement Lot" by "25" feet for USP food grade propylene glycol systems. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Fuel (above ground) | 25 | feet | The table includes setback distances from contamination sources and specifically lists "buried fuel tanks" in the permit-application siting information in Section 18-3-7, but the explicit numeric lateral distances table governs sources including contamination routes. The only explicit fuel-tank reference in the ordinance text is "buried fuel tanks" within application requirements. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Subsurface Drains | 10 | feet | The setback table lists "Footing Drains (No connection to a sewer or sump handling sewage is allowed.)" with a minimum distance of "10" feet for closed-loop wells. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Sewer Lines | 50 | feet | The setback table provides: "Sewers 50 feet. A well or closed loop well may be located to within 10 feet of a sewer provided the sewer consists of cast iron pipe with watertight mechanical joints or rubber gasket sealed joints which meet ASTM Standard C564-09a, SDR 26 or schedule 40 PVC pipe or heavier with solvent welded watertight joints or elastomeric seals (gaskets) used for push-on joints which meet ASTM Standard F477-02e1." | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Setback - Water Bodies | 25 | feet | The setback table states: "Lakes, Ponds, Streams, or Cisterns 25" feet for closed-loop wells. | Minimum Lateral Distances Between Water Wells, Closed-Loop Heat Pump Wells, MINIMUM LATERAL DISTANCES FOR CLAY AND LOAM SOILS | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Permit |  |  | Section 18-3-6 states: "No water well or closed loop well system shall be constructed, modified or deepened except in accordance with this Code, and it shall be unlawful to proceed with such work unless a permit has first been obtained from the Health Department." Section 18-4-7 adds: "No geothermal closed loop system shall be constructed or modified in the County... without first registering the location and type of geothermal closed loop system with the Department." | Section 18-3-6 - Permit Required; Section 18-4-7 - Registration of Geothermal Closed Loop System | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Inspection |  |  | Section 18-3-16: "A water well or closed loop well system shall not be placed into operation until the installation of the water well, its components and closed loop well systems have been inspected to verify compliance with the applicable provisions of this Code and approval issued by the Health Department." Section 18-4-9: "A geothermal closed loop system shall not be placed into operation until the geothermal closed loop system has been inspected by the Department to verify compliance with this Article and until written approval has been issued by the Department." Section 18-4-2 also requires the system to "be pressure tested at a minimum pressure of twenty (20) pounds per square inch... after installation to ensure that there are no leaks." | Section 18-3-16 - Inspection of Completed Work; Section 18-4-9 - Inspections | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Licensed Driller |  |  | "No person shall install a vertical closed loop well unless that person is a Geothermal Closed Loop Well Driller." | Section 18-4-6 - Registration of Contractor/Driller | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Certification |  |  | "To register with the Department, a person shall have a valid accreditation from the International Ground Source Heat Pump Association (IGSHPA) or can show that he or she has an equivalent accreditation." Also, "A Geothermal Closed Loop Well Driller shall have a valid water well contractor’s license issued under the Illinois Water Well and Pump Installation License Act (225 ILCS 345/1) or shall have a valid certification for the drilling of closed loop wells from the National Ground Water Association (NGWA) or can show that he or she has an equivalent certification." | Section 18-4-6 - Registration of Contractor/Driller | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Clinton | 17027 | Decommissioning |  |  | Section 18-4-12 provides: "Closed loop wells shall be sealed in accordance with the Illinois Water Well Construction Code. The Department shall be notified by telephone or writing at least forty-eight (48) hours prior to the commencement of any work to abandon a closed loop well." Section 18-3-5 similarly states: "Water wells or closed loop well systems that are abandoned shall be sealed in a manner prescribed by the Health Department and the 'Illinois Water Well Construction Code'." | Section 18-4-12 - Closed Loop Well Abandonment; Section 18-3-5 - Abandoned Wells or Closed Loop Well | 2024 | https://clintonco.illinois.gov/wp-content/uploads/2025-County-Code-combined.pdf
Illinois | Henry | 17073 | Definition: Well |  |  | "Closed Loop Well means a sealed, watertight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger but is limited to the construction of the bore hole, piping in the bore hole, heat exchange fluid, and the grouting of the bore hole and does not include the piping and appurtenances used in any other capacity. 'Closed Loop Well' does not include any horizontal closed loop well systems where grouting is not necessary by law or standard industry practice." | SECTION I. A. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry | 17073 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Heat Exchange System (Geothermal Exchange Systems) means sealed, water tight loop of pipe buries outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger. The term includes, but is not limited to, closed loop wells, horizontal closed loop and body of water loop systems." | SECTION I. A. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry | 17073 | Setback - Building Foundation | 15 | feet | "In order to protect the sewage disposal system and a horizontal closed loop well system, there shall be a minimum set back of fifteen (15) feet between components of the systems." The ordinance definitions also state a closed loop heat exchange system and closed loop well are "buried outside of a building foundation." | SECTION IV. COMPLIANCE PROVISION, B. SEPTIC SYSTEM SET BACK FOR HORIZONTAL CLOSED LOOP WELL SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry | 17073 | Setback - Wastewater | 15 | feet | "In order to protect the sewage disposal system and a horizontal closed loop well system, there shall be a minimum set back of fifteen (15) feet between components of the systems." | SECTION IV. COMPLIANCE PROVISION, B. SEPTIC SYSTEM SET BACK FOR HORIZONTAL CLOSED LOOP WELL SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry | 17073 | Permit |  |  | "No water well nor closed loop heat exchange system well shall be constructed, deepened, modified or sealed after abandonment, except in accordance with these regulations, and it shall be unlawful to proceed with the construction, deepening, modification or sealing of a water well without first obtaining a permit from the Henry County Health Department." | SECTION IV. COMPLIANCE PROVISION, A. PERMIT | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry | 17073 | Inspection |  |  | "Henry County Health Department shall inspect all new closed loop well systems..."; "The inspection for a closed loop well system shall include observation of the critical aspects of construction, including, at a minimum, inspecting the grouting and documenting the setback distances."; "In the case of a closed loop well, the critical elements shall include placement of the sealing grout to assure that proper materials and methods are used." | SECTION IV. E. INSPECTIONS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Henry | 17073 | Certification |  |  | "All individuals who install closed loop well systems shall possess a valid certificate of registration issued by the Illinois Department of Public Health. All Horizontal Closed Loop contractors shall annually register with Henry County Health Department. The registration shall expire on November 30 th of the year of issue." | SECTION IV. D. REGISTRATION, 2. WATER WELL CONTRACTORS, WATER WELL PUMP INSTALLERS AND CLOSED LOOP WELL CONTRACORS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/158/Henry-County-Water-Ordinance-PDF
Illinois | Jo Daviess | 17085 | Definition: Well |  |  | "HORIZONTAL CLOSED LOOP WELL: A closed loop well constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed twenty feet (20') in depth." "VERTICAL CLOSED LOOP WELL: A closed loop well constructed to contain vertical piping and the installation and grouting of the vertical loop piping when such piping exceeds twenty feet (20') in depth." | 5-7B-3: DEFINITIONS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL CLOSED LOOP SYSTEM: The entire system containing the horizontal closed loop well or wells, the vertical closed loop well or wells and the horizontal header piping." | 5-7B-3: DEFINITIONS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Setback - Public Water | 25 | feet | "When USP food grade propylene glycol is used as the geothermal coolant, the minimum setback of a closed loop well from a water well shall be twenty five feet (25')." | 5-7B-7: SETBACK DISTANCES | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Minimum Well Depth | 20 | feet | "HORIZONTAL CLOSED LOOP WELL: ... when such piping does not exceed twenty feet (20') in depth." "VERTICAL CLOSED LOOP WELL: ... when such piping exceeds twenty feet (20') in depth." | 5-7B-3: DEFINITIONS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Permit |  |  | "Application for registration for a geothermal closed loop system shall be in writing..." "A separate application is required for every ten (10) vertical wells or ten (10) horizontal loop trenches." "After an application to construct a geothermal closed loop system has been reviewed and approved, a notice to proceed shall be issued..." "No construction of a geothermal closed loop system shall commence prior to approval of the application by the department." | 5-7B-9: APPLICATION FOR REGISTRATION; 5-7B-12: APPROVAL OF APPLICATION | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Inspection |  |  | "The department shall have the authority to enter the property at any reasonable time for inspection purposes to determine compliance with this chapter." "A geothermal closed loop system shall not be placed into operation until the geothermal closed loop well has been inspected by the department to verify compliance with this chapter and until written approval has been issued by the department." "The geothermal closed loop system shall be pressure tested at a minimum pressure of twenty (20) pounds per square inch by the geothermal closed loop system contractor after installation to ensure that there are no leaks in the piping or in the equipment system." | 5-7B-10: INSPECTIONS; 5-7B-4: MATERIALS | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Licensed Driller |  |  | "No person shall install a vertical closed loop well unless that person is a geothermal closed loop well driller." "A geothermal closed loop well driller shall have a valid water well contractor's license issued under the Illinois water well and pump installation contractor's license act..." | 5-7B-8: REGISTRATION OF CONTRACTOR/DRILLER | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Certification |  |  | "To register with the department, a person shall have a valid accreditation from the International Ground Source Heat Pump Association (IGSHPA) or can show that he or she has an equivalent accreditation." "A geothermal closed loop well driller shall have a valid water well contractor's license issued under the Illinois water well and pump installation contractor's license act... or shall have a valid certification for the drilling of closed loop wells from the National Ground Water Association (NGWA) or can show that he or she has an equivalent certification." | 5-7B-8: REGISTRATION OF CONTRACTOR/DRILLER | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Jo Daviess | 17085 | Decommissioning |  |  | "Closed loop wells shall be sealed in accordance with the Illinois water well construction code. The department shall be notified by telephone or writing at least forty eight (48) hours prior to the commencement of any work to abandon a closed loop well." | 5-7B-14: CLOSED LOOP WELL ABANDONMENT | 2014 | https://codelibrary.amlegal.com/codes/jodaviesscoil/latest/jodaviessco_il/0-0-0-2393
Illinois | Lake | 17097 | Definition: Well |  |  | "The term 'well' shall include, but not be limited to the following types or categories of wells: all types or categories of water wells (including community water wells), monitoring wells, closed loop wells and injection wells (where the depth is greater than the largest surface dimension)." | § 170.01 GENERAL PROVISIONS. | 2015 | https://codelibrary.amlegal.com/codes/lakecountyil/latest/lakecounty_il/0-0-0-14327
Illinois | Lake | 17097 | Permit |  |  | "The Health Officer shall receive applications and issue permits for the installation and modification of water wells, closed loop wells and closed loop well systems, the sealing of wells, the operation of non-community water systems..." | § 170.02 HEALTH OFFICER, DUTIES AND POWERS. | 2015 | https://codelibrary.amlegal.com/codes/lakecountyil/latest/lakecounty_il/0-0-0-14327
Illinois | Lake | 17097 | Inspection |  |  | "The Health Officer shall receive applications and issue permits for the installation and modification of water wells, closed loop wells and closed loop well systems, the sealing of wells, the operation of non-community water systems, and shall inspect the premises for which the permits have been issued..." Also: "The Health Officer... shall have the authority to enter any property at any reasonable time to inspect for health and sanitation purposes, and for compliance with the provisions of this subchapter." | § 170.02 HEALTH OFFICER, DUTIES AND POWERS. | 2015 | https://codelibrary.amlegal.com/codes/lakecountyil/latest/lakecounty_il/0-0-0-14327
Illinois | McHenry | 17111 | Permit |  |  | "No person shall construct, deepen, modify, cap, or seal a water well until a permit has been issued by the Department." The ordinance also states: "A permit may be issued for a closed loop or irrigation well, when a community public water supply is reasonably available, provided that the owner/operator of the community public water supply provides written confirmation of no objection." | § 8.04.790 Permit Requirements |  | https://pub-countyofmchenry.escribemeetings.com/filestream.ashx?DocumentId=105790
Illinois | McHenry | 17111 | Inspection |  |  | "Department personnel shall have access to the property any time after a permit application has been filed in order to determine satisfactory compliance with the provisions set forth in this Ordinance." Access is deemed essential for "1. On-site layout review 2. Any stage of construction or modification of a system; and 3. Final inspection." The ordinance also states: "Department staff shall be present when a water well is sealed by a homeowner or environmental consultant." | § 8.04.790(M)-(N) Permit Requirements |  | https://pub-countyofmchenry.escribemeetings.com/filestream.ashx?DocumentId=105790
Illinois | Macon | 17115 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A sealed, watertight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger. May also be referred to as a closed loop system." | § 54.01 DEFINITIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Setback - Wastewater | 75 | feet | "there shall be a minimum set back of 75 feet between the septic field and the vertical geothermal system, and a minimum setback of 25 feet between the septic field and the horizontal geothermal system." | § 54.04 SEPTIC SYSTEM AND WELL SETBACK. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Setback - Private Water | 75 | feet | "Geothermal systems shall not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 54.04 SEPTIC SYSTEM AND WELL SETBACK. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Setback - Public Water | 200 | feet | "Geothermal systems shall not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 54.04 SEPTIC SYSTEM AND WELL SETBACK. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Minimum Well Depth | 20 | feet | "HORIZONTAL GEOTHERMAL SYSTEM. A geothermal system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth." "VERTICAL GEOTHERMAL SYSTEM. Geothermal system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth." | § 54.01 DEFINITIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Permit |  |  | § 54.02: "it shall be unlawful to proceed with the construction or modification of a geothermal system without first registering the location and type of geothermal system with the County Health Department." § 54.07(B): "No construction of a geothermal system can commence prior to approval of the application by the County Health Department." | § 54.02 REGISTRATION REQUIREMENT.; § 54.07 APPLICATION FOR INSPECTION. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Inspection |  |  | § 54.03: "Geothermal systems installed shall be exempt from the inspection requirement of this chapter provided the municipality has a geothermal system inspection process in place." § 54.07(A): "Application for inspection for a geothermal system shall be in writing." § 54.10(B): "the drilling and grouting of the holes should be witnessed (audited) by a representative of the County Health Department for each contractor annually." § 54.10(C): "The geothermal system shall be pressure tested at a minimum pressure of 20 pounds per square inch by the contractor, driller, and/or excavator after installation to ensure that there are no leaks in the piping or in the equipment system." | § 54.03 EXEMPTION.; § 54.07 APPLICATION FOR INSPECTION.; § 54.10 INSPECTIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Certification |  |  | § 54.11: "All geothermal systems shall use USP or food grade propylene glycol as the coolant in the county." § 54.01: "The product container shall be labeled 'Propylene Glycol USP' or equivalent. Any product not containing the letters 'USP' will not be acceptable for this use, unless vendor documentation is produced to demonstrate equivalency." § 54.10(D): "All plastic piping shall be watertight and conform to ASTM D2447-03 or D3035-08." | § 54.11 USE OF FOOD GRADE PROPYLENE GLYCOL AS COOLANT.; § 54.01 DEFINITIONS.; § 54.10 INSPECTIONS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Macon | 17115 | Decommissioning |  |  | The chapter includes an enacted section titled "§ 54.13 ABANDONMENT OF GEOTHERMAL SYSTEMS." | § 54.13 ABANDONMENT OF GEOTHERMAL SYSTEMS. | 2014 | https://codelibrary.amlegal.com/codes/maconcounty/latest/maconcounty_il/0-0-0-5347
Illinois | Madison | 17119 | Closed-loop Prohibitions |  |  | In the Groundwater Protection Overlay District, Zone 1 and Zone 2 regulations state: "No injection wells (including closed loop heat pump wells)." | § 93.040(D)(1)(h) and § 93.040(D)(2)(h) | 2014 | https://cms4files.revize.com/madisoncountyilus/document_center/Planning_Development/Zoning%20Ordinance.pdf
Illinois | Randolph | 17157 | Permit |  |  | "It shall be unlawful for any person to construct and/or reconstruct any individual water supply system or geothermal well within Randolph County unless he holds a valid permit issued by the Health Officer." "It shall be the responsibility of the property owner to obtain a Permit before any construction is begun on the system." | 18-5-2 PERMITS; 18-5-3 PERMIT PRIOR TO CONSTRUCTION | 2016 | https://randolphcountyil.gov/wp-content/uploads/County-Ordinances.pdf
Illinois | Randolph | 17157 | Inspection |  |  | "The Health Officer is, hereby, authorized and directed to make such inspections as are necessary to determine satisfactory compliance with this Code." "It shall be the duty of the owner or occupant of a property to give the Health Officer free access to the property for the purpose of making such inspections as are necessary to determine compliance with the requirements of this Code." | 18-5-9 INSPECTIONS BY HEALTH OFFICER; 18-10-1 RIGHT OF INSPECTION | 2016 | https://randolphcountyil.gov/wp-content/uploads/County-Ordinances.pdf
Illinois | St. Clair | 17163 | Permit |  |  | "Any owner or authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical ... system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." (IRC R105.1, Section 7-2-27). Also: "An owner, authorized agent or contractor who desires to erect, install, enlarge, alter, repair, remove, convert or replace a mechanical system, the installation of which is regulated by this code ... shall first make application to the code official and obtain the required permit for the work." (IMC 106.1, Section 7-3-34). | 7-2-27 Required; 7-3-34 When required | 2017 | https://www.co.st-clair.il.us/webdocuments/CountyCode/Building%20Regulations.pdf
Illinois | St. Clair | 17163 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to framing inspection." (IRC R109.1.2, Section 7-2-51(B)). "Exception: Backfilling of ground-source heat pump loop systems tested in accordance with Section M2105.1 prior to inspection shall be permitted." Also: "The code official ... shall make the following inspections ... 1. Underground inspection ... before backfill is put in place ... 3. Final inspection shall be made upon completion of the mechanical system." (IMC 107.2, Section 7-3-40). "Exception: Ground-source heat pump loop systems tested in accordance with Section 1208.1.1 shall be permitted to be back filled prior to inspection." | 7-2-51(B) Plumbing, mechanical, gas and electrical systems inspection; 7-3-40 Required inspections and testing | 2017 | https://www.co.st-clair.il.us/webdocuments/CountyCode/Building%20Regulations.pdf
Illinois | Stark | 17175 | Definition: Well |  |  | "Closed Loop Well means a sealed, watertight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger but is limited to the construction of the bore hole, piping in the bore hole, heat exchange fluid, and the grouting of the bore hole and does not include the piping and appurtenances used in any other capacity. 'Closed Loop Well' does not include any horizontal closed loop well systems where grouting is not necessary by law or standard industry practice." | SECTION I.A.5. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark | 17175 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Heat Exchange System (Geothermal Exchange Systems) means sealed, water tight loop of pipe buried outside of a building foundation, which is intended to recirculate a liquid solution through a heat exchanger. The term includes, but is not limited to, closed loop wells, horizontal closed loop and body of water loop systems." | SECTION I.A.3. DEFINITIONS PERTAINING TO CLOSED LOOP HEAT EXCHANGE SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark | 17175 | Setback - Wastewater | 15 | feet | "In order to protect the sewage disposal system and a horizontal closed loop well system, there shall be a minimum set back of fifteen (15) feet between components of the systems." | SECTION IV.B. SEPTIC SYSTEM SET BACK FOR HORIZONTAL CLOSED LOOP WELL SYSTEMS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark | 17175 | Permit |  |  | "No water neither well nor closed loop heat exchange system well shall be constructed, deepened, modified or sealed after abandonment, except in accordance with these regulations, and it shall be unlawful to proceed with the construction, deepening, modification or sealing of a water well without first obtaining a permit from the Stark County Health Department." | SECTION IV.A. COMPLIANCE PROVISION - PERMIT | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark | 17175 | Inspection |  |  | "For the required inspection, the Stark County Health Department shall be notified... at least 48 hours prior to the commencement of any work to construct, modify or seal after abandonment of a water well or closed loop well for which a permit has been issued." Also, "Stark County Health Department shall inspect all new closed loop well systems" and "The inspection for a closed loop well system shall include observation of the critical aspects of construction, including, at a minimum, inspecting the grouting and documenting the setback distances." | SECTION IV.C. NOTIFICATION; SECTION IV.E. INSPECTIONS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark | 17175 | Certification |  |  | "All individuals who install close loop well systems shall possess a valid certificate of registration issued by the Illinois Department of Public Health. All Horizontal Closed Loop contractors shall annually register with Stark County Health Department." | SECTION IV.D.2. REGISTRATION | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Stark | 17175 | Decommissioning |  |  | "No... closed loop heat exchange system well shall be... sealed after abandonment, except in accordance with these regulations." Also, "Stark County Health Department shall be present at the site during at least one well sealing performed by each licensed /registered contractor..." and "In the case of a closed loop well, the critical elements shall include placement of the sealing grout to assure that proper materials and methods are used." | SECTION IV.A. PERMIT; SECTION IV.E.3. ABANDONED WELL AND CLOSED LOOP WELL SEALING INSPECTIONS | 2015 | https://www.henrystarkhealth.com/DocumentCenter/View/159/Stark-County-Water-Ordinance-PDF
Illinois | Tazewell | 17179 | Permit |  |  | "The owner/developer will submit soil investigations conducted by certified soil classifier for determination of type of septic systems and minimum size of lots. The size of each lot will include area for a replacement system similar to the proposed septic system. The information on the plat must include location of proposed septic system, future site of replacement system, well and geothermal closed loop wells. This information must be submitted on forms provided by the county." | 94.32. Approval of Proposed Subdivision Plats | 2005 | https://tazewellhealth.org/225/Sewage-Disposal
Indiana | Allen | 18003 | Definition: Geothermal Heat Pump |  |  | Accessory buildings, structures, and uses shall be permitted, including but not limited to: "Geothermal system." | 3-2-3-4 Accessory Buildings, Structures and Uses | 2025 | https://www.allencounty.in.gov/DocumentCenter/View/11296/2024-AC-Solar-Amendment---Staff-report-ZORD-2025-0005?bidId=
Indiana | Floyd | 18043 | Permit |  |  | "No person shall cause or allow the construction of any outbuilding or the installation of any swimming pool, geothermal heat system, underground utility connection, or underground lawn sprinkler system in association with an existing residence or commercial facility without first obtaining a Site Approval Permit for such construction." Article VI, Section 3 adds that "Site Approval Permits for the construction of any outbuilding or the installation of any swimming pool, ... geothermal heat system, underground utility connection, or underground lawn sprinkler system shall be issued upon: (1) proper application ... (2) the payment of the fee ... and (3) a determination by the Health Officer that the proposed location of such construction or installation conforms with Residential Rule 410, and shall not damage the residential sewage disposal system or interfere with its proper operation." | ARTICLE V. PROHIBITED ACTS, SECTION 5; ARTICLE VI. RESIDENTIAL PERMITS, SECTION 3 | 2010 | https://www.in.gov/counties/floyd/health-department/files/Floyd-County-Ordinances2.pdf
Indiana | Hendricks | 18063 | Setback - Property Lines | 5 | feet | Both open-loop geothermal separation tables include "Property lines — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Setback - Building Foundation | 5 | feet | Both open-loop geothermal separation tables include "Buildings and building overhangs — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Setback - Wastewater | 100 | feet | The ordinance provides minimum separation distances for open loop geothermal heat pump systems. For residential service, listed wastewater-related sources include "Septic tanks and absorption fields — 50 feet" and "Sewage pits and dry wells — 100 feet." For systems "serving other than a residence consisting of not more than two dwelling units," the table lists "Septic tanks, absorption fields, filters — 100 feet" and "Privies — 100 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Setback - Animal Enclosures | 50 | feet | For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units," the table requires separation from "Stables, livestock runs, manure piles, etc — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Setback - Sewer Lines | 30 | feet | For "open loop geothermal heat pump systems serving a residence(s)," the ordinance states they "shall maintain the following minimum separation distances from sources of contamination," including "Sewer Pipe ... 30 feet" and "Gravity sewers outside of building foundations..." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units," the table likewise lists "Sewer Pipes — 30 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Setback - Water Bodies | 50 | feet | The ordinance sets minimum separations for open loop geothermal heat pump systems from surface waters. One table lists "Streams, lakes, ponds — 25 feet" and another for systems "serving other than a residence consisting of not more than two dwelling units" lists "Streams, lakes, ponds — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Permit |  |  | "Before commencement of construction of a well or geothermal heat pump system utilizing a well, a well repair or a pump installation, the owner or agent shall obtain a written permit signed by the Health Officer. No person shall perform any work on such project until such permit is obtained." The permit application must be made on a form provided by the Health Officer, and "such permit shall be void if the installation is not completed in one year." | SECTION III PERMITS | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Inspection |  |  | "It shall be the duty of the well driller and the owner of the property on which the well is drilled to notify the Hendricks County Health Department when the well and appurtenances are available for inspection. The Health Officer must be permitted to inspect the well and appurtenances at any reasonable time." | SECTION VI COMPLIANCE AND INSPECTION - Inspection | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Licensed Driller |  |  | "All water well drillers and pump installers operating in Hendricks County shall comply with the licensing requirements of Indiana Code 25-39-3." | SECTION V MINIMUM REQUIREMENTS - Water Well Drillers and Pump Installers | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Hendricks | 18063 | Decommissioning |  |  | "Groundwater wells must be properly abandoned in accordance with 312 IAC 13." The ordinance further states: "Any groundwater well connected to an existing structure that is scheduled for demolition must be either: a. Properly abandoned in accordance with 312 IAC 13 ... with written verification submitted to the Local Health Officer prior to initiating demolition of the structure, or b. Located by global positioning system for later abandonment, with written notification and well location submitted to the Local Health Officer prior to initiating demolition of the structure." | SECTION V MINIMUM REQUIREMENTS - Well Abandonment | 2016 | https://www.co.hendricks.in.us/egov/documents/1488393194_4415.pdf
Indiana | Lake | 18089 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System (Geothermal Heat Exchange) Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. Geothermal energy systems consist of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump. This includes vertical closed loop, horizontal closed loop and water body closed loop systems." | 154-22-110. Definition of Words and Terms Beginning with 'G' | 2025 | https://lakecountyin.gov/departments/planning-commission/ordinances-c/unified%20development%20ordinance%20no.%202560.pdf
Indiana | Lake | 18089 | Permit |  |  | It is a civil zoning violation for the "failure to obtain a building, zoning, or other permit required under this UDO," and Article 20 states officials "may not issue permits or licenses for any use, building, activity or purpose that would be in conflict with the provisions of this UDO." | 154-20-040.E.1.b | 2025 | https://lakecountyin.gov/departments/planning-commission/ordinances-c/unified%20development%20ordinance%20no.%202560.pdf
Indiana | Pulaski | 18131 | Definition: Geothermal Heat Pump |  |  | "PRIVATE WATER WELLS. Any water well, including those serving geothermal heat pump systems, constructed to provide water to one- or two-family dwellings, totally or in part." | TITLE V: PUBLIC WORKS - PRIVATE WATER WELLS | 2014 | https://www.in.gov/localhealth/pulaskicounty/files/Pulaski-Co-Code.pdf
Indiana | St. Joseph | 18141 | Definition: Well |  |  | 'GEOTHERMAL WELL. A well that supplies water for use solely to heat and/or cool a structure.' | § 52.034 DEFINITIONS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph | 18141 | Setback - Building Foundation | 10 | feet | 'Wells shall be at least five feet outside of any existing building overhang and at least ten feet from any building foundation except geothermal, dewatering, fire suppression and monitoring wells.' | § 52.041(D) SITING OF NONPOTABLE WATER WELLS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph | 18141 | Permit |  |  | 'The owner of the real estate on which a nonpotable water well is to be constructed or his or her authorized agent shall obtain a water well permit.' 'No person shall install a well until and unless a permit is first obtained from the Health Officer and posted in a conspicuous place on the premises...' Geothermal wells are included as nonpotable wells in § 52.035(A)(2): 'Nonpotable wells... including but not limited to irrigation wells, geothermal wells, monitoring wells, dewatering wells, waterscape wells and fire suppression wells.' | § 52.038 PERMITS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph | 18141 | Inspection |  |  | For nonpotable well permits, 'The Health Officer will review the application and the proposed well location and may conduct an on-site inspection of the proposed location of the well.' The site must be staked 'at the time of the on-site inspection by the Health Officer or the permit application may be denied.' The ordinance also states, 'Upon the receipt of an application to install a well, the Health Officer shall be permitted to inspect the location, installation, condition and sampling of the wells at any stage.' | § 52.038 PERMITS; § 52.049 ENFORCEMENT | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph | 18141 | Licensed Driller |  |  | 'Any person that installs or abandons a potable or nonpotable water well ... shall first be licensed by the state in accordance with I.C. 25-39 et seq.' 'Any person that installs or abandons a potable or nonpotable water well in the county shall first obtain an annual registration from the Health Officer.' 'A licensed well driller shall be present during all well drilling or well abandonment activities.' | § 52.036 LICENSING AND REGISTRATION OF WELL DRILLERS | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | St. Joseph | 18141 | Decommissioning |  |  | 'No person shall abandon a well until and unless a well abandonment permit is first obtained from the Health Officer...' 'Any person who abandons any type of water well listed in § 52.035 shall have a current well drilling license.' 'Any potable or nonpotable well not in use for more than one year shall be abandoned according to the requirements of the Health Officer.' 'All wells shall be abandoned in a manner that restricts the movement of water within the well casing and annular space surrounding the well casing to the zone in which it originated...' 'The preferred method of abandoning wells is to remove the well casing and fill the well with a bentonite slurry or, at a minimum, bentonite pellets.' | § 52.038(D) Well abandonment permits; § 52.046 WELL ABANDONMENT PROCEDURES | 2009 | https://www.in.gov/localhealth/stjosephcounty/files/County-Code-52-Water-Regulations-2.pdf
Indiana | Wabash | 18169 | Definition: Geothermal |  |  | "Geothermal" means a system that extracts heat from the earth in heating mode and/or rejects heat into the earth in cooling mode. | Chapter 1, Definitions | 2012 | https://www.in.gov/counties/wabash/files/ordinances/Current-Wabash-County-Zoning-Ordinance.pdf
Indiana | Wabash | 18169 | Permit |  |  | "Open Loop and Closed Loop Geothermal renewable energy systems may be permitted within the jurisdictional area of this Ordinance. Discharge and drainage plans for open loop systems, which are required to drain into a pond, stream, creek, or drainage tile shall be reviewed and approved by the Wabash County Drainage Board prior to completion of the ILP." | 6.1.16. Geothermal | 2012 | https://www.in.gov/counties/wabash/files/ordinances/Current-Wabash-County-Zoning-Ordinance.pdf
Indiana | Whitley | 18183 | Definition: Well |  |  | "GEO-THERMAL WELL. A hole drilled in the earth for the purposes of utilizing the inherent cooling and heating qualities of the earth, including open loop and closed loop systems." | § 51.03 DEFINITIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Definition: Geothermal Heat Pump |  |  | The geothermal-system-type language appears within the geothermal well definition: 'GEO-THERMAL WELL. A hole drilled in the earth for the purposes of utilizing the inherent cooling and heating qualities of the earth, including open loop and closed loop systems.' | § 51.03 DEFINITIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Property Lines | 5 | feet | In the table 'Minimal Horizontal Separation Distances From Water Wells,' the ordinance lists: 'Side, rear or front lot lines 5 feet.' Because § 51.03 defines 'WATER WELL' to include 'a geo-thermal well,' this setback applies to geothermal wells covered by the chapter. | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Building Foundation | 10 | feet | In the table 'Minimal Horizontal Separation Distances From Water Wells,' the ordinance lists: 'Dwelling or other inhibiting structure 10 feet.' Because § 51.03 states that 'WATER WELL' includes 'a geo-thermal well,' this applies to geothermal wells governed by the chapter. | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Wastewater | 100 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' includes: 'Private sewage disposal systems 50 feet,' 'Commercial sewage disposal systems 100 feet,' and 'Private sewage disposal systems 100 feet (in soils where aquifers are in danger of contamination).' § 51.03 provides that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Fuel (above ground) | 50 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Permanently fixed aboveground storage tanks for fuel or chemicals 50 feet (300 gallons or more)' and 'Permanently fixed aboveground storage tanks for fuel or chemicals 25 feet (0-299 gallons).' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Fuel (below ground) | 50 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Underground storage tanks for fuel or chemicals 50 feet.' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Sewer Lines | 10 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' lists: 'Sanitary sewage lines 10 feet (horizontal).' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Water Bodies | 25 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Lake, pond, river, stream or public ditches 25 feet.' § 51.03 states that 'WATER WELL' includes 'a geo-thermal well.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Setback - Hazardous Materials/Fertilizers | 50 | feet | The table 'Minimal Horizontal Separation Distances From Water Wells' states: 'Underground storage tanks for fuel or chemicals 50 feet,' plus aboveground fuel or chemical storage tank setbacks of '50 feet (300 gallons or more)' and '25 feet (0-299 gallons).' § 51.03 includes geo-thermal wells within 'WATER WELL.' | § 51.05 CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Permit |  |  | "The owner(s) ... of any parcel of ground unto which a water well is to be installed ... shall obtain a written permit signed by the Whitley County Health Officer before any construction begins." "The water well permit is valid for a term of one year from the date of issue." "In cases of extreme emergency ... a water well may be installed without first obtaining a local permit, provided that the property owner or his or her agent obtains a local well permit within the next working day." § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(H), (N), (O) CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Inspection |  |  | § 51.05(H): "The Health Officer shall then make a site review of the area proposed, in person, within two working days of the filed application." § 51.05(I): "The Health Officer shall be allowed to inspect the work at any stage of construction... The Whitley County Health Officer shall make the inspection within two working days of the receipt of notice from the applicant." § 51.06: "The Whitley County Health Department may be present at the drilling of a water well to determine if proper drilling practices and grouting practices are being observed." § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(H)-(J); § 51.06 | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Licensed Driller |  |  | "No person shall install a water well in Whitley County, without being licensed by the State of Indiana Department of Natural Resources, under authority of I.C. 25-39-3." § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(P) CONSTRUCTION, PLACEMENT, PERMITS AND INSPECTIONS | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Certification |  |  | § 51.05(P): "No person shall install a water well in Whitley County, without being licensed by the State of Indiana Department of Natural Resources, under authority of I.C. 25-39-3." § 51.10(C): 'A well abandoned after December 31, 1987, shall be plugged ... by a registered and licensed well driller.' § 51.03 defines 'WATER WELL' to include 'a geo-thermal well.' | § 51.05(P); § 51.10(C) | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Decommissioning |  |  | § 51.03 defines 'ABANDON' as: 'To terminate operations of a well for water supply, monitoring, dewatering or geothermal purposes and to restore the site of the well in a manner that will protect ground water resources from contamination.' § 51.10(C) states: 'A well abandoned after December 31, 1987, shall be plugged with an impervious grouting material ... by a registered and licensed well driller.' § 51.10(J) adds: 'The division shall be notified in writing of a well abandonment with 30 days after plugging is completed.' | § 51.10 WELL ABANDONMENT | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Indiana | Whitley | 18183 | Other Prohibitions/Regulations |  |  | "A closed loop geo-thermal well system must be located so as to be easily accessed and must not be built over or placed under impervious materials." | § 51.05(S) | 2003 | https://www.whitleycounty.in.gov/egov/documents/1679429174_631.pdf
Iowa | Boone | 19015 | Setback - Property Lines | 10 | feet | Table I states that a "Groundwater heat pump borehole" must be at least "10" feet from "Property lines (unless a mutual easement is signed and recorded)." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone | 19015 | Setback - Building Foundation | 10 | feet | Table I lists "Groundwater heat pump borehole" with a required minimum distance of "10" feet from "Dwelling or other structure." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone | 19015 | Setback - Private Water | 50 | feet | Table I provides a row for "Groundwater heat pump borehole" and shows a minimum distance of "50" feet from a "Private water supply well." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone | 19015 | Setback - Public Water | 400 | feet | Table I states: "ALL PRIVATE SEWAGE DISPOSAL SYSTEMS SHALL BE LOCATED IN ACCORDANCE WITH THE MINIMUM DISTANCES SHOWN IN TABLE I." For "Groundwater heat pump borehole," the minimum distance is "400" feet from a "Shallow public water supply well@" and "200" feet from a "Deep public water supply well®." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone | 19015 | Setback - Subsurface Drains | 10 | feet | Table I requires a "Groundwater heat pump borehole" to be at least "10" feet from "Foundation drains or subsurface tiles." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone | 19015 | Setback - Water Lines | 100 | feet | Table I gives minimum distances from a "Groundwater heat pump borehole" to water lines: "10" feet from "Water lines continually under pressure" and "100" feet from "Suction water lines." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Boone | 19015 | Setback - Water Bodies | 100 | feet | Table I lists minimum distances for a "Groundwater heat pump borehole" from surface waters: "100" feet from "Lake or reservoir" and "25" feet from "Stream or pond." | 567-69.3(455B) Site analysis, 69.3(2) Minimum distances, Table I | 2020 | https://www.boonecounty.iowa.gov/files/county_ordinances/142_health_and_sanitation_806.pdf
Iowa | Cedar | 19031 | Definition: Well |  |  | "Well" means any excavation that is drilled, cored, driven, dug, bored, augered, jetted, washed or is otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. "Well" does not include ... lateral geothermal heat exchange systems less than 20 feet deep ... | 567--49.2(455B) Definitions | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Definition: Geothermal Heat Pump |  |  | "Closed circuit vertical heat exchangers. These provisions apply to closed circuit vertical heat exchanger construction." | 567-49.29(455B) Closed circuit vertical heat exchangers | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Property Lines | 4 | feet | Table 49.6(1): "Property lines (unless a mutual easement is signed and recorded by both parties)" — minimum lateral distance "4" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Wastewater | 1000 | feet | Table 49.6(1): "Earthen manure storage basin, runoff control basins and anaerobic lagoons" — "1000" feet; "Domestic wastewater lagoon" — "400" feet; "Sanitary landfills" — "1000" feet; "Soil absorption field, any sewage treatment system with an open discharge, pit privy or septic tank discharge line" — "100" feet; and "Septic tank, concrete vault privy" — "50" feet. Rule 49.6(2) provides an exception reducing the lagoon/basin distance to "400 feet" in specified cases. | 49.6(1) Minimum distances; 49.6(2) Exception to minimum lateral distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Public Water | 400 | feet | Table 49.6(1): "Public water supply well" — minimum lateral distance "400" feet for shallow wells and "200" feet for deep wells. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Animal Enclosures | 200 | feet | Table 49.6(1): "Formed manure storage structure, confinement building, feedlot solids settling facility, open feedlot" — minimum lateral distance "200" feet for shallow wells and "100" feet for deep wells. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Fuel (above ground) | 100 | feet | Table 49.6(1): "Liquid hydrocarbon storage tanks" — minimum lateral distance "100" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Water Lines | 10 | feet | Table 49.6(1): "Hydrants" — minimum lateral distance "10" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Sewer Lines | 50 | feet | Table 49.6(1): "Sewer of tightly joined tile or equivalent material, sewer-connected foundation drain, or sewers under pressure" — "50" feet; and "Sewer of cast iron with leaded or mechanical joints, sewer of plastic pipe with glued or compression joints" — "10" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Water Bodies | 25 | feet | Table 49.6(1): "Ditches, streams, ponds, or lakes" — minimum lateral distance "25" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table 49.6(1): "Preparation or storage area for spray materials, commercial fertilizers or chemicals that may result in groundwater contamination" — minimum lateral distance "100" feet. | 49.6(1) Minimum distances | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Minimum Well Depth | 60 | feet | "In no case shall less than 20 feet of permanent casing be installed in wells drilled in unconsolidated materials. If the alluvial aquifer where the water is to be drawn from is covered by less than 40 feet of low permeability materials, the well screen shall be set at the bottom of the water-bearing aquifer or at least 60 feet from the surface." | 49.8(1)a.(1) Depth | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Permit |  |  | County ordinance: "No water well shall be constructed in Cedar County without a permit first being obtained from the Cedar County Environmental Health Department before construction begins." State rule: "No well construction or reconstruction shall be initiated until a permit has been issued by the proper authority." | CEDAR COUNTY ORDINANCE NUMBER 27; 567-49.4(455B) General | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Inspection |  |  | "The administrative authority shall have the authority to visit wellsites during any phase of the work without prior notice." | 567-49.4(455B) General | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Licensed Driller |  |  | "All well services shall be performed by a certified well contractor or the property owner as specified in 567-Chapter 82." Also, "'Well driller' means a person certified by the department to perform well drilling services." | 567-49.4(455B) General | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Certification |  |  | "'Well driller' means a person certified by the department to perform well drilling services." | 567--49.2(455B) Definitions | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Cedar | 19031 | Decommissioning |  |  | "Abandoned wells shall be properly plugged as required in 567-Chapter 39." | 567-49.28(455B) Abandonment of wells | 2016 | https://cedarcounty.iowa.gov/files/county_ordinances/nonpublic_water_supply_wells_construction.pdf
Iowa | Dallas | 19049 | Definition: Well |  |  | "Geothermal Heat Pump Well" means an excavation exceeding a 20-ft depth that is drilled, cased, bored, augured, washed, driven, dug, jetted, or otherwise constructed for the purpose of utilizing the geothermal properties of the ground. | II. 32.02 Definitions |  | https://www.dallascountyiowa.gov/408/Private-Well-Information
Iowa | Dallas | 19049 | Permit |  |  | "Permit required. When obtaining a permit to install a geothermal heat pump system, the contractor or homeowner must apply for a permit within the Dallas County Health Department prior to construction." | IV. 32.04 Additional Requirements for Geothermal Heat Pump Wells |  | https://www.dallascountyiowa.gov/408/Private-Well-Information
Iowa | Dallas | 19049 | Inspection |  |  | "Notify County Sanitarian. The driller shall notify the County Sanitarian prior to the burial of any geothermal loops for the purpose of inspection." | IV. 32.04 Additional Requirements for Geothermal Heat Pump Wells |  | https://www.dallascountyiowa.gov/408/Private-Well-Information
Iowa | Hancock | 19081 | Definition: Well |  |  | 'Well' means any excavation that is drilled, cored, driven, dug, bored, augered, jetted, washed or is otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems less than 20 feet deep. | 567-49.2(455B) Definitions | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Setback - Property Lines | 4 | feet | Table 49.6(1) lists 'Property lines (unless a mutual easement is signed and recorded by both parties)' with a minimum lateral distance of '4' feet for 'All Wells.' | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Setback - Wastewater | 1000 | feet | Table 49.6(1) requires setbacks for wastewater-related sources, including 'Earthen manure storage basin, runoff control basins and anaerobic lagoons ... 1000' feet; 'Domestic wastewater lagoon ... 400' feet; 'Soil absorption field, any sewage treatment system with an open discharge, privy or septic tank discharge line ... 100' feet; and 'Septic tank, concrete vault privy ... 50' feet. Rule 49.6(2) states an exception: 'The minimum separation distance between a well and an anaerobic lagoon, earthen manure slurry storage basin, earthen manure storage basin, or runoff control basin shall be 400 feet' in specified cases. | 49.6(1) Minimum distances; 49.6(2) Exception to minimum lateral distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Setback - Public Water | 400 | feet | Table 49.6(1) lists 'Public water supply well' with minimum lateral distances of '400' feet for shallow wells and '200' feet for deep wells. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Setback - Fuel (above ground) | 100 | feet | Table 49.6(1) lists 'Liquid hydrocarbon storage tanks' with a minimum lateral distance of '100' feet for all wells. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Setback - Sewer Lines | 50 | feet | Table 49.6(1) lists 'sewer of tightly joined tile or equivalent material, sewer-connected foundation drain, or sewers under pressure' at '50' feet, and 'Sewer of cast iron with leaded or mechanical joints, sewer of plastic pipe with glued or compression joints' at '10' feet. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Setback - Water Bodies | 25 | feet | Table 49.6(1) lists 'Ditches, streams, ponds, or lakes' with a minimum lateral distance of '25' feet for all wells. | 49.6(1) Minimum distances, Table 49.6(1) Minimum Lateral Distances | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Minimum Well Depth | 60 | feet | 'In no case shall less than 20 feet of permanent casing be installed in wells drilled in unconsolidated materials. If the alluvial aquifer where the water is to be drawn from is covered by less than 40 feet of low permeability materials, the well screen shall be set at the bottom of the waterbearing aquifer or at least 60 feet from the surface.' | 49.8(1)a(1) Drilled wells in unconsolidated materials — Depth | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Permit |  |  | 'No well construction or reconstruction shall be initiated until a permit has been issued by the proper authority.' The administrative authority 'shall by rule require the issuance of permits.' | 567-49.4(455B) General | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Inspection |  |  | 'The administrative authority shall have the authority to visit well sites during any phase of the work without prior notice.' | 567-49.4(455B) General | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Licensed Driller |  |  | 'All well services shall be performed by a certified well contractor or the property owner as specified in 567-Chapter 82.' Also, 'Well driller' means 'a person certified by the department to perform well drilling services.' | 567-49.4(455B) General | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Hancock | 19081 | Decommissioning |  |  | 'Abandoned wells shall be properly plugged as required in 567-Chapter 39.' Also, 'Under no circumstances shall abandoned wells be used for the disposal of debris, solid waste, septic tank sludge or effluents, or for any other type of unauthorized disposal of waste materials, or as a receptacle for field tile drainage.' | 567-49.28(455B) Abandonment of wells | 2004 | https://hancockcountyia.gov/files/environmental_health/iowa_administrative_code_chapter_49_33365.pdf
Iowa | Johnson | 19103 | Definition: Well |  |  | 'Well' means any excavation that is drilled, cored, driven, dug, bored, augered, jetted, washed or is otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems less than 20 feet deep. | 567-49.2(455B) Definitions | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Setback - Property Lines | 4 | feet | Table 49.6(1) requires a minimum lateral distance from 'Property lines' of '4' feet, with footnote '1 Unless a mutual easement is signed and recorded by both parties.' | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Setback - Wastewater | 1000 | feet | Table 49.6(1) requires setbacks from multiple wastewater-related sources, including 'Earthen manure storage basin, runoff control basins and anaerobic lagoons' at '1000' feet; 'Domestic wastewater lagoon' at '400' feet; and 'Soil absorption field, any sewage treatment system with an open discharge, pit privy or septic tank discharge line' at '100' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Setback - Public Water | 400 | feet | Table 49.6(1) lists 'Public water supply well' with minimum lateral distances of '400' feet for a shallow well and '200' feet for a deep well. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Setback - Fuel (above ground) | 100 | feet | Table 49.6(1) lists 'Liquid hydrocarbon storage tanks' with a minimum lateral distance of '100' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Setback - Sewer Lines | 10 | feet | Table 49.6(1) lists 'Sewer of tightly joined tile or equivalent material, sewer-connected foundation drain, or sewers under pressure' and 'Sewer of cast iron with leaded or mechanical joints, sewer of plastic pipe with glued or compression joints' with a minimum lateral distance of '10' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Setback - Water Bodies | 25 | feet | Table 49.6(1) lists 'Ditches, streams, ponds, or lakes' with a minimum lateral distance of '25' feet. | 567-49.6(455B) Location of wells; Table 49.6(1) Minimum Lateral Distances | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Permit |  |  | 'The administrative authority shall by rule require the issuance of permits ... No well construction or reconstruction shall be initiated until a permit has been issued by the proper authority.' | 567-49.4(455B) General | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Inspection |  |  | 'The administrative authority shall have the authority to visit well sites during any phase of the work without prior notice.' Also, for vertical heat exchangers, 'Piping must be pressure-tested with air or potable water for 15 minutes at a pressure of 1.5 times the system operating pressure after installation in the borehole.' | 567-49.4(455B) General; 567-49.29(455B) Closed circuit vertical heat exchangers | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Licensed Driller |  |  | 'All well services shall be performed by a certified well contractor or the property owner as specified in 567-Chapter 82.' Also, 'Well driller' means 'a person certified by the department to perform well drilling services.' | 567-49.4(455B) General | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Certification |  |  | 'Well driller' means 'a person certified by the department to perform well drilling services.' 'Pump installer' means 'a person certified by the department to perform pump services.' | 567-49.2(455B) Definitions | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Johnson | 19103 | Decommissioning |  |  | 'Abandoned wells shall be properly plugged as required in 567-Chapter 39.' | 567-49.28(455B) Abandonment of wells | 2009 | https://www.johnsoncountyiowa.gov/sites/default/files/2020-04/Nonpublic%20Water%20Supply%20Regulations.pdf
Iowa | Mahaska | 19123 | Setback - Private Water | 100 | feet | Table I lists minimum distances for on-site wastewater systems from "Private water supply well" as "50" feet for the closed portion and "100" feet for the open portion of the treatment system. | 2.4: Minimum Distances | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska | 19123 | Setback - Public Water | 200 | feet | Table I lists minimum distances for on-site wastewater systems from "Public water supply well" as "200" feet for both the closed and open portions of the treatment system. | 2.4: Minimum Distances | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska | 19123 | Permit |  |  | "No on-site wastewater treatment and disposal system shall be installed, altered, expanded or repaired until an application for a permit has been submitted and a permit issued by the Mahaska County Board of Health or the Administrative Authority." | 1.4: Permit Requirements | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska | 19123 | Inspection |  |  | "No on-site wastewater treatment system shall be covered so as to deny final inspection by the Administrative Authority" and "No on-site wastewater treatment system for which a permit has been issued shall be put into operation until the construction, repair, alteration, or remodeling shall have been inspected and approved by the Administration Authority." | 1.4: Permit Requirements | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Mahaska | 19123 | Decommissioning |  |  | "All primary treatment sections of the sewage disposal facilities (vault or septic tank) replaced by connections to a publicly operated sewage system or when an existing sewage disposal facility is replaced or use discontinued, shall be abandoned as specified by the Administrative Authority. No sewage disposal facilities shall be abandoned until the pumping contractor has cleaned said sewage disposal facilities." | 1.8: Abandonment of an On-Site Wastewater Treatment and Disposal System | 2020 | https://www.mahaskacountyia.gov/files/board_of_supervisors/2020_ordinances_41669.pdf
Iowa | Marion | 19125 | Permit |  |  | "When obtaining a permit to install a geothermal heat pump system, the contractor or homeowner must apply for a permit within the County EH Department office prior to construction." The section also states: "The fee for obtaining a permit to install the system shall be set by the Board of Health. The additional IDNR fee still applies." | 43.07 CLOSED CIRCUIT VERTICAL HEAT EXCHANGERS |  | https://codelibrary.amlegal.com/codes/marioncounty/latest/marioncounty_ia/0-0-0-658
Iowa | Marion | 19125 | Inspection |  |  | The ordinance requires multiple inspections: "The Department shall be given no less than 24-hour notice to perform a pre-site inspection of the flagged area prior to well construction"; "The Department shall be given no less than 24-hour notice that the drilling process has begun to perform an on-site drilling inspection"; and "The Department shall be notified no less than 24 hours prior to pressurization of the system with the State approved antifreeze solution on-site during the final hook up, to perform a final inspection." | 43.07 CLOSED CIRCUIT VERTICAL HEAT EXCHANGERS |  | https://codelibrary.amlegal.com/codes/marioncounty/latest/marioncounty_ia/0-0-0-658
Iowa | Story | 19169 | Permit |  |  | Section 65.11 requires an application for a septic construction permit to include a site evaluation/design and other materials. Section 65.17 states: "Site evaluations are required prior to issuance of a construction permit." Section 65.24 provides that the site evaluation report must include a "Diagram showing the location and setbacks of existing/proposed water wells, geothermal wells, horizontal geothermal loops..." | 65.11 DOCUMENTS NEEDED FOR SEPTIC CONSTRUCTION PERMIT; 65.17 SITE EVALUATION; 65.24 SEPTIC CONSTRUCTION PERMIT TO BE ISSUED BY EH | 2021 | https://www.storycountyiowa.gov/DocumentCenter/View/11613/Signed-Ordinance-287
Iowa | Warren | 19181 | Definition: Well |  |  | "'Geothermal Heat Pump Well' means an excavation exceeding a 20-ft depth that is drilled, cased, bored, augured, washed, driven, dug, jetted, or otherwise constructed for the purpose of utilizing the geothermal properties of the ground." | 33.02 Definitions | 2021 | https://www.warrencountyia.gov/wp-content/uploads/2022/10/Chapter33.pdf
Iowa | Warren | 19181 | Permit |  |  | "Permit required. When obtaining a permit to install a geothermal heat pump system, the contractor or homeowner must apply for a permit within the Warren County Environmental Health Office prior to construction." | 33.04 Geothermal Heat Pump Wells | 2021 | https://www.warrencountyia.gov/wp-content/uploads/2022/10/Chapter33.pdf
Kansas | Stafford | 20185 | Definition: Geothermal |  |  | "RENEWABLE ENERGY : Shall include wind (CWEP), solar (CSEP), battery (CESS) & (BESS), photovoltaic, biomass, hydropower, geothermal and landfill gas resources or technologies." | Section 2-102 / Renewable Energy definition | 2026 | https://www.staffordcounty.org/uploads/1/3/3/6/133660997/updated_zoning_regulations_2026.pdf
Maryland | Anne Arundel | 24003 | Definition: Geothermal Heat Pump |  |  | "In this section, 'geothermal energy device' means a heating or cooling device that is installed using ground loop technology." | § 4-2-310. Geothermal energy | 2020 | https://codelibrary.amlegal.com/codes/annearundel/latest/annearundelco_md/0-0-0-151648
Maryland | Baltimore | 24005 | Definition: Geothermal Heat Pump |  |  | 'Geothermal energy device' means an energy device that: (a) Uses geothermal energy to heat or cool a structure or to provide hot water for use in the structure; and (b) Meets national safety and performance standards set by a nationally recognized testing laboratory for that type of device. | .01 Definitions | 2014 | https://www.baltimorecountymd.gov/files/Documents/Law/COBAR/cobarenergyconservdeviceschapter5.pdf
Maryland | Baltimore | 24005 | Permit |  |  | The applicant shall provide copies of: '(1) Receipts of all expenses paid for the purchase and installation of the energy conservation device or system; and (2) Any electrical, plumbing or other permits required by the county for the installation of the energy conservation device or system.' | .03 Administration | 2014 | https://www.baltimorecountymd.gov/files/Documents/Law/COBAR/cobarenergyconservdeviceschapter5.pdf
Maryland | Frederick | 24021 | Definition: Geothermal |  |  | "The following improvements, either new or replacement, to commercial properties qualify as energy efficiency projects or renewable energy projects under the Clean Energy Loan Program: ... (2) Geothermal energy devices" | § 1-8-454 QUALIFYING IMPROVEMENTS AND COSTS | 2016 | https://www.frederickcountymd.gov/DocumentCenter/View/373451/2016---Bill-No-16-17---Establishing-a-Clean-Energy-Loan-Program-for-Commercial-Properties
Maryland | Harford | 24025 | Definition: Geothermal Heat Pump |  |  | "Nonwater-dependent projects include: ... (5) A small-scale renewable energy system on a pier, including: ... (b) A geothermal energy system and its geothermal heat exchanger or other necessary equipment." | NONWATER-DEPENDENT PROJECT | 2024 | https://ecode360.com/9375535
Maryland | Prince George's | 24033 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy Device" means an energy conserving device that: (i) uses geothermal energy to heat or cool a structure or to provide hot water for use in the structure; and (ii) meets national safety and performance standards set by a nationally recognized testing laboratory for that kind of device. | Sec. 10-235.06(b)(2) | 2008 | https://www.princegeorgescountymd.gov/sites/default/files/media-document/dcv2184.pdf
Michigan | Alger | 26003 | Definition: Well |  |  | "Well" means "An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." The definition expressly includes "A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Alger | 26003 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and "shall be constructed in accordance with Michigan Water Well Construction and Pump Installation Code, Ground Water Quality Control (R325.1601 et seq.) ... and the Upper Peninsula of Michigan Geothermal Technical Guidance document." | 5-14 Geothermal Wells | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Arenac | 26011 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Baraga | 26013 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Baraga | 26013 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Baraga | 26013 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Baraga | 26013 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Benzie | 26019 | Definition: Well |  |  | 'Well' means a man-made opening in the surface of the earth used for the purpose of removing ground water. Wells, regulated by this Code, include: ... 'd. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formation for heating or air conditioning.' | Section 2.45 WELL | 2023 | https://www.bldhd.org/media/uploads/Environmental%20Health%20Form/bldhd_-_district_sanitary_code_(1-27-2023).pdf
Michigan | Cass | 26027 | Definition: Well |  |  | 'Well - Means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations or removing ground water for any purpose.' The definition further states: 'A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning.' | 3-42 Well | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass | 26027 | Permit |  |  | Section 9-4(B) expressly states that a 'water supply construction permit will not be required for ... A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning.' Section 9-4(C) adds: 'All Wells within a Restricted Zone must comply with Section 9-16 regulating Groundwater Use Restricted Zones regardless of whether a construction permit is required.' In the West KLA Landfill GRZ appendix, 'All Wells within the GRZ must be approved by EGLE or U.S. EPA, and the Health Department.' | 9-4 Water Supply Construction Permit Required | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass | 26027 | Inspection |  |  | The appendix states: 'Existing and new wells will be monitored by the RZ Applicant (the KLA Group) to ensure that the concentration of 1,4-dioxane ... remains below one half of its Michigan drinking water criterion.' | West KLA Landfill Groundwater Restricted Zone (GRZ) - Additional Requirements Specific to this GRZ | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass | 26027 | Decommissioning |  |  | Section 9-16(H) states: 'Any existing Well, the use of which is prohibited by Paragraph (E) and not granted an exception by Paragraph (F) shall be abandoned ... Any non-conforming Well shall be abandoned within 30 days following establishment of the Restricted Zone.' The GRZ appendix also states: 'Potable supply Wells that are replaced are to be properly abandoned in accordance with the Environmental Health Code.' | 9-16(H) Abandonment of Non-Conforming Wells; West KLA Landfill GRZ - Additional Requirements Specific to this GRZ | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Cass | 26027 | Other Prohibitions/Regulations |  |  | Section 9-16(E) provides: 'After the effective date of this Amendment, no Well may be installed, utilized, or allowed, permitted, or otherwise provided for on any Affected Premises. The use of any Well on an Affected Premises or the use of groundwater derived from an Affected Premise is prohibited.' Section 9-16(B)(11)(c) defines 'Heat Exchange Well' as 'a well for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning.' Section 9-16(F) creates only limited exceptions, including: 'Agency Approved Heat Exchange Well: If EGLE determines that the use of a Well for loop geothermal heating/cooling ... will not allow for exposure to contamination or cause migration or exacerbation of Contaminated Groundwater ... such use of the Well under terms and conditions specified by EGLE will be allowed.' | 9-16(E) Prohibition of Wells and Groundwater Use Within a Restricted Zone; 9-16(F) Exceptions | 1997 | https://vbcassdhd.org/wp-content/uploads/2025/03/ENVIRONMENTAL-HEALTH-CODE-2025-1.pdf
Michigan | Clare | 26035 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Delta | 26041 | Definition: Well |  |  | "Well" means "[a]n opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." The definition expressly includes "[a] heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. Includes both supply and return wells and the vertical boreholes for closed loop systems." | SECTION 6.1 DEFINITIONS | 2009 | https://cms3.revize.com/revize/deltapublichealth/Documents/Department/Environmental%20Health/On%20Site%20Sewage/PHDM%20Sanitary%20Code.pdf
Michigan | Delta | 26041 | Permit |  |  | "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply ... without first obtaining a water supply construction permit from the department." Because Section 6.1 defines a well to include "[a] heat exchange well ... for heating or air conditioning" and "the vertical boreholes for closed loop systems," this permit requirement applies to geothermal heat exchange wells within that defined term. | SECTION 6.3 PERMITS / 6.3.2 Construction Permits | 2009 | https://cms3.revize.com/revize/deltapublichealth/Documents/Department/Environmental%20Health/On%20Site%20Sewage/PHDM%20Sanitary%20Code.pdf
Michigan | Delta | 26041 | Inspection |  |  | Section 6.9.1 states: "The department may inspect the water system construction or well drilling process." It also provides: "An inspection of a new or extensively changed water supply system may be required by the department before the system is put into use." Section 6.9.2 adds that "[t]he final approval of a water supply system shall not be granted until ... [a]n on-site inspection has been conducted and the water supply system is found to be in compliance with this regulation, applicable codes, and permit requirements." Because Section 6.1 includes geothermal "heat exchange well[s]" and closed-loop boreholes within 'well,' these inspection provisions can govern geothermal exchange-well construction. | SECTION 6.9 WELL INSPECTION AND APPROVAL / 6.9.1 Inspection and 6.9.2 Approval | 2009 | https://cms3.revize.com/revize/deltapublichealth/Documents/Department/Environmental%20Health/On%20Site%20Sewage/PHDM%20Sanitary%20Code.pdf
Michigan | Genesee | 26049 | Definition: Well |  |  | "Well" means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include, but are not limited to: ... "A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | SECTION 4.01 - DEFINITIONS; SECTION 4.013 - WELL | 1999 | https://www.geneseecountymi.gov/departments/health_department/services/environmental_health/environmental_health_regulations.php
Michigan | Gladwin | 26051 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Gogebic | 26053 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gogebic | 26053 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply ... without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gogebic | 26053 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Gogebic | 26053 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368"; "The plugging of any well or dry hole on a parcel containing a well that serves the public, or a residence other than that of the owner, shall be plugged by a State of Michigan registered well-drilling contractor"; and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton | 26061 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton | 26061 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton | 26061 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Houghton | 26061 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Isabella | 26073 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Kalamazoo | 26077 | Definition: Well |  |  | 'Well' means an opening in the surface of the earth for the purpose of removing fresh water for a water supply well, test well, irrigation well, recharge well, industrial well, and heat exchange well. | SECTION 3.92 | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo | 26077 | Definition: Geothermal Heat Pump |  |  | 'Heat exchange well' means a well for the purpose of utilizing the geothermal properties of earth formations for heating or cooling. | SECTION 3.39 | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo | 26077 | Permit |  |  | 'Additionally, no person shall construct a heat exchange well, industrial well, irrigation well, recharge well, or test well where the installed pumping equipment produces less than 70 gallons per minute without obtaining a water supply system construction permit from the Department.' | SECTION 14.03: PERMIT FOR WATER SUPPLY SYSTEMS | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo | 26077 | Inspection |  |  | 'The Department shall inspect all new water supply system installations to determine if the construction complies with the provisions of this Code.' | SECTION 14.10: INSPECTION AND APPROVAL | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kalamazoo | 26077 | Other Prohibitions/Regulations |  |  | CHAPTER 24b states: 'Except as provided in CHAPTER 25b of this Code, no person shall install or utilize, or allow, permit, or provide for the installation or utilization of a well in any Restricted Zone. Except as provided in CHAPTER 25b of this Code, no person shall use any groundwater from any well located within a Restricted Zone.' SECTION 25b.06 further states: 'After the establishment of a Restricted Zone under this Code, the Department an individual shall not install a new well to be used for noncontact heating, cooling or processing activities within a Restricted Zone unless all of the following conditions are present...' | CHAPTER 24b; SECTION 25b.06 | 2025 | https://www.kalcounty.gov/DocumentCenter/View/840/Kalamazoo-County-Sanitary-Code-PDF.pdf
Michigan | Kent | 26081 | Definition: Well |  |  | "'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states wells include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 2.13 - Well | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent | 26081 | Permit |  |  | Section 7.0: "No person shall begin construction of a new water supply, or make extensive changes to existing water supplies, without first obtaining a water supply construction permit from the Kent County Health Department." Section 8.0: "If multiple wells of a similar nature are proposed to be constructed for the same project, a single project permit may be issued to cover all of the wells in the project." Section 12.1: "The Health Officer may issue a water supply construction permit..." and "may impose limitations or conditions..." Section 17.0: in emergencies, "a registered well driller may begin extensive changes to or construction of a new water supply without prior notification or without first obtaining a permit," but "must contact the Health Officer on the next regular working day to obtain a permit." | SECTION 7.0 - WATER SUPPLY CONSTRUCTION PERMIT REQUIRED; SECTION 8.0 - PROJECT PERMIT; Section 12.1 - Issuance; Section 17.0 - Emergency Conditions | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent | 26081 | Inspection |  |  | Section 14.0: "The Health Officer may inspect water supplies during and/or after completion of construction, as determined necessary by the Health Officer." Section 15.0 provides that "A new water supply shall not be placed into service until the construction and installation have been approved by the Health Officer" and requires that "An on-site inspection has been completed by the Health Officer, and the water supply is found to be in compliance with applicable regulations and permit requirements." | SECTION 14.0 - INSPECTION; SECTION 15.0 - APPROVAL | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent | 26081 | Licensed Driller |  |  | In an emergency, "a registered well driller may begin extensive changes to or construction of a new water supply without prior notification or without first obtaining a permit. However, the well driller must contact the Health Officer on the next regular working day to obtain a permit..." | SECTION 17.0 - EMERGENCY CONDITIONS | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Kent | 26081 | Decommissioning |  |  | "The Health Officer may require the proper abandonment of a well that is constructed without a permit or is constructed in violation of these regulations or permit requirements." | SECTION 11.0 - PLUGGING OF WELL | 1996 | https://www.kentcountymi.gov/DocumentCenter/View/1688/Kent-County-Water-Supply-Regulations-PDF
Michigan | Keweenaw | 26083 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Keweenaw | 26083 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Keweenaw | 26083 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Keweenaw | 26083 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Leelanau | 26089 | Definition: Well |  |  | 'Well' means a man-made opening in the surface of the earth used for the purpose of removing ground water. Wells, regulated by this Code, include: ... 'd. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formation for heating or air conditioning.' | Section 2.45 WELL | 2023 | https://www.bldhd.org/media/uploads/Environmental%20Health%20Form/bldhd_-_district_sanitary_code_(1-27-2023).pdf
Michigan | Luce | 26095 | Definition: Well |  |  | "Well" means "[a]n opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." It further states wells include "[a] heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Luce | 26095 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and "shall be constructed in accordance with Michigan Water Well Construction and Pump Installation Code..." | 5-14 Geothermal Wells | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Luce | 26095 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "[a]n inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." Because 5-14 provides that "Vertical closed-loop geothermal wells shall be permitted as a water well," these water-well inspection provisions apply to those geothermal wells when permitted as water wells. | 5-3.2 Construction Permits; 5-9.1 Inspection | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Luce | 26095 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." Also, "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac | 26097 | Definition: Well |  |  | "Well" means "An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." It expressly includes "A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac | 26097 | Permit |  |  | Section 5-14 states: "Vertical closed-loop geothermal wells shall be permitted as a water well." Section 5-3.2 adds: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells; 5-3.2 Construction Permits | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac | 26097 | Inspection |  |  | Section 5-3.2(H) states: "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Mackinac | 26097 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "The plugging of any well or dry hole on a parcel containing a well that serves the public, or a residence other than that of the owner, shall be plugged by a State of Michigan registered well-drilling contractor." | 5-16 Well Abandonment and Plugging | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Monroe | 26115 | Definition: Well |  |  | "'Well' is defined as an opening in the surface of the earth for the purpose of: obtaining groundwater, monitoring the quality or quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations or removing groundwater for any purpose. Wells as defined in this section shall include: ... (c) A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning;" | 300.10 Well |  | https://www.co.monroe.mi.us/DocumentCenter/View/745/Chapter-3-of-the-Monroe-County-Environmental-PDF
Michigan | Ontonagon | 26131 | Definition: Well |  |  | "Well - An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose. Wells, as defined in this Section, include but are not limited to: ... 4. A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ontonagon | 26131 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and Section 5-3.2(A) states: "No person shall begin construction of a well or water supply or make an extensive change to an existing water supply without first obtaining a water supply construction permit from the Department." | 5-14 Geothermal Wells | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ontonagon | 26131 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9 Well Inspection and Approval | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Ontonagon | 26131 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." and "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2021 | https://www.wupdhd.org/wp-content/uploads/2020/11/U.P.-Envronmental-Health-Code-Current-Draft.pdf
Michigan | Osceola | 26133 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Schoolcraft | 26153 | Definition: Well |  |  | "Well" means "An opening in the surface of the earth for the purpose of obtaining groundwater, monitoring the quality and quantity of groundwater, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing groundwater for any purpose." It expressly includes "A heat exchange well used for the purpose of utilizing the geothermal properties of the earth formations for heating or air conditioning. This includes both supply and return wells and vertical bore holes for closed-loop systems." | 5-2 Technical Definitions | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Schoolcraft | 26153 | Permit |  |  | "Vertical closed-loop geothermal wells shall be permitted as a water well" and shall be constructed in accordance with listed state code and guidance documents. | 5-14 Geothermal Wells | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Schoolcraft | 26153 | Inspection |  |  | Section 5-3.2(H): "An on-site inspection conducted by the Department during construction or portions thereof may be required as part of the water supply construction permit." Section 5-9.1 adds: "The Department may inspect the water supply system construction or well drilling process" and "An inspection of a new or extensively changed water supply system may be required by the Department before the system is put into use." | 5-3.2 Construction Permits; 5-9.1 Inspection | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Schoolcraft | 26153 | Decommissioning |  |  | "Any abandoned well, dry hole, or well that has been determined to be contaminated or to be a safety hazard shall be plugged in accordance with Part 127 of Act 368..." Also, "When a replacement well has been permitted and constructed, the existing well previously in service shall be abandoned and plugged unless remaining active and serving a beneficial use, or unless placed in a temporarily abandoned status..." | 5-16 Well Abandonment and Plugging | 2022 | https://www.lmasdhd.org/wp-content/uploads/2025/05/UPEHC-Final.pdf
Michigan | Shiawassee | 26155 | Definition: Well |  |  | "Well means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... f) A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 400.13 - WELL | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee | 26155 | Permit |  |  | "No person shall begin construction of a new water supply, or make extensive changes to existing water supplies, without first obtaining a Water Supply Construction Permit from the Shiawassee County Health Department." Section 400.13 defines a well to include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | SECTION 450 - WATER SUPPLY CONSTRUCTION PERMIT REQUIRED | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee | 26155 | Inspection |  |  | Section 493: "The Health Officer may make inspections of water supplies during and/or after completion of construction as deemed necessary." Section 494(a): "A new water supply shall not be approved by the Health Officer until ... An on-site inspection has been completed by the Health Officer, and the water supply is found to be in compliance with applicable code and permit requirements." | SECTION 493 - INSPECTION; SECTION 494 - APPROVAL | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee | 26155 | Licensed Driller |  |  | "...when the well driller is involved with repair work and it is deemed necessary to begin construction immediately on a new well, a registered well driller may begin extensive changes to or construction of a new water supply without notification or permit." | SECTION 496 - EMERGENCY CONDITIONS | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Michigan | Shiawassee | 26155 | Certification |  |  | "...a registered well driller may begin extensive changes to or construction of a new water supply without notification or permit." | SECTION 496 - EMERGENCY CONDITIONS | 1997 | https://shiawasseechd.net/wp-content/uploads/Sanitary-Code.pdf
Minnesota | Carver | 27019 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | § 152.010 DEFINITIONS. | 2024 | https://codelibrary.amlegal.com/codes/carvercounty/latest/carverco_mn/0-0-0-3098
Minnesota | Hubbard | 27057 | Definition: Geothermal Heat Pump |  |  | "Geothermal energy system. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." | Section 111. Definitions as Used in this Ordinance | 2024 | https://www.co.hubbard.mn.us/uploads/dm/16109/County_Ordinance_Number_17_Shoreland.pdf
Minnesota | Hubbard | 27057 | Permit |  |  | "Installation of geothermal energy systems shall be allowed per the following requirements. No additional permitting shall be required if a current dwelling permit is in place and the following standards are met:" and "If a current dwelling permit is in place, no additional permit shall be required." | Section 512. Geothermal Energy Systems | 2024 | https://www.co.hubbard.mn.us/uploads/dm/16109/County_Ordinance_Number_17_Shoreland.pdf
Minnesota | Hubbard | 27057 | Other Prohibitions/Regulations |  |  | Section 512 requires that for geothermal systems, "All parts of the system (except for a water discharge pipe on an open loop geothermal energy system) must be located behind the required structure setback from the ordinary high water mark." It further allows parts "in the area between the ordinary high water mark and structure setback" only when "the installation of the system parts complies with Section 902" and "the structure serviced by the system is a legal nonconformity in terms of its ordinary high water mark structure setback." | Section 512. Geothermal Energy Systems | 2024 | https://www.co.hubbard.mn.us/uploads/dm/16109/County_Ordinance_Number_17_Shoreland.pdf
Minnesota | Winona | 27169 | Permit |  |  | "A Land Disturbance Permit, located in Chapter 6 is required for the following situations when installing a Geothermal Energy System: a. When there is to be excavation or filling of land that would deprive an adjoining property owner of lateral support. b. When there is to be excavation of earthen material of more than one thousand (1,000) cubic yards, for the installation of a geothermal heat pump system. 1. When there is to be excavation of earthen material, for the installation of a geothermal heat pump system located within Shoreland, Floodplain, or on steep slopes as described in Chapter 11." | 12.4.1 Land Disturbance Permit | 2011 | https://www.winonacounty.gov/DocumentCenter/View/580/WCZO-Amendment---Renewable-Energy---Approved-June-28-2011-PDF
Montana | Lake | 30047 | Permit |  |  | Section 3-1(A): "No person(s) may proceed with any construction work, landscape modification, or maintenance which alters or disturbs the lakeshore protection zone... until she/he has obtained and has physical possession of a valid 'Lakeshore Construction Permit' issued by the governing body." Section 3-4(A): "Any work, including maintenance, which will temporarily or permanently alter, diminish, or increase the course, current or cross-sectional area of the lakeshore protection zone must first be secured by a permit from the governing body before any work is commenced." | Section 3-1 General Requirements; Section 3-4 Work for Which a Permit is Required | 2024 | https://www.lakemt.gov/DocumentCenter/View/2951/Lake-County-Lakeshore-Protection-Regulations-amended-8-2024-pdf
Montana | Lake | 30047 | Inspection |  |  | Section 3-2(A): "the governing body, the planning board, or the planning staff may conduct investigations, examinations and site evaluations... to observe and monitor construction, and/or to evaluate completed projects for compliance with approved plans." Section 5-2(N): "The applicant or his/her authorized agent shall notify the planning staff when an approved project is completed. The planning staff will then be able to initiate onsite evaluation of the project in order to assure that the project is compliant with approved plans, 'Conditions of Approval', and 'Lake County Lakeshore Protection Regulations'." | Section 3-2 Permission to Enter; Section 5-2(N) | 2024 | https://www.lakemt.gov/DocumentCenter/View/2951/Lake-County-Lakeshore-Protection-Regulations-amended-8-2024-pdf
Montana | Lake | 30047 | Other Prohibitions/Regulations |  |  | Section 5-3(N)(2)(a): "No geothermal system shall be located within the lakeshore protection zone." Section 5-3(N)(2)(b): "Geothermal heating systems that make use of the lake are prohibited." | Section 5-3(N) Geothermal Heating Systems | 2024 | https://www.lakemt.gov/DocumentCenter/View/2951/Lake-County-Lakeshore-Protection-Regulations-amended-8-2024-pdf
Montana | Lewis and Clark | 30049 | Permit |  |  | "Renewable Energy Facilities" are listed as conditional uses in RR and SR. RR §704 states: "The following uses are permitted, upon approval of a Conditional Use Permit (CUP) by the Board of Adjustment (BOA), in accordance with Section 14, of these Regulations ... 704.40 Renewable Energy Facilities." SR §804 likewise states: "The following uses are permitted, upon approval of a Conditional Use Permit (CUP) by the Board ... 804.42 Renewable Energy Facilities." Section 3 defines "Renewable Energy Facility" as "A site, together with its accessory facilities, where energy is generated using renewable resources. Such sites may include but are not limited to solar farms, wind turbines, or geothermal facilities." | SECTION 7 Rural Residential Mixed-Use District (RR) / SECTION 8 Suburban Residential Mixed-Use District (SR) | 2022 | https://www.lccountymt.gov/files/assets/county/v/1/government/commission-bocc/documents/resolutions/2022/resolution_2022-113.pdf
Montana | Sanders | 30089 | Definition: Well |  |  | "(K) Wells: an excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed and includes any related system(s) of pumps, pipes, controls, reservoirs, or mechanical devices used for the purpose(s) of: location, diversion, artificial recharge, acquisition of groundwater or for any other similar purpose. (1) 'Well' includes, but is not limited to: ... (b) Heat exchange well: well used for extracting or injecting groundwater for heating or air conditioning purposes." | 2. Definitions and Acronyms | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders | 30089 | Setback - Wastewater | 100 | feet | Table 1 lists horizontal setback distances for well uses. For "Heat Exchange" wells, the setback to "Absorption Systems" is "100" feet. Section 4(C) states that where there is no Certificate of Subdivision Approval, "the location of the well(s) must conform to the minimum setback requirements shown in Table 1." | 4. SITING REQUIREMENTS / Table 1. Horizontal setback distances in feet* | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders | 30089 | Permit |  |  | "(A) Permit Required. A person may not construct a well within Sanders County without first obtaining a permit from the Department." The application "must include" a site plan showing, among other things, "the proposed well," "existing and proposed sewage facilities," "existing and proposed buildings," "property lines and easements," and nearby "floodplain or surface water within 100' of proposed well location." A permit expires if the well "is not installed, inspected and approved by the Department within one year after issuance." | 1. PERMITS AND APPLICATIONS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders | 30089 | Inspection |  |  | "(B) Prior to being used, all wells require a final inspection of the well location by the Department unless specific permission has been granted by the Department." "(C) When final approval is withheld ... A re-inspection must be made to confirm the deficiencies have been corrected and the system is in compliance with the regulations." "(D) The applicant or licensed well driller must notify the Department that a well is ready for inspection within two (2) business days of completion of the well." | 5. INSPECTIONS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders | 30089 | Licensed Driller |  |  | Section 5 repeatedly assigns duties to a "licensed well driller," including: "The applicant or licensed well driller must notify the Department upon correction of any and all deficiencies" and "The applicant or licensed well driller must notify the Department that a well is ready for inspection within two (2) business days of completion of the well." | 5. INSPECTIONS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Montana | Sanders | 30089 | Other Prohibitions/Regulations |  |  | "(E) Drilling of a well is prohibited if the well isolation zone, as defined in 76-4-102, encroaches onto adjacent private property without the authorization of the private property owner." | 4. SITING REQUIREMENTS | 2018 | https://co.sanders.mt.us/DocumentCenter/View/19773/Sanders-County-Well-Regulations-2018
Nebraska | Adams | 31001 | Definition: Well |  |  | "GROUND WATER HEAT PUMP WELL shall mean a well constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well constructed for the purpose of installing the underground closed loop pipe necessary to re-circulate heat transfer fluid. a. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. b. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definition of Terms | 2010 | https://adamscountyne.gov/images/PDFS/PlanningZoning/AdamsCoZoning%20Regs%20-%202010%20final.pdf
Nebraska | Antelope | 31003 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2018 | https://antelopecounty.nebraska.gov/sites/default/files/doc/Antelope%20County%20Zoning%20Regs_adopted%20041018.pdf
Nebraska | Antelope | 31003 | Permit |  |  | "No building, structure, or land ... shall hereafter be used or occupied and no building or structure or part thereof shall hereafter be erected, constructed, reconstructed, moved, or structurally altered, except in conformity with the provisions of this Resolution ... and except after receiving a zoning permit from the Antelope County Zoning Administrator." | Section 3.08 Scope of Regulations | 2018 | https://antelopecounty.nebraska.gov/sites/default/files/doc/Antelope%20County%20Zoning%20Regs_adopted%20041018.pdf
Nebraska | Cuming | 31039 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2020 | https://cumingcountyne.gov/wp-content/uploads/2021/06/2-Zoning-Regulations-Resolution-20200201-February-26-2020.pdf
Nebraska | Dawson | 31047 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2019 | https://cms8.revize.com/revize/dawnsoncounty/Dawson%20County%20Zoning.pdf
Nebraska | Furnas | 31065 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G |  | https://furnascounty.ne.gov/wp-content/uploads/sites/47/2025/06/zoning_regulations.pdf
Nebraska | Greeley | 31077 | Permit |  |  | The zoning text expressly allows geothermal only as a special use in multiple districts: "Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources in conformance with 'Net Metering' per Nebraska State Statutes 70-201to 205, as amended." This appears in AG-1 §5.15, AG-2 §5.25, RC §5.35, C §5.44, and I §5.54, each stating such uses may occur "if a special permit for such use has been obtained in accordance with Article 6." Article 6 states: "The County Board may authorize by special permit after public hearing, any of the buildings or uses designated in this resolution as permitted special uses." | 5.15 PERMITTED SPECIAL USES; 5.25 PERMITTED SPECIAL USES; 5.35 PERMITTED SPECIAL USES; 5.44 PERMITTED SPECIAL USES; 5.54 PERMITTED SPECIAL USES; Article 6 - SPECIAL USE PERMIT | 2015 | https://greeleycounty.ne.gov/wp-content/uploads/sites/34/2025/06/zoning_regulations.pdf
Nebraska | Hamilton | 31081 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 37. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 38. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 39. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 40. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2019 | https://hamiltoncountyne.gov/wp-content/uploads/2021/07/hamilton-county-zoning-current.pdf
Nebraska | Holt | 31089 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDWEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." |  | 2025 | https://holtcounty.nebraska.gov/sites/default/files/doc/Holt%20Co%20Zoning%20Update%20Final.pdf
Nebraska | Jefferson | 31095 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions | 2026 | https://jeffersoncounty.nebraska.gov/sites/default/files/doc/Redacted%20Jefferson%20Co%20NE%20Zoning%20Regs%202026.pdf
Nebraska | Kearney | 31099 | Permit |  |  | Geothermal is allowed only through district use permissions: in AG-1, RC, AGR, and R-1 it is listed as an accessory use; in C and R-M it is listed under uses requiring a special use permit; in FS it appears under special uses. Examples: 'Alternative energy systems utilizing biomass, geothermal, hydropower, solar energy systems less than 25 kW and/or wind sources...' (Secs. 5.13, 5.23, 5.33, 5.43, 5.62, 5.83); 'A building or premises may be used for the following purposes ... if a special use permit for such use has been obtained in accordance with Article 6' including geothermal in C and FS districts (Secs. 5.54, 5.73). Article 6.1 states the County or Village 'may authorize by special permit after public hearing' designated special uses, and 6.2 states applications are filed with the Clerk and heard by the Planning Commission and County or Village Board before becoming effective. | Article 6; Sections 5.14, 5.24, 5.34, 5.44, 5.54, 5.64, 5.73, 5.83 | 2020 | https://kearneycounty.ne.gov/wp-content/uploads/sites/41/2025/12/zoning_regulations.pdf
Nebraska | Lincoln | 31111 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground... 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. a. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. b. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions - G |  | https://lincolncountyne.gov/wp-content/uploads/2015/06/zonereg.pdf
Nebraska | Nance | 31125 | Permit |  |  | AG and RC list 'Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources in conformance with "Net Metering" per Nebraska State Statutes §70-2001 to §70-2005' as permitted accessory uses. AGR, HC, and I list the same 'Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources in conformance with "Net Metering" per Nebraska State Statutes §70-2001 to §70-2005' as 'PERMITTED CONDITIONAL USES.' Article 8 provides that 'a conditional permit for such use has been obtained in accordance with Article 8 of these regulations' and that 'After receiving an application and fee... the County Board of Supervisors, after recommendation of the Planning and Zoning Commission, may authorize a conditional use permitted in a zoning district.' | ARTICLE 12: AG GENERAL AGRICULTURAL DISTRICT, Section 2. PERMITTED ACCESSORY USES AND STRUCTURES; ARTICLE 13: RC RURAL CONSERVATION DISTRICT, Section 2. PERMITTED ACCESSORY USES AND STRUCTURES; ARTICLE 14: AGR AGRICULTURAL RESIDENTIAL DISTRICT, Section 3. PERMITTED CONDITIONAL USES; ARTICLE 15: HC HIGHWAY COMMERCIAL DISTRICT, Section 3. PERMITTED CONDITIONAL USES; ARTICLE 16: I INDUSTRIAL DISTRICT, Section 3. PERMITTED CONDITIONAL USES; ARTICLE 8, Section 2. Conditional Uses | 2023 | https://nancecountyne.gov/wp-content/uploads/sites/40/2025/06/Nance-County-Nebraska-Zoning-Regulations.pdf
Nebraska | Phelps | 31137 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2022 | https://phelpscounty.ne.gov/pdfs/zoning/Phelps%20County%20Final%20Draft%20Zoning%20112622.pdf
Nebraska | Seward | 31159 | Definition: Geothermal Heat Pump |  |  | "GROUND WATER HEAT PUMP WELL shall mean a well constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground... 2. Closed Loop Heat Pump well shall mean a well constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. a. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. b. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | 2.03.208 GROUND WATER HEAT PUMP WELL | 2007 | https://sewardcountyne.gov/wp-content/uploads/sites/50/2025/09/Zoning-Regulations.pdf
Nebraska | Seward | 31159 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be a closed loop system." | 4.13.03 Specific Conditions Required | 2007 | https://sewardcountyne.gov/wp-content/uploads/sites/50/2025/09/Zoning-Regulations.pdf
Nebraska | Stanton | 31167 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2025 | https://stantoncounty.nebraska.gov/sites/default/files/doc/Zoning%20Regulations%20-%20amended%20June%202025.pdf
Nebraska | Thayer | 31169 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEE Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2025 | https://thayercountyne.gov/wp-content/uploads/2025/06/Thayer-County-Zoning-Regulation-signed-2025-Redacted-Version-1.pdf
Nebraska | Washington | 31177 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G |  | http://www.co.washington.ne.us/media/draftplan/Washington_County_Zoning_Regulations_draft.pdf
Nevada | Clark | 32003 | Other Prohibitions/Regulations |  |  | The AEO key states: "4800* Renewable energy facilities (ex. Solar and geothermal facilities as well as wind turbines) shall delineate methods of mitigating possible plumes." | §30.02.26C, Airport Environs Overlay (AEO) | 2024 | https://www.clarkcountynv.gov/assets/documents/government/departments/comprehensive_planning_department/library/title-30-eff-11-20-24.pdf
Nevada | Elko | 32007 | Permit |  |  | Section 3-1-5(H) states: "Solar, Hydronics and Geothermal Code Fees: All editions of the Uniform Plumbing Code, present and future, are hereby amended and modified as follows: Table 104.5 - Solar, Hydronics and Geothermal Code Fees, the following is added: System fee schedule (note: the following do not include permit issuing fee) shall be set by resolution adopted by the Elko County commission." Section 3-1-1(I) also adopts "The 2018 Uniform Solar, Hydronics and Geothermal Code." | 3-1-5: RESTRICTIONS / 3-1-1: CODES ADOPTED | 2021 | https://codelibrary.amlegal.com/codes/elkocountynv/latest/elkocounty_nv/0-0-0-779
Nevada | Lyon | 32019 | Permit |  |  | 'Geothermal direct use wells for commercial or industrial space heating, food dehydration, or other similar such uses shall be subject to the standards listed in this chapter and Nevada Revised Statutes 534A.' | 15.336.08: GEOTHERMAL GENERATING SYSTEMS, F. Geothermal Direct Use Wells | 2025 | https://codelibrary.amlegal.com/codes/lyoncountynv/latest/lyoncounty_nv/0-0-0-8734
New Jersey | Salem | 34033 | Definition: Well |  |  | "Closed loop geothermal well" means a well or a borehole drilled to a specific depth either singly or in a series wherein a continuous closed loop of pipe is inserted from one well to another for the purpose of noncontact thermal energy transfer from a fluid in the loop to or from the earth. "Open loop geothermal well" means a well designed and installed specifically for use of the earth as a source for heat extraction/rejection. | 7:9D1.5 Definitions | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Definition: Geothermal Heat Pump |  |  | "Closed loop geothermal well" means a well or a borehole drilled to a specific depth either singly or in a series wherein a continuous closed loop of pipe is inserted from one well to another for the purpose of noncontact thermal energy transfer from a fluid in the loop to or from the earth. "Open loop geothermal well" means a well designed and installed specifically for use of the earth as a source for heat extraction/rejection. | 7:9D1.5 Definitions | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Setback - Building Foundation | 5 | feet | "All new Category 1 and Category 2 wells shall be located at least five feet horizontally from a building or any portion thereof, except for a pumphouse." Open loop geothermal wells are listed as Category 2 wells in 7:9D2.1(a)2. | 7:9D2.7 Minimum distance requirements | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Setback - Fuel (above ground) | 25 | feet | "All Category 2 wells shall be located no less than 25 feet from a fuel storage tank." Open loop geothermal wells are included in Category 2 under 7:9D2.1(a)2. | 7:9D2.7 Minimum distance requirements | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Minimum Well Depth | 50 | feet | For potable water supply wells in unconsolidated formations, "All well casing shall be no less than four inches in inner diameter and no less than 50 feet in depth." Open-loop geothermal wells are Category 2, but the 50-foot minimum depth in this section applies explicitly to potable Category 1 wells, not all geothermal wells. | 7:9D2.3 Specific requirements for the construction of Category 1 and Category 2 wells | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Permit |  |  | "the owner or authorized agent ... and the New Jersey licensed well driller of the proper class shall sign and obtain a valid New Jersey well permit from the Department prior to drilling, constructing, installing, physically altering, or redesignating the use of any well." Also, "A licensed well driller may obtain a sitewide permit when installing ... closedloop geothermal well systems," and "A State well permit shall be required prior to the construction of all wells as described in N.J.A.C.7:9D2." | 7:9D1.11 Well permits | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Inspection |  |  | The Department may, as a permit condition, require the driller to "Provide advanced notice of drilling in order to allow for the inspection of the well site by authorized representatives and/or provide for the taking of geophysical logs, geologic or water samples as necessary." Also, "Original State well permits or copies thereof shall be available onsite at all times for inspection by any authorized local and/or State representative." | 7:9D1.11 Well permits | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Licensed Driller |  |  | "No person shall drill, construct, install, repair, replace, modify, stimulate or decommission any well ... without possessing a valid New Jersey well driller's license of the proper class unless that activity is performed under the direct and immediate onsite supervision of a New Jersey licensed well driller of the proper class." Also, "No person shall conduct any operation involving the drilling ... of any well ... without the immediate onsite supervision of a licensed well driller of the proper class," and "A New Jersey licensed well driller shall be onsite and directly supervise each well drilling operation, and there shall be one licensed well driller of the proper class on site for each well drilling rig on site." | 7:9D1.6 General provisions; 7:9D2.2 General construction requirements for all wells | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Certification |  |  | For applicants lacking the required New Jersey experience, the rule requires "evidence that he or she is in possession of a valid National Ground Water Association Certification (NGWA) in the appropriate well drilling category" for journeyman/journeyman (Class B) applicants and similarly for monitoring well drilling applicants. | 7:9D1.8 Application and licensing examination procedures and requirements for well driller licenses of the proper class and pump installer licenses | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Decommissioning |  |  | "Unsuitable or nonproductive wells that cannot be used for their intended purpose shall be decommissioned in accordance with N.J.A.C. 7:9D3. These include, but are not limited to, wells which are abandoned during construction, are contaminated, exhibit a loss of supply or are damaged." Also, "When the drilling of a borehole for any well is temporarily suspended and the rig moves away from the drilling site, the borehole shall be considered abandoned and subject to the decommissioning requirements in N.J.A.C.7:9D3." In addition, activities performed without an individual permit under 7:9D1.11(g) must result in any well being "decommissioned in accordance with N.J.A.C.7:9D3." | 7:9D2.2 General construction requirements for all wells; 7:9D1.11 Well permits | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
New Jersey | Salem | 34033 | Other Prohibitions/Regulations |  |  | For dewatering wells, "The screening of a dewatering well in more than one aquifer is prohibited." | 7:9D2.5 Requirements for the installation of Category 4 wells | 2007 | https://health.salemcountynj.gov/wp-content/uploads/filebase/environmental/Wellpermits-private%20water%20testing%20PWTA/NJAC7_9D.pdf
North Carolina | Guilford | 37081 | Definition: Well |  |  | "Geothermal borehole" means "any hole in the earth which is drilled for the purpose of installing piping for heating and air conditioning systems through which water, antifreeze, water mixtures, Freon, or other media are circulated to exchange heat with the earth for the purpose of heating or cooling, or both." | Chapter 1 Definitions (33) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Definition: Geothermal |  |  | The rules define geothermal heating/cooling uses through specific geothermal terms: "Geothermal Aqueous Closed-Loop Wells" are wells with closed-loop pipe circulating potable water or water with approved additives "for heating and cooling purposes"; "Geothermal Direct Expansion Closed-Loop Wells" are wells with closed-loop pipe that circulates refrigerant gas "for heating and cooling purposes"; and "Geothermal Heating/Cooling Water Return Well" means "a well that reinjects groundwater used to provide heating or cooling for structures." | Chapter 1 Definitions (32), (34), (35) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop Geothermal Injection Well System" means "a system of continuous piping, part of which is installed in the subsurface via vertical or angled borings, through which moves a fluid that does not exit the piping, and which is used to transfer heat energy between the subsurface and the fluid in association with a heating and cooling system." Also, "Geothermal Heating/Cooling Water Return Well" means "a well that reinjects groundwater used to provide heating or cooling for structures." | Chapter 1 Definitions (16) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Setback - Building Foundation | 15 | feet | For a "Closed Loop Geothermal Injection Well System" the minimum horizontal separation from "Building perimeters, including any attached structures" is "15 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Setback - Wastewater | 50 | feet | For closed-loop geothermal injection wells, the minimum horizontal separation includes: "Septic systems including septic tank, drainfield, waste application area, and drainfield repair area ... 50 feet" and "Land-based or subsurface waste storage or disposal systems ... 50 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Setback - Fuel (above ground) | 50 | feet | The ordinance requires a 50-foot separation from "Above ground or underground storage tanks which contain petroleum fuels used for heating equipment, boilers, or furnaces, with the exception of tanks used solely for storage of propane, natural gas, or liquefied petroleum gas." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Setback - Fuel (below ground) | 100 | feet | For closed-loop geothermal injection wells, "Chemical or petroleum fuel underground storage tank systems regulated under 15A NCAC 02N with secondary containment" must be separated by "50 feet," and those "without secondary containment" by "100 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Setback - Sewer Lines | 25 | feet | For a closed-loop geothermal injection well, separation distances include "Industrial or municipal sewage or liquid waste collection or transmission sewer mains ... 15 feet," "Water-tight sewer lateral lines from a residence or other non-public system ... 15 feet," and "Other industrial or municipal sewage or liquid-waste collection or transfer facilities ... 25 feet." | Chapter 5 Section III(C)(1) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Permit |  |  | "It shall be unlawful for any person to construct, repair, or perform ground source heat pump well contractor activities in Guilford County without first obtaining a ground source heat pump well permit from the Guilford County Health Director or their designee." The permit "shall be valid for 12 months from date of issuance." The property owner must also submit DEQ forms before construction, including for "Geothermal Heating/Cooling Water Return Wells" an "APPLICATION FOR A PERMIT TO CONSTRUCT OR OPERATE INJECTION WELL(S)" and for a "Closed Loop Geothermal Injection Well System" a "NOTIFICATION OF INTENT TO CONSTRUCT OR OPERATE INJECTION WELLS." | Chapter 5 Section II Ground Source Heat Pump Well Permits | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Licensed Driller |  |  | Chapter 5 states: "Only Certified Well Contractors shall perform well contractor activities." Chapter 1 Section III(B) adds: "No person shall perform, manage, or supervise any well contractor activity without being certified according to the well contractor certification requirements of 15A NCAC 27." | Chapter 5 Section II(H); Chapter 1 Section III(B) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Guilford | 37081 | Certification |  |  | "Certified Well Contractor" means "a person certified as a well contractor with the State of North Carolina in accordance with 15A NCAC 27 (North Carolina Well Contractor Certification Commission Rules)." Section III(B) states: "No person shall perform, manage, or supervise any well contractor activity without being certified according to the well contractor certification requirements of 15A NCAC 27." | Chapter 1 Definitions (14); Chapter 1 Section III(B) | 2021 | https://www.guilfordcountync.gov/guilford-county-well-rules/open
North Carolina | Montgomery | 37123 | Permit |  |  | The fee schedule lists under "E. Heating & Air Conditioning Permits" the item "4. Geothermal System — $100.00." | FY2022 BUDGET ORDINANCE — BUILDING INSPECTIONS, E. Heating & Air Conditioning Permits | 2021 | https://nmcdn.io/e186d21f8c7946a19faed23c3da2f0da/9938771685204d8ea2bbc1353c6b7aed/files/departments/finance/budget-information/fy22-bud-ord-signed.pdf
North Carolina | Orange | 37135 | Definition: Well |  |  | "'Closed loop geothermal heat exchange injection well' or 'geothermal well' means an excavation that is drilled into which a sealed pipe loop is inserted through which fluid or gas is recirculated for the sole purpose of a vertical closed loop geothermal heat exchange system." | Section I.B.14 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Definition: Geothermal Heat Pump |  |  | "'Closed loop geothermal heat exchange system' means a system of continuous piping, part of which is installed in the subsurface, through which moves a fluid or gas that does not exit the piping, and which is used to transfer heat energy to and from the fluid or gas." | Section I.B.15 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Setback - Building Foundation | 15 | feet | For "closed loop geothermal wells that are fully grouted with an approved grout," setbacks measured "from any portion of the borehole to the potential source of contamination" include: "Building perimeters, including any attached structures — 15 ft." | Section III.C.4 table | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Setback - Wastewater | 50 | feet | For "closed loop geothermal wells that are fully grouted with an approved grout," setbacks include: "Septic tanks and drainfields, including drainfield repair areas — 50 ft." and "Land-based or subsurface waste storage or disposal systems — 50 ft." | Section III.C.4 table | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Setback - Sewer Lines | 25 | feet | For "closed loop geothermal wells that are fully grouted with an approved grout," setbacks include: "Sewer lines constructed to water main standards — 15 ft." and "Sewer lines not constructed to water main standards — 25 ft." | Section III.C.4 table | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Permit |  |  | Section I.C: "A property owner or the property owner's agent shall submit an application for a permit to construct, repair, or to abandon a well to Orange County Health Department." For geothermal-specific applications, "An application for a closed-loop geothermal well shall also include: a. The type of recirculation fluid or gas, and any additives to be used... b. A detailed site plan showing the locations of the well or wells and the horizontal piping routes... c. A detailed profile diagram showing the components of the geothermal well system... d. Any current or pending restrictions regarding groundwater use..." Section I.D further states permit validity and administration for well permits. | Section I.C; Section I.D | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Inspection |  |  | Section III.C.9: "Prior to the initiation of the grouting process, the OCHD will verify that the locations of all geothermal wells meet all applicable setbacks. The OCHD may conduct intermittent inspections of the grouting process thereafter, and shall ensure by visual inspection that each well is grouted to within one foot of land surface." Section I.E adds: "The grouting of any well shall not commence before a representative of the Health Department has inspected the annular space around the well." Section I.F requires notice "so that a final inspection can be conducted." | Section III.C.9; Section I.E; Section I.F | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Licensed Driller |  |  | "Geothermal well construction standards, installation standards and contractor certification procedures adopted by the International Ground Source Heat Pump Association (IGSHPA) are hereby enacted by reference." | Section III.C.1 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Screening |  |  | "When closed loop geothermal heat exchange injection wells are terminated below the ground surface, either: a. Each well shall have a permanent monument at grade level directly above each well... or b. The perimeter corners of each well field shall be marked at ground surface with a permanent monument..." | Section III.C.11 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Certification |  |  | "Geothermal well construction standards, installation standards and contractor certification procedures adopted by the International Ground Source Heat Pump Association (IGSHPA) are hereby enacted by reference." | Section III.C.1 | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Orange | 37135 | Decommissioning |  |  | "Any well that acts as a source or channel of contamination shall be repaired or permanently abandoned within 30 days of receipt of notice from the OCHD." Also, "All wells shall be permanently abandoned in which the casing has not been installed or from which the casing has been removed, prior to removing drilling equipment from the site." | Section IV.B | 2020 | https://www.orangecountync.gov/DocumentCenter/View/10212/Environmental-Health-Rules-Approval
North Carolina | Union | 37179 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. Geothermal energy systems consists of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump. This includes vertical closed loop, horizontal closed loop and water body closed loop systems." | Article 105 ¦ Definitions, Terms Beginning with “G” | 2015 | https://files.nc.gov/ncdeq/Environmental%20Management%20Commission/EMC%20Meetings/2017/3-May2017/AG17-23/AttachmentE_17-23_UC_EIS-AppE_CD-1.pdf
Ohio | Medina | 39103 | Inspection |  |  | Section 3.14 applies to backflow prevention and states: 'The MCSE may inspect the water use practices within the consumer's premises to determine compliance with the requirements of these Rules and Regulations.' It also requires that 'inspections, tests, and overhauls of backflow prevention devices shall be made at the expense of the water consumer' and for reduced pressure principle backflow prevention devices and double check valve assemblies they 'shall be inspected and tested for tightness at the time of installation and at least every twelve (12) months thereafter.' | Section 3.14 G. Inspections; Section 3.14 L. Inspection and Maintenance | 2013 | https://sanitaryengineer.co.medina.oh.us/downloads/rulesandregs.pdf
Arizona | Navajo | 4017 | Permit |  |  | "Any underground injection, except into a well authorized by rule or authorized by permit under the Arizona UIC program, is prohibited. The construction of any well required to have a permit is prohibited until the permit has been issued." Also, "Unless an underground injection well is authorized by rule under R18-9-I650, all injection activities including construction of an injection well are prohibited until the owner or operator is authorized by permit." Class V wells expressly include "Air conditioning return flow wells used to return to the supply aquifer the water used for heating or cooling in a heat pump." | R18-9-B607. Prohibition of Unauthorized Injection; R18-9-C616. Individual Permits; Application for Individual Permits | 2022 | https://www.navajocountyaz.gov/DocumentCenter/View/533/18-09_(15-2)_130pgs.pdf
Arizona | Navajo | 4017 | Inspection |  |  | "One of the following methods must be used to evaluate the absence of significant leaks... 1. Following an initial pressure test... 2. Pressure test with liquid or gas..." and "One of the following methods must be used to determine the absence of significant fluid movement... 1. The results of a temperature or noise log..." | R18-9-B613. Mechanical Integrity | 2022 | https://www.navajocountyaz.gov/DocumentCenter/View/533/18-09_(15-2)_130pgs.pdf
Arizona | Navajo | 4017 | Decommissioning |  |  | For Class V wells, "Prior to abandoning a Class V well, the owner or operator shall close the well in a manner that prevents the movement of fluid containing any contaminant into an USDW..." and "The owner or operator shall dispose of or otherwise manage any soil, gravel, sludge, liquids, or other materials removed from or adjacent to the well in accordance with all applicable Federal, State, and local regulations and requirements." Permit applicants must also submit "A plugging and abandonment plan that meets the requirements of R18-9-B614 and is acceptable to the Director." | R18-9-B614. Plugging and Abandoning Class I, II, III, IV, and V Wells; R18-9-C616. Individual Permits; Application for Individual Permits | 2022 | https://www.navajocountyaz.gov/DocumentCenter/View/533/18-09_(15-2)_130pgs.pdf
Oregon | Deschutes | 41017 | Permit |  |  | "11(20) High-temperature geothermal wells and small-scale geothermal energy facilities" requires application materials, and states: "For drilling applications..." specified narratives and diagrams must be provided; "When approved by the Planning Director, applications for prospect wells... may satisfy the information requirements... by submission of a copy of the applicant's prospect well permit application to the Oregon Department of Geology & Mineral Industries." It also states, "Applicants may redrill or otherwise reenter the same well-bore of any well for which a conditional use permit has already been issued as long as all conditions of the use permit continue to be met." | Section 9. Section 8.050, Specific Use Standards, subsection (20) | 1985 | https://g3mtx8smp2.execute-api.us-east-2.amazonaws.com/v1/6254/chapter_12/12.23.pdf
Oregon | Deschutes | 41017 | Decommissioning |  |  | "Site abandonment and restoration. When a well or facility is permanently abandoned; the applicant shall remove all equipment, structures, and other related material within 180 days from the date operations cease. Thereafter the applicant shall regrade the area of operations so as to match original land contours as closely as practical, and shall revegetate the area in accordance with Subsection 21 of 8.050(B)." | Section 9. Section 8.050, Specific Use Standards, subsection (20)(B) | 1985 | https://g3mtx8smp2.execute-api.us-east-2.amazonaws.com/v1/6254/chapter_12/12.23.pdf
Oregon | Douglas | 41019 | Definition: Geothermal |  |  | "GEOTHERMAL RESOURCES: The natural underground reservoirs of heat that may be exploited for the production of heat energy, including but not limited to all minerals obtained from naturally or artificially injected fluid, brine or associated gas and steam in any form whatsoever, but excluding oil, hydrocarbon gas and other hydrocarbon substances and hot waters of less than 250 degrees Fahrenheit and bottom hold temperature." | SECTION 1.090 Definitions | 2012 | https://www.douglascountyor.gov/DocumentCenter/View/2899/2012-Chapter-1-PDF
Oregon | Josephine | 41033 | Setback - Property Lines | 5 | feet | Section 84.080 states: "Any new wells drilled after the effective date of this code shall not be located within 5 feet of a property line. Furthermore, all wells shall meet the location requirements of OAR, Chapter 690, Division 210." | 84.080 - NEW WELLS | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Josephine | 41033 | Permit |  |  | Section 84.020.J states: "A water well permit shall be obtained prior to the commencement of any work for each of the following: 1. Construction of any well; 2. Alteration of any well; 3. Abandonment of any well." The same article expressly includes geothermal-related use by exempting "Down-hole heat exchange" in Section 84.020.I.4. | 84.020 - APPLICATION | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Josephine | 41033 | Certification |  |  | Section 84.050 provides: "The certified pump tester shall submit a preliminary report..."; "the certified pump tester shall attempt to notify all property owners..."; and under "CERTIFICATION AND RESPONSIBILITY": "A major or minor pump test is to be conducted by a firm, or individual, who has been certified by the Water Resources Department to have the necessary equipment and knowledge required to conduct the test." | 84.050 - TEST OBJECTIVE | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Josephine | 41033 | Decommissioning |  |  | Section 84.050 states: "Any substandard well on a lot or parcel proposed for development, must be properly abandoned or repaired as required by the Oregon Administrative Rules (OAR), Chapter 690, Division 200 to 235, for well construction, maintenance, and abandonment." Section 84.070.A adds that if water quality standards are not met, "the well must be properly constructed in accordance with OAR, Chapter 690 Division 210 and 215, or abandoned in accordance with OAR, Chapter 690 Division 220." Section 84.020.J also requires a permit for "Abandonment of any well." | 84.050 - TEST OBJECTIVE; 84.070 - WATER QUALITY OR QUANTITY TEST | 2005 | https://cms9files.revize.com/josephinecountyor/Documents%20and%20Forms/Planning/A-N/code.pdf
Oregon | Multnomah | 41051 | Permit |  |  | "For the purposes of this section, the expiration provisions in (a) and (b) shall also apply to all other Type II or III decisions associated with approval of the residential development, such as SEC or GHP permits." | § 39.1185 EXPIRATION OF TYPE II OR TYPE III DECISIONS |  | https://multnomah.granicus.com/MetaViewer.php?view_id=3&clip_id=2566&meta_id=162614
Oregon | Multnomah | 41051 | Inspection |  |  | "Inspection and enforcement. The director may take steps to ensure compliance with the requirements of Part 6, Geologic Hazards permit requirements, and Large Fill permit requirements any permit listed in subsection (A) and 39.6235, including but not limited to, inspections, peer review of engineering analysis (at the applicant's expense), post construction certification of the work... If inspection by county staff reveals erosive conditions which exceed those prescribed by the permit, work may be stopped until appropriate correction measures are completed." | § 39.6210 PERMITS REQUIRED |  | https://multnomah.granicus.com/MetaViewer.php?view_id=3&clip_id=2566&meta_id=162614
Pennsylvania | Bucks | 42017 | Definition: Well |  |  | "Geothermal well - Any well or borehole in the ground constructed for the purpose of extracting heat from or transferring heat to the ground or groundwater. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes." | SECTION ONE - GENERAL PROVISIONS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump Equipment - Any components of a heating or cooling system in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | SECTION ONE - GENERAL PROVISIONS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Driveways | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. The note adds: "Closed loop geothermal systems and monitoring wells do not have to meet isolation distance for driveways." | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Right of Way | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Property Lines | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Building Foundation | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Wastewater | 50 | feet | The isolation distance table requires setbacks from wastewater-related sources, including "Community spray irrigation sites, sewage sludge and septage disposal sites" at "100*" feet; "All sewage absorption areas including cesspools and seepage pits" at "100*" feet; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks" at "50*" feet. Note: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." This yields 50 feet from the 100* wastewater sources for closed-loop systems, which is the most restrictive closed-loop wastewater setback stated. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Private Water | 50 | feet | Section 8.2(a): "To prevent thermal degradation, the withdraw and return wells must be a minimum of 50 feet apart." | SECTION EIGHT - GEOTHERMAL WELLS, 8.2 Open-Loop Geothermal HVAC Systems | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Animal Enclosures | 100 | feet | The isolation distance table lists "Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure" at "200*" feet, and notes: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Sewer Lines | 25 | feet | The isolation distance table includes sewer-line setbacks: "Gravity sewer lines and drains carrying domestic sewage or industrial waste (unless item 9 applies)" at "50*" feet; "Gravity sewer lines and drains using cast iron pipe with watertight lead caulked or neoprene gasketed joints, or Schedule 40 polyvinyl chloride (PVC) pipe with solvent welded joints" at "10" feet; "Sewer lines and drains carrying domestic sewage or industrial waste under pressure constructed of welded steel pipe or concrete encased pipe" at "10" feet; and "Sewer lines and drains carrying domestic sewage or industrial waste under pressure using material other than items in #10" at "50*" feet. Note: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." This makes the controlling most restrictive closed-loop sewer-line setback 25 feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Pools | 10 | feet | The isolation distance table states: "Building foundations, manufactured homes, driveways, property lines, rights-of-way and swimming pool" — "10" feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Water Bodies | 25 | feet | The isolation distance table lists "Delineated wetlands or 100-year floodplain" at "25" feet, with note: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." Because this row is not marked with an asterisk, the 25-foot isolation distance remains applicable. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Setback - Hazardous Materials/Fertilizers | 150 | feet | The isolation distance table sets "Commercial preparation area or storage area of hazardous spray materials, fertilizers, or chemicals; salt piles" at "300*" feet. The note provides: "Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above." | SECTION FOUR - CONSTRUCTION SPECIFICATIONS, 4.1 Well Location | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Permit |  |  | Section 3.1(a): "It shall be unlawful to install a new well or geothermal borehole or modify an existing well without an approved well permit and submission of appropriate fees." Section 3.1(c): "The BCDH must field verify the location of the proposed wells and all applicable isolation distances as outlined in Section 4 of these regulations." Section 8.1(b): "The proposed system design must be submitted and approved by the Department prior to installation. Isolation distances according to Section 4.1 must be confirmed." Section 8.2(d): "The person requesting a geothermal permit from the Department is required to submit proof of an NPDES permit or exemption with any application." | SECTION THREE - APPLICATION TO CONSTRUCT OR MODIFY; SECTION EIGHT - GEOTHERMAL WELLS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Inspection |  |  | Section 6.2(b): "A BCDH representative is to be on site to observe the grouting of the well or borehole and any other inspections deemed necessary." Section 6.5(a): "A BCDH representative is to be on site to observe grouting of the well or borehole and any other inspection during the well construction deemed necessary." Section 6.5(b): "A BCDH representative is to be on-site to observe a 30-minute pressure test as specified in section 8.3." | SECTION SIX - INSPECTION | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Licensed Driller |  |  | Section 7.1(a): "Only well drillers with a PA DCNR license shall be permitted to construct drinking water wells, geothermal wells, test wells and monitoring wells. Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation." Section 8.2(b): "Only PA DCNR approved well drillers using PA DCNR approved well drilling rigs shall drill the withdraw and return flow wells for this type of system." | SECTION SEVEN - WELL DRILLERS; SECTION EIGHT - GEOTHERMAL WELLS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Screening |  |  | Section 8.3(c)(2): "Trench System - A minimum of 6 inches of sand or screenings is to be added to the bottom of the trench to prevent the loop piping from rubbing on stones." | SECTION EIGHT - GEOTHERMAL WELLS, 8.3 Closed-Loop Geothermal Systems | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Certification |  |  | Definition of Well Driller: "A person who is licensed by the state of Pennsylvania to drill wells, or in the case of geothermal wells has IGSHPA certification." Section 7.1(a): "Only well drillers with a PA DCNR license shall be permitted to construct ... geothermal wells ... Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation." Section 8.1(a): "Installation must be by a PA DCNR approved well driller or IGSHPA accredited geothermal system installer." Section 8.3(a)-(b): "Installation must be by a PA DCNR approved well driller or IGSHPA accredited geothermal system installer" and "The system design shall be made by an IGSHPA accredited person or firm or an engineering firm familiar with loading and heat transfer requirements..." | SECTION ONE - GENERAL PROVISIONS; SECTION SEVEN - WELL DRILLERS; SECTION EIGHT - GEOTHERMAL WELLS | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Bucks | 42017 | Decommissioning |  |  | Section 12.1(a)-(d): "A well permit must be obtained prior to abandoning all wells." "Only a PA DCNR licensed well driller is permitted to abandon a well." "Abandonment procedures shall be subject to the BCDH inspection." "Well abandonment procedures must minimally comply with the specifications referenced in the PA DEP/DCNR Water Well Abandonment Guidelines." Section 12.2(a): "The borehole must be cleared of obstructions prior to abandonment. Pumps, pipes, wiring, and air lines must be removed if possible... If the casing cannot be removed, it should be cut below the land surface." | SECTION TWELVE - WELL ABANDONMENT | 2024 | https://www.buckscounty.gov/DocumentCenter/View/2097/Rules-and-Regulations-Governing-Individual-Residential-Water-Supply-Systems-and-Construction-Specifications-PDF
Pennsylvania | Chester | 42029 | Definition: Well |  |  | "Geothermal Well": "A vertical well or borehole constructed to facilitate the installation of, or connection to, equipment used for the purpose of heating or cooling a facility. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes." | 501.4.23 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump Equipment": "Any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | 501.4.25 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Right of Way | 10 | feet | For closed-loop geothermal boreholes, the Miscellaneous table requires "10 feet" from "Property lines, all right-of-ways, easements." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Property Lines | 10 | feet | For closed-loop geothermal boreholes, the Miscellaneous table requires "10 feet" from "Property lines, all right-of-ways, easements." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Wastewater | 50 | feet | For closed-loop geothermal boreholes, the table requires "50 feet" from "Subsurface sewage absorption areas elevated sand mounds, ... seepage pits, cesspools, sewage" and "50 feet" from "Spray irrigation site perimeter, sewage sludge and septage disposal sites"; and "25 feet" from "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Fuel (above ground) | 300 | feet | For closed-loop geothermal boreholes, the Chemical Related table requires "300 feet" from "Surface or subsurface containers or tanks of greater than 1,000 gallons used for storage of materials that cannot be properly renovated by passage through soil ... including ... gasoline and all other petroleum products," and "30 feet" from similar containers or tanks of "1,000 gallons or less." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Sewer Lines | 5 | feet | For closed-loop geothermal boreholes, the table requires a minimum isolation distance of "5 feet" from "Sewer drains, public sewer laterals." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Water Bodies | 10 | feet | For closed-loop geothermal boreholes, the table requires a minimum isolation distance of "10 feet" from "Delineated wetlands, flood plains lakes, ponds or other surface waters." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop geothermal boreholes, the Chemical Related table requires "300 feet" from "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals; salt piles" and "300 feet" from "Surface or subsurface containers or tanks of greater than 1,000 gallons used for storage of materials that cannot be properly renovated by passage through soil ... including ... gasoline and all other petroleum products." | 501.14.3.2.2.1 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Permit |  |  | 501.7.1.1: "All ... geothermal wells ... require a permit." 501.7.1.2: "Geothermal wells are required to be permitted." 501.14.3.1.1: "Open-loop geothermal delivery wells and return each require a separate permit." 501.14.3.2.1.1: "Closed-loop geothermal boreholes shall be permitted in accordance with §501.7." 501.14.3.2.1.2: "All Closed-loop geothermal boreholes that are part of the project may be included on a single application, and a single permit for the project will be issued. A master plot plan showing the numbered location of each borehole must be included." | 501.7.1.1; 501.7.1.2; 501.14.3.1.1; 501.14.3.2.1.1-501.14.3.2.1.2 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Inspection |  |  | "A site inspection may be conducted by the Department at any time during the construction process." | 501.7.8.1.2 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Licensed Driller |  |  | 501.6.1: "The Department shall license all well contractors, geothermal well installation contractors, or pump installation contractors. Geothermal Well Installation Contractors must also be licensed by Department as a well contractor." 501.7.1.3: "All ... geothermal wells ... shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor who is licensed as set forth in this Section." 501.4.24: "Geothermal Well Installation Contractor" is an individual "responsible for the drilling of boreholes used for the purpose of geothermal heating or cooling of a facility" and "shall be licensed as a Well Contractor and a Geothermal Well Installation Contractor by the Department." | 501.6.1; 501.7.1.3; 501.4.24 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Decommissioning |  |  | 501.17.1: "All wells considered to be abandoned shall be filled and sealed by licensed well contractor licensed by the Department in accordance with the procedures for decommissioning listed in this section." The Department "must be notified in writing within thirty (30) days" when a well meets abandoned-well criteria, and "Written notification and proper documentation of decommissioning shall be submitted to the Department on the Well Decommissioning Form within thirty (30) days." 501.16.1-501.16.2 further state that wells replaced or removed from use, including abandoned wells, "shall be decommissioned according to the requirements of §501.17." | 501.17.1; 501.16.1-501.16.2 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Chester | 42029 | Other Prohibitions/Regulations |  |  | 501.15.1: "No new ... geothermal well ... may be permitted, and no new ... geothermal well ... may be constructed, within the delineated Plume Area of a contaminated site unless the United States Environmental Protection Agency (US EPA) or the PA DEP agree and provide written documentation that installation of the well will not have any impact on the Plume or remediation effort." 501.14.3.2.3.2.1: "Boreholes must be vertical and may not be drilled at any angle. Only vertical closed-loop geothermal boreholes require a permit. Horizontal geothermal loop installations do not require a permit." 501.14.3.1.5: "Open-loop geothermal wells systems must include a return well and may not discharge directly or indirectly into surface waters." | 501.15.1; 501.14.3.2.3.2.1; 501.14.3.1.5 | 2014 | https://www.chesco.org/DocumentCenter/View/429/501
Pennsylvania | Delaware | 42045 | Definition: Well |  |  | "Well": Any vertical excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or artificial recharge of groundwater or for the installation of ground source heat pump equipment. This includes but is not limited to test wells, test borings, geothermal and monitoring wells, in addition to wells to be utilized as individual or semi-public or public water supplies. | 501.4.46 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Definition: Geothermal |  |  | "Geothermal Well": A vertical well or borehole constructed to facilitate the installation of, or connection to, equipment used for the purpose of heating or cooling a facility. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes. | 501.4.23 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump Equipment": Any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems. | 501.4.25 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Right of Way | 10 | feet | For closed-loop geothermal boreholes, the table states: "Property lines, all right-of-ways, easements — 10 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Property Lines | 10 | feet | For closed-loop geothermal boreholes, the table states: "Property lines, all right-of-ways, easements — 10 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Wastewater | 50 | feet | For closed-loop geothermal boreholes, the table states: "Subsurface sewage absorption areas elevated sand mounds, cesspools, sewage seepage pits — 50 feet" and "Spray irrigation site perimeter, sewage sludge and septage disposal sites — 50 feet"; also "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks — 25 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Fuel (above ground) | 300 | feet | For closed-loop geothermal boreholes, the table states: "Surface or subsurface containers or tanks of greater than 1,000 gallons used for storage of materials that cannot be properly renovated by passage through soil. This includes, but is not limited to, gasoline and all other petroleum products. — 300 feet" and "... 1,000 gallons or less ... gasoline and all other petroleum products ... — 30 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Sewer Lines | 5 | feet | For closed-loop geothermal boreholes, the table states: "Sewer drains, public sewer laterals — 5 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Water Bodies | 10 | feet | For closed-loop geothermal boreholes, the table states: "Delineated wetlands, flood plains lakes, ponds or other surface waters — 10 feet" and "Rainwater pits and rain gardens — 10 feet" and "Storm drains, retention basins storm water stabilization ponds — 10 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop geothermal boreholes, the table states: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles — 300 feet." | 501.14.3.2.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Permit |  |  | 501.7.1.1: "All ... geothermal wells ... require a permit..." 501.7.1.2: "Geothermal wells are required to be permitted." 501.14.3.1.1: "Open-loop geothermal delivery wells and return each require a separate permit." 501.14.3.2.1.1: "Closed-loop geothermal boreholes shall be permitted in accordance with §501.7." | 501.7.1.1; 501.7.1.2; 501.14.3.1.1; 501.14.3.2.1.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Inspection |  |  | "A site inspection may be conducted by the Department at any time during the construction process." | 501.7.8.1.2 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Licensed Driller |  |  | 501.6.1: "The Department shall license all well contractors, geothermal well installation contractors, or pump installation contractors. Geothermal Well Installation Contractors must also be licensed by Department as a well contractor." 501.7.1.3: "All ... geothermal wells ... shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor..." 501.4.24: "Geothermal Well Installation Contractor" is the individual "responsible for the drilling of boreholes used for the purpose of geothermal heating or cooling of a facility" and "shall be licensed as a Well Contractor and a Geothermal Well Installation Contractor by the Department." | 501.6.1; 501.7.1.3; 501.4.24 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Decommissioning |  |  | 501.17.1: "All wells considered to be abandoned shall be filled and sealed by licensed well contractor licensed by the Department... Written notification and proper documentation of decommissioning shall be submitted to the Department on the Well Decommissioning Form within thirty (30) days..." 501.17.6: "Concrete, cement grout, bentonite or sealing clay shall be used as primary sealing materials and shall be placed from bottom to top by a method that will prevent segregation or dilution of materials." | 501.17.1; 501.17.6 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Delaware | 42045 | Other Prohibitions/Regulations |  |  | 501.15.1: "No new ... geothermal well may be permitted, and no new ... geothermal well may be constructed, within the delineated Plume Area of a contaminated site unless the United States Environmental Protection Agency (US EPA) or the PA DEP agree and provide written documentation that installation of the well will not have any impact on the Plume or remediation effort." 501.14.3.2.3.2.1: "Boreholes must be vertical and may not be drilled at any angle. Only vertical closed-loop geothermal boreholes require a permit. Horizontal geothermal loop installations do not require a permit." | 501.15.1; 501.14.3.2.3.2.1 |  | https://delcopa.gov/sites/default/files/2024-09/chapter500_3.pdf
Pennsylvania | Montgomery | 42091 | Definition: Well |  |  | "GEOTHERMAL WELL - A well installed for the purpose of extracting water for heating or cooling." | Section 17-4 Definitions |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Definition: Geothermal Heat Pump |  |  | "CLOSED-LOOP GEOTHERMAL WELL SYSTEM - A heat pump system using groundwater, surface water, or sub-surface as the heating/cooling source which continuously circulates a heat transferring liquid through sealed pipe and a heat exchanger. The internal liquid is not consumed from or discharged into the environment." "OPEN-LOOP GEOTHERMAL WELL SYSTEM- A heat pump system using groundwater or surface water as the heat/cooling source, circulated through the heat exchanger and returned to the environment via a separate discharge point." | Section 17-4 Definitions |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Setback - Wastewater | 100 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." Wastewater-related entries include: "Community spray irrigation site: 100 feet"; "Sewage sludge and septage disposal sites" under the same 100-foot line; "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits, single family spray irrigation system, etc." at "100 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks" at "50 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Setback - Animal Enclosures | 200 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure" at "200 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Setback - Sewer Lines | 50 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Gravity sewer lines and drains carrying domestic sewage or industrial waste" at "50 feet," with a narrower exception of "10 feet" for specified pipe materials, and "Sewer lines and drains carrying domestic sewage or industrial waste under pressure" at "50 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Setback - Water Bodies | 13 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Delineated wetlands or floodplains" at "25 feet." Applying the ordinance's express closed-loop rule yields a minimum closed-loop distance of one half that listed amount. | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Setback - Hazardous Materials/Fertilizers | 300 | feet | "Minimum isolation distances shall be maintained from the proposed individual water supply, irrigation well, and open-loop geothermal well to the facilities listed below. Closed-loop geothermal well installations require one half the isolation distances listed below at a minimum." The table lists "Commercial preparation area or storage area of hazardous spray materials, fertilizers or chemicals; salt piles" at "300 feet." | Section 17-7 Isolation Distances |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Permit |  |  | "It shall be unlawful to install or modify an individual water supply well, irrigation well or geothermal well without first obtaining a permit from MCHD." | Section 17-5 GENERAL |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Inspection |  |  | "Prior to geothermal well construction, a site meeting with MCHD will be required to layout the proposed design under actual field conditions. Any changes required based on the field design must be addressed by the designing firm before construction begins." | Section 17-6 Inspection procedure for geothermal well system |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Licensed Driller |  |  | "All permit-required wells shall be constructed by a PADCNR-licensed water well driller or an IGSHPA accredited geothermal system installer, if applicable." | Section 17-5 GENERAL |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Certification |  |  | "All permit-required wells shall be constructed by a PADCNR-licensed water well driller or an IGSHPA accredited geothermal system installer, if applicable." | Section 17-5 GENERAL |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
Pennsylvania | Montgomery | 42091 | Decommissioning |  |  | "All abandoned wells must be filled and sealed according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment form shall be submitted to MCHD within thirty (30) days of abandonment." "If applicant/homeowner chooses not to abandon the well, a nonabandonment declaration must be signed and submitted to MCHD within thirty (30) days." | Section 17-8 Abandoned Wells |  | https://assets.montgomerycountypa.gov/files/2026-05/Chapter%2017%20Individual%20Water%20Supply%20System.pdf
South Carolina | Lancaster | 45057 | Permit |  |  | "Geothermal heat exchange systems are permitted as an accessory use in all zoning districts." | 5.11.2 GEOTHERMAL ENERGY SYSTEMS [ALL DISTRICTS] | 2021 | https://www.lancastercountysc.gov/DocumentCenter/View/380/Chapter-5---Use-Regulations-PDF
Tennessee | Shelby | 47157 | Definition: Well |  |  | "Geothermal Well: A well constructed for the primary purpose of adding or removing British Thermal Units (Btu) from groundwater for heating or cooling purposes." | Section 3.20 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby | 47157 | Definition: Geothermal Heat Pump |  |  | "Groundwater Heat Pump: Any mechanical device used for heating or cooling, which adds removes British Thermal Units (Btu) from groundwater." | Section 3.22 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby | 47157 | Permit |  |  | Section 4.02(A): "A permit shall be obtained from the Department prior to beginning the installation, modification, repair, or abandonment of a water well or any other type of well..." Section 4.02(C): "If a well application is approved by the Department, the well driller shall [be] issued a permit. Receipt of the permit shall constitute permission to begin well construction..." Section 11(B)(1): "Any person requesting a permit to construct a water well for use in an underground heat pump system... shall limit such discharges by taking conservation steps established by the Department." Section 11(D): "The design of such heat pump systems, shall be approved by the applicable code, and the owner shall have a valid mechanical permit." | Section 4.02; Section 11 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby | 47157 | Inspection |  |  | Section 4.04(F): "It shall be the duty of the well driller to notify the Department when construction of a well is to begin and when the work is completed so that proper inspections may be made during and after construction..." Section 8(A): "During the construction, modification, repair, or abandonment of any well the Department may conduct such periodic inspections as it deems necessary to insure conformity with applicable standards." | Section 4.04(F); Section 8 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby | 47157 | Licensed Driller |  |  | Section 1.02(A): "all such activities which are contracted for shall be carried by those persons having a valid Tennessee License for Water Well Drillers..." Section 11(D): "All residential, commercial and industrial heat pump systems, shall be horizontal closed loop system with no discharge." | Section 1.02(A); Section 11(D) |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby | 47157 | Decommissioning |  |  | Section 9.01(A): "All abandoned wells shall be filled with Portland cement grout, a high solids bentonite grout, or a Portland cement grout and bentonite combination..." Section 9.01(B): "The owner shall submit a plan to fill at the owners expense any abandoned or condemned well within thirty (30) days after receipt of notice..." Section 9.01(C): "All abandoned wells shall be filled only by a person having a valid license from the Tennessee Department of Environment and Conservation, or be an engineer or geologist registered with the State of Tennessee." Section 9.03(B): "All wells shall be filled with the required sealing or fill material from the bottom of the well up..." and Section 9.03(C): "The grout shall be pumped into the well through a tremmie pipe in one continuous operation." | Section 9.01; Section 9.03 |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Tennessee | Shelby | 47157 | Other Prohibitions/Regulations |  |  | "Non-aqueous heat pump systems shall be prohibited." | Section 11(E) |  | https://www.shelbytnhealth.com/DocumentCenter/View/173
Utah | Millard | 49027 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System (Major). A system or facility using the thermal energy resources of the Earth (geothermal energy) to provide mechanical or electrical power or heating or cooling systems for commercial purposes which may or may not be located on the same site as the Geothermal Energy System (Major)." Also, "Geothermal Energy System (Minor). A system or facility using the thermal energy resources of the Earth (geothermal energy) to provide mechanical or electrical power or heating or cooling systems for private, non- commercial purposes for use on the same site as the Geothermal Energy System (Minor)." | APPENDIX A TABLE OF USES AND ACCOMPANYING USE DEFINITIONS | 2014 | https://millardcounty.gov/wp-content/uploads/public-notices/2014/PC_-_CODIFICATION_CORRECTIONS_PC_Public_Hearing_02052014__Z-2014-002.pdf
Utah | Millard | 49027 | Other Prohibitions/Regulations |  |  | The Table of Uses states: "X = Use Prohibited in the Zoning District (Zone)." It further states: "A Use that is not identified in the Table of Uses is determined to be a Prohibited Use in Millard County." For "Geothermal Energy System (Minor)," the table shows "X" in the "TC" zoning district. For "Geothermal Energy System (Major)," the table shows "C-2" in "RF" and "X" in "AG-20," "AG," "AI," "R1," "TC," "HC," "LI," and "HI." | APPENDIX A TABLE OF USES AND ACCOMPANYING USE DEFINITIONS | 2014 | https://millardcounty.gov/wp-content/uploads/public-notices/2014/PC_-_CODIFICATION_CORRECTIONS_PC_Public_Hearing_02052014__Z-2014-002.pdf
Virginia | Northampton | 51131 | Other Prohibitions/Regulations |  |  | The ordinance treats "Geothermal heating facilities" as a special use in the IL district and as a special use in the IG district: Section 17-3(f) lists "Geothermal heating facilities" under "Special Uses and Structures," while Section 18-3(o) likewise lists "Geothermal heating facilities" under "Special Uses and Structures." In those districts, only principal permitted uses are allowed by right under Sections 17-2 and 18-2, so geothermal heating facilities are not permitted by right there. | Section 17-2 and Section 17-3; Section 18-2 and Section 18-3 | 1992 | https://cdnsm5-hosted.civiclive.com/UserFiles/Servers/Server_14877142/File/Government/Departments_Elected%20Offices/Planning,%20Permiting%20&%20Enforcement/ordinance%201983%20zoning.pdf
Washington | Garfield | 53023 | Definition: Geothermal Heat Pump |  |  | "Alternative Energy System (Geothermal)" means "Equipment that transfer thermal energy to and/or from the ground for purposes of heating and/or cooling a building. An alternative energy system (geothermal) consists of a closed-loop system of pipes filled with liquid, a heat exchanger and a heat pump." | 1.01.030 Definitions | 2022 | https://www.garfieldcountywa.gov/media/5741
Washington | Garfield | 53023 | Permit |  |  | The land use matrix lists "Alternative energy facility" as "C-3" in the Agricultural zone and "C" in Agricultural Transition, Commercial, and Industrial zones; Mountain Cabin is "X." The ordinance states: "Allowed (A) means that the land use is allowed outright. Conditional Use (C) means that the land use may be allowed if it is granted approval pursuant to Chapter 1.05." Footnote C-3 adds: "RENEWABLE ENERGY FACILITIES ON AGRICULTURAL LANDS ARE EXEMPT FROM THE ONE ACRE CONVERSION OF AG LAND RULE, HOWEVER, APPLICANTS FOR THESE TYPES OF CONDITIONAL USES SHALL DEMONSTRATE EFFORTS TO FIRST UTILIZE NON-PRODUCTIVE LANDS WITH POOR SOILS THAT ARE NOT OTHERWISE SUITABLE FOR AGRICULTURAL PURPOSES." | 1.03.030 Permitted land uses / Land Use Matrix and C-1, C-2, C-3 footnotes | 2022 | https://www.garfieldcountywa.gov/media/5741
Washington | Garfield | 53023 | Other Prohibitions/Regulations |  |  | The land use matrix lists "Alternative energy facility" as "X" in the Mountain Cabin zone. The matrix legend states: "A - ALLOWED C - CONDITIONAL USE ... X - NOT ALLOWED." | 1.03.030 Permitted land uses / Land Use Matrix | 2022 | https://www.garfieldcountywa.gov/media/5741
Washington | Grant | 53025 | Definition: Geothermal Heat Pump |  |  | Table IV footnote 4 defines 'Closed geothermal loop' as: 'A network of underground piping carrying fluid under pressure used to heat and cool a structure.' | Section 5. Amends WAC 246-272A-0210 Location | 2025 | https://www.granthealth.org/DocumentCenter/View/853
Wisconsin | Shawano | 55115 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump (land use): Electrically powered systems that tap the stored energy of the earth. These systems use the earth's relatively constant temperature to provide heating, cooling, and hot water for homes and commercial buildings. In the FP district, each Ground Source Heat Pump must also meet the standards set forth in Section X.9.03(14) for Agricultural Structures." | X.9.03(140) Ground Source Heat Pump (land use) | 2019 | https://www.co.shawano.wi.us/i_shawano/pu/6-3-19_zoning_ordinance.pdf
California | Calaveras | 6009 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat exchange well" means "any uncased artificial excavation, constructed by any method, that uses the heat exchange capacity of the earth for heating and cooling, in which excavation the ambient ground temperature is thirty (30) degrees Celsius (eighty-six (86) degrees Fahrenheit) or less, and which excavation uses a closed loop, fluid system to prevent the discharge or escape of its fluid into surrounding aquifers or other geologic formations. Geothermal heat exchange wells include ground source heat pump wells." | 8.20.030 Definitions | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Roads | 30 | feet | Setback table: "Adjacent Road Easement where no specified right of way is identified — 30*." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Right of Way | 30 | feet | Setback table: "On-site Road Easement where no specified right of way is identified — 30**" and "Utility Easement — 10." The controlling most restrictive right-of-way/easement setback stated is 30 feet. | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Property Lines | 50 | feet | Setback table: "Property line of parcels that are less than five (5) acres in area — 10" and "Property line of parcels that are five (5) acres or more in area — 50." Because the chapter regulates "geothermal heat exchange wells," the controlling most restrictive property-line setback in this ordinance is 50 feet. | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Building Foundation | 10 | feet | Setback table: "Permanent structure — 10." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Wastewater | 150 | feet | Setback table: "Subsurface sewage leach field or other sewage dispersal area — 100"; "Watertight septic tank — 100"; "Seepage pit or cesspool (The use of cesspools is prohibited.) — 150." The controlling most restrictive wastewater setback is 150 feet. | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Animal Enclosures | 100 | feet | Setback table: "Animal enclosures — 100." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Fuel (below ground) | 150 | feet | Setback table: "Underground storage tank (petroleum products, e.g., gasoline and diesel) — 150." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Sewer Lines | 50 | feet | Setback table: "Any sewer line (e.g., sanitary, industrial, main or lateral or combined storm water drain) — 50." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Setback - Water Bodies | 25 | feet | Setback table: "Surface Water (e.g., ponds, lakes, reservoirs, streams, brooks, flood plains and seasonal drainage channels) — 25." | 8.20.270 Minimum setbacks | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Minimum Well Depth | 20 | feet | Table under 8.20.390(F): "MINIMUM DEPTH OF SEAL BELOW GROUND SURFACE" lists "Vertical geothermal exchange wells — 20." Section 8.20.390(D) also states that if a well is approved within twenty-five (25) feet of a water course, "the annular seal must extend below the bed of the water way for the applicable depth or at least ten (10) feet into an impervious, bedrock layer, whichever is deeper." | 8.20.390 Annular seal | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Permit |  |  | "No person ... shall commence to dig, bore or drill a new well or to deepen, seal, perforate, re-perforate, abandon or destroy, or otherwise commence work on a well in Calaveras County without first having received a permit to do such work." The chapter purpose expressly includes "geothermal heat exchange wells," so this enacted well-permit requirement applies to geothermal heat exchange wells covered by the chapter. | 8.20.050 Permit required | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Inspection |  |  | "The Director, at a minimum, shall conduct the following prescribed inspections: 1. Initial well site inspection; 2. Annular seal inspection; 3. Final well inspection, and 4. Well destruction inspections when required." Also: "Prior to sealing the annular space, the well contractor shall notify the Director and schedule an inspection of the sealing process... No annular seal shall be installed until permission to proceed is given by the Director." | 8.20.590 Inspections | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Licensed Driller |  |  | "No person shall undertake to dig, bore or drill any well, including but not limited to ... geothermal heat exchange well ... unless the person responsible for that construction, alteration, destruction, or abandonment possesses a C-57 Water Well Drilling Contractor license." | 8.20.040 License required | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Certification |  |  | 8.20.040(A): "No person shall undertake to dig, bore or drill any well, including but not limited to ... geothermal heat exchange well ... unless the person responsible for that construction, alteration, destruction, or abandonment possesses a C-57 Water Well Drilling Contractor license." 8.20.030(12): "'C-57 licensed Water Well Drilling Contractor' means any person or company licensed under authority of the State Contractors License Law..." | 8.20.040 License required; 8.20.030 Definitions | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Calaveras | 6009 | Decommissioning |  |  | 8.20.540: "When a well no longer functions as originally designed... or is found or declared to be abandoned, it must be destroyed by a well contractor, under a well permit issued by the Director." 8.20.550 sets destruction requirements, including: "The well shall be filled... from the bottom of the well to a level that is no deeper than twenty-five (25) feet below the ground surface" and "At least twenty (20) feet of sealing material... shall be placed on top of the fill material." | 8.20.540 Mandatory destruction of wells; 8.20.550 Sealing requirements for the destruction of wells | 2008 | https://circlexx.specialdistrict.org/files/a1fdecb42/Printable%20Well%20Ordinance.pdf
California | Lake | 6033 | Maximum Well Depth | 3000 | feet | "The drilling of new geothermal direct use well(s) shall not exceed three thousand (3,000) feet in depth. Wells exceeding two thousand (2,000) feet in depth shall require a major use permit." | (p) Geo-direct use well project | 2020 | https://www.lakecountyca.gov/DocumentCenter/View/12781/Article-27---Uses-Generally-Permitted-PDF
California | Lake | 6033 | Permit |  |  | "Wells exceeding two thousand (2,000) feet in depth shall require a major use permit." "Geothermal direct use wells proposed in conjunction with a project requiring a use permit or specific plan of development approval shall be processed with the larger project." "Geothermal direct use wells with over one thousand (1,000) feet of new road construction or located within five hundred (500) feet of a dwelling or three hundred (300) feet of a lake, perennial or seasonal creek shall require a major use permit." "A geothermal direct use well project with three (3) or more wells shall require a major use permit." "Only geothermal direct use wells utilizing downhole heat exchangers may be processed by a minor use permit. All geothermal direct use wells which remove geothermal fluids from the well bore shall require a major use permit." | (p) Geo-direct use well project | 2020 | https://www.lakecountyca.gov/DocumentCenter/View/12781/Article-27---Uses-Generally-Permitted-PDF
California | Lassen | 6035 | Permit |  |  | The ordinance establishes explicit geothermal permitting under Water Well Management: "Application: Monitoring, Test or Boring, Geothermal Well/Heat Exchange — 170.00 — Per well. Does not include permit to construct or construction inspection" and "Permit to Construct: Geothermal Well/Heat Exchange — 335.00 — Per well." It also includes related permit administration entries: "Permit Extension — 170.00 — Prior to expiration. Per permit," "Reinstatement of Expired Permit — 254.00 — Per permit," and "Drilling without a Permit or Inspection of Unpermitted Well — 254.00 — In addition to application, permit and inspection fees." | 3.18.120 Environmental health fees; s) Water Well Management | 2024 | https://ecode360.com/LA4955/laws/LF2151481.pdf
California | Lassen | 6035 | Inspection |  |  | The ordinance expressly provides for geothermal-related inspections by fee schedule reference: "Application: Monitoring, Test or Boring, Geothermal Well/Heat Exchange — 170.00 — Per well. Does not include permit to construct or construction inspection" and "Drilling without a Permit or Inspection of Unpermitted Well — 254.00 — In addition to application, permit and inspection fees." | 3.18.120 Environmental health fees; s) Water Well Management | 2024 | https://ecode360.com/LA4955/laws/LF2151481.pdf
California | Riverside | 6065 | Definition: Well |  |  | "Geothermal Heat Exchange Well" shall mean any uncased excavation by any method for the purpose of using the heat exchange capacity of the earth for heating and cooling and in which the ambient ground temperature is 86° Fahrenheit (30° Celsius) or less and which uses a closed loop fluid system to prevent the discharge or escape of its fluid into the surrounding aquifers or geologic formations. Geothermal Heat Exchange Wells are also know[n] as ground source heat pump wells (California Water Code 13713). Such wells or boreholes are not intended to produce water or steam. | Section 2.L | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside | 6065 | Permit |  |  | Section 3.A: "No person or entity... shall dig, drill, bore, drive, reconstruct or destroy... (4) geothermal heat exchange well, without first filing a written application to do so with the Department, and receiving and retaining a valid permit as provided herein." Section 3.D: "An application for a permit to construct a... geothermal heat exchange well shall be submitted to the Department on a form and in a manner prescribed by the Department." | Section 3.A; Section 3.D | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside | 6065 | Inspection |  |  | Section 13 requires inspections for certain wells and destruction activities: "A well inspection shall be requested of the Department at least two (2) working days in advance" of specified activities, including "For well and boring destruction: a. During the actual sealing of the well, b. Immediately after all well destruction work has been completed." Section 13.C adds: "If the enforcement agency fails to appear at the well site within 30 minutes of the scheduled time designated for sealing, the well may be sealed without the presence of the enforcement agency." | Section 13 | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside | 6065 | Certification |  |  | Section 3.D.2 requires permit applications to include "The C-57 license number and signature of the person responsible for constructing the well." Section 9 states: "No persons shall engage in any activity listed in Section 3. of this ordinance unless he is... in compliance with the Provisions herein and possesses a valid C57 license in accordance with the California Contractor's State License Law... or possesses a license appropriate to the activity to be engaged in." | Section 3.D.2; Section 9 | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | Riverside | 6065 | Decommissioning |  |  | Section 10 states that standards for "abandonment, or destruction of wells" are those in incorporated state bulletins. Section 22 provides: "If after thirty (30) days of abandonment, the owner has not declared to the Department a proposed reuse of the well per Section 24... and the well has been found by the Department to be a hazard... the Department shall direct the owner to destroy the well, in accordance with Section 10. of this ordinance." It further states: "Upon removal of the pump, the casing shall be provided with a threaded or equivalently secured watertight cap. The well shall be maintained so that it will not be a hazard to public health and safety until such time as it is properly destroyed." Section 24 allows an owner to file a "Declaration of Proposed Reuse" and seek an exemption from destruction requirements. | Section 10; Section 22; Section 24 | 2007 | https://rivcoeh.org/sites/g/files/aldnop361/files/migrated/Portals-0-PDF-Water-Use-Well-682-3.pdf
California | San Diego | 6073 | Definition: Well |  |  | "WELL. Any artificial excavation constructed by any method for the purpose of extracting water from or injecting water into the underground, for providing cathodic protection or electrical grounding of equipment, for making tests or observations of ground water conditions, for using the heat exchange capacity of the earth for heating and cooling, or for any other similar purpose. Wells shall include, but shall not be limited to, community water supply wells, individual domestic wells, commercial wells, industrial wells, agricultural wells, monitoring wells and salt water (hydraulic) barrier wells, as defined herein, geothermal heat exchange wells and other wells whose regulation is necessary to accomplish the purposes of this chapter." | SEC. 67.402. DEFINITIONS AS USED IN THIS CHAPTER. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Diego | 6073 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT EXCHANGE WELL. Any uncased artificial excavation, by any method, that uses the heat exchange capacity of the earth for heating and cooling, in which excavation the ambient ground temperature is 30 degrees Celsius (86 degrees Fahrenheit) or less, and which excavation uses a closed loop fluid system to prevent the discharge or escape of its fluid into surrounding aquifers or other geologic formations. Geothermal heat exchange wells include ground source heat pump wells. Such wells or boreholes are not intended to produce water or steam." | SEC. 67.402. DEFINITIONS AS USED IN THIS CHAPTER. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Diego | 6073 | Permit |  |  | "Applications for permits shall be made to the Director" and must include "a plot plan showing the location of the well and related piping" with listed surrounding features, "the proposed minimum and the proposed maximum depth of the well," "the proposed use of the well," and other specified information. "Each application shall be accompanied by a fee..." and "Permits may also include any other condition or requirement found by the Director to be necessary to accomplish the purposes of this Chapter." Section 67.423a separately provides: "Standards for the construction, repair, reconstruction or destruction of geothermal heat exchange wells shall be as set forth in the Geothermal Heat Exchange Well Draft Well Standards..." | SEC. 67.441. PERMITS. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Diego | 6073 | Inspection |  |  | "The permittee shall notify the Director in writing upon completion of the work and submit a copy of the well drilling log... A final inspection of the work shall be made by the Director unless such inspection is waived by him, and no permittee shall be deemed to have complied with this Chapter or his permit until such inspection has been performed or waived." | SEC. 67.441. PERMITS. | 2020 | https://files.amlegal.com/pdffiles/SanDiegoCo/ord10642.pdf
California | San Mateo | 6081 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat exchange well" means any artificial excavation by any method for the purpose of using the heat exchange capacity of the earth for heating and/or cooling and in which the ambient ground temperature is 86 degrees Fahrenheit or less and which uses a closed loop fluid system to prevent the discharge or escape of its fluid into the surrounding aquifers or geologic formations. Geothermal heat exchange wells are also known as ground source heat pump wells. Such wells or boreholes are not intended to produce water or steam. | 4.68.020(i) Definitions | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo | 6081 | Permit |  |  | "No Person shall dig, bore, deepen, reperforate, excavate, construct, reconstruct, inactivate, convert, destroy or repair any water well, geothermal heat exchange well or cathodic protection well, without first having applied for and obtained a Permit for such activity from the County Health Officer pursuant to the provisions of this chapter. A Permit granted pursuant to this chapter is valid only for the proposed activity listed on the Permit application and solely for the site specified therein." | 4.68.080 Permit for the construction, destruction, inactivation, repair or conversion of a water well, geothermal heat exchange well or cathodic protection well | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo | 6081 | Inspection |  |  | Section 4.68.070 provides that "Permit fees shall be charged for each Permit to cover the cost of inspection and enforcement pursuant to this chapter." Section 4.68.090 requires a geothermal well permit to "be kept available for inspection at the well site during the course of and until completion" of the work. Section 4.68.280 states: "As a condition for the issuance of a Permit under this chapter, the permittee shall allow the County Health Officer or an authorized representative to enter the property where the well is located, upon reasonable notice ... to investigate, examine and test the well and well site." | 4.68.070 Fees; 4.68.090 Placement of Permit on job site; 4.68.280 Right of inspection | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo | 6081 | Licensed Driller |  |  | "Any construction, reconstruction, repair, destruction or conversion of a water well, geothermal heat exchange or cathodic protection well shall be undertaken by a well-driller who possesses a C-57 Water Well Contractor's License as provided by state licensing law." | 4.68.040 Well-driller | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo | 6081 | Certification |  |  | "Any construction, reconstruction, repair, destruction or conversion of a water well, geothermal heat exchange or cathodic protection well shall be undertaken by a well-driller who possesses a C-57 Water Well Contractor's License as provided by state licensing law." | 4.68.040 Well-driller | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | San Mateo | 6081 | Decommissioning |  |  | Section 4.68.050 requires: "Upon completion of the construction, destruction or conversion of the well, the site shall be restored as near as possible to its original condition, and appropriate erosion control measures shall be implemented. Site restoration is the responsibility of the property owner and must be implemented within 60 days of the completion of the well, and not more than a year from the date of the Permit issuance." Section 4.68.410 states: "It is unlawful to maintain an abandoned well. Any Person owning property upon which an abandoned well is located shall obtain a Permit to destroy or inactivate the well." | 4.68.050 Mitigation of disturbance at well site; 4.68.410 Abandoned wells | 2002 | https://www.smchealth.org/sites/main/files/file-attachments/well_ordinance_209-19-2002.pdf?1664562381
California | Sonoma | 6097 | Definition: Geothermal Heat Pump |  |  | "Accessory renewable energy system: An on-site renewable energy system, including but not limited to wind, bioenergy, solar, low-temperature geothermal heating systems, geothermal heat pump systems, and fuel cells and combinations thereof, where the energy generated is used primarily to meet the energy demands of the lawful use on the property where the system is located." | Section 26-02-140, Definitions | 2013 | https://sonomacounty.gov/administrative-support-and-fiscal-services/county-administrators-office/ordinance-6046
Colorado | Boulder | 8013 | Definition: Geothermal Heat Pump |  |  | 'Renewable Energy Systems' means: 'Any renewable energy systems which meet the intent of the required on-site renewable energy offset required by other Sections of this code, including solar thermal systems, solar photovoltaic electric systems, geothermal heating systems, wood and pellet burning stoves, boilers, or furnaces, small scale wind generation systems, and other similar systems.' | N1101.3.1 Definitions | 2013 | https://bouldercounty.gov/wp-content/uploads/2017/03/buildsmart-code-2012.pdf
Colorado | Larimer | 8069 | Permit |  |  | "Any owner or owner's authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any electrical, gas, mechanical or plumbing system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." | R105.1 Required | 2022 | https://www.larimer.org/sites/default/files/uploads/2022/2021_irc_amendments_final_1.pdf
Colorado | Larimer | 8069 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to or concurrent with framing inspection. Exception: Backfilling of ground-source heat pump loop systems tested in accordance with Section M2105.28 prior to inspection shall be permitted." | R109.1.2 Plumbing, mechanical, gas and electrical systems inspection | 2022 | https://www.larimer.org/sites/default/files/uploads/2022/2021_irc_amendments_final_1.pdf
Colorado | Pitkin | 8097 | Permit |  |  | "Compliance with this section will be documented via the free Public Domain tool 'Pitkin County REMP Calculation Sheet' in the most current version at the time of permit application." Also, exterior energy uses "may be installed only if the supplemental energy meets the requirements of Appendix A. This applies to all installations for which an application for a permit or renewal of an existing permit is filed or is by law required to be filed with or without an associated Building Permit." | APPENDIX A: Section 101.1 Scope / Section 101.1.2 Exterior Energy Uses | 2024 | https://pitkincounty.com/DocumentCenter/View/32667/boccord0042024
Colorado | Pitkin | 8097 | Inspection |  |  | "Each ground source heat pump system shall be tested and balanced and commissioned in accordance with C408." | APPENDIX A: Section 106 Ground Source Heat Pump (GSHP) | 2024 | https://pitkincounty.com/DocumentCenter/View/32667/boccord0042024
Colorado | Pitkin | 8097 | Certification |  |  | "The design engineer shall certify in writing that it meets or exceeds the design coefficient of performance (COP) as specified in the 'Pitkin County REMP Calculation Sheet'. The ground loop system must be designed by a CGD (Certified Geo Exchange Designer certified by the Association of Energy Engineers) or a Professional Engineer licensed in the State of Colorado or an IGSHPA (International Ground Source Heat Pump Association) certified designer. The mechanical system must be installed by a certified IGSHPA contractor." | APPENDIX A: Section 106 Ground Source Heat Pump (GSHP) | 2024 | https://pitkincounty.com/DocumentCenter/View/32667/boccord0042024

## Municipal-Level
This data was collected with the help of generative AI. The Large Language Models used for this effort make mistakes. Always validate the data for critical use cases.
State | County | Subdivision | County Subdivision FIPS Code | Feature | Value | Units | Summary | Section | Ordinance Year | Source URL
Delaware | Sussex | Laurel-Delmar | 1000591628 | Permit |  |  | "Private wells are permitted for geothermal heating and cooling and must be approved by DNREC and Town of Laurel prior to installation." | §170-35.B. Wells | 2009 | https://delawaresourcewater.org/wp-content/uploads/2013/05/Laurel_ord2009_14.pdf
Delaware | Sussex | Laurel-Delmar | 1000591628 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal wells shall be permitted in the Town of Laurel..." | §170-35.B. Wells | 2009 | https://delawaresourcewater.org/wp-content/uploads/2013/05/Laurel_ord2009_14.pdf
Delaware |  | Blades | 1006730 | Open-loop Prohibitions |  |  | "Only vertical loop closed systems will be allowed in the Town of Blades. No horizontal, pond, or open loop systems permitted." | Section 33. GEOTHERMAL HEATING SYSTEMS | 2007 | https://blades.delaware.gov/files/2014/07/411-Water-Service-within-the-Town-of-Blades-Effective-10.08.2012.pdf
Delaware |  | Blades | 1006730 | Other Prohibitions/Regulations |  |  | "Only vertical loop closed systems will be allowed in the Town of Blades. No horizontal, pond, or open loop systems permitted." | Section 33. GEOTHERMAL HEATING SYSTEMS | 2007 | https://blades.delaware.gov/files/2014/07/411-Water-Service-within-the-Town-of-Blades-Effective-10.08.2012.pdf
Delaware | Sussex | Millsboro | 1047940 | Other Prohibitions/Regulations |  |  | "Geothermal heating/cooling systems shall not be connected to the Town's public water system. Such system shall be served solely by private wells subject to federal, state, county, and Town regulations." | § 206-1 Connection required. | 2024 | https://ecode360.com/8027891
Florida | Volusia | DeBary-Orange | 1212790793 | Screening |  |  | "Service areas and mechanical equipment located on the ground ... shall be located in the rear or to the side of buildings and screened from public view ... Screening shall, at a minimum, be at the same height as the equipment." Also, "If mechanical equipment is located at-grade, and is visible from an adjacent street or sidewalk, it shall be inset into the building façade and screened with doors, or screened by a fence or street wall ... mechanical equipment shall include any heating, ventilation, and air conditioning (HVAC) or electrical machinery ... generators, geothermal wells, and similar elements." | Sec. 5.34. Service Areas and Mechanical Equipment | 2024 | https://debary.org/DocumentCenter/View/969/2024-Land-Development-Code
Florida |  | DeBary | 1216675 | Screening |  |  | Sec. 5.34(a): "Service areas and mechanical equipment ... shall be located in the rear or to the side of buildings and screened from public view ... Screening shall, at a minimum, be at the same height as the equipment." Sec. 5.34(b): if visible from a street or sidewalk, equipment "shall be inset into the building façade and screened with doors, or screened by a fence or street wall"; the definition of mechanical equipment includes "generators, geothermal wells, and similar elements." Sec. 5.34(c): "All rooftop mounted equipment and appurtenances shall be fully screened from view from all public rights-of-way." | Sec. 5.34. Service Areas and Mechanical Equipment | 2024 | https://mccmeetings.blob.core.usgovcloudapi.net/debaryfl-pubu/MEET-Packet-5f732c36ab36436db587e8dac069e437.pdf
Florida |  | Holmes Beach | 1232150 | Screening |  |  | "Allowable encroachments into the secondary front yard setback... Heat and pool pumps not exceeding 48 inches in height (measured from adjacent grade) and used to heat a swimming pool, provided the unit is ... screened to a height equal to or greater than the height of the heat pump by vegetation a hedge along all sides of the heat pump that do not face exterior wall of the principal structure." | Section 2; 6.8 - Supplemental development standards, Z. Permitted setback Yard encroachments, 7.8 | 2024 | https://pub-holmesbeachfl.escribemeetings.com/filestream.ashx?DocumentId=3155
Florida |  | Jacksonville | 1235000 | Definition: Geothermal Heat Pump |  |  | "RR. Water Cooled Heat Pumps or Water Source Heat Pump: Single or reverse cycle mechanical devices for heating or cooling which require the use of water as a medium for heat transfer." Also under "V. Heat Pump Systems": "2. Earth Coupled Closed Loop - a closed tube heat exchanger installed in the ground either vertically or horizontally and filled with International Ground Source Heat Pump Association (IGSHPA) approved fluid circulating under pressure between the loop and the heat pump." | 8.102 Definitions | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | 1235000 | Setback - Wastewater | 50 | feet | "Injection wells shall be no closer than 50 feet from any potential source of contamination such as a septic tank or drainfield and shall not adversely impact the operation of on-site waste treatment or drainage systems." | 8.805 Water Cooled Heat Pumps (Geothermal Heat Pump Systems) | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | 1235000 | Permit |  |  | "Unless expressly exempted by Florida Statutes or Chapter 40C-3, FAC, a well construction permit must be obtained from the Department prior to the construction, repair or abandonment of all wells less than six (6) inches in diameter." Rule 8.806 also states: "A well construction permit shall be required for all injection wells." | 8.503 Permit Requirements; 8.806 Injection Wells | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | 1235000 | Inspection |  |  | "Inspection of well construction, repair and abandonment will be conducted by the Department." Also, "Upon completion of well construction, but prior to installation of any pumping related items or other well or site changes that might limit access to the well, the property owner or authorized agent shall notify the Department and may be required to make the well available for down hole logging or other testing by the Department or its representatives, if requested." | 8.509 Inspections | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | 1235000 | Certification |  |  | Rule 8.805 states: "No substances shall be introduced into closed loop installations other than IGSHPA approved fluids." Rule 8.601 requires annual contractor registration by filing "a copy of the current State Water Well Contractor license and/or certification with the Department." | 8.805 Water Cooled Heat Pumps (Geothermal Heat Pump Systems); 8.601 Registration Required | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | 1235000 | Decommissioning |  |  | "All well abandonments regulated by the Department under this Rule shall be done in accordance with the standards and requirements of Rules 62-532.440 and 40C 3.531, FAC." Further, if violations are found, "the Department may require the well to be properly abandoned or plugged... If abandonment is required, the property owner or applicant must properly abandon the well within 30 days of notification by the Department." | 8.804 Well Abandonment Requirements; 8.507 Criteria for Permit Issuance, Denial or Revocation | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Jacksonville | 1235000 | Other Prohibitions/Regulations |  |  | "Heat Pump injection wells are prohibited on a Superfund or ash site subject to an EPA Consent Decree or on a site with institutional controls where the use of groundwater or the installation of wells is restricted." | 8.805 Water Cooled Heat Pumps (Geothermal Heat Pump Systems) | 2011 | https://www.jacksonville.gov/getContentAsset/97dd2ad8-b95a-4cfc-b337-4f8b48013c6b/135b97c9-84fa-4e82-b956-0fbccec4aa1f/JEPB-Rule-8-Sept-2014.pdf?language=en
Florida |  | Lake Alfred | 1237525 | Definition: Geothermal Heat Pump |  |  | "Renewable energy devices and other sustainable development technologies including, but not limited to, solar photovoltaic (pv) panels, solar hot water, solar pool heaters, tankless water heaters, geothermal heat pumps, gray-water systems, and rainwater harvesting devices, such as rain barrels and cisterns." | Sec. 3.8. Accessory Uses and Structures Defined | 2025 | https://www.mylakealfred.com/DocumentCenter/View/2510/Unified-Land-Development-Code-ULDC---Interim-SB180---Effective-11032025
Florida |  | Lake Alfred | 1237525 | Screening |  |  | "Renewable energy devices and other sustainable development technologies including... geothermal heat pumps... Development standards within residential districts. Ancillary equipment shall comply with the following: ... Screening. The sides of any new or replacement equipment facing or visible from a street, excluding alleys, shall be landscaped as required in the landscaping and irrigation section, unless installed above the ground story." | Development standards within residential districts | 2025 | https://www.mylakealfred.com/DocumentCenter/View/2510/Unified-Land-Development-Code-ULDC---Interim-SB180---Effective-11032025
Florida | Volusia | Ormond Beach | 1253150 | Definition: Geothermal Heat Pump |  |  | "Open-loop heat pump system means a two-well (2) installation consisting of supply and injection wells into the same aquifer for thermal transfer." Also, "Open recharge heat pump system means a single-well installation producing water from an aquifer and partially returning water through infiltration to the aquifer of origin." |  | 2023 | https://library.municode.com/fl/ormond_beach/codes/land_development_code?nodeId=CH1GEAD_ARTIIADEN_S1-15PLBO
Florida | Pinellas | St. Petersburg | 1263000 | Definition: Geothermal Heat Pump |  |  | 'For the purposes of this section, "ancillary equipment" means: ... Renewable energy devices and other sustainable development technologies including, but not limited to, solar photovoltaic (pv) panels, solar hot water, solar pool heaters, tankless water heaters, geothermal heat pumps, gray-water systems and rainwater harvesting devices, such as rain barrels and cisterns.' | 16.50.020.4.2. - Ancillary equipment |  | https://cms5.revize.com/revize/stpete/Residential%20LDR%20Update%202024-2025.pdf
Florida | Pinellas | St. Petersburg | 1263000 | Screening |  |  | 'The sides of any new or replacement equipment facing or visible from a street, excluding alleys, shall be landscaped as required in the landscaping and irrigation section, except that equipment installed above the first floor [shall be] screened with material that is compatible with the architectural style of the principal structure, landscaping, or a six-foot-tall decorative fence or wall.' Also, 'In all other zoning districts ... All ancillary equipment shall be shielded from view from the adjacent properties and streets, excluding alleys, by a solid enclosure such as a fence or wall.' | 16.50.020.4.2. - Ancillary equipment |  | https://cms5.revize.com/revize/stpete/Residential%20LDR%20Update%202024-2025.pdf
Idaho | Ada | Boise City | 1608830 | Permit |  |  | "Any person desiring to connect a building or structure to the City geothermal system may apply for such service connection with the Department of Public Works on forms provided for that purpose. The Director of Public Works, or his authorized representative, shall approve or deny said application within thirty (30) days of its filing." Also, "It shall be a violation of this chapter for any person to construct or cause the construction of a service line or tap-in without approval of the Department of Public Works." | 10-3-3: SERVICE CONNECTION PROCEDURES | 2021 | https://codelibrary.amlegal.com/codes/boise_id/latest/boise/0-0-0-12610
Idaho | Ada | Boise City | 1608830 | Inspection |  |  | "Upon completion of the permitted service connection, the applicant shall promptly notify the Department of Public Works to request a service connection inspection." "Upon inspection by the Department of Public Works, the applicant may be required to reperform his work... if... the initial service connection work does not comply..." "All requests for inspection must be made to the Department of Public Works at least twenty four (24) hours prior to the requested inspection." "Should the applicant... connect facilities to the geothermal system without the facilities being inspected and approved by the Department of Public Works, the party responsible... shall be required... to excavate the connection, if necessary, and disconnect the connection... in order that a proper inspection can be made." | 10-3-3(F), (H), (I): SERVICE CONNECTION STANDARDS AND INSPECTIONS; INSPECTION; FAILURE TO INSPECT | 2021 | https://codelibrary.amlegal.com/codes/boise_id/latest/boise/0-0-0-12610
Idaho | Blaine | Carey | 1612790 | Definition: Geothermal Heat Pump |  |  | "Underground Injection Well (closed system). Closed-loop systems use an underground network of sealed, high-strength plastic piping, which acts as the earth-coupled heat exchanger. The most commonly used closed-loop piping material is high-density polyethylene (HDPE). The ground loop piping is filled with a working fluid that is continuously re-circulated without ever directly contacting the soil or water in which the loop is buried or immersed. Once filled with fluid and purged of air, nothing enters or leaves the closed loop. This eliminates the potential shortcomings of water quality and availability associated with open-loop systems." | Section 2 (W) Underground Injection Well (closed system) | 2022 | https://www.cityofcarey.org/local-codes-regulations/files/zoning-ordinance
Idaho | Blaine | Carey | 1612790 | Permit |  |  | "Whenever there is a request that requires a Conditional Use Permit for land lying within a Drinking Water Protection Zone, the Commission shall make recommendations to the Council which shall make the final decision. Both entities shall hold a duly noticed public hearing on the application at its earliest convenience." Also, Sections 10.5(i), 10.6 10.65, and 10.75 allow certain hazardous-material-related uses "except upon issuance of a Conditional Use Permit." | SECTION 10.8 CONDITIONAL USE PERMIT PROCESS | 2022 | https://www.cityofcarey.org/local-codes-regulations/files/zoning-ordinance
Idaho | Blaine | Carey | 1612790 | Other Prohibitions/Regulations |  |  | Section 10.5(d) states: "Injection well except for the following: (1) Closed systems." In Zone 1B, injection wells are prohibited except closed systems, so non-closed geothermal/open injection well configurations are banned there while closed systems remain allowed. | SECTION 10.5 PROHIBTED USES WITHIN ZONE 1B OF THE DRINKING WATER PROTECTION AREA | 2022 | https://www.cityofcarey.org/local-codes-regulations/files/zoning-ordinance
Illinois | McHenry | Algonquin | 1700685 | Definition: Geothermal Heat Pump |  |  | "Geothermal heating and cooling system installed." | Section 21.4(Q) Density Bonuses for Open Space and Innovative Design | 2003 | https://www.algonquin.org/egov/documents/1663162194_91694.pdf
Illinois | McHenry | Algonquin | 1700685 | Permit |  |  | "No application for a building permit or other permit or license or for a certificate of occupancy shall be approved... that would authorize the use or change in use of any land or building contrary to the provisions of this Chapter..." and "No Village building permit shall be issued until the appropriate local, state, or federal agencies have issued all necessary permits for the particular use." | Section 21.4(F) PERMITS | 2003 | https://www.algonquin.org/egov/documents/1663162194_91694.pdf
Illinois |  | Arlington Heights | 1702154 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System. A renewable energy system using equipment that circulates relatively constant ground temperatures throughout buildings using an underground based piping system and a heat pump." | Section 28-3 - Definitions | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | 1702154 | Setback - Right of Way | 3 | feet | Section 6.17-1(a)(3) states: "The system shall not be located within any utility easements, unless permission is granted by the applicable public and private agencies." Section 6.17-1(b)(3) adds: "The system shall be setback at least three feet from all lot lines." | Section 28-6 - General Provisions; 6.17-1(a)(3) and 6.17-1(b)(3) | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | 1702154 | Setback - Property Lines | 3 | feet | "The system shall be setback at least three feet from all lot lines." | Section 28-6 - General Provisions; 6.17-1(b)(3) | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | 1702154 | Permit |  |  | "No application for a building permit or other permit or license, or for a certificate of occupancy, shall be approved... and no permit or license shall be issued... which would authorize the use or change in use of any land or building contrary to the provisions of this Code..." This applies to geothermal energy systems because Section 6.17 establishes geothermal-specific zoning standards within this Code. | Section 28-6 - General Provisions; 6.4 Permits | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Arlington Heights | 1702154 | Other Prohibitions/Regulations |  |  | Geothermal systems are limited as follows: "The system shall be used only for the property on which it is located." "The system shall not be located within any utility easements, unless permission is granted by the applicable public and private agencies." "Each zoning lot is permitted one geothermal system." | Section 28-6 - General Provisions; 6.17-1(a)(1), 6.17-1(a)(3), 6.17-1(b)(1) | 2024 | https://library.municode.com/il/arlington_heights/codes/municipal_code?nodeId=CH28ZORE
Illinois |  | Deerfield | 1718992 | Definition: Geothermal Heat Pump |  |  | 'Geothermal Energy System: A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems.' | 2.10-B Definitions | 2015 | https://www.deerfield.il.us/DocumentCenter/View/621/Article-2-General-Provisions-PDF
Illinois |  | Deerfield | 1718992 | Permit |  |  | 'Geothermal Energy Systems shall be allowed as a Permitted Use in any zoning district, provided that a building permit is obtained and all permit requirements and general regulations are met, including: the Building Code, the Zoning Ordinance, the Lake or Cook County Health Ordinance (whichever is applicable based on the property's location), and the requirements referenced herein.' Also: 'An application for permit for all Geothermal Energy Systems shall contain the following information' including applicant/contact information and a 'Project summary including site plan and manufacturer information with specifications of materials and devices.' | 2.10-E Geothermal Energy Systems, 1. General Requirements; 2. Application Requirements | 2015 | https://www.deerfield.il.us/DocumentCenter/View/621/Article-2-General-Provisions-PDF
Illinois |  | Deerfield | 1718992 | Certification |  |  | 'Geothermal Energy System components shall conform to applicable industry standards including those of the American National Standards Institute (ANSI). Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by Underwriters Laboratories (UL) or other approved independent testing agency.' | 2.10-E Geothermal Energy Systems, 1. General Requirements | 2015 | https://www.deerfield.il.us/DocumentCenter/View/621/Article-2-General-Provisions-PDF
Illinois |  | East Dundee | 1721696 | Definition: Geothermal Heat Pump |  |  | "A GES is a central renewable heating and cooling exchange system that uses heat generated beneath the earth's surface to heat or cool buildings via underground or underwater systems that pump heat energy into a building or visa versa. Geothermal energy systems use the earth as a heat source in the winter or a heat sink in the summer." "Geothermal heat pump energy systems, or ground source heat pumps, are installed indoors and underground via a system of looped coils or piping and invisible after installation..." | SECTION 6-314.F. Geothermal Energy System (GES) Regulations; 1. Geothermal Heat Pump System (GHPS) | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Setback - Right of Way | 10 | feet | "GHPS loop fields, coils, piping or other similar underground infrastructure shall not encroach into public right-of-ways, ComEd transmission easements and right-of-ways, access roads, natural gas, fuel and other pipeline easements..." and "GHPS must maintain a minimum distance of ten (10') feet from existing storm water, sewer and water main utilities..." | SECTION 6-314.F.1.b Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Setback - Building Foundation | 20 | feet | "GHPS must maintain a minimum distance of ... twenty (20') feet from neighboring buildings or structures (except parking lots)." | SECTION 6-314.F.1.b Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Setback - Water Lines | 10 | feet | "GHPS must maintain a minimum distance of ten (10') feet from existing storm water, sewer and water main utilities..." | SECTION 6-314.F.1.b Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Setback - Sewer Lines | 10 | feet | "GHPS must maintain a minimum distance of ten (10') feet from existing storm water, sewer and water main utilities"; for irrigated systems, "Such systems must maintain a minimum distance of ten (10') feet from existing storm water infrastructure, such as culverts, and sewer utilities." | SECTION 6-314.F.1.b Setbacks; SECTION 6-314.F.2.b Width and Setbacks | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Minimum Well Depth | 8 | feet | For irrigated geothermal heat pump systems, "Loop fields, coils, pipes or other similar and associated underground/underwater infrastructure must be below the frost line and a minimum of eight (8') feet below the normal water line of a detention/retention basin." Section 6-314.F.1.a also states: "GHPS loop fields, coils, piping or other similar and associated underground infrastructure must be below the frost line." | SECTION 6-314.F.2.a Depth | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Permit |  |  | "Petitioners seeking to construct or install an ECT must submit a complete petition to the Development Services Department and apply for building permits." ECTs "include but are not limited to ... geothermal energy systems (GES)." Also, "Geothermal heat pump energy systems, or ground source heat pumps, are ... permitted in all zoning districts via an ECT Review" and "The necessary building permits shall be obtained for a GES per the Village Building Code (e.g. electrical, plumbing, mechanical etc.)." | SECTION 6-314.C. Environmental Clean Technology Review and Notification Process; SECTION 6-314.F.3.f Design and Permitting | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Dundee | 1721696 | Other Prohibitions/Regulations |  |  | "A GES shall access the earth's thermal energy below grade and shall not be visible from the public right-of-way or neighboring properties." "Tree removal for a GES is not permitted." | SECTION 6-314.F.3.a Access; SECTION 6-314.F.3.1 Tree Removal | 2015 | https://eastdundee.net/Ordinances%20and%20Resolutions/2015/Resolutions/res1715.pdf?t=202308231542250
Illinois |  | East Moline | 1722073 | Definition: Geothermal |  |  | "Geothermal Energy. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | 1722073 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump System refers to a system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site. Closed Loop Ground Source Heat Pump System refers to a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | 1722073 | Setback - Yards | 5 | feet | "All components of Ground Source Heat Pump System including pumps, borings and loops shall be set back at least five (5) feet from interior and rear lot lines." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | 1722073 | Certification |  |  | "Only closed loop Ground Source Heat Pump System utilizing Illinois Department of Public Health approved heat transfer fluids are permitted." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | 1722073 | Decommissioning |  |  | "A Ground Source Heat Pump System that is allowed to remain in a nonfunctional or inoperative state for a period of twelve (12) consecutive months, and which is not brought in operation within the time specified by the city after notification to the owner or operator of the Ground Source Heat Pump System, shall be presumed abandoned and may be declared a public nuisance subject to removal at the expense of the operator." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | 1722073 | Open-loop Prohibitions |  |  | "Only closed loop Ground Source Heat Pump System utilizing Illinois Department of Public Health approved heat transfer fluids are permitted." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | East Moline | 1722073 | Other Prohibitions/Regulations |  |  | "Ground Source Heat Pump System are prohibited in surface waters, except for storm water ponds where they are permitted." | 20. Solar Energy Systems, E. Geothermal Energy | 2019 | https://www.eastmoline.com/389/Zoning-Ordinance
Illinois |  | La Grange | 1740767 | Inspection |  |  | "All testing as required by this Subsection shall be witnessed by the Building Official or his designee. An inspection performed by the Building Official or his designee shall be required prior to the closing of any trench or ground opening associated with ground source heat pump system loop piping." | § 150.23 INTERNATIONAL RESIDENTIAL CODE, (B)(73) Subsection M2105.1 | 2021 | https://lagrangeil.gov/DocumentCenter/View/2709/Code-Update-Draft-for-Publication-6-1-21
Illinois |  | Lake Barrington | 1740884 | Other Prohibitions/Regulations |  |  | "Geothermal Energy Systems shall be prohibited within all Zoning Districts of the Village as they present a risk to the aquifer which is relied upon by most of the Village for its potable water supply." | 8-3-12-5: PROHIBITED RENEWABLE ENERGY SYSTEMS | 2023 | https://codelibrary.amlegal.com/codes/lakebarringtonil/latest/lakebarrington_il/0-0-0-23666
Illinois | Lake | Lake Villa | 1741586 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM: A system which utilizes renewable energy generated from the interior of the Earth and used to produce energy for heating buildings or serving building commercial or industrial processes. A geothermal energy system does not include systems that use energy independent of the geothermal source to raise the temperature of the extracted heat, such as heat pumps." | 10-2-2: DEFINITIONS AND ABBREVIATIONS | 2024 | https://codelibrary.amlegal.com/codes/lakevillail/latest/lakevilla_il/0-0-0-7271
Illinois |  | Oak Brook | 1754534 | Setback - Property Lines | 10 | feet | "1301.7.1. No geothermal well or water intake shall be located in any easement and/or within ten feet (10') from any property lot line." The same requirement appears in IMC 303.10.1: "No geothermal well or water intake shall be located in any easement and/or within ten feet (10') from any property lot line." | 1301.7.1; 303.10.1 | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois |  | Oak Brook | 1754534 | Permit |  |  | The code states that permits are generally required except for listed exemptions: "105.2 Work Exempt From Permit. Exemptions from permit requirements of this code shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code... Permits shall not be required for the following... Mechanical: 1. Portable heating appliance... 3. Portable cooling unit... 4. Steam, hot or chilled water piping within any heating or cooling equipment regulated by this code..." The same structure appears in the residential code at "R105.2 Work Exempt From Permit." The code also provides: "109.2 Schedule Of Permit Fees. On buildings, structures, electrical, gas, mechanical and plumbing systems or alterations requiring a permit, a fee for each permit shall be paid..." and IMC "106.5.2 Fee Schedule. On buildings, structures, electrical, gas, mechanical and plumbing systems or alterations requiring a permit, a fee for each permit shall be paid..." | 105.2 Work Exempt From Permit; R105.2 Work Exempt From Permit; 106.5.2 Fee Schedule | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois |  | Oak Brook | 1754534 | Inspection |  |  | "Any 90 day period of validity shall commence when the permit is issued, each time the work is inspected by the building official, or when an extension is granted by the building official." The residential code similarly states: "Any 90 day period of validity shall commence when the permit is issued, each time the work is inspected by the building official, or an extension is granted by the building official." | 105.5.2 Method For Determining Permit Expiration Date; R105.5.2 Method For Determining Permit Expiration Date | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois |  | Oak Brook | 1754534 | Screening |  |  | The ordinance requires concealment of exterior mechanical equipment: "M1301.6 Mechanical Equipment To Be Screened. All exterior heating, air conditioning, ventilating, generators, pool heaters, or other mechanical equipment shall be fully screened to prevent view of the equipment from any point along the finished grade at any front lot line or side lot line of the lot on which the equipment is located. Screening materials shall be as approved by the building official. Deciduous or annual plants shall not be approved as screening materials." Similar language appears in IMC 303.11 and IBC 2801.2 requiring exterior mechanical equipment to be "fully screened to prevent view." | M1301.6 Mechanical Equipment To Be Screened; 303.11 Mechanical Equipment To Be Screened; 2801.2 Exterior Mechanical Equipment To Be Screened | 2022 | https://codelibrary.amlegal.com/codes/oakbrookil/latest/oakbrook_il/0-0-0-6449
Illinois | Cook | Oak Park | 1754885 | Definition: Geothermal Heat Pump |  |  | "All heating and air conditioning shall be provided by cold climate air source or ground source heat pumps." | APPENDIX P, SECTION P301 - ELECTRIFICATION REQUIREMENTS | 2023 | https://codelibrary.amlegal.com/codes/oakparkil/latest/oakpark_il/0-0-0-2372
Illinois | Cook | Oak Park | 1754885 | Permit |  |  | "Any owner or owner's authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical or plumbing system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." Appendix P also expressly regulates geothermal HVAC use: "All heating and air conditioning shall be provided by cold climate air source or ground source heat pumps." | SECTION 105 - PERMITS; 105.1 Required | 2023 | https://codelibrary.amlegal.com/codes/oakparkil/latest/oakpark_il/0-0-0-2372
Illinois | Cook | Oak Park | 1754885 | Inspection |  |  | For emergency work affecting "heating, air conditioning, or other essential utility service," work may begin before a permit only if "(1) the work is performed in conformance with this code; (2) a permit is obtained the next regular work day; and (3) the work is inspected and approved within 48 hours of permit issuance." | SECTION 105 - PERMITS; Emergency Work | 2023 | https://codelibrary.amlegal.com/codes/oakparkil/latest/oakpark_il/0-0-0-2372
Illinois |  | Orland Park | 1756640 | Definition: Geothermal |  |  | "Renewable Energy. Refers to energy derived from existing flows of energy generated by on-going natural processes, including, but not limited to, energy generated from the sun, flowing water, wind flows, and geothermal heat flows." | SECTION 2 | 2010 | https://orlandpark.legistar.com/LegislationDetail.aspx?ID=7810611&GUID=4B86E6FD-2564-4ACA-95E6-B39B94A2EA39&Options=&Search=&FullText=1
Illinois |  | Orland Park | 1756640 | Definition: Geothermal Heat Pump |  |  | "Environmental/Clean Technology (ECT). ... Includes renewable energy (wind, solar, hydro, geo, and biomass), information technology, sustainable transportation, electric motors, lighting and other appliances and systems such as devices that are sustainable and part of or accessory to a building or site as a feature, and/or a utility that serves multiple economic and environmental purposes including, but not limited to, ... ground source heat pumps ..." | SECTION 2 | 2010 | https://orlandpark.legistar.com/LegislationDetail.aspx?ID=7810611&GUID=4B86E6FD-2564-4ACA-95E6-B39B94A2EA39&Options=&Search=&FullText=1
Illinois |  | South Barrington | 1770564 | Noise Limits | 50 | dBA | Under "Location And Manner of Installation," alternative energy systems are subject to: "Sound: Sound may not exceed fifty (50) dB at lot line." | 10-6-4(A)(3)(b) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | 1770564 | Maximum Well Depth | 20 | feet | "Closed Loop Systems: Geothermal heat pump systems are limited to a maximum below-ground depth of twenty feet (20')." | 10-6-4(C)(2) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | 1770564 | Permit |  |  | "Building Permit Required: A building permit must be obtained before the installation of any alternative energy system." | 10-6-4(A)(2) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | 1770564 | Inspection |  |  | "System Testing: Pipes for geothermal systems permitted under this section must be tested hydrostatically at 1.5 times the maximum system design pressure, but not less than 100 psi (689 kPa), for a duration of not less than fifteen (15) minutes. All geothermal systems must be pressure checked by a licensed geothermal system contractor every five (5) years from the date of its initial successful test. Results must be filed with the building officer. If the test results show the system fails to meet these requirements, system shutdown and repairs must be made at the direction of the building officer." | 10-6-4(C)(3) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | 1770564 | Certification |  |  | "Drilling: Any and all drilling associated with the installation of a ground source heat pump system must be performed by a certified geothermal drill operator." | 10-6-4(C)(4) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | 1770564 | Decommissioning |  |  | "When any alternative energy system equipment has become inoperable or damaged for a period of one hundred and eighty (180) days or more, or otherwise violates the requirements of this ordinance, it is deemed abandoned. The owner of abandoned alternative energy system equipment must remove the alternative energy system equipment within thirty (30) days following the mailing of written notice that removal is required... Upon removal the site must be restored to the condition that existed before installation of the equipment." | 10-6-4(A)(1) Inoperable or Damaged Equipment | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois |  | South Barrington | 1770564 | Open-loop Prohibitions |  |  | "Open Loop Systems: Open loop systems are prohibited." | 10-6-4(C)(1) | 2025 | https://codelibrary.amlegal.com/codes/southbarringtonil/latest/southbarrington_il/0-0-0-25120
Illinois | Whiteside | Sterling | 1772546 | Setback - Wastewater | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Setback - Private Water | 50 | feet | "Closed-loop and direct exchange wells shall be sited at least 50 feet from private potable water supply wells." | Sec. 102-631(E)(6)(a)(iv) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Setback - Animal Enclosures | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Setback - Fuel (above ground) | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Setback - Water Bodies | 10 | feet | "Closed-loop and direct exchange wells shall be sited at least ten feet from surface water bodies." | Sec. 102-631(E)(6)(a)(vii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Setback - Hazardous Materials/Fertilizers | 25 | feet | "Open-loop GSHP wells that do not also serve as a potable water supply source shall be sited at least 25 feet from existing and potential sources of contamination including, but not limited to septic tanks/fields, lagoons, livestock pens, and oil or hazardous materials storage tanks." "Closed-loop and direct exchange wells shall also be sited at least 25 feet from these potential sources of contamination." | Sec. 102-631(E)(6)(a)(ii)-(iii) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Permit |  |  | "The owner/operator/installer of the GSHP system shall submit to the city a BSO plan and comply with the regulations outlined in section 102-924." "A City of Sterling Zoning Permit shall be required as outlined under section 102-910." "A City of Sterling Building Permit shall be required as outlined under chapter 18 of the Municipal Code." "The owner/operator/installer of the GSHP system shall submit to the building and zoning superintendent approval for the system by the IDPH." "Prior to the construction of a gshp system, the owner/operator/installer must submit to the IDPH a notification of intent to construct. This notification requirement includes GSHP systems that do not include the use of wells." | Sec. 102-631(E)(1)-(3) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Licensed Driller |  |  | "Only contractors complying with 77 Ill. Adm. Code Part 915 shall be permitted to construct, alter, or decommission wells for geothermal heating and cooling systems." | Sec. 102-631(E)(4)(a) - Contractors, Well drilling | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Certification |  |  | "All construction plans must be designed and stamped by a professional engineer licensed in the State of Illinois or an individual that is certified by the ... International Ground Source Heat Pump Association (IGSHPA)." "All plumbing installation/modification shall be performed by a licensed Illinois plumber." "The installation or modification of all GSHP equipment shall be performed by an individual certified by the IGSHPA." | Sec. 102-631(E)(1), (4)(b), (4)(c) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois | Whiteside | Sterling | 1772546 | Other Prohibitions/Regulations |  |  | "GSHP wells or systems shall not be located, constructed, or operated in a manner that will cause further degradation of aquifers, wetlands, or surface water bodies." "The use of refrigerants, antifreeze chemicals, and lubricating oils is prohibited in water that is returned to the subsurface via openloop GSHP systems." "The use of plasticizers in grout used in well construction is prohibited for open-loop GSHP wells." "Closed-loop and direct exchange wells shall not be permitted within the Zone 1 of public water supply wells." "An open-loop GSHP well that does not also serve as a public water supply well shall not be permitted within the Zone 1 of a public water supply well." | Sec. 102-631(C); Sec. 102-631(E)(5)(a)-(b); Sec. 102-631(E)(6)(a)(v)-(vi) | 2023 | https://assets.parkingreform.org/assets/7cb2a221-bc96-4858-96b7-8a471d9ccb76/sterling-illinois-united-states-reduce-min-attachment.pdf?download
Illinois |  | Westmont | 1780645 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Exchange System Equipment that exchanges thermal energy between the ground (or a water source) and a building. This includes vertical closed loop, horizontal closed loop, water body closed loop system and open loop systems. Also known as ground source heat pumps and geothermal heat pumps." | Sec. 17.06 Definition of Words and Terms | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Illinois |  | Westmont | 1780645 | Permit |  |  | "To engage in the use of a building, structure or land, the use or installation of a sign, or any other activity requiring one or more permits or approvals under this zoning ordinance without obtaining such required permits or approvals" is a violation; and "The zoning administrator" is responsible for "Receiving and processing all applications for permits and development approvals under this zoning ordinance." | Sec. 15.02 Enforcement | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Illinois |  | Westmont | 1780645 | Inspection |  |  | The zoning administrator has authority for "Conducting needed inspections of structures and uses of land to determine compliance with this zoning ordinance." | Sec. 15.01 Administration | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Illinois |  | Westmont | 1780645 | Other Prohibitions/Regulations |  |  | "Underground equipment, piping and devices may be located in yard areas but may not be located in any public easement or right-of-way." | Sec. 7.17 Geothermal Heat Exchange Systems | 2025 | https://westmont.illinois.gov/DocumentCenter/View/5043/VillageofWestmentZoningOrdinance-AsAmended-Feb-19-2026
Indiana | Boone | Zionsville | 1801186372 | Open-loop Prohibitions |  |  | "The construction of new geothermal open-loop heating and/or cooling systems within the municipal boundaries is prohibited." | § 52.002 SEPTIC SYSTEMS AND GEOTHERMAL OPEN-LOOP SYSTEMS PROHIBITED | 1991 | https://codelibrary.amlegal.com/codes/zionsville/latest/zionsville_in/0-0-0-1573
Indiana | Hendricks | Center | 1806311386 | Definition: Well |  |  | "Well as defined in IC 25-39-2 a hole drilled or driven to: (1) obtain geologic information on aquifers; (2) monitor the quality or quantity of ground water; (3) obtain ground water; or (4) utilize the geothermal properties of earth formations." | SECTION I DEFINITIONS | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Setback - Property Lines | 5 | feet | Both open-loop geothermal setback tables state "Property lines — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Setback - Building Foundation | 5 | feet | Both open-loop geothermal setback tables state "Buildings and building overhangs — 5 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Setback - Wastewater | 100 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table lists "Privies — 50 feet," "Septic tanks and absorption fields — 50 feet," and "Sewage pits and dry wells — 100 feet." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units" the table lists "Septic tanks, absorption fields, filters — 100 feet" and "Privies — 100 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Setback - Animal Enclosures | 50 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table requires separation from "Stables, livestock runs, manure piles, etc — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Setback - Sewer Lines | 30 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table includes "Sewer Pipes — 30 feet." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units" the table includes "Sewer Pipe ... 30 feet" and also "Sewers and Drains — 100 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Setback - Water Bodies | 50 | feet | For "Private water supply wells and open loop geothermal heat pump systems serving a residence(s)" the table lists "Streams, lakes, ponds — 25 feet." For "open loop geothermal heat pump systems serving other than a residence consisting of not more than two dwelling units" the table lists "Streams, lakes, ponds — 50 feet." | SECTION V MINIMUM REQUIREMENTS - Well Location And Separation Distances | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Permit |  |  | "Before commencement of construction of a well or geothermal heat pump system utilizing a well, a well repair or a pump installation, the owner or agent shall obtain a written permit signed by the Health Officer. No person shall perform any work on such project until such permit is obtained." The ordinance also states: "In emergency situations, the applicant for the well permit shall notify the Health Department of the pending well installation prior to such installation" and submit the application within 24 hours of the next regular workday. | SECTION IH PERMITS | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Inspection |  |  | "It shall be the duty of the well driller and the owner of the property on which the well is drilled to notify the Hendricks County Health Department when the well and appurtenances are available for inspection. The Health Officer must be permitted to inspect the well and appurtenances at any reasonable time." | SECTION VI COMPLIANCE AND INSPECTION - Inspection | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana | Hendricks | Center | 1806311386 | Decommissioning |  |  | "Groundwater wells must be properly abandoned in accordance with 312 IAC 13." The ordinance further provides: "Any groundwater well connected to an existing structure that is scheduled for demolition must be either: a. Properly abandoned in accordance with 312 TAC 13 ... with written verification submitted to the Local Health Officer prior to initiating demolition ... or b. Located by global positioning system for later abandonment, with written notification and well location submitted to the Local Health Officer prior to initiating demolition." | SECTION V MINIMUM REQUIREMENTS - Well Abandonment | 2016 | https://www.co.hendricks.in.us/egov/apps/document/center.egov?view=item;id=258
Indiana |  | Carmel | 1810342 | Definition: Well |  |  | "A Well is any hole or shaft drilled, augured, sunk, or inserted into the earth for extraction, injection, or disposal of any material. A well shall include all mechanical and plumbing appliances connected thereto. This includes any device inserted into the earth which is intended for geothermal or heat exchange purposes whether or not said device pumps water from or into the earth directly." | § 7-51 Definitions | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | 1810342 | Permit |  |  | § 7-57(c): "Each business person shall obtain from Carmel Utilities a permit, which shall be valid for one year, from date of issue, unless otherwise revoked." § 7-62: "Within a reasonable time after an application is presented to Carmel Utilities, but before drilling is started, the owner, or his agent shall request well site approval from Carmel Utilities." § 7-75(a): "Prior to the drilling of a new well an application must be completed, approved and on file at the Carmel Utilities Office... Both a well application and inspection request must be made prior to the drilling procedure, otherwise the well drilling operation shall be stopped until arrangements satisfactory with Carmel Utilities can be established." | § 7-57 Requirements for Registration and Permits; § 7-62 Well Site Approval Required; § 7-75 Well and Permit Application and Fees | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | 1810342 | Inspection |  |  | § 7-57(d): "All wells must comply with the City's specifications as revised from time-to-time and be inspected and certified by Carmel Utilities, prior to being placed into service." § 7-70(a): "All wells are required to have two inspections: (1) During the grouting procedure; and (2) A final inspection made after all appurtenances are installed and just prior to placing the well in service." § 7-70(b): "No well shall be placed in service prior to passing final inspection." § 7-74(a): "If a well is drilled and no inspection is requested or made in accordance with this article, that well must be abandoned and sealed off..." | § 7-57(d); § 7-70 Two Well Inspections Required; § 7-74 Failure to Request Well Inspections | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | 1810342 | Licensed Driller |  |  | "All persons drilling wells must have a current drilling license from the State of Indiana." | § 7-55 State Licensing Required | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Indiana |  | Carmel | 1810342 | Decommissioning |  |  | "If a well is drilled and no inspection is requested or made in accordance with this article, that well must be abandoned and sealed off according to the City and State specifications. A new well must be drilled unless otherwise excepted in writing by the manager of the Carmel Utilities and inspection occurs in accordance with this article." | § 7-74 Failure to Request Well Inspections | 2017 | https://codelibrary.amlegal.com/codes/carmel/latest/carmel_in/0-0-0-5763
Iowa | Bremer | Waverly | 1901794607 | Definition: Geothermal |  |  | "Alternative energy system: An energy system that generates electrical power or heat management by the means of wind, solar, or geothermal energy." | Section 100.28(C) Definitions | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | 1901794607 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils, or plates, a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." Also: "Closed loop ground source heat pump system: a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." And: "Open loop ground source heat pump system: a system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | Section 100.28(C) Definitions | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | 1901794607 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings, and loops shall be set back at least 5 feet from interior side lot lines and at least 10 feet from rear lot lines." | Section 100.28(G)(2) Setbacks | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | 1901794607 | Permit |  |  | "Alternative energy systems shall require plans to be approved by the zoning official through a permit procedure as outlined in the City Code..." "Building and electrical permits must be issued through Bremer County Zoning." Under permitted uses, "Closed Loop Ground Source Heat Pump System" and "Open Loop Ground Source Heat Pump System" are listed as permitted uses. For GHPs specifically: "Open loop ground source heat pump systems are permitted only in non-residential applications and require approval through the Public Works Department subject to all applicable conditions described in this section." | Section 100.28(D) Permit Process; Section 100.28(G) Ground Source Heat Pump Systems | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | 1901794607 | Inspection |  |  | "Building permit applications for open loop ground source heat pump systems shall be accompanied by documentation of ground water quality test results that fulfill the needs of The City Public Works Department for inspection. Prior to permit approval, follow up tests are to take place and given to the City Public Works Department upon completion of the installation of the system to ensure water quality of the groundwater aquifer. The City may conduct follow up tests at the site as needed to ensure water quality of the groundwater aquifer." | Section 100.28(G)(4) Groundwater Testing | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | 1901794607 | Certification |  |  | "Building permit applications for ground source heat pump systems shall be accompanied by standard drawings of the total energy system structure, including the pumps, borings, and loops. An engineering analysis of the system showing compliance with the International Building Code and certified by a licensed professional engineer shall also be submitted. This analysis is frequently supplied by the manufacturer. Wet stamps shall not be required." | Section 100.28(G)(5) Compliance with International Building Code | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Bremer | Waverly | 1901794607 | Decommissioning |  |  | For abandoned open-loop systems: "If the open loop ground source heat pump system is determined to be abandoned, the owner, at their sole expense, shall restore site to original condition. To complete the removal of said system, the owner must remove the heat pump and any external mechanical equipment; fill pipes and coils with grout to displace heat transfer fluid. The heat transfer fluid must be removed from site and be disposed of in accordance with applicable regulations, documentation is required for removal. A final ground water quality test must be taken to ensure protection of ground water. Any piping or coiling 5 feet or less from the surface shall be removed. Removal and vegetation must be restored on site in 120 days from date of the determination of abandonment." | Section 100.28(G)(9) Maintenance | 2023 | https://www.waverlyia.com/webres/File/City%20Administration/City%20Code%20Ordinances/ZONING_07-22-2024.pdf
Iowa | Clay | Lone Tree | 1904192709 | Permit |  |  | "This chapter shall not apply to closed loop, vertical, geothermal heating and cooling loop fields. However, prior to the installation of the loop field a City permit must be obtained." | 93.09 EXCEPTIONS | 2025 | http://ww.lonetreeiowa.com/docs/Public%20Notices/Code%20Lone%20Tree%20Ver%202025%2006-June.pdf
Iowa | Dubuque | Dubuque | 1906191085 | Definition: Well |  |  | "WELL: Any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed or is otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems ..." | 16-11-20-1: DEFINITIONS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM: A mechanism for heat transfer by fluid to air processes and heat transfer by fluid to fluid processes which consists of the following basic elements: Underground loops of piping; heat transfer fluid; a heat pump; an air distribution system. 1. Open Loop Geothermal System: Ground water is pumped from a water well into a heat exchanger located in a surface building and is then pumped back into the aquifer through a different well, the same well, or to the surface of the ground or to a surface body of water, also known as pump and dump. 2. Closed Vertical Loop or Horizontal Geothermal System: A borehole extends beneath the surface. Pipes are installed with U-bends at the bottom or at the end of the boreholes. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." | 16-11-20-1: DEFINITIONS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Setback - Public Water | 1000 | feet | "Major systems may not be located within one thousand feet (1,000 feet) of a current city well or water source. Minor systems may not be located within two hundred (200) feet of a city deep (Jordan/Cambrian-Ordovician) well or within four hundred (400) feet of a city shallow (alluvial aquifer) well." | 16-11-20-3(E): LOCATION OF GEOTHERMAL SYSTEMS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Setback - Hazardous Materials/Fertilizers | 500 | feet | "No geothermal system is allowed to be constructed within a 500-foot radius of an identified leaking underground storage tank (LUST) site." | 16-11-20-3(E): LOCATION OF GEOTHERMAL SYSTEMS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Permit |  |  | "Prior to the construction of any well, the well contractor must obtain a private water well construction permit from the Dubuque County Health Department and a permit from the Building Services Department, and where applicable, an Iowa Department of Natural Resources permit ..." and "No person may dig, bore, drill, replace, modify, repair or destroy a geothermal well or any other excavation that may intersect ground water without first applying for and receiving a permit from the Building Services Department." | 16-11-20-3(B): PERMIT REQUIRED | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Inspection |  |  | "Geothermal piping systems must be tested as required by the Building Services Manager prior to operation of the system and every three (3) years thereafter. All geothermal systems must be pressure checked by a certified contractor not less than every three (3) years from the certification system date. Results of the tests must be submitted to the Building Services Department." | 16-11-20-3(I): TESTING OF SYSTEM | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Licensed Driller |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82. The certified well contractor must be on-site and in direct control of all well services being performed." | 16-11-20-3(A): GEOTHERMAL WELL STANDARDS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Certification |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82." | 16-11-20-3(A): GEOTHERMAL WELL STANDARDS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Decommissioning |  |  | "Abandonment of geothermal systems must be as required in 567 Iowa Administrative Code Section 49.28. The heat transfer fluid must be removed by a displacement with grout and the loop pipes properly capped or sealed by an approved method. The top of the borehole must also be uncovered and properly capped or sealed by an approved method." | 16-11-20-3(J): ABANDONMENT OF GEOTHERMAL SYSTEMS | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Dubuque | Dubuque | 1906191085 | Open-loop Prohibitions |  |  | "Open loop systems are prohibited." Section 16-11-20-3(A) also states: "this section is intended to prohibit all open loop geothermal systems." | 16-11-20-3(H): OPEN LOOP SYSTEMS PROHIBITED | 2015 | https://cityofdubuque.org/DocumentCenter/View/38343
Iowa | Floyd | Charles City | 1906790645 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 11. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 12. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 13. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 14. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 1: General Provisions | 2022 | https://www.cityofcharlescity.org/206/UDOZoning-Ordinance
Iowa | Linn | Cedar Rapids | 1911390577 | Definition: Well |  |  | "Well: Any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed, or otherwise constructed for the purpose of exploring for or monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer. 'Well' does not include ... lateral geothermal heat exchange systems ..." | CHAPTER 12 WATER SERVICE | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Definition: Geothermal Heat Pump |  |  | "Geothermal System: A mechanism for heat transfer by fluid to air processes and heat transfer processes consisting of the following basic elements: underground loops of piping, heat transfer fluid, a heat pump, and an air distribution system." "Open Loop Geothermal System: A geothermal system in which groundwater is pumped from a water well into a heat exchanger located in a surface building. The water is then pumped back into the aquifer through a different well or the same well, or pumped to the surface of the ground or a surface body of water, also known as pump and dump." "Closed Vertical Loop or Horizontal Geothermal System: A geothermal system in which a borehole extends beneath the surface. Pipes are installed with U-bends at the bottom or at the end of the boreholes. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." | CHAPTER 12 WATER SERVICE | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Permit |  |  | "Open loop systems require review and approval by the City Utilities Director or their designee." "Prior to the construction of any geothermal well, the well contractor must obtain a private water well construction permit from the LCPH and a permit from the City Building Services Department, and, where applicable, an Iowa Department of Natural Resources water use permit or registration ..." "No person may dig, bore, drill, replace, modify, repair, or destroy a geothermal well ... without first applying for and receiving a permit from LCPH and a permit from the Building Services Department." "Applications for building services permits required by this Section must be made on forms provided by the Building Services Department ..." | 12.43 PRIVATE WELLS, (b)(2), (b)(4), (b)(5) | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Inspection |  |  | "The Utilities Director or their designee or the Building Official may suspend or revoke any permit issued pursuant to this Section whenever ... D. The system fails any of its mandated testing requirements." | 12.43 PRIVATE WELLS, (b)(8) Permit Suspension And Revocation | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Licensed Driller |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82. The certified well contractor must be on site and in direct control of all well services being performed." | 12.43 PRIVATE WELLS, (b)(3) Closed Loop Systems | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Certification |  |  | "All well services must be performed with an Iowa Department of Natural Resources certified well contractor as required by 567 Iowa Administrative Code Chapter 82. The certified well contractor must be on site and in direct control of all well services being performed." | 12.43 PRIVATE WELLS, (b)(3) Closed Loop Systems | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Decommissioning |  |  | "Geothermal wells must be abandoned as required in 567 Iowa Administrative Code Section 49.28. The heat transfer fluid must be removed by displacement with grout and the loop pipes properly capped or sealed by an approved method. All heat transfer fluid must be safely disposed of according state and federal regulations. The top of the borehole must also be uncovered and properly capped or sealed by an approved method." | 12.43 PRIVATE WELLS, (b)(9) Abandonment Of Geothermal Systems | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Linn | Cedar Rapids | 1911390577 | Other Prohibitions/Regulations |  |  | "All loops must be located within the property boundaries of the building lot and not encroach on any easements." | 12.43 PRIVATE WELLS, (b)(6)(E) Site Plan Requirements | 2024 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/16256/1295436/pdf
Iowa | Crawford | Denison | 1919945 | Permit |  |  | "No groundwater heat pump may be installed without prior issuance of a permit issued by the Building Inspector." | 91.04 GROUNDWATER HEAT PUMPS. |  | https://codelibrary.amlegal.com/codes/denison/latest/denison_ia/0-0-0-2880
Iowa | Crawford | Denison | 1919945 | Other Prohibitions/Regulations |  |  | "This chapter does not prohibit the installation of self-contained groundwater heat pumps which do not inject materials into the surrounding soil or water." This clause expressly limits the allowed groundwater heat pump installations to self-contained systems that do not inject materials into surrounding soil or water. | 91.04 GROUNDWATER HEAT PUMPS. |  | https://codelibrary.amlegal.com/codes/denison/latest/denison_ia/0-0-0-2880
Iowa | Scott | Le Claire | 1944085 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | 1944085 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump System refers to a system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site. Closed Loop Ground Source Heat Pump System refers to a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | 1944085 | Setback - Property Lines | 5 | feet | "All components of Ground Source Heat Pump System including pumps, borings and loops shall be set back at least five (5) feet from interior and rear lot lines." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | 1944085 | Permit |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of the city's zoning ordinance." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | 1944085 | Decommissioning |  |  | "A Ground Source Heat Pump System that is allowed to remain in a nonfunctional or inoperative state for a period of twelve (12) consecutive months, and which is not brought in operation within the time specified by the city after notification to the owner or operator of the Ground Source Heat Pump System, shall be presumed abandoned and may be declared a public nuisance subject to removal at the expense of the operator." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | 1944085 | Open-loop Prohibitions |  |  | "Only closed loop Ground Source Heat Pump System utilizing Iowa Department of Public Health approved heat transfer fluids are permitted." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa | Scott | Le Claire | 1944085 | Other Prohibitions/Regulations |  |  | "Ground Source Heat Pump System are prohibited in surface waters, except for storm water ponds where they are permitted." | 20.27. GEOTHERMAL ENERGY | 2022 | https://leclaireiowa.gov/AgendaCenter/ViewFile/Agenda/_02232023-973
Iowa |  | Robins | 1967800 | Definition: Well |  |  | "Geothermal Borehole - A hole drilled or bored into the earth into which piping is inserted for use in a geothermal system." Also: "Well - any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed or is otherwise construction for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, or extracting water from or injecting water into the aquifer." | 162.02 DEFINITIONS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Definition: Geothermal Heat Pump |  |  | "Geothermal System - A geothermal system uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also: "Geothermal System - A mechanism for heat exchange, which consists of the following basic elements: Underground loops of piping; heat transfer fluid; a heat pump; an air distribution system... The pipes form a 'closed loop' and are filled with a heat transfer fluid." | 162.02 DEFINITIONS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Permit |  |  | "No person shall dig, bore, drill, replace, modify, repair or destroy a geothermal well or any other excavation that may intersect ground water without first applying for and receiving a permit from the City of Robins, Iowa. A permit is required for all closed loop horizontal and closed loop vertical systems." Also: "All proposed well drillers must obtain a permit from the Linn County Health Department..." | 162.03 PERMIT REQUIRED; 162.08 WELL PERMITS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Inspection |  |  | "Geothermal piping systems shall be tested hydrostatically at one and one half times the maximum system design pressure, but not less than 100 psi (689 kPa). The duration of each test shall be not less than 15 minutes." Also: "All geothermal systems must be checked by a licensed geothermal contractor, every year from the certification system date. Results shall be submitted to the Community Development Department..." | 162.12 TESTING OF SYSTEM |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Licensed Driller |  |  | Supporting documents must include: "Certification of the well driller as required under Iowa Administrative Code 567-49 and 567-82." | 162.04 APPLICATION PROCEDURE |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Certification |  |  | The application must include "Certification of the well driller as required under Iowa Administrative Code 567-49 and 567-82." Section 162.08 also requires drillers to "conform to Chapter 149 of the Iowa Administrative Code Section 567-49.29(455B)." | 162.04 APPLICATION PROCEDURE; 162.08 WELL PERMITS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Decommissioning |  |  | "The procedure used for abandonment of geothermal systems must be the same as currently described in Chapter 39 of the Iowa Administrative Code for Plugging Abandoned Wells. The heat transfer fluid must be removed by a displacement with grout. The top of the borehole must be uncovered and capped with grout." | 162.14 ABANDONMENT OF GEOTHERMAL SYSTEMS |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Robins | 1967800 | Open-loop Prohibitions |  |  | "Due to the serious potential adverse environmental impact with open loop systems, open loop systems are prohibited." | 162.11 OPEN LOOP SYSTEMS PROHIBITED |  | https://www.cityofrobins.org/wp-content/uploads/2022/09/CHAPTER-162-GEOTHERMAL-WELL-STANDARDS.pdf
Iowa |  | Spillville | 1974370 | Permit |  |  | "This chapter shall not apply to closed loop, vertical, geothermal heating and cooling loop fields. However, prior to the installation of the vertical loop field a city permit must be obtained. In order to receive a permit from the city, a map of the proposed loop must be provided along with a completed well installation permit signed by the county sanitarian or a member of the water supply section of the Iowa Department of Natural Resources authorized to provide water well installation permits." | 6-2-22 PRIVATE WELLS, 2.c |  | https://www.spillville.org/wp-content/uploads/2023/01/Spillville-2022-Code-of-Ordinances.pdf
Kansas | Decatur | Oberlin | 2003952000 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertically Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2024 | https://towncloud.io/go/oberlin-ks/agendas/652/pdf_packet/get_agenda_document_link
Kansas | Ellis | Ellis | 2005120450 | Permit |  |  | "It shall be unlawful to install, alter or reconstruct any plumbing or plumbing system, as defined by the plumbing code and section 4-301, in any building in the city without first making application to and receiving a permit therefor from the building inspector. The application for such permit shall be made and the permit obtained before any plumbing work is commenced." | 4-310. PLUMBING PERMIT REQUIRED; EXCEPTION | 2009 | https://ellis.ks.us/wp-content/uploads/2020/04/Ellis-City-Code-09.21.2009.pdf
Kansas | Ellis | Ellis | 2005120450 | Inspection |  |  | "Upon the completion of any plumbing work covered by this article, it shall be the duty of the person doing such work to notify the plumbing inspector and request that it be inspected." Also, when plumbing is to be concealed, "such equipment shall not be concealed until it has been inspected, approved or authorized by the plumbing inspector." The inspector may require concealed work to be opened, and "in no case shall the inspector issue a certificate of approval until satisfied that the work is in accordance with the provisions of this article." | 4-315. REQUEST FOR INSPECTION; 4-316. INSPECTION; CONCEALMENT OF PRIOR WORK; 4-318. CERTIFICATE OF APPROVAL | 2009 | https://ellis.ks.us/wp-content/uploads/2020/04/Ellis-City-Code-09.21.2009.pdf
Kansas | Ellis | Ellis | 2005120450 | Certification |  |  | "The contractor shall provide to the city clerk proof of passing the ICBO/Experior Exam." | 4-324(d). PLUMBER'S OR PLUMBING CONTRACTOR'S LICENSE REQUIRED; PLUMBING PERMITS; UNLAWFUL ACTS | 2009 | https://ellis.ks.us/wp-content/uploads/2020/04/Ellis-City-Code-09.21.2009.pdf
Kansas | Harvey | Newton | 2007950475 | Permit |  |  | "Any permit required by IMC shall be issued only to those persons who hold a current license from the City authorizing them to perform the type and nature of work described in the permit." The ordinance also states: "Any person, firm, or corporation who does any work without a permit or who fails to report permitted work as ready for inspection when completed shall pay a civil penalty as prescribed in Newton City Code 6-116." | 6-404. Permits, fees. | 2025 | https://newtonkansas.citycode.net/articleMechanicalCode.htm
Kansas | Harvey | Newton | 2007950475 | Inspection |  |  | The ordinance provides: "Any person, firm, or corporation who does any work without a permit or who fails to report permitted work as ready for inspection when completed shall pay a civil penalty as prescribed in Newton City Code 6-116." | 6-404. Permits, fees. | 2025 | https://newtonkansas.citycode.net/articleMechanicalCode.htm
Kansas | Johnson | Leawood | 2009139075 | Permit |  |  | "Any owner or authorized agent who intends to do work subject to this code ... or to erect, install, enlarge, alter, repair, remove, convert or replace any electrical, gas, mechanical, plumbing, or elevator system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." | 4-904. SECTION R105.1. PERMITS, REQUIRED | 2020 | https://www.leawood.org/DocumentCenter/View/375/2018-International-Residential-Code-Amendments-PDF
Kansas | Johnson | Leawood | 2009139075 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to framing inspection." Exception: "Back-filling of ground-source heat pump loop systems tested in accordance with Section M2105.28 prior to inspection shall be permitted." | 4-922. SECTION R109.1.3. PLUMBING, MECHANICAL, GAS AND ELECTRICAL SYSTEMS INSPECTION | 2020 | https://www.leawood.org/DocumentCenter/View/375/2018-International-Residential-Code-Amendments-PDF
Kansas | Johnson | Mission Hills | 2009147350 | Setback - Property Lines | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Setback - Building Foundation | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Setback - Water Lines | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Setback - Sewer Lines | 10 | feet | "No portion of any Closed Loop Geothermal Heat Pump System shall be located closer than ten feet (10') from any front, side or rear property line and from any underground structure or utility line." | 5-130.1.C. Setback | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Permit |  |  | Vertical systems: "Prior to beginning any construction activity, the contractor must provide to the City Administrator or his or her designee ... (ii) a completed City permit application ..." Decommissioning: "A City permit is required prior to decommissioning a Closed Loop Geothermal Heat Pump System." | 5-130.1.E.2.(a); 5-130.1.F | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Inspection |  |  | "Before grouting or backfilling installed piping, the piping must be pressure tested with water at one hundred pounds per square inch (100 PSI) for at least one (1) hour with no leaks." | 5-130.1.E.1. Piping | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Licensed Driller |  |  | "Prior to beginning any construction activity, the contractor must provide to the City Administrator or his or her designee ... (i) a copy of the contractor's Kansas water well contractor's license ..." | 5-130.1.E.2.(a) Vertical Closed Loop Geothermal Heat Pump Systems | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Certification |  |  | "Prior to beginning any construction activity, the contractor must provide to the City Administrator or his or her designee ... (i) a copy of the contractor's Kansas water well contractor's license ..." | 5-130.1.E.2.(a) Vertical Closed Loop Geothermal Heat Pump Systems | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Decommissioning |  |  | "A City permit is required prior to decommissioning a Closed Loop Geothermal Heat Pump System. To decommission the Closed Loop Geothermal Heat Pump System, the heat transfer fluid must first be removed and properly disposed in accordance with KDHE regulations. After removal of the heat transfer fluid, the loop piping must be cut off five feet (5') below the surface, filled with grout mixture that has been approved by KDHE for this purpose, and sealed with a permanent fusion cap. Following these decommissioning procedures, the excavation site must be filled and leveled." | 5-130.1.F. Decommissioning | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Johnson | Mission Hills | 2009147350 | Open-loop Prohibitions |  |  | "Closed Loop Geothermal Heat Pump Systems may be installed in any district in accordance with the provisions of this Section 5-130.1. Open Loop Geothermal Heat Pump Systems are prohibited in the City." | 5-130.1.B. Limitation | 2017 | https://www.missionhillsks.gov/DocumentCenter/View/8013/Geothermal-Requirements-Vertical-Closed-Loop
Kansas | Montgomery | Coffeyville | 2012514600 | Permit |  |  | "Any owner or authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical ... system, the installation of which is regulated by this Article ... shall first make application to the Building Official and shall obtain the required permit." Section 8-1-110 states the International Mechanical Code applies to "heating, cooling, air-conditioning and refrigeration systems, incinerators and other energy-related systems." | 8-1-138 PERMITS REQUIRED | 2025 | https://www.coffeyville.com/DocumentCenter/View/2950/Building-and-Construction-Code-Book?bidId=
Kansas | Montgomery | Coffeyville | 2012514600 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas, and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to framing inspection. Exception: Back-filling of ground-source heat pump loop systems tested in accordance with Section M2105 of the International Residential Code, as adopted by the City at Article 3 of this Chapter, as amended, prior to inspection shall be permitted." Related provisions also state: "All work for which a permit is required shall be subject to inspection" (8-1-177), "The Building Official, upon notification, shall make the inspections" (8-1-179), and "The final inspection shall be made after all work required by the building permit is completed" (8-1-190). | 8-1-182 PLUMBING, MECHANICAL, GAS AND ELECTRICAL SYSTEMS INSPECTION | 2025 | https://www.coffeyville.com/DocumentCenter/View/2950/Building-and-Construction-Code-Book?bidId=
Louisiana | Orleans | New Orleans | 2207198000 | Setback - Property Lines | 2 | feet | "Ground-based or wall-mounted mechanical equipment (with less than 7 feet of vertical clearance) including, but not limited to, heating, ventilating, geothermal energy, and air-conditioning (HVAC) units, swimming pool equipment, and back-up electrical generators, may be located in an interior side or rear yard and shall be located at least two (2) feet from the interior side or rear property line." | 21.6.T Mechanical Equipment | 2025 | https://czo.nola.gov/article-21/
Louisiana | Orleans | New Orleans | 2207198000 | Screening |  |  | "All approved ground-based mechanical equipment, including, but not limited to HVAC units, shall be screened when readily visible from the public right-of-way, excluding alleys. Screening materials may be masonry, wood, or landscape, and shall effectively screen mechanical equipment so no portion is readily visible from that public right-of-way. ... If ground-based mechanical equipment is screened by an existing structure, fence or landscape, such that it is not readily visible from that public right-of-way, it will be considered to have met these requirements." | 21.6.T Mechanical Equipment | 2025 | https://czo.nola.gov/article-21/
Maine | Androscoggin | Mechanic Falls | 2300144585 | Permit |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | Definitions | 2005 | https://www.mechanicfalls.org/2024%200110%20PB%20Packet.pdf?t=202401041100500
Maine | Androscoggin | Minot | 2300146160 | Permit |  |  | "Start of Construction - means the date the building permit was issued, provided the actual start of construction... was within 180 days of the permit date." | 14-101.2 Definitions | 2022 | https://minotme.org/vertical/Sites/%7B1666B81B-370A-463B-B8FB-32BAA0E22AAF%7D/uploads/2022_Land_Use_Code(1).pdf
Maine | Aroostook | Presque Isle | 2300360825 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C". | 41. Definitions | 2024 | https://presqueislemaine.gov/Document%20Center/Government/Ordinances/CHAPTER%2016A%20-Shoreland%20Zoning%2006-05-2024.pdf?t=202408121500510
Maine | Cumberland | Brunswick | 2300508430 | Screening |  |  | "Accessory use geothermal energy collection facilities shall be located entirely underground, except that facilities connecting underground collection facilities to an aboveground structure are permitted provided: The facilities are located on a side or rear side of the building not abutting a public or private right-of-way unless screened by a vegetative buffer of at least 50 percent opacity at the time of installation, not to exceed six (6) feet in height." Also, "Primary use geothermal energy collection facilities shall be located entirely underground, except that aboveground monitoring and control equipment are permitted provided: ... The facilities are screened from view from adjacent public or private rights-of-way by a vegetative buffer of at least 50 percent opacity at the time of installation, not to exceed six (6) feet in height." | Chapter 3 - Property Use Standards Section 3.4 - Supplementary Use Standards, Geothermal Energy Collection Facilities | 2021 | https://evocloud-prod3-public.s3.us-east-2.amazonaws.com/meetings/47/attachments/4561.pdf
Maine | Cumberland | Chebeague Island | 2300512300 | Permit |  |  | "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C)"; and "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure." | Section 108 Definitions; Section 502 Permits Required | 2018 | https://www.townofchebeagueisland.org/vertical/Sites/%7B984705D3-C709-4324-9040-19247D095968%7D/uploads/Shoreland_Zoning_Ord_eff_4-7-18.pdf
Maine | Cumberland | Freeport | 2300526525 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | Chapter 76 Definitions / Structure | 2024 | https://www.freeportmaine.com/DocumentCenter/View/2553/05-28-24_chapter_65_shoreland_zoning_ordinance
Maine | Cumberland | Harpswell | 2300531390 | Definition: Well |  |  | "A subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; a geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8 are not structures." | Structure | 2026 | https://www.harpswell.maine.gov/vertical/sites/%7B3F690C92-5208-4D62-BAFB-2559293F6CAE%7D/uploads/DEFINITIONS_March_14_2026.pdf
Maine | Cumberland | Long Island | 2300541067 | Permit |  |  | Section 4.15(B)(1)(d) states the Code Enforcement Officer may issue "a permit to place a single accessory structure" in a setback area. Section 4.17 defines "Structure" and expressly excludes "geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C" from that term: "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | 4.15 B. Principal and Accessory Structures / 4.17 Definitions | 2021 | https://townoflongisland.us/wp/wp-content/uploads/2021/05/Chapter-14-Land-Use-Ordinance.pdf
Maine | Cumberland | Pownal | 2300560685 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur..." and "Any permit required by this Ordinance shall be in addition to any other permit required by other law or ordinance." | SECTION 16. Administration; B. Permits Required | 2021 | https://www.pownalmaine.org/vertical/sites/%7BE22E4F8E-90D9-49E3-A5FC-00AC79420AA6%7D/uploads/2021_Ordinance_Amendment_Packet.pdf
Maine | Cumberland | Pownal | 2300560685 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | SECTION 16. I. Enforcement; 2. Code Enforcement Officer | 2021 | https://www.pownalmaine.org/vertical/sites/%7BE22E4F8E-90D9-49E3-A5FC-00AC79420AA6%7D/uploads/2021_Ordinance_Amendment_Packet.pdf
Maine | Cumberland | Raymond | 2300561945 | Definition: Geothermal Heat Pump |  |  | "Structure - Anything built for the support, shelter, or enclosure of persons, animals, goods, or property of any kind, together with anything constructed or erected with a fixed location on or in the ground, exclusive of vegetation, boundary walls, fences, mailboxes, lampposts, birdhouses, doghouses, tree houses designed for children's use, bus shelters, subsurface wastewater disposal systems as defined in Title 30-A, § 4201, subsection 5, geothermal heat exchange wells as defined in Title 32, § 4700-E, subsection 3-C, wells or water wells as defined in Title 32, § 4700-E, subsection 8, or other similar construction." | ARTICLE 3 - DEFINITIONS | 2025 | https://www.raymondmaine.gov/uploads/subdivision-ordinance-2025.pdf
Maine | Cumberland | Scarborough | 2300566145 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | Section 17. Definitions, Structure | 2025 | https://resources.finalsite.net/images/v1748353098/scarboroughmaineorg/yfkwzbiilgg6qrpau4mv/405C-Shoreland-Zoning-Ordinance.pdf
Maine | Cumberland | Scarborough | 2300566145 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure; or renew a discontinued nonconforming use." | Section 16. Administration, B. Permits Required | 2025 | https://resources.finalsite.net/images/v1748353098/scarboroughmaineorg/yfkwzbiilgg6qrpau4mv/405C-Shoreland-Zoning-Ordinance.pdf
Maine | Cumberland | Scarborough | 2300566145 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | Section 16. Administration, H. Enforcement, 2.b | 2025 | https://resources.finalsite.net/images/v1748353098/scarboroughmaineorg/yfkwzbiilgg6qrpau4mv/405C-Shoreland-Zoning-Ordinance.pdf
Maine | Cumberland | South Portland | 2300571990 | Permit |  |  | "The City hereby adopts ... the International Energy Conservation Code ... (the 'Stretch Energy Code') as the energy conservation and efficiency requirements for the City..." and "the requirements of this Division shall become applicable April 1, 2022 to any project that is not a 'Protected Project.'" | Sec. 5-169A. International Energy Conservation Code Adopted | 2025 | https://www.southportland.gov/DocumentCenter/View/1421/Ch-05-Buildings
Maine | Cumberland | Windham | 2300586025 | Definition: Well |  |  | "'Structure' does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface wastewater disposal systems as defined in 30-A M.R.S.A. § 4201, Subsection 5; geothermal heat exchange wells as defined in 32 M.R.S.A. § 4700-E, Subsection 3-C; or wells or water wells as defined in 32 M.R.S.A. § 4700-E, Subsection 8." | § 185-17 Definitions | 2024 | https://ecode360.com/37098623
Maine | Cumberland | Windham | 2300586025 | Permit |  |  | "Permits required. After the effective date of this chapter, no person shall, without first obtaining a permit or site plan approval, as applicable, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur..." and "Any permit required by this chapter shall be in addition to any other permit required by other law or ordinance." | § 185-16 Administration / Permits required | 2024 | https://ecode360.com/37098623
Maine | Cumberland | Windham | 2300586025 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | § 185-16 Administration / Enforcement / Code Enforcement Officer | 2024 | https://ecode360.com/37098623
Maine | Franklin | Farmington | 2300724775 | Permit |  |  | The ordinance refers to "conditions attached to permit approvals" and states that an "application fee" must accompany "the application," with appeal rights for an applicant dissatisfied with a Planning Board decision: "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." Also, "A non-refundable application fee of fifty ($50.00) dollars shall be paid to the Town Clerk and a copy of a receipt for the same shall accompany the application." | I. Enforcement, 2.b; 11-1.18 Fees | 2016 | https://farmington-maine.org/files/Ordinances%20and%20Policies/Shoreland_Zoning_Ordinance_07012018_.pdf
Maine | Franklin | Farmington | 2300724775 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement, 2.b | 2016 | https://farmington-maine.org/files/Ordinances%20and%20Policies/Shoreland_Zoning_Ordinance_07012018_.pdf
Maine | Franklin | Rangeley | 2300761840 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, Section 4700-E, subsection 3-C". | Section 38.13 Definitions | 2020 | https://www.townofrangeley.com/DocumentCenter/View/1672/Chapter-38-FINAL-DRAFT-051421
Maine | Hancock | Bar Harbor | 2300902865 | Permit |  |  | "If it is determined, based on the Federal Emergency Management Agency's Flood Boundary and Floodway Maps and Flood Insurance Rate Maps and information presented by the applicant, that the proposed development, or any part of it, is in a flood-prone area, the site plan shall not be approved until the applicant has obtained a Flood Hazard Development Permit pursuant to Chapter 90, Floodplain Management, of the Bar Harbor Code." | Flood permit | 2025 | https://ecode360.com/8374632
Maine | Hancock | Cranberry Isles | 2300914905 | Definition: Well |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | 18. Definitions | 2020 | https://www.cranberryisles-me.gov/wp-content/uploads/2021/02/Land-Use-Shoreland-Zoning-Ordinance-October-1-2020.pdf
Maine | Hancock | Mount Desert | 2300947630 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S. §4700-E.3-C ..." | Section 8 Definitions - Structure | 2026 | https://www.mtdesert.org/DocumentCenter/View/503/Subdivision-Ordinance-PDF
Maine | Hancock | Surry | 2300975280 | Permit |  |  | The ordinance expressly recognizes "geothermal heat exchange wells" in the definition of Structure: "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C... Setback requirements apply to structures." The Land Use Table also states that "For any proposed activity or use not specifically listed in the Land Use Table, the CEO will determine the permissibility and the permitting authority for such an activity or use, using the existing table for guidance." | Chapter 3, Unified Development Ordinance, Chapter 2 Definitions / Chapter 3 Section II Land Use Table 1 | 2025 | https://cms8.revize.com/revize/surryme/Conservation%20Commission/Surry%20Code%20of%20Ordinances%20v7.0%204-16-2026.pdf
Maine | Hancock | Tremont | 2300977345 | Permit |  |  | "No building, structure or land shall hereafter be used or occupied; no building or structure or part thereof shall hereafter be erected, constructed, expanded, moved, altered to change the use, or demolished... except in conformity with all of the regulations herein specified... A permit shall be obtained from the Code Enforcement officer after approval of the appropriate review authority." In Article XI, "Structure does not include... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | ARTICLE VIII, PERMIT APPLICATION AND REVIEW PROCEDURE; ARTICLE VIII.A. Permit Applicability | 2022 | https://webgen1files1.revize.com/townoftremontma/LAND%20USE%20ORDINANCE%20FINAL%202025-05-13.pdf
Maine | Hancock | Trenton | 2300977415 | Definition: Geothermal Heat Pump |  |  | "Structure – anything temporarily or permanently located, built, constructed or erected for the support, shelter or enclosure of persons, animals, goods or property of any kind or anything constructed or erected on or in the ground. ... Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | 70. Definitions | 2020 | https://www.trentonme.com/images/pdf/Trenton%20Shoreland%20Zoning.pdf
Maine | Kennebec | Benton | 2301104475 | Definition: Well |  |  | "Structure does not include fences, signs, power poles and wiring, and subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; and wells or water wells as defined in Title 32, section 4700-E, subsection 8." | Section II: Definitions Terms Used in this Ordinance | 2022 | https://www.bentonmaine.info/sites/g/files/vyhlif6671/f/uploads/land_use_ordinance_revision_march_2022_5.pdf
Maine | Kennebec | Benton | 2301104475 | Permit |  |  | "A Permit shall be obtained prior to the commencement of construction or placement of any structure within the Town of Benton..." and "1. Land Use Permit: This permit is required for the erection, alteration, rebuilding, repair, remodel, enlargement, or relocation of any proposed or existing building..." The ordinance also states in the definitions that a "Structure" "does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | Section III: Administration, Enforcement and Fees, C. Permit Requirements | 2022 | https://www.bentonmaine.info/sites/g/files/vyhlif6671/f/uploads/land_use_ordinance_revision_march_2022_5.pdf
Maine | Kennebec | Benton | 2301104475 | Inspection |  |  | The Code Enforcement Officer shall "Conduct inspections as frequently as may be necessary to insure compliance with Town Ordinances and State laws." | Section III: Administration, Enforcement and Fees, E. Code Enforcement Officer (CEO) | 2022 | https://www.bentonmaine.info/sites/g/files/vyhlif6671/f/uploads/land_use_ordinance_revision_march_2022_5.pdf
Maine | Kennebec | Fayette | 2301124950 | Definition: Well |  |  | "Structure - anything temporarily or permanently located, built, constructed, or erected ... exclusive of subsurface waste water disposal systems (as defined in 30-A M.R.S. §4201, sub-§5), geothermal heat exchange wells (as defined in 32 M.R.S. 470-E, sub-§ 3-C), or water wells (as defined in 32 M.R.S. §4700-E, sub-§ 8) ..." | ARTICLE XI. DEFINITIONS | 2024 | https://fayettemaine.org/uploads/2024-town-of-fayette-land-use-ordinance.pdf
Maine | Kennebec | Hallowell | 2301130550 | Definition: Geothermal Heat Pump |  |  | "Structure does not include patios, fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in 30-A M.R.S. § 4201(5); geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C); or wells or water wells as defined in 32 M.R.S. § 4700-E(8)." | Section 9.99 | 2021 | https://hallowell.govoffice.com/vertical/sites/%7B9B342949-3E79-4064-B52A-92C27ED57113%7D/uploads/2025.07.07_Item_11.3_-_Affordable_Housing_-_Full_Mark-up.pdf
Maine | Kennebec | Litchfield | 2301140175 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | SECTION 7 Definitions | 2022 | http://www.litchfieldmaine.org/wp-content/uploads/SHORELAND-ZONE-ORDINANCE-2022-2.pdf
Maine | Kennebec | Mount Vernon | 2301147770 | Permit |  |  | The ordinance key states: 'Yes: Allowed (no permit required but the use must comply with all applicable land use standards)'; 'PB: Requires approval by the Planning Board prior to the CEO issuing a permit'; 'CEO: Requires permit issued by the Code Enforcement Officer'; 'LPI: Requires permit issued by the Local Plumbing Inspector'; 'BI: Requires permit from the Building Inspector.' The text also defines geothermal-related scope in the 'Structure' definition by excluding 'geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C).' | Table 4-1 and Table 4-2 / Key to Table 4-1 and Table 4-2 | 2022 | https://webgen1files1.revize.com/thetownofmountvernonme/Mt_Vernon_LUO_4-5-2023.pdf
Maine | Kennebec | Winthrop | 2301186970 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure." | 109. Administration B. Permits Required | 2024 | https://www.winthropmaine.gov/DocumentCenter/View/398/Zoning-Ordinance-March-18-2019-amended-February-2-2026
Maine | Kennebec | Winthrop | 2301186970 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | 109. Administration J. Enforcement (2)(b) | 2024 | https://www.winthropmaine.gov/DocumentCenter/View/398/Zoning-Ordinance-March-18-2019-amended-February-2-2026
Maine | Knox | North Haven | 2301351620 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure; or renew a discontinued nonconforming use." | 16. Administration; B. Permits Required | 2023 | https://www.northhavenmaine.org/Shoreland%20Zone%20Ordinance%20for%20the%20Municipality%20of%20North%20Haven%20Enacted%20November%2020,%202023.pdf?t=202311201110110
Maine | Knox | North Haven | 2301351620 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | 16. Administration; I. Enforcement; (2)(b) | 2023 | https://www.northhavenmaine.org/Shoreland%20Zone%20Ordinance%20for%20the%20Municipality%20of%20North%20Haven%20Enacted%20November%2020,%202023.pdf?t=202311201110110
Maine | Knox | Owls Head | 2301356135 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles; wiring, guy wires, guy anchors and other aerial equipment normally associated with service drops; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; and wells or water wells as defined in Title 32, section 4700-E, subsection 8." | 17. Definitions | 2024 | https://webgen1files1.revize.com/owlsheadme/Final%20PH%202024%20Shoreland%20Zoning%20Ordinance%2042624.pdf
Maine | Knox | Owls Head | 2301356135 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement; (2) Code Enforcement Officer | 2024 | https://webgen1files1.revize.com/owlsheadme/Final%20PH%202024%20Shoreland%20Zoning%20Ordinance%2042624.pdf
Maine | Knox | Rockport | 2301363660 | Inspection |  |  | "The Certificate of Occupancy shall be based on inspections by the Code Officer or Third-Party Inspector, Plumbing Inspector, and Fire Chief or their designee, to ensure that the structure conforms with the Plumbing Code, National Fire Protection Life Safety Code, the Maine Uniform Building and Energy Code (MUBEC), and the Rockport Land Use Ordinance." | CHAPTER 600 - ADMINISTRATION; § 603 Certificates of Occupancy | 2026 | https://rockportmaine.gov/uploads/dm/10693/Land_Use_Ordinance__June_9_2026.pdf
Maine | Knox | South Thomaston | 2301372585 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement (2) Code Enforcement Officer | 2024 | https://souththomaston.me/wp-content/uploads/2025/01/shoreland-signed-attested-june-2024.pdf
Maine | Knox | Thomaston | 2301376365 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface wastewater disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32. section 4700-E, subsection 8." | Structure | 2026 | https://thomastonmaine.gov/vertical/sites/%7B96E8F1E7-2E12-4DA6-B00A-A7D31940B917%7D/uploads/2026_LUO_June_10_FINAL.pdf
Maine | Lincoln | Bremen | 2301506855 | Definition: Geothermal Heat Pump |  |  | "Structure does not include subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | STRUCTURE | 2022 | http://www.bremenmaine.org/wp-content/uploads/2024/03/3-22-24-Revised-Land-Use-Ordinance.pdf
Maine | Lincoln | Newcastle | 2301548645 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | IV. DEFINITIONS | 2024 | https://www.newcastlemaine.us/sites/g/files/vyhlif6211/f/uploads/shoreland_ordinance_2024.12.10.pdf
Maine | Lincoln | Wiscasset | 2301587075 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | 1.16 Definitions | 2024 | https://www.wiscasset.gov/DocumentCenter/View/204/June-2024-Ordinance-Book-PDF
Maine | Oxford | Fryeburg | 2301726910 | Definition: Well |  |  | "Structure: Anything built, constructed or erected on or in the ground... Structures do not include ... geothermal heat exchange wells as defined in Title 32, Section 4700-E subsection 3-c, or wells or water wells as defined in Title 32, Section 4700-E subsection 8." | Section 25 Definitions and Word Usage, B. Definitions | 2024 | https://www.fryeburgmaine.org/DocumentCenter/View/260/Land-Use-Ordinance
Maine | Oxford | Otisfield | 2301755960 | Definition: Well |  |  | "Structure does not include fences, poles and wiring, and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | STRUCTURE-SHORELAND ZONE | 2017 | https://otisfieldme.gov/DocumentCenter/View/961/Definitions-for-the-Town-of-Otisfields-Ordinances
Maine | Oxford | Peru | 2301758270 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur..." and "Any permit required by this Ordinance shall be in addition to any other permit required by other law or ordinance." | 16.B. Permits Required | 2018 | https://townofperumaine.org/wp-content/uploads/2021/06/Town-of-Peru-Shoreland-Zoning-Ordinance-Rev19Mar2018.pdf
Maine | Oxford | Peru | 2301758270 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | 16.I(2)(b) Code Enforcement Officer | 2018 | https://townofperumaine.org/wp-content/uploads/2021/06/Town-of-Peru-Shoreland-Zoning-Ordinance-Rev19Mar2018.pdf
Maine | Oxford | Sweden | 2301775595 | Definition: Well |  |  | In the definition of "Structure," the ordinance states: "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C." | XV. DEFINITIONS |  | https://swedenmaine.org/wp-content/uploads/2024/01/Sweden-Zoning-Ord-draft_2024-1-18_CLEAN-Indesign2.pdf
Maine | Oxford | Sweden | 2301775595 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | XII.F.2.b. On-site Inspections |  | https://swedenmaine.org/wp-content/uploads/2024/01/Sweden-Zoning-Ord-draft_2024-1-18_CLEAN-Indesign2.pdf
Maine | Penobscot | Dixmont | 2301917950 | Definition: Well |  |  | "Structure does not include fences; poles; wiring, guy wires, guy anchors and other aerial equipment normally associated with service drops; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; and wells or water wells as defined in Title 32, section 4700-E, subsection 8." | Definitions - Structure | 2016 | https://storage.googleapis.com/dixmont-media-dixmont/planning-board/ordinances/Dixmont_Shoreland_Zoning_Ordinance_Attested.pdf
Maine | Penobscot | Dixmont | 2301917950 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | Section 16(I)(2)(b) | 2016 | https://storage.googleapis.com/dixmont-media-dixmont/planning-board/ordinances/Dixmont_Shoreland_Zoning_Ordinance_Attested.pdf
Maine | Penobscot | Enfield | 2301923620 | Permit |  |  | The ordinance defines "Structure" to include "geothermal heat exchange wells as defined in Title 32, Section 4700-E, Subsection 3-C." Table 1 states "Structures accessory to allowed uses" require approval in shoreland districts: "PB" in Spring Protection and Resource Protection, "CEO" in Limited Residential and Limited Resource Lot, and "Yes" in General Development. | DEPARTMENT OF ENVIRONMENTAL PROTECTION TABLE 1 - LAND USES IN THE SHORELAND ZONE | 2017 | https://a.storyblok.com/f/63995/x/5e37863366/enfiled_shoreland_zoning_2017.pdf
Maine | Penobscot | Howland | 2301934190 | Permit |  |  | "After the effective date of this Ordinance no person shall, without first obtaining a permit, engage in any activity or use of land or structure requiring a permit in the district in which such activity or use would occur; or expand, change, or replace an existing use or structure..." and "Any permit required by this Ordinance shall be in addition to any other permit required by other law or ordinance." | Section 2691(3) B. Permits Required | 2018 | https://storage.googleapis.com/juniper-media-library/158/2024/10/Shoreland-Zoning-Amended.pdf
Maine | Penobscot | Howland | 2301934190 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | Section 2691(3) I(2)(b) Code Enforcement Officer | 2018 | https://storage.googleapis.com/juniper-media-library/158/2024/10/Shoreland-Zoning-Amended.pdf
Maine | Penobscot | Lincoln | 2301939475 | Permit |  |  | The ordinance defines a geothermal-related eligible improvement only within the PACE financing program: '"Renewable energy installation" means a fixture, product, system, device, or interacting group of devices ... that produces energy or heat from renewable resources, including ... geothermal systems....' It then establishes 'a PACE program allowing owners of qualifying property ... to access financing for energy saving improvements ... through PACE loans administered by the Trust,' and states that 'the Trust will enter into PACE agreements with owners of qualifying property.' | 2008.2.2.10; 2008.3.1; 2008.5.1.A | 2025 | https://www.lincolnmaine.org/wp-content/uploads/2025/12/Code-Master-December-2025.pdf
Maine | Piscataquis | Greenville | 2302129535 | Definition: Well |  |  | Within the shoreland zone, the ordinance states that 'Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C.' | ## Structure - | 2025 | https://greenvilleme.gov/wp-content/uploads/Greenville-Land-Use-Ordinance-9.17.2025-edit-9.18.2025.pdf
Maine | Sagadahoc | Phippsburg | 2302358515 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface wastewater disposal systems as defined in Title 30-A, Section 4201, Subsection 5; geothermal heat exchange wells as defined in Title 32, Section 4700-E, Subsection 3-C; or wells or water wells as defined in Title 32, Section 4700-E, Subsection 8." | Section 18. Definitions | 2025 | https://phippsburg.com/vertical/sites/%7B80D70921-4572-4200-8876-61A701FD14B2%7D/uploads/Shoreland_Zoning_Ordinance_(2025).pdf
Maine | Sagadahoc | Phippsburg | 2302358515 | Permit |  |  | Section 16(A)(1): "It shall be unlawful to construct, add to, alter or to commence the construction, addition, or alteration of a building, mobile home, or structure where the value of such construction or addition exceeds one thousand ($1,000) dollars without first filing with the Codes Enforcement Officer an application in writing and obtaining a permit, therefor." Section 17(B)(20): "After the effective date of this Ordinance no person shall, without first obtaining a permit from the Codes Enforcement Officer or the Planning Board, as appropriate, engage in any activity, use of land, or structure requiring a permit in the district in which such activity or use would occur..." The definitions section states: "Structure does not include... geothermal heat exchange wells as defined in Title 32, Section 4700-E, Subsection 3-C." | Section 16. General Building Requirements A. Permits Required; Section 17. Administration B. Permits Required | 2025 | https://phippsburg.com/vertical/sites/%7B80D70921-4572-4200-8876-61A701FD14B2%7D/uploads/Shoreland_Zoning_Ordinance_(2025).pdf
Maine | Sagadahoc | Phippsburg | 2302358515 | Inspection |  |  | "The Codes Enforcement Officer shall conduct on-site inspections to ensure compliance with all applicable laws and conditions attached to permit approvals." | Section 17. Administration I. Enforcement 44(b) | 2025 | https://phippsburg.com/vertical/sites/%7B80D70921-4572-4200-8876-61A701FD14B2%7D/uploads/Shoreland_Zoning_Ordinance_(2025).pdf
Maine | Somerset | Norridgewock | 2302549835 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C ..." | 17. DEFINITIONS |  | https://www.norridgewock.gov/DocumentCenter/View/441/Proposed-ordinance-PDF
Maine | Somerset | Norridgewock | 2302549835 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. ENFORCEMENT; (2) Code Enforcement Officer |  | https://www.norridgewock.gov/DocumentCenter/View/441/Proposed-ordinance-PDF
Maine | Somerset | Solon | 2302569505 | Permit |  |  | "Prior to the construction or placement of any structure, accessory, or principal, over two hundred (200) square feet in size, or an addition which exceeds one hundred (100) square feet, the landowner or designated agent is responsible for applying for and obtaining a Building Permit from the Town." The Definitions section also states: "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S. § 4700-E(3-C)." | SECTION II: PERMIT & APPLICATION, 1. PERMIT REQUIREMENT | 2024 | https://solon.maine.gov/uploads/2024.01-building-ordinance-replaces-2003.01-07-23-24-.pdf
Maine | Waldo | Lincolnville | 2302739755 | Definition: Well |  |  | "Structure does not include ... geothermal heat exchange wells as defined in 32 M.R.S.A. § 4700-E(3-C) ..." | SECTION 22 - DEFINITIONS | 2023 | https://lincolnvilleme.govoffice3.com/vertical/Sites/%7B0EE09280-1571-4126-B77C-44B66AF5BC58%7D/uploads/Land_Use_Ordinance_as_Amended_June_15_2023.pdf
Maine | Washington | Calais | 2302909585 | Inspection |  |  | The ordinance states the Code Enforcement Officer has authority for the "Inspection of each property in the Area to determine whether the property is in compliance" and for "Review and inspection of the rehabilitation of properties at various stages of completion to ensure that the same is conducted and completed in accordance with any approved designs or plans and the requirements of this Ordinance." | SECTION 3. ADMINISTRATION AND ENFORCEMENT / 3.2. Powers and Duties | 2017 | https://storage.googleapis.com/juniper-media-library/63/2024/01/LAND-USE-CODES-July-2017-amendments-2021.pdf
Maine | Washington | Cherryfield | 2302912455 | Definition: Well |  |  | Within the shoreland-zone definition of “Structure,” the ordinance states: '“Structure” includes structures temporarily or permanently located, such as parking lots, decks, patios, and satellite dishes. This definition does not include ... geothermal heat exchange wells as defined in 32 M.R.S.A. § 4700-E(3-C) ...' | Section VI-3. Definitions | 2025 | http://www.cherryfieldmaine.us/wp-content/uploads/2025/12/LUO_2025.pdf
Maine | Washington | Cherryfield | 2302912455 | Inspection |  |  | The ordinance states: 'The CEO may conduct site inspections to ensure compliance with all applicable laws and all terms and conditions attached to permits and approvals under this Ordinance.' It also states for projects with performance guarantees: 'the permit holder must deposit in escrow with the Town funds to cover the costs of site inspections to be conducted by an engineer mutually acceptable to the permit holder and the Planning Board,' and 'If the inspector finds, upon inspection ... that any of the site infrastructure or work has not been done in accordance with the plans ... the inspector must so report...' | Section VII-8.C. Inspections; Investigation of Complaints; Section VII-9.E. Inspections | 2025 | http://www.cherryfieldmaine.us/wp-content/uploads/2025/12/LUO_2025.pdf
Maine | Washington | Cherryfield | 2302912455 | Decommissioning |  |  | For projects where a performance guarantee is required, the ordinance provides that the guarantee must cover 'decommissioning of any facilities or infrastructure associated with the proposal.' It further states: 'For reclamation and decommissioning work, the permit holder must arrange for the costs to be recalculated by an engineer every five years,' the guarantee must include a schedule for 'decommissioning work,' escrow must be provided for inspections before 'commencing any ... decommissioning work,' and before release of the guarantee 'the inspector must certify ... that all required ... decommissioning work has been satisfactorily completed.' | Section VII-9.C. Scope; Amount; Section VII-9.D. Schedule; Section VII-9.E. Inspections | 2025 | http://www.cherryfieldmaine.us/wp-content/uploads/2025/12/LUO_2025.pdf
Maine | York | Limerick | 2303139195 | Permit |  |  | Article II defines "Structure" to exclude "H. Geothermal heat exchange wells as defined in 32 M.R.S.A. §4700-E, Subsection 3-C." In the Land Use Chart note, "* - Definition provided in Article II. ... Requires permit from Selectmen." Government/Municipal Facilities* are listed as a permitted use in all districts. | Article II - Definitions / Article V - District Regulations | 2022 | https://0201.nccdn.net/1_2/000/000/143/c85/zoningordinance_march2022.pdf
Maine | York | Lyman | 2303141750 | Definition: Geothermal Heat Pump |  |  | "Structure does not include ... geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C". | 17. Definitions; Structure | 2021 | https://lyman-me.gov/wp-content/uploads/2022/05/Shoreland-zoning-ordinance-amended-06-08-2021.pdf
Maine | York | Lyman | 2303141750 | Inspection |  |  | "The Code Enforcement Officer shall conduct on-site inspections to insure compliance with all applicable laws and conditions attached to permit approvals." | I. Enforcement; (2) Code Enforcement Officer; (b) | 2021 | https://lyman-me.gov/wp-content/uploads/2022/05/Shoreland-zoning-ordinance-amended-06-08-2021.pdf
Maine | York | Saco | 2303164675 | Definition: Geothermal Heat Pump |  |  | "Structure does not include fences; poles and wiring and other aerial equipment normally associated with service drops, including guy wires and guy anchors; subsurface waste water disposal systems as defined in Title 30-A, section 4201, subsection 5; geothermal heat exchange wells as defined in Title 32, section 4700-E, subsection 3-C; or wells or water wells as defined in Title 32, section 4700-E, subsection 8." | Structure | 2021 | https://ecode360.com/SA1647/laws/LF1294073.pdf
Maryland | Baltimore | 5 | 2400590380 | Definition: Geothermal Heat Pump |  |  | Table 408.3 includes the term: "GROUND SOURCE HEAT PUMP (GREATER THAN OR EQUAL TO 3.5 COP GROUND SOURCE HEAT PUMP.)" with a "6%" percentage increase for Climate Zone 4. | SECTION R408.3 MARYLAND ALTERNATIVE ADDITIONAL EFFICIENCY PACKAGE OPTIONS; TABLE 408.3 ADDITIONAL ENERGY FEATURES | 2024 | https://mgaleg.maryland.gov/pubs/LegisLegal/County-Legislation/2025-Baltimore-County-49-24.pdf
Maryland | Cecil | 5, North East | 2401590396 | Permit |  |  | "The Town of North East may issue a building permit or other approval to authorize a non-water dependent project for a smallscale renewable energy system on a pier located on State or private wetlands within the Critical Area if the project: (a) Involves the installation or placement of a small-scale renewable energy system ..." and "(iv) A closed-loop geothermal heat exchanger under a pier if the geothermal heat exchanger or any associated devices or equipment do not: (A) Extend beyond the length, width, or channelward encroachment of the pier; (B) Deleteriously alter longshore drift; or (C) Cause significant individual or cumulative thermal impacts to aquatic resources." | Section 5-12, §9(l)(3) | 2025 | https://www.northeastmd.org/wp-content/uploads/2026/02/ARTICLE-05-PART-I-II-NEZO.pdf
Maryland | Cecil | 7, Port Deposit | 2401590580 | Noise Limits | 70 | dBA | "Air-conditioning and heat-pump equipment used to cool or heat housing on residential property may not exceed 70 decibels for air-conditioning units and 75 decibels for heat pumps." | 3-1.8 Noise, f. Exceptions, E. | 2019 | https://www.portdeposit.org/_files/ugd/94e3df_060154c3d0264171aad225d951e0f363.pdf
Maryland | Montgomery | 2 | 2403190152 | Definition: Geothermal |  |  | "Geothermal energy device" means a device that: "(1) uses geothermal energy to heat or cool a structure, to provide hot water for use in the structure, or to generate electricity to be used in the structure; and (2) meets safety and performance standards set by a nationally recognized testing laboratory for that kind of device." | 52-18R(a) Definitions | 2009 | https://assets.montgomerycountymd.gov/files/20090313_2-09.pdf
Maryland | Montgomery | 2 | 2403190152 | Certification |  |  | An application must "include a certification from the Department of Permitting Services indicating that the device for which the credit is sought: (i) is a solar or geothermal energy device; and (ii) has been properly installed. The Department of Permitting Services must accept a certification by another government agency, including a municipality, that the device has been properly installed." | 52-18R(d) Application | 2009 | https://assets.montgomerycountymd.gov/files/20090313_2-09.pdf
Maryland | Montgomery | 11 | 2403190976 | Definition: Geothermal Heat Pump |  |  | "Geothermal energy device means a device that: (1) uses geothermal energy to heat or cool a structure, to provide hot water for use in the structure, or to generate electricity to be used in the structure; and (2) meets safety and performance standards set by a nationally recognized testing laboratory for that kind of device." | Sec. 52-104. Property tax credit — renewable energy. | 2023 | https://codelibrary.amlegal.com/codes/montgomerycounty/latest/montgomeryco_md/0-0-0-152134
Maryland | Montgomery | 11 | 2403190976 | Permit |  |  | "An application must ... include a certification from the Department of Permitting Services, indicating that the device for which the credit is sought: (i) is a solar or geothermal energy device; and (ii) has been properly installed." | Sec. 52-104(f) Application. | 2023 | https://codelibrary.amlegal.com/codes/montgomerycounty/latest/montgomeryco_md/0-0-0-152134
Maryland | Montgomery | 11 | 2403190976 | Inspection |  |  | "An application must ... include a certification from the Department of Permitting Services, indicating that the device for which the credit is sought ... has been properly installed." Also, "The Department of Permitting Services must accept a certification by another government agency, including a municipality, that the device has been properly installed." | Sec. 52-104(f) Application. | 2023 | https://codelibrary.amlegal.com/codes/montgomerycounty/latest/montgomeryco_md/0-0-0-152134
Maryland | Talbot | 2, St. Michaels | 2404190172 | Permit |  |  | "The Town may issue a building permit or other approval to authorize a non-water dependent project for a small-scale renewable energy system on a pier located on State or private wetlands within the Critical Area if the project..." includes "(d) A closed-loop geothermal heat exchanger under a pier if the geothermal heat exchanger or any associated devices or equipment do not: 1) extend beyond the length, width, or channelward encroachment of the pier; 2) deleteriously alter longshore drift; or 3) cause significant individual or cumulative thermal impacts to aquatic resources." | § 340-29.C. Non-water dependent project for a small-scale renewable energy system on a pier | 2020 | https://dnr.maryland.gov/criticalarea/Documents/06b_StMichaelsZoningOrdinance_Attachment2.pdf
Massachusetts | Barnstable | Brewster | 2500107980 | Definition: Well |  |  | "Well- Any hole or shaft constructed into the ground for the purpose of injecting or extracting water and other fluids, or to monitor groundwater levels and water quality." | SECTION (1) DEFINITIONS | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Definition: Geothermal Heat Pump |  |  | "Groundwater Heat Pump- A refrigeration system which can heat or cool a dwelling which operates by exchanging heat with the groundwater. The groundwater can be supplied by either a closed loop system or an open loop system consisting of a supply and discharge well." | SECTION (1) DEFINITIONS | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Setback - Roads | 10 | feet | For non-potable wells, "The following minimum distances are required: Roadway 10 feet (from edge of road layout, not edge of pavement)." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Setback - Property Lines | 10 | feet | For non-potable wells, "The following minimum distances are required: Property Line 10 feet." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Setback - Wastewater | 50 | feet | For non-potable wells, the table requires setbacks from wastewater infrastructure including "Septic tank 10 feet," "Septic leaching facility 25 feet," and "Septic distribution box 10 feet." The geothermal-specific clause adds: "Inlet and discharge wells used solely to serve open loop heat pumps shall be located not less than 50' from a septic leaching facility." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Setback - Subsurface Drains | 25 | feet | For non-potable wells, the table states: "Subsurface drains 25 feet (but recommend that this distance be maximized, as pollutants frequently travel along the outside of subsurface drainpipes.)" | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Setback - Sewer Lines | 10 | feet | The permit site plan must show the well location relative to "building sewer lines," and the minimum-distance table states: "Building sewer 10 feet." | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; A) Well Construction Permit and B) Well Location | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Permit |  |  | "No well shall be installed, altered, or repaired, until a Well Construction Permit has been obtained from the Board of Health." The permit application must include "a site plan showing the proposed location of the well in relation to building foundations, property lines, building sewer lines, subsurface drainage systems, subsurface sewage disposal systems ..." This section applies to non-potable wells, and the ordinance separately defines a "Groundwater Heat Pump" as using closed loop or open loop systems. | SECTION (3) REQUIRMENTS FOR NON POTABLE WATER WELLS; A) Well Construction Permit | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Licensed Driller |  |  | "No well shall be installed, altered, repaired, replace or abandoned except by a well driller, who is certified by MassDEP pursuant to M.G.L. Chapter 21, Section 20, 310CMR 46.00; and the Brewster Board of Health." Also, "All well drillers doing business in the Town of Brewster shall annually file with the Board of Health a copy of their current well driller registration certificates issued by the MassDEP in accordance with 310 CMR 46.00." | SECTION (2) GENERAL REQUIREMENTS; C) Well Installation, Alteration, Repair and Abandonment | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Certification |  |  | "All well drillers doing business in the Town of Brewster shall annually file with the Board of Health a copy of their current well driller registration certificates issued by the MassDEP in accordance with 310 CMR 46.00." And: "No well shall be installed, altered, repaired, replace or abandoned except by a well driller, who is certified by MassDEP pursuant to M.G.L. Chapter 21, Section 20, 310CMR 46.00; and the Brewster Board of Health." | SECTION (2) GENERAL REQUIREMENTS; B) Registration of Well Drillers and C) Well Installation, Alteration, Repair and Abandonment | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Brewster | 2500107980 | Decommissioning |  |  | "Prior to destruction of any well, the well driller must obtain a well destruction permit from the Board of Health." "Any abandoned well shall be filled and sealed with clean puddle clay, neat cement grout, bentonite or concrete grout in such a manner as to prevent it from acting as a channel for pollution to the groundwater." "Within 30 days following the completion of the plugging procedure, the certified well driller who plugged the abandoned well, test hole, or dry or inadequate boring must submit a Well Completion Report to MassDEP with a copy to the Board of Health ... and must submit a Decommissioning Report to the owner, agent and Board of Health." | SECTION (2) GENERAL REQUIREMENTS; E) Well Decommissioning | 2016 | https://www.brewster-ma.gov/health-department/files/private-well-regulations
Massachusetts | Barnstable | Eastham | 2500119295 | Definition: Well |  |  | "Well: any hole or shaft drilled into the ground to inject or withdraw water, other fluids, or gases, monitor soil gasses, monitor groundwater levels or water quality, transfer heat, or provide cathodic protection." | SECTION II: DRINKING WATER, III. DEFINITIONS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Roads | 25 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (b) 25 feet from public or private roadway." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Right of Way | 50 | feet | Section VI lists setbacks including "(c) 15 feet from right of way" and also "(i) 50 feet from any utility right of way." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Property Lines | 10 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (a) 10 feet from the property line." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Wastewater | 50 | feet | Section VI requires setbacks for wells including "(d) 50 feet from building sewer line, septic tank, or distribution box" and "(e) 25 feet from leaching field, catch basin or drywell." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Animal Enclosures | 100 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (f) 100 feet from stable, barnyard, manure storage." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Fuel (below ground) | 250 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (g) 250 feet from an underground fuel storage or pesticide tank." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Water Lines | 10 | feet | "Water supply lines shall be installed at least ten (10) feet from and eighteen (18) inches above any sewer line." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Sewer Lines | 50 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (d) 50 feet from building sewer line, septic tank, or distribution box." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Setback - Water Bodies | 25 | feet | "No well shall be permitted for use as a potable water source unless it meets the following setback requirements: (h) 25 feet from any surface water, including, but not limited to, wetlands." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Maximum Well Depth | 100 | feet | Within the Mandatory Municipal Water Supply Zone, conversion of private drinking water wells for irrigation use may be allowed only if the well "is less than 100 ft. in depth." | SECTION II: DRINKING WATER, XI. Requirements for Wells in the Mandatory Municipal Water Supply Zone | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Permit |  |  | "A Massachusetts Certified Well Driller shall obtain an electronic permit from the Board of Health prior to the commencement of construction of a private well." | SECTION II: DRINKING WATER, IV. WELL CONSTRUCTION PERMIT | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Inspection |  |  | "Each private well shall be located so that it is accessible for repair, maintenance, testing, and inspection." | SECTION II: DRINKING WATER, VI. WELL LOCATION AND USE REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Licensed Driller |  |  | "no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | SECTION II: DRINKING WATER, IX. WELL CONSTRUCTION REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Certification |  |  | Section IV requires the application to include "the well driller's name and proof of valid Massachusetts certification." Section IX states: "no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | SECTION II: DRINKING WATER, IV. WELL CONSTRUCTION PERMIT; IX. WELL CONSTRUCTION REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Decommissioning |  |  | "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." The owner "shall decommission the well" if specified criteria are met, and "Only certified well drillers may plug abandoned wells, test holes, and borings." Plugging materials and placement are specified, including introduction "at the bottom of the well or boring and placed progressively upward to a level approximately four (4) feet below the ground surface," with the top then filled with concrete and a concrete slab installed. | SECTION II: DRINKING WATER, X. DECOMMISSIONING REQUIREMENTS | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Eastham | 2500119295 | Other Prohibitions/Regulations |  |  | "In the Central Area bounded by Glacier Hills Road, Schoolhouse Road, Route 6 and Bike Trail (see attached map) all private wells (potable and non-potable) must be abandoned." | SECTION II: DRINKING WATER, XI. Requirements for Wells in the Mandatory Municipal Water Supply Zone | 2026 | https://www.eastham-ma.gov/2036/Eastham-Board-of-Health-DRAFT-Regulation
Massachusetts | Barnstable | Orleans | 2500151440 | Definition: Geothermal Heat Pump |  |  | "Groundwater Heat Pump. A refrigeration system which can heat or cool a dwelling which operates by exchanging heat with the groundwater. The groundwater can be supplied by either a closed loop system or an open loop system consisting of a supply and a discharge well." | § 185-69 Definitions | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Setback - Roads | 10 | feet | For nonpotable wells, including open-loop heat pump wells regulated in the same section, the table states: "Roadway — 10 feet from edge of road layout (not edge of pavement)." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Setback - Right of Way | 50 | feet | For nonpotable wells, the table states: "Utility rights-of way for high voltage transmission lines — 50 feet, but recommend that this distance be maximized." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Setback - Property Lines | 10 | feet | For nonpotable wells, including open-loop heat pump wells regulated in the same section, the table states: "Property Line — 10 feet." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Setback - Wastewater | 50 | feet | The nonpotable well location table requires setbacks of "Septic tank — 10 feet," "Septic leaching facility — 25 feet," and "Septic distribution box — 10 feet." A note specifically for geothermal says: "Inlet and discharge wells used solely to serve open loop heat pumps shall be located not less than 10' from a septic tank" and "Inlet and discharge wells used solely to serve open loop heat pumps shall be located not less than 50' from a septic leaching facility." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Setback - Subsurface Drains | 25 | feet | For nonpotable wells, the table states: "Subsurface drains — 25 feet, but recommend that this distance be maximized, as pollutants frequently travel along the outside of subsurface drainpipes." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Setback - Sewer Lines | 10 | feet | For nonpotable wells, the table states: "Building sewer — 10 feet." | § 185-71(B)(1) Well Location | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Permit |  |  | For open-loop heat pump wells covered as nonpotable wells: "No well shall be installed, altered, or repaired, until a Well Construction Permit has been obtained from the Board of Health." The application must be submitted by the drilling contractor or agent, and "The Board of Health must approve the location and design of the well, prior to issuance of a Well Construction permit." | § 185-71(A) Well Construction Permit | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Inspection |  |  | The ordinance states: "When the Board of Health deems it necessary, the health agent or other agent of the Board of Health, may be present to witness the taking of a water sample and/or may take the water sample and deliver it to the testing laboratory him/herself." It also requires: "Before approval, every well shall be pump tested to determine yield. The pump test shall include a draw down test at a minimum pumping rate of 5 gallons per minute for one (1) hour." | § 185-72(C)(4) Water Quality; § 185-72(D)(1) Well Yield and Water System Design | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Licensed Driller |  |  | "No well shall be installed, altered, repaired or abandoned except by a well driller, who is registered with the Water Resources Commission, Division of Water Resources, under MGL Ch. 21, Sec. 16 and 31, CMR 3.00 and the Orleans Board of Health." Also, "All well drillers doing business in the Town of Orleans, shall annually file with the Board of Health a copy of their current well driller registration issued by the Commonwealth of Massachusetts Regulations 313 CMR 3.00." | § 185-70 General requirements; § 185-71 Requirements for nonpotable water wells; § 185-72 Requirements for potable water wells | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Certification |  |  | "All well drillers doing business in the Town of Orleans, shall annually file with the Board of Health a copy of their current well driller registration issued by the Commonwealth of Massachusetts Regulations 313 CMR 3.00." | § 185-70 General requirements | 2003 | https://ecode360.com/14202077
Massachusetts | Barnstable | Orleans | 2500151440 | Decommissioning |  |  | "Prior to destruction of any well, the well driller must obtain a well destruction permit from the Board of Health." Also, "Any abandoned well shall be filled and sealed with clean puddled clay, neat cement grout, bentonite or concrete grout in such a manner as to prevent it from acting as a channel for pollution to the groundwater." | § 185-70(E) Well Destruction | 2003 | https://ecode360.com/14202077
Massachusetts | Bristol | Easton | 2500520100 | Definition: Well |  |  | "GEO THERMAL WELL — A well or wells drilled vertically in the ground that are water-filled, closed loop of one-inch high-density polyethylene (HDPE) pipe ferries heat between the earth and the house. Pipes descend four-to six-inch-diameter vertical wells... Drillers backfill each hole with bentonite grout... Pumps cycle water through the pipe loop to the heart of the system: the geothermal unit, which acts as furnace and air conditioner." | § 369-2 Definitions | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Roads | 25 | feet | "Each well shall be located... Twenty-five feet from a street layout." | § 369-4 Location and use requirements, E(6) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Property Lines | 25 | feet | "Each well shall be located... Twenty-five feet from a property line." | § 369-4 Location and use requirements, E(5) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Building Foundation | 10 | feet | "Each well shall be located... Ten feet from a dwelling or building;" | § 369-4 Location and use requirements, E(11) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Wastewater | 100 | feet | "Each well shall be located: At a minimum of 100 feet from a subsurface sewage disposal area (including reserve areas);" and "A minimum of 50 feet for irrigation and geothermal wells from sewage disposal and reserve areas. Fifty feet from a septic tank for all wells." | § 369-4 Location and use requirements, E | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Animal Enclosures | 100 | feet | "Each well shall be located... One hundred feet from a Stables, barnyard, Manure storage." | § 369-4 Location and use requirements, E(15) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Fuel (below ground) | 100 | feet | "Each well shall be located... One-hundred feet from underground oil tanks and gasoline tanks, underground oil distribution lines..." | § 369-4 Location and use requirements, E(9) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Subsurface Drains | 25 | feet | "Each well shall be located... Twenty-five feet from subsurface drains;" | § 369-4 Location and use requirements, E(8) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Sewer Lines | 50 | feet | "Each well shall be located... Fifty feet from any sewer main;" | § 369-4 Location and use requirements, E(13) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Pools | 10 | feet | "Each well shall be located... Ten feet from a permanently located swimming pool;" | § 369-4 Location and use requirements, E(12) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Water Bodies | 25 | feet | "Each well shall be located... Twenty-five feet from the normal high water mark of any lake, pond, river, stream, ditch or slough;" | § 369-4 Location and use requirements, E(10) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Setback - Hazardous Materials/Fertilizers | 250 | feet | "Each well shall be located... Two hundred fifty feet for underground pesticide;" | § 369-4 Location and use requirements, E(14) | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Inspection |  |  | "Inspections. The Board of Health or its authorized Agent may inspect the installation of the well and may at any stage of construction, require necessary modifications..." Also, "Following review of analytical results, pump tests and all other pertinent information, an inspection will be made by the Board of Health or its agent(s) to verify the well location, construction, operation of the well pump and any required posting." | § 369-3 Well construction permits, F; § 369-9 Well registration, C | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Decommissioning |  |  | "Abandoned Wells... shall be destroyed by removing, plugging or sealing by decommissioning to protect the groundwater." Also, "Only MA Registered Well Drillers may plug abandoned wells... Wells shall be plugged with neat cement grout, sand cement grout, concrete or bentonite grout... applied through a tremie pipe from the bottom of the well upward... casing shall be cut off six inches — 12 inches below existing grade... The remaining depth of casing shall be filled with concrete." | § 369-8 Decommissioning of wells | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Easton | 2500520100 | Open-loop Prohibitions |  |  | "All Geo thermal wells will be closed loop. Open loop wells or these kinds of systems will not be approved..." | § 369-4 Location and use requirements, C | 2023 | https://ecode360.com/32306544
Massachusetts | Bristol | Westport | 2500577570 | Other Prohibitions/Regulations |  |  | "The open space shall allow walking paths and other passive recreational uses, but shall not be use for the siting of any structure, building, septic system, well (drinking water or geothermal) or utilities or pipes." | 6.5.10 OPEN SPACE REQUIREMENTS | 2023 | https://cms2.revize.com/revize/westportma/Documents/Departments/Building/zoning_by-laws_5.3.23_atm_approved_web_1.pdf?t=202508271350580&t=202508271350580
Massachusetts | Dukes | Chilmark | 2500713800 | Setback - Property Lines | 50 | feet | Section 5.9 states: "Machinery or mechanical units, which are placed outside the footprint of a dwelling, shall be treated as 'structures' and shall be subject to the normal setbacks required by zoning..." Section 6.0 then provides the zoning setbacks: in Districts I, II-A, II-B, III, and VI, each structure and accessory use "shall be set back a minimum of 50 feet from each boundary line of said lot"; District IV requires 25 feet; District V requires 35 feet; and Section 6.1 provides exceptions of 25 feet or 35 feet for certain smaller pre-existing, Homesite Housing, or Youth Lots. | Section 6.0; Section 5.9 - Exterior Mechanical Noise Abatement | 2025 | https://www.chilmarkma.gov/sites/g/files/vyhlif8411/f/uploads/zbl_scan_08112025_searchable_0.pdf
Massachusetts | Dukes | Chilmark | 2500713800 | Noise Limits | 10 | dBA | Section 5.9 applies to "mechanical devices associated with and accessory to residential dwellings, such as, but not exclusively, air conditioners/heat pumps..." and requires such stationary machinery to "be placed in soundproof enclosures or to be so screened and insulated that the perceived sound levels do not rise by more than ten decibels (10 DbA) above the ambient sound level as measured at the property line." | Section 5.9 - Exterior Mechanical Noise Abatement | 2025 | https://www.chilmarkma.gov/sites/g/files/vyhlif8411/f/uploads/zbl_scan_08112025_searchable_0.pdf
Massachusetts | Dukes | Chilmark | 2500713800 | Permit |  |  | "If a swimming pool is heated, applicants are strongly encouraged to use: ... an energy efficient heating system, including on-site solar thermal or a heat pump system." The same subsection states: "A Special Permit is required for a swimming pool or a tennis court from the Zoning Board of Appeals." | Section 4.2A.3(a) - Swimming Pool and/or Tennis Court | 2025 | https://www.chilmarkma.gov/sites/g/files/vyhlif8411/f/uploads/zbl_scan_08112025_searchable_0.pdf
Massachusetts | Essex | Georgetown | 2500925625 | Definition: Well |  |  | "WELL or WATER WELL" means "Any hole or shaft constructed into the ground for the purpose of extracting or injecting water... It shall include wells connected to heat pumps." The same definition section adds "HEAT PUMP WELLS" as: "Consists of a source well and a discharge well which could be one and the same, provided that it is a closed loop system where nothing is added to or taken from the water except heat and no air is in contact with the return water. A heat pump delivers water by way of the source well from an aquifer through a heat exchanger and returns it to the aquifer via the discharge well. The system utilizes the thermal energy stored in groundwater for space heating or cooling." | § 480-3 Definitions |  | https://ecode360.com/6486648
Massachusetts | Essex | Georgetown | 2500925625 | Permit |  |  | "A well permit shall be obtained from the Board of Health prior to the construction of any water well or well system. This includes major rework or repair of existing water wells." The ordinance also requires that "An application for a water well permit must be submitted to the Board of Health" and that "The location, design and operation of the well must be approved by the Board of Health or its agent prior to construction." | § 480-7C Well construction permits |  | https://ecode360.com/6486648
Massachusetts | Essex | Georgetown | 2500925625 | Licensed Driller |  |  | "No person shall engage in the business of constructing wells within the Town of Georgetown unless he is registered with the Water Resources Commission, Division of Water Resources, as required by Water Well Drillers Registration Act (MGL C. 21, § 16)." Also, § 480-3 defines "WELL DRILLER" as a person that constructs a water well, "licensed by Water Resource Commission (§ 480-5)." | § 480-5 Registration of well drillers |  | https://ecode360.com/6486648
Massachusetts | Essex | Middleton | 2500941095 | Definition: Well |  |  | "GROUND SOURCE HEAT PUMP (GSHP) WELL — Any excavation by any method for the purpose of transferring heat to or from the earth for heating and cooling purposes in which the ambient ground temperature (prior to GSHP operations) is 90° Fahrenheit or less." | § 343-3 Definitions | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) SYSTEM — A heating and/or cooling system that transfers heat to or from the earth in which the naturally occurring, ambient ground (prior to GSHP operations) is 90° Fahrenheit or less." | § 343-3 Definitions | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Roads | 25 | feet | "Each private well shall be located at least 25 feet from any property line/road right-of-way." | § 343-6(A)(2) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Property Lines | 25 | feet | "Each private well shall be located at least 25 feet from any property line/road right-of-way." | § 343-6(A)(2) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Building Foundation | 5 | feet | "The center line of a well shall, if extended vertically, clear any projection from an adjacent structure by at least five feet." | § 343-6(A)(2) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Wastewater | 100 | feet | "All wells and/or suction lines shall be located... 50 feet from a septic tank; 100 feet from a leaching field and soil absorption system; and 100 feet from a privy." | § 343-6(A)(4) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Water Lines | 10 | feet | "Water supply lines shall be installed at least 10 feet from and 18 inches above any sewer line." | § 343-6(A)(6) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Sewer Lines | 50 | feet | § 343-6(A)(4): "All wells and/or suction lines shall be located a minimum of 10 feet from a building sewer constructed of durable corrosion-resistant material with watertight joints, or 50 feet from a building sewer constructed of any other type of pipe..." § 343-6(A)(6): "Water supply lines shall be installed at least 10 feet from and 18 inches above any sewer line." | § 343-6(A)(4); § 343-6(A)(6) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Setback - Water Bodies | 25 | feet | "Each private well shall be located at least 25 feet, laterally, from the normal high water mark of any lake, pond, river, stream, ditch, or slough." | § 343-6(A)(3) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Minimum Well Depth | 15 | feet | "Private wells drilled in bedrock shall be grouted from the top of the weathered rock interface to a minimum of 15 feet into competent bedrock." | § 343-9(G)(1) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Permit |  |  | § 343-4(A): "The property owner or his designated representative shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." § 343-6(B)(3) states: "Ground source heat pump wells are subject to the same standards as drinking water wells." | § 343-4 Well construction permit; § 343-6(B)(3) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Inspection |  |  | § 343-6(A)(1): "Each private well shall be accessible for repair, maintenance, testing, and inspection." § 343-7: "a pumping test, witnessed by the Board of Health's representative, shall be conducted" to demonstrate well capacity. | § 343-6(A)(1); § 343-7 | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Licensed Driller |  |  | § 343-4(B)(2) requires a permit application to include "The well driller's name and proof of valid state registration." § 343-9(A) states: "Pursuant to 313 CMR 3.00, no person in the business of drilling shall construct a well unless registered with the Department of Environmental Management/Office of Water Resources." | § 343-4(B)(2); § 343-9(A) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Certification |  |  | § 343-3 defines "REGISTERED WELL DRILLER" as "Any person registered with the Department of Environmental Management/Division of Water Supply Protection to dig or drill wells in the Commonwealth of Massachusetts." § 343-9(A): "no person in the business of drilling shall construct a well unless registered with the Department of Environmental Management/Office of Water Resources." § 343-10(C): "Only registered well drillers may plug abandoned wells, test holes, and borings." | § 343-3 Definitions; § 343-9(A); § 343-10(C) | 2008 | https://ecode360.com/10442189
Massachusetts | Essex | Middleton | 2500941095 | Decommissioning |  |  | § 343-10(A): "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." § 343-10(B): "The owner of the private well shall decommission the well" when listed abandonment conditions occur. § 343-10(C): "Only registered well drillers may plug abandoned wells, test holes, and borings." § 343-10(E): "Abandoned wells or borings shall be completely filled with a grout..." and § 343-10(G): "The plugging materials shall be introduced at the bottom of the well or boring and placed progressively upward..." | § 343-10 Decommissioning requirements | 2008 | https://ecode360.com/10442189
Massachusetts | Franklin | Greenfield | 2501127060 | Definition: Geothermal |  |  | "RENEWABLE ENERGY -- The following shall be considered renewable energy: ... • Geothermal ..." | § 200-2.1. Terms and words | 2021 | https://cms5.revize.com/revize/greenfield/Document_Center/Department/Planning%20&%20Development/Zoning_Ordinance.pdf
Massachusetts | Middlesex | Acton | 2501700380 | Definition: Geothermal Heat Pump |  |  | "Geothermal Wells" are referenced in the operative clause: "Notwithstanding the requirements of 9-6.4, the Health Department may grant approval for the installation of Geothermal Wells in public water supply areas..." | Regulation 9-6.4.2 | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Acton | 2501700380 | Permit |  |  | "Notwithstanding the requirements of 9-6.4, the Health Department may grant approval for the installation of Geothermal Wells in public water supply areas when the following conditions have been met:" and "A plan showing the location of the geothermal wells and detailing the system, including piping, heat transfer media and construction, shall be submitted to the Health Division for approval." | Regulation 9-6.4.2(a) | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Acton | 2501700380 | Decommissioning |  |  | "If the geothermal wells not be used for a period of two years, it shall be abandoned and permanently secured by filling the well head with a concrete slurry and by taking all other actions necessary to make the well and area safe from potential accidents and hazards." | Regulation 9-6.4.2(d) | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Acton | 2501700380 | Open-loop Prohibitions |  |  | "All wells for geothermal use shall be artesian or bedrock wells with a closed loop system in the well..." | Regulation 9-6.4.2(a) | 2020 | https://www.acton-ma.gov/138/Board-of-Health-Rules-and-Regulations
Massachusetts | Middlesex | Burlington | 2501709840 | Definition: Well |  |  | "Private Ground Source Heat Pump (Geothermal) Well: Any excavation by any method for the purpose of transferring heat to or from the earth for heating and cooling purposes in which the ambient ground temperature is 90 degrees Fahrenheit or less." | 5.2 Definitions | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | 2501709840 | Setback - Property Lines | 10 | feet | Section 5.6 states: "Private wells must meet the following setback requirements except as otherwise provided below: 10 feet from the property line." Section 5.3.E applies these regulations to "Private Ground Source Heat Pump (Geothermal) Wells" through Sections 5.8-5.12, but Section 5.3.E does not apply Section 5.6 to geothermal wells. | 5.6 Well Location and Operation Requirements | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | 2501709840 | Permit |  |  | Section 5.3.E provides that private geothermal wells are subject to "Article III, Section 5.4 and Section 5.8 through Section 5.12." Section 5.4 states: "The Property Owner and a Massachusetts Certified Well Driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." | 5.3.E Private Ground Source Heat Pump (Geothermal) Wells; 5.4 Well Construction and Operation Permit | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | 2501709840 | Licensed Driller |  |  | Section 5.4 states: "The Property Owner and a Massachusetts Certified Well Driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." The permit application must include "the well driller's name and proof of valid Massachusetts certification." Section 5.9 adds: "Only certified well drillers may plug abandoned wells, test holes, and borings." | 5.4 Well Construction and Operation Permit; 5.9 Decommissioning Requirements | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | 2501709840 | Certification |  |  | Section 5.2 defines "Certified Well Driller" as: "Any person certified with the Massachusetts Department of Environmental Protection Well Driller Program to dig or drill wells in the Commonwealth of Massachusetts." Section 5.4 requires the permit application to include "the well driller's name and proof of valid Massachusetts certification." | 5.2 Definitions; 5.4 Well Construction and Operation Permit | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Burlington | 2501709840 | Decommissioning |  |  | Section 5.8 states that the "Guidelines for Ground Source Heat Pump Wells" are "incorporated herein as requirements for private ground source heat pump (geothermal) wells." Section 5.9 further requires: "Abandoned wells, test holes, and boring shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." It also states: "The owner of a private well shall decommission the well" upon listed triggers, including when "the use of the well is to be permanently discontinued" or "the well has been out of service for at least three (3) years." "The Property Owner shall ensure that all abandoned wells and test holes or borings associated with private well installation are properly plugged before work on the site is complete." | 5.8 Additional Requirements; 5.9 Decommissioning Requirements | 2017 | https://www.burlington.org/DocumentCenter/View/13761
Massachusetts | Middlesex | Chelmsford | 2501713135 | Permit |  |  | § 201-31.7 states: "Ground source heat pump wells installed in the Town of Chelmsford must comply with all regulations of the Mass DEP as set forth in the 'Guidelines for Ground Source Heat Pump Wells.'" Within this article, § 201-31.1 requires that "A Massachusetts-certified well driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." | § 201-31.7 Geothermal wells (ground source heat pump wells); § 201-31.1 Well construction permit | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | 2501713135 | Licensed Driller |  |  | "A Massachusetts-certified well driller shall obtain a permit from the Board of Health prior to the commencement of construction of a private well." Also, "Pursuant to 310 CMR 46.02(1), no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | § 201-31.1 Well construction permit; § 201-31.6 Well construction | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | 2501713135 | Certification |  |  | "CERTIFIED WELL DRILLER — Any person certified with the Department of Environmental Protection Well Driller Program to dig or drill wells in the Commonwealth of Massachusetts." Permit applications must include "the well driller's name and proof of valid Massachusetts certification," and "no person in the business of digging or drilling shall construct a well unless certified by the MassDEP Well Drillers Program." | § 201-30.3 Definitions; § 201-31.1 Well construction permit; § 201-31.6 Well construction | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | 2501713135 | Decommissioning |  |  | "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." "The owner of a private well shall decommission the well if" specified criteria are met, including permanent discontinuance, three years out of service, hazard, disrepair, or contamination risk. "The property owner shall ensure that all abandoned wells and test holes or borings associated with the well installation are properly plugged before work at the site is completed. Only certified well drillers may plug abandoned wells, test holes, and borings." | § 201-31.9 Decommissioning | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Chelmsford | 2501713135 | Open-loop Prohibitions |  |  | "Only closed-loop GSHPW systems are approved in Town. All other well types require a variance from the Board." | § 201-31.7 Geothermal wells (ground source heat pump wells) | 2021 | https://ecode360.com/8275407
Massachusetts | Middlesex | Groton | 2501727480 | Definition: Well |  |  | "GEOTHERMAL WELL — Any shaft or hole drilled into the surface of the earth, greater than 20 feet in depth, which is used or intended to be used in connection with coring, or the drilling for, prospecting for, or the production of geothermal resources, hot water, petroleum, natural gas, or other hydrocarbon substances, or shallow extraction wells for heating, agricultural or other purposes, or is used or intended to be used for the subsurface injection into the earth of oilfield waste, gases, water or liquid substances..." | § 330-3 Definitions | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Definition: Geothermal Heat Pump |  |  | "CLOSED-LOOP GEOTHERMAL BOREHOLE — A boring drilled to facilitate the installation of a pipe loop or tubing for a ground source heat pump system whether circulating water, heat transfer fluid or refrigerant using direct exchange." Also: "OPEN-LOOP BOREHOLE — A water well designed to produce source water above land surface to provide heat transfer to a geothermal well." | § 330-3 Definitions | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Driveways | 50 | feet | The minimum-distance table states: "Public or private way, common drive, roadway easement, parking lot — 50" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Roads | 50 | feet | The minimum-distance table states: "Public or private way, common drive, roadway easement, parking lot — 50" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Right of Way | 50 | feet | The minimum-distance table states: "Public or private way, common drive, roadway easement, parking lot — 50" feet. The permit application requirements also require identifying "Utility right-of-way," but that clause does not give a numeric distance. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Property Lines | 50 | feet | The minimum-distance table states: "Property line — 50" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Building Foundation | 10 | feet | The minimum-distance table states: "Slab or foundation — 10" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Wastewater | 100 | feet | The minimum-distance table states: "Leaching facility (310 CMR 15.00) — 100" feet; "Cesspool — 100" feet; "Septic tank — 50" feet; and "Septic expansion area — 100" feet. § 330-12(A)(1) for closed-loop geothermal boreholes states: "Septic tanks — 25" feet and "Septic drain fields — 50" feet. The controlling most restrictive wastewater setback stated is 100 feet. | § 330-6 Well location and use requirements; § 330-12 Geothermal wells | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Public Water | 100 | feet | For closed-loop geothermal boreholes, § 330-12(A)(1) states: "Water wells — 100" feet. | § 330-12 Geothermal wells | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Sewer Lines | 10 | feet | The general well-location table states: "Sewer line — 100" feet. § 330-12(A)(1) separately states for closed-loop geothermal boreholes: "Sewer lines — 10" feet and "House to sewer line connection — 10" feet. The controlling most restrictive stated sewer-line separation in this ordinance is 100 feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Pools | 25 | feet | The minimum-distance table states: "In-ground pool — 25" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Setback - Water Bodies | 100 | feet | The minimum-distance table states: "Any type of surface water/wetland — 100" feet. § 330-12(A)(1) also states for closed-loop geothermal boreholes: "Springs — 100" feet. | § 330-6 Well location and use requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Minimum Well Depth | 20 | feet | "GEOTHERMAL WELL — Any shaft or hole drilled into the surface of the earth, greater than 20 feet in depth..." | § 330-3 Definitions | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Permit |  |  | "The application for a permit for the installation of an individual well, geothermal well, irrigation well, monitoring well and test well shall be made by a contractor, appropriately licensed." Also: "The property owner or his/her/their designated representative shall obtain a permit from the Board of Health or its agent prior to the commencement of construction and/or deconstruction of... heating and cooling well, agricultural well, drilled holes, bore holes, or other holes drilled by mechanical means greater than 10 feet..." | § 330-4 Well construction/deconstruction permit | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Licensed Driller |  |  | "All individual wells, geothermal wells, monitoring wells and test wells constructed pursuant to these regulations shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor." | § 330-9 Well construction requirements | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Groton | 2501727480 | Decommissioning |  |  | "A well that is abandoned shall be destroyed to protect the groundwater and to eliminate potential physical hazards. Wells shall be sealed with nonhazardous, impervious materials which shall be permanently in place. All casing materials, pumping equipment, and distribution lines shall be removed. The excavation shall be returned to the current existing grade of the surrounding land." Also: "Abandoned wells, test holes, and borings shall be decommissioned..." and "Only registered well drillers may plug abandoned wells, test holes, and borings." | § 330-10 Deconstruction requirements and irrigation wells | 2023 | https://ecode360.com/9080575
Massachusetts | Middlesex | Lexington | 2501735215 | Definition: Geothermal Heat Pump |  |  | "Any type of well constructed for the purposes of using the ambient temperature of the earth beneath the surface to heat or cool water or other fluids as part of the heating, ventilation, and air conditioning system of a building." | § 155-73H(1) Geothermal wells | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Setback - Property Lines | 50 | feet | Applicants for a Board of Health closed loop geothermal heating system well registration must provide "[a] plan depicting that the system well has a minimum setback distance of 50 feet from any private water supply well or section line or any on-site disposal system ..." | § 155-73H(7)(e) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Setback - Wastewater | 50 | feet | Applicants for a Board of Health closed loop geothermal heating system well registration must provide "[a] plan depicting that the system well has a minimum setback distance of 50 feet from any private water supply well or section line or any on-site disposal system (as defined by 310 CMR 15.002)." | § 155-73H(7)(e) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Setback - Private Water | 50 | feet | Applicants for a Board of Health closed loop geothermal heating system well registration must provide "[a] plan depicting that the system well has a minimum setback distance of 50 feet from any private water supply well ..." | § 155-73H(7)(e) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Permit |  |  | "The property owner or the well driller/digger or his agent shall submit a well construction application, prior to the commencement of construction and/or destruction of a ... geothermal well" (§ 155-72A). Also, "No well shall be constructed, altered or repaired until a well construction permit has been obtained from the Board of Health" (§ 155-71E). For closed-loop geothermal systems, "applicants ... for a Board of Health closed loop geothermal heating system well registration must attach" specified materials, including the MassDEP UIC registration form and registration ID number (§ 155-73H(7)(a)-(b)). | § 155-72 Well construction permit; § 155-73 Well construction | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Inspection |  |  | "All ground source wells installed in the Town of Lexington must be tested for the parameters outlined in the referenced Guidelines" (§ 155-73H(5)). Section § 155-73H(3) also states that installers "must comply with all state and federal regulations applicable to the well being installed ... including but not limited to requirements with respect to reinjection of return water, fluids used in the system, and testing requirements." | § 155-73 Well construction | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Licensed Driller |  |  | "No well shall be installed, altered, repaired, destroyed or abandoned except by a well driller who is registered with the Water Resources Commission, Division of Water Resources" (§ 155-71C). For geothermal wells specifically, the ordinance also requires compliance with the "Massachusetts Well Driller Certification Program (310 CMR 46.00)" (§ 155-73H(1)(d)) and states "the well driller will fully grout the well following piping installation" (§ 155-73H(7)(g)). | § 155-71 General provisions; § 155-73 Well construction | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Certification |  |  | For closed-loop systems, "if not a water only system, the Material Safety Data Sheet (MSDS) for the recirculation fluid to be used in the system must be submitted which indicated that the fluid is non-toxic and non-hazardous food grade propylene glycol." | § 155-73H(7)(c) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Decommissioning |  |  | "Prior to the destruction or abandonment of any well, a well destruction permit must be obtained" (§ 155-78A). "Abandoned wells, test holes and borings shall be decommissioned so as to prevent the well ... from being a channel for pollution into the groundwater" (§ 155-78B). "Only registered well drillers may plug abandoned wells, test holes and borings" (§ 155-78C). "Abandoned wells or borings shall be completely filled with a grout" meeting the stated permeability standard, and a report must be submitted "within 30 days after completion of destruction or abandonment" (§ 155-78D-E). | § 155-78 Well decommission | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Lexington | 2501735215 | Other Prohibitions/Regulations |  |  | "No ground source heat pump wells may be used for potable water." | § 155-73H(4) | 2022 | https://ecode360.com/10536673
Massachusetts | Middlesex | Natick | 2501743895 | Definition: Geothermal |  |  | "Renewable or Alternative Energy : The following renewable or alternative energy generation activities, products, or technologies: solar (both photovoltaic (PV) and thermal); wind; biomass power conversion or thermal technologies, including R&D related to, or the manufacture of, wood pellets; ultra low emissions high efficiency wood pellet boilers and furnaces; low impact hydro (electric or kinetic); ocean thermal, wave or tidal; geothermal; landfill gas; fuel cells that use renewable energy; advanced biofuels; combined heat and power; electric and hydrogen powered vehicles and associated technologies including advanced batteries and recharging stations." | Section 200 - Definitions | 2025 | https://natickma.gov/DocumentCenter/View/19913/06092025-Addendum-of-2024-Fall-and-2025-Spring-ATM-Zoing-Amendments
Massachusetts | Middlesex | Wakefield | 2501772215 | Definition: Well |  |  | "Well: any hole or shaft drilled into the ground to inject or withdraw water, other fluids, or gases, monitor soil gasses, monitor groundwater levels or water quality, transfer heat, or provide cathodic protection." | III. DEFINITIONS | 2019 | https://www.wakefieldma.gov/DocumentCenter/View/479/Wells-PDF
Massachusetts | Middlesex | Westford | 2501776135 | Definition: Well |  |  | "The word 'WELL', as used in these regulations, shall include any pit, pipe, excavation, casing, drill hole or other source of water to be used for any purpose of supplying potable water, irrigation water, process water, or water for a Ground Source Heat Pump (GSHP) in Westford." | DEFINITIONS | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | 2501776135 | Definition: Geothermal Heat Pump |  |  | "The words 'GSHP WELL' or GROUND SOURCE HEAT PUMP WELL, shall mean any Class V well as defined by 310 CMR 27.03(5) that uses heat transferred to or from the earth to heat and/or cool a structure." | DEFINITIONS | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | 2501776135 | Permit |  |  | "Ground Source Heat Pump Wells installed and operated in the Town of Westford must comply with all regulations of the Mass DEP as set forth in the 'Guidelines for Ground Source Heat Pump Wells'... including but not limited to requirements with respect to reinjection of return water, fluids used in the system, and testing requirements." The ordinance also lists "Massachusetts Groundwater Discharge Permits (314 CMR 5.00)" under "GROUND SOURCE HEAT PUMP WELLS: shall comply with the Mass DEP Regulations." | GROUND SOURCE HEAT PUMP WELLS | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | 2501776135 | Inspection |  |  | "The Board or its agent may require inspection of the work during its progress, including, among other things, the adequacy of the required seal, the pump test, and shall designate the notice required to be given to the Board or its agent that said work is ready for inspection." | CONSTRUCTION, PERMITS, INSPECTIONS, & CERTIFICATES | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | 2501776135 | Licensed Driller |  |  | "Every owner of a company installing wells in Westford shall be required each year to provide the Board with a copy of their well driller's certificate issued by the appropriate governing agency of the State of Massachusetts." Also: "Only certified well drillers may plug abandoned wells, test holes, and borings." | WELL DRILLERS CERTIFICATES & PERMITS / DECOMMISSIONING A WELL | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Middlesex | Westford | 2501776135 | Decommissioning |  |  | "Abandoned wells, test holes, and borings shall be decommissioned so as to prevent the well, including the annular space outside the casing, from being a channel allowing the vertical movement of water." "The owner of a private well shall decommission the well if any of the following criteria are met:" including when "the use of the well is to be permanently discontinued" or "the well has been out of service for at least three (3) years." "The property owner shall ensure that that all abandoned wells and test holes or borings associated with the well installation are properly plugged before work at the site is completed." | DECOMMISSIONING A WELL | 2019 | https://westfordma.gov/DocumentCenter/View/7622/Westford--Well-Regulation-
Massachusetts | Norfolk | Dover | 2502117405 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP WELL — Any excavation by any method for the purpose of transferring heat to or from the earth for heating and cooling purposes. Ground source heat pump wells shall be installed in accordance with MassDEP guidelines; §§ 233-6 through 233-11 of these regulations do not apply to such wells." | § 233-3 Definitions | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | 2502117405 | Permit |  |  | "Before the commencement of construction of a private well, the property owner or his designated representative shall complete the well construction application in full. No work shall commence until the application is approved by the Board or its agent." Also, "A well construction permit shall be required for the installation of any new private well..." | § 233-5 Well construction permit | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | 2502117405 | Inspection |  |  | "The agent shall review the design plans to verify such conformity." | § 233-4 Ground source heat pump wells | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | 2502117405 | Licensed Driller |  |  | § 233-5(A)(2): "The Massachusetts certified well driller's name, address, phone number and proof of valid Massachusetts well driller certification. Only a Massachusetts certified well driller may install a well." § 233-9(P): "Pursuant to 310 CMR 46.00... no person shall engage in the business of well drilling in the Commonwealth." | § 233-5 Well construction permit; § 233-9 General well design and construction parameters | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | 2502117405 | Certification |  |  | "MASSACHUSETTS CERTIFIED WELL DRILLER — Any person or company properly certified by the Commonwealth of Massachusetts pursuant to 310 CMR 46.00, or registered with the Commonwealth pursuant to the predecessor regulations (313 CMR 3.00), to install wells." § 233-5(A)(2) requires "proof of valid Massachusetts well driller certification." § 233-9(P) references "a holder of a certificate in accordance with 310 CMR 46.02, or a registration in accordance with the predecessor regulations, 313 CMR 3.00." | § 233-3 Definitions; § 233-5 Well construction permit; § 233-9 General well design and construction parameters | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Dover | 2502117405 | Decommissioning |  |  | "Abandoned wells, test holes and borings shall be decommissioned so as to prevent the well... from becoming a channel allowing the vertical movement of water and possible contamination." "The property owner shall be responsible for ensuring that all abandoned wells, test holes and borings are properly decommissioned." "Only Massachusetts certified well drillers may decommission wells, test holes and borings." "Abandoned wells, test holes or borings shall be completely filled and plugged with either neat cement grout, sand cement grout, concrete or Bentonite grout." | § 233-12 Decommissioning requirement | 2017 | https://ecode360.com/10428100
Massachusetts | Norfolk | Needham | 2502144105 | Definition: Well |  |  | "Geothermal well : Any well constructed for the location, exploration, monitoring, development, or injection of geothermal resources or the natural heat of the earth, the energy which may be extracted from the natural heat in whatever form found below the surface of the earth as defined." | SECTION 12.3 DEFINITIONS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Definition: Geothermal Heat Pump |  |  | "Open-loop geothermal well : A system which pipes clean ground water directly from a nearby aquifer to an indoor geothermal heat pump. Water leaving the home is expelled through a discharge well which is located a suitable distance from the first." "Closed-loop geothermal well: A ground source heat pump well that uses a closed-loop fluid system to prevent the discharge or escape of its fluid into the subsurface. Closed-loop heat pump wells shall not be used to produce water." "Ground source or geothermal heat pump system : A heating and/or cooling system that transfers heat to or from the earth in which the naturally occurring, ambient ground temperature is 90 degrees Fahrenheit or less." | SECTION 12.3 DEFINITIONS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Roads | 25 | feet | Section 12.12.1 states geothermal wells are governed by these regulations, and Section 12.9.1 provides: "Wells shall be located the following minimum distances from sources of contamination: B. public or private roadways - 25 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Right of Way | 25 | feet | Section 12.12.1 states geothermal wells are governed by these regulations, and Section 12.9.1 provides: "Wells shall be located the following minimum distances from sources of contamination: C. right of way or easements - 25 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Property Lines | 10 | feet | Section 12.12.1 states geothermal wells are governed by these regulations, and Section 12.9.1 provides: "Wells shall be located the following minimum distances from sources of contamination: A. property lines - 10 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Wastewater | 100 | feet | Section 12.9.1 lists wastewater-related setbacks: "E. septic pump or tank - 50 feet *"; "F. privy - 100 feet*"; "G. leaching field (cesspool) or drywell - 100 feet *." Section 12.12.2(E) also provides a geothermal-specific setback: "Geothermal wells shall be located at least 25 feet from potential sources of contamination including, but not limited to septic tanks and field, lagoons...." The most restrictive wastewater setback stated is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Private Water | 50 | feet | Section 12.12.2(D): "Geothermal wells shall be located at least 50 feet from private potable water supply wells." | SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Public Water | 10 | feet | Section 12.12.2(C): "Geothermal wells shall be sited at least 10 feet from surface water bodies, potable water, and sewer lines." | SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Animal Enclosures | 100 | feet | Section 12.9.1: "H. stable, barnyard, manure storage - 100 feet." Section 12.12.2(E) also states: "Geothermal wells shall be located at least 25 feet from potential sources of contamination including, but not limited to ... livestock pens...." The more restrictive stated setback is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Fuel (above ground) | 100 | feet | Section 12.9.1 provides: "I. aboveground fuel storage - 100 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Fuel (below ground) | 100 | feet | Section 12.9.1 provides: "J. underground fuel storage - 100 feet." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Subsurface Drains | 25 | feet | Section 12.9.1 provides: "L. subsurface drains - 25 feet *." | SECTION 12.9 LOCATION | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Sewer Lines | 50 | feet | General well setback table at Section 12.9.1: "D. sewer line - 50 feet * (10 feet from a building sewer constructed of durable corrosion resistant material with watertight joints)." Geothermal-specific Section 12.12.2(C) states: "Geothermal wells shall be sited at least 10 feet from surface water bodies, potable water, and sewer lines." The more restrictive stated sewer-line setback is 50 feet in Section 12.9.1. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Water Bodies | 100 | feet | Section 12.9.1 provides: "K. surface water, wetlands - 100 feet **." Section 12.12.2(C) also states: "Geothermal wells shall be sited at least 10 feet from surface water bodies...." The more restrictive stated setback is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Section 12.12.2(E) states: "Geothermal wells shall be located at least 25 feet from potential sources of contamination including, but not limited to ... oil or hazardous materials storage tanks." Section 12.9.1 also provides broader well setbacks including "I. aboveground fuel storage - 100 feet" and "J. underground fuel storage - 100 feet." The most restrictive explicit setback tied to hazardous/oil storage is 100 feet. | SECTION 12.9 LOCATION; SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Permit |  |  | "12.4.1 Unless otherwise specified, all sections of this regulation apply to open-loop and closed-loop well systems." "Each well permit application will be reviewed and approved by the following before a permit to construct any well will be issued." Section 12.12.2(I): "Any ground source heat pump well system with flows in excess of 15,000 gallons per day must be permitted by the DEP Groundwater Discharge Program (per 314 CMR 5.05)." Section 12.21.1: "Applicants for well permits may be required to obtain plumbing and/or building permits from the Town of Needham Building Department." | SECTION 12.4 WELL CONSTRUCTION PERMIT; SECTION 12.12 GEOTHERMAL WELLS; SECTION 12.21 OTHER PERMITS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Inspection |  |  | Section 12.12.2(L): "The contractor must notify the Water and Sewer Division and the Town Building Commissioner of completion so both Water and Sewer Division and Building Department can conduct a final inspection." Section 12.12.3: "No ground source heat pump well shall be used for its intended purpose until the Public Health Division receives a copy of the final inspection sign-off approval sheets form the Water and Sewer Division and the Building Department along with a copy of the Well Completion Report." | SECTION 12.12 GEOTHERMAL WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Licensed Driller |  |  | Section 12.4.2: "Pursuant to 310 CMR 46.00, no person in the business of digging or drilling shall construct a well unless registered with the Commonwealth of Massachusetts Department of Environmental Management, Office of Water Resources." Section 12.6.1 similarly states: "no person in the business of digging, driving, jetting, drilling or any other method shall construct a well unless registered with the Commonwealth of Massachusetts Department of Environmental Management, Office of Water Resources." Because Section 12.4.1 says "all sections of this regulation apply to open-loop and closed-loop well systems," this drilling registration requirement applies to geothermal wells covered by the regulation. | SECTION 12.4 WELL CONSTRUCTION PERMIT; SECTION 12.6 REGISTRATION REQUIREMENT | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Certification |  |  | "Well completion reports must be submitted for all activities covered under 310 CMR 46.00 including well drilling, decommissioning, Ground Source Heat Pump wells ('geothermal'), repairs, deepening, yield enhancement, pump installation and replacement. ... It should be noted that performing activities under the regulations cited without being certified in Massachusetts is a violation and the violator(s) subject to enforcement action." | SECTION 12.5 WELL COMPLETION REPORT | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Needham | 2502144105 | Decommissioning |  |  | Section 12.5.1 includes geothermal wells in decommissioning reporting: "Well completion reports must be submitted for all activities covered under 310 CMR 46.00 including ... decommissioning, Ground Source Heat Pump wells ('geothermal')...." Section 12.13.1: "A well which has not been used for two consecutive calendar years shall be considered abandoned. The owner of record of such well shall notify the Board of Health in writing that the well is abandoned and shall have a registered well driller seal the well..." Section 12.13.5: "The owner of a private well shall decommission the well if the well meets any of the following criteria..." Section 12.13.6: "Decommissioning must follow Department of Environmental Protection guidelines." | SECTION 12.5 WELL COMPLETION REPORT; SECTION 12.13 ABANDONMENT, or DECOMMISIONING OF WELLS | 2021 | https://www.needhamma.gov/DocumentCenter/View/24271/ARTICLE-12---Well-Regulation_9-29-21
Massachusetts | Norfolk | Plainville | 2502154100 | Definition: Well |  |  | "WELL OR WATER WELL — Any hole or shaft constructed into the ground for the purpose of extracting or injecting water. This definition shall not include wells to dewater excavations or stabilize hillside or earth embankments. It shall include wells connected to heat pumps." | § 784-3 Definitions | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Definition: Geothermal Heat Pump |  |  | "HEAT PUMP WELL — Consists of a source well and a discharge well which could be one in the same, provided that it is a closed loop system where nothing is added to or taken from the water except heat and no air is in contact with the return water. A heat pump delivers water by way of the source well from an aquifer through a heat exchanger and returns it to the aquifer via the discharge well. The system utilizes the thermal energy stored in groundwater for space heating or cooling." | § 784-3 Definitions | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Setback - Property Lines | 50 | feet | "A water well shall also be a minimum of 50 feet from all property lines." | § 784-8B(2) Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Setback - Wastewater | 175 | feet | The table states: "The minimum setback from a leaching area shall be determined by the soil percolation rate and the vertical clearance of the leaching area above the high groundwater (HGW)." Listed distances from leaching area include "175+" feet for certain conditions, with lower alternatives of 151 to 174, 126 to 150, 100 to 125, 150+, and 125+ feet depending on percolation and HGW. The same section also lists "Septic tank — 50" feet and "Distribution box — 100" feet. | § 784-8B(1) Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Setback - Sewer Lines | 50 | feet | The contaminants table lists "Sewer footing drains with cast-iron watertight joints — 50" feet as a minimum lateral distance. | § 784-8B(1) Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Permit |  |  | "A well construction permit shall be obtained from the Board prior to the construction of any water well or well system." "An application for a water well construction permit shall be submitted by the drilling contractor or his agent..." and "The location, design, and operation of the water well must be approved by the Board... prior to construction." | § 784-7C Well construction permits | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Inspection |  |  | "The pumping test shall be performed by a licensed pump or well drilling contractor and in the presence of the Board agent or member; a minimum of five-gallons-a-minute yield shall be deemed acceptable per dwelling unit." | § 784-19 Yield test | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Licensed Driller |  |  | "No person shall engage in the business of constructing wells within the commonwealth unless he is registered with the Water Resources Commission, Division of Water Resources, as required by the Water Well Drillers Registration Act"; § 784-6 also states "a registered well driller shall submit to the Board a report" within 30 days after completion of any water well. | § 784-5 Registration of well drillers | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Plainville | 2502154100 | Other Prohibitions/Regulations |  |  | "The construction of a well in a wetland shall be prohibited." | § 784-8D Well location with respect to contaminants and pollutants | 2019 | https://ecode360.com/15554182
Massachusetts | Norfolk | Sharon | 2502160785 | Definition: Geothermal Heat Pump |  |  | "HEAT PUMP WELLS Consists of a source well and a discharge well which could be one and the same, provided it is a closed-loop system where nothing is added to or taken from the water except heat and no air is in contact with the return water. A heat pump delivers water by way of the source well from an aquifer through a heat exchanger, and returns it to the aquifer via the discharge well. The system utilizes the thermal energy stored in groundwater for space heating or cooling." | § 300-16.1C Definitions | 2022 | https://ecode360.com/29557412
Massachusetts | Norfolk | Wellesley | 2502174175 | Setback - Yards | 20 | feet | "Heating, ventilation, air conditioning, swimming pool, electric generating, or other noise emitting equipment shall not be located in required setback areas except for Heat Pumps located in Side Yards or Rear Yards which are attached to and do not extend more than two feet from the wall of the building ... or are ground mounted and do not extend more than four feet from the foundation of the building." Tables 1-3 set yard requirements, including "Minimum Side Yard Width" of 20 ft. in all listed districts/tables, with larger values in some Table 3 districts; rear yards range from 10 ft. to 40 ft. | SECTION 5.3. YARD REGULATIONS | 2022 | https://wellesleyma.gov/DocumentCenter/View/12119/Full-Zoning-Bylaw_Version-10-1-2018
Massachusetts | Norfolk | Wellesley | 2502174175 | Setback - Building Foundation | 4 | feet | "Heating, ventilation, air conditioning, swimming pool, electric generating, or other noise emitting equipment shall not be located in required setback areas except for Heat Pumps located in Side Yards or Rear Yards which are attached to and do not extend more than two feet from the wall of the building ... or are ground mounted and do not extend more than four feet from the foundation of the building, including any pad on which the Heat Pump is mounted." | SECTION 5.3. YARD REGULATIONS | 2022 | https://wellesleyma.gov/DocumentCenter/View/12119/Full-Zoning-Bylaw_Version-10-1-2018
Massachusetts | Norfolk | Wellesley | 2502174175 | Screening |  |  | "Plans and installation of sound reduction and/or visual screening may be required if, in the opinion of the Inspector of Buildings abutters may be affected." | SECTION 5.3. YARD REGULATIONS | 2022 | https://wellesleyma.gov/DocumentCenter/View/12119/Full-Zoning-Bylaw_Version-10-1-2018
Massachusetts | Plymouth | Kingston | 2502333220 | Setback - Property Lines | 25 | feet | "All wells shall be located at sufficient distances from potential sources of pollution... The following minimum lateral distances shall apply... (e) Property lines 25 feet." | § 405-98(A)(1)(e) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | 2502333220 | Setback - Wastewater | 125 | feet | "All wells shall be located at sufficient distances from potential sources of pollution... The following minimum lateral distances shall apply... (a) Subsurface sewage disposal facilities minimum lateral distance 125 feet; (b) Septic tank 50 feet; (c) Distribution box 50 feet." | § 405-98(A)(1)(a)-(c) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | 2502333220 | Setback - Sewer Lines | 50 | feet | "All wells shall be located at sufficient distances from potential sources of pollution... The following minimum lateral distances shall apply... (d) Sewers 50 feet." | § 405-98(A)(1)(d) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | 2502333220 | Minimum Well Depth | 40 | feet | "The casing for a driven or drilled well shall have minimum length of 40 feet." | § 405-99(A) |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | 2502333220 | Permit |  |  | "A well construction permit shall be obtained from the Board of Health prior to the construction of any well." "The purpose for which any well is to be used must be indicated in the application permit." § 405-94(A)(3) lists "Heating and/or cooling" as an allowed use of a private well supply. | § 405-95 Permits |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | 2502333220 | Licensed Driller |  |  | "Construction of wells in Kingston shall be performed only by well drillers who are registered with the Massachusetts Water Resources Commission, Division of Water Resources, as required by 310 CMR 46.00, Certification of Well Drillers and Filing of Well Completion Reports." | § 405-96 Registration for well drillers |  | https://ecode360.com/37646456
Massachusetts | Plymouth | Kingston | 2502333220 | Certification |  |  | § 405-95(B): "Permit shall also include the well driller's name and proof of valid state registration under MGL c. 21G, § 20." § 405-96: wells must be performed by drillers "registered with the Massachusetts Water Resources Commission, Division of Water Resources, as required by 310 CMR 46.00, Certification of Well Drillers and Filing of Well Completion Reports." § 405-93 defines "WELL DRILLER" as a person "licensed by the Massachusetts Water Resources Commission to construct wells." | § 405-95(B); § 405-96; § 405-93 |  | https://ecode360.com/37646456
Massachusetts | Worcester | Harvard | 2502728950 | Screening |  |  | "The placement of buildings and structures in an OSC-PRD should: (a) Provide for maximum buffering of buildings and structures to adjoining properties... Such buffering includes, but is not limited to: landscaping, screening materials, natural barriers, fencing, and related measures." | § 125-35E(1)(a) Building and structure placement | 2023 | https://ecode360.com/13697267
Massachusetts | Worcester | Leominster | 2502735075 | Definition: Geothermal |  |  | "Energy system, renewable. Any facility or installation such as a windmill, hydroelectric unit, or solar collecting or concentrating array, which is designed and intended to produce energy from natural forces such as wind, water, sunlight, or geothermal heat, or from biomass, for offsite use." | Section 22-4. Definitions | 2013 | https://leominster-ma.gov/DocumentCenter/View/997
Massachusetts | Worcester | Mendon | 2502740255 | Definition: Well |  |  | "Geothermal Well - Ground source heat pump wells used for heating and cooling; further defined by DEP guidance." | Definitions | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Roads | 10 | feet | The setback table in §5.2(1) states: "Public or Private Way, Common Drive Easement ... 10" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Right of Way | 10 | feet | The setback table in §5.2(1) states: "Public or Private Way, Common Drive Easement ... 10" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Property Lines | 10 | feet | The setback table in §5.2(1) states: "Property Line ... 10" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Building Foundation | 25 | feet | The setback table in §5.2(1) states: "Dwelling Unit (Including Overhang) ... 25" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Wastewater | 100 | feet | Section 5.2(1) sets minimum lateral distances of "Leaching Facility (310 CMR 15.00) ...100," "Existing Cesspool ...100," and "Septic Tank ... 50." Section 5.3(6) also states: "Pump suction lines, if used, shall not be closer than 100 feet from the underground sewage leaching facilities or 50 feet from a septic tank (310 CMR 15.03)." | Well Construction Permit Requirements §5.2(1); §5.3(6) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Animal Enclosures | 100 | feet | The setback table in §5.2(1) states: "Stable and Manure Storage Areas ...100" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Fuel (below ground) | 200 | feet | The setback table in §5.2(1) states: "Underground Storage Tank (Outside Dwelling) ...200" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Sewer Lines | 50 | feet | The setback table in §5.2(1) states: "Sewer Line ... 50" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Setback - Water Bodies | 50 | feet | The setback table in §5.2(1) states: "Any Type of Surface Water ... 50" under "Minimum Lateral Distance (feet)." | Well Construction Permit Requirements §5.2(1) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Permit |  |  | "No private or semipublic water supply shall be installed, altered or repaired until a permit has been obtained from the Board of Health or its agent." Also, "A well construction/destruction permit shall be obtained from the Board prior to the construction/destruction or abandoning of any private well." Geothermal-specific text states: "A Geothermal well or modifications to the existing well are required to meet DEP Geothermal well guidelines." | Requirements for Private Wells and Semi-Public Water Supplies §3.2; Well Construction or Destruction Permits §§4.3-4.4; Well Construction Permit Requirements §5.1(3) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Inspection |  |  | Section 5.3(5) states: "A minimum yield of five gallons per minute (GPM) for four hours is required. When the pump test is performed, a representative of the Board or its agent may observe the initial startup. Following the pump test the well must be shown to recover to within 85% of the pre-pumped static level within 24 hours." | Well Construction Standards §5.3(5) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Licensed Driller |  |  | "No person shall engage in the business of construction or destruction of private wells within the town under these regulations unless registered as a well driller/digger with the DEP, pursuant to 310 CMR 46.00. A copy of the Well Driller’s License must accompany the application for a Well Permit." | Well Construction or Destruction Permits §4.1 | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Certification |  |  | "No person shall engage in the business of construction or destruction of private wells within the town under these regulations unless registered as a well driller/digger with the DEP, pursuant to 310 CMR 46.00. A copy of the Well Driller’s License must accompany the application for a Well Permit." | Well Construction or Destruction Permits §4.1 | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Mendon | 2502740255 | Decommissioning |  |  | The Definitions section states: "Abandonment of Water Well - Decommissioning, removal, or sealing of wells in accordance with MGL Chapter 21G Section 20." Section 5.8(2) states: "Any well now or hereafter abandoned or destroyed, including any well deemed to have been abandoned as defined in this regulation shall be brought into compliance with the requirements of this regulation any applicable rules or regulations with respect to abandonment of wells." Section 6.1 requires abandoned wells, test holes, or borings to be either "Sealed with non-hazardous, impervious materials ... with all exposed casing materials, pumping equipment, and distribution lines removed with the excavation returned to the existing grade" or "Sealed with a welded cap so as to prevent surface water or contaminants from entering the well." Section 6.3 adds: "Within 30 days after the destruction of any well, the well driller/digger shall submit to the Board a report" listing destruction details. | Definitions; Well Destruction §§6.1-6.4; Existing Wells §5.8(2) | 2025 | https://www.mendonma.gov/DocumentCenter/View/529/Private-Well-Regulations---Effective-09-24-2025
Massachusetts | Worcester | Northbridge | 2502746925 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) WELL – Well constructed for the purpose of transferring heat to or from the earth for heating and cooling purposes. GSHP wells may be Open-loop, closed-loop, or Direct Exchange." | § 201-10.B. Definitions | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Property Lines | 10 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of ... 10-feet from any property line." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Wastewater | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to, septic tanks/fields, lagoons..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Private Water | 50 | feet | "Closed loop and DX wells shall be sited at least 50-feet from any private potable water supply well... If a dual purpose well, then all Primary Potable water setbacks must be met." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Animal Enclosures | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to ... livestock pens..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Fuel (below ground) | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to ... oil ... storage tanks..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Water Bodies | 10 | feet | "Closed loop and DX wells shall be sited at least ... 10-feet from any surface water bodies." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Setback - Hazardous Materials/Fertilizers | 25 | feet | "Open-loop, Closed-loop and Direct Exchange (DX) GSHP Wells shall be set back a minimum of 25-feet from potential sources of contamination including but not limited to ... hazardous materials storage tanks..." | § 201-10.P. GSHP Wells – Setback Requirements | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Permit |  |  | "No well permit shall be issued for an Open Loop system without a DEP Underground Injection Control Registration Number. Closed Loop and Direct Exchange wells also require a UIC registration unless a Ground-Water discharge permit is required." | § 201-10.O. GSHP Wells UIC Registration | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Licensed Driller |  |  | "Pursuant to 313 CMR 3.00, Water Well Diggers and Drillers Registration Regulations, no person in the business of digging or drilling shall construct a well unless registered with the Department of Environmental Management -- Office of Water Resources." | § 201-10.C(1) Well construction | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Northbridge | 2502746925 | Certification |  |  | "REGISTERED WELL DRILLER -- Any person registered with the Department of Environmental Management/Office of Water Resources to dig or drill wells in the Commonwealth of Massachusetts." | § 201-10.B. Definitions | 2024 | https://www.northbridgemass.org/DocumentCenter/View/4845/Code-of-Regulations
Massachusetts | Worcester | Westborough | 2502775015 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat pump systems (GHPs), including Geo-Exchange, earth-coupled, ground-source, or water-source heat pumps, are deemed suitable for compliance." | (2) Sustainable Design, d. 6 Points: Geothermal heat pumps | 2024 | https://www.town.westborough.ma.us/DocumentCenter/View/4428
Massachusetts | Worcester | Westborough | 2502775015 | Permit |  |  | "Geothermal heat pump systems (GHPs), including Geo-Exchange, earth-coupled, ground-source, or water-source heat pumps, are deemed suitable for compliance." "Hybrid GHP systems, which integrate geothermal energy with other non-fossil fuel systems such as Air Source Heat Pumps, are permissible" under the sustainable design point system. | (2) Sustainable Design, d. 6 Points: Geothermal heat pumps | 2024 | https://www.town.westborough.ma.us/DocumentCenter/View/4428
Michigan | Allegan | Fennville | 2600527740 | Definition: Well |  |  | "WELL: As defined in the Michigan Water Well Construction and Pump Installation Code, Part 127, Act 368 of the public Acts of 1978, as amended, and rules; or a permanent or temporary opening in the surface of the earth for the purpose of removing water, or testing water quality, or measuring water characteristics, or measuring liquid recharge, or measuring liquid levels, or oil and gas exploration or production, or waste disposal, or dewatering purposes; or geothermal heat exchange purposes, or a cistern of a depth of 4 feet or more and with a top width of 12 inches or more." | 00.202 DEFINITIONS | 2025 | https://ecode360.com/FE6693/document/753167860.pdf
Michigan | Allegan | Fennville | 2600527740 | Permit |  |  | "General-purpose floor drains shall be connected to a public sewer system or an on-site holding tank (not a septic system) in accordance with state, county and municipal requirements (including Industrial Pretreatment criteria), unless a groundwater discharge permit has been obtained from the Michigan Department of Environmental Quality." | Sec. 00.206 CRITERIA FOR REVIEW | 2025 | https://ecode360.com/FE6693/document/753167860.pdf
Michigan |  | Holland | 2600538640 | Definition: Geothermal Heat Pump |  |  | "Geothermal heat pump system using a ground source heat exchanger for heating and cooling." | HOLLAND CIVIC CENTER PRELIMINARY ENERGY MODEL SUMMARY - Executive Summary | 2016 | https://ecode360.com/HO3221/document/295996980.pdf
Michigan | Allegan | Otsego | 2600561620 | Definition: Well |  |  | "Well means a permanent or temporary opening in the surface of the earth for the purpose of removing water, or testing water quality, or measuring water characteristics, or measuring liquid recharge, or measuring liquid levels, or oil and gas exploration or production, or waste disposal, or dewatering purposes; or geothermal heat exchange purposes, or a cistern of a depth of 4 feet or more and with a top width of 12 inches or more, or as defined in the Michigan Water Well Construction and Pump Installation Code..." | Sec. 59-4. Definitions | 2021 | https://www.cityofotsego.org/wp-content/uploads/2020/12/Groundwater-Protection-Ordinance-166.pdf
Michigan | Allegan | Otsego | 2600561620 | Inspection |  |  | The ordinance states the city will "establish legal authority of the city to carry out all inspection, surveillance and monitoring procedures necessary to ensure compliance with this chapter." | Sec. 59-1. Intent and Purpose | 2021 | https://www.cityofotsego.org/wp-content/uploads/2020/12/Groundwater-Protection-Ordinance-166.pdf
Michigan | Allegan | Plainwell | 2600564740 | Permit |  |  | "No person shall construct or install a geothermal heat pump system without first obtaining a permit from the city." "An application for a geothermal permit shall be made to the city on city approved forms." "Permits shall be issued to the owner or an agent thereof for the particular parcel of property on which the geothermal heat pump system is to be constructed and/or installs." | Sec. 39-3. GEOTHERMAL HEAT PUMP SYSTEM PERMIT REQUIRED. | 2014 | https://codelibrary.amlegal.com/codes/plainwellmi/latest/plainwell_mi/0-0-0-4687
Michigan | Allegan | Plainwell | 2600564740 | Open-loop Prohibitions |  |  | "No permit shall be issued for any open loop geothermal heat pump system per Section 39-8 below." "Open-loop systems existing prior to the date of the adoption of this chapter shall be allowed." | Sec. 39-3. GEOTHERMAL HEAT PUMP SYSTEM PERMIT REQUIRED. | 2014 | https://codelibrary.amlegal.com/codes/plainwellmi/latest/plainwell_mi/0-0-0-4687
Michigan | Gratiot | Alma | 2601540 | Permit |  |  | "No permit for the construction or alteration of a building or structure shall be issued or rezoning petition granted for any property on which a well in violation of this Section has been installed or is proposed to be installed." This applies to geothermal wells because Sec. 22-4 expressly addresses "Geothermal Wells: Professionally installed permanent closed loop wells used for heating/cooling residences and small businesses..." as an exception to the general well prohibition. | Sec.22-8. BUILDING AND ZONING PERMITS | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/10354/1067045/pdf
Michigan | Gratiot | Alma | 2601540 | Decommissioning |  |  | "Any well existing as of the effective date of this Section the use of which is prohibited by this Section shall be plugged and abandoned." Also, "Any well the use of which is permitted pursuant to Section 22-4 but which is or becomes nonfunctional shall be plugged and abandoned unless the property upon which such well is located is not served by a municipal potable water treatment and distribution system, in which case the well may be replaced or repaired..." For properties later served by municipal water, Sec. 22-4(5)(b) also states "the use of such well shall be discontinued, the well plugged and abandoned." | Sec. 22-5. ABANDONMENT OF PROHIBITED AND NONFUNCTIONAL WELLS | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/10354/1067045/pdf
Michigan | Gratiot | Alma | 2601540 | Open-loop Prohibitions |  |  | Sec. 22-3 states: "Except as provided in Section 22-4, no person shall use, install, allow, permit, or contract or provide for the installation or utilization of, a well within the City of Alma." The geothermal exception in Sec. 22-4 is limited to "Geothermal Wells: Professionally installed permanent closed loop wells used for heating/cooling residences and small businesses..." | Sec. 22-3. PROHIBITION; Sec. 22-4. EXCEPTIONS | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/10354/1067045/pdf
Michigan |  | Niles | 2602157760 | Other Prohibitions/Regulations |  |  | "The following uses and actions are prohibited within the Wellhead Protection Overlay District: ... 10. Installation or use of a geothermal well for heating and cooling systems." | Section 326 - Wellhead Protection Area, D. Prohibited Uses within the Wellhead Protection Overlay District | 2025 | https://cms3.revize.com/revize/nilesmi/FINAL%20City%20of%20Niles%20Zoning%20Ordinance%20[EFFECTIVE%208-17-25].pdf
Michigan | Branch | Bronson | 2602310860 | Permit |  |  | § 51.14(C)(3)(b): "Any proposed new well installation must be reviewed and approved by EGLE Superfund (or its successor) staff with notice to U.S. EPA prior to well placement, drilling, and construction." § 51.14(C)(5): "a person shall not install a new non-contact well within a restricted or buffer zone unless the requirements in division (C)(3)(b) above are met" and EGLE recommends in writing that use of the non-contact well will not cause specified contamination or vapor-intrusion impacts, the requester submits EGLE's written recommendation to the city, and "the city... may execute a waiver allowing installation and use of the non-contact well upon such terms and conditions that EGLE may identify or require." | § 51.14(C)(3)(b) Certain industrial use wells; § 51.14(C)(5) New, specific non-contact wells | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Branch | Bronson | 2602310860 | Inspection |  |  | For waiver conditions on existing and new non-contact wells, the ordinance states: "Such terms and conditions may include, but are not limited to, hydrogeological evaluations including pump tests"; for new wells, conditions may also include "groundwater modeling." | § 51.14(C)(4)(c); § 51.14(C)(5)(c) | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Branch | Bronson | 2602310860 | Decommissioning |  |  | § 51.14(C)(3)(b)1: "If the glacial till aquitard unit is not encountered during drilling, then the well is not to be constructed and the borehole must be properly abandoned." § 51.14(C)(3)(b)2: "If the glacial till aquitard unit is less than the ten feet minimum thickness found to be acceptable by EGLE, then the well is not to be constructed and the borehole must be properly abandoned to prevent any cross-contamination between the shallow and lower aquifers." § 51.14(E)(3)(f) also requires a description and schedule for actions "to properly plug per Well Construction Code any existing wells subject to the use prohibition within the proposed restricted or buffer zones." | § 51.14(C)(3)(b)1.-2.; § 51.14(E)(3)(f) | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan | Branch | Bronson | 2602310860 | Other Prohibitions/Regulations |  |  | § 51.14(B)(1): "no person or legal entity shall install or use or allow, permit, or otherwise provide for the installation or use of a well on any property within the restricted zone... Property within the restricted zone shall be serviced only by public water supply." § 51.14(B)(2): within the buffer zone, "no person or legal entity shall install or use... a well... which well draws its water from the shallow aquifer." Also, "The installation and use of water supply wells located within the buffer zone that draw all their water from the lower aquifer are prohibited." For heat-pump-related use specifically, § 51.14(C)(3)(a) states: "any existing well within the restricted or buffer zone shall not be used to produce industrial cooling or process water, or to service heat pumps unless it meets the requirements of division (C)(4) below." | § 51.14(B) Prohibitions; § 51.14(C)(3)(a) Certain industrial use wells | 2020 | https://codelibrary.amlegal.com/codes/bronson/latest/bronson_mi/0-0-0-12711
Michigan |  | Grand Ledge | 2603733420 | Permit |  |  | "before construction of a building or structure, the owner... shall submit an application in writing to the appropriate enforcing agency for a building permit"; "The requirements of the code may provide for issuance of construction permits for certain of the systems of a structure"; and "the construction or alteration of a building or structure shall not be commenced until a building permit has been issued." | 125.1510 Sec. 10(1), (6); 125.1511 Sec. 11(1) | 2014 | https://www.cityofgrandledge.com/DocumentCenter/View/454/State-Construction-Code-Act-PDF
Michigan |  | Grand Ledge | 2603733420 | Inspection |  |  | "An enforcing agency shall periodically inspect all construction undertaken pursuant to a building permit issued by it" and inspectors "may enter and inspect the premises and construction thereon" to ensure compliance. The enforcing agency must also give "at least 12 hours' notice of the time of any final inspection... of the work covered by the building permit" pursuant to the certificate of use and occupancy application. | 125.1512 Sec. 12(1)-(2); 125.1513 Sec. 13 | 2014 | https://www.cityofgrandledge.com/DocumentCenter/View/454/State-Construction-Code-Act-PDF
Michigan | Eaton | Delta | 2604521520 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy Systems: A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." | Definitions | 2019 | https://www.deltami.gov/defaults/Government/Ordinances/Delta%20Township%20Zoning%20Ordinance-4-19-21.pdf
Michigan | Genesee | Swartz Creek | 2604977700 | Definition: Well |  |  | "Well means an opening in the surface of the earth for the purpose of removing fresh water through non-mechanical or mechanical means for any purpose other than a public emergency or conducting response actions that are consistent with" specified environmental statutes. | Definitions - K | 2018 | https://cityofswartzcreekmi.gov/images/2018-02-12-Council-Packet.pdf
Michigan | Genesee | Swartz Creek | 2604977700 | Permit |  |  | Section 9(G): "Upon review and approval by the MDEQ, geothermal Wells may be used if no impact by plume or influence on plume will occur with use of Well; or an unauthorized discharge may occur." Section 11 adds: "No influential Well may be used or installed without approval by the MDEQ." | SECTION 9. EXCEPTIONS; SECTION 11. INFLUENTIAL WELLS | 2018 | https://cityofswartzcreekmi.gov/images/2018-02-12-Council-Packet.pdf
Michigan | Genesee | Swartz Creek | 2604977700 | Decommissioning |  |  | "Any existing Well, the use of which is prohibited by this Ordinance, shall be plugged or abandoned in conformance with all applicable laws, rules, regulations, permit and license requirements... or... in conformance with the protocol developed consistent with the American Standards for Testing and Materials Standard No. D5299-92. Any non-conforming well shall be plugged within 30 days following establishment of the restricted zone." Section 6(C) also requires "abandonment and plugging" of wells on affected premises. | SECTION 8. NON-CONFORMING WELLS | 2018 | https://cityofswartzcreekmi.gov/images/2018-02-12-Council-Packet.pdf
Michigan |  | Traverse City | 2605580340 | Permit |  |  | "No person shall install a private well, without first obtaining a permit from the City Director of Public Services." | Section 1044.14(b) - Prohibitions; permits | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/15455/883088/pdf
Michigan |  | Traverse City | 2605580340 | Decommissioning |  |  | "A well meeting the above criteria may be used temporarily for water until the City water service is available within 200 feet of the property, at which time the well shall be properly capped and abandoned... The cost of proper abandonment of a well that was temporarily allowed under this section... shall be the owner's responsibility." | Section 1044.14(c) - Temporary use | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/15455/883088/pdf
Michigan |  | Traverse City | 2605580340 | Open-loop Prohibitions |  |  | "A private well for an open loop geothermal system shall be prohibited." | Section 1044.14(b) - Prohibitions; permits | 2018 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/15455/883088/pdf
Michigan |  | Barton Hills | 2605660 | Definition: Geothermal |  |  | "Geothermal System: A geothermal system pumps liquid from the ground to equipment which heats and cools buildings." | 2:41 - Definitions | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan |  | Barton Hills | 2605660 | Permit |  |  | "A person may install and operate a closed loop geothermal system only in accordance with the requirements of this section. 1. Prior to the start of construction, a permit must be approved by the County of Washtenaw. 2. Prior to the start of construction, a permit must be approved by the Village Board of Trustees upon a finding that the system complies with this section." | 2:43 - Closed Loop Geothermal System Permitted | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan |  | Barton Hills | 2605660 | Inspection |  |  | "The systems shall be tested hydrostatically at one and one half times the maximum system design pressure. The duration of each test shall be not less than 15 minutes. All geothermal systems must be pressure checked to the original standard by a licensed geothermal contractor, every three years from the certification system date. Results from the test shall be submitted to the Board of Trustees. No person shall operate a system if a test reveals that it is likely to leak the heat transfer liquid." | 2:43 - Closed Loop Geothermal System Permitted | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan |  | Barton Hills | 2605660 | Open-loop Prohibitions |  |  | "No person shall install or maintain an open loop geothermal system in the Village." | 2:42 Open Loop Geothermal System Prohibited | 2024 | https://bartonhillsvillage.org/wp-content/uploads/2024/07/Village-Code-2024.pdf
Michigan | Gratiot | Arcada | 2605703260 | Permit |  |  | 'ZONING PERMIT REQUIRED' appears in Article 18 of the Arcada Township Zoning Ordinance, and Section 18.2 establishes that a zoning permit is required under the ordinance. The ordinance also defines 'ZONING PERMIT' as '[t]he written permit issued by the Zoning Administrator indicating that a proposed structure or use of land is in compliance with the requirements of this Ordinance.' | SECTION 18.2 ZONING PERMIT REQUIRED | 2021 | https://arcadami.gov/wp-content/uploads/2024/01/2021.08.11-Arcada-Ordinance-final.pdf
Michigan | Ionia | Danby | 2606719720 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM - A system that uses a heat pump to extract heat from the earth in a heating mode and/or reject heat into the earth in a cooling mode." | Section 2.08 Definitions - G | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | 2606719720 | Setback - Property Lines | 10 | feet | "All above-ground equipment shall be a minimum of 10 feet from a side and rear lot line." | Section 3.25 D.1 | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | 2606719720 | Permit |  |  | "Closed-loop geothermal energy systems shall only be approved when an applicant demonstrates compliance with this section, and construction shall only commence after approval by the Zoning Administrator and after the issuance of a mechanical permit by the Ionia County Building Official." | Section 3.25 D. Closed-Loop Geothermal Energy System | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | 2606719720 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems are prohibited in Danby Township." | Section 3.25 C. Open-Loop Geothermal Energy Systems | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Danby | 2606719720 | Other Prohibitions/Regulations |  |  | "All components of a closed-loop geothermal energy system, including associated equipment, shall be located outside of easements, unless allowable per the easement restriction, and shall be outside of all public rights-of-way." | Section 3.25 D.2 | 2023 | https://www.danbytownship.org/_files/ugd/88ee28_c11c52c2fb8145a4ac03e20f06b61e6e.pdf
Michigan | Ionia | Ionia | 2606740860 | Definition: Geothermal Heat Pump |  |  | "It is recognized that residential buildings in the City may be constructed, or be retrofitted with geothermal heat pumps. It is recognized that these climate control systems use substantial amounts of water. It is also recognized that this water, which for the purposes of this chapter shall be identified as sending water..." | 1040.19 GEOTHERMAL HEAT SYSTEMS | 2025 | https://codelibrary.amlegal.com/codes/ionia/latest/ionia_mi/0-0-0-33038
Michigan | Ionia | Ionia | 2606740860 | Open-loop Prohibitions |  |  | "Owners of buildings in the City equipped with geothermal heat pump systems must install a closed loop system that will continuously process (heated or cooled) sending water and circulate it through the enclosed or sealed heat pump system, with no discharge of returning water out of the heat pump." Also, "No sending water from a geothermal heat pump system shall be directly or indirectly discharged out of the closed loop system." | 1040.19(b)-(c) GEOTHERMAL HEAT SYSTEMS | 2025 | https://codelibrary.amlegal.com/codes/ionia/latest/ionia_mi/0-0-0-33038
Michigan | Isabella | Mount Pleasant | 2607356020 | Definition: Well |  |  | "WELL. Any excavation that is drilled, cored, driven, dug, bored, augured, jetted, washed, or otherwise constructed for the purpose of exploring for groundwater, monitoring groundwater, utilizing the geothermal properties of the ground, or extracting water from or injecting water into an aquifer. WELL does not include... lateral geothermal heat exchange systems less than 20 feet deep..." Also: "GEOTHERMAL BOREHOLE. A hole drilled or bored into the earth into which piping is inserted for use in a geothermal system." | § 52.51(B) Definitions | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A system for heating and/or cooling buildings using the earth's thermal properties in conjunction with electricity." Also defined are system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A geothermal system that consists of the following basic elements: underground loops of piping; heat transfer fluid; a heat pump, and an air distribution system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A geothermal system in which a borehole extends beneath the surface..."; and "OPEN LOOP GEOTHERMAL SYSTEM. A geothermal system in which groundwater is pumped from a well into a heat exchanger located in a surface building..." | § 52.51(B) Definitions | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Maximum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM... A horizontal closed loop geothermal system shall be no more than 20 feet deep." | § 52.51(B) Definitions | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Permit |  |  | "No person shall: (a) Construct or install a geothermal system; (b) Dig, bore, drill, replace, modify, repair, or destroy a well that is, is intended to be, or was part of a geothermal system; or (c) Make any other excavation that may intersect groundwater without first obtaining a permit from the city and, for construction of a well, the Central Michigan Health Department." "A permit is required for any closed loop horizontal and closed loop vertical geothermal system." "All wells must be permitted by the Central Michigan District Health Department..." | § 52.51(C) Permit required; § 52.51(E) Well permits; § 52.51(G) Permit fee | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Inspection |  |  | "Pipes for geothermal system permitted under this section shall be tested hydrostatically at one and one-half times the maximum system design pressure, but not less than 100 psi (689 kPa), for a duration of not less than 15 minutes. All geothermal systems must be pressure checked by a licensed geothermal system contractor every five years from the date of its initial successful test. Results shall be filed with the City Engineer. If the test results show the system fails to meet these requirements, system shutdown and repairs shall be made at the direction of the City Engineer." | § 52.51(J) System testing | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Licensed Driller |  |  | "Boreholes shall be drilled by Michigan registered/licensed water well drillers." | § 52.51(F)(2) Permit requirements | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Certification |  |  | "Boreholes shall be drilled by Michigan registered/licensed water well drillers." "Borehole piping shall be high density polyethylene as specified in International Ground Source Heat Pump Association standards for closed loop heat pumps." | § 52.51(F)(2); § 52.51(F)(4) | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Decommissioning |  |  | "When a permit is revoked, the property owner shall immediately abandon the geothermal system as required by this section." "Abandonment of a geothermal system shall comply with the laws, rules and regulations applicable to abandonment of water supply wells. Heat transfer fluid must be removed by displacement with grout. The top of the borehole must be uncovered and capped with grout." | § 52.51(H)(4); § 52.51(K) | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Isabella | Mount Pleasant | 2607356020 | Open-loop Prohibitions |  |  | "No permit shall be issued for any open loop geothermal system because such systems are prohibited by division (I) below." "Permits may be issued only for closed loop geothermal systems." "Open loop geothermal systems are prohibited." | § 52.51(C)(2); § 52.51(F)(1); § 52.51(I) | 2024 | https://codelibrary.amlegal.com/codes/mtpleasant/latest/mtpleasant_mi_code/0-0-0-5989
Michigan | Jackson | Norvell | 2607559180 | Permit |  |  | "Permits: PRES are permitted in all zoning districts if they are designed to meet all the required regulations and with approval of a zoning permit under Article 16." | Section 8.2(A)(1) | 2026 | https://norvelltwp-mi.gov/wp-content/uploads/2026/03/Zoning-Ordinance-Final-With-Jan-20-2026-Amendment.pdf
Michigan | Jackson | Norvell | 2607559180 | Decommissioning |  |  | "Abandonment: If abandoned, the system must be removed within one (1) year." | Section 8.2(A)(7) | 2026 | https://norvelltwp-mi.gov/wp-content/uploads/2026/03/Zoning-Ordinance-Final-With-Jan-20-2026-Amendment.pdf
Michigan | Jackson | Waterloo | 2607584300 | Definition: Well |  |  | "Well’ means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose. Wells as defined in this section include: ... f. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 501.6 Well | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Jackson | Waterloo | 2607584300 | Permit |  |  | "No person shall begin construction of a new water supply, or make extensive changes to existing water supplies, without first obtaining a water supply construction permit from the Jackson County Health Department." Because Section 501.6 defines a well to include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning," this permit requirement expressly reaches geothermal heat exchange wells as a type of well/water supply. | Section 507 Water Supply Construction Permit Required | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Jackson | Waterloo | 2607584300 | Inspection |  |  | "The Health Officer shall make inspections of water supplies during and/or after completion of construction as deemed necessary. It shall be the responsibility of the well driller to notify the Health Officer of the dates and times the well will be ready for the required inspections. Well drillers may be required to notify the Health Officer of the dates and times the well will be under construction." Under Section 501.6, wells include "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | Section 512 Inspection | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Jackson | Waterloo | 2607584300 | Decommissioning |  |  | "The Health Officer may require the abandonment of a well that is constructed without a permit or is constructed in violation of this code or permit requirements." In addition, "Any abandoned well shall be properly filled and sealed to prevent it from becoming a hazard or serving as a channel for possible contamination of groundwater or the escape of subterranean gases. Procedures to be followed in properly filling and sealing an abandoned water well shall be approved by the Health Officer..." Section 501.6 includes "a heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning" within the definition of well. | Section 516 Well Abandonment | 1995 | https://waterlootwpmi.gov/~waterloo/wp-content/uploads/2022/06/Jackson-County-Sanitary-Code.pdf
Michigan | Kent | Cedar Springs | 2608114200 | Decommissioning |  |  | "Well abandonment. When a well is plugged, formal well abandonment logs must be completed and provided to the city's department of public works, except in cases where wells were abandoned in the past and no well abandonment logs are available." Also, Sec. 14-403(7) states: "Allow the presence of an abandoned well ..." is prohibited, and "A well shall not be considered abandoned if it has been properly closed pursuant to state law." | Sec. 14-404. Requirements and restrictions within the wellhead protection zone. | 2021 | https://cityofcedarsprings.org/wp-content/uploads/2021/11/Cedar-Springs-Code-with-STUL.pdf
Michigan | Kent | Cedar Springs | 2608114200 | Other Prohibitions/Regulations |  |  | "Within the WHPZ, no person shall, nor cause or allow another over whom that person has control, to: ... (8) Install or use a geothermal well for heating and cooling systems." | Sec. 14-403. Prohibited activities within the wellhead protection zone. | 2021 | https://cityofcedarsprings.org/wp-content/uploads/2021/11/Cedar-Springs-Code-with-STUL.pdf
Michigan | Kent | Plainfield | 2608164660 | Other Prohibitions/Regulations |  |  | "The following uses and actions are prohibited within the Wellhead Protection Overlay district... K. Installation or use of a geothermal well for heating and cooling systems." | SECTION 27.03 - SPECIFICALLY PROHIBITED USES AND ACTIONS | 2006 | https://www.plainfieldmi.org/DocumentCenter/View/339/Zoning-Ordinance---May-18-2025-PDF
Michigan | Lapeer | Arcadia | 2608703280 | Definition: Geothermal Heat Pump |  |  | "It is recognized that certain residential structures in the Township are being equipped with geothermal heat pumps. It is further recognized that geothermal heat pumps use water which, if not properly drained, can cause excess wetness or flooding on nearby properties, resulting in undesirable conditions." | Section 1. GEOTHERMAL HEAT PUMPS |  | https://www.arcadiatownship.org/images/Ordinances/ArcadiaTwp-Ord-2200-Geothermal-Drainage.pdf
Michigan | Lapeer | Arcadia | 2608703280 | Other Prohibitions/Regulations |  |  | Section 2 requires owners with geothermal heat pumps to do one of the following: "1 Install a drain system that will contain the water on the owner’s property so as to prevent the drainage of water onto other parcels of land. 2, Install a drain system that will direct any excess water into a lake, stream, spring fed pond, or a public drain under the jurisdiction of the Lapeer County Drain Commissioner. 3. Install a closed loop system that recirculates geothermal heat pump water rather than discharge the water." Section 3 adds: "No drainage from geothermal heat pumps shall be directly or indirectly onto any road right-of-way or road ditch." | Section 2. DRAINAGE; Section 3. ROAD RIGHT-OF-WAY |  | https://www.arcadiatownship.org/images/Ordinances/ArcadiaTwp-Ord-2200-Geothermal-Drainage.pdf
Michigan | Macomb | Eastpointe | 2609924290 | Setback - Property Lines | 5 | feet | 'Accessory uses and structures such as ... heat pumps, and other mechanical equipment ... must be set back a minimum of five feet from the property line.' | Section 7.01(A)(2) Accessory Buildings | 2026 | https://www.eastpointemi.gov/EastpointeZoningOrdinance_Amended%20Through%20March%2016%202026.pdf
Michigan | Muskegon | Montague | 2612155100 | Definition: Well |  |  | "Well means an opening in the surface of the earth for the purpose of removing fresh water through non-mechanical or mechanical means for any purpose other than a public emergency or conducting response actions..." | Sec. 82-142. Definitions. | 2020 | https://cityofmontague.org/wp-content/uploads/2019/12/Chapter_82_UTILITIES_20191216.pdf
Michigan | Muskegon | Montague | 2612155100 | Decommissioning |  |  | "Any existing well at the time of the enactment of a restricted zone on any affected parcel within that restricted zone shall be plugged/abandoned... in accordance with applicable laws, regulations and ordinances" unless an exception applies. Sec. 82-148 adds that the owner "shall immediately take steps" to comply for domestic use water within 365 days from notice and that "Any existing well in violation of this division shall then be plugged or abandoned in conformance with applicable legal requirements." Sec. 82-149 states "any well in violation of this division shall be immediately taken out of service and lawfully abandoned in compliance with applicable legal requirements." | Sec. 82-145. Prohibition.; Sec. 82-148. Enforcement.; Sec. 82-149. Penalty. | 2020 | https://cityofmontague.org/wp-content/uploads/2019/12/Chapter_82_UTILITIES_20191216.pdf
Michigan | Muskegon | Montague | 2612155100 | Other Prohibitions/Regulations |  |  | "Except as provided in section 82-146 no person shall install or utilize, or allow, permit, or provide for the installation or utilization of a well on any affected parcel; or use any groundwater from an affected parcel." This applies within the restricted zone established by Sec. 82-143. | Sec. 82-145. Prohibition. | 2020 | https://cityofmontague.org/wp-content/uploads/2019/12/Chapter_82_UTILITIES_20191216.pdf
Michigan | Oakland | Farmington | 2612527380 | Permit |  |  | "Any owner or owner's authorized agent who intends to ... erect, install, enlarge, alter, repair, remove, convert or replace any ... mechanical ... system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." The mechanical residential fee table also specifically lists geothermal entries: "Geothermal: Plans Required"; "Heat Pump $50.00"; "Plan Review if Required Minimum $50.00". | SECTION 8 - MECHANICAL FEES | 2019 | https://www.farmgov.com/media/1uipszhv/1072019-_191007.pdf
Michigan | Oakland | Farmington | 2612527380 | Inspection |  |  | The mechanical residential fee table expressly includes geothermal inspection/test items: "Geothermal: Plans Required"; "Manifold Test - Underground $75.00"; and a general mechanical "Observable / Re-Inspection $50.00." | SECTION 8 - MECHANICAL FEES | 2019 | https://www.farmgov.com/media/1uipszhv/1072019-_191007.pdf
Michigan | Oakland | Ferndale | 2612527880 | Definition: Geothermal |  |  | "Geothermal Energy. A closed loop system that uses buried high-density polyethylene (HDPE) plastic piping installed in drilled and grouted boreholes that conductively exchanges thermal (heat) energy with the ground via circulating water or a water/antifreeze mixture through the piping system." | Article 20. Glossary – Definitions G-H | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Oakland | Ferndale | 2612527880 | Setback - Property Lines | 10 | feet | For "Ground-Source Heat Pump Systems (either vertical or horizontal loops)," the code states: "Allowed in all yards, however, the setback for private system ground loops must be a minimum of 10-feet from all lot lines." It also states: "The setback for groundloops within a networked system that are adjacent to a co-participating lot (that is also served by the networked GSHP system) can be setback a maximum of 5-feet." | Section 3.04 Accessory Structures: Distributed Energy Systems | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Oakland | Ferndale | 2612527880 | Permit |  |  | In the 'Distributed Energy Resource (DER) Uses' table under 'Heat Pump Systems (HPS),' "Ground-Source (Single Lot)" is listed as "S" in R-1 and R-2, while "Networked Ground-Source" is listed as "P" in all districts and "Ground-Source (Single Lot)" is "-" in CBD. | Section 2.05 Schedule of Permitted Uses | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Oakland | Ferndale | 2612527880 | Other Prohibitions/Regulations |  |  | In the 'Distributed Energy Resource (DER) Uses' table under 'Heat Pump Systems (HPS),' "Ground-Source (Single Lot)" is marked "-" in the CBD district, and the code states in Section 1.04(B): "Any use not expressly permitted within the Schedule of Permitted Uses is prohibited." | Section 2.05 Schedule of Permitted Uses | 2025 | https://www.ferndalemi.gov/PDFs/Zoning%20Code%2006232025.pdf
Michigan | Roscommon | Gerrish | 2614331960 | Definition: Well |  |  | "A 'Well' means an opening in the surface of the earth for the purpose of obtaining ground water, monitoring the quality or quantity of ground water, obtaining geologic information on aquifers, recharging aquifers, purging aquifers, utilizing the geothermal properties of earth formations, or removing ground water for any purpose." The definition further states: "Wells as defined in this section include: ... F. A heat exchange well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | ARTICLE II - DEFINITIONS, 37. WELL | 2018 | https://gerrishtownship.org/wp-content/uploads/2025/04/CMHD-Sanitary-Code-Eff-1-5-2018-GTPC.pdf
Michigan | Roscommon | Roscommon | 2614369560 | Permit |  |  | "Any building moved into Roscommon Township shall conform to this Ordinance and require a Land Use Permit from the Zoning Administrator." | SECTION 1.4 REGULATED STRUCTURES AND USES | 2025 | https://roscommontownshipmi.gov/wp-content/uploads/2025/09/Zoning-Ordinance-86-Rev-July-2025.pdf
Michigan | Saginaw | Buena Vista | 2614511560 | Noise Limits | 50 | dBA | 'Sound emitted by any source is considered a noise disturbance when its average A-weighted sound level exceeds the limit set forth for the receiving zoning district... Residential Districts 7:00 a.m. to 10:00 p.m. 55 dB(A); 10:00 p.m. to 7:00 a.m. 50 dB(A). Non-Residential Districts 7:00 a.m. to 6:00 p.m. 62 dB(A); 6:00 p.m. to 7:00 a.m. 55 dB(A).' | Section 509(C)(3) | 2026 | https://www.bvct.org/2300112%20-%20Adopted%20Zoning%20Ordinance%20Bueva%20Vista%20Township%20Eff%203-25-26.pdf?t=202604070758250
Michigan | St. Clair | East China | 2614723820 | Setback - Yards | 3 | feet | "A central air-conditioning condenser unit, heat pump, or any other noise-producing mechanical system components which are typically required to be located on the exterior of the house shall be located within three feet of the main building within the rear yard, and clear of side yard setbacks." | § 480-61(P)(1) Heating and/or cooling units located outside of single-family homes | 2023 | https://ecode360.com/9688304
Michigan | St. Clair | East China | 2614723820 | Setback - Building Foundation | 3 | feet | "A central air-conditioning condenser unit, heat pump, or any other noise-producing mechanical system components which are typically required to be located on the exterior of the house shall be located within three feet of the main building within the rear yard, and clear of side yard setbacks." | § 480-61(P)(1) Heating and/or cooling units located outside of single-family homes | 2023 | https://ecode360.com/9688304
Michigan | St. Clair | East China | 2614723820 | Permit |  |  | "Administrative review and approval of a plot plan by the Building Official ... is required before a building permit may be issued for ... (b) Accessory structures and uses in any zoning district." | § 480-72(A)(1)(b) Site plan review | 2023 | https://ecode360.com/9688304
Michigan | Washtenaw | Pittsfield | 2616164560 | Permit |  |  | The ordinance states generally that a person who intends "to erect, install, enlarge, alter, repair, remove, convert, or replace any ... mechanical ... system, the installation of which is regulated by this code ... shall first make application to the building official and obtain the required permit." It then creates a geothermal-specific exemption under mechanical permits: "Mechanical permits shall not be required for any of the following: ... When installing geothermal vertical closed loops under the supervision of a mechanical contractor licensed in HVAC as long as the company meets both of the following: - Has obtained a certificate of registration as a well drilling contractor - Has installed the geothermal vertical closed loops in accordance with the department of environmental quality's best practices regarding geothermal heat pump closed loops." | Required Permits / Work Exempt from Permits |  | https://www.pittsfield-mi.gov/152/Required-Permits
Michigan | Washtenaw | Pittsfield | 2616164560 | Certification |  |  | For the geothermal mechanical-permit exemption, the company must have "obtained a certificate of registration as a well drilling contractor" and must install the loops "under the supervision of a mechanical contractor licensed in HVAC." | Work Exempt from Permits |  | https://www.pittsfield-mi.gov/152/Required-Permits
Michigan | Wayne | Wyandotte | 2616388900 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. All the pipes, valves, headers, and other equipment and material, required for the purpose of constructing a vertical heat exchanger (VHE), or ground source heat pump loop system, installed in the city right-of- way for the purpose of providing a renewable source of energy for heating and cooling systems in residential, commercial and industrial buildings." Also: "PRIVATE GEOTHERMAL SYSTEM. All the pipes, valves, headers and other equipment and material, required for the purpose of constructing a vertical heat exchanger (VHE), or ground source heat pump loop system, installed on private property for the purpose of providing a renewable source of energy for heating and cooling systems in residential, commercial and industrial buildings." | § 180.002 DEFINITIONS. | 2010 | https://codelibrary.amlegal.com/codes/wyandotte/latest/wyandotte_mi/0-0-0-11451
Michigan | Wayne | Wyandotte | 2616388900 | Permit |  |  | "A plumbing permit shall be required prior to the installation, alteration or modification of vertical heat exchangers and ground source heat pump loop systems." "(A) The permit shall be secured from the City Engineer." "(B) No alterations or additions shall be made to an existing vertical heat exchanger or ground source heat pump loop system after installation and inspection without first notifying the City Engineer and securing a permit thereof." "(C) Division (A) above shall not apply to repair work of valves and fittings." | § 180.020 PERMIT REQUIRED. | 2010 | https://codelibrary.amlegal.com/codes/wyandotte/latest/wyandotte_mi/0-0-0-11451
Michigan | Van Buren | Decatur | 2621040 | Permit |  |  | "Before any connection is made to any water main, application for a permit must be made in writing by the owner of the premises to be served, or by his, her or their authorized representative at the office of the Village Clerk." This applies to geothermal-related premises only where Section 3.1(e) allows a private well to be maintained on premises connected to the System if "the premises maintains a closed geothermal heating system and the private well is an integral part of said system." | Section 3.2(a) Permit Application | 2020 | https://cms5.revize.com/revize/decatur/Document_Center/Forms/Ordinances/Ordinance-2020-001-Water-System.pdf
Michigan | Kalkaska | Kalkaska | 2642260 | Definition: Well |  |  | "'Well' means any opening in the surface of the earth for the purpose of removing fresh water or a test well, recharge well, waste disposal well, or a well-used temporarily for dewatering purposes during construction... and also including all of the following: ... (3) 'Heat Exchange Well' means a well for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | §51.66(2)(e) Definitions | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | 2642260 | Permit |  |  | "No permit for construction or alteration of a building or structure, nor any permit for any zoning approval, shall be issued for any improvement on an affected parcel which has, or proposes, a water supply from a well in violation of this Ordinance." | §51.66(10) Building and Zoning Permits | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | 2642260 | Inspection |  |  | "The Village Manager or other authorized Village representative may enter the lands upon which any well subject to this Ordinance is situated or proposed, for the purposes of inspecting those lands and well and for maintaining compliance with the provisions of this Ordinance." | §51.66(11) Enforcement | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | 2642260 | Decommissioning |  |  | §51.66(6): "Any existing well at the time of the enactment of a restricted zone on any affected parcel within that restricted zone shall be plugged at the expense of the applicant for that particular restricted zone... unless such existing well falls within one of the exceptions listed in Section 7." §51.66(8): "Any existing well, the use of which is prohibited by Section 6 or is otherwise an abandoned water well, shall be plugged in conformance with all applicable laws, rules, regulations, permit and license requirements, orders and directives of any governmental entity or agency of competent jurisdiction." | §51.66(6) Wells and Groundwater Use Prohibition; §51.66(8) Plugging of Non-Conforming Wells | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Michigan | Kalkaska | Kalkaska | 2642260 | Closed-loop Prohibitions |  |  | "Heat Exchange Well - Vertical Closed Loop Geothermal. The Village of Kalkaska shall not allow the use of a vertical closed loop geothermal well within a restricted zone unless an exception to the restrictions is granted." | §51.66(7)(6) Exceptions to Prohibition of Well Use | 2016 | https://kalkaskavillage.com/clientdata/pages/files/Title%20V%20Public%20Works.pdf
Minnesota | Anoka | Andover | 2700301486 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEM: An energy transfer of generating system such as ground source heat pump, wind or solar energy system." | 9-14-2: DEFINITIONS | 2024 | https://www.andovermn.gov/DocumentCenter/View/256/Title-9---Building-Regulations-PDF-
Minnesota | Anoka | Andover | 2700301486 | Permit |  |  | "Water-fed Heat Extractors and Air Conditioning Equipment may be installed only in accordance with the city, county, state and federal law." | 9-2-1: WATER-FED HEAT EXTRACTORS AND AIR CONDITIONING EQUIPMENT | 2024 | https://www.andovermn.gov/DocumentCenter/View/256/Title-9---Building-Regulations-PDF-
Minnesota | Anoka | Nowthen | 2700347536 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." The ordinance also defines related GHP types: "Closed loop ground source heat pump system: A system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." "Open loop ground source heat pump system: A system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." "Horizontal ground source heat pump system: A closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." "Vertical ground source heat pump system: A closed loop ground source heat pump system where the loops or coils are installed vertically in one or more borings below the land surface." | 11-2-2: TERMS | 2025 | https://www.cityofnowthen.gov/media/196
Minnesota |  | Royalton | 2700956176 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system means a system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." Also: "Closed loop ground source heat pump system means a system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface." "Open loop ground source heat pump system means a system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | 18.03 - Definitions | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least eight feet from interior side lot lines and at least ten feet from rear lot lines." | 18.04(b)(2) - Setbacks | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Setback - Yards | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least eight feet from interior side lot lines and at least ten feet from rear lot lines." Also, "Above-ground equipment associated with ground source heat pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable zoning district." | 18.04(b)(2) - Setbacks | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Maximum Well Depth | 20 | feet | "Horizontal ground source heat pump system means a closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." | 18.03 - Definitions | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Permit |  |  | "A building permit and interim conditional use permit, if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." | 18.04(e) - Permits | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of Ordinance 47 Sec. 9." | 18.04(b)(5) - Screening | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code and the Minnesota Department of Health." | 18.04(c) - Safety | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... (1) The heat pump and any external mechanical equipment shall be removed. (2) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted. (3) Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 18.04(d) - Abandonment | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in section 18.03 are permitted. Open loop ground source heat pump systems are not permitted." | 18.04(b)(1) - System requirements | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Royalton | 2700956176 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the City of Royalton are not permitted." | 18.04(b)(1) - System requirements | 2013 | https://cityofroyaltonmn.gov/vertical/sites/%7BF29AE369-80CF-4CFB-BE87-851B6F04B18E%7D/uploads/Zoning_Ordiance.pdf
Minnesota |  | Sartell | 2700958612 | Permit |  |  | "Geothermal system. 1. Permitted accessory use in all zoning districts on the condition it meets the requirements of this Section and other provisions of the Code." | 10-8-17: GEOTHERMAL, SOLAR, AND WIND ENERGY CONVERSION SYSTEMS; A. Geothermal system. |  | https://cms5.revize.com/revize/sartell/TITLE%2010%20ZONING%20REGULATIONS%20RV%202024.pdf
Minnesota | Carver | Hamburg | 2701926666 | Permit |  |  | The ordinance allows geothermal only as an accessory use in listed districts: "Solar collection and geo-thermal heating and cooling systems used in conjunction with permitted uses" are permitted accessory uses in the A-1, R-1, R-2, B, and I districts. It also states: "Uses not specifically identified in this ordinance as a permitted use, a conditional use, an interim use or accessory use shall be prohibited." Separately, "It shall be unlawful to use any structure or land for any purpose requiring a conditional use permit in the zoning district in which the property is located without first obtaining a conditional use permit from the city." | SECTION C. ADMINISTRATION AND ENFORCEMENT, Subdivision 6. Conditional Use Permit; SECTION D. GENERAL PROVISIONS, Subdivision 1; SECTION E, Subdivisions 3-7 | 2009 | http://www.cityofhamburgmn.com/Forms/Ordinance%20Number%20133%20(Zoning).pdf
Minnesota | Carver | Hamburg | 2701926666 | Other Prohibitions/Regulations |  |  | "Uses not specifically identified in this ordinance as a permitted use, a conditional use, an interim use or accessory use shall be prohibited." Geothermal is expressly listed only as an accessory use: "Solar collection and geo-thermal heating and cooling systems used in conjunction with permitted uses." | SECTION D. GENERAL PROVISIONS, Subdivision 1. Uses Not Provided for Within a Zoning District | 2009 | http://www.cityofhamburgmn.com/Forms/Ordinance%20Number%20133%20(Zoning).pdf
Minnesota | Carver | Mayer | 2701941138 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | Section 152.003 - Definitions | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM (GSHPS). A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site." | Section 152.003 - Definitions | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Setback - Property Lines | 10 | feet | "All components of Ground Source Heat Pump Systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | Section 152.102(B)(3) - Location | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Setback - Yards | 10 | feet | "Ground Source Heat Pump Systems shall only be located in the rear yard as defined by the City of Mayer zoning ordinance." Also, "All components of Ground Source Heat Pump Systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | Section 152.102(B)(3) - Location | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Permit |  |  | "A building permit shall be obtained for any Ground Source Heat Pump System prior to installation." Also, "Borings for Ground Source Heat Pump System where the pipes or coils are installed vertically below the land shall also be subject to approval by the Minnesota Department of health." | Section 152.102(B)(8) - Building Permit | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Screening |  |  | "Ground Source Heat Pump Systems installed for use in a commercial, industrial or institutional uses are considered mechanical equipment and shall be screened in accordance with the requirements of the City's zoning ordinance, if required. Ground source heat pumps installed for residential use shall be exempt from the screening requirement." | Section 152.102(B)(4) - Screening | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Certification |  |  | "The Ground Source heat Pump System shall be certified by Underwriters Laboratories, inc., and comply with the requirements of the international building code." | Section 152.102(B)(6) - Certification | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Decommissioning |  |  | "Any Ground Source Heat Pump System which is inoperable for twelve (12) successive months shall be deemed to be abandoned and shall be deemed a public nuisance. The owner shall remove the abandoned system at their expense after obtaining a demolition permit." Further: "The heat pump and any external or aboveground mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid, which is to be captured and disposed of in accordance with state and federal regulations"; and "The top of the pipe, coil or boring shall be uncovered and sealed." | Section 152.102(B)(7) - Abandonment | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Open-loop Prohibitions |  |  | "All Ground Source heat Pump Systems shall be closed loop systems that circulate heat transfer fluids as allowed by this section through pipes or coils buried beneath the land surface." The ordinance also defines "OPEN LOOP GROUND SOURCE HEAT PUMP SYSTEM" separately, but the operative rule requires all GHP systems to be closed loop. | Section 152.102(B)(2) - System Requirements | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | Mayer | 2701941138 | Other Prohibitions/Regulations |  |  | "Ground Source Heat Pump Systems in public water bodies or water bodies owned or managed by the City of Mayer shall be prohibited except for stormwater ponds managed by the City of Mayer and when accessory to a City of Mayer facility." | Section 152.102(B)(1)(b) - Accessory Use | 2014 | https://greenstep.pca.state.mn.us/sites/default/files/26.1MayerActionFile.pdf
Minnesota | Carver | New Germany | 2701945556 | Permit |  |  | Accessory uses in multiple districts expressly include "Solar collection and geo-thermal heating and cooling systems used in conjunction with permitted uses" in the A - Agricultural District, R-1 Single Family Residential District, R-2 Multiple Family Residential District, B - Business/Commercial District, and I - Industrial District. In the PUD District, "All permitted uses and accessory uses of the R-1 Single Family Residential District and R-2 Multiple Family Residential District are allowed" in residential areas, and "All permitted uses and accessory uses of the B - Business/Commercial District" and "I- Industrial District" are allowed in commercial and industrial areas of the PUD District. | CHAPTER VIII, Section 2 (Zoning District Regulations) | 2011 | http://cityofnewgermany.com/wp-content/uploads/2018/04/Ordinance-100-final.pdf
Minnesota | Ramsey | Arden Hills | 2702026 | Definition: Geothermal |  |  | "Geothermal energy - Hot water or steam extracted from geothermal reservoirs in the earth's crust. Water or steam extracted from geothermal reservoirs can be used for geothermal heat pumps, water heating, or electricity generation." | Exhibit V - Definitions |  | https://codelibrary.amlegal.com/codes/ardenhills/latest/ardenhills_mn/0-0-0-14021
Minnesota | Ramsey | Arden Hills | 2702026 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump - A heat pump in which the refrigerant exchanges heat (in a heat exchanger) with a fluid circulating through an earth connection medium (ground or ground water). The fluid is contained in a variety of loop (pipe) configurations depending on the temperature of the ground and the ground area available. Loops may be installed horizontally or vertically in the ground or submersed in a body of water." | Exhibit V - Definitions |  | https://codelibrary.amlegal.com/codes/ardenhills/latest/ardenhills_mn/0-0-0-14021
Minnesota | Chisago | Chisago City | 2702511350 | Definition: Geothermal |  |  | "Geothermal Energy. Renewable energy generated from the interior of the earth and used to produce energy for heating buildings or serving building commercial or industrial processes." | 6.12 C. Geothermal Energy Sources and Systems, 1. Definitions | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | 2702511350 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Ground Source Heat Pump System. A system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." Also: "Ground Source Heat Pump System (GSHPS). A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. The energy must be used on-site." | 6.12 C. Geothermal Energy Sources and Systems, 1. Definitions | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | 2702511350 | Permit |  |  | "A building permit is required with all new installation of a Ground Source Heat Pump System." | 6.12 C. Geothermal Energy Sources and Systems, 1. Permits and Applications | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | 2702511350 | Decommissioning |  |  | "A GSHPS that is allowed to remain in a nonfunctional or inoperative state for a period of twelve (12) consecutive months, and which is not brought in operation within the time specified by the city after notification to the owner or operator of the GSHPS, shall be presumed abandoned and may be declared a public nuisance subject to removal at the expense of the operator." | 6.12 C. Geothermal Energy Sources and Systems, 5. Abandonment | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | 2702511350 | Open-loop Prohibitions |  |  | "Only closed loop GSHPS utilizing Minnesota Department of Health approved heat transfer fluids are permitted." | 6.12 C. Geothermal Energy Sources and Systems, 3. Design and Placement | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Chisago | Chisago City | 2702511350 | Other Prohibitions/Regulations |  |  | "GSHPS are prohibited on surface waters, except for stormwater ponds where they are permitted." | 6.12 C. Geothermal Energy Sources and Systems, 3. Design and Placement | 2025 | https://www.ci.chisago.mn.us/vertical/sites/%7B4CF416A7-935D-4E3F-82DF-F3E06B5985B0%7D/uploads/6.0_Communicty_Design_.pdf
Minnesota | Clay | Barnesville | 2702703574 | Permit |  |  | "The city requires that all geothermal heating systems be registered." "Property owners are required to register their systems by providing the City Administrator with all state-approved permits prior to installation." "Before installing geothermal heating systems, residents are required to obtain a city building permit." | § 151.122 CITY REQUIREMENTS. | 2023 | https://codelibrary.amlegal.com/codes/barnesvillemn/latest/barnesville_mn/0-0-0-5453
Minnesota | Clay | Barnesville | 2702703574 | Inspection |  |  | "city officials may, upon reasonable notice to the owner, enter upon any property within the city... for purposes of inspecting geothermal facilities, or monitoring the operational characteristics of such facilities" and "The city shall provide affected property owners or occupants with reasonable prior notice... Such inspections or monitoring shall be conducted in accordance with applicable city and state procedures for inspections." | § 151.123 CITY INSPECTION AND MONITORING OF GEOTHERMAL FACILITIES. | 2023 | https://codelibrary.amlegal.com/codes/barnesvillemn/latest/barnesville_mn/0-0-0-5453
Minnesota | Clay | Dilworth | 2702715976 | Permit |  |  | "Any person, including the city, desiring to construct, install or alter a geothermal heating system within the city shall first apply for a geothermal heating system permit at the City Hall on forms provided for that purpose. No person shall commence construction or alteration of a geothermal heating system prior to the owner of a proposed geothermal heating system receiving a permit." | § 54.07 APPLICATION FOR GEOTHERMAL HEATING SYSTEM PERMIT | 2009 | https://codelibrary.amlegal.com/codes/dilworthmn/latest/dilworth_mn/0-0-0-1245
Minnesota | Dakota | Lakeville | 2703735180 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems shall be set back a minimum of five feet (5') from interior side lot lines and ten feet (10') from rear lot lines." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: C. Location | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Setback - Yards | 10 | feet | "Ground source heat pump systems shall only be located in the rear yard as defined by this title." "All components of ground source heat pump systems shall be set back a minimum of five feet (5') from interior side lot lines and ten feet (10') from rear lot lines." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: C. Location | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation." "Borings for ground source heat pump systems where the pipes or coils are installed vertically below the land shall also be subject to approval by the Minnesota department of health." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: G. Building Permit | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Screening |  |  | "Ground source heat pump systems shall be screened in accordance with the requirements of section 11-21-13 of this title." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: D. Screening | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Certification |  |  | "The ground source heat pump system shall be certified by Underwriters Laboratories, Inc., and comply to the requirements of the international building code." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: E. Certification | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Decommissioning |  |  | "Any ground source heat pump system which is inoperable for twelve (12) successive months shall be deemed to be abandoned and shall be deemed a public nuisance. The owner shall remove the abandoned system at their expense after obtaining a demolition permit" including: "The heat pump and any external or aboveground mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid, which is to be captured and disposed of in accordance with state and federal regulations"; and "The top of the pipe, coil or boring shall be uncovered and sealed." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: F. Abandonment | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed loop systems that circulate heat transfer fluids as allowed by this section through pipes or coils buried beneath the land surface." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: B. System Requirements | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Dakota | Lakeville | 2703735180 | Other Prohibitions/Regulations |  |  | "Ground source heat systems in public water bodies or water bodies owned or managed by the city of Lakeville shall be prohibited except when accessory to a city of Lakeville facility." | 11-29-7: GROUND SOURCE HEAT PUMP SYSTEMS: A. Accessory Use | 2010 | https://codelibrary.amlegal.com/codes/lakevillemn/latest/lakeville_mn/0-0-0-7811
Minnesota | Fillmore | Lanesboro | 2704535450 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | § 151.33(A) Definitions | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | 2704535450 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, boring and loops shall be set back at least five feet from interior side lot lines and at least ten feet from rear lot lines." | § 151.33(B)(b)(ii) Setbacks | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | 2704535450 | Permit |  |  | "A building permit and a conditional use permit if required shall be obtained for any ground source heat pump prior to installation. Borings for vertical systems are subject to approve from the MN Dept. of Public Health." In addition, "no alternative energy system shall be located, constructed, erected, moved, reconstructed, extended, enlarged or structurally altered within the City until a permit for the system has been issued by the City" and "a zoning permit must be obtained from the city prior to the construction of any system." | § 151.33(B)(e) Permits; § 151.33(E) Permits for Alternative Energy Systems | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | 2704535450 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and in order to suppress noise and hide from public view materials and designs matching those used for the structure will be incorporated into a plan design. Where miscellaneous exterior equipment cannot be fully hidden with matching building materials, landscaping may be used as additional screening. Screening remains subject to the requirements of the applicable zoning district." | § 151.33(B)(b)(v) Screening | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | 2704535450 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirement of the State Building Code and the Minnesota Department of Health." | § 151.33(B)(c) Safety | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | 2704535450 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed" and "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable state and federal regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 151.33(B)(d) Abandonment | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota | Fillmore | Lanesboro | 2704535450 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids are permitted. One loop ground source heat pump systems are not permitted." | § 151.33(B)(b)(i) System Requirements | 2019 | https://lanesboro-mn.gov/wp-content/uploads/2023/08/CHAPTER-151.pdf
Minnesota |  | Pine Island | 2704951136 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | SEC. 11.73, Subd. 4.C. Location | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Setback - Yards | 10 | feet | "Ground source heat pump systems shall only be located in the rear yard as defined by this chapter." Also, "All components of ground source heat pump systems shall be set back a minimum of five (5) feet from interior side lot lines and ten (10) feet from rear lot lines." | SEC. 11.73, Subd. 4.C. Location | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation." The ordinance also states: "Borings for ground source heat pump systems where the pipes or coils are installed vertically below the land shall also be subject to approval by the Minnesota Department of Health." | SEC. 11.73, Subd. 4.G. Building Permit | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Screening |  |  | "Ground source heat pump systems shall be screened in accordance with the requirements of Section 11.70, Subdivision 7 of this Chapter." | SEC. 11.73, Subd. 4.D. Screening | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Certification |  |  | "The ground source heat pump system shall be certified by Underwriters Laboratories, Inc., and comply to the requirements of the international building code." | SEC. 11.73, Subd. 4.E. Certification | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Decommissioning |  |  | "Any ground source heat pump system which is inoperable for 12 successive months shall be deemed to be abandoned and shall be deemed a public nuisance. The owner shall remove the abandoned system at their expense after obtaining a demolition permit" including: "The heat pump and any external or aboveground mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid, which is to be captured and disposed of in accordance with state and federal regulations"; and "The top of the pipe, coil or boring shall be uncovered and sealed." | SEC. 11.73, Subd. 4.F. Abandonment | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed loop systems that circulate heat transfer fluids as allowed by this subdivision through pipes or coils buried beneath the land surface." | SEC. 11.73, Subd. 4.B. System Requirements | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota |  | Pine Island | 2704951136 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems shall only be located in the rear yard as defined by this chapter." Also: "Ground source heat pump systems shall not encroach upon drainage and utility easements." | SEC. 11.73, Subd. 4.C. Location | 2015 | https://pineislandmn.gov/vertical/sites/%7B52A5D060-3422-4069-8E86-A961C2752B7F%7D/uploads/Code-Chapter-11.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Definition: Geothermal |  |  | "Geothermal Project: Ground source heat pump systems which use the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. Systems include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; a heat pump unit that processes heat for use or disperses heat for cooling and an air distribution system. This includes open and closed loop as well as horizontal and vertical ground source heat pump systems" | Section 28, Subd. 2. Definitions | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Ground Source Heat Pump System: A system which circulates a heat transfer fluid through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." "Open Loop Ground Source Heat Pump System: A system using groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a body of water or into an injection well." "Horizontal Ground Source Heat Pump System: A closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." "Vertical Ground Source Heat Pump System: A closed loop ground source heat pump system where the loops or coils are installed vertically in one or more borings below the land surface." | Section 28, Subd. 2. Definitions | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Permit |  |  | "Within all zoning districts, no structure or land shall be used for a ground source heat pump system except by Conditional Use Permit (CUP) issued in accordance with Section 22, Subdivision 10." Also: "A permit from the MN Department of Health must be obtained prior to boring and installing a vertical ground source heat pump system." | Section 28, Subd. 4. Conditional Uses; Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Inspection |  |  | "A listing or schedule of when and what improvements, subject to inspection and approval by the City Engineer shall be required..." "A provision requiring all improvements to be inspected by the City Engineer during construction at the expense of the Subdivider." "SUBD. 4. INSPECTION. All required improvements shall be inspected by the City Engineer during construction at the expense of the subdivider." | Section 5, Subd. 1. Developer's Agreement; Section 5, Subd. 4. Inspection | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Certification |  |  | "All systems must be certified by Underwriters Laboratories, Inc. (UL)." Also: "All ground source heat pump systems shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the MN State Building Code." | Section 28, Subd. 4. Conditional Uses; Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained from the City Building Official. The heat pump and any external mechanical equipment shall be removed. Pipes or coils below ground shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid must be captured and disposed of in accordance with applicable MN Pollution Control agency regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | Section 28, Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Open-loop Prohibitions |  |  | "Open loop ground source heat pump systems are prohibited; only closed loop ground source heat pump systems utilizing heat transfer fluid are allowed as a conditional use." Also: "Only closed loop ground source heat pump systems utilizing heat transfer fluids are permitted. Open loop ground source heat pump systems are prohibited." | Section 28, Subd. 3. Prohibited Uses; Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Goodhue | Zumbrota | 2704972328 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in public waters are also prohibited." | Section 28, Subd. 7. Ground Source Heat Pump Systems Standards | 2010 | https://www.ci.zumbrota.mn.us/vertical/sites/%7BD28444D6-FB41-4D43-9B2E-396CF731B123%7D/uploads/12.2017_Zoning__Subdivision_Ordinance.pdf
Minnesota | Hennepin | Brooklyn Park | 2705307966 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils, or plates; fluid that absorbs and transfers heat; and a heat pump unit the processes heat for use or disperses heat for cooling; and an air distribution system." | §152.107 DEFINITIONS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | 2705307966 | Setback - Property Lines | 10 | feet | §152.1001(C)(2)(a): "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least 5 feet from interior side lot lines and at least 10 feet from rear lot lines." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | 2705307966 | Permit |  |  | §152.1001(C)(4): upon abandonment, "The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | 2705307966 | Screening |  |  | §152.1001(C)(3): "Ground source heat pumps are considered mechanical equipment subject to screening requirements of §152.1023." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | 2705307966 | Decommissioning |  |  | §152.1001(C)(4): "If the ground source heat pump remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Brooklyn Park | 2705307966 | Open-loop Prohibitions |  |  | §152.1001(C)(1): "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in §152.107 are permitted. Open loop ground source heat pump systems are not permitted." | §152.1001 ALTERNATIVE ENERGY SYSTEMS |  | https://www.brooklynpark.org/wp-content/uploads/2024/07/CH152-Clean-1.pdf
Minnesota | Hennepin | Corcoran | 2705313168 | Permit |  |  | "Mechanical (Residential) $75.00 per unit + State Surcharge Fee ($1.00) (Furnace, AC or Gas line) ... The following qualify as a 'unit' Furnace, AC, Air Exchange, In-floor heat, Boiler, Geothermal System, Ground System Heat Pump, Garage Heater, etc." | 2023 CITY OF CORCORAN BUILDING PERMIT AND RELATED FEES SCHEDULE – OVER THE COUNTER PERMITS | 2023 | https://cdnsm5-hosted.civiclive.com/UserFiles/Servers/Server_15543680/File/Our%20Community/City%20Code/Proposed%20Ordinances/Ordinance%202023-XXX%20Rental%20and%20Property%20Maintenance%20Code%20Draft%20Version%205.pdf
Minnesota | Hennepin | Corcoran | 2705313168 | Inspection |  |  | The fee schedule lists explicit inspection requirements/fees, including: "Inspection outside normal business hours; minimum two hour charge $90.00 per hr.," "Re-inspection Fee $45.00 per hr.," "Inspections for which no fee is specifically indicated $60.00 per hr.," and "Site Inspection Fee RESIDENTIAL $45.00 ea. COMMERCIAL $80.00 ea." | 2023 CITY OF CORCORAN BUILDING PERMIT AND RELATED FEES SCHEDULE – OTHER INSPECTIONS AND FEES | 2023 | https://cdnsm5-hosted.civiclive.com/UserFiles/Servers/Server_15543680/File/Our%20Community/City%20Code/Proposed%20Ordinances/Ordinance%202023-XXX%20Rental%20and%20Property%20Maintenance%20Code%20Draft%20Version%205.pdf
Minnesota | Hennepin | Medina | 2705341480 | Setback - Property Lines | 10 | feet | "No portions of the geothermal system shall be permitted to be located within or below drainage and utility easements or within 10 feet of any property line." | Section 828.09.2. Geothermal Systems, Subd. 2 | 2023 | https://www.medinamn.gov/files/assets/city/v/1/admin/documents/city-code-book/may-2025-changes/828.pdf
Minnesota | Hennepin | Medina | 2705341480 | Other Prohibitions/Regulations |  |  | "Geothermal systems shall not be permitted within or under wetlands." | Section 828.09.2. Geothermal Systems, Subd. 3 | 2023 | https://www.medinamn.gov/files/assets/city/v/1/admin/documents/city-code-book/may-2025-changes/828.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump systems" are regulated in Sec. 42-76(b), which establishes standards for this system type as an alternative energy system. | Sec. 42-76(b) | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Setback - Property Lines | 10 | feet | "Except as otherwise allowed for systems within public waters (by conditional use permit), all components of ground source heat pump systems including pumps, borings and loops shall be set back at least ten feet from all lines..." | Sec. 42-76(b)(2)b.1 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Setback - Water Bodies | 25 | feet | "Except as otherwise allowed for systems within public waters (by conditional use permit), all components of ground source heat pump systems including pumps, borings and loops shall be set back at least ten feet from all lines and 25 feet from the ordinary high water level of any public water body." | Sec. 42-76(b)(2)b.1 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Noise Limits | 55 | dBA | "Audible noise from ground source heat pump systems shall not exceed 55 dB(A) when measured from the outside of the nearest residence, business, school, hospital, religious institution, or other inhabited structure." | Sec. 42-76(b)(2)d | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation." Also, "Borings for vertical systems are subject to approval by the state department of public health." | Sec. 42-76(b)(4) | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Inspection |  |  | "Ground source heat pump systems shall be subject to inspection by the city's building official every three years and at the property owner's expense in accordance with the city's fee schedule." | Sec. 42-76(b)(4)c | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the screening requirements of section 42-64(j) of this chapter." | Sec. 42-76(b)(2)e | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | Sec. 42-76(b)(2)f | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The property owner shall remove the abandoned system and restore vegetation upon the site at his/her expense after a demolition permit has been obtained..." Subsection (a): "The heat pump and any external mechanical equipment shall be removed." Subsection (b): "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring (where it connects to mechanical equipment) shall be capped in a secure manner." | Sec. 42-76(b)(3) | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in article 1, division 2 are permitted. Open loop ground source heat pump systems are prohibited." | Sec. 42-76(b)(2)a.1 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Spring Park | 2705362014 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems located within public waters are prohibited." | Sec. 42-76(b)(2)a.2 | 2024 | https://www.ci.spring-park.mn.us/vertical/sites/%7B6E2AA72B-6F0B-4352-AB43-82BCBB41D083%7D/uploads/PC_Agenda_Packet_-_10-8-2025.pdf
Minnesota | Hennepin | Wayzata | 2705368818 | Permit |  |  | "105 Work exempt from permit. Permits shall not be required for the following:" followed by a list of exempt work items that does not include ground-source heat pump systems. The code scope states in 1346.0101 that "This code shall regulate the design, installation, maintenance, alteration, and inspection of mechanical systems... utilized to provide control of environmental conditions within buildings," which encompasses mechanical GHP systems under this code. | 1346.0105 SECTION 105 WORK EXEMPT FROM PERMIT |  | https://www.wayzata.org/DocumentCenter/View/209/Minnesota-Mechanical-Fuel-Gas-Code-PDF
Minnesota | Hennepin | Wayzata | 2705368818 | Inspection |  |  | "106 Required inspections. The building official, upon notification from the permit holder or the permit holder’s agent, shall make the following inspections..." including "Underground inspection shall be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place" and "Final inspection shall be made upon completion of the mechanical system. Exception: Ground-source heat pump loop systems tested in accordance with this code shall be permitted to be backfilled prior to inspection." | 1346.0106 SECTION 106 REQUIRED INSPECTIONS |  | https://www.wayzata.org/DocumentCenter/View/209/Minnesota-Mechanical-Fuel-Gas-Code-PDF
Minnesota | McLeod | Winsted | 2708571086 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump System. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | 1501.018.C. Definitions | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet (5') from interior side lot lines..." | 1501.018.D.2.b. Setbacks | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Setback - Yards | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet (5') from interior side lot lines and at least ten feet (10') from rear lot lines." Also: "Above-ground equipment associated with ground source heat pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable zoning district." | 1501.018.D.2.b. Setbacks | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Permit |  |  | "Those permits as required, and a conditional use permit if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." Also, in 1501.018.I.2: "no alternative energy system shall be located, constructed, erected, moved, reconstructed, extended, enlarged or structurally altered within the City until a permit for the system ('system permit') has been issued by the City." In 1501.018.I.3: "a zoning certificate must be obtained from the City prior to the construction of any system." In 1501.018.I.4: "a building permit must be obtained from the City prior to the construction of any system when construction activity is of such a nature that a building permit is required." | 1501.018.D. Ground Source Heat Pump Systems | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and in order to suppress noise and hide from public view materials and designs matching those used for the structure will be incorporated into a plan design. Where miscellaneous exterior equipment cannot be fully hidden with matching building materials, landscaping may be used as additional screening. Screening remains subject to the requirements of the applicable zoning district." | 1501.018.D.2.e. Screening | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | 1501.018.D.3. Safety | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained" and "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable state and federal regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | 1501.018.D.4. Abandonment | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | McLeod | Winsted | 2708571086 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in Section 1501.018.C., are permitted. Open loop ground source heat pump systems are not permitted." | 1501.018.D.2.a.I. System requirements | 2022 | https://winsted.mn.us/vertical/Sites/%7B671DA7CC-04DA-49E0-BEE2-9F92D425D1A3%7D/uploads/Chapter_15_TOC_All_Sections_01-18-22.pdf
Minnesota | Ramsey | North St. Paul | 2712347221 | Definition: Well |  |  | "CLOSED LOOP GROUND SOURCE GEOTHERMAL SYSTEM. A system that circulates a heat transfer fluid, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water whereby the temperature of the surrounding earth or water is transferred to the structure at the ground surface." "HORIZONTAL GEOTHERMAL SYSTEM. A closed loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." "VERTICAL GEOTHERMAL SYSTEM. A closed loop ground source heat pump system where the loops or coils are installed vertically in one or more borings below the land surface." | § 154.003 DEFINITIONS | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A system that uses the relatively constant temperature of the stored energy of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. Also called a ground source heat pump system." | § 154.003 DEFINITIONS | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet from side, front and rear lot lines." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; ii. Setbacks | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval by the Minnesota Department of Public Health." Also under water-based systems: "Ground source heat pump systems in public waters may be permitted as a conditional use..." subject to DNR approval, owner/association consent, and "demonstrated compliance with applicable city permit requirements." | (I) Alternative energy systems; 1. Ground source heat pump systems; (e) Permits | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Inspection |  |  | "All wiring, installation of pipes, grading and all other installations and construction shall be subject to inspection." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; iii. Construction | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements for the applicable zoning district." Related screening requirement: "Building utility services and structures such as meters, transformers, refuse containers, including dumpsters, ancillary equipment and the like shall be either located inside the principal building, inside an accessory building, or, where outside be entirely screened from off-site views." Also, for rooftop equipment: "All rooftop equipment, with the exception of solar and wind equipment, shall be screened from view from adjacent streets and public rights-of-way." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; vi. Screening | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the State Building Code." | (I) Alternative energy systems; 1. Ground source heat pump systems; (c) Certification | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained..." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | (I) Alternative energy systems; 1. Ground source heat pump systems; (d) Abandonment | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in this section are permitted. Open loop ground source heat pump systems are not permitted." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; i. System requirements | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | Ramsey | North St. Paul | 2712347221 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the city are not permitted." | (I) Alternative energy systems; 1. Ground source heat pump systems; (b) General standards; i. System requirements | 2022 | https://www.northstpaul.org/DocumentCenter/View/5863/Zoning-Code
Minnesota | St. Louis | Duluth | 2713717000 | Definition: Geothermal Heat Pump |  |  | "Accessory solar or geothermal power equipment. Accessory uses and structures that are clearly subordinate in size and use to the primary use and structure on the property, and that are used to reduce energy consumption or to generate energy from non-fossil fuel and non-carbon dioxide emitting sources on the property. These structures and uses may include but are not limited to the following, and may be located at ground level or above or below ground unless specifically limited in this Chapter, provided that they meet all other applicable requirements of this Chapter: solar photovoltaic modules, solar thermal hot water collectors, solar arrays; and geothermal heat pumps, earth tubes, or downhole heat exchangers." | 50-41.1 Definitions: A | 2025 | https://duluthmn.gov/media/xgicauxa/udc-2025.pdf
Minnesota | Scott | Elko New Market | 2713918662 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet (5') from interior side lot lines and at least ten feet (10') from rear lot lines." | 11-14-2(B)(1)(a) Setbacks | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | 2713918662 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval by the Minnesota department of public health." | 11-14-2(D) Permits | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | 2713918662 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the screening requirements of section 11-5-4 of this title." | 11-14-2(B)(3) Screening | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | 2713918662 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the state building code." | 11-14-2(B)(4) Safety | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | 2713918662 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained..." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted"; and "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 11-14-2(C) Abandonment | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | 2713918662 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in section 11-2-2 of this title are permitted. Open loop ground source heat pump systems are not permitted." | 11-14-2(B)(1)(a) System Requirements | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Elko New Market | 2713918662 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the city of Elko New Market are not permitted." | 11-14-2(B)(1)(c) System Requirements | 2011 | https://codelibrary.amlegal.com/codes/elkonewmarketmn/latest/elkonewmarket_mn/0-0-0-6613
Minnesota | Scott | Jordan | 2713932174 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least 5 feet from interior side lot lines and at least 10 feet from rear lot lines." | § 154.392(B)(2)(a) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | 2713932174 | Permit |  |  | "A building permit shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval by the Minnesota Department of Public Health." | § 154.392(D) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | 2713932174 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and shall be screened from view to the extent possible without impacting their function." | § 154.392(B)(5) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | 2713932174 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the State Building Code." | § 154.392(B)(6) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | 2713932174 | Decommissioning |  |  | "If a ground source heat pump system remains nonfunctional or inoperative for a continuous period of 1 year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... (1) The heat pump and any external mechanical equipment shall be removed. (2) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted. (3) Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | § 154.392(C) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | 2713932174 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in this section are permitted. Open loop ground source heat pump systems are not permitted." | § 154.392(B)(1)(a) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Scott | Jordan | 2713932174 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the City of Jordan are not permitted." | § 154.392(B)(1)(c) | 2017 | https://codelibrary.amlegal.com/codes/jordan/latest/jordan_mn/0-0-0-13518
Minnesota | Washington | Dellwood | 2715616 | Definition: Geothermal Heat Pump |  |  | "Geo-thermal heating systems, also known as watered heating systems and air conditioning units..." | 96.01 GEO-THERMAL HEATING SYSTEMS, WATER FED HEAT EXTRACTORS AND WATER FED AIR CONDITIONING UNITS | 2015 | https://www.dellwood.us/wp-content/uploads/2024/01/Dellwood-Code-Book-2023.pdf
Minnesota | Washington | Dellwood | 2715616 | Permit |  |  | "No person shall erect, construct, or alter any geo-thermal or water fed heating system, in the City of Dellwood without first securing a building permit therefore and paying the permit fee as established by the Council from time to time." Also, the permit application "shall include a description of the system clearly showing that the system employs a closed loop recirculating water system with property equipment to prevent discharge of any water in the ordinary use of the system." | 96.02 PERMIT REQUIRED | 2015 | https://www.dellwood.us/wp-content/uploads/2024/01/Dellwood-Code-Book-2023.pdf
Minnesota | Washington | Dellwood | 2715616 | Open-loop Prohibitions |  |  | "Geo-thermal heating systems, also known as watered heating systems and air conditioning units are prohibited, except those systems which are constructed and installed with a closed, recirculating ground loop water system..." and "No system shall be permitted which allows discharge of water onto the surface, or into a seepage pit/drainfield system, or into any natural or artificial drainage- ways." | 96.01 GEO-THERMAL HEATING SYSTEMS, WATER FED HEAT EXTRACTORS AND WATER FED AIR CONDITIONING UNITS | 2015 | https://www.dellwood.us/wp-content/uploads/2024/01/Dellwood-Code-Book-2023.pdf
Minnesota | Washington | Newport | 2716345790 | Definition: Geothermal Heat Pump |  |  | "Heat pump system, ground source means a heat pump system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | Sec. 36-16. Terms defined. | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Setback - Property Lines | 20 | feet | "All air conditioning units excluding window units shall be located a minimum of 20 feet from all lot lines, but not within the front yard." | Sec. 36-422(j) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Setback - Yards | 20 | feet | For ground source heat pump systems, "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet from interior side lot lines and at least ten feet from rear lot lines." Separately, "All air conditioning units excluding window units shall be located a minimum of 20 feet from all lot lines, but not within the front yard." | Sec. 36-424(b)(2)b.1; Sec. 36-422(j) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Permit |  |  | "A building permit and interim conditional use permit, if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the state department of public health." | Sec. 36-424(b)(5) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of division 3 of this article." Division 3 states: "All utility equipment, such as heating and ventilating equipment, meters and other devices shall be completely screened from eye-level view of adjacent properties and streets. Equipment shall be screened with a screen wall, berm, or landscaping if located on the ground. If on the roof, the equipment shall be screened with a parapet or screen wall of materials compatible with the principal structure..." | Sec. 36-424(b)(2)e.; Sec. 36-448(f) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc., and meet the requirements of the state building code." | Sec. 36-424(b)(3) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... The heat pump and any external mechanical equipment shall be removed. Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations... Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | Sec. 36-424(b)(4) | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids, as defined in section 36-16, are permitted. Open loop ground source heat pump systems are not permitted." | Sec. 36-424(b)(2)a.1. | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Newport | 2716345790 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the city are not permitted." | Sec. 36-424(b)(2)a.3. | 2026 | https://www.newportmn.gov/Ordinances/2026/Ordinance%20No%202026-02-%20Repealing%20and%20Replacing%20Chapters%2028%20and%2036.pdf?t=202601091537090
Minnesota | Washington | Oak Park Heights | 2716347914 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | 401.17.C. Definitions; Alternative Energy Systems Related/Ground Source Heat Pumps (Geothermal Heating) | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Setback - Property Lines | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five (5) feet from interior side lot lines and at least ten (10) feet from rear lot lines." | 401.17.G.2.b. Setbacks | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Permit |  |  | "Permits. A building permit and a conditional use permit, if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." Also, "Ground source heat pump systems in public waters may be permitted as a conditional use in accordance with Section 401.17.D and Section 401.03 of this Ordinance, subject to approval from the Minnesota Department of Natural Resources and subject to written consent of all property owners and/or approval by an association in accordance with its adopted bylaws." | 401.17.G. Ground Source Heat Pumps (Geothermal Heating) | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and subject to the requirements of Section 401.15.E.10.c." | 401.17.G.2.e. Screening | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | 401.17.G. Safety | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one (1) year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted"; "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 401.17.G. Abandonment | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in Section 401.17.C.4 of this Ordinance are permitted. Open loop ground source heat pump systems are not permitted." | 401.17.G.2.a. System Requirements | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Washington | Oak Park Heights | 2716347914 | Other Prohibitions/Regulations |  |  | "Ground source heat pump systems in water bodies owned or managed by the City of Oak Park Heights are not permitted." | 401.17.G.2.a. System Requirements | 2024 | https://www.cityofoakparkheights.com/vertical/sites/%7B22E6E0E6-5B6F-460C-B43E-F48433F4DDAB%7D/uploads/CC401_Amended_11.26.2024)_(1).pdf
Minnesota | Winona | St. Charles | 2716956788 | Setback - Yards | 10 | feet | "All components of ground source heat pump systems including pumps, borings and loops shall be set back at least five feet from interior side lot lines and at least ten feet from rear lot lines." Also, "Above-ground equipment associated with ground source heat pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable zoning district." | § 152.76(B)(2)(a)-(b) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | 2716956788 | Permit |  |  | "Those permits as required, and a conditional use permit if required, shall be obtained for any ground source heat pump system prior to installation. Borings for vertical systems are subject to approval from the Minnesota Department of Public Health." | § 152.76(E) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | 2716956788 | Screening |  |  | "Ground source heat pumps are considered mechanical equipment and in order to suppress noise and hide from public view materials and designs matching those used for the structure will be incorporated into a plan design. Where miscellaneous exterior equipment cannot be fully hidden with matching building materials, landscaping may be used as additional screening. Screening remains subject to the requirements of the applicable zoning district." | § 152.76(B)(5) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | 2716956788 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the State Building Code." | § 152.76(C) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | 2716956788 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable state and federal regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 152.76(D) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Minnesota | Winona | St. Charles | 2716956788 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids as defined in § 152.75 (C) are permitted. Open loop ground source heat pump systems are not permitted." | § 152.76(B)(1)(a) | 2011 | https://codelibrary.amlegal.com/codes/stcharlesmn/latest/stcharles_mn/0-0-0-5592
Missouri | St. Charles | O'Fallon | 2954074 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL OR GROUND-SOURCE HEAT-PUMP SYSTEM. A system for heating and/or cooling buildings using the earth's thermal properties in conjunction with electricity. This system may include open and closed loop systems." | Section 400.910 Definitions | 2025 | https://ecode360.com/43322073
Missouri | St. Charles | O'Fallon | 2954074 | Permit |  |  | Section 400.920(C): "It shall be unlawful for any renewable energy system to be constructed, erected, and/or installed without a building permit." Section 400.920(D): "Geothermal energy systems ... may be approved by the Planning and Development Department in accordance with this Article by the issuance of a building permit." Section 400.955(A): "A completed building permit with all the applicable electrical and mechanical engineering information and drawings." | Section 400.920 General Provisions; Section 400.955 Application Requirements For Geothermal Systems | 2025 | https://ecode360.com/43322073
Missouri | St. Charles | O'Fallon | 2954074 | Decommissioning |  |  | "Any system that is out of service for a continuous period of twelve (12) months will be considered abandoned and must be removed within ninety (90) days. If such system is not removed within ninety (90) days, the City may remove such system at the owner's expense after giving the owner notice and an opportunity to be heard with respect to removal." | Section 400.990 Abandonment | 2025 | https://ecode360.com/43322073
Missouri | St. Charles | O'Fallon | 2954074 | Other Prohibitions/Regulations |  |  | Section 400.950(A): "Setback Requirements. Drilling and trenching for geothermal heat pump systems shall be prohibited on any easement." | Section 400.950 Geothermal Systems | 2025 | https://ecode360.com/43322073
Missouri | Phelps | Rolla | 2962912 | Permit |  |  | Section 35-189(a) states: "Private wells may be utilized for closed loop heat pump systems... A construction permit and an operation permit as provided in Sections 35-185 and 35-186 of this Code are required." Section 35-185(a) adds: "Before commencement of drilling, installation, or construction... the owner... shall first obtain a written construction permit signed by the General Manager of the Rolla Municipal Utilities." Section 35-186(a) provides that after completion, "the Rolla Municipal Utilities shall issue an operation permit." | Section 35-189 Private Wells For Heat Pumps; Section 35-185 Construction Permit Required Prior To Commencement Of Drilling, Installation, Or Construction; Application; Fee; Inspection Provisions; Section 35-186 Permit For Operation Of Private Well Or Water Supply | 2017 | https://ecode360.com/42770538
Missouri | Phelps | Rolla | 2962912 | Inspection |  |  | Section 35-185(b) states: "Prior to completion of the private well or water supply, the Rolla Municipal Utilities shall be allowed to inspect the work at any stage of the drilling, installation, or construction" and the permit holder must notify the utility "before any underground portions are covered" and "when the work is ready for final inspection." It further provides: "The inspection shall be made within sixty (60) hours... of the receipt of notice." Section 35-186(a) says the operation permit is issued after completion "to the satisfaction of the Rolla Municipal Utilities," and Section 35-186(b) adds: "Rolla Municipal Utilities, at its discretion, shall perform yearly inspections of the installation to verify compliance with applicable ordinances." | Section 35-185 Construction Permit Required Prior To Commencement Of Drilling, Installation, Or Construction; Application; Fee; Inspection Provisions; Section 35-186 Permit For Operation Of Private Well Or Water Supply | 2017 | https://ecode360.com/42770538
Missouri | Phelps | Rolla | 2962912 | Decommissioning |  |  | Section 35-183 requires owners "to plug any existing private wells in accordance with 10 CSR 23-3.110" and provides that when the grandfather clause no longer applies, "the private well shall be properly plugged as stipulated herein." | Section 35-183 Plugging Of Existing Wells And Connection To Public Water Supply | 2017 | https://ecode360.com/42770538
Missouri | Phelps | Rolla | 2962912 | Open-loop Prohibitions |  |  | Section 35-189(b) states: "Private wells shall not be permitted for any type of open loop heat pump system, as defined and discussed in 10 CSR 23-5 in the Missouri, Code of State Regulations." | Section 35-189 Private Wells For Heat Pumps | 2017 | https://ecode360.com/42770538
Missouri | Ste. Genevieve | Ste. Genevieve | 2964180 | Permit |  |  | "It is unlawful for any person, without first obtaining a construction permit, to: Install, alter or modify any electrical, plumbing or mechanical system of a building where the cost is in excess of five hundred dollars ($500.00)." Ground-source heat pump work is explicitly within the mechanical/plumbing/electrical system context, and the same section states: "Application for such permit shall be made to the Clerk and shall be accompanied by plans and specifications in duplicate..." and "No permit shall be issued until after approval of plans." | Section 500.190 Construction Permits | 2025 | https://ecode360.com/27816792
Missouri | Ste. Genevieve | Ste. Genevieve | 2964180 | Inspection |  |  | Section 500.190(E) provides: "The Building Inspector shall make or cause to be made such inspections as are necessary to see to the enforcement of the provisions of this Article and to make any tests or examinations of materials or methods to be used for the purpose of seeing that they comply with the provisions of this Article." | Section 500.190 Construction Permits | 2025 | https://ecode360.com/27816792
Missouri |  | University City | 2975220 | Permit |  |  | "Type of Permit Fee ... Geothermal system (per system) $90.00." This appears within the Mechanical Code permit fee schedule, which states: "The fee charged for each mechanical permit shall be as scheduled below." | Section 500.080, 106.5.2 Fee schedule | 2013 | https://www.ucitymo.org/documentcenter/view/14300
Missouri |  | University City | 2975220 | Inspection |  |  | Mechanical Code: "In addition to the inspections normally provided, the Code Official shall require that additional inspections or reinspections be conducted due to non-compliance with Code requirements or due to work which is not ready for inspection or not accessible for inspection at the time of a scheduled inspection." Also, "All third-party inspections shall be in accordance with Section 110.4.90 of the Building Code of University City." Building Code Section 110.4.90 provides: "All third-party inspections, qualifications, and reliability must be preapproved by the Building Official." | Section 500.080, 107.90 Extra inspections; Section 500.020, 110.4.90 Third-party inspections | 2013 | https://www.ucitymo.org/documentcenter/view/14300
Montana | Flathead | Flathead | 3002991118 | Definition: Well |  |  | "Heating/Cooling Exchange Well" means a Well for the purpose and with the attributes set forth in Section 2-2-119(1) of this Ordinance. | 1-1-104(30) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | 3002991118 | Permit |  |  | "Before appropriating water for a use described in this subsection (1), approval of the Engineer is required." Also, "An applicant must file a completed application form and obtain approval from the Engineer before drilling any Well(s) ... and putting water to use pursuant to this Section." Once approved, "the Engineer shall issue an authorization to develop the Appropriation Right for a Heating/Cooling Exchange Well." | 2-2-119(1)-(5) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | 3002991118 | Inspection |  |  | For completed appropriations, "The Office of the Engineer shall review the certified statement and may then inspect the Appropriation, and if it determines that the Appropriation has been completed in substantial accordance with the Appropriation Right or Change in Use authorization, it shall issue" the final document. Staff analysis of applications may also include "field inspection by Staff." | 2-2-114; 2-2-107(2)(c) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | 3002991118 | Decommissioning |  |  | "If an Appropriation Right for a Heating/Cooling Exchange Well is revoked by the Board ... or is determined to be abandoned ... or is voluntarily abandoned, the Appropriator shall, within 180 days of the revocation or voluntary abandonment, follow the well abandonment procedures, standards, and rules adopted by the board of water well contractors pursuant to 37-43-202, MCA ... for any Well associated with the revoked or abandoned Appropriation Right for a Heating/Cooling Exchange Well." | 2-2-119(7) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Montana | Flathead | Flathead | 3002991118 | Other Prohibitions/Regulations |  |  | "Aquifer Injection and Injection Wells are not allowed except when used exclusively for Heating/Cooling Exchange Wells." | 1-1-111(3) | 2015 | https://www.frwmb.gov/unitary-administration-management-ordinance/
Nebraska | Adams | Hastings | 3100121415 | Definition: Well |  |  | "Water Well. Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, obtaining hydrogeologic information, or extracting water from or injecting water into the underground water reservoir." | 32-601(19). Definitions. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Adams | Hastings | 3100121415 | Definition: Geothermal Heat Pump |  |  | "Geothermal Water Source Heat Pump System. The installation, operation, or use of any well, device, piping, or other apparatus for the purpose of utilizing the geothermal properties of groundwater, whereby water passes through a heat exchanger to provide heating or cooling from the geothermal properties of the groundwater, and the spent water is discharged to the surface or subsurface. This system is sometimes referred to as a 'pump and dump' system." | 32-601(9). Definitions. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Adams | Hastings | 3100121415 | Permit |  |  | Section 32-615.01 states: "Geothermal Water Source Heat Pump Systems may be installed and operated within the City of Hastings, and its two mile extraterritorial jurisdiction, subject to permitting and other applicable requirements of the Hastings City Code." Section 32-616 requires a "well permit for a domestic water well or a nonpotable water well within the City of Hastings or its two mile extraterritorial jurisdictional area" and lists required application information including "the depth of the proposed well" and "an accurate diagram showing the location of the proposed well in respect to the boundaries of the property, the nearest street, road, or highway intersection, and any on site septic or waste disposal system." | 32-615.01. Geothermal water source heat pump systems.; 32-616. Permitting of water wells; application for well permit. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Adams | Hastings | 3100121415 | Other Prohibitions/Regulations |  |  | Section 32-615.01 provides that geothermal water source heat pump systems "may be installed and operated" but adds: "In no event shall the spent water from any Geothermal Water Source Heat Pump System be directed or allowed to enter into or onto any publicly maintained street right of way, road right of way, ditch, storm sewer system, or sanitary sewer system." It also requires that discharge "shall be dedicated to a beneficial use" and "shall not include chemical additives for cleaning or descaling." | 32-615.01. Geothermal water source heat pump systems. | 2014 | https://dwee.nebraska.gov/sites/default/files/icts_files/Hastings%20Area_Mechanism_Ordinance%204421.pdf
Nebraska | Hall | Alda | 3100625 | Setback - Public Water | 1000 | feet | Section 3-124 provides: "Under no circumstances shall the Alda Village Board approve any permit to drill or operate any of the below described facilities within the indicated number of feet from the Village of Alda water wells:" The table lists "All water wells, including, but not limited to, domestic supply wells, irrigation wells, stock wells, sandpoint wells, and heat pump wells — 1,000 feet." | Section 3, Chapter 3, Article 1, Section 3-124 | 2001 | https://dwee.nebraska.gov/sites/default/files/publications/ATTLGRBL.pdf
Nebraska | Hall | Alda | 3100625 | Permit |  |  | Section 3-122 states: "it shall be unlawful for any person, corporation or other legal entity to drill and/or operate any of the following facilities ... without first having obtained a permit from the Alda Village Board of Trustees," including "heat pump wells." Section 3-123 adds that the owner "must complete and submit an application" to the Village Clerk, and the Village Board of Trustees "shall approve or deny such permit." | Section 1 / Section 2, Chapter 3, Article 1, Sections 3-122 and 3-123 | 2001 | https://dwee.nebraska.gov/sites/default/files/publications/ATTLGRBL.pdf
Nebraska | Hall | Alda | 3100625 | Other Prohibitions/Regulations |  |  | Section 3-124 states: "Under no circumstances shall the Alda Village Board approve any permit to drill or operate" listed facilities within the stated distances from municipal wells. The table includes "heat pump wells" with a prohibited distance of "1,000 feet" from the Village of Alda water wells. | Section 3, Chapter 3, Article 1, Section 3-124 | 2001 | https://dwee.nebraska.gov/sites/default/files/publications/ATTLGRBL.pdf
Nebraska | Butler | David City | 3102312315 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth, as an integral part of the HVAC system of a principal structure." It further defines system types: "Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground"; "Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid"; "Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer"; and "Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions | 2025 | https://www.davidcityne.com/vimages/shared/vnews/stories/62a09a9a6c318/David_City%20Zoning_Ordinance_1504%20Redacted.pdf
Nebraska | Cass | Weeping Water | 3102593383 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a F or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | Section 2.03 Definitions | 2023 | https://www.weepingwater.org/documents/216/Weeping_Water_Zoning_and_Subdivision_Regulations_FINAL_DRAFT_8.29.23.pdf
Nebraska | Gage | Beatrice | 3103390 | Permit |  |  | Sec. 26-189: "Repair of a water well shall not commence before a repair permit has been issued by the city to the owner of the land on which such well is located... In the case of emergency repairs, such repairs may be made without first obtaining the repair permit; provided, however, said permit shall be obtained within ten (10) calendar days subsequent to such emergency repair." Sec. 26-190: "If such applicant's well is found to be in compliance with the 'Water Well Regulations and Standards of the City of Beatrice' and its ordinances, a permit shall then be issued." | Sec. 26-189. Repair of water well; permit required.; Sec. 26-190. Permit for water well; application; fees. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Gage | Beatrice | 3103390 | Inspection |  |  | "Within sixty (60) calendar days following the repair of the water well, the owner shall be required to have the well inspected by the community development director." | Sec. 26-189. Repair of water well; permit required. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Gage | Beatrice | 3103390 | Decommissioning |  |  | "Whenever a person shall abandon or destroy a water well, such person shall first contact the community development director for the purpose of inspection of such abandonment or destruction process from its inception. All abandoned water wells shall be properly abandoned or destroyed in accordance with applicable regulations and standards on file within the city clerk's office." | Sec. 26-191. Abandoned water well. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Gage | Beatrice | 3103390 | Other Prohibitions/Regulations |  |  | "Discharge, recharge, or reinjection wells are prohibited except for the disposal of water where only the temperature of the water has been altered, provided that the maximum water temperature shall not exceed ninety (90) degrees Fahrenheit. It shall be deemed a violation of this section to reinject or inject any chemically altered water or hazardous substance of any kind into or above the groundwater aquifer." | Sec. 26-188. Use of water well; when permitted. | 2026 | https://www.beatrice.ne.gov/media/xybl55e2/26-6-recodifying-all-the-ordinances-of-the-city-of-beatrice-nebraska-adopting-and-enacting-a-new-code-for-the-city.pdf
Nebraska | Furnas | Beaver City | 3103495 | Definition: Geothermal Heat Pump |  |  | "Any well utilizing geothermal properties of the ground shall meet the following guidelines..." | § 52.47 GEOTHERMAL WELLS | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Furnas | Beaver City | 3103495 | Setback - Public Water | 1000 | feet | § 52.46(A) states: "It shall be unlawful to place, maintain, construct or replace any of the following facilities or structures... within the indicated number of feet from the city's public water supply wells." The table lists "Water well — 1,000 feet." | § 52.46 DESIGNATED DISTANCE FROM MUNICIPAL WATER SOURCES; PROHIBITED | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Furnas | Beaver City | 3103495 | Setback - Sewer Lines | 50 | feet | § 52.46(A) provides that listed facilities may not be placed within specified distances from the city's public water supply wells; the table includes "Sanitary sewer line — 50 feet." | § 52.46 DESIGNATED DISTANCE FROM MUNICIPAL WATER SOURCES; PROHIBITED | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Furnas | Beaver City | 3103495 | Permit |  |  | "It shall be unlawful for any person, corporation or other legal entity to drill and/or operate any of the following facilities within the corporate limits or zoning jurisdiction of the city without first having obtained the proper permit from the City Council: potable water well; any other well, including heat pumps..." Subsection (B) adds: "In order to obtain a permit to drill and/or operate any of the facilities listed above, the owner of the property on which the proposed facility is to be located must make application to the City Council... After reviewing said application, the Council must approve or deny such permit." | § 52.45 PERMIT REQUIRED | 2026 | https://codelibrary.amlegal.com/codes/beavercityne/latest/beavercity_ne/0-0-0-1575
Nebraska | Dawson | Gothenburg | 3104791169 | Permit |  |  | The ordinance lists geothermal as a special-use category in multiple districts: "Alternative energy systems utilizing Biomass, Geothermal, Hydropower, Solar and/or Wind sources..." may be used "if a special permit for the use has been obtained" in the AG, AG-1, R-1, R-2, R-3, R-4, C-1, C-2, I-1, and I-2 districts. | § 152.018(D)(12); § 152.019(D)(5); § 152.020(D)(6); § 152.021(D)(10); § 152.022(D)(9); § 152.023(D)(8); § 152.024(D)(6); § 152.025(D)(6); § 152.026(D)(7); § 152.027(D)(7) | 2009 | https://ci.gothenburg.ne.us/pdf/Zoning.pdf
Nebraska | Dodge | North Bend | 3105334720 | Definition: Well |  |  | "GEOTHERMAL WELL OR CLOSED LOOP HEAT PUMP WELL. A well constructed for the purpose of installing the underground closed loop necessary to circulate fluid from a closed loop heat pump system." | § 172.002 DEFINITIONS | 2015 | https://www.northbendne.com/_files/ugd/fce8b2_80e4f1b66eb14ed7ac1f49af4438726b.pdf
Nebraska | Dodge | North Bend | 3105334720 | Setback - Public Water | 1000 | feet | "Under no circumstances shall the City Council approve any permit to drill or operate any of the below described facilities within the indicated number of feet from the City of North Bend Municipal water wells: ... Any other well within 1,000 feet." The chapter also defines "GEOTHERMAL WELL OR CLOSED LOOP HEAT PUMP WELL" in § 172.002, making that well type an in-scope well category. | § 172.024 DRILLING OR INSTALLATION OF OTHER FACILITIES WITHIN DESIGNATED DISTANCE PROHIBITED | 2015 | https://www.northbendne.com/_files/ugd/fce8b2_80e4f1b66eb14ed7ac1f49af4438726b.pdf
Nebraska | Dodge | North Bend | 3105334720 | Permit |  |  | § 172.022(B) states it is unlawful to "drill and/or operate" listed facilities "without having first obtained the proper permit from the governing body of the city;" and § 172.023 provides: "In order to obtain a permit to drill and/or operate any of the facilities listed in § 172.022, the owner of the property... must make application on the proper form..." The same chapter separately defines "GEOTHERMAL WELL OR CLOSED LOOP HEAT PUMP WELL" in § 172.002. | § 172.022 WELLS; § 172.023 PROCEDURE TO OBTAIN PERMIT | 2015 | https://www.northbendne.com/_files/ugd/fce8b2_80e4f1b66eb14ed7ac1f49af4438726b.pdf
Nebraska | Lincoln | Brady | 3106085 | Other Prohibitions/Regulations |  |  | "It shall be unlawful for any person, firm, partnership, corporation or school district to establish or cause to be established any water well for the purpose of extracting water or injecting water within the corporate limits of the municipality; provided, such wells shall be permitted use in operating water to air heat pumps or heat exchangers." | § 52.24 PRIVATE WELLS |  | https://codelibrary.amlegal.com/codes/bradyne/latest/brady_ne/0-0-0-1189
Nebraska | Franklin | Franklin | 3106117530 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2019 | https://cdn.prod.website-files.com/616efa093e9c59154f8da1d1/61797bbe7e24c9625d52571f_Franklin%20Zoning%20and%20Subdivision%20Regulations.pdf
Nebraska | Hall | Grand Island | 3107919595 | Definition: Geothermal Heat Pump |  |  | "Geothermal water source heat pump systems" are the systems governed by this section; subsection A states that such systems "may be installed and operated within the City of Grand Island" and regulates "any discharge of the spent water from any such system." | 40-17 Geothermal Water Source Heat Pump Systems | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hall | Grand Island | 3107919595 | Permit |  |  | "It shall be unlawful for any person... to install a well to be used for geothermal heat transfer purposes... without obtaining a permit for said well." Subsection A also states systems are allowed "subject to permitting and other applicable requirements of the Grand Island City Code." | 40-17(D) Prohibited Acts | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hall | Grand Island | 3107919595 | Open-loop Prohibitions |  |  | "New open-loop systems are prohibited in the City of Grand Island and its two (2) mile jurisdictional boundary." The ordinance adds that previously installed open-loop systems are exempt only "until the system requires overhaul and/or replacement." | 40-17(B) | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Hall | Grand Island | 3107919595 | Other Prohibitions/Regulations |  |  | "It shall be unlawful to connect or discharge any water from said well... to the city stormwater conveyance system without first obtaining a permit for the connection." Subsection A further provides: "In no event shall the spent water from any geothermal water source heat pump system be directed toward or allowed to enter into or onto any publicly maintained street right of way, road right of way, ditch, storm sewer system, or sanitary sewer system." | 40-17(D)(3) | 2025 | https://codelibrary.amlegal.com/codes/grandislandne/latest/grandisland_ne/0-0-0-26984
Nebraska | Keith | Ogallala | 3110192218 | Setback - Public Water | 1000 | feet | "The minimum distance separating the municipal water supply wells of the city from potential sources of contamination shall be as follows: (1) One thousand feet: All water wells, including but not limited to, domestic supply wells, irrigation wells, stock wells, and heat pump wells." | § 52.075 ENCROACHMENT OF POTENTIAL SOURCES OF CONTAMINATION | 2018 | https://www.ogallala-ne.gov/your_government/municipal_code/docs/MunicipalCode_191008_250325.pdf
Nebraska | Keith | Ogallala | 3110192218 | Permit |  |  | "Any person who intends to construct a potential source of contamination or enlarge an existing potential source of contamination shall file a written application for a permit with the City Manager. The City Manager may approve a permit which conforms to the distance requirements of this section; provided, however, if the City Manager determines that the proposed construction poses a risk of contaminating a municipal water supply well, the City Manager shall deny the permit." | § 52.075 ENCROACHMENT OF POTENTIAL SOURCES OF CONTAMINATION | 2018 | https://www.ogallala-ne.gov/your_government/municipal_code/docs/MunicipalCode_191008_250325.pdf
Nebraska | Madison | Norfolk | 3111992133 | Definition: Well |  |  | "Water Well shall mean any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground, obtaining hydrogeologic information, or extracting water from the underground water reservoir." | Water Well shall mean | 2021 | https://bloximages.newyork1.vip.townnews.com/norfolkdailynews.com/content/tncms/assets/v3/editorial/8/d0/8d0d11e2-96e3-11eb-9478-779ac98dea93/606c6ee3ebdf8.pdf.pdf
Nebraska | Thayer | Deshler | 3112840 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2024 | https://www.deshlernebraska.com/wp-content/uploads/2024/05/Deshler-NE-Zoning-Ord-2024-rv1-redacted-for-posting.pdf
Nebraska | Pierce | Plainview | 3113992378 | Setback - Public Water | 1000 | feet | § 3-137 provides: "Under no circumstances shall the Plainview City Council approve any permit to drill or operate any of the above-described facilities within the below-referenced number of feet from the City of Plainview Municipal water wells:" including "Potable Water Well 1,000 feet" and "Any Other Well 1,000 feet." Read with § 3-135, closed-loop systems used for heating and cooling are the only new wells allowed and "shall be subject to setbacks and permits as otherwise set forth in this code." | § 3-137 DRILLING OR INSTALLATION OF OTHER FACILITIES WITHIN DESIGNATED DISTANCE FROM MUNICIPAL WATER SOURCES; PROHIBITED | 1996 | https://codelibrary.amlegal.com/codes/plainviewne/latest/plainview_ne/0-0-0-1291
Nebraska | Pierce | Plainview | 3113992378 | Permit |  |  | § 3-135 states: "On or after November 21, 2002, no new water wells of any type shall be drilled or operated within the corporate limits, with the exception of closed loop systems used for heating and cooling. Closed loop systems shall be subject to setbacks and permits as otherwise set forth in this code." § 3-136 adds: "In order to obtain a permit to drill and/or operate any of the facilities listed in section 3-135, the owner of property on which the proposed facility is to be located, must make application on the proper form provided by the Governing Body of the City of Plainview... the Plainview City Council must approve or deny said permit." | § 3-135 DRILLING AND OPERATION OF WELLS, AND OTHER UNDERGROUND FACILITIES OR CONTAMINATING FACILITIES UNLAWFUL; § 3-136 WELLS AND OTHER FACILITIES; PROCEDURE TO OBTAIN PERMIT | 1996 | https://codelibrary.amlegal.com/codes/plainviewne/latest/plainview_ne/0-0-0-1291
Nebraska | Red Willow | McCook | 3114591882 | Permit |  |  | "All fences constructed in the City of McCook shall comply with the provision of this section and obtain a building permit." | Section 2102. Fences, Walls, Hedges | 2017 | https://www.cityofmccook.com/276/Zoning-Ordinance-PDF
Nebraska | Saunders | Wahoo | 3115550965 | Permit |  |  | "If a Building Permit for the construction of a residence is issued by the City of Wahoo for an undeveloped lot in any of the Areas, a domestic potable water well may be installed only if permitted by the Board of Public Works of the City of Wahoo." | § 5.22.06(3) Water, Potable and Non-Potable | 2005 | https://www.wahoo.ne.us/vimages/shared/vnews/stories/50364172e06a0/wahoozoning%20regulations%20to%208-20-2014.pdf
Nebraska | Saunders | Wahoo | 3115550965 | Other Prohibitions/Regulations |  |  | "Any existing water wells which are being used for a well-to-well ground source heat pump system will be allowed to remain in service until said system is not permitted by the State of Nebraska, said water to be used for non-potable purposes only." | § 5.22.06(3)(d) Water, Potable and Non-Potable | 2005 | https://www.wahoo.ne.us/vimages/shared/vnews/stories/50364172e06a0/wahoozoning%20regulations%20to%208-20-2014.pdf
Nebraska | Stanton | SBE | 3116792862 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump System: A well, constructed for the purpose of utilizing the geothermal properties of the earth. 1. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. ... 2. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 3. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 4. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | G | 2023 | https://stantoncounty.nebraska.gov/sites/default/files/doc/2017%20Zoning%20Regulations%20approved%20nov%202017%20-%20amended%202023.pdf
Nebraska | Stanton | SBE | 3116792862 | Permit |  |  | "No building, structure, or land ... shall hereafter be used or occupied and no building or structure or part thereof shall hereafter be erected, constructed, reconstructed, moved, or structurally altered, except in conformity with the provisions of this Resolution ... and except after receiving a zoning permit from the Stanton County Zoning Administrator..." Also: "Any structure over 64 square feet in size shall require a permit from the Stanton County Zoning Office." | ARTICLE 3: GENERAL REGULATIONS, Section 3.07 Scope of Regulations | 2023 | https://stantoncounty.nebraska.gov/sites/default/files/doc/2017%20Zoning%20Regulations%20approved%20nov%202017%20-%20amended%202023.pdf
Nebraska | Clay | Harvard | 3121345 | Setback - Public Water | 100 | feet | "Systems utilizing the geothermal properties of the ground for water wells... (F) Must be located no closer than 100 feet to the city's drinking water source." | § 52.56 GEOTHERMAL SYSTEMS | 2002 | https://codelibrary.amlegal.com/codes/harvardne/latest/harvard_ne/0-0-0-1779
Nebraska | Clay | Harvard | 3121345 | Open-loop Prohibitions |  |  | "Systems utilizing the geothermal properties of the ground for water wells: (A) Must be a closed loop system." | § 52.56 GEOTHERMAL SYSTEMS | 2002 | https://codelibrary.amlegal.com/codes/harvardne/latest/harvard_ne/0-0-0-1779
Nebraska | Platte | Humphrey | 3123480 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEM shall mean a well, constructed for the purpose of utilizing the geothermal properties of the earth. 12. Open Loop Heat Pump well shall mean a well that transfers heat via pumped ground water which is discharged above and/or below ground. For below ground discharge, refer to NDEQ Title 122. 13. Closed Loop Heat Pump well shall mean a well, constructed for the purpose of installing the underground closed loop pipe necessary to recirculate heat transfer fluid. 14. Horizontal Closed Loop means a trench or pit essentially parallel to the horizon and into which a closed loop pipe is placed for the purpose of heat transfer. 15. Vertical Closed Loop means a borehole essentially perpendicular to the horizon into which a closed loop pipe is placed for the purpose of heat transfer." | ARTICLE 2: DEFINITIONS | 2019 | https://www.cityofhumphrey.com/vimages/shared/vnews/stories/5cbdbfcf3869e/Humphrey%20Zoning_070318.pdf
Nebraska | Sherman | Rockville | 3142075 | Definition: Well |  |  | "WATER WELL. Any excavation that is drilled, corralled, bored, washed, dug, driven, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal property of the ground or extracting water from or injecting water into the underground water. WATER WELL shall not include any excavation made for obtaining or prospecting for oils, natural gas, minerals, or products mined or quarried or inserting media to repressure oil or natural gas bearing formation." | § 51.23 WATER WELLS. (A) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Sherman | Rockville | 3142075 | Setback - Public Water | 1000 | feet | "It shall be unlawful to place, maintain, construct, or replace any of the following structures or conduct any of the following activities within the distance specified below from any existing village water well, water storage tanks, or existing underground water mains." The table lists "Water well — 1,000 feet." | § 51.23 WATER WELLS. (C)(1) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Sherman | Rockville | 3142075 | Setback - Water Lines | 500 | feet | "It shall be unlawful to place, maintain, construct, or replace any of the following structures or conduct any of the following activities within the distance specified below from any existing village water well, water storage tanks, or existing underground water mains." The table lists "Village water main — 500 feet." | § 51.23 WATER WELLS. (C)(1) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Sherman | Rockville | 3142075 | Permit |  |  | "The construction of a water well, within the corporate limits or within one mile of the corporate limits of the village, shall not be started unless a permit approved by the Village Board has been obtained." Also, for closer placement approved under division (E), "No installation shall be made without the approval of both the Village Board and Department of Health of the state." | § 51.23 WATER WELLS. (D) and (E)(2) | 2008 | https://codelibrary.amlegal.com/codes/rockvillene/latest/rockville_ne/0-0-0-1509
Nebraska | Lincoln | Sutherland | 3147920 | Setback - Public Water | 1000 | feet | The table of minimum distances from municipal water supply wells lists: "All water wells, including, but not limited to, domestic supply wells, irrigation wells, stock wells and heat pump wells — 1,000" feet. | § 53.26 MUNICIPAL WATER SUPPLY PROTECTION | 2013 | https://codelibrary.amlegal.com/codes/sutherlandne/latest/sutherland_ne/0-0-0-1754
Nebraska | Lincoln | Sutherland | 3147920 | Permit |  |  | "Any person who intends to construct a potential source of contamination or enlarge an existing potential source of contamination shall file a written application for a permit with the Board of Trustees." The Board "may approve a permit which conforms to the distance requirements of this section" and "shall deny the permit" if the proposed construction poses a contamination risk to a municipal water supply well. | § 53.26(C) MUNICIPAL WATER SUPPLY PROTECTION | 2013 | https://codelibrary.amlegal.com/codes/sutherlandne/latest/sutherland_ne/0-0-0-1754
Nebraska | Lancaster | Waverly | 3151770 | Definition: Well |  |  | "For purposes of this Article, 'water well' shall mean any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed for the purpose of exploring for ground water, monitoring ground water, utilizing the geothermal properties of the ground or extracting water from or injecting water into the underground water reservoir." | § 51.39 WELL - HEAD PROTECTION: DEFINITIONS | 2021 | https://www.citywaverly.com/vimages/shared/vnews/stories/620ea640e9a25/Wavelry%20Municipal%20Code.pdf
Nebraska | Lancaster | Waverly | 3151770 | Setback - Public Water | 500 | feet | Section 51.40 states: "It shall be unlawful to place, maintain, construct, or replace any of the following structures or conduct any of the following activities within the distance specified below from existing Municipal water well:" The table lists "Closed-Loop Food Grade Heat Pump" at "500" "Feet" ("150" meters). | § 51.40 WELL - HEAD PROTECTION: PLACEMENT, MAINTENANCE AND CONSTRUCTION; PROHIBITIONS | 2021 | https://www.citywaverly.com/vimages/shared/vnews/stories/620ea640e9a25/Wavelry%20Municipal%20Code.pdf
Nebraska | Lancaster | Waverly | 3151770 | Permit |  |  | "Any well that penetrates the aquifer for purposes of extracting water or injecting water or any other substance, or for purposes of testing or monitoring ground water must have a permit issued by the City. Ground source heat pumps with closed loop systems used for heating and cooling of facilities are exempt from the permit requirement." | § 51.28 MANDATORY HOOKUP | 2021 | https://www.citywaverly.com/vimages/shared/vnews/stories/620ea640e9a25/Wavelry%20Municipal%20Code.pdf
Nevada | Washoe | Reno North | 3203194703 | Definition: Geothermal Heat Pump |  |  | "Rebates for Solar/Renewable Technologies. (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno North | 3203194703 | Permit |  |  | "City Facilitation of Market Mechanisms in the Buildings Sector - Various city policies to facilitate the purchase of energy efficient appliances and the purchase of solar/renewable technologies ... Policies could include ... Rebates for Solar/Renewable Technologies, (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southeast | 3203194709 | Definition: Geothermal Heat Pump |  |  | "Rebates for Solar/Renewable Technologies. (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southeast | 3203194709 | Permit |  |  | "City Facilitation of Market Mechanisms in the Buildings Sector - Various city policies to facilitate the purchase of energy efficient appliances and the purchase of solar/renewable technologies ... Policies could include ... Rebates for Solar/Renewable Technologies, (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southwest | 3203194712 | Definition: Geothermal Heat Pump |  |  | "Rebates for Solar/Renewable Technologies. (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
Nevada | Washoe | Reno Southwest | 3203194712 | Permit |  |  | "City Facilitation of Market Mechanisms in the Buildings Sector - Various city policies to facilitate the purchase of energy efficient appliances and the purchase of solar/renewable technologies ... Policies could include ... Rebates for Solar/Renewable Technologies, (photovoltaics, solar hot water heaters, geothermal heat pumps, etc.)" | Appendix B — Secondary Strategies | 2008 | https://www.reno.gov/Documents/Business%20and%20Development/Development%20Services/Zoning%20Code/PUD%20Handbooks/Spring%20Mountain%20Appendices%20BR.pdf?t=202604061203370
New Hampshire | Belknap | Alton | 3300101060 | Permit |  |  | "If water is discharged back into the bedrock well for geothermal applications, then the applicant must demonstrate that the discharge water is not contaminated and is in compliance with the standards and requirements of the New Hampshire Department of Environmental Services." | 5.12 SURFACE WATERS | 2012 | https://alton.nh.gov/wp-content/uploads/2026/01/Site-Plan-Review-Regulations.pdf
New Hampshire | Belknap | Alton | 3300101060 | Screening |  |  | "Air conditioners, heat pumps, compressors, generators, fans, and other devices which produce noise shall be so located and screened as to meet the above noise standard, and so not to be visually offensive to adjacent property owners or as seen from public streets. Each site plan shall indicate the location of all such devices and include a brief description of how this standard will be met." | 5.17 NOISE | 2012 | https://alton.nh.gov/wp-content/uploads/2026/01/Site-Plan-Review-Regulations.pdf
New Hampshire | Cheshire | Keene | 3300539300 | Definition: Geothermal |  |  | "Geothermal heating and cooling systems (e.g. groundwater wells and subsurface heat exchange installations)" are listed as permitted uses in the Surface Water Protection Overlay District without a surface water protection conditional use permit. | Section 11.5 PERMITTED USES | 2025 | https://keenenh.gov/wp-content/uploads/2026/01/Land-Development-Code_Amended-November-2025.pdf
New Hampshire | Coos | Carroll | 3300710100 | Definition: Geothermal Heat Pump |  |  | "Accessory Use - A use customarily incidental and subordinate to the principal building or use and located on the same lot with such principal building or lot. The following examples are considered accessory uses, but are not limited to, antennas, swimming pools, satellite dishes, garages, barns, storage sheds, storage of a registered camper or recreational vehicle, and renewable energy facilities for on-site use including wind, solar and geothermal." | Section 202. Definitions | 2024 | https://carrollnh.org/wp-content/uploads/2024/07/2024-Zoning-Ordinance.pdf
New Hampshire | Coos | Carroll | 3300710100 | Setback - Yards | 20 | feet | Section 202 defines setback/yard applicability for accessory geothermal use: "renewable energy facilities for on-site use including wind, solar and geothermal. All accessory uses must follow zoning set-back requirements." The ordinance defines "Yard - That portion of a lot formed by the required setback which may not be occupied by a building or other structure." District yard setbacks include RES 1: "SIDE SETBACK: 20 Feet"; RES 2 residential: "SIDE SETBACK: 20 Feet"; R-B: "SIDE SETBACK: 20 Feet"; RU: "SIDE SETBACK: 30 feet." | Section 202. Definitions; Section 403.2 Residential: RES 1; Section 403.3 Residential: RES 2; Section 403.4 Residential - Business: R-B; Section 403.6 Rural: RU | 2024 | https://carrollnh.org/wp-content/uploads/2024/07/2024-Zoning-Ordinance.pdf
New Hampshire | Grafton | Lisbon | 3300942020 | Definition: Geothermal |  |  | "1.28 Renewable Energy Facility : A facility for the generation of solar, wind or geothermal energy." | ARTICLE I DEFINITIONS §1.28 | 2023 | https://www.lisbon.nh.gov/DocumentCenter/View/344/Zoning-Ordinances-Regulations-2023-PDF
New Hampshire | Grafton | Waterville Valley | 3300979380 | Permit |  |  | "Small wind, solar or geothermal energy systems designed primarily to supply energy for on-site use" are listed as accessory uses ("a") in all districts shown in the use table. Article VIII states: "Permit Required - After passage of this Ordinance, it shall be unlawful to change the nature or extent of the use of any building or lot, erect and use any building, sign or other structure, or alter any existing sign or the size of any building or other structure, or relocate any building or other structure in any district without first obtaining a permit from the Selectmen or their agent." | Article IV - Uses | 2026 | https://www.watervillevalleynh.gov/planning-board/files/zoning-ordinance-2026-updated
New Hampshire | Merrimack | Bradford | 3301306980 | Permit |  |  | Within the SWOD Buffer, "Conditional Uses" include "p. Geothermal heating and cooling systems, including but not limited to related groundwater wells and subsurface heat exchange installations." The ordinance further states: "An application for a CUP will be considered at a public hearing" and "Completed Conditional Use Permit Applications will include" specified materials. | Article XI SURFACE WATER PROTECTION OVERLAY DISTRICT (SWOD), D. Uses / E. Conditional Use Permit Requirements | 2025 | https://bradfordnh.gov/uploads/2025-bradford-zoning-ordinance.pdf
New Hampshire | Merrimack | Bradford | 3301306980 | Inspection |  |  | During construction on parcels including land within the SWOD Buffer, "the boundaries of the SWOD Buffer areas will be marked on the site with stakes and flagging along the buffer perimeter. Such markings will remain in place until all construction is complete and has been inspected and approved." | Article XI SURFACE WATER PROTECTION OVERLAY DISTRICT (SWOD), D. Uses | 2025 | https://bradfordnh.gov/uploads/2025-bradford-zoning-ordinance.pdf
New Hampshire | Rockingham | Rye | 3301566180 | Definition: Geothermal |  |  | "RENEWAL ENERGY SYSTEMS: Renewal energy systems include solar systems, small wind energy systems, geothermal systems and hydro systems. (added 9-20-2022)" | § 202-1.14. Definitions | 2022 | https://www.ryenh.gov/DocumentCenter/View/5460
New Jersey | Atlantic | Linwood | 3400140530 | Definition: Geothermal |  |  | "RENEWABLE ENERGY SYSTEM — Any structure or installation, such as a small wind energy system, solar- collecting array, or geothermal system, which is designed and intended to produce energy from natural forces such as wind, sunlight or geothermal heat." | § 273-4 Definitions | 2021 | https://ecode360.com/14620824
New Jersey | Atlantic | Linwood | 3400140530 | Permit |  |  | "A zoning permit shall be required for the installation of a renewable energy system." Also, "An owner shall submit an application to the Zoning Officer for a permit for a renewable energy system." | § 273-6A; § 273-8A | 2021 | https://ecode360.com/14620824
New Jersey | Atlantic | Linwood | 3400140530 | Inspection |  |  | "The Zoning Officer may enter any property for which a permit has been issued under this chapter to conduct inspections to determine whether the conditions stated in the permit have been met." | § 273-10B | 2021 | https://ecode360.com/14620824
New Jersey | Atlantic | Linwood | 3400140530 | Decommissioning |  |  | "A renewable energy system that is out of service for a continuous twelve-month period will be deemed abandoned." If abandoned, "the owner of the renewable energy system shall remove the system at the owner's sole expense within three months after the owner receives the notice of abandonment." | § 273-7 | 2021 | https://ecode360.com/14620824
New Jersey | Bergen | River Vale | 3400363690 | Permit |  |  | The ordinance expressly includes geothermal-type systems in the permit fee schedule: Plumbing Subcode fees, § 90-4A(3)(b)[23]: "Heating and cooling equipment such as ground source, heat pump systems, heat pumps, solar thermal systems but not limited to these systems: $125 each." Mechanical subcode fees, § 90-4A(5)(b): "Replacement of heating and cooling equip such as ground source, heat pump systems, heat pumps solar: $150." Also, § 90-4A states: "The fee for a construction or zoning permit shall be the sum of the subcode fees listed... and shall be paid before the permit is issued." | § 90-4 Fees | 2024 | https://ecode360.com/11325645
New Jersey | Burlington | Mount Laurel | 3400549020 | Permit |  |  | "The fee for the installation of a geothermal system shall be $81.00." | § 66-3 Fees, (2) Plumbing Subcode Fees, a.13 | 2021 | https://cms7files.revize.com/mountlaurel/Document%20Center/Department/Municipal%20Clerk's%20Office/Upcoming%20Ordinances/O5.21.pdf
New Jersey | Cape May | Middle | 3400945810 | Definition: Geothermal |  |  | "Any structure or installation, such as a wind turbine, solar collecting array, or geothermal system, which is designed and intended to produce energy from natural forces, such as wind, sunlight or geothermal heat." | § 250-629B. Definition | 2018 | https://ecode360.com/9072391
New Jersey | Cape May | Middle | 3400945810 | Setback - Building Foundation | 10 | feet | "The minimum separation distance required between any structures associated with the renewable energy system and any other structures or buildings on site is 10 feet." Section § 250-629B defines a renewable energy system to include "a ... geothermal system." | § 250-629C(3) | 2018 | https://ecode360.com/9072391
New Jersey | Cape May | Middle | 3400945810 | Permit |  |  | "Permit. A zoning permit and construction permit shall be required for the installation of a renewable energy system." Section § 250-629B defines a renewable energy system to include "a ... geothermal system." | § 250-629E(2) Permit requirements | 2018 | https://ecode360.com/9072391
New Jersey | Hunterdon | Kingwood | 3401937065 | Definition: Well |  |  | "CLOSED LOOP GEOTHERMAL WELL. A well or borehole drilled or a shallow trench installed in the earth, wherein a series of pipes is installed into the opening and connected to a heat exchange system in the dwelling. The pipes form a 'closed loop' (hence the name) and are filled with a heat transfer fluid. The fluid is circulated through the piping from the opening into the heat exchanger and back. The system functions in the same manner as the open looped system, except there is no pumping of groundwater." | § 153-21 Definitions | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Setback - Wastewater | 50 | feet | For vertical closed loop geothermal wells, the separation table requires "Septic leaching fields — 50 feet" and "Septic tank — 25 feet." For horizontal closed loop geothermal systems, the table requires "Septic leaching fields — 25 feet" and "Septic tank — 25 feet." | § 153-39B(1)(a) and § 153-39C(1) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Setback - Private Water | 100 | feet | For vertical closed loop geothermal wells, the separation table requires "On-site or off-site water supply well(s) — 100 feet." Horizontal systems require "On-site or off-site water supply well(s) — 50 feet." | § 153-39B(1)(a) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Setback - Public Water | 500 | feet | For both vertical and horizontal closed loop geothermal systems, the separation tables require "Public water supply well or future well site — 500 feet." | § 153-39B(1)(a) and § 153-39C(1) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Setback - Hazardous Materials/Fertilizers | 500 | feet | For both vertical and horizontal closed loop geothermal systems, the separation tables require "Known groundwater plume of contamination (as mapped by a governmental agency) — 500 feet." | § 153-39B(1)(a) and § 153-39C(1) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Permit |  |  | "No person shall locate, construct or alter any geothermal well within the Township of Kingwood until a permit for the location, construction or alteration of such well has been issued by the administrative authority." Also, "Compliance with all state permitting requirements is a prerequisite to the issuance of a Kingwood Township geothermal well construction permit." | § 153-38 Geothermal well construction permit | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Inspection |  |  | "All closed loop systems must be hydrostatically pressure tested at not less than 1 1/2 times working pressure for two hours." Also, "The heat exchanger installer shall certify that the installed system meets pressure test and heat exchange fluid requirements." | § 153-39B(4) and § 153-39B(6) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Certification |  |  | "At the completion of the geothermal system construction, the applicant shall submit an as-built survey with GPS coordinates for each well, one geologic/well log and well completion certificates. The heat exchanger installer shall certify that the installed system meets pressure test and heat exchange fluid requirements." | § 153-39B(6) | 2022 | https://ecode360.com/10106816
New Jersey | Hunterdon | Kingwood | 3401937065 | Decommissioning |  |  | "All geothermal wells shall be abandoned in accordance with the latest and most applicable NJDEP requirements. Records of decommissioning/abandonment shall be submitted to the Township and administrative authority. Any wells/borings that are drilled and not used for a geothermal installation must be abandoned immediately as per NJDEP requirements." Also, "Any geothermal well not in normal operation for a period of 24 months or more shall be considered inactive and shall be abandoned. The tubing in such wells must be flushed with clean water until all of the ground heat exchanger circulating fluids have been flushed out." | § 153-39D | 2022 | https://ecode360.com/10106816
New Jersey | Mercer | Ewing | 3402122185 | Inspection |  |  | The ordinance expressly sets fees for geothermal inspections: "[5] Geothermal inspections: [a] Residential: $50. [b] Commercial: $100." It also establishes related inspection categories generally under administrative fees, including "Off hour inspections" and "Expedited inspections," but the geothermal-specific inspection requirement is the quoted geothermal inspection fee. | § 172-25A(2) Plumbing subcode fees; § 172-25A(5) Administrative Fees | 2023 | https://ecode360.com/EW1628/document/744062108.pdf
New Jersey | Mercer | Lawrence | 3402139510 | Permit |  |  | "The fee for plan review of a building for compliance under the alternate systems and nondepletable energy source provisions of the energy subcode shall be $240.00 for one- and two-family residences ... and for all other structures as per Ordinance No. 1893-06 For GeoThermal Heating/Cooling Systems." | CERTIFICATES AND OTHER PERMITS | 2009 | https://www.lawrencetwp.com/media/Departments/Construction/Construction%20Permit%20Fees.pdf
New Jersey | Monmouth | Bradley Beach | 3402506970 | Permit |  |  | "The fee for the installation of a geo-thermal system shall be $75." | § 160-3(B)(2)(n) | 2026 | https://ecode360.com/7043039
New Jersey | Monmouth | Howell | 3402533300 | Permit |  |  | The Electrical Subcode fee schedule expressly includes geothermal equipment under electrical permit fee calculations: 'Electrical devices (This includes transformers and generators and P V devices)' with fee brackets by kW, and the average ratings table lists 'Geothermal: range from 3.8 KW to 19.2KW, plus heat pump 2.6 KW to 7.4KW.' | § 139-86, Article XXXVI Uniform Construction Code Fees, C. Electrical Subcode fees, (2)(b) Electrical devices | 2011 | http://nj-howelltownship.civicplus.com/AgendaCenter/ViewFile/Item/18?fileID=81
New Jersey | Monmouth | Sea Girt | 3402566330 | Screening |  |  | "All exterior mechanical equipment, including units for heat, ventilation, air- conditioning, pool pumps and accessories, heat pumps, other than individual air-conditioners to serve a building property shall be located in the rear yard and/or on the top story of either the principal or accessory buildings, either inside or outside." If installed on the buildings, "they shall not be visible from the front or side street or from ground level of immediately adjacent properties and shall be located behind a solid non-transparent physical buffer such as a parapet wall or solid short fence so as to dampen noise effects on neighboring properties." | § 17-5.4 Mechanical Equipment | 2026 | https://ecode360.com/36181331
New Jersey | Monmouth | Wall | 3402576460 | Permit |  |  | "No person shall drill, construct, install or redesignate the use of any well until a permit shall have been issued by the Board of Health." | § 222-54-10. Permit required. | 2018 | https://www.wallnj.gov/DocumentCenter/View/4184/Ordinance-19-2018-Well-Regulation
New Jersey | Monmouth | Wall | 3402576460 | Inspection |  |  | "The Wall Township Health Department shall have access and entry to any property upon which there is located a well or individual sewage disposal system for the purpose of inspecting and/or testing the same." | § 222-54-8. Right of entry. | 2018 | https://www.wallnj.gov/DocumentCenter/View/4184/Ordinance-19-2018-Well-Regulation
New Jersey | Morris | Morris | 3402748090 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM — A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." | § 95-34.4B Definitions | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | 3402748090 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM, CLOSED-LOOP — A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." Also: "OPEN-LOOP GEOTHERMAL SYSTEM — A type of geothermal system that utilizes a water-supply well and a water pump to deliver groundwater to a water-source heat pump." | § 95-34.4B Definitions | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | 3402748090 | Setback - Right of Way | 25 | feet | "Geothermal systems shall not encroach on public drainage, utility roadway or trail easements of any nature." Also: "All geothermal systems shall be located a minimum distance of 25 feet from any property line." | § 95-34.4E(4) and (5) | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | 3402748090 | Setback - Property Lines | 25 | feet | "All geothermal systems shall be located a minimum distance of 25 feet from any property line." | § 95-34.4E(5) | 2020 | https://ecode360.com/10355002
New Jersey | Morris | Morris | 3402748090 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems are prohibited." | § 95-34.4E(2) | 2020 | https://ecode360.com/10355002
New Jersey | Passaic | Bloomingdale | 3403106340 | Permit |  |  | The construction permit fee schedule includes a specific geothermal entry: "Installation or removal of Geothermic or Photovoltaic systems — $30 per $1,000." The section also states: "The fee for a construction permit shall be the sum of the subcode fees listed in the Fee Schedule hereunder, and shall be paid before the permit is issued." | § 11-1.2 Fees | 2024 | https://ecode360.com/36000989
New Jersey | Somerset | Branchburg | 3403507180 | Definition: Geothermal Heat Pump |  |  | "On or after the connection date, a nonpotable well may be installed, maintained, or used for geothermal heating and cooling purposes only." | § BH3A-5A RESTRICTIONS ON NONPOTABLE WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | 3403507180 | Permit |  |  | "Any well installed, maintained or used for geothermal hearing and cooling purposes must be registered with the State of New Jersey as a nonpotable well." | § BH3A-5A(b) RESTRICTIONS ON NONPOTABLE WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | 3403507180 | Inspection |  |  | "Every well closed and sealed shall be approved by the Township Health Department." | § BH3A-6 CLOSING AND SEALING OF WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | 3403507180 | Decommissioning |  |  | "Not later than the Mandatory Connection Date, all private wells within a Ground Water Impact Area shall be closed and sealed by the owner in accordance with State regulations." | § BH3A-6 CLOSING AND SEALING OF WELLS | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Branchburg | 3403507180 | Other Prohibitions/Regulations |  |  | "On and after the Mandatory Connection Date, there shall be no well installations of any type within a Ground Water Impact Area. Wells used solely for groundwater monitoring, and owned or controlled by the New Jersey Department of Environmental Protection, are permitted." | § BH3A-7 FUTURE WELL INSTALLATIONS PROHIBITED | 2012 | https://ecode360.com/36034454
New Jersey | Somerset | Bridgewater | 3403507720 | Permit |  |  | "geothermal facilities, as an accessory use only, are permitted in all zones when wholly provided within a principal structure. Board review is not required if the geothermal facility is located within a principal structure." Also: "All renewable energy facilities require approval from the Zoning Officer and construction office prior to receiving a building permit. Applications for an energy facility shall include information demonstrating compliance with the provisions of this ordinance." | Section 126-335(B)(6) and (9) | 2012 | https://ecode360.com/BR0606/document/753042732.pdf
New Jersey | Sussex | Sparta | 3403769690 | Definition: Well |  |  | "CLOSED LOOP GEOTHERMAL WELL - Shall mean a well into which a continuous closed loop of pipe is inserted for the purpose of non-contact thermal energy transfer from a fluid in the loop to or from the earth." | 19-3.4. Definitions | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | 3403769690 | Permit |  |  | "No person shall locate, construct or alter any geothermal well system until a permit for the location, construction or alteration of geothermal well system shall have been issued by the Sussex County Health Department." Also, "All proposed geothermal systems will require a permit application, and must include a list of equipment to be served and system design drawings." | 19-1.4(c); 19-11.3(a) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | 3403769690 | Certification |  |  | "Geothermal wells shall be constructed or altered by a duly licensed New Jersey geothermal well installation contractor who is licensed as set forth pursuant to N.J.A.C. 7:9D-1.7 and 1.8 and in complete conformance with the Township standards in effect at the time." | 19-11.1(a) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | 3403769690 | Decommissioning |  |  | "After connection to the Township's water utility system, each property owner shall seal their well(s) in compliance with Sussex County Health Department regulations and with the requirements of the Department of Environmental Protection, Division of Water Resources, and in accordance with the standard specifications for sealing abandoned wells which have been adopted by that agency. All wells must be closed by a New Jersey licensed well driller." | 19-6.10 | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | 3403769690 | Open-loop Prohibitions |  |  | "Only Closed Loop Geothermal Well systems are allowed to be installed within Sparta Township. Open loop geothermal well systems are prohibited." | 19-11.2(a) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Sussex | Sparta | 3403769690 | Other Prohibitions/Regulations |  |  | "Cross connections between a private geothermal well system and public water supply systems are strictly prohibited." | 19-11.2(b) | 2022 | https://www.spartanj.org/DocumentCenter/View/563/22-11
New Jersey | Union | Clark | 3403913150 | Permit |  |  | Chapter 122 establishes permit fees that apply to items requiring permits, including a geothermal-specific electrical fee entry: under Electrical § 122-2B(9)(j), 'Geothermal, kw range of 3.8 to 19.2; heat pump, 2.6 kw to 7.4 kw: $40.' The chapter also states in § 122-2G(1)(a): 'Any item required to have a permit not listed in fees: All subcodes: $125.' | § 122-2 Fees; G. Minimum fee | 2025 | https://ecode360.com/13977161
New Jersey | Union | Rahway | 3403961530 | Permit |  |  | "Plan review. The fee for plan review shall be 25% of the amount to be charged for the construction permit..." and "For complete installation, replacement or conversion of heating ventilation/air-conditioning equipment, boilers and furnaces: $75." The chapter also lists electrical fees and includes an average field rating entry for "Geothermal: kw range of 3.8 to 19.2; and heat pump, 2.6 to 7.4 kw." | § 177-3 Fees | 2026 | https://ecode360.com/9583051
New Mexico | Eddy | Carlsbad | 3512150 | Definition: Geothermal Heat Pump |  |  | "Geothermal energy system. A geothermal energy collection and conversion device that produces electricity or other form of energy primarily used for heating/cooling." | SEC. 56-31. DEFINITIONS. | 2017 | https://irp.cdn-website.com/f12fb9e8/files/uploaded/Chapter-56-Zoning-Ordinance-2017.pdf
New York | Broome | Binghamton | 3600706618 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY - Thermal energy generated and stored in the Earth" | SECTION III. DEFINITIONS | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Definition: Geothermal Heat Pump |  |  | "There are several types of geothermal systems, also known as 'ground source heating pumps'. They include closed loop, open loop, and direct exchange systems and are distinguished by the type of ground heat exchange (GHX) installed in the earth for heat transfer." | Part IV, A. Permitting Geothermal Systems | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal energy systems shall be located a minimum distance of 25 feet from any property line." | Part IV, B.4(b) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Building Foundation | 10 | feet | "All geothermal energy systems shall be located a minimum distance of... Ten feet from any building foundation." | Part IV, B.4(d)(ii) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Wastewater | 100 | feet | "All geothermal energy systems shall be located a minimum distance of... Seventy-five feet from any sewage disposal structure, such as a septic tank or cesspool or leaching field, except a supply well in an open loop system shall be a minimum of one hundred feet from such sewage disposal structure." | Part IV, B.4(d)(v) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Public Water | 100 | feet | "All geothermal energy systems shall be located a minimum distance of... One hundred feet from potable water wells" | Part IV, B.4(d)(vi) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Fuel (below ground) | 25 | feet | "All geothermal energy systems shall be located a minimum distance of... Twenty-five feet from any potential source of contamination, such as underground fuel tanks, except a supply well in an open loop system shall be a minimum of 50 feet from such potential source of contamination." | Part IV, B.4(d)(iii) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Water Lines | 10 | feet | "All geothermal energy systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | Part IV, B.4(d)(i) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Sewer Lines | 10 | feet | "All geothermal energy systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | Part IV, B.4(d)(i) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Setback - Water Bodies | 100 | feet | Permitted geothermal systems must be those that are "not proposed to be located within" a "Freshwater wetland or within 100 feet landward of the aforementioned" and a "Regulated freshwater surface water body." | Part IV, A.5(f)(ii)-(iii) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Maximum Well Depth | 20 | feet | "All horizontal closed-loop systems shall be no more than 20 feet deep." This depth limit is repeated in the setbacks section: "All horizontal closed-loop systems shall be no more than 20 feet deep." | Part IV, B.2(b)(v); B.4(a) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Permit |  |  | "Geothermal energy systems shall be permitted, installed, and erected within the Town pursuant to a building permit... no building permit shall be issued to construct a geothermal energy system until all other applicable permits have been secured." Also, "All permit applications shall be submitted to the Code Enforcement Officer on forms it provides." | Part IV, A.4; Part IV, B.1 | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Inspection |  |  | The ordinance requires "on or before final inspection, certification by the design engineer and/or installer that the geothermal system was installed as designed" and states that "The individual piping loops and circuits, and fully constructed piping network for all geothermal systems shall be pressure tested for integrity of original material and joints prior to backfill." | Part IV, B.1(d); B.2(a)(i)1 | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Certification |  |  | Permit applications must include "Certification by the design engineer and/or installer that the geothermal system complies with all applicable regulations" and, before final inspection, "certification by the design engineer and/or installer that the geothermal system was installed as designed." Applications also require "an engineering analysis... certified by a licensed professional engineer." For closed-loop systems, "Closed loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer," and borefields over 50 tons "must be designed by an IGSHPA certified geothermal designer." For open loop systems, contractors "must be registered with the NYSDEC." For DX systems, contractors must show they "completed a DX system installers training course and are certified by an applicable equipment and material manufacturer." | Part IV, B.1(c)-(d), (f); B.2(b)(i)-(ii); B.2(c)(i); B.2(d)(i) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned... The owner shall remove the abandoned system at his/her expense... after obtaining a demolition permit." "Closed loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends." "Open loop wells shall be decommissioned per NYSDEC requirements." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout..." and "Water body geothermal systems shall be completely removed from the bottom of the body of water." | Part IV, B.5 | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Broome | Binghamton | 3600706618 | Other Prohibitions/Regulations |  |  | Permitted geothermal systems must be those that are "not proposed to be located within" specified sensitive areas, including "Freshwater wetland or within 100 feet landward," "Regulated freshwater surface water body," "Coastal erosion hazard areas," "Historic... resources," "Identified wellhead protection areas and aquifer protection districts," and "Lake Protection Overlay District." The ordinance also states: "Discharge of water from open loop systems into storm or sanitary sewer systems shall be prohibited, except upon written approval..."; "Discharge of water from open loop systems into a waterway or freshwater wetland is not allowed unless approved..."; and "The use of open loop systems within identified wellhead protection areas is prohibited." | Part IV, A.5(f); B.2(c)(vii)1-2, (x) | 2020 | https://townofbinghamton.com/wp-content/uploads/2020/10/TOB-Draft-Solar-Law-REV.-8-31-20-.pdf
New York | Clinton | Plattsburgh | 3601958585 | Screening |  |  | Section 5.2 G.1: "At-grade electrical transformers and HVAC equipment shall be screened from public view by a solid visual barrier." Section 5.2 G.2: "To the maximum extent practical, all roof-mounted and ground-mounted mechanical equipment shall be screened from view or isolated so as not to be visible from any public right-of-way or residential district within 150 feet of the subject lot... Roof screens, when used, shall be coordinated with the building to maintain a unified appearance." Section 5.14 D.6.a-b: "All off-street loading, service, dumpster or mechanical equipment areas shall be located in the rear or side of the building and screened from view from the public right-of-way... Dumpster areas and mechanical equipment shall be screened from view by a wall of landscaping or screening walls on at least three sides which is equal or more in height to the equipment being screened." Section 5.14 D.8.b: "Mechanical equipment such as HVAC heating and cooling installed on rooftops shall be fully screened from view from adjacent public right of ways, properties and pedestrian walkways with the use of parapets or sloped parapet roof designs." Section 5.14 E.1.d(1): "Rooftop mechanical equipment... should be screened so as to not be visible from public view from adjoining roadways. Screening should consist of architecturally compatible materials, parapets, sloped roof form or walls that are at least as high as the equipment being screened." | Section 5.2 G. Mechanical equipment; Section 5.14 D.6 Equipment Screening; Section 5.14 D.8.b Roof-Mounted Mechanical Equipment; Section 5.14 E.1.d Specialty equipment |  | https://www.townofplattsburghny.gov/wp-content/uploads/2026/04/2026-Zoning-Ordinance.pdf
New York | Dutchess | Rhinebeck | 3602761357 | Permit |  |  | "All other uses and activities that are permitted in the applicable underlying zoning district shall be permitted in the aquifer protection area, provided that a special use permit is issued by the Planning Board..." and "Each application submitted to the Town for the establishment of a use or the development of land and/or buildings and structures within the aquifer protection area shall include identification of any necessary federal, state or county permits, copies of all such permit applications and copies of all related correspondence between the applicant and the permitting agency or agencies." Also, for open-loop geothermal wells: "Open-loop geothermal wells shall be in compliance with the New York State DEC's requirements governing injection wells and/or the United States EPA's Class V well injection program requirements found in 40 CFR Part 146, Underground Injection Control Program: Criteria and Standards." | § 125-54(D)(2) and § 125-54(D)(3) | 2019 | https://ecode360.com/14083825
New York | Dutchess | Rhinebeck | 3602761357 | Decommissioning |  |  | "Any well that is abandoned, meaning that its use has been permanently discontinued, or which is in a state of disrepair such that it cannot be used for its intended purpose or for observation purposes, shall be sealed in accordance with the requirements of the Dutchess County Department of Health." | § 125-54(D)(1)(q) | 2019 | https://ecode360.com/14083825
New York | Jefferson | Henderson | 3604534055 | Definition: Geothermal Heat Pump |  |  | "The following are accessory uses and structures that are permitted in all zoning districts and to any lot size without the need of review by the planning board: ... wells for heat pumps ..." | SCEDULE II Permitted Principal, Permitted Accessory & Special Uses | 2019 | https://www.townofhendersonny.org/uploads/6/0/3/1/60311435/zoning_laws_2020.pdf
New York | Jefferson | Le Ray | 3604542015 | Setback - Yards | 10 | feet | "All components of geothermal energy systems, including pumps, borings and loops, shall be set back at least five feet from side lot lines and at least 10 feet from rear lot lines." | § 158-128B(1) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Setback - Building Foundation | 10 | feet | "All borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off site." | § 158-128B(2) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Noise Limits | 50 | dBA | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less." | § 158-128B(5) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Permit |  |  | "A building permit shall be obtained from the Jefferson County Fire Prevention and Building Codes Department for any geothermal energy system prior to installation." "Borings for vertical systems are subject to any and all required approvals and permits from the NYSDEC Division of Waters the New York State Department of Health." | § 158-128E Permits | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less." "In addition to screening for noise control, geothermal energy systems are considered mechanical equipment and are subject to screening by landscaping, fencing or other methods to enhance the view." | § 158-128B(5) and (6) Design standards | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Certification |  |  | "Geothermal energy systems shall be certified by Underwriters' Laboratories, Inc., and shall meet the requirements of the New York State Building Code as adopted by the Town of LeRay." | § 158-128C Standards and certifications | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance." "Upon notice to the owner by the Zoning Enforcement Officer, within 180 days the owner shall remove the abandoned system at his/her expense..." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." "Geothermal energy systems shall be completely removed from the bottom of any water body." | § 158-128D Abandonment | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems utilizing heat transfer fluids as defined in Article I are permitted. Open-loop geothermal energy systems are not permitted." | § 158-128A(1) Applicability | 2021 | https://ecode360.com/29145485
New York | Jefferson | Le Ray | 3604542015 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems in water bodies owned or managed by the Town of LeRay are not permitted." | § 158-128A(3) Applicability | 2021 | https://ecode360.com/29145485
New York | Jefferson | Watertown | 3604578619 | Other Prohibitions/Regulations |  |  | "Equipment, piping, and all other devices shall not be located in any easement or right-of-way." | Sec. 310-56 Geothermal Energy Systems | 2023 | https://www.watertown-ny.gov/media/PlanningZoning/Zoning%20Ordinance/2023%20Feb%20FINAL_Full%20Ordinance_small.pdf
New York | Jefferson | Wilna | 3604582348 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEMS Are a system of ground-source heat pumps that can also be designed as direct exchange systems, which circulate a refrigerant through a copper pipe instead of a typical ground loop. Direct exchange systems are highly efficient at heat extraction and rejection." | ARTICLE III DEFINITIONS | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Setback - Property Lines | 10 | feet | "All components of geothermal energy systems, including pumps, borings and loops, shall be set back at least five feet from side lot lines and at least 10 feet from rear lot lines." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Setback - Building Foundation | 10 | feet | "All borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off site." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Noise Limits | 50 | dBA | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Permit |  |  | "A building permit shall be obtained from the Town of Wilna Code Enforcement Officer." Also, "Borings for vertical systems are subject to any and all required approvals and permits from the NYSDEC Division of Water and the New York State Department of Health." | Section 740 Energy Systems, A. Geothermal energy systems, 5. Permits | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts." Also, "In addition to screening for noise control, geothermal energy systems are considered mechanical equipment and are subject to screening by landscaping, fencing or other methods to enhance the view." | Section 740 Energy Systems, A. Geothermal energy systems, 2. Design standards | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Certification |  |  | "Geothermal energy systems shall be certified by Underwriters' Laboratories, Inc., and shall meet the requirements of the New York State Building Code as adopted by the Town of Wilna." | Section 740 Energy Systems, A. Geothermal energy systems, 3. Standards and certifications | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance." "Upon notice to the owner by the Zoning Enforcement Officer, within 180 days the owner shall remove the abandoned system at his/her expense after a hearing by the Wilna Town Board." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." "Geothermal energy systems shall be completely removed from the bottom of any water body." | Section 740 Energy Systems, A. Geothermal energy systems, 4. Abandonment | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems utilizing heat transfer fluids as defined in Article I arc permitted. Open-loop geothermal energy systems are not permitted." | Section 740 Energy Systems, A. Geothermal energy systems, 1. Applicability | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Jefferson | Wilna | 3604582348 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems in water bodies owned or managed by the Town of Wilna are not permitted." | Section 740 Energy Systems, A. Geothermal energy systems, 1. Applicability | 2024 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B20D0439C-0000-C22D-9306-587CFB81CD96%7D&DocTitle=Statement%20of%20Compliance%20Wilna
New York | Lewis | Croghan | 3604919081 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL CLOSED-LOOP SYSTEM: Closed-loop systems use a ground loop (typically made of polyethylene or PVC piping) that circulates water or antifreeze to exchange heat with the ground or a groundwater source..."; "GEOTHERMAL ENERGY SYSTEMS: Are a system of ground-source heat pumps that can also be designed as direct exchange systems, which circulate a refrigerant through a copper pipe instead of a typical ground loop."; "GEOTHERMAL OPEN-LOOP SYSTEM: Open-loop systems circulate water for heat extraction and rejection directly from local groundwater sources." | ARTICLE III. DEFINITIONS | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Setback - Property Lines | 10 | feet | "All components of geothermal energy systems, including pumps, borings and loops, shall be set back at least five feet from side lot lines and at least 10 feet from rear lot lines." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Setback - Building Foundation | 10 | feet | "All borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off site." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Noise Limits | 50 | dBA | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Permit |  |  | "A building permit shall be obtained from the Lewis County Code Enforcement Officer."; "Borings for vertical systems are subject to any and all required approvals and permits from the NYSDEC Division of Water and the New York State Department of Health." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels as measured at the property boundary to 50 decibels or less as to mitigate adverse noise impacts."; "In addition to screening for noise control, geothermal energy systems are considered mechanical equipment and are subject to screening by landscaping, fencing or other methods to enhance the view." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Certification |  |  | "Geothermal energy systems shall be certified by Underwriters' Laboratories, Inc., and shall meet the requirements of the New York State Building Code as adopted by the Town of Croghan." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance." "Upon notice to the owner by the Zoning Enforcement Officer, within 180 days the owner shall remove the abandoned system at his/her expense after a hearing by the Croghan Town Board" including: "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted"; and "Geothermal energy systems shall be completely removed from the bottom of any water body." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems utilizing heat transfer fluids as defined in Article XII are permitted. Open-loop geothermal energy systems are not permitted." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Lewis | Croghan | 3604919081 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems in water bodies owned or managed by the Town of Croghan are not permitted unless municipally owned/operated." | Section 1020 Geothermal Energy Systems | 2025 | https://lewiscountyny.gov/wp-content/uploads/2025/01/T-Croghan-25-1-Zoning-Law-Update.pdf
New York | Monroe | Penfield | 3605557144 | Definition: Geothermal |  |  | "GEOTHERMAL, HEAT TRANSFER FLUID — Nontoxic, food-grade or United States Pharmacopeia (USP)-grade fluids of potable water or aqueous solution of propylene glycol not to exceed 25% by weight." | Section 3. Amendment to Section 250-2.2 Terms Defined | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — A system that harnesses the relatively constant temperature of the earth or a body of water to provide space heating and/or cooling. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." | Section 3. Amendment to Section 250-2.2 Terms Defined | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Setback - Building Foundation | 10 | feet | "All vertical borings and loops shall be set back at least 10 feet from the foundation of any structure, either on or off-site." | D. Geothermal Energy Systems (GES) - General Requirements | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Maximum Well Depth | 150 | feet | "All vertical boring shall be limited to a depth of 150 feet from the surface elevation." | D. Geothermal Energy Systems (GES) - General Requirements | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Permit |  |  | "Borings for vertical systems are subject to any and all required approvals and permits from the NYS Department of Environmental Conservation, NYS Department of Health, and any other applicable state or federal agencies." Also, "When a GES is included as part of a proposed development that requires a site plan or the GES' area of disturbance triggers site plan approval set forth in 250, Planning Board review and approval shall be required." | D. Geothermal Energy Systems (GES) - Additional Permitting Required | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Screening |  |  | "Geothermal heat pumps shall be screened to reduce noise levels..." Also, "GES equipment outside of structures should be located and/or screened in a way that minimizes views of the equipment." | D. Geothermal Energy Systems (GES) - General Requirements; Site Plan Application Required | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Decommissioning |  |  | "If a GES remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and the following decommissioning actions are required. [1] The heat pump and any external mechanical equipment shall be removed. [2] Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil, or boring shall be uncovered and grouted. [3] All GES components shall be completely removed from any water body." | D. Geothermal Energy Systems (GES) - Abandonment | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Penfield | 3605557144 | Open-loop Prohibitions |  |  | "Only Closed-loop GES that utilize heat transfer fluids as defined in 250-2.2 are permitted. Open-loop GES, as defined in 250-2.2, are not permitted." | D. Geothermal Energy Systems (GES) - Applicability | 2025 | https://ecode360.com/PE0095/laws/LF2302652.pdf
New York | Monroe | Perinton | 3605557221 | Setback - Property Lines | 5 | feet | "All ground-mounted exterior mechanical devices, such as air conditioners, heat pumps, and generators, must be located in a side or rear yard, no closer than five feet from a property line." | § 208-14M(2)(a) | 2024 | https://ecode360.com/6741309
New York | Monroe | Perinton | 3605557221 | Screening |  |  | "All ground-mounted exterior mechanical devices, such as commercial refuse containers, ventilating and air-conditioning units (except window and wall units), shall be enclosed and/or screened." | § 208-14M(1)(a) | 2024 | https://ecode360.com/6741309
New York | Monroe | Pittsford | 3605558365 | Definition: Geothermal Heat Pump |  |  | "Geothermal system for heating and or cooling. Subject to § 185-113C(4)." | § 185-113A(19) Accessory uses and structures |  | https://ecode360.com/48538733
New York | Monroe | Pittsford | 3605558365 | Setback - Property Lines | 10 | feet | "All accessory uses and structures shall follow the primary structure minimum setback requirements of the zoning district in which it is located, with the following exceptions: ... (c) Geothermal systems must maintain a minimum setback of 10 feet from all property lines." | § 185-113C(4)(c) Size and location restrictions |  | https://ecode360.com/48538733
New York | Niagara | Royalton | 3606364034 | Definition: Geothermal Heat Pump |  |  | "ALTERNATE ENERGY SYSTEMS: Structures, equipment, devices or construction techniques used for the production of heat, light, cooling, electricity or other forms of energy on a site and may be attached to or separate from the principal structure. Current examples include windmills, solar collectors, solar greenhouses, heat pumps or other related devices. For the purposes of this Local Law, this definition shall apply to individual residences or businesses; commercial generating plants are excluded." | Section 210 Definitions | 2008 | https://www.niagaracountybusiness.com/file-library/100219/town_royalton_zoning_ordinance.pdf
New York | Oneida | Utica | 3606576540 | Inspection |  |  | "The systems shall be tested hydrostatically at 1 1/2 times the maximum system design pressure, but not less than 100 psi. The duration of each test shall not be less than 15 minutes. All geothermal systems must be pressure checked to the original standard by a licensed geothermal contractor every three years from the certification system date. Results from the test shall be submitted to the Building Department. No person shall operate a system if a test reveals that it is likely to leak the heat transfer liquid." | Sec. 2-29-350(c)(2) Geothermal energy systems | 2024 | https://ecode360.com/14017100
New York | Oneida | Utica | 3606576540 | Certification |  |  | "Applicant shall submit a certificate of compliance demonstrating that the proposed system has been tested and approved by Underwriters Laboratories (UL) or other approved independent testing agency." | Sec. 2-29-350(c)(1) Geothermal energy systems | 2024 | https://ecode360.com/14017100
New York | Oneida | Utica | 3606576540 | Open-loop Prohibitions |  |  | "Open loop geothermal systems. No person shall install or maintain an open loop geothermal system within the City." | Sec. 2-29-350 Geothermal energy systems | 2024 | https://ecode360.com/14017100
New York | Orleans | Yates | 3607383448 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEMS: Structures, equipment, devices or construction techniques used for the production of heat, light, cooling, electricity or other forms of energy on site and may be attached to or separate from the principal structure. Current examples include windmills, solar collectors and solar greenhouses, heat pumps, or other related devices. For the purposes of this Local Law, this definition shall apply to individual residences and businesses. Commercial generating plants, the prime function of which is selling energy, are excluded." | SECTION 210 DEFINITIONS | 2016 | https://www.townofyates.org/Forms/Yates%20Zoning%20Book%20Revised.pdf
New York | Orleans | Yates | 3607383448 | Permit |  |  | "No building or structure shall be erected, enlarged, structurally altered or moved, no new use shall be established, and no building permit shall be granted pursuant to the Codes of New York State, until a zoning permit therefore has been issued by the Zoning Officer." | SECTION 300 PERMITS REQUIRED | 2016 | https://www.townofyates.org/Forms/Yates%20Zoning%20Book%20Revised.pdf
New York | Orleans | Yates | 3607383448 | Inspection |  |  | "The applicant shall notify the Zoning Enforcement Officer when the structure or use is ready for final inspection. The Zoning Enforcement Officer shall then make a final inspection. If satisfied that the regulations pertaining to the project have been complied with and that the project has been completed as specified on the approved application, the Zoning Enforcement Officer shall issue a certificate of Zoning Compliance granting permission to occupy or use the structure." | SECTION 306 CERTIFICATE OF ZONING COMPLIANCE | 2016 | https://www.townofyates.org/Forms/Yates%20Zoning%20Book%20Revised.pdf
New York | Saratoga | Ballston | 3609104220 | Definition: Geothermal |  |  | "There are several types of Geothermal Systems, also known as Ground Source Heat Pumps. They include Closed Loop, Open Loop, and Direct Exchange systems and are distinguished by the type of Ground Heat Exchanger (GHX) installed in the earth for heat transfer." | § 57-1(B) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Definition: Geothermal Heat Pump |  |  | "There are several types of Geothermal Systems, also known as Ground Source Heat Pumps. They include Closed Loop, Open Loop, and Direct Exchange systems and are distinguished by the type of Ground Heat Exchanger (GHX) installed in the earth for heat transfer." | § 57-1(B) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Property Lines | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Property line" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Building Foundation | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Building foundation" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Wastewater | 75 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Sewage disposal structure, e.g., septic tank, cesspool" requires: Closed Loop and DX Systems: "25"; Open Loop Supply Well <45 gpm: "50"; Open Loop Supply Well >45 gpm: "75"; Open Loop Return Well <45 gpm: "25"; Open Loop Return Well >45 gpm: "50." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Private Water | 100 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Private water supply well" requires: Closed Loop and DX Systems: "25"; Open Loop Supply Well <45 gpm: "25"; Open Loop Supply Well >45 gpm: "50"; Open Loop Return Well <45 gpm: "50"; Open Loop Return Well >45 gpm: "100." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Public Water | 200 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Public water supply well" requires: Closed Loop and DX Systems: "100"; Open Loop Supply Well <45 gpm: "100"; Open Loop Supply Well >45 gpm: "100"; Open Loop Return Well <45 gpm: "200"; Open Loop Return Well >45 gpm: "200." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Water Lines | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "On-site utility, sewage and water line, lined catch basin" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Sewer Lines | 10 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "On-site utility, sewage and water line, lined catch basin" requires "10" feet for Closed Loop and DX Systems, Open Loop Supply Well <45 gpm, Open Loop Supply Well >45 gpm, Open Loop Return Well <45 gpm, and Open Loop Return Well >45 gpm. | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Setback - Hazardous Materials/Fertilizers | 50 | feet | In the table "Setbacks and Separation Distances for Geothermal Systems (in feet)," the row for "Potential source of contamination, e.g. underground petroleum storage tank, chemical use and waste storage area, etc." requires: Closed Loop and DX Systems: "25"; Open Loop Supply Well <45 gpm: "25"; Open Loop Supply Well >45 gpm: "50"; Open Loop Return Well <45 gpm: "25"; Open Loop Return Well >45 gpm: "25." | § 57-3(D) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Minimum Well Depth | 20 | feet | "An open loop system where the depth to groundwater is at least 20 feet below the surface." | § 57-2(B)(3) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Permit |  |  | "Geothermal systems may be permitted, installed, and erected pursuant to a building permit" and "Permit applications shall be submitted to the Building Department on forms it provides." | § 57-2(A); § 57-3(A) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Inspection |  |  | "The individual piping loops, circuits, and fully constructed piping network for all Geothermal Systems shall be pressure tested for integrity of original material and joints prior to backfill in accordance with the manufacturer's instructions and the governing standards or guidelines." | § 57-3(A)(2)(a)[1] | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Licensed Driller |  |  | "Open Loop system contractors must be registered by NYSDEC for drilling and installing wells and installing and start-up of submersible pumps." | § 57-3(A)(2)(c)(1) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Certification |  |  | "Certification of (1) through (5) above must be performed by a licensed Professional Engineer." "Closed Loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques." "Closed Loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA Certified Geothermal Designer in good standing with IGSHPA." "DX system contractors shall demonstrate they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | § 57-3(A)(1)(a)[6]; § 57-3(A)(2)(b)(1)-(2); § 57-3(A)(2)(d)(1) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Decommissioning |  |  | "If the Geothermal System remains nonfunctional or inoperative for a continuous period of one year, the Building Inspector may require that the buried ground heat exchanger be taken out of service by the property owner." "Closed Loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends. If the heat transfer fluid contains regulated materials (e.g., antifreeze, biocides, or corrosion inhibitors), the heat transfer fluid shall be contained and disposed of in accordance with applicable regulations." "Open Loop wells shall be decommissioned per NYSDEC requirements." | § 57-3(C) | 2025 | https://ecode360.com/49590886
New York | Saratoga | Ballston | 3609104220 | Other Prohibitions/Regulations |  |  | Geothermal systems eligible for a building permit must satisfy the criterion that the system "Is not proposed to be located within the following areas of potential sensitivity:" "100-year flood hazard zones considered V or AE zone on the FEMA Flood Maps," "Tidal or freshwater wetland," "Regulated tidal or freshwater surface water body," and "Coastal erosion hazard area." | § 57-2(B)(7); § 57-2(C) | 2025 | https://ecode360.com/49590886
New York | Seneca | Fayette | 3609925505 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEMS: Structures, equipment, devices, or construction techniques used for the production of heat, light, cooling, electricity, or other forms of energy on site and may be attached to or separate from the principal structure. Current examples include wind turbines, solar collectors and solar greenhouses, heat pumps, wind-powered air compressors, or other related devices." | SECTION 210 DEFINITIONS | 2018 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B95110B70-ABD5-4ECC-BD43-A56D00C37638%7D
New York | Seneca | Fayette | 3609925505 | Permit |  |  | "No building or structure shall be erected, enlarged, structurally altered or moved, no new use shall be established, and no building permit shall be issued ... until a land use permit therefore has been issued by the Land Use Officer. No alterations to an existing building shall be made without a land use permit, unless pursuant to the New York State Uniform Fire Prevention and Building Code such alterations do not require a building permit." | SECTION 301 PERMITS REQUIRED | 2018 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B95110B70-ABD5-4ECC-BD43-A56D00C37638%7D
New York | Seneca | Fayette | 3609925505 | Inspection |  |  | "The applicant shall notify the Land Use Officer when the structure and/or land use is ready for final inspection. The Land Use Officer shall then make a final inspection. If satisfied that the standards, conditions and regulations pertaining to the project have been complied with ... the Land Use Officer shall issue a certificate of compliance..." | SECTION 307 CERTIFICATE OF COMPLIANCE | 2018 | https://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B95110B70-ABD5-4ECC-BD43-A56D00C37638%7D
New York | Suffolk | Brookhaven | 3610310000 | Definition: Geothermal Heat Pump |  |  | "There are several types of geothermal systems, also known as 'ground source heating pumps,' typically used on Long Island for space heating and cooling. They include closed loop, open loop, and direct exchange systems and are distinguished by the type of ground heat exchange (GHX) installed in the earth for heat transfer." | § 85-808B | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 25 feet from any property line." | § 85-810D(2) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Setback - Building Foundation | 10 | feet | "All geothermal systems shall be located a minimum distance of... Ten feet from any building foundation." | § 85-810D(4)(b) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Setback - Wastewater | 75 | feet | "All geothermal systems shall be located a minimum distance of... Fifty feet from any sewage disposal structure, such as a septic tank or cesspool or leaching field, except a supply well in an open loop system shall be a minimum of 75 feet from such sewage disposal structure." | § 85-810D(4)(e) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Setback - Fuel (below ground) | 25 | feet | "All geothermal systems shall be located a minimum distance of... Twenty-five feet from any potential source of contamination, such as underground fuel tanks, except a supply well in an open loop system shall be a minimum of 50 feet from such potential source of contamination." | § 85-810D(4)(c) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Setback - Water Lines | 10 | feet | "All geothermal systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | § 85-810D(4)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Setback - Sewer Lines | 10 | feet | "All geothermal systems shall be located a minimum distance of... Ten feet from any water, sewage or utility line." | § 85-810D(4)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Maximum Well Depth | 20 | feet | "All horizontal closed-loop systems shall be no more than 20 feet deep." The same limit is repeated in setbacks: "All horizontal closed-loop systems shall be no more than 20 feet deep." | § 85-810B(2)(f); § 85-810D(1) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Permit |  |  | "Geothermal energy systems shall be permitted, installed, and erected within the Town pursuant to a building permit so long as they meet the provisions of this article and all applicable sections of the Town Code. Further, no building permit shall be issued to construct a geothermal energy system until all other applicable permits have been secured." Also, "Geothermal energy systems shall be constructed pursuant to a building permit so long as the geothermal energy system meets the criteria set forth in § 85-810, subject to obtaining all other necessary approvals." | § 85-808E; § 85-809A | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Inspection |  |  | "Subsequent to installation and on or before final inspection, certification by the design engineer and/or installer that the geothermal system was installed as designed..." and "The individual piping loops and circuits, and fully constructed piping network for all geothermal systems shall be pressure tested for integrity of original material and joints prior to backfill..." | § 85-810A(4); § 85-810B(1)(a)[1] | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Licensed Driller |  |  | "Open loop system contractors must be registered with the NYSDEC for drilling and installing wells and installing and start-up of submersible pumps..." | § 85-810B(3)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Certification |  |  | "Closed loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques..."; "Closed loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA certified geothermal designer in good standing with the IGSHPA."; "DX system contractors shall demonstrate that they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | § 85-810B(2)(a); § 85-810B(2)(b); § 85-810B(4)(a) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned... The owner shall remove the abandoned system at his/her expense... after obtaining a demolition permit." "Closed loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends." "Open loop wells shall be decommissioned per NYSDEC requirements." "The heat pump and any external mechanical equipment shall be removed." "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid..." | § 85-811 | 2026 | https://ecode360.com/8598848
New York | Suffolk | Brookhaven | 3610310000 | Open-loop Prohibitions |  |  | "The use of open loop systems within identified wellhead protection areas is prohibited." | § 85-810B(3)(j) | 2026 | https://ecode360.com/8598848
New York | Suffolk | Shelter Island | 3610366839 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A geothermal system uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings. It shall include both open-loop geothermal and closed-loop geothermal systems." | § 74-4 Definitions | 2009 | https://ecode360.com/13841397
New York | Suffolk | Shelter Island | 3610366839 | Decommissioning |  |  | "Any person... who installs such a geothermal system in violation of this prohibition shall immediately remove the system and be liable for a penalty of $1,000 per day until such system is removed." | § 74-6 Penalties for offenses | 2009 | https://ecode360.com/13841397
New York | Suffolk | Shelter Island | 3610366839 | Closed-loop Prohibitions |  |  | "The installation of a geothermal system is prohibited in the Town of Shelter Island." Section 74-4 defines "GEOTHERMAL SYSTEM" to "include both open-loop geothermal and closed-loop geothermal systems." | § 74-5 Installation prohibited | 2009 | https://ecode360.com/13841397
New York | Suffolk | Shelter Island | 3610366839 | Open-loop Prohibitions |  |  | "The installation of a geothermal system is prohibited in the Town of Shelter Island." Section 74-4 defines "GEOTHERMAL SYSTEM" to "include both open-loop geothermal and closed-loop geothermal systems." | § 74-5 Installation prohibited | 2009 | https://ecode360.com/13841397
New York | Suffolk | Smithtown | 3610368000 | Definition: Geothermal Heat Pump |  |  | "There are several types of geothermal systems, also known as 'ground source heat pumps,' typically used on Long Island for space heating and cooling. They include: closed loop, open loop, and direct exchange systems and are distinguished by the type of ground heat exchanger (GHX) installed in the earth for heat transfer." | § 112-1.4A(2) | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Property Lines | 10 | feet | The setbacks table lists "Property line" with a separation distance of 10 feet across the geothermal system categories shown. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Building Foundation | 10 | feet | The setbacks table lists "Building foundation" with a separation distance of 10 feet for the geothermal system categories shown. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Wastewater | 75 | feet | The setbacks table includes "Sewage disposal structure, e.g., septic tank, cesspool" with values of 25 feet for several system categories, 50 feet for one >45 gpm category, and 75 feet for an open-loop category. It also includes "Stormwater recharge structure, e.g., leach field, unlined catch basin" with values up to 50 feet. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Private Water | 100 | feet | The setbacks table lists "Private water supply well" with distances of 25 feet for closed loop and DX systems, 50 feet for some open-loop categories, and 100 feet for the most restrictive open-loop category (>45 gpm return well). | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Public Water | 200 | feet | The setbacks table lists "Public water supply well" with distances of 100 feet for closed loop and DX systems and for some open-loop categories, and 200 feet for the more restrictive open-loop categories (>45 gpm). | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Water Lines | 10 | feet | The setbacks table lists "On-site utility, sewage and water line, lined catch basin" with a separation distance of 10 feet across all shown geothermal system categories. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Sewer Lines | 10 | feet | The setbacks table lists "On-site utility, sewage and water line, lined catch basin" with a separation distance of 10 feet across all shown geothermal system categories. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Setback - Hazardous Materials/Fertilizers | 50 | feet | The setbacks table lists "Potential source of contamination; e.g., underground petroleum storage tank, chemical use and waste storage area, etc." with values of 25 feet in several categories and 50 feet in some open-loop categories. | § 112-1.4C(4) Setbacks and separation distances | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Permit |  |  | "Geothermal systems may be permitted, installed, and erected pursuant to a building permit" and "Permit applications shall be submitted to the Building Department on forms it provides" with required materials including a plot plan, engineer/installer certifications, and for open loop systems a one-line electrical diagram. | § 112-1.4B(1); § 112-1.4C(1)(a) | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Inspection |  |  | "The individual piping loops, circuits, and fully constructed piping network for all geothermal systems shall be pressure tested for integrity of original material and joints prior to backfill in accordance with the manufacturer’s instructions and the governing standards or guidelines." | § 112-1.4C(1)(b)[1][a] | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Licensed Driller |  |  | "Open loop system contractors must be registered by NYSDEC for drilling and installing wells and installing and start-up of submersible pumps." | § 112-1.4C(1)(b)[3][a] | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Certification |  |  | "Certification of Subsection C(1)(a)[1] through [5] above must be performed by a licensed professional engineer." "Closed loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques." "Closed loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA certified geothermal designer in good standing with IGSHPA." "DX system contractors shall demonstrate they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | § 112-1.4C(1)(a)[6]; § 112-1.4C(1)(b)[2]-[4] | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the Chief Building Inspector may require that the buried ground heat exchanger be taken out of service by the property owner." "Closed loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends." "Open loop wells shall be decommissioned per NYSDEC requirements." | § 112-1.4C(3) | 2026 | https://ecode360.com/15097677
New York | Suffolk | Smithtown | 3610368000 | Other Prohibitions/Regulations |  |  | "Discharge of water from open loop systems into storm or sanitary sewer systems shall be prohibited, except upon written approval by the SCDHS, NYSDEC, or other authority having jurisdiction." "Discharge of water from open loop systems into a waterway or tidal or freshwater wetland is not allowed unless approved by applicable federal, state, and local authorities." | § 112-1.4C(1)(b)[3][g][i]-[ii] | 2026 | https://ecode360.com/15097677
New York | Sullivan | Cochecton | 3610516661 | Definition: Geothermal Heat Pump |  |  | "Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. A geothermal energy system consists of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump." | § 240-25 Renewable energy systems, B. Special definitions | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | 3610516661 | Setback - Property Lines | 5 | feet | "Renewable energy systems are not permitted within 10 feet of any property line or 35 feet of the front lot line, except for underground systems, which may extend to within five feet of a property line..." Geothermal systems are included within renewable energy systems, and underground systems receive the specific 5-foot property-line setback. | § 240-25 Renewable energy systems, C(4) Setbacks | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | 3610516661 | Setback - Yards | 35 | feet | "Renewable energy systems are not permitted within 10 feet of any property line or 35 feet of the front lot line, except for underground systems, which may extend to within five feet of a property line..." | § 240-25 Renewable energy systems, C(4) Setbacks | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | 3610516661 | Permit |  |  | "Building permits shall be required for all renewable energy system installations as defined herein." | § 240-25 Renewable energy systems, C(6) Permit requirements | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | 3610516661 | Inspection |  |  | "All renewable energy systems must be inspected and approved by a qualified third-party electrical inspector approved by the Town of Cochecton and, if connected to the local electric utility transmission grid, approved by the appropriate utility." | § 240-25 Renewable energy systems, C(2) Qualified installations | 2018 | https://ecode360.com/26992708
New York | Sullivan | Cochecton | 3610516661 | Other Prohibitions/Regulations |  |  | "No part of any such system shall be located within public rights-of-way." "...no portion of a geothermal system shall be located within a stream or the Upper Delaware River." "Vertical or deep-bore geothermal systems are not permitted within [designated water well protection] zones." | § 240-25 Renewable energy systems, D(1)-(2) Geothermal energy system standards | 2018 | https://ecode360.com/26992708
New York | Sullivan | Lumberland | 3610543786 | Setback - Roads | 10 | feet | "All components of a closed-loop ground-source heat pump system, including pumps, borings and loops, shall be set back at least five feet from interior side lot lines and at least 10 feet from front and rear lot lines." Read together with § 250-38B(4): aboveground equipment "shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way." | § 250-38B(3) Location of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | 3610543786 | Setback - Property Lines | 10 | feet | "All components of a closed-loop ground-source heat pump system, including pumps, borings and loops, shall be set back at least five feet from interior side lot lines and at least 10 feet from front and rear lot lines." | § 250-38B(3) Location of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | 3610543786 | Setback - Yards | 10 | feet | "All components of a closed-loop ground-source heat pump system, including pumps, borings and loops, shall be set back at least five feet from interior side lot lines and at least 10 feet from front and rear lot lines." In addition, "Aboveground equipment associated with a closed-loop ground-source heat pump system shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way..." | § 250-38B(3)-(4) Location of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | 3610543786 | Permit |  |  | "Closed-loop ground-source heat pump systems using a nontoxic and food-grade fluid as a heat transfer fluid are permitted in all districts. Installation of a closed-loop ground-source heat pump system requires a building permit." | § 250-38A(1) Site plan approval required | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | 3610543786 | Decommissioning |  |  | "If a closed-loop ground-source heat pump system remains nonfunctional or inoperative for a continuous period of 12 months, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove such system..." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed"; "Pipes and coils below the land surface shall be filled with grout to displace the heat transfer fluid..."; and "Pond and similar ground-source heat pump systems shall be completely removed from the body of water." | § 250-38C Abandonment and removal of ground-source heat pump system | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | 3610543786 | Open-loop Prohibitions |  |  | "Open-loop ground-source heat pump systems... are prohibited in every district within the Town." | § 250-38A(2) Site plan approval required | 2016 | https://ecode360.com/26934437
New York | Sullivan | Lumberland | 3610543786 | Other Prohibitions/Regulations |  |  | "...closed-loop ground-source heat pump systems utilizing a heat transfer fluid that is not a nontoxic and food- grade liquid are prohibited in every district within the Town." | § 250-38A(2) Site plan approval required | 2016 | https://ecode360.com/26934437
New York | Ulster | Denning | 3611120247 | Other Prohibitions/Regulations |  |  | "Restrictions: Geothermal Systems are permitted as long as it does not interfere with the groundwater aquifer and does not affect or contaminate the groundwater of surrounding properties." | §510 - GEOTHERMAL SYSTEMS | 2019 | https://www.denningny.gov/wp-content/uploads/2023/05/TOD-ZONING-LAW-2019.pdf
New York | Ulster | Rochester | 3611163011 | Definition: Geothermal Heat Pump |  |  | "Green energy/energy conservation/passive house development. ... The Planning Board shall certify the development incorporates sufficient energy conservation measures such as, but not limited to: LEED net zero construction, geothermal (ground source heat pump) or passive solar heating, and natural habitat preservation." | § 140-10. Lot development standards, B.3 Density Bonus | 2024 | https://ecode360.com/RO1435/laws/LF2209768.pdf
New York | Ulster | Woodstock | 3611183052 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP GEOTHERMAL SYSTEM. A geothermal system that continuously circulates water or a mixture of water and nontoxic, food-grade antifreeze through buried or submerged plastic pipes and passes the fluid through a heat exchange system. The loop is filled just once and the same water mixture is used again and again." "OPEN LOOP GEOTHERMAL SYSTEM. A geothermal system that withdraws water from an extraction well or body of water, passes the water through a heat exchange system, and discharges the temperature-altered water either into the ground in a discharge or return well or to the ground surface or into surface water." | § 260-40.a(F) Definitions | 2023 | https://woodstockny.gov/application/files/6917/6624/6982/Zoning_Edits_Accepted_October_3rd_2023.pdf
New York | Ulster | Woodstock | 3611183052 | Open-loop Prohibitions |  |  | The ordinance states that in the WDWP-O District, "the following uses and activities are specifically prohibited," including "Open loop geothermal systems." | § 260-40.a(D) Permitted and prohibited uses and activities in the Water District Wellhead Protection (WDWP-O) Overlay District | 2023 | https://woodstockny.gov/application/files/6917/6624/6982/Zoning_Edits_Accepted_October_3rd_2023.pdf
New York | Westchester | Peekskill | 3611956979 | Definition: Geothermal Heat Pump |  |  | "A Closed Loop system uses buried high-density polyethylene (HDPE) plastic piping installed in drilled and grouted boreholes that conductively exchanges thermal (heat) energy with the ground via circulating water or a water/antifreeze mixture through the piping system." "A Direct Exchange system uses buried copper tubing that conductively exchanges heat energy with the ground via circulating a refrigerant through the tubing." Also: "There are two types of Geothermal Systems, also known as Ground Source Heat Pumps, permitted to be used in the City of Peekskill, for space heating and cooling. They include: Closed Loop, and Direct Exchange systems and are distinguished by the type of Ground Heat Exchanger (GHX) installed in the earth for heat transfer." | Geothermal Systems, 1. Definitions / 2 |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Property Lines | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "Property Line — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Building Foundation | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "Building Foundation — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Wastewater | 25 | feet | Table entries for "Closed Loop and DX Systems" state: "Sewage Disposal Structure, e.g. septic tank, cesspool — 25*" and "Storm water Recharge Structure, e.g., leach field, unlined catch basin — 25." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Private Water | 25 | feet | Table entry for "Closed Loop and DX Systems" states: "Private water supply well — 25." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Public Water | 100 | feet | Table entry for "Closed Loop and DX Systems" states: "Public water supply well — 100*." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Water Lines | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "On-Site Utility, Sewage and Water Line, Lined Catch Basin — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Sewer Lines | 10 | feet | Table entry for "Closed Loop and DX Systems" states: "On-Site Utility, Sewage and Water Line, Lined Catch Basin — 10." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Setback - Hazardous Materials/Fertilizers | 25 | feet | Table entry for "Closed Loop and DX Systems" states: "Potential Source of contamination, e.g. Underground Petroleum Storage Tank, Chemical Use and Waste Storage Area, etc. — 25." | SETBACKS and SEPARATION Distances for Geothermal Systems (in feet) |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Permit |  |  | The ordinance provides: "Geothermal Systems may be permitted, installed, and erected pursuant to a building permit and subject to the project meeting all other requirements including compliance with applicable plumbing, electrical and mechanical codes." It further states: "Permitted Geothermal Systems eligible to receive a building permit are those that are of a system listed above and comply with the applicable General Requirements" and that permit applications "shall be submitted to the Building Department on forms it provides." | Geothermal Systems, 5.A-B; General Requirements, 1 |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Inspection |  |  | The ordinance states: "The individual piping loops, circuits, and fully constructed piping network for all Geothermal Systems shall be pressure tested for integrity of original material and joints prior to backfill in accordance with the manufacturer's instructions and the governing standards or guidelines." | 2. Design Standards and Guidelines, 2.A.a |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Certification |  |  | The ordinance requires specific credentials: "Certification of (a) through (d) above must be performed by a licensed Professional Engineer." It also states, "Closed Loop borefield installers must be trained and accredited by IGSHPA and certified by the piping manufacturer in polyethylene pipe heat-fusion or electro-fuse welding techniques, whichever is used." For larger systems, "Closed Loop borefields that will supply greater than 50 tons of heating/cooling capacity must be designed by an IGSHPA Certified Geothermal Designer in good standing with IGSHPA." For DX systems, "DX system contractors shall demonstrate they have successfully completed a DX system installers training course and are certified by an applicable equipment and material manufacturer to install DX systems." | General Requirements, 1.A.e; 3.A; 3.B; 4.A |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Westchester | Peekskill | 3611956979 | Decommissioning |  |  | "If the Geothermal System remains nonfunctional or inoperative for a continuous period of one year, the Building Director may require that the buried ground heat exchanger be taken out of service by the property owner." Also: "Closed Loop piping systems shall be decommissioned by flushing and filling the piping with potable water and capping off the ends. If the heat transfer fluid contains regulated materials (e.g., antifreeze, biocides, or corrosion inhibitors), the heat transfer fluid shall be contained and disposed of in accordance with applicable regulations." | 6. Decommissioning |  | https://www.cityofpeekskillny.gov/DocumentCenter/View/174/Geo-Thermal-Permit-Requirements-PDF
New York | Wyoming | Sheldon | 3612166773 | Definition: Geothermal Heat Pump |  |  | "ALTERNATIVE ENERGY SYSTEMS: Structures, equipment, devices or construction techniques used for the production of heat, light, cooling, electricity or other forms of energy on site and may be attached to or separate from the principal structure. Current examples include windmills, solar collectors and solar greenhouses, heat pumps, or other related devices. For the purposes of this Local Law, this definition shall apply to individual residences, farms and businesses." | Section 2010 Definitions | 2016 | https://www.sheldonzoning.com/resources/files/Current_Sheldon_Zoning_Law_complete.pdf
New York | Wyoming | Sheldon | 3612166773 | Permit |  |  | "No use or structure shall be established, erected, demolished nor land developed until a Zoning Permit has been issued by the Zoning Officer... A Building Permit may also be required pursuant to the NYS Uniform Fire Prevention and Building Code." Section 3010 adds that "A zoning permit for a permitted use... may be issued by the Zoning Officer" and Section 3020 requires zoning permit applications with sketch maps/site plans showing "existing and proposed buildings," "water and sewage disposal systems," "parking areas and driveway location," and other site information. | Section 3000 Permits Required | 2016 | https://www.sheldonzoning.com/resources/files/Current_Sheldon_Zoning_Law_complete.pdf
New York | Wyoming | Sheldon | 3612166773 | Inspection |  |  | "Within fifteen (15) days of the receipt of this letter, the Zoning Officer shall conduct a final inspection of the premises to determine whether the new use complies with the requirements of this Local Law." A Certificate of Compliance is issued only if the Zoning Officer determines the building or use complies; otherwise violations must be corrected first. | Section 3050 Certificate of Compliance | 2016 | https://www.sheldonzoning.com/resources/files/Current_Sheldon_Zoning_Law_complete.pdf
New York |  | New York | 3651000 | Definition: Geothermal |  |  | § 3-125(a): 'Geothermal system. The term "geothermal system" means a geothermal system as defined in section one of local law number 32 for the year 2013.' | § 3-125(a) | 2023 | https://codelibrary.amlegal.com/codes/newyorkcity/latest/NYCadmin/0-0-0-503
New York |  | New York | 3651000 | Definition: Geothermal Heat Pump |  |  | § 3-125.1(a): 'Geothermal exchange system. The term "geothermal exchange system" means a system owned by the city that is used to exchange heat between the earth and two or more buildings for the purpose of providing heating, cooling or hot water to two or more buildings. The term "geothermal exchange system" may also include a waste heat system.' § 3-128(a): 'For purposes of this section, the term "geothermal system" means a system used to exchange geothermal energy between the earth and one or more buildings to provide heating or cooling.' | § 3-125.1(a) Definitions; § 3-128(a) | 2023 | https://codelibrary.amlegal.com/codes/newyorkcity/latest/NYCadmin/0-0-0-503
North Dakota | Cass | Horace | 3801738900 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY. A source of energy generated from solar, water, geothermal, or similar sources, which is capable of providing energy and utility provisions to a permitted use." | Section 4-2.2 Definitions A | 2024 | https://cms7files.revize.com/cityofhoracend/Horace1.pdf
North Dakota | Cass | Oxbow | 3801760480 | Permit |  |  | "Geothermal energy systems are allowed for a private home, group of homes, or as an alternative energy solution to be shared by the entire neighborhood and/or commercial properties. Any geothermal energy system must be guaranteed parts and labor for a minimum of ten (10) years by the vendor." | 6.14. ALTERNATIVE ENERGY SYSTEMS | 2015 | https://oxbownd.com/documents/546/Oxbow_Land_Development_Code.pdf
Ohio | Hamilton | Amberley | 3901672 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEMS (GES). A system that extracts heat from the earth by an open or closed system. An open system typically utilizes a well that is drilled to extract ambient tepid water, whereby the system extracts the heat and returns the water to the earth through the well. A closed system is normally a network of pipe or tubing that circulates water to transfer the heat from the earth to the liquid within the closed loop, whereby the system extracts the hear and recycles the liquid to repeat the cycle." | § 158.02 DEFINITIONS. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | 3901672 | Setback - Right of Way | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | 3901672 | Setback - Property Lines | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | 3901672 | Setback - Yards | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way. Geothermal energy systems located underground may be permitted in the front yard." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | 3901672 | Setback - Water Lines | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | 3901672 | Setback - Sewer Lines | 10 | feet | "Geothermal energy systems shall not be located within ten feet of any property line, utility lines, or right-of-way." | § 158.30 LOCATION. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio | Hamilton | Amberley | 3901672 | Permit |  |  | § 158.06: "The installation of any alternative energy system, or the replacement or alteration of more than 50% of an existing alternative energy system, shall require a permit from the village to be considered and administered by the Board of Zoning Appeals." § 158.07: "The owner of the property upon which an alternative energy system is installed shall ensure that the design, installation, and maintenance of such systems comply with all applicable regulations ... as well as obtain all required permits and approvals from the village." Because "alternative energy system" is defined to include geothermal, these permit requirements apply to geothermal energy systems. | § 158.06 PERMIT REQUIRED.; § 158.07 COMPLIANCE. | 2010 | https://codelibrary.amlegal.com/codes/amberleyvillage/latest/amberleyvillage_oh/0-0-0-11386
Ohio |  | Fairfield | 3901725970 | Definition: Well |  |  | "Geothermal Well. This term, as it applies to Source Water Protection, refers to well(s) that have been drilled to access and utilize heat sources from within the earth." | 1157.10 Source Water Protection Program Definitions | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio |  | Fairfield | 3901725970 | Permit |  |  | "All new wells and boreholes must be registered by the well or borehole owner with the Public Utilities Director no later than 15 days prior to installation of the well or borehole." | 1157.06.G.2 Wells or Boreholes - Installation and Maintenance | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio |  | Fairfield | 3901725970 | Licensed Driller |  |  | "All new wells or boreholes must be installed by a State-recognized well driller." | 1157.06.G.2 Wells or Boreholes - Installation and Maintenance | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio |  | Fairfield | 3901725970 | Decommissioning |  |  | "All wells or boreholes which are not maintained for production, standby, or observation purposes are to be permanently sealed according to the State of Ohio Technical Guidance Manual for Sealing Abandoned and Unsealed Wells or Boreholes... The Facility Operator must notify the Public Utilities Director no later than 15 days prior to abandonment of the well or borehole and all paperwork associated with the well or borehole abandonment process must be filed with the Ohio Department of Natural Resources and the City of Fairfield Development Services Department." | 1157.06.G.3 Abandonment of Wells or Boreholes | 2025 | https://www.fairfield-city.org/DocumentCenter/View/18042/Zoning-Code-Template_Fairfield_2026-updates6-1
Ohio | Cuyahoga | Bay Village | 3903504416 | Permit |  |  | Under the building permit fee schedule for "D Heating and Air Conditioning," the ordinance lists "(6) Solar Heat/Geothermal System" with permit fees of "C. Residential $125.00" and "D. Commercial $250.00." | 1305.02 FEES FOR BUILDING PERMITS | 2014 | https://www.cityofbayvillage.gov/DocumentCenter/View/564/Ordinances-14-60-thru-14-64---First-Reading-5-19-14-Second-Reading-6-2-14-Adopted-6914-PDF
Ohio | Cuyahoga | Berea | 3903505690 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP GROUND SOURCE HEAT PUMP SYSTEM. A system that circulates a heat transfer fluid, typically food-grade antifreeze, through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." "GEOTHERMAL ENERGY SYSTEM. A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system. Also referred to as a ' ground source heat pump. '" "OPEN LOOP GROUND SOURCE HEAT PUMP SYSTEM. A system that uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | CHAPTER 400 Definitions |  | https://cityofberea.org/DocumentCenter/View/3647/Exhibit-A-Definitions-current
Ohio | Cuyahoga | Cleveland Heights | 3903516014 | Setback - Yards | 10 | feet | Residential districts: Schedule 1121.12(a) lists 'Freestanding air conditioning machinery, emergency generator, above-ground components of geothermal energy systems, and other similar equipment' as permitted in 'Rear and side, except not in required minimum side yard (see Section 1121.08)' with side lot line setback 'AA-10 & A&B-5.' Multiple-family districts: Schedule 1123.12(a) lists 'Freestanding air conditioning machinery, above-ground components of geothermal energy systems, emergency generator and other similar equipment' and states '(a) Shall maintain the same minimum yard requirement as for a principal use set forth in Section 1123.07.' Section 1123.07 requires side yards of 15 feet abutting MF, C or S districts and up to 25 feet abutting AA, A or B districts. | Schedule 1121.12(a) / Schedule 1123.12(a) | 2023 | https://www.clevelandheights.gov/DocumentCenter/View/14834
Ohio | Cuyahoga | Cleveland Heights | 3903516014 | Screening |  |  | For residential districts, Schedule 1121.12(a) applies to 'Freestanding air conditioning machinery, emergency generator, above-ground components of geothermal energy systems, and other similar equipment' and requires 'standard screening, see note (m).' Note (m) states: 'Standard screening means a fence, masonry wall or evergreen hedge which is eighty percent (80%) or more solid and either six (6) feet high or a height adequate to screen the view from a person six (6) feet tall standing on a public street or on adjacent property.' | Schedule 1121.12(a), Note (m) | 2023 | https://www.clevelandheights.gov/DocumentCenter/View/14834
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Definition: Geothermal Heat Pump |  |  | "The installation and construction of a geothermal energy system, referred to as a ground source heat pump system..." | 1155.08 GEOTHERMAL ENERGY SYSTEM STANDARDS | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Roads | 10 | feet | The setback chart requires 10 feet from "Dedicated public right-of-way and all property lines" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Property Lines | 10 | feet | The setback chart requires 10 feet from "Dedicated public right-of-way and all property lines" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Building Foundation | 10 | feet | The setback chart requires 10 feet from "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Wastewater | 25 | feet | The setback chart requires 25 feet from "Septic tanks, aerobic tanks, or holding tanks," 25 feet from "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields," 25 feet from "Sewage seepage pits and cesspools," and 25 feet from "Spray irrigation sites, sewage sludge, and septage disposal sites." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Animal Enclosures | 25 | feet | The setback chart requires 25 feet from "Farm silos, barnyards, privies, and fuel tanks" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Fuel (above ground) | 25 | feet | The setback chart requires 25 feet from "Farm silos, barnyards, privies, and fuel tanks" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Water Lines | 15 | feet | The setback chart requires 15 feet from "Existing water and forced sewer buried utilities and/or utility trenches" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Sewer Lines | 15 | feet | The setback chart requires 10 feet from "Gravity sewer lines and drains carrying domestic sewage or industrial waste" and 15 feet from "Existing water and forced sewer buried utilities and/or utility trenches" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Water Bodies | 15 | feet | The setback chart requires 15 feet from "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" for a "Borehole and Geothermal Supply and Geothermal Return Well." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The setback chart requires 300 feet from a "Preparation area or storage area of hazardous spray materials, fertilizers of chemicals, or salt piles" and states "150 feet if borehole is cased and grouted inside and out." | 1155.08(d)(1) Setbacks | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Permit |  |  | "A building permit and shall be obtained for any ground source heat pump system prior to installation or usage." | 1155.08(i) Building Permit Required | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Certification |  |  | "Ground source heat pumps shall be certified by Underwriters Laboratories, Inc. and meet the requirements of the Ohio State Basic Building Code." | 1155.08(g) Safety | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of three hundred sixty five days, the system shall be deemed to be abandoned... The owner shall remove the abandoned system at their expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid... The top of the pipe, coil or boring shall be uncovered and grouted"; "Lake ground source heat pump systems shall be completely removed from the bottom of the body of water." | 1155.08(h) System Abandonment | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Middleburg Heights | 3903549644 | Open-loop Prohibitions |  |  | "Open loop ground source heat pump systems are not permitted." | 1155.08(c) System Requirements | 2022 | https://codelibrary.amlegal.com/codes/middleburghtsoh/latest/middleburghtszone_oh/0-0-0-12186
Ohio | Cuyahoga | Oakwood | 3903557750 | Permit |  |  | Section 3 states: "Fees shall be charged for the examination of plans, permits to proceed and for the inspection of all types of construction, installation demolition, removal or alteration work performed on all types of property within the Municipality in accordance with schedules adopted from time to time by Council and on file in the Building Department." Exhibit A lists a residential HVAC permit category for "SOLAR OR GEOTHERMAL" with a fee of "150.00." Exhibit B lists a commercial HVAC permit category for "SOLAR OR GEOTHERMAL" with a fee of "250.00." | SECTION 3; EXHIBIT A; EXHIBIT B | 2025 | https://www.oakwoodvillageoh.com/wp-content/uploads/2025/06/2025-28_Building_Department_Fees.pdf
Ohio | Cuyahoga | Pepper Pike | 3903561686 | Permit |  |  | Section 1446.23 states: "The fee for a permit for HVAC work shall be as follows:" and includes line item "(8) GEO Thermal Systems ¦ $100.00." | 1446.23 HVAC MECHANICAL PERMIT FEE | 2011 | https://codelibrary.amlegal.com/codes/pepperpike/latest/pepperpike_oh/0-0-0-47077
Ohio | Franklin | Grandview Heights | 3904931304 | Permit |  |  | "(g) (1) Prior to the commencement of any heating or ventilation installation, an application for heating or ventilation permit shall be made at the Department of Building and Zoning, and a heating or ventilation permit shall be secured from the Director." Also, under "REFRIGERATION; HEAT PUMPS PERMIT FEES," the ordinance states: "(b) (1) The fee for heat pumps shall be as follows: (Based on cooling BTU/hr.) Up to and including 5 tons $75.00; Each additional 5 tons or fraction thereof 5.00," and "(4) The fee for replacement of refrigeration and/or heat pump system shall be per the above schedule." | 1325.01 PERMITS REQUIRED | 2026 | https://www.grandviewheights.gov/DocumentCenter/View/11129/02092026-Regular-Council-Packet
Ohio | Franklin | Grandview Heights | 3904931304 | Inspection |  |  | "All work for which a permit is required shall be subject to inspection by the Director of Building and Zoning." "No part of the work shall be made inaccessible for inspection until it has been inspected, tested and approved." "There shall be a final inspection and approval on all buildings and mechanical equipment governed by this Code, when completed and ready for occupancy and use." Section 1325.09 adds: "The Director of Building and Zoning upon notification from the permit holder or his agent shall make the following inspections..." including a "Final Inspection." | 1325.05 INSPECTION REQUIRED; 1325.07 APPROVALS REQUIRED; 1325.09 TYPES OF INSPECTIONS | 2026 | https://www.grandviewheights.gov/DocumentCenter/View/11129/02092026-Regular-Council-Packet
Ohio | Franklin | Plain | 3904962974 | Screening |  |  | "Any residence or building using well water as a source of heating or cooling (groundwater heat pump) shall cease to use the well water for heating or cooling if the water level in surrounding or nearby wells is depleted or reduced to the point that those wells must be deepened." | Section 409.02 | 2020 | https://plaintownship.org/wp-content/uploads/2023/01/Plain-Township-Zoning-Resolution-1.pdf
Ohio | Franklin | Westerville | 3904983342 | Setback - Property Lines | 5 | feet | "Setbacks. All underground piping and other geothermal appurtenances shall be no closer than five feet to any property line." | 1176.07(b)(3) | 2011 | https://codelibrary.amlegal.com/codes/westerville/latest/westerville_oh/0-0-0-18600
Ohio | Franklin | Westerville | 3904983342 | Decommissioning |  |  | "All alternative energy systems and related components shall be properly maintained and kept in operation. Any alternative energy system that remains nonfunctional or inoperative for a continuous period of 120 days shall be deemed to be abandoned and shall constitute a public nuisance... The owner shall be notified of the violation and shall be responsible for the removal of the abandoned system and all associated structures and equipment within 60 days. Removal of an alternative energy system shall require approval of the Chief Building Official." | 1176.1 | 2011 | https://codelibrary.amlegal.com/codes/westerville/latest/westerville_oh/0-0-0-18600
Ohio | Franklin | Westerville | 3904983342 | Open-loop Prohibitions |  |  | "All geothermal energy systems must be closed loop systems. Open loop systems are not permitted." | 1176.07(b)(1) | 2011 | https://codelibrary.amlegal.com/codes/westerville/latest/westerville_oh/0-0-0-18600
Ohio | Geauga | Bainbridge | 3905503590 | Open-loop Prohibitions |  |  | Section 177.01(bb) lists as a prohibited use: "Open loop geothermal heating systems." | 177.01 PROHIBITED USES SPECIFIED. | 2024 | https://bainbridgetwp.com/wp-content/uploads/sites/4/2024/03/Zoning-Resolution-Effective-3-27-2024-Z-2023-2.pdf
Ohio | Geauga | Russell | 3905569232 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating System - Any heating or cooling system which uses ground water or the earth as a heat source or heat sink." | Section 2.1 Words and Terms Defined | 2025 | https://russelltownship.us/includes/uploads/Photo_Zoning/Russell_Township_Zoning_Resolution_v2_1.pdf
Ohio | Geauga | Russell | 3905569232 | Permit |  |  | "No geothermal heating system shall be installed within the Township without obtaining a zoning certificate from the Zoning Inspector. The applicant shall supply the Zoning Inspector with a list of specifications describing the type of system utilized, the name and address of the installer, and the specific equipment and systems to be utilized to ensure compliance with the requirements and regulations of the Township's Zoning Resolution." | Section 4.12 Geothermal Heating Systems | 2025 | https://russelltownship.us/includes/uploads/Photo_Zoning/Russell_Township_Zoning_Resolution_v2_1.pdf
Ohio | Geauga | Russell | 3905569232 | Open-loop Prohibitions |  |  | "All geothermal systems permitted in the Township shall be installed and maintained as closed loop systems." The section further defines closed loop systems as designed "to prohibit the discharge of water, chemicals or hazardous substances on the surface of the ground, into the ground or into ground water." | Section 4.12 Geothermal Heating Systems | 2025 | https://russelltownship.us/includes/uploads/Photo_Zoning/Russell_Township_Zoning_Resolution_v2_1.pdf
Ohio | Geauga | South Russell | 3905573684 | Permit |  |  | "No water well being utilized in a geothermal heating unit, as defined in Section 1030.04 shall be drilled in the Village unless prior to such drilling a permit has been secured from the Building Inspector of the Village." Also, "Permits to drill for groundwater source heat pumps, geothermal heating units and other such systems will be denied in areas where inadequate domestic supplies exist at the time application is made for such permit." | 1030.01 PERMIT REQUIRED. | 1986 | https://codelibrary.amlegal.com/codes/southrussell/latest/southrussell_oh/0-0-0-33528
Ohio | Geauga | South Russell | 3905573684 | Decommissioning |  |  | "The water well shall be constructed, operated, maintained and abandoned in compliance with the Ohio Administrative Code, Chapter 3745-9, and as may hereinafter be amended, together with the requirements of the County Health Department or such other governmental agency having jurisdiction." | 1030.04 OPERATION REQUIREMENTS. | 1986 | https://codelibrary.amlegal.com/codes/southrussell/latest/southrussell_oh/0-0-0-33528
Ohio | Geauga | South Russell | 3905573684 | Other Prohibitions/Regulations |  |  | "No geothermal heating unit or similar device shall use, as its source of water, a central water system or the appurtenances to such central water system within the Village." | 1030.04 OPERATION REQUIREMENTS. | 1986 | https://codelibrary.amlegal.com/codes/southrussell/latest/southrussell_oh/0-0-0-33528
Ohio | Greene | Xenia | 3905786772 | Inspection |  |  | Table P14.1 lists under Mechanical Permits: 'Geothermal trench/pressure test ¦ $125 per inspection.' Table P14.2 likewise lists under Mechanical Permits: 'Geothermal trench/pressure test ¦ $90 per inspection.' | Table P14.1 G.1 - Chapter 1402: Ohio Building Code; Table P14.2 G.2 - Chapter 1404: Residential Code | 2024 | https://files-backend.assets.thrillshare.com/documents/asset/uploaded_file/4479/Xeniacity/bef52d06-1cda-441a-92e3-30e1ec2781ab/Ord_2023-38_Amending_XCO_Part_Ten_Title_Four_U.pdf?disposition=inline
Ohio | Hamilton | Mariemont | 3906147600 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP SYSTEMS. A geothermal heat pump system which relies on the contained circulation of geothermal fluids through an underground loop of pipes. The loops act as a subsurface heat exchanger, which transports the heat to or from the ground. The loop of pipe is installed either vertically in borings or horizontally in trenches." "OPEN LOOP SYSTEMS. A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring or surface water. The source for heat, groundwater is moved from the ground to a heat pump. The water is then transferred to a discharge area, typically a surface water body, storm or sanitary sewer system, or recharge well." | § 151.141 DEFINITIONS. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Setback - Property Lines | 3 | feet | "Geothermal installations are allowed in a side or rear yard with the following provisions: (1) Well locations must be setback three feet from all side or rear property lines." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Setback - Yards | 3 | feet | "Geothermal installations are not allowed in any front yard." "Geothermal installations are allowed in a side or rear yard with the following provisions: (1) Well locations must be setback three feet from all side or rear property lines." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Setback - Water Lines | 10 | feet | "Geothermal installations are allowed in a side or rear yard with the following provisions: ... (2) A minimum of ten feet from any public utilities (electrical, gas, water, sewer)." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Setback - Sewer Lines | 10 | feet | "Geothermal installations are allowed in a side or rear yard with the following provisions: ... (2) A minimum of ten feet from any public utilities (electrical, gas, water, sewer)." | § 151.142 APPLICABILITY. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Permit |  |  | "All applications for a geothermal heating system permit shall be accompanied by an application fee, which shall be non-refundable, and such fee will be according to a fee schedule established by village resolution. Engineering and other professional fees incurred in the review of the permit application shall be paid by the applicant." Also, § 151.142(A) states: "No person shall install a geothermal system in any zoning district in the village without compliance with the provisions of this chapter..." | § 151.145 FEES. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Inspection |  |  | "Any leakage of the geothermal fluid requires the system to be shut down immediately until successful repairs are completed and inspected." "Officials may, upon notice to the applicant, enter upon any property within the village for purposes of inspecting geothermal systems or monitoring the operational characteristics of such facilities." | § 151.146 MAINTENANCE AND ABANDONMENT. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Decommissioning |  |  | "The applicant shall notify the municipality within 30 days of the abandonment of any geothermal heating system." "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... The heat pump and any external mechanical equipment shall be removed. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe/coil shall be properly capped." | § 151.146 MAINTENANCE AND ABANDONMENT. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Mariemont | 3906147600 | Open-loop Prohibitions |  |  | "Open loop systems shall be prohibited." | § 151.144 DESIGN AND PERFORMANCE STANDARDS. | 2024 | https://codelibrary.amlegal.com/codes/mariemont/latest/mariemont_oh/0-0-0-24057
Ohio | Hamilton | Springdale | 3906174104 | Setback - Property Lines | 7 | feet | "Any wall bracket or ground supported air conditioning, heat pump, or electric generator unit shall not project into or be located in a front yard, but such unit may be located in a side yard if it is no closer than seven feet to the side lot line..." and "Units may be located in the rear yard if they are not less than seven feet from a rear or side lot line." | 153.252(F)(1) Air Conditioning, Heat Pump, and Fixed Electric Generator Equipment | 2020 | https://cms2.revize.com/revize/springdaleoh/Documents/Department/Development%20Regulations/Zoning%20Code/756.pdf
Ohio | Hamilton | Springdale | 3906174104 | Setback - Yards | 7 | feet | "Any wall bracket or ground supported air conditioning, heat pump, or electric generator unit shall not project into or be located in a front yard, but such unit may be located in a side yard if it is no closer than seven feet to the side lot line..." and "Units may be located in the rear yard if they are not less than seven feet from a rear or side lot line." | 153.252(F)(1) Air Conditioning, Heat Pump, and Fixed Electric Generator Equipment | 2020 | https://cms2.revize.com/revize/springdaleoh/Documents/Department/Development%20Regulations/Zoning%20Code/756.pdf
Ohio | Hamilton | Springdale | 3906174104 | Screening |  |  | "...if the unit is ground mounted, is screened from view from the front lot line. Such screening shall consist of landscaping, fencing, or other type of structure. In all cases, screening shall be consistent with the aesthetics and design of the residence and neighborhood." | 153.252(F)(1) Air Conditioning, Heat Pump, and Fixed Electric Generator Equipment | 2020 | https://cms2.revize.com/revize/springdaleoh/Documents/Department/Development%20Regulations/Zoning%20Code/756.pdf
Ohio | Hamilton | Wyoming | 3906186730 | Open-loop Prohibitions |  |  | "No person, firm, partnership, or corporation shall install an open loop geothermal system in the City of Wyoming." | 959.03 OPEN LOOP GEOTHERMAL SYSTEMS PROHIBITED. | 2024 | https://codelibrary.amlegal.com/codes/wyoming/latest/wyoming_oh/0-0-0-35754
Ohio | Huron | Willard | 3907785232 | Setback - Water Lines | 10 | feet | "No service line shall be installed closer than ten feet horizontally or eighteen inches vertically to any sewer." | § 5. TERMS AND CHARGES FOR INSTALLATION OF TAPS AND SERVICE CONNECTIONS | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | 3907785232 | Setback - Sewer Lines | 10 | feet | "No service line shall be installed closer than ten feet horizontally or eighteen inches vertically to any sewer." | § 5. TERMS AND CHARGES FOR INSTALLATION OF TAPS AND SERVICE CONNECTIONS | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | 3907785232 | Permit |  |  | "Plans for the installation of backflow prevention devices for the purpose of containment must be submitted to the City for review and approval." Also: "Plans for new installations and improvements to existing facilities should be evaluated prior to construction to determine the degree of hazard to the potable water system." | PART VI § 3. WATER SYSTEM | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | 3907785232 | Inspection |  |  | For geothermal systems, "An approved backflow prevention assembly shall be installed on each service line to a consumer's water system serving any of the following systems... (8) Geothermal heating systems or chemically treated heating systems." The ordinance then requires: "Double check valve assemblies... [and] reduced pressure principle assemblies... shall be inspected and tested for tightness at the time of installation and at least every twelve months thereafter." It also states inspections, tests, and overhauls "shall be performed by a licensed plumber who is qualified and certified to inspect, test and overhaul backflow prevention devices." | PART VI § 10. INSPECTION AND MAINTENANCE | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Huron | Willard | 3907785232 | Certification |  |  | To inspect, test, and overhaul required backflow prevention assemblies, "The individual must possess a current valid backflow tester certification from the Ohio Department of Commerce, Division of Industrial Compliance." | PART VI § 11. APPROVAL TO INSPECT, TEST, AND OVERHAUL BACKFLOW PREVENTION ASSEMBLIES | 2020 | https://www.willardohio.gov/uploads/1/4/4/5/144541287/willard_rules_and_regulations_final_version_nov_11_2019.pdf
Ohio | Lake | Kirtland | 3908540642 | Definition: Geothermal |  |  | "Geothermal Energy System" means "an energy system that derives its heat energy from the earth." | § 1468.02 DEFINITIONS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | 3908540642 | Definition: Geothermal Heat Pump |  |  | "Geothermal systems (also known as a ground source heat pump system)". | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | 3908540642 | Setback - Right of Way | 10 | feet | "Piping and geothermal fields shall have a minimum setback from property lines and public right-of ways of ten feet." | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | 3908540642 | Setback - Property Lines | 10 | feet | "Piping and geothermal fields shall have a minimum setback from property lines and public right-of ways of ten feet." | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | 3908540642 | Permit |  |  | "A zoning permit and building permit shall be obtained for any alternative energy system prior to installation or usage." Section 1468.03(d) separately states: "Alternative energy systems, except for geothermal, as provided in § 1468.06(a)(1) and (2), shall be permitted, as a conditional use..." | § 1468.03 ADMINISTRATION. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | 3908540642 | Inspection |  |  | "The Administrator may enter onto any property for which a zoning permit has been issued under this chapter to conduct an inspection to determine whether the conditions stated in the permit have been met." | § 1468.03 ADMINISTRATION. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lake | Kirtland | 3908540642 | Screening |  |  | "Piping and geothermal fields are permitted in front lots or under parking areas so long as they are buried and not visible in the final site and landscaping plan." | § 1468.06 GEOTHERMAL ENERGY SYSTEMS. | 2023 | https://codelibrary.amlegal.com/codes/kirtland/latest/kirtland_oh/0-0-0-46473
Ohio | Lorain | Oberlin | 3909357834 | Permit |  |  | The fee schedule expressly establishes geothermal-specific heating permits: "Geothermal System (New) $200.00," "Geothermal Unit (Replace) $150.00," and "Geothermal Loop System (Replace) $75.00." The ordinance also states a general enforcement provision: "Penalty for starting work without first obtaining required Permit or Required Contractor Registration ... Permit Fee/Registration PLUS 300%." | Heating Permits | 2014 | https://www.cityofoberlin.com/wp-content/uploads/2017/05/ORD_14-19.pdf
Ohio | Lorain | Penfield | 3909361532 | Setback - Roads | 70 | feet | Article 4.15(D)(1): "All loops must maintain the following setbacks: 1. Front Yard – 70 feet from road right-of-way." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Setback - Property Lines | 15 | feet | Article 4.15(D)(2): "Side yard – 15 feet from property line." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Setback - Yards | 15 | feet | Article 4.15(D): "All loops must maintain the following setbacks:" including "2. Side yard – 15 feet from property line" and "3. Rear yard – 15 feet from property line." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Setback - Wastewater | 15 | feet | Article 4.15(D)(4): "15 feet on either side of any water line and/or septic system." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Setback - Water Lines | 15 | feet | Article 4.15(D)(4): "15 feet on either side of any water line and/or septic system." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Minimum Well Depth | 5 | feet | Article 4.15(F): "Horizontal loops must have a minimum of a one (1) acre lot and must be installed at least five (5) feet deep." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Permit |  |  | "Closed Loop Geothermal Technologies are permitted in all districts with proper permitting." Also, Article 4.10 requires for a zoning permit: "A completed detailed plot plan depicting the structure or pond to be built, its measurements and the measurements to the four property lines. Plan to include existing structures, if any, and layout of septic systems and geothermal lines. (Effective 10/09)" and Article 4.15(B) states: "A diagram of location of all loop construction must be provided on the site layout and attached to the permit application." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Licensed Driller |  |  | Article 4.15(F): "Vertical loops must be have a minimum of one half (1/2) acre lot and must be installed by a certified well driller." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Open-loop Prohibitions |  |  | "Open Loop Geothermal Technologies are not permitted in any district." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Lorain | Penfield | 3909361532 | Other Prohibitions/Regulations |  |  | Article 4.15(E): "Loops may not be connected to any well water supply or home water supply." | Article 4.15 GEOTHERMAL (Effective 10/09) | 2024 | https://www.penfieldtownship.com/_files/ugd/c8a414_063e67515a824a48b668942e36df0d25.pdf
Ohio | Montgomery | Clayton | 3911315644 | Permit |  |  | The ordinance and attached agreement establish permit requirements and fees for geothermal work, including a listed fee item for "Geothermal trench/pressure test" ($75.00 in the residential fee schedule; $100.00 in the OBC-covered fee list). The agreement also states NIC shall "Prepare permits (Certificates of Plan Approval) and certificates of occupancy/completion when the installed work complies with all applicable building code regulations, ordinances, and statutes" and "Examine plans and specifications for proposed work" under the applicable codes. | Clayton Proposed Fee Schedule / Agreement § 2(a), (e) | 2022 | https://www.clayton.oh.us/DocumentCenter/View/5523/O-11-22-35
Ohio | Montgomery | Clayton | 3911315644 | Inspection |  |  | The agreement requires inspections: NIC "shall exercise enforcement authority for inspections and make inspections on behalf of Clayton"; "Inspections shall be performed on a daily basis during regular business hours"; and NIC shall "Perform job inspections of all work described on the application and plans, including the installation of equipment." The fee schedule also expressly lists "Geothermal trench/pressure test," plus fees for "Re-Inspection" and "Out of Normal Hours Inspection." | Agreement § 1; § 2(d); Clayton Proposed Fee Schedule | 2022 | https://www.clayton.oh.us/DocumentCenter/View/5523/O-11-22-35
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Definition: Geothermal |  |  | "Geothermal Heating and Cooling System" - "A mechanical system for space heating or cooling that relies on the transfer of thermal energy between the earth, including ground water, and a heat transfer fluid and consists of a heat pump, a heat exchange well or loop, and a heat distribution network." | 947.01(d) Geothermal Definitions | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop System" - "A low-temperature geothermal heating and cooling system that circulates a heat transfer fluid, usually water with an antifreeze additive, through a loop or multiple loops of piping installed below the ground surface or within a surface water body." "Open-Loop System" - "A geothermal heating and cooling system that withdraws water from an extraction well or body of water, passes the water through a heat exchange system, and discharges the temperature-altered water either into the ground in a discharge or return well or to the ground surface or into surface water." | 947.01(d) Geothermal Definitions | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Permit |  |  | "Before installing, drilling or otherwise constructing a geothermal heating and cooling system within the City of New Philadelphia, Ohio, an application shall be submitted to the New Philadelphia City Health Department for a permit for the drilling and/or construction of such geothermal heating and cooling system... All such permits shall remain in force for one year from the date of submittal to the City of New Philadelphia." | 947.05 Regulation of Geothermal Heating/Cooling Systems | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Inspection |  |  | Section 947.05(f) states: "The requirements of Section 947.03 shall apply to any and all geothermal heating and cooling system wells constructed, maintained or abandoned within the City." Section 947.03(d)(1) then provides: "All sources of water supply other than the municipal water system shall henceforth be subject to inspection and approval by the New Philadelphia City Health Department and/or the Water Department Superintendent." In addition, for certified testing of required backflow assemblies, 945.04(b)(6) states: "it shall be the duty of the customer user at any premises where backflow prevention assemblies are installed to have certified inspections and operational tests made at least once per year." | 947.03(d)(1); 947.08(g) Water Withdrawal Regulations as applied by 947.05(f) | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Certification |  |  | "No person shall engage in the work or business of installing of geothermal systems within the City of New Philadelphia without first obtaining a license from the City." "the Director of Public Service shall issue a Geothermal Heating and Cooling Installer's License for a period of one year expiring December 31 of the year of registration." "At the time of application, the applicant shall enter into a bond payable to the City of New Philadelphia of five thousand dollars ($5,000)..." | 947.06 Bonding/Registration of Geothermal Installers | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Decommissioning |  |  | "The application fee for the abandonment/de-commissioning of a geothermal heating and cooling system shall be fifty dollars ($50.00)." Section 947.05(f) adds: "The requirements of Section 947.03 shall apply to any and all geothermal heating and cooling system wells constructed, maintained or abandoned within the City." Section 947.03(d)(4) requires that "Abandonment shall be in accordance with OAC 3745-9-10," and 947.03(d)(6) requires for abandoned wells: "a copy of the abandonment report required by Ohio R.C. 1521.05(C) shall be submitted to this office within (30) days of the completion of the abandonment process." | 947.05(e)-(f); 947.03(d)(4),(6) | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Tuscarawas | New Philadelphia | 3915755216 | Other Prohibitions/Regulations |  |  | "No geothermal heating and cooling system or part thereof shall be drilled or otherwise constructed in the current five year time of travel zone or within one-half mile from the center of the municipal water well field." | 947.05(b) Regulation of Geothermal Heating/Cooling Systems | 1973 | http://www.newphilaoh.com/downloads/Complete-Codified-Ordinance_1.pdf
Ohio | Wood | Northwood | 3917357190 | Noise Limits | 10 | dBA | "Noise from any renewable energy system shall be limited to no more than ten (10) decibels above the original ambient sound level beyond the property line, considering both daytime and night measurements pursuant to measurement with a sound decibel meter." The chapter also states: "Other types of renewable energy systems such as, geothermal energy, hydrogen, biomass or other similar technologies shall meet the minimum requirements of this chapter and the respective zoning district." | 1251.04 DEVELOPMENT STANDARDS | 2023 | https://cms9files1.revize.com/northwoodoh/ORD%202022-45.pdf
Ohio | Wood | Northwood | 3917357190 | Permit |  |  | "All renewable energy systems shall require a zoning permit." The same section also states: "Other types of renewable energy systems such as, geothermal energy, hydrogen, biomass or other similar technologies shall meet the minimum requirements of this chapter and the respective zoning district." | 1251.04 DEVELOPMENT STANDARDS | 2023 | https://cms9files1.revize.com/northwoodoh/ORD%202022-45.pdf
Ohio | Wood | Northwood | 3917357190 | Decommissioning |  |  | "Any renewable energy system, including related equipment, that becomes inoperable shall be repaired or removed at the owner's expense within one (1) year of the date the system became inoperable." | 1251.05 INOPERABLE RENEWABLE ENERGY SYSTEMS | 2023 | https://cms9files1.revize.com/northwoodoh/ORD%202022-45.pdf
Ohio |  | Dublin | 3922694 | Definition: Geothermal |  |  | "Equipment for the collection of solar, wind or geothermal energy or its conversion to electrical energy or heat for use on the same property or for incidental sale to a utility when that equipment is accessory to a permitted or approved conditional principal use of the property." | Chapter 153.002 - Definitions, (18)(b): RENEWABLE ENERGY EQUIPMENT OR ALTERNATIVE ENERGY EQUIPMENT |  | https://dublinohiousa.gov/dev/dev/wp-content/uploads/2021/10/C5_Dublin-Zoning-Code-Regs.pdf
Ohio |  | Dublin | 3922694 | Setback - Yards | 5 | feet | "Ground-mounted equipment for the collection of geothermal energy is permitted only to the rear of and within five feet of the principal structure." Similar rear-yard placement language also appears in Chapter 153.172 - Architectural Review - Uses: "The collection of geothermal energy is permitted only to the rear of and within five feet of the principal structure." | Chapter 153.059 - Bridge Street District - Uses, (j) Renewable energy equipment |  | https://dublinohiousa.gov/dev/dev/wp-content/uploads/2021/10/C5_Dublin-Zoning-Code-Regs.pdf
Ohio |  | Dublin | 3922694 | Screening |  |  | "Ground-mounted equipment for the collection of geothermal energy is permitted only to the side or rear of the principal structure, and equipment must be adequately screened." Additional geothermal-specific concealment language appears in Chapter 153.059(j)(4): "Ground-mounted renewable energy equipment shall be sited to minimize view from the public right-of-way and adjacent properties, and shall be camouflaged to the extent that the equipment can function normally," and Chapter 153.172(j)(2)(c): "Ground-mounted renewable energy equipment shall be sited to minimize view from the public right-of-way and surrounding properties and shall be camouflaged to the extent that the equipment can function normally." | Chapter 153.038 - EAZ Innovation Districts - District Uses, (C)(31)(a) |  | https://dublinohiousa.gov/dev/dev/wp-content/uploads/2021/10/C5_Dublin-Zoning-Code-Regs.pdf
Ohio | Butler | Oxford | 3959234 | Permit |  |  | The fee ordinance expressly lists geothermal-specific permit/inspection line items under the Building Official schedules: residential includes "Geothermal trench/pressure test 75.00" and commercial includes "Geothermal Trench/Pressure Test 100.00 per inspection." | C) INSPECTIONS (Building Official) |  | https://www.cityofoxford.org/Documents/%20Government/%20City%20Charter%20and%20Codified%20Ordinances/Fee%20Ordinances/2023%20Fee%20Ordinance.pdf?t=202603230833000
Ohio | Butler | Oxford | 3959234 | Inspection |  |  | Under Building Official inspection fees, the ordinance includes geothermal-specific inspection items: residential "Geothermal trench/pressure test 75.00" and commercial "Geothermal Trench/Pressure Test 100.00 per inspection." | C) INSPECTIONS (Building Official) |  | https://www.cityofoxford.org/Documents/%20Government/%20City%20Charter%20and%20Codified%20Ordinances/Fee%20Ordinances/2023%20Fee%20Ordinance.pdf?t=202603230833000
Ohio | Paulding | Paulding | 3961252 | Permit |  |  | "Any person, firm, group or corporation, either owner or agent who tampers with or attempts to use facilities provided by the village without first obtaining the necessary permits and approvals is in violation of the rules and regulations." | § 52.22 GENERAL CONDITIONS | 2020 | https://codelibrary.amlegal.com/codes/pauldingoh/latest/paulding_oh/0-0-0-1968
Ohio | Lucas | Swanton | 3975896 | Definition: Geothermal |  |  | "Geothermal System : Any energy system where thermal transfer is extracted from heat stored in the earth and designed to deliver a heating and cooling resource to any building/structure." | SECTION 2 DEFINITIONS | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | 3975896 | Setback - Property Lines | 10 | feet | "A geothermal system shall be located at least ten (10) feet from adjacent property lines and from the foundation of any building/structure." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | 3975896 | Setback - Building Foundation | 10 | feet | "A geothermal system shall be located at least ten (10) feet from adjacent property lines and from the foundation of any building/structure." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | 3975896 | Setback - Wastewater | 25 | feet | "A geothermal system shall be located at least twenty-five (25) feet from leach fields and any potable water source." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | 3975896 | Setback - Public Water | 25 | feet | "A geothermal system shall be located at least twenty-five (25) feet from leach fields and any potable water source." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | 3975896 | Permit |  |  | "Before installation of geothermal system, a zoning permit must be obtained; the following requirement must be met to obtain a zoning permit for the installation of a geothermal system: 1. Site plan: A detailed site plan shall be required in accordance with the requirements of Section 9.17." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Lucas | Swanton | 3975896 | Open-loop Prohibitions |  |  | "All geothermal systems must have a closed loop technologies. Open loop systems are not permitted." | 9.21.2 Specific Requirements | 2022 | https://cdn.toledo.oh.gov/uploads/documents/Plan-Commission/Zoning-Resolutions/Swanton-2-27-23.pdf
Ohio | Champaign | Urbana | 3979072 | Definition: Geothermal Heat Pump |  |  | "A CLOSED-LOOP SYSTEM IS DEFINED AS A PIPE AND HEAT EXCHANGER NETWORK SEALED FROM ITS SURROUNDING ENVIRONMENT." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Setback - Property Lines | 5 | feet | "THE LOCATION OF ALL UNITS AND PIPING LOOPS SHALL BE A MINIMUM OF FIVE FEET (5') FROM ALL SIDE AND REAR PROPERTY LINES..." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Setback - Building Foundation | 5 | feet | "ALL BURIED GEOTHERMAL PIPES IN SYSTEMS CONTAINING ANTIFREEZE PASSING PARALLEL WITHIN 5 FEET OF ANY WALL, STRUCTURE OR WATER PIPE SHALL BE INSULATED WITH R2 MINIMMUM CLOSED CELL INSULATION." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Setback - Private Water | 25 | feet | "AN OVERALL ISOLATION RADIUS OF ... 25’ AWAY FROM ANY PRIVATE WATER SUPPLY WELLS SHALL BE MAINTAINED." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Setback - Public Water | 300 | feet | "AN OVERALL ISOLATION RADIUS OF 300’ AWAY FROM ANY PUBLIC WATER SUPPLY WELLS... SHALL BE MAINTAINED." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Setback - Water Lines | 2 | feet | "THERE SHALL BE A 2’ MINIMUM SEPARATION BETWEEN SUPPLY/RETURN LINES AND WATER/SEWER LINES." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Setback - Sewer Lines | 2 | feet | "THERE SHALL BE A 2’ MINIMUM SEPARATION BETWEEN SUPPLY/RETURN LINES AND WATER/SEWER LINES." | 6. PIPE AND UNIT PLACEMENT | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Permit |  |  | "A NOMINAL PERMIT FEE WILL BE CHARGED FOR ANY GEOTHERMAL INSTALLATION WITHIN THE CITY OF URBANA." | PERMITTING AND INSPECTION | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Inspection |  |  | "THE FEE COVERS AN INITIAL INSPECTION (BEFORE THE LOOP INSTALLATION WHILE THE PRESSURE TESTING IS BEING PERFORMED) AND A FINAL INSPECTION (TO MAKE SURE GROUTING AND BACKFILLING PROCEDURES ARE FOLLOWED) BY THE CITY ENGINEERING DEPARTMENT." | PERMITTING AND INSPECTION | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Certification |  |  | "ALL GEOTHERMAL SYSTEM INSTALLERS SHALL BE IGSHPA (INTERNATIONAL GROUND SOURCE HEAT PUMP ASSOCIATION) CERTIFIED." | 2. INSTALLER CERTIFICATION | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Ohio | Champaign | Urbana | 3979072 | Open-loop Prohibitions |  |  | "ONLY GEOTHERMAL CLOSED-LOOP SYSTEMS SHALL BE INSTALLED... NO OPEN-LOOP SYSTEMS WILL BE PERMITTED." | 1 | 2012 | https://www.urbanaohio.com/uploads/1/2/4/6/124631710/1167.30_-_geothermal_closed-loop_piping_system__ground_heat_exchanger_.pdf
Oklahoma | Tulsa | Tulsa | 4075000 | Definition: Geothermal Heat Pump |  |  | “Geothermal Heat Exchange System Equipment that exchanges thermal energy between the ground (or a water source) and a building. This includes vertical closed loop, horizontal closed loop, water body closed loop system and open loop systems. Also known as ground source heat pumps and geothermal heat pumps.” | Section 95.100 ¦ Terms Beginning with “G” | 2025 | http://tulsaplanning.org/plans/TulsaZoningCode.pdf
Oklahoma | Tulsa | Tulsa | 4075000 | Permit |  |  | “Unless otherwise expressly allowed by this zoning code or state law, any violation of a provision of this zoning code—including any of the following—are subject to the remedies and penalties provided for in this zoning code. 85.020-D To engage in the use of a building, structure or land, the use or installation of a sign, or any other activity requiring one or more permits or approvals under this zoning code without obtaining such required permits or approvals.” | Section 85.020 ¦ Violations | 2025 | http://tulsaplanning.org/plans/TulsaZoningCode.pdf
Oklahoma | Tulsa | Tulsa | 4075000 | Other Prohibitions/Regulations |  |  | “Underground equipment, piping and devices may not be located in any public easement or right-of-way.” | Section 45.080-B ¦ Location | 2025 | http://tulsaplanning.org/plans/TulsaZoningCode.pdf
Oregon |  | Adams | 4100350 | Definition: Geothermal |  |  | "Geothermal Area - Means any parcel of land that is or reasonably appears to be underlain by geothermal resources. (ORS 522.005.)" "Geothermal Resources - The natural heat of the earth, the energy, in whatever form, below the surface of the earth, present in, resulting from, or created by, or which may be extracted from, the natural heat, and all minerals in solution or other products obtained from naturally heated fluids, brines, associated gases and steam, in whatever form, found below the surface of the earth..." | Chapter 1.3 Definitions | 2003 | http://www.cityofadamsoregon.com/uploads/3/1/2/3/3123389/development_code.pdf
Oregon | Jackson | Ashland | 4103050 | Noise Limits | 45 | dBA | Section 9.08.170(E)(3)(a) states: "No person shall operate a commercial or residential heat pump, air-conditioning unit, or similar mechanical device if noise levels from its operation exceed forty-five (45) dBA from the closest property line of a residential property on an adjacent parcel of land characterized as a noise sensitive area." Section 9.08.170(E)(3)(b) adds a separate limit for older units: "No person shall operate a commercial or residential heat pump, air-conditioning unit, or similar mechanical device that was installed prior to 1981 if noise levels from its operation exceed fifty (50) dBA..." | 9.08.170 Unnecessary Noise | 2017 | https://ashland.municipal.codes/AMC/9.08.280
Oregon | Polk | Dallas | 4117700 | Permit |  |  | "A building permit shall not be issued until the Planning Official has issued a Land Use Review approval in accordance with the provisions of Chapter 4.2, or has otherwise found that such review is not required. The Planning Official may determine that this Code requires other permits or approvals in lieu of or before Land Use Review approval may be granted." | 1.2.080 Building Permit And Certificate Of Occupancy | 2026 | https://dallasor.municipalcodeonline.com/book?type=development#name%3DARTICLE_1_GENERAL_PROVISIONS
Oregon | Multnomah | Gresham | 4131250 | Definition: Geothermal |  |  | "Geothermal energy is generated from heat stored in the earth." | 2.381.4 Geothermal Energy | 2013 | https://www.greshamoregon.gov/globalassets/government/city-codes-and-policies/comprehensive-plan/comprehensive-plan---volume-1---section-2.000.pdf
Oregon | Multnomah | Gresham | 4131250 | Definition: Geothermal Heat Pump |  |  | "Low Temperature Geothermal: This approach utilizes the relatively constant and mild temperatures naturally found at shallow depths in the soil and groundwater throughout the year. The ground-source heat pump transfers heat stored in the earth or in groundwater into a building during the winter and transfers heat out of a building and into the ground during the summer." Also: "A ground-source heat pump has two main parts: - Either a closed-loop or open-loop system in the ground where the heat transfer occurs with the soil or groundwater." | 2.381.4 Geothermal Energy | 2013 | https://www.greshamoregon.gov/globalassets/government/city-codes-and-policies/comprehensive-plan/comprehensive-plan---volume-1---section-2.000.pdf
Oregon | Klamath | Klamath Falls | 4139700 | Definition: Well |  |  | "Well. Any artificial opening or artificially altered natural opening, however made, by which geothermal fluids or ground water flows under natural pressure or is artificially withdrawn, or is used to operate a heat exchanger within the well, provided that this definition shall not include a natural spring." | 8.254 DEFINITIONS | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | 4139700 | Permit |  |  | "Any person, including the City, desiring to construct, install, or alter a well within the City shall first apply for a Well Permit at the Geothermal Data Center... No person shall commence construction or alteration of a well prior to the owner of a proposed well receiving a Well Permit." | 8.268 APPLICATION FOR WELL PERMIT | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | 4139700 | Inspection |  |  | Section 8.282: "Upon completion of any well construction or alteration, but prior to regular use, the owner shall promptly notify the Geothermal Data Center to request a well completion inspection and written report thereof..." Section 8.296: "City officials may, upon reasonable notice to the owner, enter upon any property within the City for purposes of inspecting wells and/or geothermal facilities, or monitoring the operational characteristics of such wells and/or facilities..." | 8.282 COMPLETION INSPECTION; 8.296 CITY INSPECTION AND MONITORING OF WELLS AND GEOTHERMAL FACILITIES | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | 4139700 | Decommissioning |  |  | Section 8.264(2): the City Manager shall offer technical assistance "during the conversion or abandonment of such discharging wells or facilities." Section 8.298: when a well is wasteful or defective, the City Manager shall notify the owner and "require said owner to repair or adjust the well within 60 days; a well continuing a wasteful or defective operation after expiration of the 60 days shall be prosecuted as a violation of this Ordinance." | 8.264 PRE-ORDINANCE SURFACE DISCHARGE ELIMINATION; 8.298 WASTEFUL OR DEFECTIVE WELLS | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Oregon | Klamath | Klamath Falls | 4139700 | Other Prohibitions/Regulations |  |  | "No well constructed or altered after the effective date of this Ordinance shall be operated or altered in such a manner as to cause thermal ground water to be discharged onto the surface of the ground or into any public ditch or drainage facility. Construction and routine maintenance of wells shall be exempt from said prohibition..." | 8.284 POST-ORDINANCE SURFACE DISCHARGES | 2019 | https://klamathfalls.city/DocumentCenter/View/273/Chapter-8---Building-and-Fire-Protection-8025-8400-8150-8110-8800-PDF
Arizona |  | Dewey-Humboldt | 419145 | Permit |  |  | "Mechanical permits. A mechanical permit shall not be required for the following:" followed by exempt items such as "A portable heating appliance," "A portable cooling unit," and certain minor equipment work. Ground-source heat pump systems are not listed among the mechanical permit exemptions, while the code elsewhere states in Section 105.8 that persons performing installation or repair of "mechanical" systems to which the code applies must comply with the code. | § 150.01 Administrative Code, Section 105.2 — Work exempt from permit | 2021 | https://codelibrary.amlegal.com/codes/deweyhumboldt/latest/deweyhum_az/0-0-0-11034
Arizona |  | Dewey-Humboldt | 419145 | Inspection |  |  | "Rough inspection of plumbing, mechanical, gas and electrical systems shall be made prior to covering or concealment, before fixtures or appliances are set or installed, and prior to slab grade inspection, or at the time of rough-in inspection prior to insulation." The section adds: "Exception: Back-filling of ground-source heat pump loop systems tested in accordance with Sections M2105.1 of the 2018 International Residential Code and 1208.1. of the 2018 International Mechanical Code prior to inspection shall be permitted." | § 150.01 Administrative Code, Section 110.2.6 — Plumbing, mechanical, gas and electrical systems inspection | 2021 | https://codelibrary.amlegal.com/codes/deweyhumboldt/latest/deweyhum_az/0-0-0-11034
Pennsylvania | Adams | Franklin | 4200127320 | Definition: Well |  |  | "Well — Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or monitoring of groundwater. This includes but is not limited to test wells, test borings, monitoring wells, geothermal wells, domestic wells, irrigation wells, or commercial wells." | Section 201: Definitions | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Definition: Geothermal |  |  | "Geothermal — A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." | Section 201: Definitions | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop Geothermal — A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere. The heat transfer fluid is potable or beneficial reuse water and may have approved antifreeze added." Also: "Open-Loop Geothermal — A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump. The discharge water from the water-source heat pump may be returned to the subsurface through a recharge well or infiltration bed, or may be discharged into a pond, lake, or stream. A spring may also be the source of the ground water supply." | Section 201: Definitions | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Roads | 10 | feet | Table 1 requires a minimum setback from "Dedicated public right-of-way" of "10" for "Boreholes (ft)." Section 102 states the ordinance applies to "vertical closed-loop geothermal wells and/or boreholes." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Building Foundation | 10 | feet | Table 1 requires a minimum setback from "Building foundations (except for buildings enclosing water wells, water well pumps, and/or any other source of pollution as approved)" of "10" for "Boreholes (ft)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Wastewater | 25 | feet | For boreholes, Table 1 sets setbacks of "25" ft from "Septic tanks, aerobic tanks or holding tanks"; "25" ft from "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields"; "25" ft from "Sewage seepage pits, cesspools"; and "25" ft from "Domestic spray irrigation sites, sewage sludge and septage disposal sites." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Animal Enclosures | 25 | feet | Table 1 lists "Farm silos, barnyards, privies and fuel tanks" with a borehole setback of "25" ft. | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Fuel (above ground) | 25 | feet | Table 1 lists "Farm silos, barnyards, privies and fuel tanks" with a borehole setback of "25" ft. | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Water Lines | 15 | feet | Table 1 states for "Existing water and forced sewer buried utilities and/or utility trenches" that boreholes must be "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench centerline." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Sewer Lines | 10 | feet | Table 1 lists "Public or on lot gravity sewer lines and drains carrying domestic sewage or industrial waste" with a minimum setback of "10 or according to easement" for "Boreholes (ft)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Water Bodies | 25 | feet | Table 1 requires a minimum setback from "Lakes, ponds, streams or other surface waters" of "25" for "Boreholes (ft)." Section 102 includes "vertical closed-loop geothermal wells and/or boreholes" within the ordinance scope. | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table 1 lists "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" with a minimum setback of "100" for "Boreholes (ft)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Permit |  |  | Section 300 states: "No person, firm, or corporation shall make a penetration of soil and, or rock that is augered, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed that is regulated by this Ordinance until a Drilling Permit has been issued." Section 102 makes the ordinance applicable to "vertical closed-loop geothermal wells and/or boreholes." Section 400.C.1 adds that work may begin only "after the Drilling Permit has been issued and the Code Enforcement Officer has conducted the preliminary inspection of the site." | Section 300: Well Drilling Permit Required; Section 400: Drilling Permits | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Inspection |  |  | Section 400.C.1 requires that work may begin only after "the Code Enforcement Officer has conducted the preliminary inspection of the site." Section 401.D states: "A preliminary/pre-construction inspection shall be conducted at the site before any well or borehole drilling is commenced." At that inspection, the officer determines "Compliance with setback distances as found in Table 1 of Section 302.C." Section 401.E also provides: "Code Enforcement Officer reserves the right to inspect the site at any time to determine if the well is in compliance with the Drilling Permit, the standards within this ordinance, and to observe the implementation of any of the standards listed in the Adams County Construction Standards and Material Specifications for Wells & Geothermal Systems." | Section 400.C.1; Section 401: Inspection/Reviews | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Decommissioning |  |  | "Existing wells that are being replaced that are not grouted with approved grout or do not have a sanitary well cap shall be decommissioned or mitigated in accordance with the Adams County Construction Standards and Material Specifications for Wells & Geothermal Systems." | Section 305: Well Abandonment | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Franklin | 4200127320 | Open-loop Prohibitions |  |  | "Geothermal wells shall only be constructed as part of Closed-Loop Geothermal systems. Open-Loop Geothermal systems are prohibited." | Section 301: Geothermal Wells | 2021 | https://ecode360.com/FR2051/laws/LF1304901.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Definition: Well |  |  | "Well - Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or monitoring of groundwater. This includes but is not limited to test wells, test borings, monitoring wells, geothermal wells, domestic wells irrigation wells, or commercial wells." | Section 201: Definitions | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Definition: Geothermal Heat Pump |  |  | "Geothermal - A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode." "Closed-Loop Geothermal - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." "Open-Loop Geothermal - A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump." | Section 201: Definitions | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Roads | 10 | feet | For boreholes, Table 1 requires 10 ft from "Dedicated public right-of-way." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Building Foundation | 10 | feet | For boreholes, Table 1 requires 10 ft from "Building foundations (except for buildings enclosing water wells, water well pumps, and/or any other source of pollution as approved)." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Wastewater | 25 | feet | For boreholes, Table 1 requires 25 ft from "Septic tanks, aerobic tanks or holding tanks," 25 ft from "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields," 25 ft from "Sewage seepage pits, cesspools," and 25 ft from "Domestic spray irrigation sites, sewage sludge and septage disposal sites." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Animal Enclosures | 25 | feet | For boreholes, Table 1 requires 25 ft from "Farm silos, barnyards, privies and fuel tanks." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Fuel (above ground) | 25 | feet | For boreholes, Table 1 requires 25 ft from "Farm silos, barnyards, privies and fuel tanks." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Water Lines | 15 | feet | For boreholes, Table 1 requires setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench centerline." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Sewer Lines | 15 | feet | Table 1 requires boreholes to be set back from "Public or on lot gravity sewer lines and drains carrying domestic sewage or industrial waste" by "10 or according to easement" and from "Existing water and forced sewer buried utilities and/or utility trenches" by "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench centerline." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Water Bodies | 25 | feet | For boreholes, Table 1 requires a 25 ft setback from "Lakes, ponds, streams or other surface waters." Section 102 states the ordinance applies to "vertical closed-loop geothermal wells and/or boreholes." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Setback - Hazardous Materials/Fertilizers | 100 | feet | For boreholes, Table 1 requires 100 ft from "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles." | Section 302.C Table 1: Minimum Well and Borehole Setback Distances | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Permit |  |  | Section 300 states: "No person, firm, or corporation shall make a penetration of soil and, or rock that is augered, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed that is regulated by this Ordinance until a Drilling Permit has been issued." Section 102 makes the ordinance applicable to "vertical closed-loop geothermal wells and/or boreholes." Section 400.C.1 adds: "The applicant may initiate work ... after the Drilling Permit has been issued and the Zoning Officer has conducted the preliminary inspection of the site." | Section 300: Well Drilling Permit Required; Section 400: Drilling Permits | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Inspection |  |  | Section 402.A provides: "The Zoning Officer shall conduct all inspections required by this Ordinance." Section 402.D states: "A preliminary/pre-construction inspection shall be conducted at the site before any well or borehole drilling is commenced." Section 402.E states: "A final inspection shall be conducted at the site upon the completion of the well drilling and other related processes." Section 400.C.1 also requires work to begin only after "the Zoning Officer has conducted the preliminary inspection of the site." | Section 402: Inspection / Reviews | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Decommissioning |  |  | Section 305 states: "Existing wells that are being replaced that are not grouted with approved grout or do not have a sanitary well cap shall be decommissioned or mitigated in accordance with the Adams County Construction Standards and Material Specifications for Wells & Geothermal Systems." | Section 305: Well Abandonment | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Hamiltonban | 4200132200 | Open-loop Prohibitions |  |  | Section 301.B states: "Geothermal wells shall only be constructed as part of Closed-Loop Geothermal systems. Open-Loop Geothermal systems are prohibited." | Section 301: Geothermal Wells | 2015 | http://www.hamiltonban.com/getmedia/302d222f-8f97-4142-ae7b-71d31345c7b5/Ordinance2015-04.pdf
Pennsylvania | Adams | Highland | 4200134424 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop - a geothermal heat exchanger that circulates a nontoxic antifreeze heat transfer fluid through a loop or multiple loops of polyethylene piping installed below the ground surface or within a surface water body." | SECTION 8 - GEOTHERMAL WELLS - Geothermal Heat Pump Systems (GHPS), A. DEFINITION | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Driveways | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Property lines, driveways, all right-of- ways, easements" at "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Right of Way | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Property lines, driveways, all right-of- ways, easements" at "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Property Lines | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Property lines, driveways, all right-of- ways, easements" at "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Building Foundation | 20 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Principal structure/dwelling" at "20 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Wastewater | 100 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists wastewater-related setbacks including "Subsurface sewage absorption areas elevated sand mounds, cesspools, sewage seepage pits" - "100 feet"; "Spray irrigation site perimeter, sewage sludge and seepage disposal sites" - "100 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, privies, holding tanks" - "50 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Fuel (above ground) | 150 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Surface or subsurface containers or tanks of greater than 1000 gallons used for storage of materials that cannot be properly renovated by passage through soil... includ[ing] gasoline and all other petroleum products" at "150 feet," and also lists smaller tanks at 30 feet. | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Sewer Lines | 50 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Sewer drains, public sewer laterals" at "50 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Water Bodies | 10 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" at a "MINIMUM DISTANCE" of "10 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Setback - Hazardous Materials/Fertilizers | 150 | feet | Section 8 states: "Minimum isolation distances from the proposed Closed-Loop Borehole to the facilities listed as in section 104." Section 104 lists "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles" at "150 feet." | SECTION 104 - DESIGN STANDARDS, 1. DRILLED WELLS; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Permit |  |  | Section 106 provides: "No construction, drilling, or digging for any well/water supply for the production of water for any purposes shall commence unless the property owner... has obtained a well permit." Section 8.B.2 adds that for closed-loop boreholes, "Any proposed deviation from the isolation distances prescribed in section 104 must be approved in writing by the Township, or his designee, with reasons stated for such deviation." | SECTION 106 - REGISTRATION; SECTION 8 - GEOTHERMAL WELLS - B.2. BOREHOLE LOCATIONS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Inspection |  |  | Section 8.B.3(d): "Pressure testing is required with water at 100 psi for 30 minutes with no leaks observed." Section 107 states that upon a permit application, the Township representative shall "perform an inspection of the premises on which the well is to be constructed." | SECTION 8 - GEOTHERMAL WELLS - B.3. CONSTRUCTION; SECTION 107 - INSPECTION | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Certification |  |  | Section 8.B.3(b): "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." Section 5.B also states water testing must be conducted "by a certified laboratory." | SECTION 8 - GEOTHERMAL WELLS - B.3. CONSTRUCTION; SECTION 5 WELL CERTIFICATION, B. Water Quality | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Decommissioning |  |  | "Wells, cisterns and water storage tanks, which are no longer in use, shall be removed, filled or otherwise maintained in a condition such as to prevent access... and to effectively prevent pollution of groundwater. Abandoned wells or wells with no future planned use... shall be tremie grouted from the bottom up in one continuous operation using cement with five percent (5%) bentonite grout or other DEP-approved method." | SECTION 7 - ABANDONED WATER SUPPLIES | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Highland | 4200134424 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be allowed in Highland Township." | SECTION 8 - GEOTHERMAL WELLS - Geothermal Heat Pump Systems (GHPS), B.1. ALLOWED SYSTEMS | 2015 | http://www.highlandtownshippa.com/getmedia/f323b614-45ee-4547-b250-3b39ef98965d/WellOrdinance.pdf
Pennsylvania | Adams | Reading | 4200163616 | Definition: Well |  |  | The ordinance defines "Heat exchange well" as "a well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | §26-104.I(1) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Definition: Geothermal Heat Pump |  |  | The ordinance defines geothermal heat pump system types: "Closed-loop–a geothermal heat exchanger that circulates a nontoxic antifreeze heat transfer fluid through a loop or multiple loops of polyethylene piping installed below the ground surface or within a surface water body"; "Direct exchange–a type of closed-loop heat exchanger that uses loops of copper tubing installed in pits, trenches or vertical borings in the earth, through which a refrigerant is circulated"; and "Open-loop–a geothermal heat exchanger that withdraws groundwater from a supply well, passes the groundwater through a heat pump, and discharges the temperature-altered water back either to the ground in a discharge (return) well or to the ground surface or into surface water." | §26-104.I(1) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Right of Way | 10 | feet | For closed-loop boreholes, the ordinance requires under miscellaneous sources: "Property lines, all right-of-ways, easements. 10 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Property Lines | 10 | feet | For closed-loop boreholes, the ordinance requires under miscellaneous sources: "Property lines, all right-of-ways, easements. 10 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Wastewater | 100 | feet | For closed-loop boreholes, the ordinance requires minimum isolation distances from sewage-related sources: "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits. 100 feet"; "Spray irrigation site perimeter, sewage sludge and seepage disposal sites. 50 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks. 50 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Fuel (above ground) | 300 | feet | For closed-loop boreholes, the ordinance states: "Surface or subsurface containers or tanks of greater than 1000 gal. used for storage of materials that cannot be properly renovated by passage through soil. This includes, but is not limited to, gasoline and all other petroleum products. ... 300 feet" and "...containers or tanks of 1000 gal. or less... This includes, but is not limited to, gasoline and all other petroleum products... 100 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Sewer Lines | 5 | feet | For closed-loop boreholes, the ordinance lists under sewage-related sources: "Sewer drains, public sewer laterals. 5 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Water Bodies | 50 | feet | For closed-loop boreholes, the ordinance states: "Minimum isolation distances from the proposed Closed-Loop Borehole... Delineated wetlands, flood plains, lakes, ponds, or other surface waters. 50 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop boreholes, the ordinance requires: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles. 300 feet"; and "Surface or subsurface containers or tanks of greater than 1000 gal. used for storage of materials that cannot be properly renovated by passage through soil... 300 feet." It also lists "Identified NPL Site (Superfund Sites) plume area. 300 feet." | §26-104.I(2)(a)1)a) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Permit |  |  | For closed-loop systems, the ordinance provides: "Closed-Loop Geothermal Boreholes shall be permitted in accordance with paragraph .I(3). Each borehole must be permitted using a single application. A fee shall be charged for each borehole." | §26-104.I(2)(c)1) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Inspection |  |  | The ordinance states: "The Inspection Officer or designated Township employee shall be responsible for insuring that the borehole is drilled in the permitted location" and also requires "Pressure testing ... with water at 100 psi for 30 minutes with no leaks observed. Evidence of testing from the installer must be provided to the Township." | §26-104.I(2)(b)2); §26-104.I(2)(b)7) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Certification |  |  | The ordinance states: "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer. The well contractor shall be responsible for insuring that the pipe loop is installed in accordance with the specifications of the ground source heat pump system manufacturer, the International Ground Source Heat Pump Association, National Groundwater Association, the pipe manufacturer..." | §26-104.I(2)(b)4) | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Adams | Reading | 4200163616 | Decommissioning |  |  | The ordinance provides: "Wells, springs, cisterns and water storage tanks, which are no longer in use, shall be removed, filled or otherwise maintained..." and specifically, "Abandoned wells shall be tremie grouted from the bottom up in one continuous operation using cement with 5 percent bentonite grout or other DEP-approved method." It also states: "The Township shall also be given the opportunity to conduct an inspection at the time of abandonment of a well/water supply." | §26-104.G; §26-108.3 | 2009 | http://www.readingtownship.net/getmedia/aff8a1c1-92d5-4cab-a102-01d5d571adb9/Chapter26.pdf
Pennsylvania | Allegheny | Brentwood | 4200308416 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 210-9 Definitions | 2026 | https://ecode360.com/29424067
Pennsylvania | Allegheny | Brentwood | 4200308416 | Minimum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM ... A horizontal closed loop system shall be no more than 20 feet deep." | § 210-9 Definitions | 2026 | https://ecode360.com/29424067
Pennsylvania | Allegheny | Heidelberg | 4200333592 | Setback - Property Lines | 10 | feet | "Geothermal energy facilities shall meet the accessory structure setbacks that may apply in the zoning district within which the facility is constructed, and where no such setback is specified, the facility shall be no closer than 10 feet from any property line." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | Heidelberg | 4200333592 | Permit |  |  | "Accessory geothermal energy facilities shall be permitted by conditional use in the M - Manufacturing Zoning District." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | Heidelberg | 4200333592 | Screening |  |  | "Required landscape buffering may be modified so that tall tree species may be replaced with lower-growing tree species where the required tree species may interfere with the functioning of the geothermal energy facility..." and "Secure perimeter fencing shall be installed around the geothermal energy facility... The fence shall be supplemented with screening material which creates a visual barrier that is at least 80% opaque." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | Heidelberg | 4200333592 | Certification |  |  | "A design certification by a certified engineer shall be required, consisting of the proposed foundation design and analysis of soil conditions." | Alternative energy facilities; h. Geothermal energy facilities | 2020 | https://ecode360.com/34882567
Pennsylvania | Allegheny | O'Hara | 4200356384 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY FACILITY - A generating facility capable of capturing and converting hydrothermal energy into hydronic or electrical energy sources." | Section 72-2.1 Strict Construction | 2020 | https://www.ohara.pa.us/sites/g/files/vyhlif6181/f/uploads/zoning_ord_1361.pdf
Pennsylvania | Allegheny | O'Hara | 4200356384 | Setback - Property Lines | 20 | feet | Geothermal accessory-use clauses state: "Geothermal energy facilities shall meet the accessory structure setbacks that may apply in the zoning district within which the facility is constructed and where no such setback is specified, the facility shall be no closer than (10) ten feet from any property line." Separately, the district yard tables set accessory-structure setbacks: CD districts: "Permitted accessory structures shall be located no closer than twenty feet (20') to the side or rear property line" (Section 72-8.7); C district: "Permitted accessory structures shall be located no closer than twenty feet (20') to the side or rear property line" (Section 72-9.5); SM district: "Permitted accessory structures shall be located no closer than twenty feet (20') to the side or rear property line" (Section 72-10.6). | Sections 72-8.7, 72-9.5, and 72-10.6 | 2020 | https://www.ohara.pa.us/sites/g/files/vyhlif6181/f/uploads/zoning_ord_1361.pdf
Pennsylvania | Allegheny | O'Hara | 4200356384 | Permit |  |  | District permit sections provide: "A Zoning/Building permit shall be required prior to the erection, construction or alteration of any structure proposed in relation to those uses enumerated in this Article." Geothermal Energy Facility is enumerated as a permitted accessory use and/or conditional use in the listed district articles. Section 72-1.2 also states: "No building or structure shall be used, located, erected, constructed, altered, enlarged or moved... except in full compliance with all of the provisions of this Ordinance and after the lawful issuance of all permits and certificates required by this Ordinance." | Sections 72-4.8, 72-5.8, 72-6.8, 72-7.8, 72-8.9, 72-9.7, 72-10.8, and Section 72-1.2 | 2020 | https://www.ohara.pa.us/sites/g/files/vyhlif6181/f/uploads/zoning_ord_1361.pdf
Pennsylvania | Allegheny | Pine | 4200360272 | Permit |  |  | "Non-contaminated HVAC condensation and water from geothermal systems" are authorized discharges only under Section 801.C, and Section 801.B states that non-stormwater discharges are prohibited "except ... discharges authorized under a state or federal permit." | Section 801. Prohibited Discharges and Connections | 2018 | https://ecode360.com/PI1032/laws/LF1059482.pdf
Pennsylvania | Allegheny | Plum | 4200361536 | Definition: Geothermal |  |  | 'RENEWABLE ENERGY SOURCE - Any method, process or substance whose supply is rejuvenated through natural processes and, subject to those natural processes, remains relatively constant, including, but not limited to, biomass conversion, geothermal energy, solar and wind energy and hydroelectric energy and excluding those sources of energy used in the fission and fusion processes.' | RENEWABLE ENERGY SOURCE | 2018 | https://www.plumboro.com/sites/g/files/vyhlif3686/f/pages/plum_zoning_ordinance.pdf
Pennsylvania |  | Adamstown | 4200364 | Definition: Well |  |  | "GEOTHERMAL BOREHOLE. A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 320-7 Terms defined. | 2026 | https://ecode360.com/31736387
Pennsylvania |  | Adamstown | 4200364 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy-generating system that uses the earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also defined are system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system... The pipes form a closed loop and are filled with a heat transfer fluid"; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A borehole that extends beneath the surface. Pipes are installed with U-bends at the bottom of the borehole. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes"; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM. Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | § 320-7 Terms defined. | 2026 | https://ecode360.com/31736387
Pennsylvania | Allegheny | Swissvale | 4200375816 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES – A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 202: Definitions | 2017 | https://swissvaleborough.com/DocumentCenter/View/101/Swissvale-Zoning-Ordinance-2017-PDF
Pennsylvania | Allegheny | Swissvale | 4200375816 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM – An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM – A mechanism for heat exchange which consists of the following basic elements: underground loops of piping; heat transfer fluid; a heat pump; an air distribution system... The pipes form a closed loop and are filled with a heat transfer fluid..." and "OPEN LOOP GEOTHERMAL SYSTEM – Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | Section 202: Definitions | 2017 | https://swissvaleborough.com/DocumentCenter/View/101/Swissvale-Zoning-Ordinance-2017-PDF
Pennsylvania | Allegheny | Swissvale | 4200375816 | Maximum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM ... A horizontal closed loop system shall be no more than twenty (20) feet deep." | Section 202: Definitions | 2017 | https://swissvaleborough.com/DocumentCenter/View/101/Swissvale-Zoning-Ordinance-2017-PDF
Pennsylvania | Allegheny | Wilkinsburg | 4200385188 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES. A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Allegheny | Wilkinsburg | 4200385188 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy-generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Allegheny | Wilkinsburg | 4200385188 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A mechanism for heat exchange which consists of the following basic elements: underground loops of piping; heat transfer fluid; a heat pump; an air distribution system. An opening is made in the earth. A series of pipes is installed into the opening and connected to a heat exchange system in the building. The pipes form a closed loop and are filled with a heat transfer fluid. The fluid is circulated through the piping from the opening into the heat exchanger and back. The system functions in the same manner as the open loop system except there is no pumping of groundwater." "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A borehole that extends beneath the surface. Pipes are installed with U-bends at the bottom of the borehole. The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." "OPEN LOOP GEOTHERMAL SYSTEM. Water is pumped from a water well or other water source into a heat exchanger located in a surface building. The water drawn from the Earth is then pumped back into the ground through a different well or in some cases the same well, also known as 'reinjection.' Alternatively, the groundwater could be discharged to a surface water body also known as a 'pump and dump.' In the heating mode, cooler water is returned to the Earth, and in the cooling mode, warmer water is returned to the surface water body or well." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Allegheny | Wilkinsburg | 4200385188 | Maximum Well Depth | 20 | feet | In the definition of "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM," the ordinance states: "A horizontal closed loop system shall be no more than 20 feet deep." | § 260-202 Definitions |  | https://ecode360.com/8425217
Pennsylvania | Lancaster | Akron | 4200540 | Setback - Right of Way | 25 | feet | "All systems shall be set back a minimum of twenty-five (25) feet from any property line or right-of-way line and a minimum of one hundred (100) feet from any potable water supply wells." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | 4200540 | Setback - Property Lines | 25 | feet | "All systems shall be set back a minimum of twenty-five (25) feet from any property line or right-of-way line and a minimum of one hundred (100) feet from any potable water supply wells." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | 4200540 | Setback - Public Water | 100 | feet | "All systems shall be set back a minimum of twenty-five (25) feet from any property line or right-of-way line and a minimum of one hundred (100) feet from any potable water supply wells." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | 4200540 | Permit |  |  | "Manufacturer specifications shall be submitted as part of any building or zoning application." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Lancaster | Akron | 4200540 | Open-loop Prohibitions |  |  | "Geothermal heat pumps are permitted in all zoning districts as an accessory use under the following conditions: 1. Open-loop systems shall not be permitted." | SECTION 27-1511. GEOTHERMAL ENERGY SYSTEMS | 2023 | https://www.akron-pa.com/wp-content/uploads/2023/07/Zoning-62023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | §27-202. Definitions | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system..."; "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a water-supply well, or other source, and a pump to deliver groundwater to a heat exchanger." | §27-202. Definitions | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, Geothermal Energy Systems shall be set back a minimum distance of twenty-five (25) feet from any property line." | §27-1630.A.(3)(e) Setback Requirements | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Setback - Wastewater | 100 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 100 feet from on-lot sewage disposal systems." | §27-1630.A.(3)(e) Setback Requirements | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Maximum Well Depth | 20 | feet | "All closed horizontal loop systems shall be no more than twenty (20) feet deep." | §27-1630.A.(3)(f) Closed-loop Geothermal Systems | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Permit |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to all applicable industry standards... The manufacturer specifications shall be submitted as part of the application. A zoning permit and building permit, under the PA Uniform Construction Code, shall be required." | §27-1630.A.(3)(a) Design and Permitting | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Decommissioning |  |  | "If the Geothermal Energy System is ever abandoned or enters into a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the Geothermal Energy System within six (6) months from the date the system enters such a state." "Any earth disturbance as a result of the removal or permanent sealing of the Geothermal Energy System shall be graded and reseeded." | §27-1630.A.(3)(h)-(i) | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Oley | 4201156672 | Other Prohibitions/Regulations |  |  | "Only the following types of Geothermal Energy Systems shall be permitted: i. Closed horizontal loop; ii. Closed vertical loop; and, iii. Open horizontal loop systems relying upon injection wells or watercourses." "Extraction of water from surface waters shall be prohibited." "Discharge of water from open-loop systems into sanitary sewer systems shall be prohibited." "Discharge of water from open-loop systems into storm sewers, and onto roads, shall be prohibited." "Discharge of water from open-loop systems into a watercourse shall be prohibited." | §27-1630.A.(3)(b), §27-1630.A.(3)(g)(i)-(ii) | 2022 | https://oleytownship.org/wrp/wp-content/uploads/2023/03/CHAPTER-27.-ZONING-2023.pdf
Pennsylvania | Berks | Reading | 4201163624 | Setback - Roads | 1.1 | structure-height-multiplier | "All alternative energy systems and/or any appurtenant structures shall be set back from all public roads a distance of not less than 1.1 times the alternative energy system's height... to the right-of-way line of all public roads." | § 600-1012 D(5) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | 4201163624 | Permit |  |  | "No alternative energy system shall be located, modified or constructed within the City of Reading unless a permit has been issued to the facility owner in accordance with the provisions of this section of the Zoning Ordinance." The same installation rule is repeated in § 600-1012 J(1)(a). Geothermal heat pumps are included as alternative energy systems in § 600-1012 B. | § 600-1012 D(6); J(1)(a) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | 4201163624 | Certification |  |  | "For alternative energy system categories in which installer certification exists, a certified installer shall be required for more complex installations, nonresidential installations, or if recommended by the manufacturer." | § 600-1012 J(1)(b) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | 4201163624 | Decommissioning |  |  | "The facility owner or operator shall, at his/her expense, completely remove any alternative energy system within 12 months after the end of its useful life." The system "will be presumed to be at the end of its useful life if no energy is generated for a continuous period of 12 months." If the owner fails to remove it, "the City may take such measures as necessary to complete removal ... at the expense of the facility owner and operator." | § 600-1012 J(5)(a)-(b) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Reading | 4201163624 | Other Prohibitions/Regulations |  |  | "The geothermal heat pump may not be in contact with an aquifer or be sited within any aquifer's recharge zone." | § 600-1012 F(2)(c) | 2015 | https://codelibrary.amlegal.com/codes/readingpa/latest/reading_pa/0-0-0-25325
Pennsylvania | Berks | Shillington | 4201170248 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 10 feet from any property line." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | 4201170248 | Noise Limits | 50 | dBA | § 27-620 states: "No continuous noise in excess of the following limits shall be permitted at the property line of the site on which the noise sources originates," including "R-1 and R-2 Residential Zoning Districts ... 50 dBA" for "8:00 p.m. to 6:00 a.m." It also lists other limits: R-1/R-2 "55 dBA" daytime; R-3 "60 dBA" daytime and "55 dBA" nighttime; Commercial/L-C/Industrial "60 dBA" daytime and "55 dBA" nighttime. § 27-624 makes geothermal heating systems a permitted accessory use and subjects them to Borough requirements: "The design and installation of geothermal systems ... shall ... comply with ... all other applicable federal, state and Borough requirements." | § 27-620 Environmental Performance Standards for Nonresidential Uses; § 27-624 Alternative Energy Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | 4201170248 | Maximum Well Depth | 40 | feet | Under "For closed-loop systems, the following shall apply": "All horizontal closed-loop systems shall be no more than 40 feet deep." The same section repeats under "Height and Setback Restrictions": "All horizontal closed-loop systems shall be no more than 40 feet deep." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | 4201170248 | Permit |  |  | The abandonment provision states: "The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | 4201170248 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | 4201170248 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained... The heat pump and any external mechanical equipment shall be removed. Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Shillington | 4201170248 | Open-loop Prohibitions |  |  | Under geothermal heating systems: "Only the following types of geothermal energy systems shall be permitted: Closed horizontal loop. Closed vertical loop. Open-loop systems are not permitted within the Borough." | § 27-624 Alternative Energy Systems - Geothermal Heating Systems | 2014 | https://ecode360.com/31517215
Pennsylvania | Berks | Spring | 4201172824 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, ACCESSORY - a sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes, but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop." | Section 202. Definitions | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | 4201172824 | Minimum Well Depth | 20 | feet | "All wells serving geothermal heating and/or cooling systems shall be equipped with watertight and durable casing pipe. The casing shall be carried to a minimum depth of 20 feet and grouted in place." Also, "Boreholes must be grouted from a minimum depth of 20 feet below grade to the ground surface with an approved grout." | Section 327(C)(5)(e)-(f) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | 4201172824 | Certification |  |  | "Geothermal energy systems shall conform to the applicable industry standards including those of the American National Standards Institute (ANSI). Applicants shall submit certificates of compliance demonstrating that the system has been tested and approved by Underwriters Laboratories (UL) or other approved independent testing agency." | Section 327(C)(5)(c) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | 4201172824 | Open-loop Prohibitions |  |  | "No person shall install an open loop geothermal system. It shall be permissible to operate an open loop geothermal system provided that such unit was legally installed on the property prior to the enactment of this Ordinance". | Section 327(C)(5)(b) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | Spring | 4201172824 | Other Prohibitions/Regulations |  |  | "Equipment, piping and devices shall not be located within any easement or right-of-way." | Section 327(C)(5)(d)(2) - Geothermal Energy System, Accessory | 2015 | https://www.springtwpberks.org/wp-content/uploads/2023/09/2015-Zoning-Ordinance-Amendments-Ordinance-415.pdf
Pennsylvania | Berks | West Reading | 4201183928 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of 10 feet from any property line." | § 455-168 Alternative energy systems, D(2)(b) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | 4201183928 | Maximum Well Depth | 40 | feet | "All horizontal closed-loop systems shall be no more than 40 feet deep." The same limit is repeated under height and setback restrictions: "All horizontal closed-loop systems shall be no more than 40 feet deep." | § 455-168 Alternative energy systems, D(1)(d)[2] and D(2)(a) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | 4201183928 | Permit |  |  | "Geothermal heating systems shall be permitted as an accessory use in all zoning districts and shall be subject to the following regulations"; for multi-property systems, "there shall be documentation provided to the Borough showing that the parties are in agreement to the removal of the system." The abandonment section also states: "The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained." | § 455-168 Alternative energy systems, D. Geothermal heating systems | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | 4201183928 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | § 455-168 Alternative energy systems, D(1)(c) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | 4201183928 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." Removal must include: "The heat pump and any external mechanical equipment shall be removed" and "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 455-168 Alternative energy systems, D(3) Abandonment | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | West Reading | 4201183928 | Open-loop Prohibitions |  |  | "Open-loop systems are not permitted within the Borough." | § 455-168 Alternative energy systems, D(1)(b) | 2025 | https://ecode360.com/WE3192/laws/LF2448399.pdf
Pennsylvania | Berks | Wyomissing | 4201186880 | Permit |  |  | "3.10 Mechanical Permits (new or replacement heaters, furnaces, boilers, H20 heaters, fuel burning appliances, a/c units, exhaust systems, and geothermal/solar-thermal mechanical systems)" and "Miscellaneous Mechanical Fee... $150.00 PA $4.50." | 3.10 Mechanical Permits | 2025 | https://wyomissingboro.org/DocumentCenter/View/523
Pennsylvania | Bucks | Doylestown | 4201719784 | Definition: Well |  |  | "GEOTHERMAL WELL — Any well or borehole in the ground constructed for the purpose of extracting heat from or transferring heat to the ground or groundwater. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes." | § 202 Definitions | 2011 | https://ecode360.com/16053299
Pennsylvania | Bucks | Doylestown | 4201719784 | Permit |  |  | "it shall be unlawful for any person to locate, drill or have drilled any ... geothermal well ... or to alter an existing ... geothermal well ... until a permit for such location, drilling, installation or alteration shall have been issued by the Borough Manager of the Borough of Doylestown." | § 203 Permits | 2011 | https://ecode360.com/16053299
Pennsylvania | Bucks | Doylestown | 4201719784 | Licensed Driller |  |  | "All wells drilled within the Borough of Doylestown must be drilled by a well driller licensed by the Commonwealth of Pennsylvania." | § 204 Application and Forms | 2011 | https://ecode360.com/16053299
Pennsylvania | Bucks | Dublin | 4201720104 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM - a system that uses a heat pump to extract heat from the earth in heating mode and/ or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, a ground source heat pump system (GSHP) and a GeoExchange® system." | Section 1; Section 3-103. Definitions | 2025 | https://ecode360.com/DU3825/laws/LF2318336.pdf
Pennsylvania | Bucks | East Rockhill | 4201721760 | Definition: Geothermal Heat Pump |  |  | "GROUND-SOURCE HEAT PUMP SYSTEM (Also known as 'geothermal energy system') — A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; an approved fluid that absorbs and transfers heat; and a heat pump unit that processes heat for use or disperses heat for cooling; and an air-distribution system. Open-loop ground-source heat pump systems are not permitted in East Rockhill Township." | § 13-403 Definitions | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Setback - Right of Way | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines and rights-of-way." | § 13-406(C)(3) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Setback - Property Lines | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines and rights-of-way." | § 13-406(C)(3) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Setback - Building Foundation | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (4) Twenty-five feet from existing or proposed structures." | § 13-406(C)(4) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Setback - Wastewater | 25 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (2) Twenty-five feet from any existing or proposed individual or community on-lot sewage disposal system, including any primary or alternate drainfield sites." | § 13-406(C)(2) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Setback - Private Water | 100 | feet | "The perimeter of the GSHP subsurface loops shall meet the following minimum isolation requirements: (1) One hundred feet from any existing or proposed drinking water wells." | § 13-406(C)(1) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Minimum Well Depth | 2.5 | feet | "The depth of the tubing or heat transfer element must be at least 30 inches below the surface of the ground." | § 13-406(J) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Permit |  |  | "No person shall: (1) construct or install a GSHP; (2) dig, bore, drill, replace, modify, repair and/or destroy a well that is, is intended to be, or was part of a GSHP; or (3) make any other excavation that may intersect groundwater without first applying for and obtaining the appropriate permit from the Township and paying the requisite permit fee in full. A permit is required for any GSHP within East Rockhill Township." It also states: "Application for a permit for the drilling of a well and/or the installation and/or construction of a GSHP shall be made to the Township Code Enforcement Officer." | § 13-406(A) Geothermal Energy Systems | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Inspection |  |  | Section E requires "A written plan ... provide for the operation and periodic inspection of the GSHP system." Section I requires prior to activation "written documentation of the GSHP system testing and certification." Section L states: "The owner of the GSHP shall submit an annual inspection report certifying the integrity of the system." In addition, § 13-409 provides: "The Building Inspector and/or Code Enforcement Officer, or other designated Township representative, shall require the proper maintenance and use of all alternative energy systems and will inspect every alternative energy system for which a permit is required within 10 days after work is completed on the alternative energy system." | § 13-406(E), § 13-406(I), § 13-406(L), § 13-409 | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Licensed Driller |  |  | "GSHP well drilling shall only be undertaken by a Pennsylvania-licensed well driller." | § 13-406(G) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Certification |  |  | Section D(1) states: "All joints shall be sealed by heat fusion or IGSHPA-certified process." Section I(4) requires prior to activation: "Written documentation of the GSHP system testing and certification." | § 13-406(D)(1); § 13-406(I)(4) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Decommissioning |  |  | § 13-406(E)(2) requires "A system closure plan for use in the event of the discontinuance of the use of the GSHP system." More generally, § 13-408 states: "If an alternative energy system remains nonfunctional or inoperative for a continuous period of six months, the system shall be deemed to be abandoned and constitute a public nuisance and shall thereafter be removed by the property owner." It further requires: "The alternative energy system owner, at his/her sole expense, shall complete decommissioning of the system within six months after the end of the useful life of the system, or within six months of damage which prevents the system from operating in a safe manner at full capacity or according to industry standards." "The owner shall remove the abandoned and/or decommissioned system after a demolition or other requisite permit has been obtained from the Township. Removal includes the entire structure, including foundations to below natural grade, external mechanical equipment and transmission equipment." | § 13-406(E)(2); § 13-408 | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Open-loop Prohibitions |  |  | "Closed-loop systems are permitted within East Rockhill Township with the appropriate permit. Open-loop systems are not permitted in East Rockhill Township." Section A repeats: "Only closed-loop systems are permitted within East Rockhill Township. No open-loop system shall be permitted within East Rockhill Township." | § 13-406 Geothermal Energy Systems | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | East Rockhill | 4201721760 | Other Prohibitions/Regulations |  |  | "Ground-source heat pump systems shall not encroach on public drainage and/or stormwater, utility, roadway or trail easements." | § 13-406(K) | 2011 | https://ecode360.com/31217187
Pennsylvania | Bucks | Lower Southampton | 4201745112 | Permit |  |  | The fee schedule expressly lists a geothermal-specific permit charge under plumbing permits: "4. Well installation ... c) Geothermal unit (each) $150.00" and also states generally, "PERMIT FEES MAY BE DOUBLED FOR FAILURE TO PULL PERMITS." | PART 3 - PLUMBING PERMITS | 2024 | https://lowersouthamptontownship.org/wp-content/uploads/2024/04/2024-LSTWP-Fee-Schedule-April-10-revised.pdf
Pennsylvania | Bucks | Middletown | 4201749120 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY. A renewable source of energy generated from solar, water, wind, geothermal, or similar sources, which is capable of providing energy and utility provisions to a permitted use." | § 500-202, Specific terms | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." Also: "GROUND SOURCE HEAT PUMP. A geothermal heat pump that uses the earth itself as a heat source and heat sink. It is coupled to the ground by means of a closed-loop heat exchanger installed horizontally or vertically underground." | § 500-202, Specific terms | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Right of Way | 10 | feet | Table 1 states: "Dedicated public right-of-way and property lines — 10 feet." Section 500-2903.C.9 provides that wells and boreholes regulated by the ordinance must use the minimum isolation distances listed in Table 1. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Property Lines | 10 | feet | Table 1 states: "Dedicated public right-of-way and property lines — 10 feet." Section 500-2903.C.9 provides that wells and boreholes regulated by the ordinance must use the minimum isolation distances listed in Table 1. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Building Foundation | 10 | feet | Table 1 states: "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved) — 10 feet." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Wastewater | 50 | feet | Table 1 includes multiple wastewater setbacks: "Septic tanks, aerobic tanks, or holding tanks — 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields — 50 feet"; "Sewage seepage pits and cesspools — 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites — 25 feet." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Animal Enclosures | 25 | feet | Table 1 states: "Farm silos, barnyards, privies, and fuel tanks — 25 feet." Section 500-2903.C.9 applies Table 1 to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Fuel (above ground) | 25 | feet | Table 1 states: "Farm silos, barnyards, privies, and fuel tanks — 25 feet." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Water Lines | 15 | feet | Table 1 states: "Existing water and forced sewer buried utilities and/or utility trenches — 15 feet or outside easement." Section 500-2903.C.9 applies these Table 1 isolation distances to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Sewer Lines | 15 | feet | Table 1 states: "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 15 feet or according to easement." It also states: "Existing water and forced sewer buried utilities and/or utility trenches — 15 feet or outside easement." | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Water Bodies | 25 | feet | Table 1 states: "Delineated wetlands, flood plains, lakes, ponds, or other surface waters — 25 feet." Section 500-2903.C.9 makes Table 1's minimum isolation distances applicable to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table 1 states: "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles — 300 feet; 150 feet (if borehole is cased and grouted inside and out)." Section 500-2903.C.9 applies Table 1 to geothermal wells and boreholes. | § 500-2903.C.9; Table 1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Noise Limits | 55 | dBA | "Audible sound from any alternative and/or emerging energy facility shall not exceed 55 dBA, as measured at the applicant's property line. Middletown Township has the right to inspect, measure, and record sound levels at the applicant's expense." | § 500-2903.G.1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." Also: "No alternative or emerging energy facility shall be located, modified, or constructed within Middletown Township unless a permit has been issued to the landowner in accordance with the provisions of this Section." | § 500-2903.C; § 500-2906.A | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Inspection |  |  | § 500-2907.B: "The landowner shall consult with a qualified inspector every 12 months to determine if the alternative and emerging energy facility is operating in accordance with the specifications of the manufacturer. A copy of the report shall be submitted to Middletown Township, and Middletown Township shall have the right to inspect." § 500-2910.B: "Middletown Township reserves the right to inspect an alternative or emerging energy system, at any time, if the system appears inoperable, or constitutes a danger to life or property." § 500-2903.G.1: "Middletown Township has the right to inspect, measure, and record sound levels at the applicant's expense." | § 500-2907.B; § 500-2910.B; § 500-2903.G.1 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well. In all cases, the well drilling rig must also be approved by the Pennsylvania Department of Environmental Protection." | § 500-2903.C.7 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well." | § 500-2903.C.7 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Decommissioning |  |  | § 500-2903.C.6 states: "The geothermal system must be installed, maintained, and decommissioned in conformance with the IGSHPA Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards..." Section 500-2909 further provides: "The landowner or energy facility operator shall, at its expense, complete decommissioning of the alternative or emerging energy facility within 12 months after the end of the useful life of the alternative and emerging system" and "All disturbed earth shall be restored, graded, and reseeded." | § 500-2903.C.6; § 500-2909 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Middletown | 4201749120 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems are prohibited." | § 500-2903.C.3 | 2021 | https://www.middletownbucks.org/getattachment/8c634572-8eac-4ec6-b92e-11108ffe3c41/Ord-No-21-07.pdf?lang=en-US
Pennsylvania | Bucks | Milford | 4201749384 | Permit |  |  | "Geothermal wells shall be allowed in open space where approved by the Board of Supervisors." | Section 251 - Open Space | 2019 | https://milfordtownship.org/wp-content/uploads/2020/05/ord_174_AMU-Amendment.pdf
Pennsylvania | Bucks | Newtown | 4201754184 | Definition: Geothermal Heat Pump |  |  | "Closed Loop Geothermal System. A heating and/or cooling system that utilizes the earth's thermal energy to heat and/or cool a building through the use of a series of underground pipes." | Part 6 - Building Permits, H. Closed Loop Geothermal System | 2022 | https://www.boroughofnewtown.com/media/2023%20Fee%20Schedule.pdf
Pennsylvania | Bucks | Newtown | 4201754184 | Permit |  |  | Part 6 states building permit fees apply, and "all fees referenced within this part shall be doubled if the project is started without the applicable permits and/or approvals." The fee schedule specifically lists "Closed Loop Geothermal System" with "Fee is $350." Part 1.E also states: "The applicant assumes all risks for any actions taken by the applicant prior to the issuance of an appropriate permit for which an application has been made." | Part 6 - Building Permits; Part 1 - General Provisions; Part 6 - Building Permits, H. Closed Loop Geothermal System | 2022 | https://www.boroughofnewtown.com/media/2023%20Fee%20Schedule.pdf
Pennsylvania | Bucks | Nockamixon | 4201754576 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM (also known as 'GEOTHERMAL ENERGY SYSTEM') A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include closed loops of pipe, coils or plates; an approved fluid that absorbs and transfers heat; a heat pump unit that processes heat for use or disperses heat for cooling; and an air-distribution system. Open-loop ground source heat pump systems are not permitted in Nockamixon Township." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Nockamixon | 4201754576 | Maximum Well Depth | 20 | feet | "HORIZONTAL GROUND SOURCE HEAT PUMP SYSTEM A closed-loop ground source heat pump system where the loops or coils are installed horizontally in a trench or series of trenches no more than 20 feet below the land surface." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Nockamixon | 4201754576 | Certification |  |  | "HEAT TRANSFER FLUID A Township-approved nontoxic and food-grade fluid..." and the closed-loop definition states: "A system that circulates an approved heat transfer fluid through pipes or coils buried beneath the land surface or anchored to the bottom in a body of water." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Nockamixon | 4201754576 | Open-loop Prohibitions |  |  | The ordinance expressly states in the GHP definition and again in the open-loop definition: "Open-loop ground source heat pump systems are not permitted in Nockamixon Township." The open-loop definition further describes such a system as one that "uses groundwater as a heat transfer fluid by drawing groundwater from a well to a heat pump and then discharging the water over land, directly in a water body or into an injection well." | § 234-9 Definitions | 2023 | https://ecode360.com/33335792
Pennsylvania | Bucks | Northampton | 4201754688 | Definition: Well |  |  | 'Geothermal well - Any well or borehole in the ground constructed for the purpose of extracting heat from or transferring heat to the ground or groundwater. These shall include wells drilled as supply and/or return wells for open-loop systems; or closed-loop geothermal boreholes.' | SECTION TWO - DEFINITIONS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Definition: Geothermal Heat Pump |  |  | 'Open-Loop Geo-Thermal System-These systems draw groundwater from a source well, to a heat exchanger, and then discharge the water via injection wells or return flow wells.' Also: 'Ground Source Heat Pump Equipment Any components of a heating or cooling system in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems.' | SECTION TWO - DEFINITIONS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Setback - Wastewater | 100 | feet | Section 4.1 requires minimum isolation distances. The table lists wastewater-related sources including 'Community spray irrigation sites, sewage sludge and septage disposal sites' and 'Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits, single family spray irrigation system, etc.' at 100 feet, and 'Septic tanks, aerobic tanks, sewage pump tanks, holding tanks.' at 50 feet. The note states: 'Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above.' The application form likewise notes: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Setback - Animal Enclosures | 100 | feet | The Section 4.1 isolation-distance table includes 'Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure.' The application-form table gives this distance as 200 feet and notes: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Setback - Sewer Lines | 50 | feet | The Section 4.1 table lists 'Gravity sewer lines and drains carrying domestic sewage or industrial waste (unless item 9 applies)' and 'Sewer lines and drains carrying domestic sewage or industrial waste under pressure (except welded steel pipe or concrete encased pipe).' The application-form table gives these distances as 50 feet, with a narrower 10-foot case for specified gravity sewage lines using certain pipe materials. The note states: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Setback - Water Bodies | 12.5 | feet | Section 4.1 states: 'For all wells, minimum isolation distances shall be maintained...' The table lists 'Delineated wetlands or 100-year floodplain' at 25 feet, and the note provides: 'Closed loop geothermal systems shall meet one half the isolation distances noted with an asterisk (*) above.' The application form separately states: 'Note: Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *' for starred items only, but in the adopted regulations table the wetland/floodplain row is listed among isolation distances for all wells at 25 feet. | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Setback - Hazardous Materials/Fertilizers | 150 | feet | Section 4.1's table includes 'Commercial preparation area or storage area of hazardous spray materials, fertilizers or chemicals; salt piles.' The application-form table gives this isolation distance as 300 feet and notes: 'Closed loop Geothermal Systems, shall meet one half the isolation distances noted with an *.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / Individual Residential Water-Supply Isolation Distances | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Minimum Well Depth | 30 | feet | Section 4.2(a) states: 'The casing shall be carried to a minimum depth of (30) feet and (5) feet into hard bedrock or other impervious strata, whichever is deeper, and grouted in place.' | SECTION FOUR - CONSTRUCTION SPECIFICATIONS / 4.2 Casing | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Permit |  |  | Section 7.1(b): 'The proposed system design must be submitted and approved by the Department prior to installation. Isolation distances according to Section 4.1 must be confirmed.' Section 7.3(b): 'The proposed system design must be submitted to and approved by the Department prior to construction.' Section 7.2(d): 'The person requesting a geothermal permit from the Department is required to submit proof of an NPDES permit or exemption with any application.' | SECTION SEVEN GEO-THERMAL WELLS / SECTION THREE - APPLICATION TO CONSTRUCT OR MODIFY | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Inspection |  |  | Section 5.2(a): 'A BCDH representative is to be on site to observe the installation of the well casing,' Section 5.2(b): 'A BCDH representative is to be on-site to observe the grouting of the well and any other inspection during the well construction.' Section 7.3(c): 'Prior to construction, a site meeting with the Department will be required to layout the proposed design under actual field conditions.' Also, 'The system must be pressure tested prior to backfilling or grouting but after flushing the pipe to remove debris.' | SECTION FIVE - INSPECTION / SECTION SEVEN GEO-THERMAL WELLS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Licensed Driller |  |  | Section 6.1(a): 'Only well drillers with a PA DCNR license shall be permitted to construct individual residential water supply wells. Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation.' Section 7.2(b): 'Only PA DCNR approved well drillers using PA DCNR approved well drilling rigs shall drill the withdraw and return flow wells for this type of system.' | SECTION SIX - WELL DRILLERS / SECTION SEVEN GEO-THERMAL WELLS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Certification |  |  | The ordinance specifies concrete credentials: 'Well Driller - A person who is licensed by the state of Pennsylvania to drill wells, or in the case of geo-thermal wells has IGSHPA certification.' Section 6.1(a): 'Geothermal well drillers shall have a PA DCNR or IGSHPA accreditation.' Section 7.1(a): 'Installation must be by a PA DCNR approved well driller or a IGSHPA accredited geothermal system installer.' Section 7.3(b): 'The system design shall be made by a IGSHPA accredited person or firm or an engineering firm familiar with loading and heat transfer requirements for the site specific proposed HVAC system.' | SECTION TWO - DEFINITIONS / SECTION SIX - WELL DRILLERS / SECTION SEVEN GEO-THERMAL WELLS | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Decommissioning |  |  | The Northampton Township form states: 'In event this well is abandoned, owner will assume responsibility for plugging or sealing it in a manner satisfactory to the Township.' Section Eleven provides: 'A permit must be obtained prior to abandoning all wells.' 'Abandonment procedures shall be subject to the BCDH inspection.' 'Well abandonment procedures must minimally comply with the specifications referenced in the PA DEP/DCNR Water Well Abandonment Guidelines.' 'A copy of the PA DEP/DCNR Water Well Abandonment Form shall be submitted to the BCDH within ten days of abandonment.' | GENERAL CONDITIONS / SECTION ELEVEN - WELL ABANDONMENT | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Northampton | 4201754688 | Other Prohibitions/Regulations |  |  | Section 7.2(f): 'Under no circumstances may additives of any kind be placed in this type of geothermal system to enhance heat transfer or reduce freezing points of the circulating water.' Section 7.3(c) also states: 'Copper piping is not acceptable for heat transfer use.' | SECTION SEVEN GEO-THERMAL WELLS / 7.2 Open-Loop Geo-thermal HVAC Systems | 2011 | https://www.northamptontownship.com/media/1521/well-permit-application-and-well-information.pdf
Pennsylvania | Bucks | Plumstead | 4201761616 | Noise Limits | 28 | dBA | "Measurements can also be taken with approved equipment in weighted terms, with limits as shown below..." Table: "dBA ¦ 46 ¦ 56." The section also states: "The sound level of any operation... shall not exceed the levels designated below." | § 27-2310 Noise | 2026 | https://ecode360.com/14150522
Pennsylvania | Bucks | Solebury | 4201771752 | Definition: Well |  |  | "Boring/Borehole. A penetration of soil and/or rock that is augured, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed which is generally cylindrical in shape and whose diameter is generally smaller than its depth of penetration." | §27-3202. Definitions | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Definition: Geothermal |  |  | "Alternative Energy. A renewable source of energy generated from solar, water, wind, geothermal, or other renewable sources, which is capable of providing energy and utility provisions to a permitted use." | §27-3202. Definitions | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Definition: Geothermal Heat Pump |  |  | "Geothermal System. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earthsource heat pump system, and a GeoExchange system." Also: "Ground Source Heat Pump. A geothermal heat pump that uses the earth itself as a heat source and heat sink. It is coupled to the ground by means of a closedloop heat exchanger installed horizontally or vertically underground." | §27-3202. Definitions | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Right of Way | 15 | feet | Table I states: "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." The ordinance also states, "Geothermal systems shall not encroach on public drainage, utility roadway or trail easements of any nature." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance or twenty five Feet (25) feet from any property line." Table I also lists "Dedicated public right-of-way and property lines — at least 10 feet," but the more restrictive stated property-line setback is 25 feet. | §27-3204.3.K | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Building Foundation | 10 | feet | Table I lists: "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved) — at least 10 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Wastewater | 50 | feet | Table I lists multiple wastewater-related setbacks: "Septic tanks, aerobic tanks, or holding tanks — at least 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields — 25-50 feet"; "Sewage seepage pits and cesspools — at least 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites — at least 25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Animal Enclosures | 25 | feet | Table I lists: "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Fuel (above ground) | 25 | feet | Table I lists: "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Water Lines | 15 | feet | Table I lists: "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Sewer Lines | 15 | feet | Table I lists: "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 5-'15 feet or according to easement" and "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Water Bodies | 25 | feet | Table I lists: "Delineated wetlands, flood plains, lakes, ponds, or other surface waters — 10-25 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table I lists: "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles — 300 feet 100-150 feet (if borehole is cased and grouted inside and out)." It also lists "Any other source or potential source of pollution — at least 300 feet." | §27-3204.3.O; Table I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Noise Limits | 55 | dBA | "Audible sound from any alternative and/or emerging energy facility shall not exceed 55 dBA, as measured at the applicant's property line." | §27-3204.7.A | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Maximum Well Depth | 15 | feet | "All horizontal closed loop systems shall be no more than 15 feet deep." | §27-3204.3.I | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." Also, "No alternative or emerging energy facility shall be located, modified, or constructed within Solebury Township unless a permit has been issued to the landowner in accordance with the provisions of this Section." | §27-3204.3.B; §27-3206.1 | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well drilier, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well. In all cases, the well drilling rig must also be approved by Pennsylvania Department of Environmental Protection." | §27-3204.3.M | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well drilier, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well." | §27-3204.3.M | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Decommissioning |  |  | "The geothermal system must be installed, maintained, and decommissioned in standards conforming to IGSHPA Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards..." Also, "If a geothermal system remains nonfunctional or inoperative for a continuous period of one (1) year (or longer timeframe where approved by the Township), the system/well piping should be drained of all heat transfer fluids and all well heads should be temporarily sealed and secured with a locking water-tight cap unless the well is otherwise abandoned/sealed in accordance with BCDH/Township regulations." Chapter-wide decommissioning also states: "The landowner or energy facility operator shall, at its expense, complete decommissioning of the alternative or emerging energy facility within 12 months after the end of the useful life..." and "All disturbed earth shall be restored, graded, and reseeded." | §27-3204.3.G; §27-3204.3.T; §27-3209.1-4 | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Solebury | 4201771752 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems shall be prohibited." | §27-3204.3.C | 2019 | https://ecode360.com/SO1688/laws/LF2420459.pdf
Pennsylvania | Bucks | Springfield | 4201773016 | Definition: Geothermal Heat Pump |  |  | "Accessory Geothermal Heat Pump. A ground-integrated facility to provide heating and cooling to structures on a lot." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Roads | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "At least 10 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Right of Way | 15 | feet | Table 1 requires setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "At least 15 feet or outside easement." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Property Lines | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "At least 10 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Building Foundation | 10 | feet | Table 1 requires setback from "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" of "At least 10 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Wastewater | 50 | feet | Table 1 requires setbacks from wastewater-related features including "Septic tanks, aerobic tanks, or holding tanks" at "At least 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields" at "25-50 feet"; "Sewage seepage pits and cesspools" at "At least 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites" at "At least 25 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Animal Enclosures | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "At least 25 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Fuel (above ground) | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "At least 25 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Water Lines | 15 | feet | Table 1 requires setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "At least 15 feet or outside easement." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Sewer Lines | 15 | feet | Table 1 lists "Gravity sewer lines and drains carrying domestic sewage or industrial waste" at "5-15 feet or according to easement" and "Existing water and forced sewer buried utilities and/or utility trenches" at "At least 15 feet or outside easement." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Water Bodies | 25 | feet | Table 1 lists setbacks for geothermal boreholes/supply/return wells from "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" at "10-25 feet" and from an "Identified NPL Site (Superfund) plume area" at "At least 300 feet." The ordinance also includes "Any other source or potential source of pollution" at "At least 100 feet." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table 1 requires setback from "Preparation area of storage area of hazardous spray materials, fertilizers of chemicals, or salt piles" of "300 feet; 100-150 feet (if borehole is cased and grouted inside and out)." | (16) H-16 Accessory Geothermal Heat Pump; Table 1 | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Permit |  |  | "It shall be unlawful to install a new geothermal subsurface facility (wells, horizontal or sub-aqueous tubing emplacements) or modify an existing subsurface facility without a valid permit." "Prior to constructing a new geothermal facility or modifying an existing system; property owner shall file all appropriate applications with Springfield Township, Bucks County, or other regulating agency and pay all applicable fees." "If the geothermal facility construction is not completed in two years of the permit issuance date, the approval to construct shall expire." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Inspection |  |  | "Springfield Township must field verify the location of the proposed geothermal installations and all applicable isolation distances." "The IGSHPA recommendation that the heat exchanger be isolated and tested to 150 percent of design pressure or 300 percent of system operating pressure shall be followed. No leaks shall occur within a 30-minute period." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Licensed Driller |  |  | "Only a PA DEP-licensed well driller or an International Ground Source Heat Pump Association (IGSHPA)-accredited geothermal system installer shall conduct trench excavation or drilling of a geothermal well. In all cases, the well drilling rig must also be approved by PA DEP." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Certification |  |  | "Only a PA DEP-licensed well driller or an International Ground Source Heat Pump Association (IGSHPA)-accredited geothermal system installer shall conduct trench excavation or drilling of a geothermal well." "The standing column well geothermal system... shall be installed by a geothermal well installation contractor who is certified in the proper installation methods as specified by the manufacturer." "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer..." | (16) H-16 Accessory Geothermal Heat Pump | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Decommissioning |  |  | "In the event of the proposed discontinuance of the use of the ground source heat pump system, a system closure plan will be prepared and submitted to Springfield Township for its approval." "A geothermal system shall be abandoned in a manner acceptable to Springfield Township and shall comply with the laws, rules, and regulations applicable to the abandonment of water wells. Any and all heat transfer fluid must be removed by displacement with grout in a manner acceptable to Springfield Township. The top of the borehole must be uncovered and capped with grout in a manner acceptable to Springfield Township." | (16) H-16 Accessory Geothermal Heat Pump; (i)-(j) | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Springfield | 4201773016 | Open-loop Prohibitions |  |  | "Only closed loop systems or standing column well systems are allowed. Open loop systems with separate supply and reinjection wells or surface discharge sites are prohibited." | (16) H-16 Accessory Geothermal Heat Pump; (h) Geothermal Heat Pump Regulations | 2023 | https://codelibrary.amlegal.com/codes/springfieldpa/latest/springfieldt_pa/0-0-0-5322
Pennsylvania | Bucks | Tinicum | 4201776784 | Definition: Geothermal Heat Pump |  |  | "Geothermal system, closed loop: An energy system that circulates water or a water solution through the earth to use and extract heat without drawing groundwater and discharging the water or solution into an aquifer or aquitard." "Geothermal system, open loop: An energy system that circulates water or a water solution through the earth to use and extract heat by drawing groundwater into the system and/ or discharging the water or solution into an aquifer or aquitard." | SECTION 1. Section 809.03 | 2025 | https://tinicumtownship.org/wp-content/uploads/2025/04/272-Ordinance-Closed-Loop-signed-adopted.pdf
Pennsylvania | Bucks | Tinicum | 4201776784 | Permit |  |  | "A Well Permit Application for a closed loop geothermal system shall follow the procedures contained in Subsection C. above." Also, "No Well Permit shall be issued for an open loop geothermal system." | SECTION 2. Section 809.12(E)(1)-(2) | 2025 | https://tinicumtownship.org/wp-content/uploads/2025/04/272-Ordinance-Closed-Loop-signed-adopted.pdf
Pennsylvania | Bucks | Tinicum | 4201776784 | Open-loop Prohibitions |  |  | "Open loop geothermal systems are not permitted anywhere within Tinicum Township. No Well Permit shall be issued for an open loop geothermal system." | SECTION 2. Section 809.12(E)(2) | 2025 | https://tinicumtownship.org/wp-content/uploads/2025/04/272-Ordinance-Closed-Loop-signed-adopted.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Definition: Well |  |  | "GEOTHERMAL WELL - a well installed for the purpose of heating or cooling a facility. These shall include wells drilled as supply and/or return wells for open-loop systems, or closed-loop geothermal boreholes." | §302. Definitions | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP EQUIPMENT - any components of a heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | §302. Definitions | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Roads | 10 | feet | For closed-loop geothermal boreholes, §305.3.A table lists under miscellaneous: "Dedicated road right-of-way — 10 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Right of Way | 5 | feet | For closed-loop geothermal boreholes, §305.3.A table lists under miscellaneous: "Property lines, rights-of-way, easements — 5 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Property Lines | 5 | feet | For closed-loop geothermal boreholes, §305.3.A table lists under miscellaneous: "Property lines, rights-of-way, easements — 5 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Wastewater | 50 | feet | For closed-loop geothermal boreholes, §305.3.A table requires: "Surface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits — 50 feet" and "Spray irrigation site perimeter, sewage sludge and seepage disposal sites — 50 feet"; also "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks — 25 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Fuel (above ground) | 300 | feet | For closed-loop geothermal boreholes, §305.3.A table states: "Surface or subsurface containers or tanks of greater than 1,000 gal. used for storage of materials which cannot be properly renovated by passage through soil. This includes, but is not limited to, gasoline and all other petroleum products. (If borehole is cased and grouted inside and out) — 300 feet (150 feet)" and "Surface or subsurface containers or tanks of 1,000 gal. or less ... including ... gasoline and all other petroleum products ... — 30 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Sewer Lines | 5 | feet | For closed-loop geothermal boreholes, §305.3.A table lists "Sewer drains, public sewer laterals — 5 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Water Bodies | 10 | feet | For closed-loop geothermal boreholes, §305.3.A table states minimum isolation distances to pollution sources, including "Delineated wetlands, floodplains, lakes, ponds or other surface waters — 10 feet." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Setback - Hazardous Materials/Fertilizers | 300 | feet | For closed-loop geothermal boreholes, §305.3.A table requires setbacks from chemical-related sources: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles. (If borehole is cased and grouted inside and out) — 300 feet (150 feet)." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Minimum Well Depth | 40 | feet | §305.2.A provides that open-loop geothermal delivery and return wells "must meet all Authority isolation distance requirements listed in this Part." §303.2.A states: "The source of supply shall be from a water bearing formation drawn not less than forty (40) feet from the ground surface." | §303. Drilled Water Supply Wells; §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Permit |  |  | §305.3.C states: "Closed-loop geothermal boreholes shall be permitted in accordance with §310. Each borehole must be permitted using a single application. A separate fee will be charged for each borehole." §310.2 provides: "It shall be unlawful for any person to locate, drill or have drilled any well ... until a permit ... shall have been issued by the Authority." §310.3.B states: "No monitoring well, test well, or geothermal well shall be used until it has received written approval for use from the Authority." | §305. Geothermal Wells; §310. Permit Procedure | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Licensed Driller |  |  | §305.1 states: "Licenses Only Pennsylvania-licensed well drillers shall install wells within Warminster Township." §302 also defines "GEOTHERMAL WELL INSTALLATION CONTRACTOR" as an individual responsible for drilling geothermal boreholes who "is licensed as a well contractor and geothermal well installation contractor by the Department." | §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Certification |  |  | §302 defines "GEOTHERMAL WELL INSTALLATION CONTRACTOR" as an individual responsible for geothermal borehole drilling who "is licensed as a well contractor and geothermal well installation contractor by the Department." §305.3.B.3 states: "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | §302. Definitions; §305. Geothermal Wells | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warminster | 4201780952 | Decommissioning |  |  | §312.1 states: "Whenever a public water supply or another well replaces an existing well, it shall be the responsibility of the property owner to have the existing well properly abandoned by a licensed well contractor in accordance with §307 Abandonment of Wells... No well may exist in a decommissioned state." §312.2 adds: "All wells that are to be abandoned, or wells that are removed from use or a useable status such as decommissioned wells or any well that meets the definition of an abandoned well according to §302. shall be abandoned according to the requirements of §307." §307 requires one of the listed abandonment methods to be used and that a sealing report be filed with the Authority. | §307. Abandonment of Wells; §312. Water Source Replacements | 2009 | https://warminstertownship.org/wp-content/uploads/2013/03/SWM_ord_adopted_091009.pdf
Pennsylvania | Bucks | Warrington | 4201781048 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY — Energy generated due to variations in the subsurface temperature of soil, and/or use of hot springs, ground- or surface water temperature gradients. There are two basic types of geothermal systems, closed loop, and open loop. Closed-loop systems that take advantage of soil temperature gradients can be either horizontal or vertical and utilize piping buried at different depths in the earth's soil. Open-loop systems utilize either ground (well) or surface (lake/stream) water as the heat exchange medium, taking advantage of water temperature gradients in the earth or in bodies of surface water. Open-loop systems are strictly prohibited in Warrington Township." | § 370-202. Definitions of terms | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | 4201781048 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY FACILITY — A passive or mechanical energy generation facility, whose main purpose is to convert geothermal energy into thermal energy to a permitted use. Such facilities may use closed loop piping, heat exchangers, and mechanical infrastructure and related appurtenant facilities." | § 370-202. Definitions of terms | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | 4201781048 | Permit |  |  | § 370-1003.C(1): "Geothermal energy systems are permitted provided that a permit is obtained, and such facilities are limited to heating and cooling of buildings and located on a lot with a permitted use in accordance with the applicable provisions of this Ordinance." § 370-1005.A: "No alternative or emerging energy facility shall be located, modified or constructed within Warrington Township unless a permit has been issued to the landowner in accordance with the provisions of this section of this Article. Geothermal energy systems are exempt from the permit application process, but not exempt from the special exception application process." | § 370-1003.C(1) and § 370-1005.A | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | 4201781048 | Open-loop Prohibitions |  |  | In the geothermal definition, the ordinance states: "Open-loop systems are strictly prohibited in Warrington Township." | § 370-202. Definitions of terms | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warrington | 4201781048 | Other Prohibitions/Regulations |  |  | "Geothermal energy systems are permitted provided that a permit is obtained, and such facilities are limited to heating and cooling of buildings and located on a lot with a permitted use in accordance with the applicable provisions of this Ordinance." | § 370-1003.C(1) | 2021 | https://cms3.revize.com/revize/warringtontownship/Documents/Department/Planning%20Development%20Zoning/2021-08-25-Final-Zoning-Ordinance.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System. A system that uses a heat pump to extract heat from the earth in heating and / or reject heat into the earth in cooling mode. It may also be referred to a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." | Section 195-16.1(10) G(10) Geothermal Energy System | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Roads | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "at least 10 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Property Lines | 10 | feet | Table 1 requires setback from "Dedicated public right-of-way and property lines" of "at least 10 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Building Foundation | 10 | feet | Table 1 requires setback from "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" of "at least 10 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Wastewater | 50 | feet | Table 1 includes multiple wastewater-related setbacks: "Septic tanks, aerobic tanks, or holding tanks" — "at least 25 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields" — "at least 50 feet"; "Sewage seepage pits and cesspools" — "at least 25 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites" — "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Animal Enclosures | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Fuel (above ground) | 25 | feet | Table 1 requires setback from "Farm silos, barnyards, privies, and fuel tanks" of "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Water Lines | 15 | feet | Table 1 lists "Existing water and forced sewer buried utilities and/or utility trenches" with a required setback of "at least 15 feet or outside easement." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Sewer Lines | 15 | feet | Table 1 requires setback from "Gravity sewer lines and drains carrying domestic sewage or industrial waste" of "at least 15 feet or according to easement." It also lists "Existing water and forced sewer buried utilities and/or utility trenches" at "at least 15 feet or outside easement." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Water Bodies | 25 | feet | Table 1 requires geothermal boreholes/wells to be setback from "Delineated wetlands, flood plains, lakes, ponds, or other surface waters" by "at least 25 feet." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Table 1 lists "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" with a setback of "at least 300 feet" and "at least 150 feet (if borehole is cased and grouted inside and out)." | Table 1 | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without all necessary permits, including but not limited to, zoning permits, and grading permits. Permit applications shall be accompanied by a site plan, prepared, signed, and sealed by a qualified professional licensed in the Commonwealth of Pennsylvania, which identifies property lines, lot area, location of existing natural and manmade features, location of the proposed closed-loop geothermal system, bore holes, ownership information for adjoining properties, and setback measurements from property lines, street lines, and occupied buildings." | Section 195-16.1(10) G(10)(1) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Inspection |  |  | "The landowner shall consult with a qualified inspector when requested by the Township to determine if the geothermal system is operating in accordance with the specifications of the manufacturer. A copy of the report shall be submitted to the Township and the Township shall have the right to inspect." Also, "An independent and certified professional engineer may be retained by the Township to inspect the decommissioning of the geothermal system. All such inspection fees shall be paid by the applicant or landowner." | Section 195-16.1(10) G(10) Maintenance; Decommissioning | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall drill a geothermal well. In all cases, the well drilling rig must also be approved by Pennsylvania Department of Environmental Protection." | Section 195-16.1(10) G(10) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall drill a geothermal well." | Section 195-16.1(10) G(10) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Decommissioning |  |  | "The landowner or Geothermal Energy System operator shall, at its expense, complete decommissioning of the geothermal system within 12 months after the end of the useful life. The geothermal system will presume to be at the end of its useful life if no energy is generated for a continuous period of 12 months. The removal of the above-ground geothermal system components shall be completed within 6 months of decommissioning. All disturbed earth shall be restored, graded, and reseeded. The landowner shall secure a permit to decommission the Geothermal Energy System... If the landowner or facility operator fails to complete decommissioning during the prescribed period of 12 months, the Township may take such measures as necessary to complete decommissioning..." | Section 195-16.1(10) G(10) Decommissioning | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Warwick | 4201781144 | Open-loop Prohibitions |  |  | "Open-loop geothermal systems (geothermal systems which expel the water after it leaves the structure) are prohibited." | Section 195-16.1(10) G(10)(2) | 2021 | https://ecode360.com/WA1313/laws/LF1429063.pdf
Pennsylvania | Bucks | Wrightstown | 4201786624 | Permit |  |  | The fee schedule states: "In the event construction is started without the required zoning and building permit(s), permit fees will be doubled." It also lists a geothermal-specific permit item under "TANK PERMITS": "Geothermal $200 Plus Inspection Fees." | BUILDING, ZONING, & ELECTRICAL PERMITS / TANK PERMITS | 2026 | https://www.wrightstownpa.org/media/2291/2026-fee-schedule-final.pdf
Pennsylvania | Bucks | Wrightstown | 4201786624 | Inspection |  |  | The schedule provides: "Residential and Commercial Building and Fire Code Inspection Fees- $100 per inspection," "A reinspection required as a result of incomplete or improper work will be invoiced to the permit holder at an additional charge of $100 per inspection," and under "TANK PERMITS" lists "Geothermal $200 Plus Inspection Fees." | BUILDING, ZONING, & ELECTRICAL PERMITS / TANK PERMITS | 2026 | https://www.wrightstownpa.org/media/2291/2026-fee-schedule-final.pdf
Pennsylvania | Cambria | Adams | 4202100308 | Definition: Geothermal |  |  | "Renewable energy sources," "Any method, process or substance whose supply is rejuvenated through natural processes and, subject to those natural processes, remains relatively constant, including, but not limited to, bio-mass conversion, geothermal energy, solar and wind energy and hydroelectric energy and excluding those sources of energy used in the fission and fusion processes." | SECTION 202 Definitions | 2007 | https://cambriaplanning.org/wp-content/uploads/2015/03/adamstownnshipzoningcomplete.pdf
Pennsylvania | Centre | Ferguson | 4202725624 | Definition: Well |  |  | "A bored, drilled, driven, or dug well for the emplacement of fluids into the ground (except open loop geothermal heat pump systems)." |  | 2024 | https://ecode360.com/36116571
Pennsylvania | Centre | Ferguson | 4202725624 | Definition: Geothermal Heat Pump |  |  | "A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump. The discharge water from the water-source heat pump may be returned to the subsurface through a recharge well or infiltration bed, or may be discharged into a pond, lake, or stream. A spring may also be the source of the ground water supply." |  | 2024 | https://ecode360.com/36116571
Pennsylvania | Centre | Ferguson | 4202725624 | Maximum Well Depth | 20 | feet | "A borehole which is constructed to receive heat exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20 feet below grade as the subsurface conditions warrant." |  | 2024 | https://ecode360.com/36116571
Pennsylvania | Centre | Halfmoon | 4202731992 | Definition: Well |  |  | "VERTICAL CLOSED-LOOP BOREHOLE. A borehole which is constructed to receive heat-exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20 feet below grade as the subsurface conditions warrant." "DECOMMISSIONED VERTICAL CLOSED-LOOP BOREHOLE. A vertical closed-loop borehole whose original purpose and use have been permanently discontinued or which is in such a state of disrepair that its original purpose cannot be reasonably achieved." | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Centre | Halfmoon | 4202731992 | Definition: Geothermal |  |  | "CLOSED-LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere. The heat transfer fluid is potable or beneficial reuse water and may have approved antifreeze added." "DIRECT-EXCHANGE (DX) GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system where the heat pump refrigerant is circulated through metal piping installed in vertical, inclined, or horizontal boreholes." "OPEN-LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system that utilizes a water-supply well and a water pump to deliver groundwater to a water-source heat pump." "STANDING-COLUMN GEOTHERMAL SYSTEM. A type of open-loop geothermal heating and/or cooling system that circulates groundwater from a water well through a water-source heat pump and returns the discharge water ... to the same water well it was pumped from." | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Centre | Halfmoon | 4202731992 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEATING AND/OR COOLING SYSTEM. A system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a 'geothermal heat pump system,' a 'ground-coupled heat pump system,' an 'earth-source heat pump system,' and a 'GeoExchange system.'" | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Centre | Halfmoon | 4202731992 | Minimum Well Depth | 20 | feet | "VERTICAL CLOSED-LOOP BOREHOLE. A borehole which is constructed to receive heat-exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20 feet below grade as the subsurface conditions warrant." | § 255-7B Definitions | 2023 | https://ecode360.com/38330271
Pennsylvania | Chester | Charlestown | 4202912744 | Definition: Geothermal Heat Pump |  |  | The ordinance uses the term in operative text as: "geothermal systems and related boreholes for geothermal heat pump systems." | § 27-2303 General Provisions, Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | 4202912744 | Setback - Property Lines | 10 | feet | "Minimum Setbacks. Geothermal boreholes and wells shall be set back in accordance with the following: (4) A minimum of 10 feet from any property line." | § 27-2303(D)(4) | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | 4202912744 | Setback - Wastewater | 50 | feet | "Minimum Setbacks. Geothermal boreholes and wells shall be set back in accordance with the following: (1) A minimum of 50 feet from on-lot sewage disposal systems, or spray irrigation site perimeter." | § 27-2303(D)(1) | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | 4202912744 | Setback - Water Bodies | 10 | feet | "Minimum Setbacks. Geothermal boreholes and wells shall be set back in accordance with the following: (2) A minimum of 10 feet from surface waters, floodplains or wetlands." | § 27-2303(D)(2) | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | 4202912744 | Permit |  |  | "Permit Required. No person shall install, construct or otherwise implement a new alternative energy system within the Township without first obtaining the required permit(s) from the Township. No person shall modify any existing alternative energy system in the Township without first obtaining a permit from the Township." For geothermal specifically: "A zoning permit and building permit, under the Pennsylvania Uniform Construction Code, shall be required." | § 27-2303 General Provisions; Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | 4202912744 | Decommissioning |  |  | "The geothermal system shall be installed, maintained, and decommissioned in conformance with standards established by the IGSHPA Closed-loop/Geothermal Heat Pump Systems Design and Installation Standards, as same may be amended from time to time." | § 27-2303 General Provisions, Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | Charlestown | 4202912744 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be permitted in the Township." | § 27-2303 General Provisions, Regulations for Geothermal Systems | 2017 | https://ecode360.com/31265721
Pennsylvania | Chester | East Bradford | 4202920824 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the earth’s thermal properties, in conjunction with electricity, to provide for the heating and cooling of Buildings." | SECTION 115-201. DEFINITIONS OF TERMS |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Bradford | 4202920824 | Permit |  |  | "No person shall repair, modify, install, construct, or otherwise implement any Alternative Energy System(s) within the Township, without first obtaining all applicable permits from the Township." "A zoning permit and all other applicable permits shall be obtained prior to installation of any Alternative Energy System." For geothermal specifically: "An approved Chester County Health Department permit shall be included with the permit application submitted to the Township. If the total land disturbance is in excess of one (1) acre, an approved Chester County Conservation District and/or NPDES permit may also be required as part of the permit application." | SECTION 115-1703. ALTERNATIVE ENERGY; B. Applicability; C. General requirements for all Alternative Energy Systems; F. Geothermal Energy Systems |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Bradford | 4202920824 | Certification |  |  | "The design, installation and operation of Geothermal Energy Systems shall be permitted in conformance with all applicable regulations under Section 501 of the Chester County Health Department Rules and Regulations and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | SECTION 115-1703(F)(2) |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Bradford | 4202920824 | Decommissioning |  |  | General alternative energy systems: "The property owner shall be responsible to remove or properly restore any Alternative Energy System when determined to be a safety hazard by the Township or other regulatory authority." "If any Alternative Energy System is ever removed, any earth disturbance as a result of the removal of the any Alternative Energy System shall be graded and reseeded to the satisfaction of the Township." Geothermal-specific: "where the use of any Geothermal Energy System is abandoned, the property owner shall be responsible to cap and seal the in-ground portion(s) of the system. The property owner may further be required to evacuate (pump out) the fluid(s) in the system and to fill the borehole(s) with bentonite or an acceptable alternative." | SECTION 115-1703(C)(10)-(11); SECTION 115-1703(F)(4) |  | https://www.eastbradford.org/DocumentCenter/View/2268/Third-Draft-East-Bradford-Township-Zoning-Ordinance-Update
Pennsylvania | Chester | East Caln | 4202920920 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: An energy-generating system utilizing the earth's thermal properties to meet all or part of the heating requirements of the on-site user. Specific terms include: ... CLOSED-LOOP GEOTHERMAL SYSTEM A type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, nontoxic heat transfer fluid; a heat pump; and an air distribution system; intended to utilize the earth's constant temperature for improved heat pump efficiency. ... OPEN-LOOP GEOTHERMAL SYSTEM A type of geothermal heating and/or cooling system that utilizes a water-supply well, or other sources, and a pump to deliver groundwater to a heat exchanger." | § 225-3 Definitions and word usage | 2026 | https://ecode360.com/10740718
Pennsylvania | Chester | East Caln | 4202920920 | Open-loop Prohibitions |  |  | "OPEN-LOOP GEOTHERMAL SYSTEM ... The discharge water from the heat exchanger may be returned to the subsurface through a recharge well or infiltration bed or may be discharged into a pond, lake, or stream. [PROHIBITED]" | § 225-3 Definitions and word usage | 2026 | https://ecode360.com/10740718
Pennsylvania | Chester | East Marlborough | 4202921480 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM An energy generating system that uses the earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | SECTION 202. DEFINITIONS OF TERMS | 2019 | https://www.eastmarlborough.org/wp-content/uploads/2019-zoning-ordinance.pdf
Pennsylvania | Chester | East Vincent | 4202922000 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy generating system that uses the earth's thermal properties, in conjunction with electricity, to provide for the heating and cooling of buildings." | SECTION 27-1925.B. Definitions | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | East Vincent | 4202922000 | Permit |  |  | "A zoning permit and all other applicable permits shall be required prior to installation of any renewable energy system." For geothermal specifically: "An approved Chester County Health Department permit shall be submitted as part of the permit application. Based on its proposed overall land disturbance, an approved Chester County Conservation District permit may also be required as part of the permit application." Also, "Any application for a geothermal energy system shall include a erosion and sedimentation control plan in accordance with the East Vincent Township Subdivision and Land Development Ordinance." | SECTION 27-1925.C.1; SECTION 27-1925.G.1; SECTION 27-1925.G.3 | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | East Vincent | 4202922000 | Certification |  |  | "The design, installation and operation of geothermal energy systems shall be permitted in conformance with all applicable regulations under Section 501 of the Chester County Health Department Rules and Regulations and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | SECTION 27-1925.G.2 | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | East Vincent | 4202922000 | Decommissioning |  |  | "If the geothermal energy system enters into a state of disrepair, it shall be the responsibility of the property owner to properly maintain the geothermal energy system or to decommission the system within six (6) months from the date the system enters such a state or immediately in any case determined to be a safety hazard." "Where the use of any geothermal energy system is abandoned, it shall be the responsibility of the property owner to cap and seal the in-ground portion(s) of the system. The property owner may further be required to evacuate (pump out) the fluid(s) in the system and to fill the borehole(s) with bentonite or an acceptable alternative." "If a geothermal energy system is ever removed, any earth disturbance as a result of its removal shall be in accordance with an approved erosion and sediment control plan and fully graded and reseeded to the satisfaction of the Township." | SECTION 27-1925.G.5-6 | 2024 | https://www.eastvincent.org/vertical/sites/%7B5B8F1E55-6CA8-450E-BB40-12A8385B1313%7D/uploads/EVT_ZO_and_Map_-_PC_Review_Draft_(5).pdf
Pennsylvania | Chester | Franklin | 4202927376 | Definition: Well |  |  | "WELL — Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the location, acquisition or artificial recharge of groundwater or for the installation of ground source heat pump equipment. This includes, but is not limited to, test wells, test borings, geothermal and monitoring wells, in addition to wells to be utilized as individual or semipublic or public water supplies." | § 26-117 Definitions | 2009 | https://ecode360.com/30847013
Pennsylvania | Chester | Franklin | 4202927376 | Permit |  |  | § 26-102 states: "This Part shall apply to all wells to be drilled..." and "This Part shall further apply to the reconstruction, major repair and other changes to existing wells." § 26-112 states: "Geothermal well systems shall meet all standards as outlined in Chester County Health Departments Rules and Regulations, § 501.14.3." | § 26-102 Applicability; § 26-112 Geothermal Wells | 2009 | https://ecode360.com/30847013
Pennsylvania | Chester | Franklin | 4202927376 | Licensed Driller |  |  | "WELL DRILLER — Any water well contractor licensed by the Commonwealth of Pennsylvania, his employees or representatives in responsible charge of drilling or otherwise constructing a well." | § 26-117 Definitions | 2009 | https://ecode360.com/30847013
Pennsylvania | Chester | Kennett | 4202939344 | Definition: Well |  |  | "BOREHOLES - A penetration of soil and/or rock that is augured, drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed which is generally cylindrical in shape and whose diameter is generally smaller than its depth of penetration. Used in closed vertical loop geothermal systems." | Section 2, Chapter 240, § 240-201, Definition of Terms | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | Section 2, Chapter 240, § 240-201, Definition of Terms | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, non-toxic heat transfer fluid; a heat pump; and an air distribution system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere..."; "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a water-supply well, or other source, and a pump to deliver groundwater to a heat exchanger." | Section 2, Chapter 240, § 240-201, Definition of Terms | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, Geothermal Energy Systems shall be set back a minimum distance of twenty-five (25) feet from any property line." | § 240-1943.A, Setback requirements | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Setback - Wastewater | 100 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 100 feet from on-lot sewage disposal systems." | § 240-1943.A, Setback requirements | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Setback - Public Water | 200 | feet | "The return well shall be located a minimum distance of two hundred (200) feet from wells on adjacent properties." | § 240-1943.A.10(c)(ii), Underground injection of water | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Permit |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards... and shall comply with the Township Building Code and with all other applicable Township requirements. A zoning permit and building permit, consistent with the PA Uniform Construction Code, shall be required. Applicable manufacturer specifications shall be submitted as part of the application for any permit." For open-loop systems, "Prior to the issuance of any permit for the installation of an open-loop Geothermal Energy System, the Township shall receive a report of the yield of the supply and recharge of the groundwater system..." | § 240-1943.A.2, Design and permitting | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Decommissioning |  |  | "If the Geothermal Energy System is ever abandoned or enters into a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the Geothermal Energy System within six (6) months from the date the system enters such a state." "Any earth disturbance as a result of the removal or permanent sealing of the Geothermal Energy System shall be graded and reseeded." | § 240-1943.A.11-.12, Abandonment or disrepair; Decommissioning | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Kennett | 4202939344 | Other Prohibitions/Regulations |  |  | "Extraction of water from surface waters shall be prohibited." "Discharge of water from open-loop systems into sanitary sewer systems shall be prohibited." "Discharge of water from open-loop systems into storm sewers, and onto roads, shall be prohibited." "Discharge of water from open-loop systems into a watercourse shall be prohibited." | § 240-1943.A.10(a)-(b), Open-loop Geothermal Energy Systems | 2012 | https://www.kennett.pa.us/DocumentCenter/View/257/Ordinance-200-Alternative-Energy-PDF
Pennsylvania | Chester | Penn | 4202958808 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: An energy generating system that uses the earth's thermal properties in conjunction with electricity to provide heating and cooling of buildings." | SECTION 201. DEFINITION OF TERMS | 2019 | https://www.penntownship.us/sites/g/files/vyhlif1061/f/uploads/penn_township_zoning_ordinances_adopted_2019.pdf
Pennsylvania | Chester | Pocopson | 4202961800 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." The ordinance also defines system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system..."; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM. A type of geothermal heating and/or cooling system..." | § 250-6 Definitions and word usage | 2026 | https://ecode360.com/6537874
Pennsylvania | Chester | Thornbury | 4202976568 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM An energy generating system that uses the Earth's thermal properties, in conjunction with electricity, to provide for the heating and cooling of buildings." | § 155-1619B Definitions |  | https://ecode360.com/36852550
Pennsylvania | Chester | Thornbury | 4202976568 | Permit |  |  | "A zoning permit and all other applicable permits shall be required prior to installation of any renewable energy system." For geothermal systems specifically: "An approved Chester County Health Department permit shall be submitted as part of the permit application. Based on its proposed overall land disturbance, an approved Chester County Conservation District permit may also be required as part of the permit application." Also, "Any application for a geothermal energy system shall include a stormwater management plan as required under Chapter 116." | § 155-1619C(1); § 155-1619F(1); § 155-1619F(3) |  | https://ecode360.com/36852550
Pennsylvania | Chester | Thornbury | 4202976568 | Certification |  |  | "The design, installation and operation of geothermal energy systems shall be permitted in conformance with all applicable regulations under Section 501 of the Chester County Health Department Rules and Regulations and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | § 155-1619F(2) |  | https://ecode360.com/36852550
Pennsylvania | Chester | Thornbury | 4202976568 | Decommissioning |  |  | "If the geothermal energy system enters into a state of disrepair, it shall be the responsibility of the property owner to properly maintain the geothermal energy system or to decommission the system within six months from the date the system enters such a state or immediately in any case determined to be a safety hazard." "Where the use of any geothermal energy system is abandoned, it shall be the responsibility of the property owner to cap and seal the in-ground portion(s) of the system. The property owner may further be required to evacuate (pump out) the fluid(s) in the system and to fill the borehole(s) with bentonite or an acceptable alternative." "If a geothermal energy system is ever removed, any earth disturbance as a result of its removal shall be in accordance with an approved erosion and sediment control plan and fully graded and reseeded to the satisfaction of the Township." | § 155-1619F(5); § 155-1619F(6) |  | https://ecode360.com/36852550
Pennsylvania | Chester | Upper Uwchlan | 4202979352 | Definition: Geothermal Heat Pump |  |  | § 77-8B-C-D regulates "Geothermal systems" and requires that they "shall be closed-loop systems" and use approved heat-transfer fluids, indicating the term refers to geothermal heating/cooling exchange systems governed by this section. | § 77-8 Geothermal systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | 4202979352 | Permit |  |  | § 77-4A: "All systems including modifications to existing systems must obtain permits under the Township Building Code and Pennsylvania Uniform Construction Code in effect at the time of application and construction." § 77-8E: "In-ground bed/tank systems require a Township grading permit." | § 77-4 Compliance with other codes and standards required; § 77-8 Geothermal systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | 4202979352 | Decommissioning |  |  | § 77-9A: "The alternative energy system owner shall, at its sole expense, complete decommissioning of the system within 12 months after the end of the useful life of the system, or after 12 months of nonuse..." § 77-9A(1): "Decommissioning of a geothermal system shall include purging the system of the working fluid and disposing of the fluid in accordance with guidelines issued by the Pennsylvania Department of Environmental Protection." § 77-9A(2): "The geothermal in-ground fluid system and boreholes shall be backfilled with bentonite clay or equivalent material." | § 77-9 Decommissioning of systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | 4202979352 | Open-loop Prohibitions |  |  | § 77-8C: "Geothermal systems shall be closed-loop systems." | § 77-8 Geothermal systems | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | Upper Uwchlan | 4202979352 | Other Prohibitions/Regulations |  |  | § 77-3C(1): "Geothermal systems are specifically prohibited in the following areas: (1) C-1 Village District and historical districts designated by the Board of Supervisors in the Zoning Ordinance." | § 77-3 Permitted and prohibited district uses | 2023 | https://ecode360.com/26913000
Pennsylvania | Chester | West Goshen | 4202983080 | Setback - Property Lines | 10 | feet | "All wells drilled for closed loop geothermal energy systems shall be set back ... a minimum of 10 feet from property lines. All wells drilled for open loop geothermal energy systems shall be set back ... a minimum of 10 feet from property lines." | §84-57.16(A)(3) | 2025 | https://www.westgoshen.org/DocumentCenter/View/1809/Ordinance-No-1-2025---Zoning-Ordinance-Amendment-Geothermal-Wells
Pennsylvania | Chester | West Goshen | 4202983080 | Setback - Building Foundation | 30 | feet | "All wells drilled for closed loop geothermal energy systems shall be set back a minimum of 10 feet from any building foundation... All wells drilled for open loop geothermal energy systems shall be set back a minimum of 30 feet from any building foundation..." | §84-57.16(A)(3) | 2025 | https://www.westgoshen.org/DocumentCenter/View/1809/Ordinance-No-1-2025---Zoning-Ordinance-Amendment-Geothermal-Wells
Pennsylvania | Chester | West Goshen | 4202983080 | Permit |  |  | "Prior to the installation of a geothermal energy system, the property owner shall provide a copy of the permit issued by Chester County and obtain a zoning permit pursuant to this chapter and a grading permit pursuant to Chapter 69 of the West Goshen Township Code." | §84-57.16(A)(2) and §84-57.16(B)(2) | 2025 | https://www.westgoshen.org/DocumentCenter/View/1809/Ordinance-No-1-2025---Zoning-Ordinance-Amendment-Geothermal-Wells
Pennsylvania | Chester | West Marlborough | 4202983464 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES - A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 112 Definitions | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | Section 112 Definitions | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Setback - Roads | 20 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than ... twenty feet (20') from any property lines and street rights-of-way." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Setback - Property Lines | 20 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than ... twenty feet (20') from any property lines and street rights-of-way." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Setback - Wastewater | 25 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than ... twenty-five feet (25') from any existing or planned on-lot sewage disposal systems..." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Setback - Private Water | 100 | feet | "No geothermal system sub-surface loops and/or related geothermal boreholes shall be located closer than one hundred feet (100') from any existing or planned drinking water wells that serve one principal use." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Marlborough | 4202983464 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be permitted." | Section 301.5.8 Alternative Energy Systems | 2017 | https://www.westmarlboroughpa.gov/wp-content/uploads/2023/05/zoning-ordinance.pdf
Pennsylvania | Chester | West Nantmeal | 4202983664 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY. A source of energy generated from solar, water, wind, geothermal or similar sources which is capable of providing energy and utility provisions to a permitted use." | § 215-7 Specific terms; ALTERNATIVE AND EMERGING ENERGY FACILITIES; A. ALTERNATIVE ENERGY | 2026 | https://ecode360.com/35800116
Pennsylvania | Chester | West Sadsbury | 4202983968 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | §202. Definitions | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM, CLOSED HORIZONTAL LOOP - A type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, nontoxic heat transfer fluid; a heat pump; and an air distribution system..." and "GEOTHERMAL SYSTEM, CLOSED VERTICAL LOOP - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." | §202. Definitions | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal systems shall be set back a minimum distance of 10 feet from any property line." | §1230(g) Setback requirements | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Setback - Wastewater | 25 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 25 feet from on-lot sewage disposal systems or potable wells." | §1230(g)(1) Potential pollution sources | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Setback - Public Water | 25 | feet | "Geothermal boreholes or trenches (in the case of horizontal loop systems) shall be set back a minimum of 25 feet from on-lot sewage disposal systems or potable wells." | §1230(g)(1) Potential pollution sources | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application. A zoning permit and building permit, under the Pennsylvania Uniform Construction Code, shall be required." Also: "A geothermal energy system shall be permitted by right in all zoning districts as an accessory use." | §1230. Geothermal Energy Systems | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Inspection |  |  | "Geothermal heating and/or cooling system vertical heat exchange boreholes containing loop pipes shall be tremie grouted... West Sadsbury Township shall be notified prior to grouting activities. At the discretion of the Township, the Township or its representative may perform inspections of the borehole grouting." Also, "For geothermal projects proposed in Zone 2, the project shall be reviewed and requires approval by the Township Engineer and the Township's Professional Geologist as part of the permit process." And: "In Zone 2, no drilling or grouting shall be performed without inspections by the Township Engineer or the Township's Professional Geologist. A twenty-four-hour notice is required prior to starting the project, and to schedule inspections." | §1230(h)(2), (4), (5) | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Screening |  |  | "All or any mechanical equipment (appurtenances) associated with and necessary for the operation of the geothermal energy system shall comply with all accessory setbacks for the district in which the system is installed." | §1230(f) Appurtenances | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to all applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | §1230(b) Design and permitting | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Decommissioning |  |  | "The agreement shall include that if the geothermal energy system is abandoned or is in a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the geothermal energy system within six months from the date the system enters such a state." Also: "Any earth disturbance as a result of the removal or permanent sealing of the geothermal energy system shall be graded and reseeded." | §1230(i)-(j) Abandonment or disrepair; Decommissioning | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Open-loop Prohibitions |  |  | "Only the following types of geothermal energy systems shall be permitted: (1) Closed horizontal loop; (2) Closed vertical loop." In addition, "Within Zone 2 of the designated wellhead protection area, geothermal systems are limited to closed-loop systems as defined within this section." | §1230(c) Permitted types; §1230(d) Wellhead protection areas | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | West Sadsbury | 4202983968 | Other Prohibitions/Regulations |  |  | "All geothermal energy systems... shall be prohibited from construction and use within Zone 1 of the designated wellhead protection areas." | §1230(d) Wellhead protection areas | 2018 | https://www.westsadsburytwp.org/wp-content/uploads/2014/05/Zoning-Ordinance-August-2018.pdf
Pennsylvania | Chester | Westtown | 4202984104 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the Earth's thermal properties, in conjunction with electricity, to provide for the heating and cooling of buildings." Also defined are system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM — A type of geothermal heating and/or cooling system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM — A type of geothermal heating and/or cooling system..."; and "OPEN-LOOP GEOTHERMAL SYSTEM — A type of geothermal heating and/or cooling system..." | § 170-201 Definitions | 2026 | https://ecode360.com/12396648
Pennsylvania | Chester | West Vincent | 4202984160 | Setback - Wastewater | 100 | feet | "Any recharge well must be located at least 100 feet from any subsurface septic or sewage disposal system." | § 390-145B(1)(e) | 2024 | https://ecode360.com/32402746
Pennsylvania | Chester | West Vincent | 4202984160 | Permit |  |  | "No geothermal heat pump shall be installed or used without a building permit first being issued by the Township." | § 390-145B(1)(a) | 2024 | https://ecode360.com/32402746
Pennsylvania | Chester | West Vincent | 4202984160 | Other Prohibitions/Regulations |  |  | "The discharge or effluent from a geothermal heat pump system must be returned to the groundwater through a recharge well and the system so maintained that there is no outflow to the surface of the ground or any surface waters." | § 390-145B(1)(d) | 2024 | https://ecode360.com/32402746
Pennsylvania | Chester | Willistown | 4202985352 | Inspection |  |  | "Upon presentation of proper credentials, duly authorized representatives of the Township may enter at reasonable times upon any property within the Township to inspect the implementation, condition, or operation and maintenance of the stormwater controls or BMPs... Inspections, including but not limited to a final inspection, of all constructed BMPs, conveyances, or other stormwater facilities and related improvements may be conducted to confirm compliance with this article and with the final approved SWM site plan prior to the issuance of any occupancy permit, use permit, or other form of final approval of the project by the Township." Also, "The landowner or the owner's designee shall inspect SWM BMPs, facilities and/or structures installed under this article" at stated frequencies, with written inspection reports. | § 73-45 Right of entry; § 73-43 Operation and maintenance responsibilities | 2026 | https://ecode360.com/11712374
Pennsylvania | Cumberland | Camp Hill | 4204111000 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY SYSTEM: Any one (1) or more method and facility used in the conversion, storage, and distribution including electrical infrastructure, transmission lines, and other appurtenant Structures and facilities of renewable energy sources, including but not limited to sunlight, wind, rain, tides, and geothermal heat." | § 202. Definitions | 2023 | https://cms8.revize.com/revize/camphillborough/Departments/Code%20Enforcement-Zoning/2023%20Zoning%20Ordinance/2023%20ZONING%20ORDINANCE%202023-04.pdf
Pennsylvania | Cumberland | Dickinson | 4204119144 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | § 205-12 Definitions | 2020 | https://ecode360.com/36501835
Pennsylvania | Cumberland | Monroe | 4204150472 | Permit |  |  | "Green Energy Projects - Green energy projects, including the installation of solar panels, wind energy systems or geothermal heating, are subject to a 25% permit fee discount, but in no case will the overall permit fee be reduced below $150." The resolution also establishes building permit categories and fees for "Residential Building Permit Review and Inspections," "Commercial Building Permit Review," and related inspections under Monroe Township's administration and enforcement of the Pennsylvania Uniform Construction Code. | Fee Schedule item 1 / note 1 | 2012 | https://cms6.revize.com/revize/monroetwppa/RESOLUTIONS/2012/2012-06.pdf
Pennsylvania | Cumberland | Silver Spring | 4204170792 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP SYSTEM - A well or wells installed for the purpose of heating or cooling. The system can be either closed or open loop." | SECTION 203 SPECIFIC TERMS | 2022 | https://www.sstwp.org/Documents/Departments/Community%20Development/Permit%20Forms%20Applications/Silver%20Spring%20SLDO%20Adopted%20March%202022%20-%20Formatted%20with%20signature%20page%20(1)_202205181140007159.pdf?t=202507211024550
Pennsylvania | Cumberland | South Middleton | 4204172336 | Definition: Geothermal Heat Pump |  |  | 'Abandonment of Well - An abandoned or unused well may be defined as one or more of the following: ... (vii.) An inactive geothermal groundwater heat exchange system.' | 1404(4)(a) - Definitions | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Cumberland | South Middleton | 4204172336 | Permit |  |  | For geothermal exchange systems in Zone 2: 'a. No such systems shall be permitted within 200 feet of the WHPA Zone 1 boundary. b. Submittal of evidence that 1) the landowner is aware that only food-based antifreeze may be used in piping, 2) professionally designed & installed piping will be encased to prevent leakage, & 3) the recommendations in DEP's Ground Source Heat Pump Manual for protecting water quality will be utilized.' For abandoned geothermal systems treated as abandoned wells: 'A zoning permit demonstrating planned compliance with DEP's water well abandonment guidelines shall be required prior to the sealing of a well.' | Table 1404(7) Use 19; Table 1404(7) Use 27 | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Cumberland | South Middleton | 4204172336 | Decommissioning |  |  | Definition: 'Abandonment of Well - An abandoned or unused well may be defined as ... (vii.) An inactive geothermal groundwater heat exchange system.' Operative rule in Table 1404(7) Use 27: 'a. Wells shall be sealed within 30 days of abandonment b. A zoning permit demonstrating planned compliance with DEP's water well abandonment guidelines shall be required prior to the sealing of a well. c. Certification by a licensed well driller, professional engineer or registered professional geologist of the sealing of the well consistent with DEP guidelines shall be required.' | 1404(4)(a); Table 1404(7) Use 27 - Abandonment of Wells | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Cumberland | South Middleton | 4204172336 | Other Prohibitions/Regulations |  |  | Table 1404(7) lists '19. Geothermal Exchange Systems (groundwater & ground loop)' as 'Not Permitted' in Zone 1 of the Wellhead Protection Area. | Table 1404(7) Use 19 - Geothermal Exchange Systems (groundwater & ground loop) | 2016 | https://www.smiddleton.com/DocumentCenter/View/120/Article-14-PDF
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Definition: Well |  |  | "Geothermal Boreholes: A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Definition: Geothermal |  |  | "Geothermal: Of, relating to, or utilizing the heat of the earth's interior." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System: An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Setback - Property Lines | 25 | feet | "All parts of the geothermal system shall be located a minimum distance of twenty-five (25) feet from any property line." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Setback - Public Water | 25 | feet | "All parts of the geothermal system shall be located a minimum distance of twenty-five (25) from any on-lot wells." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Maximum Well Depth | 20 | feet | "Closed Horizontal Loop Geothermal System ... A horizontal closed loop system shall be no more than twenty (20) feet deep." | SECTION 1: Definitions / Geothermal Terms | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design and installation comply with applicable industry standards." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Middle Paxton | 4204349040 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in the Township." | Section 1322. Geothermal Energy Systems | 2013 | https://www.middlepaxtontwp.org/wp-content/uploads/2022/05/Zoning-Ordinance-orientation-fixed.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum of 25 feet from all property lines, except as otherwise specified." | § 27-1102, Subsection 24.E(3)(c) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 27-1102, Subsection 24.E(3)(d) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Setback - Private Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 27-1102, Subsection 24.E(3)(d) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Maximum Well Depth | 20 | feet | "A horizontal closed-loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 27-1102, Subsection 24.E(3)(a) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Permit |  |  | "Required Permit. The design and installation of geothermal energy systems shall conform to applicable industry standards and the UCC. At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 27-1102, Subsection 24.E(4) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Certification |  |  | "At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 27-1102, Subsection 24.E(4) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Decommissioning |  |  | General decommissioning rules state: "Except for geothermal systems, the alternative energy system owner shall, at its expense, complete decommissioning of the system within 12 months after the end of the useful life of the system, or after 12 months of nonuse." For geothermal specifically: "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his or her expense after a demolition permit has been obtained," and "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 27-1102, Subsection 24.C(1); § 27-1102, Subsection 24.E(5) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Dauphin | Upper Paxton | 4204379216 | Open-loop Prohibitions |  |  | "Closed-loop geothermal energy systems are permitted in all zoning districts as an accessory use to a principal use of the site. Open-loop geothermal energy systems are prohibited within the Township." | § 27-1102, Subsection 24.E(1) | 2019 | https://upperpaxtontwp.org/gencode/Chapter%2027%20-%20Zoning.pdf
Pennsylvania | Delaware | Aston | 4204503336 | Permit |  |  | "Alternative energy sources, which include but are not limited to ground source heat pumps (geothermal), solar energy systems, and wind energy systems are permitted in all districts by conditional use only." Also, "The alternative energy system shall require a Building Permit and any other associated permits..." | 1292.27 ALTERNATIVE ENERGY SOURCES | 2012 | https://astontownship.net/download/ordinances/Aston%20Township%20Zoning%20Ordinance%202011.pdf
Pennsylvania | Delaware | Aston | 4204503336 | Decommissioning |  |  | "If an alternative energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." | 1292.27 ALTERNATIVE ENERGY SOURCES | 2012 | https://astontownship.net/download/ordinances/Aston%20Township%20Zoning%20Ordinance%202011.pdf
Pennsylvania | Delaware | Brookhaven | 4204509080 | Permit |  |  | "Fees for installation of gas appliances (' 1484.03): ... (d) Solar systems and geothermal systems: $50." | § 208.06(N)(3)(d) - Fees for installation of gas appliances | 2013 | https://brookhavenboro.com/wp-content/uploads/2019/11/Administrative-Code.pdf
Pennsylvania | Delaware | Edgmont | 4204522584 | Definition: Well |  |  | "GEOTHERMAL WELL — A well(s) installed for the purpose of heating and/or cooling the dwelling or building on a property (see 'closed-loop geothermal borehole')." | § 365-168A |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Definition: Geothermal Heat Pump |  |  | "GROUND-SOURCE HEAT PUMP — A ground-source heat pump, which shall include, but not be limited to, any components of a heating and/or cooling system (including supply wells) installed in a closed-loop geothermal borehole and used for heating and/or cooling of a building or dwelling using a heat transfer fluid or direct exchange system." | § 365-168A |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Right of Way | 10 | feet | The setback table lists "Rights-of-way and easements — 10" as a minimum isolation distance for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Property Lines | 40 | feet | The table sets minimum isolation distances from "Property lines of properties served by public sewers — 10" and from "Property lines of properties served by on-lot septic systems — 40" for closed-loop geothermal boreholes. | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Building Foundation | 10 | feet | The setback table requires a minimum isolation distance of "Building foundations — 10" for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Wastewater | 50 | feet | The setback table for "closed-loop geothermal boreholes" requires minimum isolation distances of "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits — 50" and "Septic tanks, aerobic tanks, sewage pump tanks and holding tanks — 25." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Fuel (above ground) | 30 | feet | The table lists "Exterior surface or subsurface containers or tanks used for storage of materials that cannot be properly disposed of by passage through soil; this includes, but is not limited to, gasoline and all other petroleum products, and propane — 30" for closed-loop geothermal boreholes. | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Sewer Lines | 10 | feet | The table lists "Sewer drains and public sewer laterals — 10" as a minimum isolation distance for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Water Bodies | 50 | feet | The setback table states: "Delineated wetlands, floodplains, lakes, ponds or other surface waters — 50" minimum isolation distance for "closed-loop geothermal boreholes." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The table requires separation from "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals or salt piles ... 300 (150)" for closed-loop geothermal boreholes, with "300" generally and "(150)" "[i]f borehole is cased and grouted inside and out." | § 365-168C(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Permit |  |  | "No person shall install, construct, drill or excavate to facilitate the construction or installation of a ground-source heat pump for use as a heating and/or cooling system for a residential or commercial building within the Township without first obtaining a ground-source heat pump permit from the Township. No person shall drill or excavate to repair or modify or to facilitate the repair or modification of a ground-source heat pump system in the Township without first obtaining a ground-source heat pump permit." | § 365-168D(1) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Inspection |  |  | "Prior to commencing any work under any permit, the property shall be staked to accurately identify the approved location of each proposed geothermal borehole. The Township shall inspect the property and shall sign off on each location prior to any drilling or installation." The contractor must also provide before activation: "Written documentation verifying the ground-source heat pump system has been successfully pressure tested and it is ready for use and operation." | § 365-168E(1), (7)(d) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Decommissioning |  |  | "In the event of the discontinuance of the use of the ground-source heat pump system, a system closure plan shall be prepared and submitted to the Township for approval." | § 365-168F |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Open-loop Prohibitions |  |  | The ordinance states: "All ground-source heat pump systems shall be closed-loop systems" and under prohibited uses, "No open-loop systems shall be permitted." | § 365-168B(3), (4)(a) |  | https://ecode360.com/34067174
Pennsylvania | Delaware | Edgmont | 4204522584 | Other Prohibitions/Regulations |  |  | Under prohibited uses, the ordinance states: "Class V wells (as defined by U.S. EPA) are prohibited" and "A ground-source heat pump system shall not be connected in any way to any sanitary sewage disposal or stormwater system." | § 365-168B(4)(b), (c) |  | https://ecode360.com/34067174
Pennsylvania | Erie | Edinboro | 4204922608 | Definition: Geothermal Heat Pump |  |  | "OPEN LOOP — A geothermal heat pump system that withdraws water from a well or surface water supply, passes it through a heat exchanger, and discharges the water to a surface water body, storm or sanitary sewer system, or recharge well." Also: "CLOSED LOOP SYSTEMS — Systems which rely on the contained circulation of fluids through an underground pipe circuit" and "DIRECT EXPANSION or DX — A system which circulates refrigerant in a closed underground loop." | § 13-401 Definitions | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | 4204922608 | Permit |  |  | "No person, partnership, corporation or other entity shall... install, construct, drill or excavate to facilitate the construction or installation of ground source heat pump for use as a heating and/or cooling system for any residential, commercial or industrial structures without first obtaining a building permit." | § 13-402 General Provisions | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | 4204922608 | Inspection |  |  | "Prior to backfilling, in-ground joints shall be pressure tested to 500 psi for a minimum of 15 minutes, with no pressure loss. Should any buried portion fail, refrigeration shall be recaptured, and the loop shall be repaired or abandoned." | § 13-405 Installation of Direct Expansion (DX) Systems | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | 4204922608 | Decommissioning |  |  | "Whenever a ground source heat pump system is permanently removed from service, and the pipes are not removed from the ground, the outside loop pipes shall be filled with materials meeting specifications for grout." | § 13-407 Provisions for the Decommissioning of Ground Source Heat Pump Systems | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | 4204922608 | Open-loop Prohibitions |  |  | "Shall not be permitted." | § 13-403 Installation of Open Loop Systems | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | Edinboro | 4204922608 | Other Prohibitions/Regulations |  |  | "In specific areas of the Home Rule Borough of Edinboro where, as determined by the Borough of Edinboro Engineer, local geological conditions, including but not limited to karst or permafrost, do not meet the requirements for installation and/or efficient operation of geothermal heat pump systems, the Borough Engineer may prohibit the installation of one or more types of geothermal heat pump systems." | § 13-402 General Provisions | 2011 | https://ecode360.com/32168343
Pennsylvania | Erie | North East | 4204954952 | Definition: Geothermal |  |  | "RENEWABLE ENERGY SOURCE: Any method, process or substance whose supply is rejuvenated through natural processes and, subject to those natural processes, remains relatively constant including, but not limited to, biomass conversion, geothermal energy, solar and wind energy, and hydroelectric energy..." | Sec. 201 General Definitions | 2011 | https://www.northeastborough.com/wp-content/uploads/2020/02/ZoningOrdinance.pdf
Pennsylvania | Erie | North East | 4204954952 | Permit |  |  | Sec. 507 states: "This use may be permitted in all districts as a special exception use, if approved by the Zoning Hearing Board." Sec. 405 lists "Renewable Energy Source (D) (Sec.705)" as "S" in R-A, R-B, C-1, and M-1 districts. | Sec. 507 Renewable Energy Source; Sec. 405 Permitted Use and Special Exception Use Table | 2011 | https://www.northeastborough.com/wp-content/uploads/2020/02/ZoningOrdinance.pdf
Pennsylvania | Erie | North East | 4204954952 | Inspection |  |  | "Applications, Zoning Certificates, Building Permits, and Inspection. He/she shall receive applications for zoning certificates and building permits and make all inspection in accordance with the provisions of this Zoning Ordinance." Also: "The Zoning Officer may examine or cause to be examined all structures and/or land for which an application has been filed for zoning certificates, and he/she may conduct such inspections from time to time during and at completion of the work for which a zoning certificate has been issued." | Sec. 602 Duties of the Zoning Officer | 2011 | https://www.northeastborough.com/wp-content/uploads/2020/02/ZoningOrdinance.pdf
Pennsylvania | Erie | Summit | 4204975208 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM: Any excavation that is drilled, cored, bored, washed, driven, dug, jetted, or otherwise constructed when the intended use of such excavation is for the open-loop or closed-loop circulation of a geothermal fluid vertically, or the location, acquisition or artificial recharge of groundwater." | Section 202 – Specific Terms | 2025 | https://summittownship.com/wp-content/uploads/2026/01/2021-02-Summit-Township-Zoning-Ordinance-Amended-2025-12-20-BLANK-LAST-PAGE.pdf
Pennsylvania | Franklin | Greene | 4205530944 | Definition: Well |  |  | "GEOTHERMAL WELL — A well installed for the purpose of heating or cooling a facility. This shall include wells drilled as supply and return wells for an open loop system, or closed loop geothermal boreholes." | § 101-4 Definitions | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP EQUIPMENT — Any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed loop applications using heat transfer fluid or direct exchange systems." | § 101-4 Definitions | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Driveways | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (11) Property lines, driveways, rights-of-way or easements: 10 feet." | § 101-14(E)(11) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Right of Way | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (11) Property lines, driveways, rights-of-way or easements: 10 feet." | § 101-14(E)(11) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Property Lines | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (11) Property lines, driveways, rights-of-way or easements: 10 feet." | § 101-14(E)(11) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Wastewater | 100 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (4) Subsurface sewage absorption areas, elevated sand mounds, seepage pits, cesspools or other on-lot sewage disposal systems: 100 feet. (5) Spray irrigation perimeter, sewage sludge or septage disposal sites: 100 feet. (6) Septic tanks, aerobic tanks, sewage pumps or holding tanks: 50 feet." | § 101-14(E)(4)-(6) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Fuel (above ground) | 300 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (9) Surface or subsurface containers or tanks of greater than 1,000 gallons' capacity used for storage of materials that cannot be properly renovated by passage through soil. This includes gasoline, diesel fuel and other petroleum products: 300 feet (can be reduced to 150 feet if the borehole is cased and grouted inside and out). (10) Surface or subsurface containers or tanks of 1,000 gallons or less used for storage of materials like heating oil or other petroleum products: 30 feet." | § 101-14(E)(9)-(10) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Fuel (below ground) | 300 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (9) Surface or subsurface containers or tanks of greater than 1,000 gallons' capacity used for storage of materials that cannot be properly renovated by passage through soil. This includes gasoline, diesel fuel and other petroleum products: 300 feet (can be reduced to 150 feet if the borehole is cased and grouted inside and out). (10) Surface or subsurface containers or tanks of 1,000 gallons or less used for storage of materials like heating oil or other petroleum products: 30 feet." | § 101-14(E)(9)-(10) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Sewer Lines | 5 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (7) Sanitary sewer lines, drains or laterals: five feet." | § 101-14(E)(7) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Water Bodies | 10 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (1) Delineated wetlands, floodplains, lakes, ponds, streams or other surface waters: 10 feet." | § 101-14(E)(1) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Setback - Hazardous Materials/Fertilizers | 300 | feet | "Closed loop geothermal boreholes must maintain the following minimum isolation distances... (8) Preparation or storage area of hazardous spray materials, fertilizers, chemicals or salt piles: 300 feet (can be reduced to 150 feet if the borehole is cased and grouted inside and out)." | § 101-14(E)(8) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Permit |  |  | § 101-7(A)(1): "Any installation, repair or modification requires a permit from the Township." § 101-14(H): "The geothermal well installation contractor shall be responsible for insuring that the borehole is drilled in the permitted location..." | § 101-7 Permit procedures; § 101-14 Geothermal wells | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Licensed Driller |  |  | § 101-7(A)(1): "All individual and semipublic water supplies shall be constructed by a duly licensed well or pump installation contractor." § 101-14(H): "The geothermal well installation contractor shall be responsible for insuring that the borehole is drilled in the permitted location..." | § 101-7 Permit procedures; § 101-14 Geothermal wells | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Certification |  |  | § 101-14(J): "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | § 101-14 Geothermal wells | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Greene | 4205530944 | Decommissioning |  |  | "Whenever an existing well is replaced, the property owner shall be responsible for the decommissioning of the existing well by a licensed contractor. No well shall exist in an abandoned state." | § 101-14(O) | 2010 | https://ecode360.com/11174837
Pennsylvania | Franklin | Washington | 4205581240 | Definition: Well |  |  | "Geothermal Well - Any excavation that is drilled, cored, bored, washed, driven, dug, jetted or otherwise constructed when the intended use of such excavation is for the circulation of a geothermal fluid vertically, or the location, acquisition or artificial recharge of groundwater. (Includes open and closed loop vertical systems)" | Section 165-2. Definitions and Terms. | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating System - A geothermal heat pump system which relies on the contained circulation of geothermal fluids to obtain and to utilize geothermal resources." Also: "Closed Loop Systems - A geothermal heat pump system which relies on the contained circulation of geothermal fluids through an underground loop of pipes." "Open Loop System - A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring or surface water." | Section 165-2. Definitions and Terms. | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Driveways | 10 | feet | Table in §165-13(B): "Property lines, driveways, and private roads — 10" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Right of Way | 20 | feet | Table in §165-13(B): "Dedicated public right of ways — 20" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Property Lines | 10 | feet | Table in §165-13(B): "Property lines, driveways, and private roads — 10" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Building Foundation | 30 | feet | Table in §165-13(B): "Building foundations (except for buildings enclosing water wells and/or water well pumps) — 30" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Wastewater | 100 | feet | Table in §165-13(B): "Septic tanks, aerobic tanks or holding tanks — 50" feet; "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields — 100" feet; "Sewage seepage pits, cesspools — 100" feet; "Spray irrigation sites, sewage sludge and septage disposal sites — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Animal Enclosures | 100 | feet | Table in §165-13(B): "Farm silos, barnyards, privies and fuel tanks — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Fuel (above ground) | 100 | feet | Table in §165-13(B): "Farm silos, barnyards, privies and fuel tanks — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Sewer Lines | 50 | feet | Table in §165-13(B): "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 50" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Water Bodies | 25 | feet | §165-13(A): "Geothermal wells shall not be sited in floodplains." Table in §165-13(B): "Lakes, ponds, streams or other surface waters — 25" feet; "Rainwater pits, ditches — 25" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table in §165-13(B): "Preparation areas or storage areas of hazardous spray materials, fertilizers or chemicals, salt piles — 100" feet. | Section 165-13. Well Siting Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Permit |  |  | §165-7: "Any persons desiring to construct, install, or alter a Geothermal Heating System within the Township shall first apply for a Geothermal Heating System permit... No Person shall commence construction or Alteration of a Geothermal Heating System prior to the Owner... receiving a permit." §165-11(A): "Before any drilling or site preparation begins, the well driller shall apply for a Well Permit from the Township." §165-11(E): "No Geothermal Well shall be put into service without receiving a Geothermal Well permit and meeting the requirements of this Chapter." §165-8(C): "All applicants for a Geothermal Heating System permit shall also obtain a building permit as per the UCC..." | Section 165-7. Application for Geothermal Heating System Permit / Section 165-11. Wells for Geothermal Systems - Procedures. | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Inspection |  |  | §165-15: "The following inspections shall be required by the Township and Authority: A. Site inspection before any work is done... B. Inspection of the installed loop (pressure test). C. Inspection of grouting. D. Inspection of the completely installed system before operations commence and upon commencement of operations. E. Periodic inspections no less than once every three years. F. Inspection if geothermal system or well is abandoned." §165-11(B): "During the well drilling and construction process, the Township or Authority may enter the premises to determine if the well is being installed according to the requirements of this Chapter." §165-16(B): "Abandonment procedures shall be subject to Township inspection." | Section 165-15. Inspection / Section 165-11(B) / Section 165-16(B) | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Licensed Driller |  |  | §165-12: "All Geothermal Heating Systems and wells installed for the purposes of heating and cooling a facility must adhere to the International Ground Source Heat Pump Association's (IGSHPA) Design & Installation Standards and the installer(s) and well driller(s) must be certified by the IGSHPA." §165-12(A)(1): "All geothermal wells in the Township shall be constructed in accordance with PA Act 610 (Water Well Drillers License Act)." §165-16(A): "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller..." | Section 165-12. Geothermal Well Construction Requirements / A. Construction by Licensed Driller | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Certification |  |  | §165-12: "All Geothermal Heating Systems and wells installed for the purposes of heating and cooling a facility must adhere to the International Ground Source Heat Pump Association's (IGSHPA) Design & Installation Standards and the installer(s) and well driller(s) must be certified by the IGSHPA." | Section 165-12. Geothermal Well Construction Requirements | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Decommissioning |  |  | §165-16(A): "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment form shall be submitted to the Township within thirty (30) days of abandonment." §165-16(B): "Abandonment procedures shall be subject to Township inspection." | Section 165-16. Well Abandonment | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Closed-loop Prohibitions |  |  | §165-6(A)(1): "All Geothermal Heating Systems shall be prohibited within Zone 1 of the Wellhead Protection District." | Section 165-6. Post Chapter Geothermal Heating Systems | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Open-loop Prohibitions |  |  | §165-6(A)(1): "All Geothermal Heating Systems shall be prohibited within Zone 1 of the Wellhead Protection District." Also: "Open Loop Systems shall be prohibited within Zone 2 of the Wellhead Protection District." | Section 165-6. Post Chapter Geothermal Heating Systems | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Franklin | Washington | 4205581240 | Other Prohibitions/Regulations |  |  | §165-6(A)(1): "All Geothermal Heating Systems shall be prohibited within Zone 1 of the Wellhead Protection District." | Section 165-6. Post Chapter Geothermal Heating Systems | 2013 | https://www.washtwp-franklin.org/download/ordinances/zoning_ordinances/Ordi_242-Geothermal%20Heating%20Systems.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Definition: Well |  |  | "Heat Exchange Well- a well used for the purpose of utilizing the geothermal properties of earth formations for heating or air conditioning." | SECTION 105 - DESIGN STANDARDS, A. DEFINITIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Definition: Geothermal Heat Pump |  |  | "Closed-Loop - a geothermal heat exchanger that circulates a nontoxic antifreeze heat transfer fluid through a loop or multiple loops of polyethylene piping installed below the ground surface or within a surface water body." "Open-Loop - a geothermal heat exchanger that withdraws groundwater from a supply well, passes the groundwater through a heat pump, and discharges the temperature-altered water back to the ground in a discharge (return) well." "Direct Exchange - a type of closed-loop heat exchanger that uses loops of copper tubing installed in pits, trenches or vertical borings in the earth, through which a refrigerant is circulated." | SECTION 105 - DESIGN STANDARDS, A. DEFINITIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Driveways | 10 | feet | Minimum isolation distance for "Driveways" is "10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Right of Way | 10 | feet | Minimum isolation distance for "Property lines, all right-of-ways, easements" is "10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Property Lines | 10 | feet | Minimum isolation distance for "Property lines, all right-of-ways, easements" is "10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Building Foundation | 20 | feet | Minimum isolation distance for "Dwellings and structures" is "20 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Wastewater | 100 | feet | Minimum isolation distances include: "Subsurface sewage absorption areas, elevated sandmounds, cesspools, sewage seepage pits. 100 feet"; "Spray irrigation site perimeter, sewage sludge, and seepage disposal site. 100 feet"; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks. 50 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Private Water | 50 | feet | Minimum isolation distance for "Potable Water Well" is listed as "Hand Dug Well 50 feet" and "Drilled/Cased Well 25 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Animal Enclosures | 100 | feet | Minimum isolation distance for "Farm structures (silos, barnyards, manure pit, etc.)" is "100 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Fuel (above ground) | 300 | feet | Minimum isolation distance for "Surface or subsurface containers or tanks greater than 1000 gal. used for storage of materials that cannot be properly renovated by passage through soil. This includes, but not limited to, gasoline and all other petroleum products" is "300 feet (150 feet)." The table also lists tanks "of 1000 gal. or less... For example, the type of tanks frequently used in homes using oil for heating purposes. 50 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Sewer Lines | 50 | feet | Minimum isolation distances include "Private Sewer Drains 50 feet" and "Public sewer laterals. 10 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Water Bodies | 50 | feet | Minimum isolation distance for "Delineated wetlands, flood plains, lakes, ponds or other surface waters" is "50 feet." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Minimum isolation distance for "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles" is "300 feet (150 feet)" when borehole casing and grouting conditions apply. The table also lists "Identified NPL site (Superfund Sites) plume area. 300 feet (or as regulated by PA DEP)." | SECTION 105(B)(1)(a) - BOREHOLE LOCATIONS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Minimum Well Depth | 15 | feet | "If the closed-loop borehole penetrates bedrock it must be grouted from a depth of fifteen feet (15') into the bedrock to the top of the borehole." | SECTION 105(B)(2)(e) | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Permit |  |  | SECTION 103: "No construction, drilling, digging, reconstruction, major repair or other change of or for any geothermal well shall commence unless the property owner, or his/her duly authorized agent, shall apply for and receive a permit..." SECTION 105(B)(3)(a): "Each borehole must be permitted using a single application. A fee will be charged for each borehole." SECTION 110: permits remain effective for "one (1) year" with a one-time written extension request allowed, "limited to thirty (30) days." | SECTION 103 - PERMITS; SECTION 105(B)(3) - PERMITTING; SECTION 110 - EFFECTIVE DATE OF PERMIT | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Inspection |  |  | SECTION 105(B)(2)(b): "The Inspection Officer or designated Township employee shall inspect to determine that the borehole is drilled in the permitted location." SECTION 106: "Upon receipt of an application for a well permit, the Township... shall within seven (7) business days, perform an inspection of the premises on which the well is to be constructed." SECTION 109: "The applicant shall be responsible for costs associated with inspection of work under this ordinance." | SECTION 105(B)(2)(b); SECTION 106 - INSPECTION; SECTION 109 | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Licensed Driller |  |  | The geothermal well permit application must include: "Name and license number of well driller." | SECTION 103 - PERMITS | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Certification |  |  | "The pipe loop is to be installed by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer... in accordance with the specifications of the ground source heat pump system manufacturer, the pipe manufacturer, the International Ground Source Heat Pump Association (IGSHPA) and the National Ground Water Association." | SECTION 105(B)(2)(c) | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Huntingdon | Franklin | 4206127416 | Open-loop Prohibitions |  |  | "OPEN-LOOP' GEOTHERMAL SYSTEMS ARE PROHIBITED WITHIN THE TOWNSHIP." | SECTION 105(C)(1) | 2011 | https://franklintownship.org/wp-content/uploads/wellsfinal.pdf
Pennsylvania | Indiana | Indiana | 4206336816 | Definition: Geothermal Heat Pump |  |  | Figure 400.1 lists "Geothermal Energy System" as an "ACCESSORY USES" category in the Table of Permissible Uses. | §460-405 Figure 400.1 – Table of Permissible Uses |  | https://ecode360.com/IN2678/document/753169213.pdf
Pennsylvania | Juniata | Port Royal | 4206762304 | Permit |  |  | "Private wells shall be permitted within the Borough solely for the purpose of supplying underground water to a closed loop geothermal heat system servicing that particular structure and for providing solely nonpotable water for non-household consumption." | §26-209. Miscellaneous Provisions | 2010 | https://portroyalborough.org/ordinances/
Pennsylvania | Juniata | Port Royal | 4206762304 | Inspection |  |  | "Before activating such system, inspection, and approval of the system must be obtained from the Borough." | §26-209. Miscellaneous Provisions | 2010 | https://portroyalborough.org/ordinances/
Pennsylvania | Juniata | Port Royal | 4206762304 | Other Prohibitions/Regulations |  |  | "Private wells shall be permitted within the Borough solely for the purpose of supplying underground water to a closed loop geothermal heat system servicing that particular structure and for providing solely nonpotable water for non-household consumption." "Further, no water from the geothermal well shall be used for domestic water consumption." | §26-209. Miscellaneous Provisions | 2010 | https://portroyalborough.org/ordinances/
Pennsylvania | Lancaster | Clay | 4207113960 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of ten (10) feet from any property line." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | 4207113960 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | 4207113960 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | 4207113960 | Open-loop Prohibitions |  |  | "Only closed loop geothermal energy systems shall be permitted." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Clay | 4207113960 | Other Prohibitions/Regulations |  |  | "For all closed loop geothermal systems relying upon circulating fluids, only nontoxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | SECTION 548. GEOTHERMAL SYSTEMS | 2016 | https://claytwp.com/wp-content/uploads/2023/02/article_v._supplementary_district_regulations.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Definition: Well |  |  | "GEOTHERMAL BOREHOLE. A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 301.5 Alternative Energy Sources - Definitions | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM. An energy generating system that uses the earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also defines system types including: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM. A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; and an air distribution system"; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM. A borehole that extends beneath the surface..."; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM. Water is pumped from a water well or other water source into a heat exchanger..." | Section 301.5 Alternative Energy Sources - Definitions | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Setback - Right of Way | 25 | feet | "Geothermal systems shall not encroach on public drainage, utility, roadway or trail easements of any nature." Also, "Above-ground equipment associated with geothermal pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum distance of twenty-five (25) feet from any property line, unless documentation in the form of a written agreement with the adjoining property owner(s) is provided." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum distance of... twenty-five (25) feet from any existing septic system." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum distance of one hundred (100) feet from existing potable water wells..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Permit |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards... The manufacturer specifications shall be submitted as part of the application." Also, under abandonment: "The owner shall remove the abandoned system at their expense after a demolition permit has been obtained..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Decommissioning |  |  | "Abandonment. If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained... a. The heat pump and any external mechanical equipment shall be removed. b. Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Conoy | 4207115824 | Open-loop Prohibitions |  |  | "Only closed loop geothermal energy systems shall be permitted. Open-loop geothermal energy systems are prohibited within the Township." | Section 301.5 Alternative Energy Sources - Geothermal Energy Systems | 2025 | https://conoytownship.org/wp-content/uploads/2026/01/ZONING-ORDINANCE-2025-AMENDED.pdf
Pennsylvania | Lancaster | Denver | 4207118888 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum of 25 feet from all property lines, except as otherwise specified." | § 200-55.1(D)(3)(c) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 200-55.1(D)(3)(d) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 200-55.1(D)(3)(d) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Maximum Well Depth | 20 | feet | "A horizontal closed-loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 200-55.1(D)(3)(a) Development standards | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Permit |  |  | "The design and installation of geothermal energy systems shall conform to applicable industry standards and the UCC. At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 200-55.1(D)(4) Required permit | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Certification |  |  | "At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 200-55.1(D)(4) Required permit | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his or her expense after a demolition permit has been obtained"; "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 200-55.1(D)(5) Decommissioning | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Denver | 4207118888 | Open-loop Prohibitions |  |  | "Closed-loop geothermal energy systems are allowed in all zoning districts as an accessory use to a principal use of the site. Open-loop geothermal energy systems are prohibited within the Borough." | § 200-55.1(D)(1) Zoning districts allowed | 2022 | https://ecode360.com/12261304
Pennsylvania | Lancaster | Drumore | 4207120032 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY - A source of energy generated from solar, wind, or geothermal sources, which is capable of providing basic utility provisions to a permitted use." | Section 112 Definitions | 2015 | https://www.drumoretownship.org/DocumentCenter/View/50/Article-1-Background-Provisions
Pennsylvania | Lancaster | Earl | 4207120688 | Setback - Property Lines | 10 | feet | "All parts of the geothermal system shall be located a minimum distance of 10 feet from any property line." | § 27-1414.A(3) | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | Earl | 4207120688 | Permit |  |  | "The following alternative energy systems are approved by right and require a zoning permit. These alternative energy systems are also subject to approval pursuant to the Township's building code, as may be applicable:" "Closed loop geothermal systems shall be permitted in all zoning districts upon approval of a zoning and building permit..." | § 27-1414.A. Alternative Energy Systems Permitted by Right | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | Earl | 4207120688 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the ANSI, the IGSHPA, ASTM, the ARI, or other similar certifying organizations... The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design complies with, and the installation shall comply with, applicable industry standards." | § 27-1414.A(1) | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | Earl | 4207120688 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in Earl Township." | § 27-1414.A. Alternative Energy Systems Permitted by Right | 2025 | https://earltownship.com/wp-content/uploads/2025/06/Part-14-General-Reguations.pdf
Pennsylvania | Lancaster | East Cocalico | 4207120984 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system. [Added 6-19-2014 by Ord. No. 2014-05]" | § 220-11 Definitions and word usage | 2018 | https://ecode360.com/10746660
Pennsylvania | Lancaster | East Cocalico | 4207120984 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature. [Added 6-19-2014 by Ord. No. 2014-05]" | § 220-11 Definitions and word usage | 2018 | https://ecode360.com/10746660
Pennsylvania | Lancaster | East Donegal | 4207121032 | Definition: Geothermal Heat Pump |  |  | 'Geothermal Energy System, Closed-Loop'. A type of geothermal heating and/or cooling system, not designed or used for the generation of power, that utilizes various devices and equipment in which the heat transfer fluid (potable water) is not exposed to the atmosphere. The heat transfer fluid may contain an approved antifreeze solution. 'Closed-Loop Geothermal System, Horizontal'. A mechanism for heat exchange which consists of various devices and equipment installed horizontally in the earth and are connected to the heat exchange system of the building in which the heat transfer fluid is circulated through the piping. 'Closed-Loop Geothermal System, Vertical': A mechanism for heat exchange which consists of various devices and equipment installed vertically in the earth and are connected to the heat exchange system of the building in which the heat transfer fluid is circulated through the piping. | Section 201 - Terms Defined | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | 4207121032 | Permit |  |  | 'Accessory alternative energy systems shall be permitted by right in all zoning districts, subject to the following conditions:' Section 602.4.C.1 states: 'Geothermal energy systems are permitted in any zoning district.' | Section 602.4 - Alternative Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | 4207121032 | Screening |  |  | Section 602.4.C.5 states: 'Any associated above-ground appurtenances shall comply with all accessory use setback requirements of a zoning district.' Read together with Section 605, projections may include 'HVAC and other utility appurtenances.' | Section 602.4 - Alternative Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | 4207121032 | Open-loop Prohibitions |  |  | Section 602.4.C.2 states: 'Only "closed-loop" geothermal energy systems are permitted. "Open-loop" geothermal energy systems are prohibited.' | Section 602.4.C - Geothermal Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Donegal | 4207121032 | Other Prohibitions/Regulations |  |  | Section 602.4.C.4 states: 'Geothermal energy systems shall not encroach into any utility, roadway or other recorded easement.' | Section 602.4.C - Geothermal Energy Systems | 2017 | https://eastdonegaltwp.com/wp-content/uploads/2016/05/FINAL-DRAFT-DOCUMENT_Ord.-Format.pdf
Pennsylvania | Lancaster | East Drumore | 4207121040 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." [Added 1-12-2012 by Ord. No. 1-2012] | § 120-6. Definitions | 2020 | https://eastdrumoretownship.org/wp-content/uploads/2022/04/ED-Zoning-Ordinance-2021-1.pdf?ref=writing.strisker.com
Pennsylvania | Lancaster | East Earl | 4207121072 | Definition: Well |  |  | "Geothermal Boreholes - A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 202. DEFINITIONS | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System - An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." Also defined are system types: "Closed Horizontal Loop Geothermal System - A mechanism for heat exchange which consists of ... underground loops of piping; heat fluid; a heat pump; an air distribution system... The pipes form a closed loop and are filled with a heat transfer fluid" and "Open Loop Geothermal System - Water is pumped from a water well or other water source into a heat exchanger located in a surface building." | Section 202. DEFINITIONS | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Setback - Property Lines | 10 | feet | "All parts of the geothermal system shall be located a minimum distance of ten (10) feet from any property line." | Section 2205.BBB.1.c Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Maximum Well Depth | 20 | feet | "Closed Horizontal Loop Geothermal System ... A horizontal closed loop system shall be no more than twenty (20) feet deep." | Section 202. DEFINITIONS | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Permit |  |  | Section 2304 states: "No building or structure shall be erected, constructed, reconstructed, structurally altered, or moved, and no land or building changed in use or any new use commenced until a zoning permit has been secured from the Zoning Officer." For geothermal applications, Section 2205.BBB.1 requires application materials: "The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design complies with and the installation shall comply with applicable industry standards." | Section 2304; Section 2305; Section 2205.BBB.1 | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the ANSI, the IGSHPA, ASTM, the ARI, or other similar certifying organizations, and shall comply with the Building Code and with all other applicable Township requirements." | Section 2205.BBB.1.a Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in the Township." | Section 2205.BBB.1 Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Earl | 4207121072 | Other Prohibitions/Regulations |  |  | "In all closed loop geothermal systems relying upon circulating fluids, only nontoxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | Section 2205.BBB.1.b Geothermal Energy Systems | 2017 | https://eastearltwp.org/images/documents/EAST_EARL_Proposed_Zoning_Ordinance_Ver_10.pdf
Pennsylvania | Lancaster | East Lampeter | 4207121344 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heat Pump: An energy system utilized for heating and cooling purposes through a series of heat-exchanging pipes or tubes integrated into the ground, groundwater or surface water with a heat-exchanging media that flows through a closed loop system. A pump forces either water or air through the system where it either gains or loses temperature before it circulates back to the heat pump." | Section 2020: Definitions of Specific Terms | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | 4207121344 | Setback - Roads | 15 | feet | For geothermal heat pumps, "All geothermal heat pumps and appurtenant structures and/or facilities associated with their operation shall be setback from all property lines a distance of not less than the normal setback requirements for accessory buildings/structures in that zoning district or at least fifteen (15) feet from all property lines and all street right of way lines, whichever is larger." | Section 23050.1.C.1.e | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | 4207121344 | Setback - Property Lines | 15 | feet | For geothermal heat pumps, "All geothermal heat pumps and appurtenant structures and/or facilities associated with their operation shall be setback from all property lines a distance of not less than the normal setback requirements for accessory buildings/structures in that zoning district or at least fifteen (15) feet from all property lines and all street right of way lines, whichever is larger." | Section 23050.1.C.1.e | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | 4207121344 | Setback - Yards | 15 | feet | For geothermal heat pumps, "No visible appurtenant structures and/or facilities associated with the operation of a geothermal heat pump shall be permitted in the front yard of the lot on which it is located and shall be a minimum of fifteen (15) feet to the rear of the front face of the principal building." | Section 23050.1.C.1.f | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | East Lampeter | 4207121344 | Open-loop Prohibitions |  |  | "Geothermal heat pumps designed with an open loop system shall be prohibited." | Section 23050.1.C.1.h | 2019 | https://eastlampetertownship.org/wp-content/uploads/bsk-pdf-manager/2020/02/6-20-19-ORD-344-APRVD.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM - An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | Section 114 Definitions | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Setback - Property Lines | 10 | feet | "All parts of the geothermal system shall be located a minimum distance of ten (10) feet from any property line..." | Section 461.4 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Setback - Wastewater | 100 | feet | "All parts of the geothermal system shall be located a minimum distance of ten (10) feet from any property line, fifty (50) feet from any septic tank, and one hundred (100) feet from any septic leaching system." | Section 461.4 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Setback - Private Water | 25 | feet | "All parts of the geothermal system shall be located a minimum distance of twenty-five (25) feet from any on-lot wells." | Section 461.5 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application, and the applicant shall provide documentation to demonstrate that the design complies with, and the installation shall comply, with applicable industry standards." | Section 461.2 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Screening |  |  | "Above ground equipment associated with geothermal pumps shall not be installed in the front yard of any lot or the side yard of a corner lot adjacent to a public right-of-way and shall meet all required setbacks for the applicable Zone." | Section 461.6 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Certification |  |  | "The design and installation of Geothermal Systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the ANSI, the IGSHPA, ASTM, the ARI, or other similar certifying organizations, and shall comply with the Building Code and with all other applicable Township requirements." | Section 461.2 | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Eden | 4207122336 | Open-loop Prohibitions |  |  | "Open loop geothermal systems shall not be permitted in the Township." | Section 461 Geothermal Energy Systems | 2024 | https://www.edentownship.org/_files/ugd/ca28e6_12bf43fa35a843c79b281bb00194dea7.pdf
Pennsylvania | Lancaster | Elizabethtown | 4207123016 | Permit |  |  | "In addition to all other requirements to obtain a zoning permit, the application shall state the kind of system to be installed; the name, address and telephone number of the proposed installer; and the plot plan of the lot, indicating the size of lot and location of the geothermal boreholes for heat pump systems." Also: "No person shall (1) construct or install a geothermal system; (2) dig, bore, drill, replace, modify, repair or destroy a well that is intended to be or was part of a geothermal system; or (3) make any other excavation that may intersect groundwater without first obtaining a permit from the Borough." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | 4207123016 | Inspection |  |  | "Said site shall be available for inspection prior to completion." Also under System Testing: "All geothermal systems installed under the provisions of this Section must be tested." "The system shall be tested hydrostatically at 1 1/2 times the maximum system design pressure but not less than 200 psi." "The duration of each test shall be not less than 15 minutes." "All geothermal systems must be pressure checked to the original standard by a geothermal contractor licensed in the Commonwealth of Pennsylvania once every three years from the system's certification date. Results of the test shall be submitted to the Borough's Building Code Inspector." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | 4207123016 | Licensed Driller |  |  | "All boreholes shall be drilled by Pennsylvania registered/licensed water well drillers." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | 4207123016 | Certification |  |  | "All boreholes shall be drilled by Pennsylvania registered/licensed water well drillers." "The contractor shall provide data sheets indicating that the grout meets the requirements of NSF/ANSI Standard 60, Drinking Water Treatment Chemicals — Health Effects." "All geothermal systems must be pressure checked to the original standard by a geothermal contractor licensed in the Commonwealth of Pennsylvania once every three years from the system's certification date." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | 4207123016 | Decommissioning |  |  | "System Abandonment. Heat transfer fluid must be removed by displacement with grout. The top of the borehole must be uncovered and capped with grout." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Elizabethtown | 4207123016 | Open-loop Prohibitions |  |  | "Open Loop Geothermal System Prohibited. No person shall install or maintain an open loop system within the Borough." | § 1327 Geothermal Systems | 2023 | https://ecode360.com/27499093
Pennsylvania | Lancaster | Lititz | 4207143816 | Other Prohibitions/Regulations |  |  | 'The following discharges are authorized unless they are determined to be significant contributors to pollution ... Non-contaminated HVAC condensation and water from geothermal systems.' Section 801.F adds: 'In the event that the Borough or DEP determines that any of the discharges identified in Section 801.E above significantly contribute to pollution of the waters of this Commonwealth, the Borough or DEP will notify the responsible person(s) to cease the discharge.' | Section 801.E | 2019 | https://www.lititzborough.org/1303/Stormwater-Management-Ordinance
Pennsylvania | Lancaster | Manheim | 4207146888 | Permit |  |  | "it will be necessary for any property owner owning property within Manheim Borough to obtain a permit from the Borough Building Code Official prior to installation of any type of geothermal boreholes for heat pump systems on said land within the Borough." The application "shall state the kind of system to be installed, the name, address and telephone number of the proposed installer, the plot plan of the lot indicating the size of lot and location of the geothermal boreholes for heat pump systems." | § 132-1 Permit required. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | 4207146888 | Inspection |  |  | "Said site shall be available for inspection prior to completion." | § 132-1 Permit required. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | 4207146888 | Certification |  |  | "Pipes must be heat fused and the joints water pressure tested, with a minimum test pressure of 200 pounds per square inch, by a contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | § 132-5 Regulations. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | 4207146888 | Decommissioning |  |  | "All bore holes must be backfilled (preferably with bentonite), capped and sealed." | § 132-5 Regulations. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | 4207146888 | Open-loop Prohibitions |  |  | "Types of geothermal boreholes for heat pump systems not permitted to be installed within the Borough is the open loop system." | § 132-4 Not permitted. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | 4207146888 | Other Prohibitions/Regulations |  |  | "Closed loop (vertical). May only be installed on lots where the Codes Compliance Officer determines that the lot is too small for a closed loop (horizontal) system or in cases in which rock hinders the excavation and/or installation process." | § 132-3 Permitted types. | 2009 | https://ecode360.com/15954580
Pennsylvania | Lancaster | Manheim | 4207146896 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM (GEOTHERMAL HEAT PUMPS) - An energygenerating system that uses a heat pump in conjunction with the earth's thermal properties to heat and cool buildings. Such systems may be categorized as or include: A. BOREHOLES - A hole drilled or bored into the earth into which piping is inserted for use in a closed-vertical-loop geothermal system. B. CLOSED-LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump and a water source heat pump in which the heat transfer fluid is not exposed to the atmosphere. The heat transfer fluid is potable or beneficial reuse water and may have approved antifreeze added. C. OPEN-LOOP GEOTHERMAL SYSTEM - A type of geothermal heating and/or cooling system that utilizes a water pump to deliver water from a well or other source to a heat exchanger. The discharge water from the heat exchanger may be returned to the subsurface through an injection or recharge well or infiltration bed or may be discharged into a pond, lake or stream." | SECTION 503. DEFINITIONS | 2023 | https://www.manheimtownship.org/DocumentCenter/View/7917/8ARTICLE-5---Definitions
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, CLOSED LOOP A type of geothermal heating or cooling system, not designed or used for the generation of power, that utilized a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere..." and "GEOTHERMAL ENERGY SYSTEM, OPEN LOOP A type of geothermal heating or cooling system that utilizes a water-supply well and water pump to deliver ground water to a water-source heat pump." | § 270-32. Definitions | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Setback - Property Lines | 25 | feet | "Geothermal energy systems shall be located a minimum of 25 feet from all property lines, except as otherwise specified." | § 270-63.D(14)(d)[3](c) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Setback - Wastewater | 25 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells and a minimum of 25 feet from any existing septic system." | § 270-63.D(14)(d)[3](d) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells..." | § 270-63.D(14)(d)[3](d) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Maximum Well Depth | 20 | feet | "A closed horizontal loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 270-63.D(14)(d)[3](a) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Permit |  |  | WP District: "Any geothermal exchange system shall only be permitted if the applicant provides written evidence that the system will comply with the DEP Ground Source Heat Pump Manual as it pertains to protection of water quality." Also, "Construction and Permit. The design and installation of geothermal energy systems shall conform to applicable industry standards and the UCC. At the time of application for a permit, the applicant shall submit manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 270-49.E(4); § 270-63.D(14)(d)[4] | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Decommissioning |  |  | "If the geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his/her expense after a demolition permit has been obtained... (i) The heat pump and any external mechanical equipment shall be removed; and (ii) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with the applicable regulations. The top of the pipe, coil, or boring shall be uncovered and grouted." | § 270-63.D(14)(d)[5] | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Open-loop Prohibitions |  |  | "Closed-loop geothermal energy systems are allowed in all zoning districts as an accessory use to a principal use of the site. Open-loop geothermal energy systems are prohibited within the Borough." | § 270-63.D(14)(d)[1] | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mount Joy | 4207151656 | Other Prohibitions/Regulations |  |  | Within the WP Wellhead Protection District, the following uses are prohibited: "Underground injection wells." | § 270-49.E(3)(f) | 2016 | https://mountjoyborough.com/wp-content/uploads/Chapter-270-Zoning-draft-1.5.16-clean-2.pdf
Pennsylvania | Lancaster | Mountville | 4207152016 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY SYSTEM — Any one or more method and facilities used in the conversion, storage, and distribution including electrical infrastructure, transmission lines, and other appurtenant structures and facilities of renewable energy sources, including but not limited to sunlight, wind, rain, tides, and geothermal heat." | § 202 Definitions | 2019 | https://ecode360.com/42252150
Pennsylvania | Lancaster | New Holland | 4207153696 | Definition: Well |  |  | "GEOTHERMAL WELL - a drilled hole used in connection with a geothermal system." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 1. Definitions | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP GEOTHERMAL SYSTEM - a geothermal system in which the same liquid is continuously running through piping in a closed circuit, and during its operation, no new liquid is introduced to the system or used liquid discharged from the system." "OPEN LOOP GEOTHERMAL SYSTEM - a geothermal system in which liquid is run through piping after being drawn from a source and is then discharged to that source or an alternate location." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 1. Definitions | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Setback - Roads | 25 | feet | "No well shall be permitted within 25 feet of a cartway." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Setback - Property Lines | 25 | feet | "A geothermal well shall be set back at least 25 feet from all lot lines." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Setback - Wastewater | 100 | feet | "No geothermal well shall be located within 100 feet of any existing drinking water wells or any planned drinking water wells, or 100 feet of any septic system." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Setback - Public Water | 100 | feet | "No geothermal well shall be located within 100 feet of any existing drinking water wells or any planned drinking water wells..." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Permit |  |  | "No person shall (1) construct or install a geothermal system, (2) dig, bore, drill, replace, modify, repair, and/or destroy a well that is, is intended to be, or was part of a geothermal system, or (3) make any other excavation that may intersect groundwater without first obtaining a permit from the Borough. A permit is required for any geothermal system within New Holland Borough." The ordinance also requires that "No permit for such a well shall be issued until the plans, specifications, and site plans have been approved by the Borough for compliance with this Part." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 2. Permits | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Decommissioning |  |  | "A geothermal system shall be abandoned in a manner acceptable to the Borough and shall comply with the laws, rules, and regulations applicable to the abandonment of water wells. Any and all heat transfer fluids must be removed by displacement with grout in a manner acceptable to the Borough. The top of the borehole must be uncovered and capped with grout in a manner acceptable to the Borough." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; Requirements and Standards | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | New Holland | 4207153696 | Open-loop Prohibitions |  |  | "No person shall construct or install an Open Loop Geothermal System." | §108. UCC Requirements for Geothermal Heating; § 403.29 Geothermal Systems; 2. Permits | 2014 | https://newhollandborough.org/wp-content/uploads/2016/02/Chapter-5-Code-Enforcement.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY PRODUCTION FACILITIES - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from natural sources (e.g. solar panels, wind turbines, hydro turbines, geo-thermal exchangers, and similar technologies.)" | Section 112 Specific Words and Phrases | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of twenty five feet (25) feet from any property line." | Section 404.1.3 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Setback - Private Water | 200 | feet | For open loop systems with underground injection, "The return well shall be located a minimum distance of two hundred (200) feet from wells on adjacent properties" and "The return well shall be located a minimum distance of one hundred (100) feet from the on-site well." | Section 404.1.5.2(F)-(I) | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Maximum Well Depth | 20 | feet | "Horizontal closed loop systems shall be no more than twenty (20) feet deep." | Section 404.1.4.2 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." Also, Section 400.2 states for permitted uses: "these standards must be satisfied prior to approval of any application for a land development (when applicable) or a zoning permit." Section 200.3.1, 201.3.1, 202.3.1, 203.3.1, 204.3.1, and 418.6.1 list "Alternative energy production facilities (Geothermal Systems...)" as accessory uses "subject to the requirements of Section 404." | Section 404.1 Geothermal Systems | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Licensed Driller |  |  | "Vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | Section 454.21.3 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Open-loop Prohibitions |  |  | "Discharge of water from open loop systems into sanitary sewer systems shall be prohibited, except upon approval by the sanitary sewage system provider." "Discharge of water from open loop systems into storm sewers shall not be permitted." "The use of open loop systems within identified well head protection areas is prohibited." | Section 404.1.5.2(A)-(B),(L) | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Providence | 4207162832 | Other Prohibitions/Regulations |  |  | "Only the following types of geothermal energy systems shall be permitted: ... Closed horizontal loop; ... Closed vertical loop; and ... Open horizontal loop systems relying upon injection wells or water courses." | Section 404.1.2 | 2022 | http://providencetownship.com/wp-content/uploads/2022/08/ZO-2022.pdf
Pennsylvania | Lancaster | Quarryville | 4207163064 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, CLOSED-LOOP — A type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." "GEOTHERMAL ENERGY SYSTEM, OPEN-LOOP — A type of geothermal heating or cooling system that utilizes a water-supply well and a water pump to deliver groundwater to a water-source heat pump." | § 217-2 Definitions and word usage | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Setback - Right of Way | 10 | feet | Aboveground equipment associated with geothermal pumps "shall meet all minimum accessory structure setbacks required for the zoning district" and "shall not be installed in ... the yard of a corner lot adjacent to a public right-of-way." | § 217-3C(6) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Setback - Property Lines | 10 | feet | "Geothermal energy systems shall be located a minimum of 10 feet from all property lines, except as otherwise specified." | § 217-3C(3) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Setback - Yards | 10 | feet | "Aboveground equipment associated with geothermal pumps shall not be installed in the front yard of any lot or the yard of a corner lot adjacent to a public right-of-way and shall meet all minimum accessory structure setbacks required for the zoning district." | § 217-3C(6) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Setback - Wastewater | 100 | feet | "Geothermal energy systems shall be located a minimum of 50 feet from treatment tanks, dosing tanks, lift pump tanks, filter tanks and chlorine contact/storage tanks of an on-lot sewage disposal system. Geothermal energy systems shall be located a minimum of 100 feet from the absorption area of an on-lot sewage disposal system. Geothermal energy systems shall be located a minimum of 100 feet from the perimeter of any spray field of an on-lot sewage disposal system." | § 217-3C(5) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Setback - Public Water | 100 | feet | "Geothermal energy systems shall be located a minimum of 100 feet from existing potable water wells." | § 217-3C(4) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Maximum Well Depth | 20 | feet | "A horizontal closed-loop system shall be installed a maximum of 20 feet below the average finished grade of the area in which located." | § 217-3C(1) | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Permit |  |  | "Any person seeking to install a geothermal energy system shall apply for and obtain a permit from the Borough prior to commencing installation." The applicant must file information demonstrating compliance and pay the Borough fee. The ordinance also requires submission of "manufacturer certificates of design and circulating fluid compliance obtained by the geothermal energy system manufacturer from a reputable certifying organization." | § 217-3D | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Inspection |  |  | "Any person installing a geothermal energy system shall obtain all inspections required by the UCC. The Construction Code Official shall have the authority to inspect for compliance with all requirements of this chapter as well as compliance with all requirements of the UCC." | § 217-3E | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Decommissioning |  |  | "If a geothermal energy system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition permit has been obtained." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed" and "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | § 217-3F | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Quarryville | 4207163064 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal energy systems are permitted within the Borough. Open-loop geothermal energy systems are prohibited within the Borough." | § 217-3A | 2021 | https://ecode360.com/33946445
Pennsylvania | Lancaster | Rapho | 4207163440 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES – A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | Section 202.A.142.c | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | 4207163440 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY SYSTEM – A system or facility used in the conversion, storage, and distribution of renewable energy sources, including electrical infrastructure, transmission lines, and other appurtenant structures and facilities. For purposes of this Zoning Ordinance, this term includes but not limited to renewable energy sources such as sunlight, wind, rain, tides, and geothermal heat facilities." | Section 202.A.23 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | 4207163440 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL TERMS & PHRASES ... when used in Article 5 ... relating to the 'Geothermal Energy Systems' (§ 502.A.) shall have the meaning given to them..." including: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM – A mechanism for heat exchange ... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system..."; "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM – A borehole that extends beneath the surface. Pipes are installed with U-bends at the bottom of the borehole..."; "GEOTHERMAL ENERGY SYSTEM – An energy generating system that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings."; and "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM – Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | Section 202.A.142 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | 4207163440 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | Section 502.A.4.b | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | 4207163440 | Permit |  |  | Section 502.A.1 states: "The manufacturer specifications shall be submitted as part of the application." Section 502 governs accessory alternative energy systems, including geothermal energy systems, so geothermal applications must include manufacturer specifications as part of the approval application. | Section 502.A.1; Section 902 (referenced) | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | 4207163440 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations..." | Section 502.A.1 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Rapho | 4207163440 | Other Prohibitions/Regulations |  |  | Section 502.A.2 states: "Only the following types of geothermal energy systems shall be permitted: a. Closed horizontal loop; b. Closed vertical loop; and c. Open horizontal loop systems relying upon injection wells or water courses." Section 502.A.5.b.(6) further states: "The use of open loop systems within identified well head protection areas is prohibited." | Section 502.A.2; Section 502.A.6 | 2022 | https://www.raphotownship.com/DocumentCenter/View/1406/Rapho-Township-Zoning-Ordinance-amended-through-2022-10-20
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM – an energy generating system that uses the Earth’s thermal properties in conjunction with a power source such as electricity to provide greater efficiency in the heating and cooling of buildings." | §104. Definitions | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Setback - Property Lines | 25 | feet | "Unless otherwise specified, geothermal system shall be located a minimum distance of twenty five feet (25) feet from any property line." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than twenty (20) feet deep." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Permit |  |  | "In addition to all other requirements to obtain a zoning permit, the applicant shall state the kind of system to be installed; the name, address and telephone number of the proposed installer; and the plot plan of the lot, indicating the size of the lot and the location of the geothermal boreholes for the heat pump system." Also: "Nor shall any person dig, bore, drill, replace, modify or destroy a well that is intended to be or was part of a geothermal system nor make any other excavation that may intersect groundwater without first obtaining a permit from the Borough." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Inspection |  |  | "Said site shall be available for inspection prior to completion." Also: "All geothermal systems installed under the provisions of this Section shall be tested hydrostatically at one and one half times the maximum system design pressure, but not less than 200 psi. The duration of each test shall be not less than 15 minutes." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Licensed Driller |  |  | "All bore holes shall be drilled by a Pennsylvania registered and licensed water well driller." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Certification |  |  | "All bore holes shall be drilled by a Pennsylvania registered and licensed water well driller." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a permit has been obtained... (1) The heat pump and any external mechanical equipment shall be removed and (2) Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations. The top of the pipe, coil or boring shall be uncovered and grouted." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Open-loop Prohibitions |  |  | "Open loop geothermal systems are prohibited. No person shall install, maintain or operate an open loop system within the Borough." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Terre Hill | 4207176400 | Other Prohibitions/Regulations |  |  | "The only type of geothermal boreholes permitted to be drilled within the Borough are: (1) Air to air; (2) Closed loop horizontal; and (3) Closed loop vertical." | §503.32 Requirements for Geothermal Energy System | 2019 | https://www.terrehillboro.com/wp-content/uploads/2019/03/THB-Proposed-Zoning.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | SECTION 113 SPECIFIC WORDS AND PHRASES | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Setback - Property Lines | 20 | feet | "No geothermal system sub-surface loops and related geothermal boreholes shall be located closer than... twenty feet (20') from any and any property lines." | SECTION 405.T.4 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Setback - Wastewater | 25 | feet | "No geothermal system sub-surface loops and related geothermal boreholes shall be located closer than... twenty-five feet (25’) from any existing or planned on-lot sewage disposal systems..." | SECTION 405.T.4 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Setback - Public Water | 100 | feet | "No geothermal system sub-surface loops and related geothermal boreholes shall be located closer than one hundred feet (100’) from any existing or planned drinking water wells..." | SECTION 405.T.4 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Permit |  |  | "Within every Zone, alternative energy systems are permitted accessory uses by right" and "Any physical modification to an existing alternative energy system that materially alters the size, type and quantity of the facilities shall require a zoning permit"; also "In addition to those materials required in Section 901.B. of this Ordinance for a zoning permit, applicants for alternative energy systems shall be required to submit..." Section 405.T governs geothermal systems as part of these alternative energy systems. | SECTION 405 ALTERNATIVE ENERGY SYSTEMS | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Inspection |  |  | "With respect to each geothermal system well installation, the Pennsylvania-licensed well driller and/ or system installer shall provide to the Township, before activation of the system, copies of... Written documentation of the geothermal system testing and certification." | SECTION 405.T.7.D | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | SECTION 405.T.3 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Certification |  |  | "Prior to installation, all installation specifications and drawings for the geothermal system must be certified by a registered engineer within the Commonwealth of PA as conforming to the installation standards of the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air-Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations." | SECTION 405.T.2 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Decommissioning |  |  | "The applicant shall maintain the geothermal system in a safe condition and good repair at all times. Whenever a geothermal system endangers the public safety, the Zoning Officer shall give written notice to the owner... that such geothermal system shall be made safe or removed. The disposal of geothermal systems shall comply with all applicable Township, county, state, and federal regulations" and "In the event of the proposed discontinuance of the use of the geothermal system, a system closure plan will be prepared and submitted to the Township for its approval by the landowner prior to the conveyance by the landowner of the land to any third party." | SECTION 405.T.6 and 405.T.7.E.2 | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Upper Leacock | 4207179080 | Open-loop Prohibitions |  |  | "Only closed loop geothermal systems shall be permitted." | SECTION 405.T The following provisions shall specifically apply to geothermal systems | 2016 | https://www.ultwp.com/sites/g/files/vyhlif3966/f/uploads/official_zoning_ordinance.pdf
Pennsylvania | Lancaster | Warwick | 4207181168 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM" means "[a]n energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 340-10 Definitions | 2026 | https://ecode360.com/11671453
Pennsylvania | Lancaster | Warwick | 4207181168 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM" means "[a] type of geothermal heating and/or cooling system that consists of the following basic elements: underground loops of piping; approved, nontoxic heat transfer fluid; a heat pump; and an air distribution system." "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM" means "[a] type of geothermal heating and/or cooling system that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM" means "[a] type of geothermal heating and/or cooling system that utilizes a water-supply well, or other source, and a pump to deliver groundwater to a heat exchanger." | § 340-10 Definitions | 2026 | https://ecode360.com/11671453
Pennsylvania | Lancaster | West Cocalico | 4207182728 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM, CLOSED-LOOP" is defined as "A type of geothermal heating or cooling system, not designed or used for the generation of power, that utilizes a pressurized heat exchanger consisting of pipe, a circulating pump, and a water-source heat pump in which the heat transfer fluid is not exposed to the atmosphere." It further states: "The heat transfer fluid is potable water and may have approved antifreeze added." "GEOTHERMAL ENERGY SYSTEM, OPEN LOOP" is defined as "A type of geothermal heating or cooling system that utilizes a water-supply well and a water pump to deliver ground water to a water-source heat pump. The discharge water from the water-source heat pump may be returned to the subsurface through a recharge well or infiltration bed or may be discharged into a pond, lake or stream. A spring may also be the source of the ground water supply." | GEOTHERMAL ENERGY SYSTEM, CLOSED-LOOP / GEOTHERMAL ENERGY SYSTEM, OPEN LOOP | 2024 | https://ecode360.com/37307777
Pennsylvania | Lancaster | West Hempfield | 4207183152 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES" means "A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 201.2 Terms defined. GEOTHERMAL TERMS [Added 8-3-2010 by Ord. No. 4-10] | 2020 | https://ecode360.com/32127028
Pennsylvania | Lancaster | West Hempfield | 4207183152 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM" means "An energy generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." The same geothermal terms section also defines system types: "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM" as "A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system" and "OPEN LOOP GEOTHERMAL SYSTEM" as a system where "Water is pumped from a water well or other water source into a heat exchanger located in a surface building." | § 201.2 Terms defined. GEOTHERMAL TERMS [Added 8-3-2010 by Ord. No. 4-10] | 2020 | https://ecode360.com/32127028
Pennsylvania | Lancaster | West Hempfield | 4207183152 | Maximum Well Depth | 20 | feet | The definition of "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM" states: "A horizontal closed loop system shall be no more than 20 feet deep." | § 201.2 Terms defined. GEOTHERMAL TERMS [Added 8-3-2010 by Ord. No. 4-10] | 2020 | https://ecode360.com/32127028
Pennsylvania | Lebanon | North Cornwall | 4207554928 | Definition: Geothermal |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | SECTION 113 - SPECIFIC WORDS AND PHRASES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | 4207554928 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM - Any device installed as an accessory use that supplies energy principally for the principal use of the property that is derived from the exchange of underground temperature." | SECTION 113 - SPECIFIC WORDS AND PHRASES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | 4207554928 | Setback - Private Water | 20 | feet | "No geothermal system sub-surface loops will be located closer than twenty (20) feet from any existing or planned drinking water wells." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | 4207554928 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | 4207554928 | Certification |  |  | "The geothermal system shall conform to the International Ground Source Heat Pump Association (IGSHPA) installation standards, as same may be amended and updated from time." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | North Cornwall | 4207554928 | Open-loop Prohibitions |  |  | "The following provisions shall specifically apply to geothermal systems: a. Only closed loop geothermal systems shall be permitted." | SECTION 319.B.11 - ALTERNATIVE ENERGY PRODUCTION FACILITIES | 2020 | https://www.nctown.org/resource/Ordinances/North%20Cornwall%20Township%20Zoning%20Ordinance%20No.%20317.pdf
Pennsylvania | Lebanon | South Londonderry | 4207572296 | Setback - Private Water | 20 | feet | 'No geothermal system sub-surface loops will be located closer than twenty (20) feet from any existing or planned drinking water wells.' | Section 404.F | 2024 | https://www.southlondonderry.org/uploads/6/1/2/6/61268441/slt_2024_zoning_ordinance_final.pdf
Pennsylvania | Lebanon | South Londonderry | 4207572296 | Open-loop Prohibitions |  |  | 'The following provisions shall specifically apply to geothermal systems: Only closed loop geothermal systems shall be permitted.' | Section 404.F | 2024 | https://www.southlondonderry.org/uploads/6/1/2/6/61268441/slt_2024_zoning_ordinance_final.pdf
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Definition: Well |  |  | "GEOTHERMAL WELL — Any excavation that is drilled, cored, bored, washed, driven, dug, jetted or otherwise constructed where the intended use of such excavation is for the circulation of geothermal fluid vertically, or the location, requisition or artificial recharge of groundwater. (includes open- and closed-loop vertical systems)." | § 12-102 Definitions | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Definition: Geothermal |  |  | "GEOTHERMAL HEAT — Heat derived from geothermal resources, or heat derived from groundwater." Also: "GEOTHERMAL FLUID — Any fluid transporting or capable of transporting geothermal heat." | § 12-102 Definitions | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEATING SYSTEM — A geothermal heat pump system which relies on the contained circulation of geothermal fluids to obtain and to utilize geothermal resources." Also: "CLOSED-LOOP SYSTEMS — Geothermal heat pump system which relies on the contained circulation of geothermal fluids through any underground loop of pipes..." and "OPEN-LOOP SYSTEM — A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring, or surface water." | § 12-102 Definitions | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Permit |  |  | § 12-107: "Any persons desiring to construct, install, or alter a geothermal heating system within the Township shall first apply for a geothermal heating system permit... No person shall commence construction or alteration of a geothermal heating system prior to... applying for and receiving a permit." § 12-106: "All open-loop geothermal heating systems are permitted, provided they are reviewed and approved by the Township prior to construction" and "Vertical closed-loop systems shall be permitted, provided they are reviewed and approved by the Township prior to construction." § 12-111: "Before any drilling or site preparation begins the well driller shall apply for a well permit from the Township" and "No geothermal well shall be put into service without receiving a geothermal well permit..." | §§ 12-106, 12-107, 12-111 | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Inspection |  |  | § 12-115: "The following inspections shall be required by the Township: Site inspection before any work is done... Inspection of the installed loop (pressure test); Inspection of grouting; Inspection of the completely installed system before operations commence and upon commencement of operations; Periodic inspections no less than once every three years; Inspection if geothermal system or well is abandoned..." § 12-116: "Abandonment procedures shall be subject to Township inspection." § 12-117 authorizes Township entry "for purposes of inspecting geothermal facilities or monitoring the operational characteristics of such facilities..." | §§ 12-115, 12-116, 12-117 | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Licensed Driller |  |  | § 12-112(A)(1): "All geothermal wells in the Township shall be constructed in accordance with Pennsylvania Act 610 (Water Well Drillers License Act)." § 12-116: "All abandoned wells must be filled and sealed by a PA/DCNR licensed water well driller..." § 12-111(A): "Before any drilling or site preparation begins the well driller shall apply for a well permit from the Township." | §§ 12-111, 12-112, 12-116 | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Certification |  |  | "All geothermal heating systems and wells installed for the purposes of heating and/or, cooling a facility must adhere to the International Ground Source Heat Pump Associations (IGSHPA) design and installation standards, and the installer(s) and well driller(s) must be certified by the IGSHPA." | § 12-112 Geothermal Well Construction Requirements | 2025 | https://ecode360.com/30862575
Pennsylvania | Lebanon | West Lebanon | 4207583312 | Decommissioning |  |  | "All abandoned wells must be filled and sealed by a PA/DCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR water well abandonment form shall be submitted to the Township within 30 days of abandonment. Abandonment procedures shall be subject to Township inspection." | § 12-116 Well Abandonment | 2025 | https://ecode360.com/30862575
Pennsylvania | Lehigh | Emmaus | 4207723584 | Setback - Right of Way | 20 | feet | Table 27-4.H.a states: "Dedicated public Right-of-Way — 20" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, underground geothermal systems shall be located a minimum distance of 10 feet from any Lot Line." | §27-412 Accessory Uses, 2.I.(3)(b) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Setback - Wastewater | 100 | feet | Table 27-4.H.a states: "Septic tanks, aerobic tanks or holding tanks — 50" feet and "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields — 100" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Setback - Sewer Lines | 50 | feet | Table 27-4.H.a states: "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 50" feet; and for "Existing water and forced sewer buried utilities and/or utility trenches" the system must be "Outside existing Easement or, if no Easement exists, no less than 50 feet from the utility or trench center line." | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Setback - Water Bodies | 50 | feet | Table 27-4.H.a states: "Lakes, ponds, streams, or other surface waters — 50" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Table 27-4.H.a states: "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles — 100" feet. | §27-412 Accessory Uses, 2.I.(3)(c), Table 27-4.H.a | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Permit |  |  | "The owner shall remove the abandoned system at their expense after a demolition Permit has been obtained..." | §27-412 Accessory Uses, 2.I.(5) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Certification |  |  | "The installer must have at least one representative who is certified by the International Ground Source Heat Pump Association (IGSHPA)." | §27-412 Accessory Uses, 2.I.(1) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at their expense after a demolition Permit has been obtained..." The ordinance further requires: "The heat pump and any external mechanical equipment shall be removed"; "Pipes or coils below the land surface shall be filled with grout to displace the heat transfer fluid. The heat transfer fluid shall be captured and disposed of in accordance with applicable regulations"; and "All abandoned wells shall be reported to PA DCNR on its forms and a copy provided to the municipality." | §27-412 Accessory Uses, 2.I.(5) | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Emmaus | 4207723584 | Open-loop Prohibitions |  |  | "Open-Loop Geothermal Energy Systems and any system not meeting the definition of a Closed-Horizontal-Loop Geothermal Energy System or closed-vertical-loop geothermal energy system are prohibited in the Borough." | §27-412 Accessory Uses, 2.I. Geothermal Energy Systems | 2024 | https://www.emmauspa.gov/DocumentCenter/View/806/Proposed-Emmaus-Borough-Zoning-Ordinance
Pennsylvania | Lehigh | Fountain Hill | 4207727008 | Permit |  |  | The fee schedule lists: "GENERATOR (backup power) OR GEOTHERMAL SYSTEMS: - $ 200.00 plan submission, Building, Mechanical and Electrical Only." The resolution also states under surcharge rates: "FAILURE TO OBTAIN A PERMIT BEFORE WORK BEGINS" and "ALL PERMIT FEES DOUBLED." | Uniform Construction Code Building Permit Fee Schedule / GENERATOR (backup power) OR GEOTHERMAL SYSTEMS | 2022 | https://www.fountainhill.org/wp-content/uploads/2022/03/Current-Fee-Schedule.pdf
Pennsylvania | Lehigh | Fountain Hill | 4207727008 | Inspection |  |  | The resolution states: "Please call 610-867-5124 for any costs not included on these sheets or with any questions. TO SCHEDULE INSPECTIONS REQUIRE 48 HOURS NOTICE." It also includes geothermal systems under the building permit schedule as "Building, Mechanical and Electrical Only," and separately provides "RESIDENTIAL BUILDING INSPECTIONS (when not included in above pricing): $ 75.00 per hour as well as failed inspections." | Uniform Construction Code Building Permit Fee Schedule / MISCELLANEOUS FEES; note on scheduling inspections | 2022 | https://www.fountainhill.org/wp-content/uploads/2022/03/Current-Fee-Schedule.pdf
Pennsylvania | Lehigh | South Whitehall | 4207772632 | Definition: Geothermal Heat Pump |  |  | "GEOEXCHANGE ENERGY SYSTEM, OPEN LOOP — A geoexchange energy system which extracts surface or ground water into a heat pump, and discharges water back into the ground through a different well." | § 350-05 Definition of terms | 2019 | https://ecode360.com/48196093
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Setback - Private Water | 20 | feet | "No geothermal system sub-surface loops will be located closer than twenty feet (20') from any existing drinking water wells or any planned drinking water wells;" | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Permit |  |  | "Prior to installation, all installation specifications and drawings for the geothermal system must be approved by the Township's geotechnical consultant as conforming to the International Ground Source Heat Pump Association (IGSHPA) installation standards..." | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Inspection |  |  | Before activation, the driller and/or installer must provide "written documentation of the geothermal system testing and certification"; for closed-loop systems, "System leak testing shall be 150 percent higher than operating pressure." | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Licensed Driller |  |  | "The vertical geothermal system well (or wells) installation will be made only by a Pennsylvania-licensed well driller;" | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Certification |  |  | "Prior to installation, all installation specifications and drawings for the geothermal system must be approved by the Township's geotechnical consultant as conforming to the International Ground Source Heat Pump Association (IGSHPA) installation standards..." and before activation the driller and/or installer must provide "written documentation of the geothermal system testing and certification." | Section 404.H | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Decommissioning |  |  | "In the event of the proposed discontinuance of the use of the geothermal system, a system closure plan will be prepared and submitted to the Township for its approval by the landowner prior to the conveyance by the landowner of the land to any third party." | Section 404.H.e.2 | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Open-loop Prohibitions |  |  | "Every geothermal system to be installed or constructed in areas of the Township underlain by carbonate bedrock, as depicted on the Natural and Cultural Features Map as Carbonate Geology, and Floodplain Zones, Riparian Buffers, Wetlands and Buffers, and PNDI sites regulated by Section 515 of this Ordinance must be a 'closed-loop' system." | Section 404.H.f | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Lehigh | Upper Saucon | 4207779288 | Other Prohibitions/Regulations |  |  | "No geothermal system shall be connected in any way to any facilities for sanitary sewer or stormwater management." | Section 404.H.g | 2010 | https://www.uppersaucon.org/wp-content/uploads/2016/02/ord141-A.pdf
Pennsylvania | Luzerne | Hazleton | 4207933408 | Screening |  |  | "All mechanical, electrical, communication, and service equipment, including satellite dishes, air conditioning units, large vents and vent pipes, heat pumps and mechanical equipment, and other appurtenances shall be concealed by or integrated within the roof form or screened from view at ground level of nearby streets by parapets, walls, fences, landscaping, or other approved means." | SECTION 505. DOWNTOWN OVERLAY DISTRICT, s. Screening | 2020 | https://hazletoncity.org/images/Hazleton_2020_Draft_Zoning_Ordinance.pdf
Pennsylvania | Mercer | Springfield | 4208573080 | Definition: Well |  |  | "Abandonment of Well – An abandoned or unused well may be defined as one of the following: ... 6. An inactive geothermal groundwater heat exchange system." | Section 602.2 Special Definitions | 2018 | http://www.springfield-mercer.org/images/_4-2018_Zoning_Ordinance_-_October_2,_2018.pdf
Pennsylvania | Monroe | Paradise | 4208957856 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP Any geothermal, earth-coupled, geoexchange, water-coupled, groundwater, ground-coupled, closed-loop, coiled, open, or water source heat pump system used for heating and/or cooling which utilizes groundwater extracted from a well." | § 1-16 Defined terms | 2026 | https://ecode360.com/38606445
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Right of Way | 25 | feet | The geothermal setback table lists "Dedicated public right-of-way and property lines — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Property Lines | 25 | feet | The geothermal setback table lists "Dedicated public right-of-way and property lines — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Building Foundation | 25 | feet | The geothermal setback table lists "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved) — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Wastewater | 100 | feet | The geothermal setback table requires: "Septic tanks, aerobic tanks, or holding tanks — at least 100 feet"; "Subsurface sewage disposal systems, elevated sand mounds, or other sewage disposal fields — 100 feet"; "Sewage seepage pits and cesspools — at least 100 feet"; and "Spray irrigation sites, sewage sludge, and septage disposal sites — at least 100 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Animal Enclosures | 25 | feet | The geothermal setback table lists "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Fuel (above ground) | 25 | feet | The geothermal setback table lists "Farm silos, barnyards, privies, and fuel tanks — at least 25 feet." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Water Lines | 15 | feet | The geothermal setback table requires separation from "Existing water and forced sewer buried utilities and/or utility trenches" of "at least 15 feet or outside easement." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Sewer Lines | 15 | feet | The geothermal setback table lists "Gravity sewer lines and drains carrying domestic sewage or industrial waste — 5-15 feet or according to easement" and "Existing water and forced sewer buried utilities and/or utility trenches — at least 15 feet or outside easement." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The geothermal setback table requires wells and boreholes to be separated from "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" by "300 feet 100-150 feet (if borehole is cased and grouted inside and out)." | § 470-31.F(8) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." | § 470-31.F(3) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Licensed Driller |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well." | § 470-31.F(6) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Certification |  |  | "Only a Pennsylvania Department of Environmental Protection licensed well driller, or an IGSHPA-accredited geothermal system installer, shall conduct the drilling of a geothermal well. In all cases, the well drilling rig must also be approved by Pennsylvania Department of Environmental Protection." | § 470-31.F(6) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Decommissioning |  |  | The ordinance requires the geothermal system to be "installed, maintained, and decommissioned in standards conforming to International Ground Source Heat Pump Association (IGSHPA) Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards" and further states: "If the geothermal energy system is ever abandoned or enters into a state of disrepair, it shall be the responsibility of the property owner to remove, permanently seal, or properly maintain the geothermal energy system within 12 months from the date the system enters such a state. Any earth disturbance as a result of the removal or permanent sealing of the geothermal energy system shall be graded, reseeded and revegetated with native species to its pre-disturbance condition." | § 470-31.F(5), § 470-31.F(13) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Pocono | 4208961728 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems are prohibited." | § 470-31.F(2) | 2024 | https://irp.cdn-website.com/5dacd758/files/uploaded/4-22-24-Zoning-SALDO-Meeting-13-Agenda-and-Materials.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) - Any system of mechanical and electrical facilities designed for the purpose of withdrawing heat from, or discharging heat to the ground, groundwater or surface waters." | ARTICLE II: Chapter 27, Part 2, Section 202 (Definitions) | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Setback - Roads | 10 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 10 feet from any property line or public road right-of-way line." | ARTICLE I, Section 508, Paragraph 1, H.2.a | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, geothermal systems shall be located a minimum distance of 10 feet from any property line or public road right-of-way line." | ARTICLE I, Section 508, Paragraph 1, H.2.a | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Permit |  |  | Inspection subsection: "Applicable plan review and inspection fees shall be paid at the time of application for a building permit." Abandonment subsection: "The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." | ARTICLE I, Section 508, Paragraph 1, H.4.a; H.6 | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Inspection |  |  | "The Township Building Code Inspector or his or her designee shall observe the pressure testing." "The Township Building Code Inspector or his or her designee shall observe grouting of the vertical boreholes for the GSHP system wells." "The GSHP system installer shall contact the Township Building Code Inspector or his or her designee a minimum of 48 hours in advance to inspect grouting and to verify pressure testing." | ARTICLE I, Section 508, Paragraph 1, H.4.b-d | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Licensed Driller |  |  | "GSHP system well drilling shall only be undertaken by a Pennsylvania licensed well driller." | ARTICLE I, Section 508, Paragraph 1, H.1.c | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Decommissioning |  |  | Operation and maintenance: "A GSHP system closure plan in the event of the discontinuation of the use of the geothermal system." Abandonment: "If the GSHP system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner(s) shall remove the abandoned system at their expense after a demolition permit has been obtained..." Further, "The heat pump and any external mechanical equipment shall be removed." "All abandoned wells shall be filled and sealed according to the PADEP/DCNR Water Well Abandonment Guidelines." "Pipes or coils below the land surface shall be filled and capped in accordance with IGSHPA standards." | ARTICLE I, Section 508, Paragraph 1, H.5.b.2; H.6 | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Monroe | Stroud | 4208974880 | Open-loop Prohibitions |  |  | "Only closed horizontal loop or closed vertical loop GSHP systems are permitted. Open-loop GSHP systems are not permitted." | ARTICLE I, Section 508, Paragraph 1, H.1.a | 2021 | https://ecode360.com/ST3854/laws/LF2270793.pdf
Pennsylvania | Montgomery | Collegeville | 4209115192 | Definition: Well |  |  | "GEOTHERMAL WELL. A well(s) installed for the purpose of heating and/or cooling the dwelling or building on a property." | § 680-210 Definitions | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Definition: Geothermal Heat Pump |  |  | "CLOSED-LOOP GEOTHERMAL HEATING/COOLING SYSTEM. A closed or sealed system designed to heat and/or cool a dwelling or building which circulates water, heat transfer fluid or refrigerant through underground loops. The loops are installed either in closed-loop boreholes or horizontally in trenches or ponds and exchange heat with the ground." "GEOTHERMAL HEATING/COOLING SYSTEM. A mechanism for heat exchange which consists of the following basic elements: underground loops of piping, heat transfer fluid, a heat pump, and air distribution system." "OPEN-LOOP GEOTHERMAL HEATING/COOLING SYSTEM. An open or unsealed system designed to heat and/or cool a building which uses a ground water supply well to extract groundwater which is passed through a heat pump and into any discharge well or other area." | § 680-210 Definitions | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Setback - Right of Way | 10 | feet | Under "Isolation distances," the minimum setback from "Property lines and all rights-of-way and easements" is "10" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Setback - Property Lines | 10 | feet | Under "Isolation distances," the minimum setback from "Property lines and all rights-of-way and easements" is "10" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Setback - Wastewater | 50 | feet | Under "Isolation distances," closed-loop geothermal boreholes must be at least "50" feet from "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits" and at least "25" feet from "Septic tanks, aerobic tanks, sewage pump tanks and holding tanks." | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Setback - Fuel (above ground) | 300 | feet | Under "Isolation distances," the minimum setback from "Surface or subsurface containers or tanks of greater than 1,000 gal. used for storage of materials that cannot be properly disposed of by passage through the soil. This includes, but is not limited to, gasoline and all other petroleum products" is "300" feet; the table also shows "(If borehole is grouted and cased inside and out) (150)." The table further requires "30" feet from "Surface or subsurface containers or tanks of less than 1,000 gal.... For example, the type of tank used in homes for storing oil for heating purposes." | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Setback - Water Bodies | 10 | feet | Under "Isolation distances," closed-loop geothermal boreholes must observe minimum setbacks from "Delineated wetlands, floodplains, lakes, ponds, or other surface waters" of "10" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Setback - Hazardous Materials/Fertilizers | 5 | feet | Under "Isolation distances," the minimum setback from a "Preparation area or storage area of hazardous spray materials, fertilizers, chemicals, or salt piles" is "5" feet. | § 680-213B | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Permit |  |  | "Geothermal heating/cooling system equipment shall be permitted as an accessory use in any zoning district upon receipt of a permit from the Zoning Officer." "No person shall install, construct, drill, or excavate to facilitate the construction or installation of a geothermal heating/cooling system for use as a heating and/or cooling system for a structure, residential or nonresidential within the Borough without first obtaining a geothermal heating/cooling system permit from the Borough. No person shall drill or excavate to repair or modify or to facilitate the repair or modification of a ground source heat pump system in the Borough without first obtaining a ground source heat pump permit." | § 680-213A | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Inspection |  |  | "All applicants for ground source heat pump permits shall pay all fees for application and inspection as established by resolution by Borough Council, from time to time." | § 680-213A(2) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Certification |  |  | "The pipe loop is to be installed by a geothermal well installation contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." The contractor must also provide before activation "Written documentation of the geothermal heating/cooling system testing and certification." | § 680-213C(10) and § 680-213C(12)(d) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Decommissioning |  |  | "In the event of the proposed discontinuance of the geothermal heating/cooling system, a system closure plan will be prepared and submitted to the Borough for its removal." "If a geothermal heating/cooling system is inoperable for six consecutive months, the owner shall be notified. Within three months of receiving the notice, the owner shall either restore the system to operating condition or remove it, at the owner's expense. The heat transfer fluid must be removed by a displacement with grout. The top of the borehole must be uncovered and capped with grout." | § 680-213C(13)(e) and (f) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Open-loop Prohibitions |  |  | "Closed-loop systems. All geothermal heating/cooling systems shall be closed-loop systems. No open-loop systems shall be permitted." | § 680-213C(1) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | Collegeville | 4209115192 | Other Prohibitions/Regulations |  |  | "All geothermal heating/cooling systems in areas underlain by carbonate bedrock must be vertical loop systems." | § 680-213C(7) | 2011 | https://ecode360.com/32861290
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Roads | 10 | feet | The table requires a setback from "Dedicated public right-of-way and property lines" of "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Right of Way | 15 | feet | The table requires a setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "15 feet or outside easement." It also lists "Dedicated public right-of-way" at "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Property Lines | 10 | feet | The table requires a setback from "Dedicated public right-of-way and property lines" of "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Building Foundation | 10 | feet | The table requires a setback from "Building foundations (except buildings enclosing water wells and/or water well pumps)" of "10 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Wastewater | 100 | feet | The table lists wastewater-related setbacks including: "Community spray irrigation site sewage sludge and septage disposal site" at "50 feet" closed-loop and "100 feet" standing-column; "Subsurface sewage absorption areas, elevated sand mounds, cesspools, sewage seepage pits, single-family spray irrigation system, etc." at "50 feet" closed-loop and "100 feet" standing-column; and "Septic tanks, aerobic tanks, sewage pump tanks, holding tanks" at "25 feet" closed-loop and "50 feet" standing-column. | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Animal Enclosures | 200 | feet | The table requires setbacks from "Farm silos, barnyards, manure pits or tanks or other storage areas of animal manure" of "100 feet" for closed-loop systems and "200 feet" for standing-column well systems. | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Water Lines | 15 | feet | The table requires a setback from "Existing water and forced sewer buried utilities and/or utility trenches" of "15 feet or outside easement." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Sewer Lines | 50 | feet | The table sets isolation distances from "Gravity sewer lines and drains carrying domestic sewage or industrial waste" at "25 feet" closed-loop and "50 feet" standing-column. It also lists "Gravity sewer lines and drains using cast-iron pipe with watertight lead-caulked or neoprene-gasketed joints, or Schedule 40 PVC pipe with solvent-welded joints" at "5 feet" and "10 feet," and "Sewer lines and drains carrying domestic sewage or industrial waste under pressure" at "25 feet" and "50 feet." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Water Bodies | 25 | feet | The isolation-distance table requires separation from "Delineated wetlands, floodplains, lakes, ponds, streams, or other surface waters" of "12.5 feet" for "Closed-Loop Systems" and "25 feet" for "Standing-Column Well Systems." Footnote: "These amounts are the minimum isolation distances required by Montgomery County Health Department (MCHD) Code § 17-7." | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Setback - Hazardous Materials/Fertilizers | 300 | feet | The table requires setbacks from "Commercial preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles" of "150 feet" for closed-loop systems and "300 feet" for standing-column well systems. | § 95-165 Renewable energy systems, C.(3)(b) Isolation distances |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Permit |  |  | "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." "Prior to constructing a new geothermal well or modifying an existing geothermal well, the property owner shall file all appropriate applications with the municipality, county, or other regulating agency and pay all applicable fees." "The Borough shall approve or deny the application within 15 working days of receipt of a complete application and the appropriate fee." | § 95-165 Renewable energy systems, C.(1) Permitting |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Inspection |  |  | "The Borough shall field verify the location of the proposed geothermal well(s) and all applicable isolation distances." "Abandonment procedures may be subject to MCHD inspection." | § 95-165 Renewable energy systems, C.(1)(d) and C.(5)(d) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Licensed Driller |  |  | "All wells shall be constructed by a Pennsylvania Department of Conservation and Natural Resources (DCNR) licensed water well driller or an International Ground Source Heat Pump Association (IGSHPA) accredited geothermal system installer." | § 95-165 Renewable energy systems, C.(2)(b) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Certification |  |  | "All wells shall be constructed by a Pennsylvania Department of Conservation and Natural Resources (DCNR) licensed water well driller or an International Ground Source Heat Pump Association (IGSHPA) accredited geothermal system installer." "The geothermal system shall be designed and installed in conformance with IGSHPA Heat Pump Systems Design and Installation Standards..." | § 95-165 Renewable energy systems, C.(2)(b) and C.(4)(a) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Decommissioning |  |  | "All abandoned wells shall be filled and sealed according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment Form shall be submitted to MCHD within 30 days of abandonment." "Any and all heat transfer fluid shall be removed by displacement with grout. The top of the borehole shall be uncovered and capped with grout in a manner acceptable to the Borough and MCHD." "If the applicant/homeowner chooses not to abandon the well, a nonabandonment declaration shall be signed and submitted to MCHD within 30 days." | § 95-165 Renewable energy systems, C.(5) Decommissioning requirements |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Open-loop Prohibitions |  |  | "Only closed-loop geothermal well systems or standing-column geothermal well systems are allowed." "Open-loop geothermal well systems, except for standing-column geothermal well systems, are prohibited. Separate supply and reinjection wells are prohibited." | § 95-165 Renewable energy systems, C.(2)(c)-(d) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | East Greenville | 4209121200 | Other Prohibitions/Regulations |  |  | "Separate supply and reinjection wells are prohibited." | § 95-165 Renewable energy systems, C.(2)(d) |  | https://ecode360.com/40872574
Pennsylvania | Montgomery | Lower Frederick | 4209144912 | Permit |  |  | The fee schedule expressly includes geothermal permits: "Building, Plumbing, Electrical and Mechanical Permits" with a "Zoning permit (when building, plumbing, electrical and/or mechanical permits are needed) $50.00"; "MECHANICAL PERMIT FEES: a. Residential* $100.00; b. Non-Residential* $150.00"; and under zoning permits, "i. Wind turbine, solar panel, geo-thermal installations $300.00." | 1. APPLICATION/PLAN REVIEW FEES / 1. MECHANICAL PERMIT FEES / 8. ZONING PERMIT FEES | 2023 | https://lowerfrederick.org/wp-content/uploads/2023/04/2023-Fee-Schedule_adopted-2023.4.04.pdf
Pennsylvania | Montgomery | Lower Frederick | 4209144912 | Inspection |  |  | The ordinance imposes inspection-related requirements/fees for geothermal installations through general permit administration: "Re-inspections (will be assessed on a per inspection basis) $75.00" appears under building, plumbing, electrical, mechanical, and zoning fees; mechanical fees also state "*Additional inspections based on plan review at a cost of $75.00 per inspection"; and the failure-to-comply section refers to "any required permit(s) or inspections" and allows the Township to require "approved proof of compliance, such as soil compaction testing, electrical certifications, compressed air testing of pipes, or other similar testing deemed necessary and deemed acceptable to the Township." | 1. APPLICATION/PLAN REVIEW FEES / 8. ZONING PERMIT FEES / 24. FAILURE TO COMPLY FEES | 2023 | https://lowerfrederick.org/wp-content/uploads/2023/04/2023-Fee-Schedule_adopted-2023.4.04.pdf
Pennsylvania | Montgomery | Lower Moreland | 4209145008 | Permit |  |  | "The applicant shall demonstrate compliance with all applicable regulations of Chapter 17 of the Montgomery County Public Health Code relating to Individual Water Supply, Irrigation Well, and Geothermal Well System Regulations." | ARTICLE 5(b) Geothermal Wells | 2020 | https://www.lowermoreland.org/UserFiles/Servers/Server_15465051/File/Solar%20Panels%20Requirements.pdf
Pennsylvania | Montgomery | Lower Moreland | 4209145008 | Open-loop Prohibitions |  |  | "Open loop geothermal well systems, except for standing column well systems, shall be prohibited." | ARTICLE 5(b)[3] | 2020 | https://www.lowermoreland.org/UserFiles/Servers/Server_15465051/File/Solar%20Panels%20Requirements.pdf
Pennsylvania | Montgomery | Lower Moreland | 4209145008 | Other Prohibitions/Regulations |  |  | "Separate supply and reinjection wells shall be prohibited." | ARTICLE 5(b)[3] | 2020 | https://www.lowermoreland.org/UserFiles/Servers/Server_15465051/File/Solar%20Panels%20Requirements.pdf
Pennsylvania | Montgomery | Lower Salford | 4209145096 | Permit |  |  | The fee schedule lists a specific geothermal permit category under zoning: "Well Permit ... (2) Geothermal Well $325.00 (Each)." It also states generally for this section: "All Fees referenced within this section shall be doubled if the project is started without the applicable Permits and/or Approvals." | A. BUILDING AND ZONING PERMITS, 6. ZONING, (e) Well Permit | 2025 | https://lowersalfordtownship.org/media/2466/01-january-6-2025-reorganization-packet.pdf
Pennsylvania | Montgomery | Narberth | 4209152664 | Permit |  |  | "No building shall be constructed or altered in the Borough nor the use of any building changed nor vacant land occupied until the Zoning Officer has determined plans to be in conformity with the provisions of this chapter." Also, "The Zoning Officer shall issue no permit unless it conforms to all applicable ordinances, statutes and regulations." | § 500-803 Permits | 2023 | https://ecode360.com/34355883
Pennsylvania | Montgomery | Narberth | 4209152664 | Inspection |  |  | "No permit shall be considered as complete or permanently effective until the Zoning Officer has noted on the permit that the work has been inspected and approved as being in conformity with the provisions of this chapter." | § 500-803 Permits | 2023 | https://ecode360.com/34355883
Pennsylvania | Montgomery | Trappe | 4209177304 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM - An energy system that uses a heat pump to extract heat from the earth in heating mode and/or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, an earth-source heat pump system, and a GeoExchange system." | § 340-10 Terminology | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Right of Way | 10 | feet | Under "Minimum Setbacks": "Property lines and right-of-way lines: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Property Lines | 10 | feet | Under "Minimum Setbacks": "Property lines and right-of-way lines: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Building Foundation | 10 | feet | Under "Minimum Setbacks": "Building foundations: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Wastewater | 25 | feet | Under "Minimum Setbacks": "Subsurface sewage disposal or storage systems: 25'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Water Lines | 15 | feet | Under "Minimum Setbacks": "Domestic water lines or sanitary force mains: 15'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Sewer Lines | 10 | feet | Under "Minimum Setbacks": "Gravity sanitary sewer lines: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Water Bodies | 10 | feet | Under "Minimum Setbacks": "Delineated wetlands, floodplains, surface waters: 10'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Setback - Hazardous Materials/Fertilizers | 300 | feet | Under "Minimum Setbacks": "Hazardous materials storage: 300'." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Permit |  |  | Under "Permitting": "It shall be unlawful to install a new geothermal well or modify an existing geothermal well without a valid permit." "Prior to constructing a new geothermal well or modifying an existing geothermal well, the property owner shall file all appropriate applications with the Borough, county, or other regulating agency and pay all applicable fees." "If geothermal well construction is not completed within three (3) years of the permit issuance date, the approval to construct shall expire." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Licensed Driller |  |  | "Only an PA DCNR-licensed well driller or a geothermal system installer accredited by the International Ground Source Heat Pump Association (IGSHPA) shall conduct the drilling of a geothermal well. The well drilling rig must also be approved by PA DCNR." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Certification |  |  | "Only an PA DCNR-licensed well driller or a geothermal system installer accredited by the International Ground Source Heat Pump Association (IGSHPA) shall conduct the drilling of a geothermal well." Also, "The pipe loop is to be installed by a geothermal well installation contractor who is certified in the proper method of heat fusion specified by the pipe manufacturer." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Decommissioning |  |  | "The geothermal system must be installed, maintained, and decommissioned in accordance with IGSHPA Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards, latest version." Also under "Abandonment": "A geothermal system shall be abandoned in a manner acceptable to the Borough and shall comply with the laws, rules, and regulations applicable to the abandonment of water wells." "Any and all heat transfer fluid must be removed by displacement with grout in a manner acceptable to the Borough." "The top of the borehole must be uncovered and capped with grout in a manner acceptable to the Borough." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Trappe | 4209177304 | Closed-loop Prohibitions |  |  | "Closed loop systems are prohibited." | § 340-216. Geothermal System | 2022 | https://trappeborough.com/wp-content/uploads/2022/08/Zoning-Ordinance.pdf
Pennsylvania | Montgomery | Upper Dublin | 4209179008 | Definition: Well |  |  | "GEOTHERMAL BOREHOLE or BOREHOLE — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 255-260. Definitions. | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | 4209179008 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An alternative energy system serving as a mechanism for heat exchange that uses the Earth’s thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings ... Geothermal heat pumps come in two basic configurations: closed loop and open loop systems." | § 255-260. Definitions. | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | 4209179008 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than 20 feet deep." | § 255-262(B)(5) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | 4209179008 | Permit |  |  | "Open loop geothermal energy systems are prohibited with the exception of standing column well geothermal systems in which water is circulated from and back to the same borehole, in which case such open loop geothermal energy system may be permitted with conditional use approval in all zoning districts subject to demonstration by the applicant for conditional use approval that the proposed site for the standing column well geothermal system has the requisite geological and groundwater properties for the proper functioning of the system." | § 255-262(B)(2) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | 4209179008 | Decommissioning |  |  | "If a geothermal energy system remains unserviceable for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove or seal the system within six months of abandonment after a demolition permit has been obtained..." "Any aboveground mechanical equipment, wiring, piping, coils, and other components shall be removed." "Underground pipes or coils should be removed and the resulting void space filled, or if abandoned in place, underground pipes and coils shall be filled with grout to displace the heat transfer fluid. The top of any pipe, coil or boring shall be uncovered and grouted." "Heat transfer fluid shall be captured and disposed of in accordance with applicable regulations." "When a geothermal energy system is removed, any disturbed earth as a result of the removal of the system shall be restored, graded and reseeded." | § 255-262(D)(1)-(2) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | Upper Dublin | 4209179008 | Open-loop Prohibitions |  |  | "Open loop geothermal energy systems are prohibited with the exception of standing column well geothermal systems in which water is circulated from and back to the same borehole, in which case such open loop geothermal energy system may be permitted with conditional use approval..." | § 255-262(B)(2) | 2023 | https://codelibrary.amlegal.com/codes/upperdublin/latest/upperdublintwp_pa/0-0-0-29302
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Definition: Well |  |  | "Vertical Closed-Loop Borehole. A borehole which is constructed to receive heat-exchanger loop pipes and grout material. Fill material may be used below a minimum depth of 20' below grade as the subsurface conditions warrant." | SECTION ONE. Article II, § 201 - Terms Defined | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating and/ or Cooling System. A system that uses a heat pump to extract heat from the earth in heating mode and/ or reject heat into the earth in cooling mode. It is also called a geothermal heat pump system, a ground-coupled heat pump system, and earth-source heat pump system and a Geo Exchange system." Also: "Ground-Coupled Heat Pump. A geothermal heat pump that uses the earth itself as a heat source and heat sink. It is coupled to the ground by means of a closedloop heat exchanger installed horizontally or vertically underground." | SECTION ONE. Article II, § 201 - Terms Defined | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Roads | 10 | feet | Setback table: "Dedicated public right-of-way" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Right of Way | 10 | feet | Setback table: "Property lines and all rights-of-way and easements" — "10" feet. Also: "Existing water and forced sewer buried utilities and/or utility trenches" — "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench." | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Property Lines | 10 | feet | Setback table: "Property lines and all rights-of-way and easements" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Building Foundation | 10 | feet | Setback table: "Building foundations (except for buildings enclosing water wells and/or water well pumps and any other source of pollution as approved)" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Wastewater | 25 | feet | Setback table includes: "Septic tanks, aerobic tanks or holding tanks" — "25" feet; "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields" — "25" feet; "Sewage seepage pits, cesspools" — "25" feet; "Spray irrigation sites, sewage sludge and septage disposal sites" — "25" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Animal Enclosures | 25 | feet | Setback table: "Farm silos, barnyards, privies and fuel tanks" — "25" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Fuel (above ground) | 300 | feet | Setback table includes: "Farm silos, barnyards, privies and fuel tanks" — "25" feet; and "Surface or subsurface containers or tanks of greater than 1000 gallons used for storage of materials that cannot be properly disposed of by passage through soil. This includes, but is not limited to gasoline and all other petroleum products (if borehole is cased and grouted inside and out)" — "300" feet; plus "Surface or subsurface containers of tanks of 1000 gallons or less ... including ... gasoline and all other petroleum products ..." — "30" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Subsurface Drains | 10 | feet | Setback table: "Rainwater pits, ditches" — "10" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Water Lines | 15 | feet | Setback table: "Existing water and forced sewer buried utilities and/or utility trenches" — "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench." | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Sewer Lines | 15 | feet | Setback table: "Gravity sewer lines and drains carrying domestic sewage or industrial waste" — "10 or according to easement." Also: "Existing water and forced sewer buried utilities and/or utility trenches" — "Outside existing easement or, if no easement exists, no less than 15 feet from the utility or trench." | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Water Bodies | 25 | feet | Setback table: "Lakes, ponds, streams or other surface waters" — "25" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Setback - Hazardous Materials/Fertilizers | 100 | feet | Setback table: "Preparation area or storage area of hazardous spray materials, fertilizers of chemicals, salt piles" — "100" feet. | SECTION FOUR. Article IV, § 467.C - Setbacks | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Permit |  |  | "Closed-Loop geothermal systems shall be permitted as an accessory use in any zoning district, upon receipt of a permit from the zoning officer and compliance with the requirements of this ordinance." Also: "An applicant who seeks to install a closed-loop geothermal system shall submit an application for a zoning permit." | SECTION FOUR. Article IV, § 467 - Geothermal Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Decommissioning |  |  | "The geothermal heating and/or cooling system must be installed, maintained and decommissioned utilizing standards conforming to the International Ground Source Heat Pump Association (IGSHPA) Closed-Loop/Geothermal Heat Pump System Design and Installation Standards, 2010 edition..." Also: "In the event of the proposed discontinuance of the use of the ground source heat pump system or geothermal system, a system closure plan will be prepared and submitted to the Township for its approval. At a minimum, any and all heat transfer fluid must be removed by displacement with grout in a manner acceptable to the Township engineer. The top of the borehole must be uncovered and capped with grout in a manner acceptable to the Township." | SECTION FOUR. Article IV, § 467.D-F - Geothermal Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Open-loop Prohibitions |  |  | "Due to the serious potential for adverse environmental impact, any open-loop geothermal systems ... are prohibited in West Pottsgrove Township." | SECTION FOUR. Article IV, § 467.B - Prohibited Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Montgomery | West Pottsgrove | 4209183912 | Other Prohibitions/Regulations |  |  | "Due to the serious potential for adverse environmental impact, any ... direct exchange (DX) geothermal systems are prohibited in West Pottsgrove Township." | SECTION FOUR. Article IV, § 467.B - Prohibited Systems | 2011 | https://ecode360.com/WE6592/laws/LF2633737.pdf
Pennsylvania | Northampton | East Allen | 4209520736 | Permit |  |  | "Monitoring, agricultural, and geothermal wells not used to supply water for human consumption do not require permits under this section." | § 250-39.3 Regulations governing the construction and closure of individual water supply wells | 2016 | https://ecode360.com/12791288
Pennsylvania | Northampton | Hanover | 4209532432 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (sometimes referred to as 'GSHP') Any system of mechanical and electrical facilities designed for the purpose of withdrawing heat from, or discharge heat to, the ground, groundwater, or surface waters." | § 90-3 Definitions | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Setback - Right of Way | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines, rights-of-way." | § 90-5B(3) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Setback - Property Lines | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) Twenty-five feet from property lines, rights-of-way." | § 90-5B(3) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Setback - Building Foundation | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (4) Twenty-five feet from existing or proposed structures." | § 90-5B(4) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Setback - Wastewater | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (2) Twenty-five feet from any existing or proposed individual or community on-lot sewage disposal system, including any primary or alternate drainfield sites." | § 90-5B(2) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Setback - Private Water | 100 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (1) One hundred feet from any existing or proposed drinking water wells." | § 90-5B(1) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Minimum Well Depth | 2.5 | feet | "The depth of the tubing or heat transfer element must be at least 30 inches below the surface of the ground." | § 90-7D | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Permit |  |  | "No person shall install, construct, modify, drill, or excavate to facilitate any construction/installation and/or modification of a GSHP for use as a heating and/or cooling system for any building or structure without first obtaining from the Township a permit allowing for the construction or modification of a GSHP." Also, "A permit under the provision of this chapter shall be required prior to any person: (a) Construction or modifying a GSHP; (b) Drilling or redrilling any vertical GSHP; and (c) Decommissioning or abandoning an existing GSHP." | § 90-4 Construction permits | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Inspection |  |  | "Piping shall be flushed and pressure-tested before vertical borings are sealed or before horizontal trenches are backfilled. The Township Code Enforcement Officer or his or her designee shall observe pressure testing;" "The Township Code Enforcement Officer, or his or her designee, shall observe grouting of the vertical boreholes for the GSHP wells;" and "GSHP system installer shall contact the Township Code Enforcement Officer, or his or her designee, a minimum of 24 hours in advance to inspect grouting pond piping and to verify pressure testing." | § 90-8 Inspections | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Licensed Driller |  |  | "GSHP well drilling shall only be undertaken by a Pennsylvania licensed well driller." | § 90-6A(1) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Certification |  |  | "All joints shall be sealed by heat fusion or IGSHPA certified process;" and prior to activation, the driller and/or installer shall provide "Written documentation of the GSHP system testing and certification." | § 90-5C(2); § 90-6B(4) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Decommissioning |  |  | The ordinance requires permit application "[w]here a person proposes to construct, modify, or decommission a GSHP," and states that a permit is required prior to "(c) Decommissioning or abandoning an existing GSHP." It also requires "A system closure plan for use in the event of the discontinuance of the use of the GSHP system." | § 90-4B(1), (2); § 90-5D(2) | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Hanover | 4209532432 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed-loop systems. (1) Open-loop GSHP systems shall not be permitted." | § 90-5 GSHP system standards | 2009 | https://ecode360.com/13776108
Pennsylvania | Northampton | Lower Mount Bethel | 4209545016 | Setback - Wastewater | 20 | feet | "No portion of a geothermal energy system shall be constructed within 20 feet of a water supply well, a sewage disposal facility or a carbonate geologic feature..." | § 27-1202(D) Isolation Distances | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | 4209545016 | Setback - Public Water | 20 | feet | "No portion of a geothermal energy system shall be constructed within 20 feet of a water supply well, a sewage disposal facility or a carbonate geologic feature..." | § 27-1202(D) Isolation Distances | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | 4209545016 | Permit |  |  | "A zoning permit and building permit pursuant to the PA Uniform Construction Code, shall be required prior to installation of any geothermal energy system. Applicable manufacturer specifications and any PA Department of Environmental Protection (PA DEP) or Northampton County Health Department correspondence shall be submitted to Lower Mount Bethel Township as part of the application for any permit." | § 27-1202(B) Permitting | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | 4209545016 | Certification |  |  | "The design, installation and operation of geothermal energy systems shall be permitted in conformance with all applicable regulation under PA DEP and the PA Uniform Construction Code... and shall conform to applicable industry standards, including those of the American National Standards Institute (ANSI), the International Ground Source Heat Pump Association (IGSHPA), the American Society for Testing and Materials (ASTM), the Air Conditioning and Refrigeration Institute (ARI), or other similar certifying organizations... Such conformance shall be certified by the installer of the system on a form adopted by resolution of the Board of Supervisors from time to time." | § 27-1202(C) Design | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | 4209545016 | Decommissioning |  |  | "If the geothermal energy system enters into a state of disrepair, it shall be the responsibility of the property owner to properly maintain the geothermal energy system or to decommission the system within six months from the date the system enters such a state or immediately in any case determined to be a safety hazard." "Where the use of any geothermal energy system is abandoned, it shall be the responsibility of the property owner to evacuate (pump out) the fluid(s) in the system, to fill the borehole(s) with bentonite or an equivalent alternative acceptable to the Township, and to conform to any applicable PA DEP well abandonment guidelines within 90 days from the date the system is abandoned or immediately in any case determined to be a safety hazard." "Any earth disturbance as a result of decommissioning or removal of any geothermal energy system shall be graded and reseeded." | § 27-1202(G)-(H) Disrepair; Abandonment and Decommissioning | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Mount Bethel | 4209545016 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems shall not be permitted." | § 27-1202(A) Permitted Use | 2022 | https://ecode360.com/42185523
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (also shown as GSHP) Any system of mechanical and electrical facilities designed for the purpose of withdrawing heat from, or discharging heat to the ground, groundwater or surface waters." | § 94-3 Definitions | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Setback - Right of Way | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) 25 feet from property lines, rights-of-way." | § 94-5(B)(3) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Setback - Property Lines | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (3) 25 feet from property lines, rights-of-way." | § 94-5(B)(3) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Setback - Building Foundation | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (4) 25 feet from existing or proposed structures." | § 94-5(B)(4) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Setback - Wastewater | 25 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (2) 25 feet from any existing or proposed individual or community on-lot sewage disposal system including any primary or alternate drainfield sites." | § 94-5(B)(2) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Setback - Private Water | 100 | feet | "The perimeter of the GSHP subsurface loops, vertical or horizontal, shall meet the following minimum isolation requirements: (1) 100 feet from any existing or proposed drinking water wells." | § 94-5(B)(1) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Minimum Well Depth | 2.5 | feet | For horizontal closed-loop systems, "The depth of the tubing or heat transfer element must be at least 30 inches below the surface of the ground." | § 94-7(D) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Permit |  |  | "No person shall install, construct, modify, drill, or excavate to facilitate the construction/installation and modification of a GSHP for use as a heating and/or cooling system for any building or structure without first obtaining from the Township a permit allowing for the construction of a GSHP." Also, "A permit under the provision of this chapter shall be required prior to any person: (a) Constructing or modifying a GSHP. (b) Drilling or redrilling any vertical GSHP. (c) Decommissioning or abandoning an existing GSHP." | § 94-4 Construction permits | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Inspection |  |  | "Piping shall be flushed and pressure tested before vertical borings are sealed or before horizontal trenches are backfilled. The Township Code Enforcement Officer or his or her designee shall observe pressure testing." Also, "The Township Code Engineer, or his or her designee, shall observe grouting of the vertical boreholes for the GSHP wells." And, "GSHP system installer shall contact the Township Engineer, or his or her designee, a minimum of 24 hours in advance to inspect grouting pond piping and to verify pressure testing." | § 94-8 Inspections | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Licensed Driller |  |  | "GSHP well drilling shall only be undertaken by a Pennsylvania licensed well driller." | § 94-6(A)(1) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Certification |  |  | "GSHP systems shall be designed and constructed in accordance with the International Ground Source Heat Pump Association (hereafter IGSHPA) Installation Standards..."; "All joints shall be sealed by heat fusion or IGSHPA certified process"; and prior to activation, the driller and/or installer must provide "Written documentation of the GSHP system testing and certification." | § 94-5(A)(2); § 94-5(C)(1); § 94-6(B)(4) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Decommissioning |  |  | The permit application applies where a person proposes to "construct, modify, or decommission a GSHP," and "A permit under the provision of this chapter shall be required prior to any person: ... (c) Decommissioning or abandoning an existing GSHP." The ordinance also requires "A system closure plan for use in the event of the discontinuance of the use of the GSHP system." | § 94-4(B)(1); § 94-4(B)(2)(c); § 94-5(D)(2) | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Open-loop Prohibitions |  |  | "All ground source heat pump systems shall be closed-loop systems. Open-loop GSHP systems shall not be permitted." | § 94-5 Standards for GSHP systems | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Lower Saucon | 4209545104 | Other Prohibitions/Regulations |  |  | "GSHP systems to be designed and constructed in the Township's Watershed Protection or Carbonate Geology Districts shall be horizontal closed-loop systems. Outside the Watershed Protection or Carbonate Geology Districts, either vertical or horizontal closed-loop GSHP systems may be used." | § 94-5 Standards for GSHP systems | 2021 | https://ecode360.com/10518039
Pennsylvania | Northampton | Williams | 4209585256 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL SYSTEM (CLOSED LOOP) Any heating and/or cooling system that utilizes the earth's thermal energy to heat and/or cool a building through the use of a series of underground pipes in which the same liquid is circulated through piping in a continuous configuration such that no new liquid is introduced to the system or used liquid discharged from the system." "GEOTHERMAL SYSTEMS (OPEN LOOP) Any heating and/or cooling system that utilizes the earth's thermal energy to heat and/or cool a building through the use of a series of underground pipes in which the same liquid is circulated through piping in a continuous configuration after being drawn from a source and is then discharged to that source or an alternate location." | § 27-201 Definitions; Terms Defined | 2025 | https://ecode360.com/31570532
Pennsylvania | Perry | Marysville | 4209947968 | Definition: Well |  |  | "GEOTHERMAL WELL - a well installed for the purpose of heating or cooling a facility. These shall include wells drilled as closed-loop geothermal boreholes." | § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | 4209947968 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP EQUIPMENT - any components of a heating or cooling system installed in a well or borehole. This shall include pumps for supply wells used solely for heating or cooling and pipe loops for use in closed-loop applications using a heat transfer fluid or direct exchange systems." | § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | 4209947968 | Permit |  |  | "The installation, repair, or alteration of any well... requires a permit prior to the beginning of the installation... Geothermal wells are required to be permitted." § 23-101 also states the Chapter is intended "to require a permit for the construction of a well... and the drilling of boreholes used for the installation of ground source heat pump equipment." | § 23-301. General. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | 4209947968 | Licensed Driller |  |  | § 23-301(2): "All private or public water supplies and geothermal wells, monitoring wells and test wells constructed pursuant to this Chapter shall be constructed or altered by a duly licensed well contractor, geothermal well installation contractor, or pump installation contractor who is licensed as set forth in this Chapter." § 23-201 defines "GEOTHERMAL WELL INSTALLATION CONTRACTOR" as an individual "responsible for the drilling of boreholes used for the purpose of geothermal heating or cooling of a facility" and states that this individual "is licensed as a well contractor and/or a geothermal well installation contractor." | § 23-301. General.; § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Perry | Marysville | 4209947968 | Decommissioning |  |  | "BACKFILLING - the process of sealing a borehole for the purpose of decommissioning a well or enclosing the closed-loop of a ground source heat pump equipment system." Also, "DECOMMISSIONING - the process of properly filling and sealing a well, in accordance with this Chapter." | § 23-201. Definitions. | 2015 | https://codelibrary.amlegal.com/codes/marysville/latest/marysvl_pa/0-0-0-5659
Pennsylvania | Washington | Charleroi | 4212512704 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 338-202 Definitions |  | https://ecode360.com/32070838
Pennsylvania | Washington | Charleroi | 4212512704 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 338-202 Definitions |  | https://ecode360.com/32070838
Pennsylvania | Washington | Charleroi | 4212512704 | Minimum Well Depth | 20 | feet | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM ... A horizontal closed loop system shall be no more than 20 feet deep." | § 338-202 Definitions |  | https://ecode360.com/32070838
Pennsylvania | Westmoreland | Washington | 4212981336 | Inspection |  |  | Section 403(D): "The filing of an application for either preliminary or final approval shall constitute authorization for the Washington Township Board of Supervisors, Planning Commission, Municipal Authority of Washington Township, Sewage Enforcement Officer, Solicitor and Engineer or their agents or representatives as they may designate to make such on-site inspections, before, during and after construction, as may be required to effectively administer this Ordinance." Section 407(C)-(D): "Inspections of Improvements shall be made by the Township Engineer or his assigned agent." The contractor "shall contact the Township engineer before backfilling any storm sewer, retaining wall foundation, culvert, inlet or manhole; before spreading sub-base or applying base course to any street, or before covering any other structures that are part of the Improvements included under the bond. The engineer shall inspect the work... The engineer shall reinspect the work..." Section 407(F): after completion, the Township engineer must "make a final inspection of all Improvements covered by the bond." | Section 403 — Application Procedures for Development Other Than Minor Subdivisions; Section 407 — Construction of Improvements | 2017 | https://www.washingtontownship.com/_files/ugd/241b02_2a8ec24dd39b46e089251cce31eeabcc.pdf
Pennsylvania | Wyoming | Falls | 4213125128 | Definition: Geothermal Heat Pump |  |  | "Ground Source Heat Pump -Any geothermal, earth-coupled, geo-exchange, water-coupled, groundwater, ground-coupled, closed-loop, coiled, open, or water source heat pump system used for heating and/or cooling which utilizes groundwater extracted from a well." | §707.12 Definitions | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | Wyoming | Falls | 4213125128 | Setback - Wastewater | 100 | feet | "Horizontal closed loop ground source heat pumps must be a minimum of twenty-five (25) feet from any existing or permitted on-lot sewage disposal system. Vertical closed loop ground source heat pumps must be a minimum of one hundred (100) feet from any existing or permitted on-lot sewage disposal system, unless the entire borehole around the annulus of the loop is grouted with bentonite slurry." | §707.8(I)(2)-(3) Ground Source Heat Pumps | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | Wyoming | Falls | 4213125128 | Permit |  |  | "Applicants for open loop ground source heat pumps that discharge to the surface must either obtain a National Pollutant Discharge Elimination System (NPDES) permit from the Pennsylvania Department of Environmental Protection, or demonstrate that such permit is not required." | §707.8(I)(6) Ground Source Heat Pumps | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | Wyoming | Falls | 4213125128 | Other Prohibitions/Regulations |  |  | "Closed loop ground source heat pumps that treat extracted water in any way, or involve circulation of toxic refrigerants below the surface, are prohibited. Water treatment associated with open loop ground source heat pumps is prohibited." | §707.8(I)(4)-(5) Ground Source Heat Pumps | 2016 | https://www.fallspa.gov/wp-content/uploads/2021/11/Falls-Township-Wyoming-County-Zoning-Ordinance-1-4-16.pdf
Pennsylvania | York | Carroll | 4213311432 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL HEAT PUMP SYSTEMS. A geothermal heat pump (GHP) or ground source heat pump (GSHP) is a central heating and/or cooling system that transfers heat to or from the ground." | § 450-112 Definitions | 2023 | https://ecode360.com/37602037
Pennsylvania | York | Fawn | 4213325408 | Definition: Geothermal |  |  | "GEOTHERMAL HEAT -Heat derived from geothermal resources, or heat derived from groundwater." "GEOTHERMAL FLUID -Any fluid transporting or capable of transporting geothermal heat." | Section 2. Definitions | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Definition: Geothermal Heat Pump |  |  | "CLOSED LOOP SYSTEMS -A geothermal heat pump system which relies on the contained circulation of geothermal fluids through an underground loop of pipes. The loops act as a subsurface heat exchanger, which transports the heat to or from the ground." "GEOTHERMAL HEATING SYSTEM -A geothermal heat pump system which relies on the contained circulation of geothermal fluids to obtain and to utilize geothermal resources." "OPEN LOOP SYSTEMS -A geothermal heat pump system which relies on the circulation of groundwater from a supply well, spring or surface water." | Section 2. Definitions | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Driveways | 10 | feet | Section 13 table: "Driveways — 10 ft." Section 18 table: "Driveways — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Right of Way | 10 | feet | Section 13 table: "Property lines and right-of-way easements — 10 ft." Section 18 table: "Property lines and right-of-way easements — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Property Lines | 10 | feet | Section 13 table: "Property lines and right-of-way easements — 10 ft." Section 18 table: "Property lines and right-of-way easements — 10 ft." Section 23 exemption applies only to agricultural adaptations and states the installation is "a minimum of 200 feet from property boundaries." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements; Section 23. Exemption | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Building Foundation | 20 | feet | Section 13 table for wells: "Building foundations — 20 ft." Section 18 table for horizontal systems: "Building foundations — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Wastewater | 50 | feet | Section 13 table: "Septic tanks - active — 50 ft." and "Septic drain fields, seepage pits, privies, or cesspools - 50 ft." Section 18 table: "Septic tanks - active — 10 ft." and "Septic drain fields, seepage pits, privies, or cesspools - 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Sewer Lines | 25 | feet | Section 13 table: "On-lot sewage system line — 25 ft." Section 18 table: "On-lot sewage system line — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Pools | 25 | feet | Section 13 table: "Swimming pools — 25 ft." Section 18 table: "Swimming pools — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Setback - Water Bodies | 25 | feet | Section 13 table: "Lakes, ponds, or surface water — 25 ft." and "Storm water retention/detention ponds berm (measured from top to bottom) — 25 ft." Section 18 table: "Lakes, ponds, or surface water — 20 ft." and "Storm water retention/detention ponds berm (measured from top to bottom) — 10 ft." | Section 13. Well Siting Requirements; Section 18. Closed Loop, Horizontal Geothermal Siting Requirements | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Maximum Well Depth | 800 | feet | "The depth of any well shall not exceed 800 ft." | Section 12. Well Construction Requirements, a. Construction by Licensed Driller | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Permit |  |  | Section 7: "Any persons desiring to construct, install, or alter a Geothermal Heating System within the Township shall first apply for a Geothermal Heating System permit at the Township Office... No Person shall commence construction or alteration of a Geothermal Heating System prior to the Owner of a proposed Geothermal Heating System receiving a permit." Section 11: "No geothermal well shall be installed without receiving a well permit... Before any drilling or site preparation begins, the well driller shall apply for a Well Permit from the Township Well Officer." Section 17: "Prior to any on lot excavation or installation of the horizontal closed loop system a permit for same shall be secured from the permit officer." | Section 7, Application for Geothermal Heating System Permit; Section 11. Geothermal Wells for Closed Loop, Vertical Systems — Requirements/ Procedures; Section 17. Closed Loop, Horizontal Installation — Requirements/Procedures | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Inspection |  |  | Section 15: "The following inspections shall be required by the Township: a. Site inspection before any work is done, showing the location of proposed work. b. Inspection of grouting. c. Inspection of the completely installed system before operations commence and upon commencement of operations. d. Inspection if geothermal system or well is abandoned." Section 11(b): "During the well drilling and construction process, the Township Well Officer may enter the premises to determine if the well is being installed according to the requirements of the Township." Section 20: Township officials may enter property "for purposes of inspecting geothermal facilities, or monitoring the operational characteristics of such facilities." | Section 15. Inspection; Section 11. Geothermal Wells for Closed Loop, Vertical Systems — Requirements/ Procedures; Section 20. Township Monitoring of Geothermal Facilities | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Licensed Driller |  |  | Section 12(a)(1): "All geothermal wells in the Township shall be constructed in accordance with PA Act 610 (Water Well Drillers License Act)." Section 16: "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller..." | Section 12. Well Construction Requirements, a. Construction by Licensed Driller; Section 16. Well Abandonment | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Certification |  |  | Section 12(a)(1): "All geothermal wells in the Township shall be constructed in accordance with PA Act 610 (Water Well Drillers License Act)." Section 16: "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines." | Section 12. Well Construction Requirements, a. Construction by Licensed Driller; Section 16. Well Abandonment | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Decommissioning |  |  | "All abandoned wells must be filled and sealed by a PADCNR licensed water well driller according to the PADEP/DCNR Water Well Abandonment Guidelines. A copy of the PADEP/DCNR Water Well Abandonment form shall be submitted to the Township within thirty (30) days of abandonment. Abandonment procedures shall be subject to Township inspection and shall follow PADEP guidelines." | Section 16. Well Abandonment | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Fawn | 4213325408 | Other Prohibitions/Regulations |  |  | "No Geothermal Heating System constructed or altered after the effective date of this Ordinance shall be operated or altered in such a manner as to cause Geothermal Fluids or Thermal Groundwater to be discharged onto the surface of the ground or into any public ditch or drainage facility." | Section 19. Surface Discharges | 2015 | https://www.fawntwp.org/wp-content/uploads/2018/05/FawnTwpGeothermalWellOrdinance.pdf
Pennsylvania | York | Hellam | 4213333728 | Setback - Right of Way | 20 | feet | The isolation distance table requires 20 feet from "Dedicated public right-of-way." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Property Lines | 10 | feet | "Unless otherwise specified, underground geothermal systems shall be located a minimum distance of 10 feet from any property line." | § 490-25M(3)(b) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Wastewater | 100 | feet | The isolation distance table requires 50 feet from "Septic tanks, aerobic tanks or holding tanks"; 100 feet from "Subsurface sewage disposal systems, elevated sand mounds, other sewage disposal fields"; 100 feet from "Sewage seepage pits, cesspools"; and 25 feet from "Spray irrigation sites, sewage sludge and septage disposal sites." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Animal Enclosures | 50 | feet | The isolation distance table requires 50 feet from "Farm silos, barnyards, privies and fuel tanks." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Fuel (above ground) | 50 | feet | The isolation distance table requires 50 feet from "Farm silos, barnyards, privies and fuel tanks." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Water Lines | 50 | feet | The isolation distance table requires geothermal wells/boreholes to be "Outside existing easement or, if no easement exists, no less than 50 feet from the utility or trench center line" for "Existing water and forced sewer buried utilities and/or utility trenches." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Sewer Lines | 50 | feet | The isolation distance table requires "50 or according to easement" from "Gravity sewer lines and drains carrying domestic sewage or industrial waste." It also requires geothermal wells/boreholes to be "Outside existing easement or, if no easement exists, no less than 50 feet from the utility or trench center line" for "Existing water and forced sewer buried utilities and/or utility trenches." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Water Bodies | 50 | feet | The isolation distance table requires 50 feet from "Lakes, ponds, streams or other surface waters." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Setback - Hazardous Materials/Fertilizers | 100 | feet | The isolation distance table requires 100 feet from "Preparation area or storage area of hazardous spray materials, fertilizers or chemicals, salt piles." | § 490-25M(3)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Minimum Well Depth | 50 | feet | "Geothermal heating and/or cooling system vertical heat exchange boreholes containing loop pipes may be filled with approved grout or bridging or fill materials from their total depth up to a minimum depth of 50 feet below grade. These vertical heat exchange boreholes must be filled with only approved grout from a minimum depth of 50 feet below grade up to the ground surface." | § 490-25M(5)(a) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Permit |  |  | "The construction documents submitted with the application for a permit shall be accompanied by a site plan..." | § 490-25M(4) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Inspection |  |  | "All materials and construction practices shall conform to the requirements stated in Closed-Loop/Geothermal Heat Pump Systems Design and Installation Standards, such as, but not limited to, standards for pressure testing, heat transfer fluids, etc." | § 490-25M(5)(c) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Certification |  |  | "The installer must have at least one representative who is certified by IGSHPA." | § 490-25M(1) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Decommissioning |  |  | "If the geothermal system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The owner shall remove the abandoned system at his/her expense after a demolition permit has been obtained..." Subsection (a) requires removal of "The heat pump and any external mechanical equipment"; Subsection (b) requires below-grade pipes or coils to "be filled with grout to displace the heat transfer fluid" and the fluid to "be captured and disposed of in accordance with applicable regulations"; Subsection (c) requires reporting abandoned wells to DCNR and providing a copy to the municipality. | § 490-25M(6) | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Hellam | 4213333728 | Open-loop Prohibitions |  |  | "Open-loop geothermal energy systems and any system not meeting the definition of a closed-horizontal-loop geothermal energy system or closed-vertical-loop geothermal energy system are prohibited in the Township." | § 490-25M | 2026 | https://ecode360.com/9981277
Pennsylvania | York | Mount Wolf | 4213352056 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 211-6C Definitions | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy generating system that uses the earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 211-6D Definitions | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Definition: Geothermal Heat Pump |  |  | "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM — A mechanism for heat exchange... underground loops of piping; heat transfer fluid; a heat pump; an air distribution system..." "CLOSED VERTICAL LOOP GEOTHERMAL SYSTEM — A borehole that extends beneath the surface. Pipes are installed... The pipes are connected to the heat exchanger and heat transfer fluid is circulated through the pipes." "OPEN HORIZONTAL LOOP GEOTHERMAL SYSTEM — Water is pumped from a water well or other water source into a heat exchanger located in a surface building..." | § 211-6A-B, E Definitions | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Setback - Public Water | 200 | feet | "The return well shall be located a minimum distance of 200 feet from wells on adjacent properties." | § 211-3E(2)(e)[2] Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Maximum Well Depth | 20 | feet | "All horizontal closed loop systems shall be no more than 20 feet deep." Also repeated in § 211-6A: "A horizontal closed loop system shall be no more than 20 feet deep." | § 211-3D(2) Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." | § 211-3 Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Inspection |  |  | "Installation requirements for extraction wells shall be the same as those for potable water wells, with respect to those regulations designed to prevent aquifer contamination (grouting, etc.), or in conformance with IGSHPA standards, as determined by the Borough Engineer." | § 211-3E(1)(b) Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Certification |  |  | "Discharge of water from open loop systems into a watercourse shall require certification by a licensed professional engineer registered by the Commonwealth of Pennsylvania that the design of the watercourse is such that the watercourse can be expected to retain its capacity to meet the needs of the geothermal system over the lifetime of the system and of any other water discharges for which it is used." | § 211-3E(2)(c) Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Mount Wolf | 4213352056 | Other Prohibitions/Regulations |  |  | "Only the following types of geothermal energy systems shall be permitted: (1) Closed horizontal loop; (2) Closed vertical loop; and (3) Open horizontal loop systems relying upon injection wells or watercourses." | § 211-3B Geothermal heat pump systems | 2020 | https://ecode360.com/32418428
Pennsylvania | York | Springettsbury | 4213372992 | Definition: Well |  |  | "GEOTHERMAL BOREHOLES — A hole drilled or bored into the earth into which piping is inserted for use in a closed vertical loop geothermal system." | § 325-209 Definitions | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM — An energy-generating system that uses the Earth's thermal properties in conjunction with electricity to provide greater efficiency in the heating and cooling of buildings." | § 325-209 Definitions | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Setback - Private Water | 100 | feet | "No geothermal energy system shall be located within 100 feet of any existing drinking water wells or any planned drinking water wells." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Maximum Well Depth | 20 | feet | In the definition of "CLOSED HORIZONTAL LOOP GEOTHERMAL SYSTEM," the ordinance states: "A horizontal closed loop system shall be no more than 20 feet deep." | § 325-209 Definitions | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Permit |  |  | "No person shall install, construct, drill or excavate to facilitate the construction or installation of a geothermal energy system for use as a heating and/or cooling system for a structure without first obtaining a geothermal energy system permit from the Township. No person shall drill or excavate to repair or modify or to facilitate the repair or modification of a geothermal energy system in the Township without first obtaining a zoning permit." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Licensed Driller |  |  | "The vertical geothermal energy well (or wells) installation shall be made only by a Pennsylvania-licensed well driller." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Certification |  |  | Before activation, the driller and/or installer must provide the Township "[w]ritten documentation of the geothermal energy system testing and certification." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Decommissioning |  |  | The required written operation plan must provide that "[i]n the event of the proposed discontinuance of the use of the geothermal energy system, a system closure plan will be prepared and submitted to the Township for its approval." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Open-loop Prohibitions |  |  | "All geothermal energy systems shall be closed systems. No open loop ground-source heat pump systems shall be permitted." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
Pennsylvania | York | Springettsbury | 4213372992 | Other Prohibitions/Regulations |  |  | "All geothermal energy systems in areas underlain by carbonate bedrock must be vertical loop systems. Outside the carbonate bedrock areas, either vertical or horizontal closed loop geothermal energy system may be used..." | § 325-212 Geothermal energy system requirements | 2011 | https://ecode360.com/15178605
South Carolina | Chesterfield | Cheraw | 4513600 | Setback - Yards | 3 | feet | "Heat pumps or air conditioning units outside principal or accessory structures shall be placed no closer than three feet (3) from any side or rear property line." | 8-5.6 Heat pumps or air conditioning units outside principal or accessory structures | 2025 | https://cms8.revize.com/revize/cherawsc/Document_Center/Government/Zoning/2020%20ZO%20Updated%20to%202025.pdf
South Carolina | Florence | Florence | 4525810 | Definition: Geothermal |  |  | "Renewable energy systems include photovoltaic arrays (solar electric panels), solar water heaters, and geothermal heating and cooling systems." | Sec. 3-8.1.6 Renewable Energy Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | 4525810 | Definition: Geothermal Heat Pump |  |  | "Geothermal Heating and Cooling System means a system of pipes used to heat and cool buildings by exchanging heat with the ground. There are four types of systems: A. Vertical loop systems use pipes that are oriented vertically by insertion into a bore hole that extends deep into the ground. B. Horizontal loop systems use pipes that are oriented horizontally, installed in trenches that are typically five or more feet deep. C. Lake loop systems use pipes that extend into waterbodies, where they exchange heat with the water instead of the ground. D. Open loop systems extract groundwater and then discharge it into a drainage ditch or waterbody." | Division 7-25.2 Definitions / Geothermal Heating and Cooling System | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | 4525810 | Setback - Property Lines | 2 | feet | "Closed loop systems (horizontal loop systems and vertical loop systems) are permitted, provided that the loops are set back at least two feet from property lines and outside of utility easements." | Sec. 3-8.1.6(E) Geothermal Heating and Cooling Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | 4525810 | Permit |  |  | "Systems approved pursuant to this Section shall not generate power as a commercial enterprise." Also, "Community Geothermal Facility. A facility that serves more than an individual home or business shall be permitted in any district if a subdivision or portion of a subdivision: Has land in common ownership where certain components of the system are located; and Has a homeowners' association to maintain any off-site components." | Sec. 3-8.1.6 Renewable Energy Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | 4525810 | Open-loop Prohibitions |  |  | "Open loop systems are not permitted." | Sec. 3-8.1.6(E) Geothermal Heating and Cooling Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Florence | Florence | 4525810 | Other Prohibitions/Regulations |  |  | "Lake loop systems are permitted if the water body is entirely within the property lines of the parcel proposed for development." | Sec. 3-8.1.6(E) Geothermal Heating and Cooling Systems | 2018 | https://www.cityofflorencesc.gov/sites/default/files/uploads/Business/updated-02-11-20-original-font.pdf
South Carolina | Charleston | Mount Pleasant | 4548535 | Other Prohibitions/Regulations |  |  | § 51.115(E): "Discharge from ground water source heat pump prohibited. No discharge shall be allowed from a ground water source heat pump." | § 51.115 RESTRICTED DISCHARGES | 2016 | https://codelibrary.amlegal.com/codes/mtpleasantsc/latest/mpleasant_sc/0-0-0-114011
South Carolina |  | Sullivan's Island | 4570090 | Permit |  |  | "It shall be unlawful to erect, construct, improve, alter or repair any building, sign or other structure or any part thereof or alter any parcel of land in preparation of such erection, construction, improvement or repair without first having obtained from the Building Inspector a written permit for such erection, construction, improvement, alteration or repair, pursuant to the provisions of this subchapter." | § 150.35 REQUIRED. | 2020 | https://codelibrary.amlegal.com/codes/sullivansislandsc/latest/sullivansisland_sc/0-0-0-3258
South Dakota | Lincoln | Harrisburg | 4608327260 | Permit |  |  | "Any person who commences work on a mechanical system before obtaining the necessary permits shall be subject to a Late Application Fee..." Also, in CHAPTER 9.05 - EXISTING BUILDING CODE, 105.1 Required: "Any owner or authorized agent who intends to... install, add, alter, remove, convert, or replace any... mechanical... system, the installation of which is regulated by this code... shall first make application to the Building Official and obtain the required permit." | CHAPTER 9.06 - MECHANICAL AND FUEL GAS CODE, 106.5.1 Work commencing before permit issuance | 2020 | https://www.harrisburgsd.gov/DocumentCenter/View/212/Harrisburg-SD-Codified-Municipal-Ordinances-Updated-June-30-2020-PDF
South Dakota | Lincoln | Harrisburg | 4608327260 | Inspection |  |  | "The mechanical inspector, upon notification from the permit holder or the permit holder's agent, shall make the following inspections... 1. Underground inspection... after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place... 2. Rough-in inspection... prior to the installation of wall or ceiling membranes. 3. Final inspection shall be made upon completion of the mechanical system. Exception: Ground-source heat pump loop systems tested in accordance with Section 1208.1.1 shall be permitted to be backfilled prior to inspection." | CHAPTER 9.06 - MECHANICAL AND FUEL GAS CODE, 107.2 Required inspections and testing | 2020 | https://www.harrisburgsd.gov/DocumentCenter/View/212/Harrisburg-SD-Codified-Municipal-Ordinances-Updated-June-30-2020-PDF
South Dakota | Union | Elk Point | 4612718620 | Permit |  |  | "Any person who commences work on a mechanical system before obtaining the necessary permits shall be subject to a Late Application Fee..." and "An owner, authorized agent, or contractor who desires to erect, install, enlarge, alter, repair, remove, convert, or replace an installation regulated by this code... shall first make application to the Building Official and obtain the required permit for the work." | CHAPTER 9.05 - MECHANICAL AND FUEL GAS CODES, 106.5.1 Work commencing before permit issuance | 2022 | https://files.frontdeskgworks.com/city/1912/media/elkpointmunicipalordinances.docx
South Dakota | Union | Elk Point | 4612718620 | Inspection |  |  | "The mechanical inspector... shall make the following inspections... 1. Underground inspection... 2. Rough-in inspection... 3. Final inspection shall be made upon completion of the mechanical system. Exception: Ground-source heat pump loop systems tested in accordance with Section 1208.1.1 shall be permitted to be backfilled prior to inspection." | CHAPTER 9.05 - MECHANICAL AND FUEL GAS CODES, 107.2 Required inspections and testing | 2022 | https://files.frontdeskgworks.com/city/1912/media/elkpointmunicipalordinances.docx
Arizona | Cochise | Sierra Vista | 466820 | Permit |  |  | "Application for construction, installation, and use of alternative energy systems will follow the normal building permit process." Section 151.06.003(B) states the contemplated systems include "geothermal systems." | Section 151.06.003 Alternative Energy Systems | 2026 | https://codelibrary.amlegal.com/codes/sierravista/latest/sierravistaUDO/0-0-0-1386
Texas | Tarrant | Arlington | 4804000 | Definition: Geothermal Heat Pump |  |  | "Geoexchange System A system comprised of a central pump that transfers heat to or from the ground by passing fluid through underground coils in the ground or in body of surface water for the purpose of preconditioning air used in building heating or cooling." | 12.3.5. ACCESSORY USES AND STRUCTURES B. Alternative Energy System c. Geoexchange System | 2025 | https://www.arlingtontx.gov/files/assets/city/v/5/city-secretary/documents/city-code-of-ordinances/unified-development-code-chapter.pdf
Texas |  | Benbrook | 4807552 | Setback - Property Lines | 5 | feet | "Placement: No portion of a closed-loop system may be constructed within five feet (5') of a property line or within a dedicated easement without obtaining written permission from the City and/or all franchised utilities." | 17.84.130.C.1.b | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas |  | Benbrook | 4807552 | Permit |  |  | "Building Permit Required: A building permit must be obtained prior to the construction or installation of a closed-loop geothermal heat pump system." The ordinance also lists required application contents, including permit fee, survey and legal description, plan view layout, electrical line drawing, and standard installation drawings. | 17.84.130.C.1.c | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas |  | Benbrook | 4807552 | Decommissioning |  |  | "Abandoned: If a closed-loop geothermal heat pump system has been abandoned meaning not in operation for a period of six (6) months or is defective or is deemed to be unsafe by the Building Official, the closed-loop geothermal heat pump system shall be required to be repaired by the owner to meet federal, state and local safety standards, or be removed by the property owner within the time period allowed by the Building Official in accordance with federal, state and local regulations. If the owner fails to remove or repair the defective or abandoned closed-loop geothermal heat pump system, the City may pursue legal action to the system removed at the owner's expense." | 17.84.130.C.2.d | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas |  | Benbrook | 4807552 | Open-loop Prohibitions |  |  | "Open-loop systems shall be prohibited." | 17.84.130.C.1.a | 2013 | http://www.ci.benbrook.tx.us/AgendaCenter/ViewFile/Item/204?fileID=122
Texas | Nueces | Corpus Christi | 4817000 | Definition: Geothermal Heat Pump |  |  | "Essential domestic activity" ... "does not include ... non-closed system geothermal heating/cooling systems." | Rule 1.1 Definitions | 2025 | https://www.corpuschristitx.gov/media/k4rg0ztp/2025gmp_withappendices_final.pdf
Texas |  | Lake Worth | 4841056 | Setback - Property Lines | 5 | feet | "Placement. No portion of a closed-loop system may be constructed within five feet (5 ft.) of a property line or within a dedicated easement without obtaining written permission from the city and/or all franchised utilities." | § 14.06.021(d)(1)(B) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | 4841056 | Permit |  |  | "Building permit required. A building permit must be obtained prior to the construction or installation of a closed-loop geothermal heat pump system." The ordinance also lists required application contents, including "a survey and legal description," "a plan view layout," "electrical plan required," and "standard installation drawings of the closed loop geothermal installation." | § 14.06.021(d)(1)(C) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | 4841056 | Certification |  |  | "Any closed-loop geothermal heat pump system must be installed according to the manufacturer's recommendations and under the seal of a professional engineer registered in the State of Texas." | § 14.06.021(d)(2) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | 4841056 | Decommissioning |  |  | "Abandoned. If a closed-loop geothermal heat pump system has been abandoned meaning not in operation for a period of six (6) months or is defective or is deemed to be unsafe by the city manager and/or designee, the closed-loop geothermal heat pump system shall be required to be repaired by the owner to meet federal, state and local safety standards, or be removed by the property owner within the time period allowed by the city manager and/or designee in accordance with federal, state and local regulations. If the owner fails to remove or repair the defective or abandoned closed-loop geothermal heat pump system, the city may pursue legal action to [have] the system removed at the owner's expense." | § 14.06.021(d)(2)(D) | 2019 | https://ecode360.com/40375001
Texas |  | Lake Worth | 4841056 | Open-loop Prohibitions |  |  | "Open-loop systems shall be prohibited." | § 14.06.021(d)(1)(A) | 2019 | https://ecode360.com/40375001
Texas | Atascosa | Pleasanton | 4858280 | Permit |  |  | § 52.02.2(C): "It shall be unlawful for any person to reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled beat exchange system... without first applying for and securing a permit from the Public Works Department." § 52.04 repeats the same requirement for repair or closure work. § 52.05 adds: "Every application for a permit for the drilling, construction, repair, or plugging of a well or the construction, repair, or plugging of a well for the purpose of an earth-coupled heat exchange system, shall be considered incomplete unless all information requested by the Public Works Department application form has been provided." | § 52.02.2 PERMIT FOR NEW WELL REQUIRED; § 52.04 PERMIT FOR REPAIR OR CLOSURE OF EXISTING WELL REQUIRED; § 52.05 APPLICATION FOR PERMIT; INFORMATION REQUIRED | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | 4858280 | Inspection |  |  | § 52.06(A): "It shall be the duty of the Public Works Director to consider every permit application submitted under this chapter, to inspect the property where any well will be drilled, sunk, dug, or bored..." § 52.06(B) states: "Divisions (A)(2), (3) and (4) of this section do not apply to injection wells for the purpose of an earth-coupled heat exchange system." | § 52.06 INSPECTION BEFORE ISSUANCE OF PERMIT | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | 4858280 | Decommissioning |  |  | § 52.02.2(C): "It shall be unlawful for any person to reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled beat exchange system... without first applying for and securing a permit from the Public Works Department." § 52.04 likewise provides that no person may "reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled beat exchange system" without first securing a permit. | § 52.02.2 PERMIT FOR NEW WELL REQUIRED; § 52.04 PERMIT FOR REPAIR OR CLOSURE OF EXISTING WELL REQUIRED | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | 4858280 | Open-loop Prohibitions |  |  | § 52.02(C): "An open system, geothermal well that draws water from an aquifer and is circulated through the heat exchange system or geothermal wells which inject water into an aquifer will not be permitted within the limits of the city." | § 52.02 PROHIBITED ACTIVITIES | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas | Atascosa | Pleasanton | 4858280 | Other Prohibitions/Regulations |  |  | § 52.02(A): "It shall be unlawful for anyone to drill, maintain, or otherwise construct or have constructed... injection wells for the purpose of a earth-coupled heat exchange system, within the city or the Public Works Department service area." § 52.02(B): "To preserve the water quality of the aquifer, the construction of any bore hole, injection well for the purpose of an earth-coupled heat exchange system, or water well for the purpose of an earth-coupled heat exchange system located over the Carrizo-Wilcox Aquifer Recharge Zone and Transition Zone shall be prohibited." | § 52.02 PROHIBITED ACTIVITIES | 2023 | https://codelibrary.amlegal.com/codes/pleasanton/latest/pleasanton_tx/0-0-0-8796
Texas |  | San Antonio | 4865000 | Permit |  |  | "It shall be unlawful for anyone to drill, maintain, or otherwise construct or have constructed... injection wells for the purpose of a earth-coupled heat exchange system, within the City of San Antonio or SAWS Water Quality Division." Section 34-567(b) adds: "All drilling or construction of... injection wells for the purpose of an earth-coupled heat exchange system, shall be done in strict compliance with the terms of the well drilling permit, the SAWS Water Well Permitting Procedures, and 30 TAC, Chapter 238." Section 34-568 further states: "It shall be unlawful for any person to reconstruct, repair, correct, or plug a well or injection well for the purpose of earth-coupled heat exchange system... without first applying for and securing a permit from the SAWS Water Quality Division." | Sec. 34-567. Permit for drilling new well required. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | 4865000 | Inspection |  |  | "It shall be the duty of the SAWS Water Quality Division to consider every permit application submitted under this division, to inspect the property where any well will be drilled, sunk, dug, or bored..." Section 34-573(c) also refers to "any water well that was constructed without a permit and associated inspections." | Sec. 34-570. Inspection before issuance of permit. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | 4865000 | Decommissioning |  |  | Section 34-568 makes a permit mandatory to "plug a well or injection well for the purpose of earth-coupled heat exchange system." Section 34-574(c) states: "Every abandoned well shall be filled and plugged in accordance with all applicable TNRCC regulations and SAWS Water Well Permitting Procedures..." Section 34-573(d) authorizes SAWS to order an owner "to plug this well in such a manner as prescribed by the SAWS Board" when the well is contaminating or defective. | Sec. 34-568. Permit for repair or closure of existing well required.; Sec. 34-574. Abandoned Wells. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | 4865000 | Open-loop Prohibitions |  |  | Section 34-567(e) states: "An open system, geothermal well that draws water from an aquifer and is circulated through the heat exchange system or geothermal wells which inject water into an aquifer will not be permitted within the limits of the City of San Antonio and within SAWS Water Quality Division." | Sec. 34-567. Permit for drilling new well required. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Texas |  | San Antonio | 4865000 | Other Prohibitions/Regulations |  |  | Section 34-567(d) states: "To preserve the water quality of the aquifer, the construction of any bore hole, injection well for the purpose of an earth-coupled heat exchange system, or water well for the purpose of an earth-coupled heat exchange system located over the Edwards Aquifer Recharge Zone and Transition Zone shall be prohibited." | Sec. 34-567. Permit for drilling new well required. | 1997 | https://www.saws.org/protecting-our-environment/water-resource-compliance-protection/groundwater_protection/citycode/
Utah |  | Millcreek | 4950150 | Screening |  |  | "HVAC systems, utility meters, and overhead powerlines/utilities -shall be screened from view from a pedestrian perspective from the adjacent street." | 19.44.060 SUBDIVISION OF ATTACHED DWELLING UNITS | 2018 | https://www.millcreekut.gov/AgendaCenter/ViewFile/Item/75?fileID=485
Utah |  | Murray | 4953230 | Definition: Geothermal Heat Pump |  |  | "GROUND SOURCE HEAT PUMP (GSHP) SYSTEM: Means a central heating and/or cooling system that pumps heat to or from the ground. It uses the earth as a heat source in the winter or a heat sink in the summer. These systems reduce operational costs of heating and cooling by taking advantage of moderate ground temperatures. GSHP as used in this chapter includes, but is not limited to, any such systems commonly referred to as Geothermal Wells, Geothermal Heat Pump Wells, Geothermal Heat Pumps, Closed-loop Heating/Cooling Exchange Wells, and Heat Exchange Units." | 13.30.030: DEFINITIONS | 2021 | https://www.murray.utah.gov/DocumentCenter/View/12337
Utah |  | Murray | 4953230 | Other Prohibitions/Regulations |  |  | "The City restricts GSHP wells drilled in Source Protection Zones 1 through 4 as follows: 1. GSHP wells of any depth are prohibited in Zones 1 and 2. 2. GSHP wells less than 30' are restricted in zones 3 and 4." | 13.30.070(C) Ground Source Heat Pump wells | 2021 | https://www.murray.utah.gov/DocumentCenter/View/12337
Vermont | Windsor | Woodstock | 5002785975 | Noise Limits | 55 | dBA | 'Generators, heat pumps, and or air condition units or compressors when placed outdoors shall not require a permit if they comply with the following: ... D. Shall not exceed 55 decibels as measured 3 (three) feet from the unit.' | SECTION 533 GENERATORS/HEAT PUMPS/AC | 2020 | https://www.townofwoodstock.org/fileadmin/files/Archive/2020/10/TOWN-Zoning-Regulations-searchable-1.pdf
Vermont | Windsor | Woodstock | 5002785975 | Permit |  |  | 'Generators, heat pumps, and or air condition units or compressors when placed outdoors shall not require a permit if they comply with the following...' and 'F. An exception may be granted in special circumstances with a Conditional use Approval; G. If placed within the Design Review District, a Design Review permit is required.' | SECTION 533 GENERATORS/HEAT PUMPS/AC | 2020 | https://www.townofwoodstock.org/fileadmin/files/Archive/2020/10/TOWN-Zoning-Regulations-searchable-1.pdf
Vermont | Windsor | Woodstock | 5002785975 | Screening |  |  | 'Generators, heat pumps, and or air condition units or compressors when placed outdoors shall not require a permit if they comply with the following: ... C. Shall be screened from public view.' | SECTION 533 GENERATORS/HEAT PUMPS/AC | 2020 | https://www.townofwoodstock.org/fileadmin/files/Archive/2020/10/TOWN-Zoning-Regulations-searchable-1.pdf
Washington |  | Shoreline | 5363960 | Permit |  |  | "Air-to-water heat pump manufacturers shall report the hourly heating output or heating efficiency with and without defrost operation at 32°F ... The hourly heating output or heating efficiency with and without defrost operation shall be documented on the mechanical permit drawings." | Section C403.3.2 | 2021 | http://cosweb.ci.shoreline.wa.us/uploads/attachments/cck/council/staffreports/2021/staffreport111521-9a.pdf
Wisconsin |  | New Auburn | 5500556350 | Setback - Property Lines | 4 | feet | "Air-conditioning equipment and heat pumps... shall be located at least four feet from side and rear property lines." | § 350-63. Other accessory uses, B. Air-conditioning equipment and heat pumps | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | New Auburn | 5500556350 | Setback - Yards | 4 | feet | "Air-conditioning equipment and heat pumps... shall not be located forward the front faces of the principal building and shall be located at least four feet from side and rear property lines." | § 350-63. Other accessory uses, B. Air-conditioning equipment and heat pumps | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | New Auburn | 5500556350 | Noise Limits | 65 | dBA | "No operation or activity shall transmit any noise exceeding 75 dBA from 7:00 a.m. to 10:00 p.m. and 65 dBA from 10:00 p.m. to 7:00 a.m. beyond the property line." | § 350-80. Noise | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | New Auburn | 5500556350 | Screening |  |  | "Any object that has potential for safety, or attractive nuisance problems must, at the discretion of the Zoning Administrator, be security fenced." | § 350-63. Other accessory uses, B. Air-conditioning equipment and heat pumps | 2023 | https://assets.parkingreform.org/assets/45f019d4-3f38-4665-8e4b-adc8c8d84cab/new-auburn-wisconsin-united-states-attachment.pdf?download
Wisconsin | Brown | Allouez | 5500901150 | Definition: Geothermal |  |  | "GEOTHERMAL ENERGY SYSTEM (GEOTHERMAL HEAT EXCHANGE). Equipment that transfers thermal energy to and/or from the ground for the purposes of heating and/or cooling a building. Geothermal energy systems consist of a closed-loop system of pipes filled with liquid, a heat exchanger and heat pump. This includes vertical closed loop, horizontal closed loop and water body closed loop systems." | 475-159 TERMS BEGINNING WITH 'G' |  | https://www.villageofallouezwi.gov/wp-content/uploads/2020/07/Allouez-Zoning-Ordinance-Fradt.pdf
Wisconsin | Brown | Allouez | 5500901150 | Permit |  |  | "To engage in the use of a building or land or any other activity requiring one or more permits or approvals under this zoning ordinance without obtaining such required permits or approvals" is unlawful, and "To engage in the use of a building or land or any other activity requiring one or more permits or approvals under this zoning ordinance in any way inconsistent with any such permit or approval" is also a violation. | 475-141 VIOLATIONS |  | https://www.villageofallouezwi.gov/wp-content/uploads/2020/07/Allouez-Zoning-Ordinance-Fradt.pdf
Wisconsin | Brown | Allouez | 5500901150 | Other Prohibitions/Regulations |  |  | "No portion of a geothermal energy system may be located within a stream or stream buffer." | 475-78 F. Geothermal Energy Systems |  | https://www.villageofallouezwi.gov/wp-content/uploads/2020/07/Allouez-Zoning-Ordinance-Fradt.pdf
Wisconsin | Brown | Denmark | 5500919700 | Setback - Property Lines | 25 | feet | Section 315-91(C)(3)(c) provides: "Above ground equipment shall comply with the setback requirements of the respective zoning district." Section 315-91(C)(3)(e) adds: "Geothermal energy systems shall conform to all setbacks requirements for Accessory Structures." Accessory-structure side/rear lot-line setbacks vary by district, including R-1 side/rear 8 ft.; R-2 side/rear 8 ft.; R-3 side/rear 5 ft.; R-4 side/rear 10 ft.; RD-1 side/rear 10 ft.; B-1 rear 25 ft.; B-2 side/rear 10 ft.; I-1 rear 25 ft.; I-2 rear 25 ft. | 315-91 Alternative Energy Systems, C(3)(c)-(e); district setback tables | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | 5500919700 | Setback - Wastewater | 75 | feet | "Geothermal energy systems shall conform to all setbacks requirements for Accessory Structures and shall: 1. Be setback a minimum of 75 feet between a vertical geothermal energy system and a personal onsite wastewater treatment system. 2. Be setback a minimum of 25 feet between a horizontal geothermal energy system and a personal onsite wastewater treatment system." | 315-91 Alternative Energy Systems, C(3)(e)1-2 | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | 5500919700 | Setback - Private Water | 75 | feet | "...except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 315-91 Alternative Energy Systems, C(3)(e)3 | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | 5500919700 | Setback - Public Water | 200 | feet | "Geothermal energy systems shall... Not be located closer than 200 feet to a well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 315-91 Alternative Energy Systems, C(3)(e)3 | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | 5500919700 | Permit |  |  | Section 315-9(D): "No structure, land, water, or air shall hereafter be used, and no structure or part thereof shall hereafter be located, erected, moved, reconstructed, extended, enlarged, converted, or structurally altered without a zoning permit..." Section 315-91(C)(2)(b) states the purpose is to "Oversee the permitting of geothermal systems." | 315-9 Interpretation; 315-91 Alternative Energy Systems, C. Geothermal Energy Systems | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | 5500919700 | Certification |  |  | "A geothermal energy system shall conform to applicable industry standards including those of ANSI. Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by UL or other approved independent testing agency." | 315-91 Alternative Energy Systems, C(3)(b) | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Brown | Denmark | 5500919700 | Other Prohibitions/Regulations |  |  | "Equipment, piping and devices shall not be located in any easement or right-of-way." | 315-91 Alternative Energy Systems, C(3)(d) | 2024 | https://ecode360.com/DE3661/laws/LF2142432.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Wastewater | 1000 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Wastewater-related distances include: "Two hundred feet between a well field and ... private onsite wastewater treatment system (POWTS) treatment tank or holding tank component and associated piping"; "Four hundred feet between a well field and a POWTS dispersal component with a design capacity of less than 12,000 gallons per day"; and "One thousand feet between a well field and ... agricultural, industrial, commercial or municipal waste water treatment plant treatment units, lagoons, or storage structures; ... or POWTS dispersal component with a design capacity of 12,000 gallons per day or more." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Public Water | 1200 | feet | Section 13-1-30(f) subjects "Geothermal wells, systems or heat exchange drilling" to the "separation distances in Section (h)." Section (h) says: "The following separation distances as specified in s. NR 811.12(5)(d), Wis. Adm. Code, shall be maintained within the Wellhead protection overlay district." The largest listed distance is "Twelve hundred feet between a well field and any solid waste storage..." while other listed distances from the municipal well/well field include 10 feet, 50 feet, 200 feet, 300 feet, 400 feet, 600 feet, and 1,000 feet. | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Fuel (above ground) | 1200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Relevant above-ground fuel tank distances include: "Ten feet between a well and an emergency or standby power system ... that has a double wall above ground storage tank"; "Two hundred feet between a well field and ... one or two family residential heating fuel oil underground storage tank or above ground storage tank"; "Three hundred feet between a well field and any farm above ground storage tank..."; "Six hundred feet between a well field and any ... above ground storage tank system with double wall, or single wall tank with secondary containment and under a canopy..."; and "Twelve hundred feet between a well field and ... any single wall farm ... above ground storage tank or other single wall ... above ground storage tank..." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Fuel (below ground) | 1200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Underground fuel tank distances include: "Two hundred feet between a well field and ... one or two family residential heating fuel oil underground storage tank..."; "Three hundred feet between a well field and any farm underground storage tank system or other underground storage tank system with double wall and with electronic interstitial monitoring..."; "Six hundred feet between a well field and any farm underground storage tank system or other underground storage tank system with double wall and with electronic interstitial monitoring..."; and "Twelve hundred feet between a well field and ... any single wall farm underground storage tank or single wall farm above ground storage tank or other single wall underground storage tank..." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Sewer Lines | 200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Section (h)(2) states: "Fifty feet between a well and a storm sewer main or a sanitary sewer main where the sanitary sewer main is constructed of water main class materials and joints." Section (h)(3) states: "Two hundred feet between a well field and any sanitary sewer main not constructed of water main class materials..." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Water Bodies | 400 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Section (h)(6) requires "Four hundred feet between a well field and ... a storm water retention or detention pond." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Setback - Hazardous Materials/Fertilizers | 1200 | feet | Geothermal wells/systems are conditional uses "subject to the separation distances in Section (h)." Hazardous-material related distances include: "Three hundred feet between a well field and any ... underground storage tank system ... These requirements apply to tanks containing ... hazardous substances"; "Three hundred feet between a well field and ... above ground storage tank system ... These requirements apply to tanks containing ... hazardous substances"; "Six hundred feet between a well field and any ... underground storage tank system ... [and] above ground storage tank system ... These requirements apply to tanks containing ... hazardous substances"; and "Twelve hundred feet between a well field and ... any single wall ... underground storage tank or above ground storage tank ... These requirements apply to tanks containing ... hazardous substances; and bulk pesticide or fertilizer handling or storage facilities." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Permit |  |  | In the Wellhead Protection Overlay District, "Geothermal wells, systems or heat exchange drilling, along with any associated piping and/or ground loop component installations" are listed as conditional uses. Section 13-1-30(f) states these uses "may be conditionally permitted ... in accordance with Title 13, Chapter 1 Article D Conditional Uses and subject to the separation distances in Section (h) Separation Distances." Article D then requires "Application for conditional use permits" and Village Board approval before the permit is issued. | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT; (f) Conditional Uses; ARTICLE D Conditional Uses |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Inspection |  |  | Section 13-1-30(h)(2), which applies because geothermal wells/systems are subject to Section (h), requires testing of certain sewer infrastructure: "Gravity sanitary sewers shall be successfully air pressure tested in place. The air pressure test shall meet or exceed the requirements of the 4 psi low pressure air test... Force mains shall be successfully pressure tested with water to meet the AWWA C600 pressure and leakage testing requirements for one hour at 125% of the pump shut-off head." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (h) Separation Distances |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin | Crawford | Gays Mills | 5502328450 | Other Prohibitions/Regulations |  |  | The overlay ordinance states that certain uses are prohibited in the Wellhead Protection Overlay District, but "Geothermal wells, systems or heat exchange drilling, along with any associated piping and/or ground loop component installations" are instead listed in Section 13-1-30(f) as uses that "may be conditionally permitted ... subject to the separation distances in Section (h) Separation Distances." | SEC. 13-1-30: WELLHEAD PROTECTION OVERLAY DISTRICT, (g) Prohibited Uses |  | https://www.gaysmills.gov/wp-content/uploads/2026/04/T-13-Zoning-April-2026.pdf
Wisconsin |  | Belleville | 5502506300 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as 'ground source heat pumps,' along with any associated piping and/or ground loop component installations." | § 615-18.1.F(5) | 2017 | https://assets.parkingreform.org/assets/52b52ef6-63ed-40fb-96c7-e77e66fdf1cf/belleville-wisconsin-united-states-attachment.pdf?download
Wisconsin |  | Belleville | 5502506300 | Permit |  |  | In the Groundwater Protection Overlay District, "Geothermal wells, also known as 'ground source heat pumps,' along with any associated piping and/or ground loop component installations" are listed as "Conditional uses." Section 615-20.A states that the Zoning Administrator may issue "a conditional use permit" only "after review, public hearing, and approval by the Plan Commission." | § 615-18.1.F(5); Article IV; § 615-20.A | 2017 | https://assets.parkingreform.org/assets/52b52ef6-63ed-40fb-96c7-e77e66fdf1cf/belleville-wisconsin-united-states-attachment.pdf?download
Wisconsin | Dane | DeForest | 5502519350 | Permit |  |  | Within the WP Wellhead Protection Overlay District, "Geothermal wells, systems, or heat exchange drilling, along with any associated piping and/or ground loop component installations" are listed as "conditional uses." The ordinance further provides that "No application for a conditional use permit shall be placed on any agenda for action... unless the Zoning Administrator has determined that a complete application has been submitted." | §15.155(5) CONDITIONAL USES; §15.16(3) APPLICATION, PROCEDURES, AND CRITERIA | 2026 | https://www.deforestwi.gov/DocumentCenter/View/86/Chapter-15-Zoning-Code-PDF
Wisconsin | Dane | Maple Bluff | 5502548750 | Definition: Geothermal |  |  | "Such energy generating equipment includes solar, wind, and geothermal energy systems that convert energy from the sun, wind, or earth into usable thermal, mechanical, chemical, or electrical energy, where such energy system is accessory to the principal use of the parcel, and primarily supplies energy to such principal use." | § 225-3-5 C. Small exterior communication or energy system | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dane | Maple Bluff | 5502548750 | Permit |  |  | "Prior to installation or expansion, shall be subject to Building Board approval per § 225-8-5 ... Following such approval, a building permit shall also be required." Also, for geothermal systems, "All activities, materials, structures, and products associated with the installation and maintenance of the system shall comply with applicable state-approved standards and drilling permit procedures..." | § 225-3-5 C(2) and C(10)(d) | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dane | Maple Bluff | 5502548750 | Certification |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of the system shall comply with applicable state-approved standards and drilling permit procedures and shall meet the certification standards established by the IGSHPA or other professional geothermal system accreditation association recognized by the State of Wisconsin." | § 225-3-5 C(10)(d) | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dane | Maple Bluff | 5502548750 | Other Prohibitions/Regulations |  |  | For open loop geothermal systems, "Such systems may not be installed directly in a navigable body of water." | § 225-3-5 C(10)(e) | 2025 | https://villageofmaplebluff.com/wp-content/uploads/2025/07/Chapter-225_Village-of-Maple-Bluff-Zoning-Ordinance_Adopted.pdf
Wisconsin | Dodge | Mayville | 5502750200 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | § 430-48.1 GWP Groundwater Protection Overlay District, Conditional uses | 2023 | https://ecode360.com/9525348
Wisconsin | Dodge | Mayville | 5502750200 | Permit |  |  | "The following uses may be conditionally permitted in the Wellhead Protection Area under § 430-49, Conditional uses, and subject to the separation distances in Subsection H, Separation distances. ... Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | § 430-48.1 GWP Groundwater Protection Overlay District, Conditional uses | 2023 | https://ecode360.com/9525348
Wisconsin | Dunn | Wheeler | 5503386575 | Permit |  |  | "The following uses may be conditionally permitted in the Wellhead protection overlay district in accordance with Article E Conditional Uses and subject to the separation distances in Section (h) Separation Distances. ... (5) Geothermal wells, systems or heat exchange drilling, along with any associated piping and/or ground loop component installations." | Sec. 13-1-53 WP Wellhead Protection Overlay District; Conditional Uses | 2025 | https://villageofwheelerwi.com/wp-content/uploads/2025/12/well-head-protection-plan20251210_18043137.pdf
Wisconsin | Iowa | Barneveld | 5504775 | Permit |  |  | "The following uses may be conditionally permitted in the Wellhead protection overlay district in accordance with Chapter 280 Article IV Conditional Uses and subject to the separation distances in Section (J) Separation Distances. ... 5) Geothermal wells, systems or heat exchange drilling, along with any associated piping and/ or ground loop component installations." | H. Conditional Uses | 2025 | https://ecode360.com/BA3856/laws/LF2493855.pdf
Wisconsin | Juneau | New Lisbon | 5505756900 | Definition: Geothermal Heat Pump |  |  | Conditional uses in the Groundwater Protection Overlay District include: "Geothermal wells, also known as ground source heat pump, along with any associated piping and/or ground loop component installations." | § 520-25.1 Groundwater Protection Overlay District | 2018 | https://ecode360.com/15204104
Wisconsin | Juneau | New Lisbon | 5505756900 | Permit |  |  | The ordinance states: "The following uses may be conditionally permitted in the Groundwater Protection Overlay District... Geothermal wells, also known as ground source heat pump, along with any associated piping and/or ground loop component installations." It further states these uses are "governed by the conditional use provisions in Article V of this chapter." | § 520-25.1 Groundwater Protection Overlay District | 2018 | https://ecode360.com/15204104
Wisconsin | Manitowoc | Reedsville | 5507166875 | Permit |  |  | Table 3 lists "Geothermal equipment for private use not associated with a public or private utility" as an accessory use and marks it "Yes" under the conditional-use reference column; Section 8-12-4(A)(1) states: "A conditional use permit shall be required for the establishment of each use listed as a conditional use in Table 1 of this Chapter." | Table 3 - Table of Allowed Accessory Uses; 8-12-4: CONDITIONAL USE PERMITS | 2026 | https://storage.googleapis.com/juniper-media-library/506/2026/03/Ordinance%202026-01%20Amending%20Title%208.pdf
Wisconsin | Marathon | Rothschild | 5507369725 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." | § 590-32 C(2)(d) | 2026 | https://ecode360.com/15464803
Wisconsin | Marathon | Rothschild | 5507369725 | Permit |  |  | In the Wellhead Protection Overlay District, "Only the following uses may be conditionally permitted... (d) Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." Section E adds that "The Village shall permit conditional uses in the Groundwater Protection Overlay Districts" subject to application, referral, review, and hearing procedures. | § 590-32 C(2)(d); § 590-32 E | 2026 | https://ecode360.com/15464803
Wisconsin | Marathon | Schofield | 5507372150 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." | § 55-673(c)(2)(d) Conditional Uses | 2016 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/14110/801091/pdf
Wisconsin | Marathon | Schofield | 5507372150 | Permit |  |  | Geothermal wells/ground source heat pumps are listed as a conditional use: "Geothermal wells, also known as ground source heat pumps, along with any associated piping and/or ground loop component installations." The ordinance then states: "The City shall permit conditional uses in the Groundwater Protection Overlay District subject to" the application, review, hearing, and standards in § 55-673(e). | § 55-673(c)(2)(d); § 55-673(e) Administration of Conditional Use Permits | 2016 | https://mcclibraryfunctions.azurewebsites.us/api/ordinanceDownload/14110/801091/pdf
Wisconsin | Marathon | Weston | 5507386050 | Definition: Geothermal Heat Pump |  |  | "A Geothermal Energy System (GES) is a central heating and/or cooling system that uses the moderate temperatures of subsurface ground or a body of water to assist with the heating or cooling of a building or a building’s water. A GES requires an underground heat exchanger, in the form of a network of underground or underwater pipes or tubes filled with a liquid medium (refrigerant, water mixed with anti-freeze, or water). The liquid medium within the heat exchanger is transferred between a structure and the heat exchanger via pumps. In an Open Loop GES, ground or surface water is continuously drawn from an outside source through the heat exchanger pipes and discharged after use. In a Closed Loop GES, the system is designed so that heat exchanger fluid does not come in direct contact with soils, groundwater, or surface water." | Section 94.4.09(19) Geothermal Energy System (GES) | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | 5507386050 | Setback - Roads | 10 | feet | "Underground GES pipes or tubes shall be set back a minimum of 10 feet from any lot line, public right-of-way, buried utility line, utility easement, and permanently protected natural resource area." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 2 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | 5507386050 | Setback - Right of Way | 10 | feet | "Underground GES pipes or tubes shall be set back a minimum of 10 feet from any lot line, public right-of-way, buried utility line, utility easement, and permanently protected natural resource area." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 2 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | 5507386050 | Setback - Property Lines | 10 | feet | "Underground GES pipes or tubes shall be set back a minimum of 10 feet from any lot line, public right-of-way, buried utility line, utility easement, and permanently protected natural resource area." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 2 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | 5507386050 | Permit |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable State-approved standards and drilling permit procedures..." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 5 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | 5507386050 | Certification |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable State-approved standards and drilling permit procedures and shall meet the certification standards established by the IGSHPA or other professional geothermal system accreditation association recognized by the State of Wisconsin." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 5 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Marathon | Weston | 5507386050 | Other Prohibitions/Regulations |  |  | "GESs may not be installed directly in a navigable body of water..." | Section 94.4.09(19) Geothermal Energy System (GES), Performance Standard 6 | 2025 | https://storage.googleapis.com/juniper-media-library/193/2025/08/250312_Town_of_Weston_Zoning_Ordinance_ADOPTED.pdf
Wisconsin | Oneida | Rhinelander | 5508567200 | Definition: Geothermal Heat Pump |  |  | "A geothermal energy system (GES) is a central heating and/or cooling system that uses the moderate temperatures of subsurface ground or a body of water to assist with the heating or cooling of a building or a building's water. A GES requires an underground heat exchanger, in the form of a network of underground or underwater pipes or tubes filled with a liquid medium (refrigerant, water mixed with antifreeze, or water). The liquid medium within the heat exchanger is transferred between a structure and the heat exchanger via pumps. In an open loop GES, ground or surface water is continuously drawn from an outside source through the heat exchanger pipes and discharged after use. In a closed loop GES, the system is designed so that heat exchanger fluid does not come in direct contact with soils, groundwater, or surface water." | 5.07.4.09(13) Geothermal energy system (GES) | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Oneida | Rhinelander | 5508567200 | Permit |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable state-approved standards and drilling permit procedures..." | 5.07.4.09(13) Performance standards | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Oneida | Rhinelander | 5508567200 | Certification |  |  | "All activities, materials, structures, and products associated with the installation and maintenance of a GES shall comply with applicable state-approved standards and drilling permit procedures and shall meet the certification standards established by the IGSHPA or other professional geothermal system accreditation association recognized by the State of Wisconsin." | 5.07.4.09(13) Performance standards | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Oneida | Rhinelander | 5508567200 | Other Prohibitions/Regulations |  |  | "GESs may not be installed directly in a navigable body of water..." | 5.07.4.09(13) Performance standards | 2025 | https://cms3.revize.com/revize/rhinelander/SIGNED%20ORDINANCE%202025-11%20-%20AMENDING%20ACCESSORY%20AND%20MISC%20LAND%20USE%20TYPES.pdf
Wisconsin | Outagamie | Buchanan | 5508710750 | Permit |  |  | Table 525-32-1 lists "Geothermal equipment for private use not associated with a public or private utility" and the "Is Permit Required?" column states "Yes." | Table 525-32-1: Accessory Uses, Buildings and Structures | 2024 | https://d3n9y02raazwpg.cloudfront.net/buchanan/fe958e2f-c4fa-11ee-8fe8-0050569183fa-301dd9fd-e864-4fb1-8bf5-0961d018c857-1710285886.pdf
Wisconsin | Racine | Wind Point | 5510187700 | Definition: Geothermal |  |  | "Geothermal Energy System. A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems." | Sec. 36-301. Definitions | 2024 | https://cms3.revize.com/revize/windpoint/Documents/Government/Agenda%20and%20Minutes/Plan%20Commission/2024/Plan%20Commission%20Agenda%20&%20Meeting%20Packet%2001.04.2024.pdf
Wisconsin | Racine | Wind Point | 5510187700 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System, Horizontal. A geothermal energy system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth." "Geothermal Energy System, Vertical. A geothermal energy system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth." | Sec. 36-301. Definitions | 2024 | https://cms3.revize.com/revize/windpoint/Documents/Government/Agenda%20and%20Minutes/Plan%20Commission/2024/Plan%20Commission%20Agenda%20&%20Meeting%20Packet%2001.04.2024.pdf
Wisconsin | Sauk | Merrimac | 5511151350 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | §185-21A(6)(e) Conditional Uses |  | https://merrimacwi.gov/vertical/sites/%7BCBEFE108-6CEC-4014-B024-0697DD562493%7D/uploads/Proposed_WHPP_ORD_185-21A_as_Posted.pdf
Wisconsin | Sauk | Merrimac | 5511151350 | Permit |  |  | "The following uses may be conditionally permitted under Chapter 185 Zoning, Article IV Conditional Uses, in the Wellhead Protection Area Overlay District... (e) Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | §185-21A(6) Conditional Uses |  | https://merrimacwi.gov/vertical/sites/%7BCBEFE108-6CEC-4014-B024-0697DD562493%7D/uploads/Proposed_WHPP_ORD_185-21A_as_Posted.pdf
Wisconsin | Sauk | North Freedom | 5511158025 | Definition: Geothermal Heat Pump |  |  | "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations." | 3.11(f)(5) Conditional Uses | 1996 | https://storage.googleapis.com/juniper-media-library/239/2026/01/CHAPTER%2016%20ZONING.pdf
Wisconsin | Sauk | North Freedom | 5511158025 | Permit |  |  | In the Groundwater Protection Overlay District, "Geothermal wells, also known as ground source heat pump along with any associated piping and/or ground loop component installations" are listed under "Conditional Uses." Section 4.1 states: "The Village Plan Committee may authorize the Village Board to issue a zoning permit for conditional uses after review and a public hearing." Section 4.2 requires applications for zoning permits for conditional uses, and Section 4.4 states the Plan Committee reviews and approves, approves with conditions, or rejects the application. | 3.11(f) Conditional Uses; 4.1 PERMITS; 4.2 APPLICATION; 4.4 REVIEW AND APPROVAL | 1996 | https://storage.googleapis.com/juniper-media-library/239/2026/01/CHAPTER%2016%20ZONING.pdf
Wisconsin | Sauk | North Freedom | 5511158025 | Inspection |  |  | "The Village Board will act as the administrator and enforcement officer for the provisions of this Ordinance. Their duties shall be to interpret and administer this Ordinance and to issue, after on-site inspection, all permits required by this Ordinance." Also, "any trustee may enter at any reasonable time onto any public or private lands or waters to make a zoning inspection." | 2.3 ZONING ADMINISTRATOR DESIGNATED | 1996 | https://storage.googleapis.com/juniper-media-library/239/2026/01/CHAPTER%2016%20ZONING.pdf
Wisconsin | Sawyer | Spider Lake | 5511375450 | Permit |  |  | "a Conditional Use Permit is required for the construction, installation or modification of alternative or renewable energy systems. These systems include, but are not limited to: solar systems, wind energy systems, geothermal units, and energy producing digester systems." | Section 6.11(A) Purpose and Intent | 2019 | https://storage.googleapis.com/juniper-media-library/534/2026/03/2019_FINAL_Ord_17-88_land_use_ordinance-1.pdf
Wisconsin | Sawyer | Spider Lake | 5511375450 | Inspection |  |  | "For the purpose of issuance of necessary permits and inspections, all alternative energy systems are deemed to be structures. As a condition of the issuance of the Conditional Use Permit for an alternative or renewable energy system, the permit holder shall allow access to the site by the Zoning Administrator." | Section 6.11(C)(1) General | 2019 | https://storage.googleapis.com/juniper-media-library/534/2026/03/2019_FINAL_Ord_17-88_land_use_ordinance-1.pdf
Wisconsin | Sawyer | Spider Lake | 5511375450 | Decommissioning |  |  | An applicant for an alternative or renewable energy system must provide "[a] description of the decommissioning process and the cost of decommissioning or removal of the system." | Section 6.11(B) Conditional Use | 2019 | https://storage.googleapis.com/juniper-media-library/534/2026/03/2019_FINAL_Ord_17-88_land_use_ordinance-1.pdf
Wisconsin | Sheboygan | Mitchell | 5511753375 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems." | 17.120 Application of Definitions, B. Definitions | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | 5511753375 | Setback - Property Lines | 10 | feet | 17.52 C.3.c requires: "Above ground equipment shall comply with the setback requirements of the respective zoning district." The referenced district standards are generally "Side and rear yard setbacks -10-feet or the height of the building or structure, whichever is greater" in AG-1, adopted by reference in AG-2, AG-3, R-1, C-1, IN-1, and M-1; R-2 uses the AG-1 standards except for street setback wording. | 17.30 AG-1 Large Parcel General Agricultural District; 17.31 AG-2 Animal Intensive Agricultural District; 17.32 AG-3 Smaller Parcel General Agricultural District; 17.33 R-1 Small Lot Residential District; 17.34 R-2 Large Lot Residential District; 17.35 C-1 Commercial District; 17.37 IN-1 Institutional District; 17.38 M-1 Manufacturing District; 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | 5511753375 | Setback - Wastewater | 75 | feet | 17.52 C.3.e provides: "Geothermal energy systems shall conform to all setbacks requirements for accessory structures and shall: (1) Be setback a minimum of 75 feet between a vertical geothermal energy system and a personal onsite wastewater treatment system. (2) Be setback a minimum of 25 feet between a horizontal geothermal energy system and a personal onsite wastewater treatment system." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | 5511753375 | Setback - Private Water | 75 | feet | 17.52 C.3.e(3) states geothermal systems shall "Not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | 5511753375 | Setback - Public Water | 200 | feet | 17.52 C.3.e(3) states geothermal systems shall "Not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | 5511753375 | Permit |  |  | The ordinance makes geothermal systems a conditional use in several districts: "Geothermal energy systems" are listed under "Conditional Uses" in R-1, R-2, and C-1. It also states in 17.52 C.1.b that the purpose is to "Oversee the permitting of geothermal systems." Separately, 17.100.B provides: "A Building Permit shall be required for the construction or alteration of any building or structure..." and 17.100.A states the Building Permit verifies conformity with applicable law. | 17.33 R-1 Small Lot Residential District; 17.34 R-2 Large Lot Residential District; 17.35 C-1 Commercial District; 17.52 C. Geothermal Energy Systems; 17.100 Building Permits | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Sheboygan | Mitchell | 5511753375 | Certification |  |  | 17.52 C.3.b states: "A geothermal energy system shall conform to applicable industry standards including those of ANSI. Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by UL or other approved independent testing agency." | 17.52 C. Geothermal Energy Systems | 2022 | https://assets.parkingreform.org/assets/08e8ef62-fd40-4dec-9fbf-bccaacc07bac/town-of-mitchell-wisconsin-united-states-attachment.pdf?download
Wisconsin | Taylor | Little Black | 5511944900 | Permit |  |  | "The owner of any building or structure in the town... who constructs, installs... any building or structure within the Town shall seek and obtain from the Zoning Administrator a Zoning Permit prior to commencing... any construction, installation... of any building." Section 5.4.B adds: "A Zoning Permit shall be issued if and only if it has been satisfactorily determined... that the use of land and buildings set forth in the zoning permit application is consistent and in compliance with this ordinance." For conditional uses, Section 9.2.B requires "a copy of all federal, state, and county permits necessary for the proposed use." | Section 5.2 / 5.4 / 9.2 | 2018 | https://www.townoflittleblack.com/townoflittleblack/Ordinances%20and%20Permits/90%20Zoning/ZONING%20CODE%20OF%20LITTLE%20BLACK%202017-2-15%20.pdf
Wisconsin | Taylor | Little Black | 5511944900 | Inspection |  |  | "Upon completion of a project for which a zoning permit is required, the owner shall notify the Zoning Administrator and request an inspection to determine completion and compliance with this Ordinance. The inspection must be made before a zoning certificate of compliance may be issued." | Section 5.4.F | 2018 | https://www.townoflittleblack.com/townoflittleblack/Ordinances%20and%20Permits/90%20Zoning/ZONING%20CODE%20OF%20LITTLE%20BLACK%202017-2-15%20.pdf
Wisconsin | Taylor | Little Black | 5511944900 | Open-loop Prohibitions |  |  | Residential District purpose clause states: "Residential normal water usage is acceptable with the exception of open loop geothermal." Separately, Section 12.5.R prohibits "Any use requiring continuous pumping of a groundwater well." | Section 12.1 / 12.5.R | 2018 | https://www.townoflittleblack.com/townoflittleblack/Ordinances%20and%20Permits/90%20Zoning/ZONING%20CODE%20OF%20LITTLE%20BLACK%202017-2-15%20.pdf
Wisconsin | Washington | Polk | 5513163875 | Definition: Geothermal |  |  | 'Geothermal Energy System. A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems.' Also: 'Geothermal Energy System, Horizontal. A geothermal energy system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth.' 'Geothermal Energy System, Vertical. A geothermal energy system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth.' | 17.13.01(B)(21)-(23) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Setback - Yards | 25 | feet | Section 17.7.03(C)(4) requires: 'Above ground equipment shall comply with the setback requirements of the respective zoning district.' Section 17.7.03(C)(6) adds: 'Geothermal energy systems shall conform to all setbacks requirements for accessory structures.' The accessory-structure yard rule in Section 17.6.02(E) states such structures 'shall not be closer than 25 feet to a rear lot line (unless a greater setback is required by the applicable zoning district).' | 17.7.03(C)(4), 17.7.03(C)(6), 17.6.02(E) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Setback - Wastewater | 75 | feet | Section 17.7.03(C)(6)(a): 'Be setback a minimum of 75 feet from a personal onsite wastewater treatment system.' | 17.7.03(C)(6)(a) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Setback - Private Water | 75 | feet | Section 17.7.03(C)(6)(b) creates an exception for private wells: geothermal systems may be closer than 200 feet 'when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system.' | 17.7.03(C)(6)(b) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Setback - Public Water | 200 | feet | Section 17.7.03(C)(6)(b): geothermal systems shall 'Not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system.' | 17.7.03(C)(6)(b) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Permit |  |  | Section 17.2.03 states: 'Applications for a Building Permit shall be made in duplicate to the Zoning Administrator...' and the permit application must include site and use information, with the permit 'granted or denied in writing by the Building Inspector and issued by the Zoning Administrator within 30 days.' Section 17.12.01 adds that 'all persons, firms, or corporations performing work in the Town of Polk for which this Chapter requires the application for a permit... shall pay a fee.' Geothermal systems are regulated in Chapter 17.7.03 as accessory systems under this chapter. | 17.2.03 BUILDING AND ZONING PERMIT; 17.12.01 FEES | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Inspection |  |  | Section 17.2.02(B) provides: 'The Duty of the Zoning Administrator or his designee, shall be to investigate all complaints, give notice of violations, and enforce the provisions of Chapter 17. The Zoning Administrator and his designee, may enter at any reasonable time onto any public or private lands or waters to make a Zoning Inspection.' | 17.2.02 COMPLIANCE | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | Polk | 5513163875 | Other Prohibitions/Regulations |  |  | Section 17.7.03(C)(5) states: 'Equipment, piping and devices shall not be located in any easement or right-of-way.' | 17.7.03(C)(5) | 2022 | https://cdn.townweb.com/townofpolk-wi.gov/wp-content/uploads/2022/02/Chapter-17-Zoning-Ordinance-Adopted-01.04.2022.pdf
Wisconsin | Washington | West Bend | 5513185375 | Setback - Wastewater | 75 | feet | "Geothermal energy systems shall conform to all setbacks requirements for Accessory Structures and shall: (1) Be setback a minimum of 75 feet between a vertical geothermal energy system and a personal onsite wastewater treatment system. (2) Be setback a minimum of 25 feet between a horizontal geothermal energy system and a personal onsite wastewater treatment system." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | 5513185375 | Setback - Private Water | 75 | feet | "[Geothermal systems shall] not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | 5513185375 | Setback - Public Water | 200 | feet | "[Geothermal systems shall] not be located closer than 200 feet to a water well, except when the well is a private water system well and when the owner is the same for both the water well and the geothermal system, in which case the water well shall not be closer than 75 feet from the geothermal system." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | 5513185375 | Permit |  |  | "A geothermal energy system shall require a Conditional Use permit in all zoning districts." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Washington | West Bend | 5513185375 | Certification |  |  | "A geothermal energy system shall conform to applicable industry standards including those of ANSI. Applicants shall submit certificate of compliance demonstrating that the system has been tested and approved by UL or other approved independent testing agency." | § 325-96 Geothermal Energy Systems — Standards | 2024 | https://cdn.townweb.com/townofwestbend.com/wp-content/uploads/2024/10/Public-Hearing-Ordinance.pdf
Wisconsin | Winnebago | Winchester | 5513987650 | Definition: Geothermal |  |  | "Geothermal Energy System. A sealed, watertight loop of pipe buried outside of a building foundation, intended to re-circulate a liquid solution through a heat exchanger. This includes but is not limited to: vertical closed loop, horizontal closed loop and body of water closed loop systems." "Geothermal Energy System, Horizontal. A geothermal energy system constructed to contain horizontal piping and the installation and grouting of the horizontal piping when such piping does not exceed 20 feet in depth." "Geothermal Energy System, Vertical. A geothermal energy system constructed to contain vertical piping and the installation and grouting of the vertical piping exceeding 20 feet in depth." | 17.300 Definitions(115)-(117) | 2024 | https://townofwinchesterwi.gov/wp-content/uploads/2024/07/Chapter-17-Zoning-Ordinance-Approved-07-15-2024.pdf
Wisconsin | Winnebago | Wolf River | 5513988475 | Definition: Geothermal |  |  | "ALTERNATIVE ENERGY: Energy fueled in ways that do not use up natural resources or harm the environment such as solar, wind, and geothermal". | CHAPTER A DEFINITIONS, SECTION 1.01 DEFINITIONS | 2015 | https://townofwolfrivercom-old.townweb.com/wp-content/uploads/2016/05/Town-Zoning-Ordinance.pdf
Wisconsin | Winnebago | Wolf River | 5513988475 | Permit |  |  | Section 1.03(2): "after the effective date of this Ordinance, no structure, land or water shall be developed, and no structure or part thereof shall be located, erected, moved, reconstructed, enlarged, extended, converted or structurally altered without a Zoning/Building Permit and without full compliance with this Ordinance." Section 1.13: "No heat pumps that discharge water shall be installed in any facility in the Town of Wolf River unless and until the proposed installation is reviewed by the Planning and Zoning Committee... If the Planning and Zoning Committee is satisfied that such conditions are met... the heat pump installation may proceed, and the Zoning Administrator shall note the location of such installation." Section 1.21(3): "A Zoning/Building Permit shall be granted or denied in writing by the Zoning Administrator within thirty (30) days after filing of the application." | SECTION 1.03 GENERAL PROVISIONS; SECTION 1.13 HEAT PUMPS; SECTION 1.21 ZONING / BUILDING PERMITS | 2015 | https://townofwolfrivercom-old.townweb.com/wp-content/uploads/2016/05/Town-Zoning-Ordinance.pdf
California |  | Emeryville | 622594 | Definition: Geothermal Heat Pump |  |  | "ELECTRIC HEATING APPLIANCE. A device that produces heat energy to create a warm environment by the application of electric power to resistance elements, refrigerant compressors, or dissimilar material junctions, as defined in the California Mechanical Code." | Section 202: Definitions | 2022 | https://www.emeryville.org/files/assets/city/v/1/development/documents/building-permits/repealing-and-replacing-buidling-regulations.pdf
California |  | Emeryville | 622594 | Permit |  |  | Where combustion equipment is allowed, "the construction drawings shall indicate electrical infrastructure and physical space accommodating the future installation of an electrical heating appliance ... as certified by a registered design professional or licensed electrical contractor." The ordinance also states that all-electric requirements apply to "new construction buildings and qualifying alteration projects" under Sections 4.106.5 and 5.106. | Section 5.106.13.2 Requirements for combustion equipment; Section 4.106.5.2 Requirements for combustion equipment | 2022 | https://www.emeryville.org/files/assets/city/v/1/development/documents/building-permits/repealing-and-replacing-buidling-regulations.pdf
California |  | Huntington Beach | 636000 | Permit |  |  | "the Uniform Solar, Hydronics and Geothermal Code... 2021 Edition" is adopted by reference, and the chapter states it is adopted "for the purpose of protecting public health and safety by prescribing minimum standards for the use, design and installation of solar energy systems; by requiring a permit and inspection for installation, alteration and replacement of said equipment." It further states: "From the date on which this chapter takes effect, the provisions thereof shall be controlling within the corporate limits of the City of Huntington Beach." | § 17.60.010 Adoption. | 2025 | https://ecode360.com/43801882
California |  | Huntington Beach | 636000 | Inspection |  |  | "the Uniform Solar, Hydronics and Geothermal Code... 2021 Edition" is adopted by reference, and the chapter states it is adopted "for the purpose of protecting public health and safety by prescribing minimum standards for the use, design and installation of solar energy systems; by requiring a permit and inspection for installation, alteration and replacement of said equipment." It further states: "From the date on which this chapter takes effect, the provisions thereof shall be controlling within the corporate limits of the City of Huntington Beach." | § 17.60.010 Adoption. | 2025 | https://ecode360.com/43801882
California |  | Palo Alto | 655282 | Inspection |  |  | 'Alterations which install new or replacement heat pumps shall meet the applicable requirements of subsections i, ii, iii, and v.' Subsection ii requires that minimum airflow rate be 'confirmed through field verification and diagnostic testing' and refrigerant charge be verified by either: 'The installer and rater shall perform the standard charge verification procedure as specified in Reference Residential Appendix Section RA3.2.2' or 'The ECC-Rater shall verify the charge using RA3.2.2 and RA3.3.' Subsection iii similarly requires weigh-in charging 'as verified by an ECC-Rater according to the procedures specified in Reference Residential Appendix RA3.2.3.2.' | 16.17.140 Section 150.2(b)1.F | 2025 | https://www.paloalto.gov/files/assets/public/v/1/development-services/building-division/adoptive-ordinances/2025-edition/urgent_ord_5665-cenc-1.pdf
California |  | Piedmont | 656938 | Noise Limits | 50 | dBA | 'Machines and other devices located on the exterior of structures which generate sounds perceptible outside the perimeters of the lot on which they are located must be installed with sound transmission control measures to adequately minimize or eliminate the transmission of the sound to a level not to exceed 50 decibels, A-weighted, at the nearest property line to the source.' The section adds that it 'includes, but is not limited to, pool and spa filter systems, air conditioning units, heat pumps, generators, and exterior mounted blowers for exhaust systems.' | 8.02.020 CC. Appendix BG, Section BG105 - Mechanically Generated Noise Sources | 2026 | https://piedmont.ca.gov/common/pages/GetFile.ashx?key=r0lBARG3
California |  | Piedmont | 656938 | Permit |  |  | For qualifying single-family additions or alterations, the ordinance states: 'An alteration of or addition to a single family building, with a stated project value of $35,000 or more, is required to submit documentation that one item from the following list of Energy Efficiency and Electrification measures is included in the scope of work...' The list includes: '*Replace fuel gas furnace with an electric heat pump system meeting the Requirements of the 2025 California Energy Code Section 150.2(b)C...' and another measure may be implemented if it 'is submitted with the application for a building permit.' | 8.02.070 E. Section 150.2(d) - Single Family Additions or Alterations | 2026 | https://piedmont.ca.gov/common/pages/GetFile.ashx?key=r0lBARG3
California | San Bernardino | San Bernardino | 665000 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL FACILITY. Any space or process, heating or cooling apparatus or system used to pump, convey or transport geothermal resources or thermal ground water, including, but not limited to, ground water heat pumps, fluid heat exchangers, well and circulating pumps, pipelines, valves, fittings or controls." | § 13.20.115 GEOTHERMAL FACILITY. | 1983 | https://codelibrary.amlegal.com/codes/sanbernardinoca/latest/sanbernardino_ca/0-0-0-14939
California | Santa Cruz | Santa Cruz | 669112 | Permit |  |  | "The chief building official shall charge and receive such fees for services, inspections, and permits relating to any work subject to this chapter..." Section 3 states: "This ordinance shall take effect and be in full force thirty (30) days after final adoption." | 18.15.050 PERMIT FEES | 2023 | https://www.santacruzca.gov/files/assets/city/v/1/pl/documents/green-building-program/ordinance-202312-energy-reach-code.pdf
California | Santa Cruz | Santa Cruz | 669112 | Inspection |  |  | "The chief building official shall charge and receive such fees for services, inspections, and permits relating to any work subject to this chapter..." | 18.15.050 PERMIT FEES | 2023 | https://www.santacruzca.gov/files/assets/city/v/1/pl/documents/green-building-program/ordinance-202312-energy-reach-code.pdf
California |  | South Gate | 673080 | Permit |  |  | "9.13.010 Adoption by Reference to the Uniform Solar, Hydronics and Geothermal Code. Except as provided herein, the 2024 Edition of the Uniform Solar, Hydronics and Geothermal Code ... is hereby adopted by reference as though fully set forth herein"; and "The Building Official shall not issue a permit pursuant to the Building Code unless he or she determines an applicant and a property owner have first complied with all regulations in Title 9, and with all other provisions of the South Gate Municipal Code ... that pertain to the work and/or installations for which a permit is sought." | Section 13, 9.13.010 Adoption by Reference to the Uniform Solar, Hydronics and Geothermal Code; Section 2, [A]105.8 Permit Issuance - Additional Prerequisites | 2026 | https://ecode360.com/SO4650/laws/LF2686687.pdf
California |  | South Gate | 673080 | Inspection |  |  | "The final inspection shall be made after all work required by the building permit is completed. All work and installations that are authorized by the building permit shall not become lawful until a permit holder has obtained a final inspection approval from the Building and Safety Division, which shall be in writing." Also, "Construction, work, or installations occurring in connection with a permit that do not remain visible and accessible for an inspection ... are unlawful" and noncompliant work is subject to a correction notice "following an inspection." | Section 2, 110.3.12 Final inspection; [A]110.7 Concealed and/or Inaccessible Construction; [A]110.8 Corrections | 2026 | https://ecode360.com/SO4650/laws/LF2686687.pdf
California | Lassen | Susanville | 677364 | Definition: Well |  |  | "Well" means "any artificial opening or artificially altered natural opening, however made, by which geothermal fluids or thermal groundwater is sought or through which geothermal fluids or thermal groundwater flows under natural pressure or is artificially withdrawn, or is used to operate a heat exchanger within the well, provided that this definition shall not include a natural spring." | § 13.12.030 Definitions |  | https://ecode360.com/44217318
California | Lassen | Susanville | 677364 | Definition: Geothermal Heat Pump |  |  | "Geothermal facility" means "any space or process heating or cooling apparatus or system used to pump, convey or transport geothermal resources or thermal groundwater, including, but not limited to, groundwater heat pumps, fluid heat exchangers, well and circulating pumps, pipelines, valves, fittings or controls." | § 13.12.030 Definitions |  | https://ecode360.com/44217318
California |  | Wildomar | 685446 | Definition: Well |  |  | "Geothermal heat exchange well" means "any uncased excavation by any method for the purpose of using the heat exchange capacity of the earth for heating and cooling and in which the ambient ground temperature is 86° Fahrenheit (30° Celsius) or less and which uses a closed loop fluid system to prevent the discharge or escape of its fluid into the surrounding aquifers or geologic formations. Geothermal heat exchange wells are also known as ground source heat pump wells (California Water Code Section 13713). Such wells or boreholes are not intended to produce water or steam." | § 13.20.020 Definitions | 2008 | https://ecode360.com/43471046
California |  | Wildomar | 685446 | Permit |  |  | "No person or entity... shall dig, drill, bore, drive, reconstruct or destroy... (4) geothermal heat exchange well, without first filing a written application to do so with the Department, and receiving and retaining a valid permit as provided in this chapter." The section also states: "An application for a permit to construct a... geothermal heat exchange well shall be submitted to the Department" and lists required application contents. | § 13.20.030 Permit requirements | 2008 | https://ecode360.com/43471046
California |  | Wildomar | 685446 | Inspection |  |  | "A well inspection shall be requested of the Department at least two working days in advance of" specified activities, including for "all wells" any "special inspection" required by permit and for "well and boring destruction" both "[d]uring the actual sealing of the well" and "[i]mmediately after all well destruction work has been completed." | § 13.20.130 Required inspection of wells | 2008 | https://ecode360.com/43471046
California |  | Wildomar | 685446 | Certification |  |  | The geothermal permit application must include "[t]he C-57 license number and signature of the person responsible for constructing the well." Separately, "No persons shall engage in any activity listed in Section 13.20.030 unless he or she... possesses a valid C-57 license in accordance with the California Contractor's State License Law... or possesses a license appropriate to the activity to be engaged in." | § 13.20.030 Permit requirements; § 13.20.090 Licensing and registration of water well drillers and contractors | 2008 | https://ecode360.com/43471046
California |  | Wildomar | 685446 | Decommissioning |  |  | "If after 30 days of abandonment, the owner has not declared to the Department a proposed reuse of the well... and the well has been found by the Department to be a hazard... the Department shall direct the owner to destroy the well, in accordance with Section 13.20.100." Also, "Upon removal of the pump, the casing shall be provided with a threaded or equivalently secured watertight cap. The well shall be maintained so that it will not be a hazard to public health and safety until such time as it is properly destroyed." In addition, "As a condition of a construction or reconstruction permit, any abandoned wells on the property shall be destroyed in accordance with standards provided in this chapter." | § 13.20.220 Well abandonment; § 13.20.030(E) | 2008 | https://ecode360.com/43471046
Colorado |  | Carbondale | 812045 | Definition: Geothermal |  |  | Table C409.1.2.3.1 lists "Geothermal energy" as an energy source with a threshold of "> 1,000,000 Btu/h (300 kW) heating" for required measurement devices. | Table C409.1.2.3.1 ENERGY SOURCE THRESHOLDS | 2025 | https://carbondalegov.community.diligentoneplatform.com/document/c1af4225-b3f7-4809-a65b-210bd4c9d9d3/
Colorado | Montezuma | Dolores | 820770 | Definition: Well |  |  | "Geothermal boreholes: A hole drilled or bored into the earth into which piping is inserted for use a closed vertical loop geothermal system." | Section 2.6. - General definitions | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Definition: Geothermal Heat Pump |  |  | "Ground source heat pump system: A system that uses the relatively constant temperature of the earth or a body of water to provide heating in the winter and cooling in the summer. System components include open or closed loops of pipe, coils or plates; a fluid that absorbs and transfers heat; a heat pump unit that processes heat for use or disperses heat for cooling; and an air distribution system." Also defined are "Ground source heat pump system, closed loop," "Ground source heat pump system, horizontal," "Ground source heat pump system, open loop," and "Ground source heat pump system, vertical." | Section 2.6. - General definitions | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Setback - Property Lines | 5 | feet | "All components of ground source heat pump systems including pumps, borings, and loops shall be setback at least five feet from all property lines." | Section 4.5.G.1.c(3)(i) - Setbacks | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Setback - Public Water | 25 | feet | "All parts of the heat pump system shall be located a minimum distance of 25 feet from any on-lot or adjacent lot wells." | Section 4.5.G.1.c(3)(iii) - Setbacks | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Maximum Well Depth | 20 | feet | "Depth: All horizontal closed loop systems shall be installed to no more than 20 feet in depth." | Section 4.5.G.1.c(2) - Generally Applicable Standards | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Permit |  |  | "Detailed plans of a vertical system shall be reviewed and approved by the zoning administrator prior to installation." | Section 4.5.G.1.b(2) - Installation of Vertical Systems | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Screening |  |  | "Ground source heat pump systems are considered mechanical equipment and are subject to mechanical screening requirements of the zoning district." | Section 4.5.G.1.c(4) - Screening | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Certification |  |  | "Vertical systems may only be installed by a geothermal installer or vertical closed loop (VCL) driller accredited by the International Ground Source Heat Pump Association (IGSHPA) or installer with an equivalent accreditation or certification from a nationally recognized organization, as determined by the zoning administrator." | Section 4.5.G.1.b(1) - Installation of Vertical Systems | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Decommissioning |  |  | "If the ground source heat pump system remains nonfunctional or inoperative for a continuous period of one year, the system shall be deemed to be abandoned and shall constitute a public nuisance. The property owner shall shut down the system as follows: (1) The heat pump and any external mechanical equipment shall be removed. (2) Pipes or coils beneath the land surface shall be drained and filled with grout. The top of the pipe, coil, or boring shall be uncovered and grouted." | Section 4.5.G.1.d - Abandonment | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Montezuma | Dolores | 820770 | Open-loop Prohibitions |  |  | "Only closed loop ground source heat pump systems utilizing heat transfer fluids are permitted. Open loop ground source heat systems are prohibited." | Section 4.5.G.1.c(1)(i) - Generally Applicable Standards | 2023 | https://townofdolores.colorado.gov/sites/townofdolores/files/documents/Appendix_A___LAND_USE_CODE%20Muni%20Code%20codification.pdf
Colorado | Garfield | Glenwood Springs | 830780 | Screening |  |  | "Ground-mounted mechanical equipment" may "encroach five feet into required side and rear yards provided no element is located closer than two feet from any property line and the equipment complies with screening standards in 070.40.050(f), Screening, Fences, and Walls." | 070.20.190 Measurements and Exceptions (d) Building Height; Table 20.20: Authorized Exceptions to Setback Standards | 2022 | https://www.cogs.us/DocumentCenter/View/3490/New-Development-Code-Adopted-August-2-2018
Colorado | Gunnison | Gunnison | 833640 | Definition: Geothermal Heat Pump |  |  | "Geothermal heating and cooling systems are systems that use buried pipes to exchange heat with the ground, cooling buildings in the summer and warming them in the winter." | OTHER USE STANDARDS § C.2. Geothermal Heating and Cooling Systems | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | 833640 | Setback - Property Lines | 5 | feet | "Closed loop systems (horizontal loop systems and vertical loop systems) are permitted, provided that the loops are contained entirely within the lot and are setback five feet from property lines." | OTHER USE STANDARDS § C.2.a | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | 833640 | Permit |  |  | "Such manifest shall be located at the system and available for inspection and testing by the Public Works Director or designee to ensure the safety of the City's water well systems." | OTHER USE STANDARDS § C.2.e | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | 833640 | Inspection |  |  | "Such manifest shall be located at the system and available for inspection and testing by the Public Works Director or designee to ensure the safety of the City's water well systems." | OTHER USE STANDARDS § C.2.e | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Gunnison | Gunnison | 833640 | Open-loop Prohibitions |  |  | "Open loop systems are prohibited. (Ordinance #8, Series 2021)" | OTHER USE STANDARDS § C.2.f | 2023 | https://cms8.revize.com/revize/gunnisonco/Departments/Planning/Land%20Development%20Code/LDC_04_11_23.pdf
Colorado | Archuleta | Pagosa Springs | 856860 | Definition: Geothermal |  |  | "GEOTHERMAL WATER means the means raw geothermal water produced by the Two Wells." and "GEOTHERMALLY HEATED WATER means non-potable fresh water that is heated in a heat exchanger using water directly from geothermal wells and delivered to Customers." | Section 1-02 DEFINITIONS |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | 856860 | Definition: Geothermal Heat Pump |  |  | "GH SYSTEM means the geothermal heating system which is owned and operated by the Town, consisting of all Facilities, improvements and appurtenances, associated with providing raw Geothermal Water or geothermally heated non-potable fresh water for heating purposes." Also: "GEOTHERMAL SERVICE means the ability of a Customer to receive Geothermal Water or Geothermally Heated Water to a Customer Tap for Customer Uses pursuant to these Regulations." | Section 1-02 DEFINITIONS |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | 856860 | Permit |  |  | "Any Customer desiring to contract to receive Geothermal Water or Geothermally Heated Water for Customer Uses may apply for a Geothermal Water Tap with the Geothermal Department." The Director "shall approve or deny said application within thirty (30) days." Also, "It shall be a violation of these regulations for any person to construct or cause the construction of a Service Line or Tap-in without approval of the Department." | Section 1-03 SERVICE CONNECTION PROCEDURES; Section 1-03 G. Violations |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | 856860 | Inspection |  |  | "Upon completion of the permitted Customer Tap, and prior to covering the Tap-in and any in-ground Facilities, the Customer shall promptly notify the Department to request a service connection inspection." "Upon inspection by the Geothermal Department, Customers may be required to perform additional work... if... the initial Tap-in work and Customer Facilities fail to comply..." "All requests for inspection must be made to the Department at least twenty-four (24) hours in advance." If a customer connects without the Department "first inspecting and approving the construction and Tap-in," the customer must excavate and disconnect so "a proper inspection can be made." | Section 1-03 F. Service Connection Standards and Inspections; Section 1-03 H. Inspection; Section 1-03 I. Failure to Apply or Inspect |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado | Archuleta | Pagosa Springs | 856860 | Other Prohibitions/Regulations |  |  | "Glycol circulated in Pex piping shall be used in all sidewalk, driveway and parking area heating systems. Such systems shall include a heat exchanger and closed loop system..." | Section 1-03.2 Heating of Sidewalks/Driveways/Parking Areas |  | https://www.pagosasprings.co.gov/DocumentCenter/View/279
Colorado |  | Ridgway | 864200 | Permit |  |  | The ordinance imposes permit requirements on mechanical work that would encompass heat pump installation: IMC amendment §106.5.1 states, "Any person who commences any work on a building, structure, electrical, gas, mechanical or plumbing system before obtaining the necessary permits shall be subject to a fee..." and IMC amendment §106.5.2 provides, "The fees for mechanical work, or alterations requiring a permit, shall be derived using Appendix ABL of 202418 International Residential Code." Parallel permit language appears in IRC §R108.6 and IBC §109.2 for work on "mechanical" systems. | Exhibit B, 6-1-3(CD)(3); 6-1-3(CD)(4); 6-1-3(B)(8); 6-1-3(A)(10) | 2026 | https://townofridgway.colorado.gov/sites/g/files/lrnvjt1246/files/documents/Ordinance-No.-03-2026.pdf
Colorado |  | Ridgway | 864200 | Inspection |  |  | IBC amendment §110.5 reads: "It shall be the duty of the holder of the building permit or their duly authorized agent to notify the Building Official when work is ready for inspection. It shall be the duty of the permit holder to provide access to and means for inspections of such work that are required by this code. Inspection requests shall be made a minimum of forty-eight (48) twenty-four hours in advance." In addition, §6-1-2(B) authorizes entry "to inspect or enforce the provisions of this Section and any of the codes adopted herein by reference." | Exhibit B, 6-1-3(A)(156); 6-1-2(B) | 2026 | https://townofridgway.colorado.gov/sites/g/files/lrnvjt1246/files/documents/Ordinance-No.-03-2026.pdf
Colorado |  | Superior | 875640 | Permit |  |  | "Applicable permit fees for the installation of a renewable energy source system, such as solar electric, wind or geothermal, shall be exempt from Town permit fees." | Sec. 18-14-90. - Permit fee. | 2022 | https://townofsuperior.granicus.com/MetaViewer.php?view_id=4&clip_id=2058&meta_id=98287
Connecticut | Capitol | Coventry | 911017800 | Definition: Geothermal |  |  | "Passive Geothermal : A dwelling specifically designed to use natural and architectural components to collect and store the heat of the earth's interior without using any external mechanical power." | Section 2.02 Definitions | 2026 | https://www.coventry-ct.gov/DocumentCenter/View/9347/FINAL-3-28-25-ZONING-REGULATIONS
Connecticut | Capitol | East Windsor | 911024800 | Screening |  |  | "All parking areas not contained within structures shall be appropriately screened and landscaped." | 802.17 PARKING AND ACCESS DRIVES | 2025 | https://portal.ct.gov/-/media/csc/1_dockets-medialibrary/1_media_do500_600/do547/applicantsubmissions/application/2-town-of-east-windsor-zoning-regulations.pdf?rev=590dadec2f244e76b43acc59a0a6f738&hash=8CC873552D0629FDC31B646F4DCE3008
Connecticut | Capitol | Granby | 911032640 | Definition: Geothermal Heat Pump |  |  | "GEOTHERMAL ENERGY SYSTEM: An energy system that utilizes the production of energy from underneath the earth's surface to generate heating and cooling for buildings through the use of ground source heat pumps and underground closed loop piping systems." | Section 1.4 Definitions | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | 911032640 | Setback - Property Lines | 10 | feet | "All system components, including pumps, borings, tanks, and loops shall be setback at least 10 feet from all property lines." | Section 8.29.2.2 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | 911032640 | Permit |  |  | Section 8.29.2.6 states: "A plot plan showing the proposed system, system specifications, and other information as required by the Building Official, shall be submitted with the Building Permit." Section 10.2.1.1 further provides: "It shall be unlawful to commence, for any purpose, the construction or alteration of any building or excavation for any building or structure or to commence any use of land or buildings until the application and plans thereof shall have been approved by the Building Official and a written permit shall have been issued by the Building Official." | Section 8.29.2.6; Section 10.2.1.1 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | 911032640 | Screening |  |  | "Above-ground equipment is considered mechanical equipment and is subject to mechanical screening requirements of the zoning district." | Section 8.29.2.4 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | Granby | 911032640 | Decommissioning |  |  | "All unused systems shall be removed within twelve (12) months of cessation of operations." | Section 8.29.2.5 | 2026 | https://www.granby-ct.gov/DocumentCenter/View/612/Zoning-Regulations-updated-92025-PDF
Connecticut | Capitol | West Hartford | 911082590 | Definition: Geothermal Heat Pump |  |  | "A mechanism for using ground source heat pumps for heating and/or cooling a building which consists of a length of closed underground piping (which may be installed horizontally or vertically) containing heat transfer fluid; a heat exchange mechanism; and an air distribution system. This definition is expressly intended to exclude any form of open loop geothermal system." | § 177-37.3 Alternative energy systems — Definitions | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | West Hartford | 911082590 | Maximum Well Depth | 20 | feet | "Horizontal closed loop systems shall be no more than 20 feet deep." | § 177-37.3 Alternative energy systems — Closed loop geothermal systems | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | West Hartford | 911082590 | Permit |  |  | "The manufacturer specifications shall be submitted as part of the application." | § 177-37.3 Alternative energy systems — Closed loop geothermal systems | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | West Hartford | 911082590 | Open-loop Prohibitions |  |  | "Open loop geothermal systems are prohibited in all zones." | § 177-37.3 Alternative energy systems — Prohibited equipment | 2023 | https://ecode360.com/7295486
Connecticut | Capitol | Windsor | 911087000 | Permit |  |  | "No geothermal system shall be installed or modified without first obtaining a Building Permit." Also, "Geothermal systems utilizing surface waters, wells, or trenches in an area regulated by the Floodplain Ordinance or the Inland Wetlands and Watercourses Commission (IWWC) shall not be installed without a Floodplain Permit or an Inland Wetlands and Watercourses Permit, respectively." | Section 14.1 - Geothermal Energy Facilities, General Requirements | 2022 | https://www.windsorct.gov/DocumentCenter/View/1374/Latest-Annotated-Zoning-Regulations-11-09-22-PDF
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Definition: Geothermal Heat Pump |  |  | "Geothermal Energy System. An energy system that utilizes the production of energy from underneath the Earth’s surface to generate heating and cooling for buildings through the use of ground source heat pumps and underground closed loop piping systems." | Section 2.2 Defined Terms | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Permit |  |  | Section 5.1.B.2 states geothermal systems are allowed and that permitting applies as follows: "Permitted without a Zoning Permit... b. All Closed-Loop Geothermal Energy Systems in all zones." Section 5.1.B.5 adds: "An approval under this Section does not relieve any person of the requirement to obtain other necessary permit approvals if applicable," including wetland, floodplain, or other regulated activities. | Section 5.1.B.2-5 Renewable Energy System Structures | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Inspection |  |  | No geothermal-specific inspection, witness, pressure test, flow test, or final approval inspection requirement is stated in the provided text. | Section 5.1.B Renewable Energy System Structures | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Screening |  |  | The ordinance allows the Town to require submittals including "an A-2 Survey and project narrative showing detailed information, including maps, plans sheets, or dimensioned sketches, showing the proposed location, including setbacks from property lines, adjacent roadways and sight line studies, distances from structures on neighboring properties, and height." | Section 5.1.B.8 Requirements for All Systems | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards." | Section 5.1.B.11 Requirements for Geothermal Energy Systems | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Decommissioning |  |  | No abandonment, plugging, sealing, removal, or restoration requirement for geothermal systems is stated in the provided text. | Section 5.1.B Renewable Energy System Structures | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Cromwell | 913018080 | Other Prohibitions/Regulations |  |  | "Only non-toxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | Section 5.1.B.11 Requirements for Geothermal Energy Systems | 2025 | https://www.cromwellct.gov/DocumentCenter/View/639/Town-of-Cromwell-Zoning-Regulations-Effective-June-2-2025
Connecticut | Lower Connecticut River Valley | Old Saybrook | 913057320 | Permit |  |  | "Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs." Also, "Any person conducting regulated activities that are within the authority of the Commissioner must submit an application or obtain a permit or exemption from the Commissioner prior to engaging in the activity." The definition of "regulated aquifer activity" includes "wastewater discharges to ground water... except discharges from... (iii) a heat pump system" when permitted by the Commissioner. | SECTION 9 Permit Requirements | 2021 | https://www.oldsaybrookct.gov/DocumentCenter/View/977/Aquifer-Protection-Area-Regulations-PDF
Connecticut | Lower Connecticut River Valley | Old Saybrook | 913057320 | Inspection |  |  | "The Agency or its agent may make regular inspections, except at private residences, at reasonable hours, of all regulated activities for which permits or registrations have been issued by these regulations." | SECTION 14 Enforcement | 2021 | https://www.oldsaybrookct.gov/DocumentCenter/View/977/Aquifer-Protection-Area-Regulations-PDF
Connecticut | Naugatuck Valley | Oxford | 914058300 | Permit |  |  | The ordinance includes a heat-pump-specific permit carve-out within the definition of regulated activity: wastewater discharges to groundwater are regulated, except for discharges from a "Heat pump system" that "have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes." It also states generally that "All regulated activities are prohibited in aquifer protection areas, except" a regulated activity that "has received a permit issued pursuant to §22a-354i-8 ... or Section 9 of the APA Regulations." | SECTION 2. DEFINITIONS; SECTION 4. PROHIBITED AND REGULATED ACTIVITIES; SECTION 9. PERMIT REQUIREMENTS | 2010 | https://www.oxford-ct.gov/DocumentCenter/View/329/town_of_oxford_apa_regulations_approved_010908_lsrevised2_18_10
Connecticut | Naugatuck Valley | Oxford | 914058300 | Other Prohibitions/Regulations |  |  | "All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (B) of this section." In the definitions, regulated activities include "Wastewater discharges to ground water other than domestic sewage and stormwater," except for certain permitted systems including a "Heat pump system" that has received a permit from the Commissioner. | SECTION 4. PROHIBITED AND REGULATED ACTIVITIES | 2010 | https://www.oxford-ct.gov/DocumentCenter/View/329/town_of_oxford_apa_regulations_approved_010908_lsrevised2_18_10
Connecticut | Naugatuck Valley | Watertown | 914080490 | Permit |  |  | "Groundwater heat pumps supplying heating and cooling for other than a detached single-family residence" are "only permitted in the APOZ subject to Special Permit approval in accordance with Section 8.4 and Site Plan approval in accordance with Section 8.3," and such systems are allowed only if "restricted to closed-loop types." | Section 4.1.E.22 - Aquifer Protection Overlay Zone, Special Permit Uses | 2024 | https://www.watertownct.org/Documents/Government/Agendas%20and%20Minutes/Planning%20and%20Zoning%20Commission/2026/Minutes/Watertown%20ZR%20-%20Adopted%20-%20Effective%20123024%20CL2.pdf?t=202604100051420
Connecticut | Naugatuck Valley | Watertown | 914080490 | Screening |  |  | Business districts: "Building mechanical equipment located outside the principal structure, including radio and television reception equipment, provided that such equipment shall be properly screened." Industrial districts: "Building mechanical equipment located outside the structure provided that such equipment shall be properly screened." ARH overlay: "Mechanical equipment and refuse containers shall be screened from view on at least three sides and to the satisfaction of the Commission on all sides." DRD overlay: "Mechanical equipment and refuse containers shall be screened from view on at least three sides and to the satisfaction of the Commission on all sides." | Section 2.3 Accessory Uses and Structures; Section 3.3 Accessory Uses And Structures; Section 4.3.F.54; Section 4.5.E.107 | 2024 | https://www.watertownct.org/Documents/Government/Agendas%20and%20Minutes/Planning%20and%20Zoning%20Commission/2026/Minutes/Watertown%20ZR%20-%20Adopted%20-%20Effective%20123024%20CL2.pdf?t=202604100051420
Connecticut | Naugatuck Valley | Watertown | 914080490 | Open-loop Prohibitions |  |  | In the APOZ, "Groundwater heat pumps supplying heating and cooling for other than a detached single-family residence" are allowed only if "restricted to closed-loop types." | Section 4.1.E.22 - Aquifer Protection Overlay Zone, Special Permit Uses | 2024 | https://www.watertownct.org/Documents/Government/Agendas%20and%20Minutes/Planning%20and%20Zoning%20Commission/2026/Minutes/Watertown%20ZR%20-%20Adopted%20-%20Effective%20123024%20CL2.pdf?t=202604100051420
Connecticut | Northeastern Connecticut | Plainfield | 915059980 | Permit |  |  | Section 4(a) states: "All regulated activities are prohibited in aquifer protection areas, except as specified in Subsection (b) of this Section." Section 4(b)(2) then provides that a regulated activity is not prohibited if it "has received a permit issued pursuant to §22a‐354i‐8 of the Regulations of Connecticut State Agencies or Section 9 of the APA Regulations." In the definition of "Regulated activity," Section 2(a)(35)(F) includes "wastewater discharges to ground water other than domestic sewage and stormwater, except for discharges from the following that have received a permit from the Commissioner pursuant to §22a‐430 of the Connecticut General Statutes: ... (iii) heat pump system." | SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2012 | https://www.plainfieldct.org/Document%20Center/Department/Planning%20&%20Zoning/Regulations%20&%20Ordinances/aquiferprotectionregs.pdf?t=202104021433310
Connecticut | Northeastern Connecticut | Plainfield | 915059980 | Inspection |  |  | Section 12(a)(5)(A)(iv) requires "a record‐keeping system" for hazardous materials and states that "such record‐keeping system shall be maintained at the subject facility and shall be made available thereat for inspection during normal business hours by the Commissioner and the municipal aquifer protection agency." Section 12(a)(5)(C) likewise states that "the materials management plan shall be maintained at the subject facility and shall be made available thereat for inspection during normal business hours by the Commissioner and the municipal aquifer protection agency." | SECTION 12. Best Management Practices | 2012 | https://www.plainfieldct.org/Document%20Center/Department/Planning%20&%20Zoning/Regulations%20&%20Ordinances/aquiferprotectionregs.pdf?t=202104021433310
Connecticut | South Central Connecticut | Bethany | 917004580 | Permit |  |  | "Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs." Also, "The Agency shall process permit applications for those registrants that have registered pursuant to section 8 of the APA Regulations..." and under the definition of regulated activity, wastewater discharges from a "heat pump system" are listed as a regulated activity exception only when they "have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes." | SECTION 9. Permit Requirements | 2022 | https://bethanyct.gov/filestorage/216/228/288/3270/TOWN-OF-BETHANY-ZONING-REGULATIONS-EFFECTIVE-_October_10%2C_2022.pdf
Connecticut | South Central Connecticut | Bethany | 917004580 | Inspection |  |  | "The Agency may impose reasonable conditions or limitations on any permit issued under this section to assure protection of the ground water, including, but not limited to... ground water monitoring." Also, materials management plan records "shall be made available thereat for inspection during normal business hours by the Commissioner and the municipal aquifer protection agency." | SECTION 14. Enforcement / SECTION 9. Permit Requirements | 2022 | https://bethanyct.gov/filestorage/216/228/288/3270/TOWN-OF-BETHANY-ZONING-REGULATIONS-EFFECTIVE-_October_10%2C_2022.pdf
Connecticut | South Central Connecticut | Bethany | 917004580 | Other Prohibitions/Regulations |  |  | "All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section." The ordinance definition of "regulated activity" includes wastewater discharges to groundwater, except for discharges from certain systems, including a "heat pump system," that "have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes." | SECTION 4. Prohibited and Regulated Activities | 2022 | https://bethanyct.gov/filestorage/216/228/288/3270/TOWN-OF-BETHANY-ZONING-REGULATIONS-EFFECTIVE-_October_10%2C_2022.pdf
Connecticut | South Central Connecticut | Wallingford | 917078740 | Permit |  |  | "Regulated Activity" includes "wastewater discharges to ground water other than domestic sewage and stormwater, except for discharges from the following that have received a permit issued by the Commissioner pursuant to Section 22a-430 of the Connecticut General Statutes: ... (iii) heat pump system." Section 4 states: "All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section," and subsection (b) allows "a regulated activity which has received a permit issued pursuant to §22a-354i-8 ... or Section 9 of the APA Regulations." Section 9(a) provides: "Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs." | SECTION 2. Definitions; SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2009 | https://www.wallingfordct.gov/customer-content/www/CMS/files//PZAPARegs41615.pdf
Connecticut | Southeastern Connecticut | East Lyme | 918023400 | Permit |  |  | Section 2(a)(35)(F) includes as a regulated activity 'wastewater discharges to ground water other than domestic sewage and storm water, except for discharges from the following that have received a permit from the Commissioner pursuant to §22a-430 of the Connecticut General Statutes: ... (iii) heat pump system ...'. Section 4(a) states: 'All regulated activities are prohibited in aquifer protection areas, except as specified in Subsection (b) of this Section.' Section 4(b)(2) allows 'A regulated activity which has received a permit issued pursuant to §22a-354i-8 of the Regulations of Connecticut State Agencies or Section 9 of the APA Regulations.' Section 9(a) states: 'Any person may apply for a permit to add a regulated activity to a facility where a registered regulated activity occurs.' | SECTION 2. Definitions; SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2012 | https://eltownhall.com/wp-content/uploads/Aquifer-Protection-Regulations-effective-December-14-2012.pdf
Connecticut | Southeastern Connecticut | Windham | 918086790 | Inspection |  |  | "the Formal Application under these Regulations shall constitute authorization for the Commission to enter upon the property to obtain additional information or to inspect proposed improvements" and "The Commission may perform an official Site Inspection prior to or during the statutory review period." | Section 4.1.15; Section 4.3.4 | 2014 | https://windhamct.gov/DocumentCenter/View/1768/Subdivision-Regulations-Effective-August-9-2014
Connecticut | Western Connecticut | Greenwich | 919033620 | Permit |  |  | Site plan applications must include "[t]wo copies of a brief narrative addressing ... (B) The potential and use of renewable energy systems, as well as highly energy efficient equipment such as air and ground source heat pumps, hot water heat pumps and fuel cells." | Sec. 6-14(c)(22) | 2023 | https://www.greenwichct.gov/DocumentCenter/View/37847/2023-Building-Zone-Regulations
Connecticut | Western Connecticut | Ridgefield | 919063970 | Definition: Geothermal Heat Pump |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards." | Section 7.16.H - Requirements for Geothermal Energy Systems | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Ridgefield | 919063970 | Permit |  |  | "Permitted (without a Zoning Permit): ... b. All closed-loop geothermal energy systems in all zones." | Section 7.16.D - Permits Required | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Ridgefield | 919063970 | Certification |  |  | "The design and installation of geothermal systems and related boreholes for geothermal heat pump systems shall conform to applicable industry standards." | Section 7.16.H - Requirements for Geothermal Energy Systems | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Ridgefield | 919063970 | Open-loop Prohibitions |  |  | Section 7.16.D permits only "All closed-loop geothermal energy systems in all zones" without a zoning permit, and Section 7.16.H regulates "All closed-loop geothermal systems" and requires that "Only non-toxic, biodegradable circulating fluids such as food grade propylene glycol shall be permitted." | Section 7.16.D and 7.16.H | 2021 | https://www.ridgefieldct.org/sites/g/files/vyhlif4916/f/uploads/11.5.2021_regs_07_rev_parking_legislation.pdf
Connecticut | Western Connecticut | Sherman | 919068310 | Definition: Geothermal |  |  | "Energy Efficient Designed Dwellings — Dwellings which have been designed to harness wind, sun, and/or geothermal heat sources to provide primary or supplemental energy to such dwelling." | SECTION 610. DEFINITIONS | 2026 | https://municipal-documents.s3.amazonaws.com/uploads/sherman-ct/planning-zoning/documents/regulations/154750/ZONING%20REGULATIONS%20Last%20amended%20May%201%202026.pdf
Connecticut | Western Connecticut | Sherman | 919068310 | Definition: Geothermal Heat Pump |  |  | "Energy Efficient Structures — Wind powered generators, solar panel arrays, geothermal wells and pumps, and other structures which are designed and used to provide primary or supplemental energy as an accessory to a permitted principal use: does not include energy production facilities as a principal use." | SECTION 610. DEFINITIONS | 2026 | https://municipal-documents.s3.amazonaws.com/uploads/sherman-ct/planning-zoning/documents/regulations/154750/ZONING%20REGULATIONS%20Last%20amended%20May%201%202026.pdf
Connecticut | Western Connecticut | Wilton | 919086370 | Permit |  |  | 'Groundwater heat pumps supplying heating and cooling for other than a detached single-family residence' are 'permitted subject to Special Permit and Site Plan approvals in accordance with 29-10 and 29-11,' provided 'such systems shall be designed to treat, if necessary, and return discharged water to the groundwater.' | Section 29-9.D.4.c Special Permit Uses | 2019 | https://www.wiltonct.gov/sites/g/files/vyhlif10026/f/uploads/zoning_regs_revised_jun_25_2019_updated_app_b_0.pdf
Connecticut | Naugatuck Valley | Naugatuck | 949880 | Permit |  |  | Section 4(a) states: 'All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section.' Section 4(b)(2) then provides an exception for 'a regulated activity which has received a permit issued pursuant to §22a-354i-8 of the Regulations of Connecticut State Agencies or section 9 of the APA Regulations.' In the definition of 'Regulated activity,' Section 2(a)(35)(F) includes 'wastewater discharges to ground water other than domestic sewage and storm water, except for discharges from the following that have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes: ... (iii) heat pump system ...' | SECTION 4. Prohibited and Regulated Activities; SECTION 9. Permit Requirements | 2006 | https://www.naugatuck-ct.gov/filestorage/166/237/239/Final_Aquifer_Protection_Regulations.pdf
Connecticut | Naugatuck Valley | Naugatuck | 949880 | Other Prohibitions/Regulations |  |  | Section 4(a) provides: 'All regulated activities are prohibited in aquifer protection areas, except as specified in subsection (b) of this section.' Section 2(a)(35)(F) defines one regulated activity as 'wastewater discharges to ground water other than domestic sewage and storm water,' while carving out only specified discharges that 'have received a permit from the Commissioner pursuant to section 22a-430 of the Connecticut General Statutes,' including '(iii) heat pump system.' | SECTION 4. Prohibited and Regulated Activities | 2006 | https://www.naugatuck-ct.gov/filestorage/166/237/239/Final_Aquifer_Protection_Regulations.pdf

## Column Descriptions
Column | Description
State | Name of state
County | Name of county
Subdivision | Name of subdivision
Jurisdiction Type | String representation of the type of jurisdiction
County Subdivision FIPS Code | FIPS code for the subdivison pulled from the U.S. Census Bureau
Feature | The kind of ordinance that was extracted
Value | Numerical value for the extracted ordinance
Units | Units corresponding to the numerical ordinance value
Summary | Brief summary of the ordinance text. For qualitative ordinances, this is the only field that is extracted
Section | Section from which ordinance value/text was retrieved
Ordinance Year | Latest year that the ordinance was enacted or amended or became effective
Source URL | URL from which the ordinance document was retrieved

## Ordinance Types
Feature | Description
Setback - Driveways | Minimum required separation from driveways or drive areas
Setback - Property Lines | Minimum required separation from property lines, lot lines, or parcel boundaries when the ordinance text explicitly states the setback is measured from that boundary
Setback - Yards | Minimum required separation from front yard, side yard, rear yard, or similar yard-based setback areas
Setback - Private Water | Minimum required separation from private water supplies, such as drinking water wells or private water supplies
Setback - Public Water | Minimum required separation from public water supply wells, intakes, or related infrastructure
Setback - Building Foundation | Minimum required separation from building or structure foundations
Setback - Wastewater | Minimum required separation from any wastewater-related infrastructure, including: (a) traditional onsite systems such as septic tanks, aerobic/holding tanks, leach fields, subsurface sewage disposal systems, elevated sand mounds, sewage seepage pits, and cesspools; and (b) land-application wastewater such as spray irrigation sites, sewage sludge disposal sites, and septage disposal sites
Setback - Water Lines | Minimum required separation from water service lines and related service piping
Setback - Sewer Lines | Minimum required separation from sanitary/storm sewer lines
Setback - Animal Enclosures | Minimum required separation from animal enclosures, barns, pens, corrals, stables, feedlots, or similar livestock areas
Setback - Roads | Minimum required separation from public road rights-of-way
Setback - Right of Way | Minimum required separation from any right-of-way or utility/drainage/access easements not already captured under road right-of-way
Setback - Fuel (above ground) | Minimum required separation from above-ground fuel tanks or storage areas
Setback - Fuel (below ground) | Minimum required separation from underground fuel tanks or storage areas
Setback - Subsurface Drains | Minimum required separation from subsurface drains, tile drains, or underdrain systems
Setback - Water Bodies | Minimum required separation from streams, springs, lakes, ponds, rivers, floodplains, wetlands, or other surface waters
Setback - Pools | Minimum required separation from swimming pools, spas, or similar water recreation structures
Setback - Hazardous Materials/Fertilizers | Minimum required separation from hazardous materials storage/handling areas, chemical storage/handling areas, or fertilizer storage/handling areas
Noise Limits | Maximum allowable operational noise for GHP systems
Minimum Well Depth | Minimum depth requirement for GHP boreholes/wells
Maximum Well Depth | Maximum depth limits or depth-related requirements for GHP boreholes/wells
Definition: Well | Ordinance definition text for 'Geothermal Well' (or equivalent term)
Definition: Geothermal | Ordinance definition text for 'Geothermal'
Definition: Geothermal Heat Pump | Ordinance definition text for 'ground source heat pump system', 'geothermal heat pump system', or equivalent term
Licensed Driller | A drilling-specific credential requirement for the GHP drilling activity (i.e. to be performed by a licensed well or otherwise credentialed driller)
Certification | Required driller certification, accreditation, license class, or professional credential
Screening | Requirements for visual or physical concealment of above-ground geothermal equipment (i.e. barriers, screening, fences, walls, landscaping, berms, opaque enclosures, parapets, louvers, or screening panels)
Permit | Permit requirements governing GHP installation, drilling, or operation (i.e. mechanical, geothermal well, environmental, zoning, or health approvals), including triggering conditions
Inspection | Requirements for inspection, witnessing, approval visit, or mandated pressure/flow or similar compliance test tied to GHP drilling, installation, or operation
Decommissioning | Requirements for abandonment, plugging, sealing, removal, and/or site restoration when GHP systems are retired, fail, or wells are abandoned
Closed-loop Prohibitions | Prohibitions or moratoria for construction, installation, siting, or deploymenton of closed-loop geothermal systems
Open-loop Prohibitions | Prohibitions or moratoria for construction, installation, siting, or deploymenton of open-loop geothermal systems
Other Prohibitions/Regulations | Catchall for other geothermal-related prohibitions or moratoria on construction, installation, siting, or deployment not captured above (i.e. standing-column well bans, vertical borefield bans, district-specific bans, proximity or location-based band, or explicit bans on a geothermal installation method)