## Averaged Data
Date/Time | Total Net Power Output (Calcuated) | Gross Power Output (Veris) | Pump Parasitic Load | Cooling Fan Parasitic Load (Calculated) | Geothermal Header Hot Water Temperature | Hot Water Supply Temperature | Hot Water Return Temperature | Hot Water Supply Flow Rate | Ambient Temperature (GM Sensor) | MESO West Weather Data Station ID: HMHNV | Date/Time | Ambient Temperature | Relative Humidity | Wind Speed | Wind Gust | Wind Direction | Dew Point
| kW | kW | kW | kW | F | F | F | gpm | F |  |  | F | % | mph | mph | Degrees | F
5/9/2013 17:00:06 to 5/9/2013 17:59:56 | 35.992 | 45.319 | 2.3908 | 6.9362 | 225.7456 | 223.3347 | 195.7572 | 134.6206 | 81.3042 |  | 5-9-2013 17:25 PDT | 78 | 15 | 14 | 22 | 11 | 37.8
5/9/2013 18:00:06 to 5/9/2013 18:59:56 | 37.7366 | 47.0727 | 2.4 | 6.9362 | 226.0575 | 223.6214 | 195.2986 | 134.0186 | 78.2375 |  | 5-9-2013 18:23 PDT | 72.9 | 23 | 7.2 | 10.7 | 346 | 41.8
5/9/2013 19:00:06 to 5/9/2013 19:59:56 | 39.1923 | 48.5284 | 2.4 | 6.9362 | 226.4283 | 224.1744 | 195.4419 | 134.7878 | 75.2528 |  | 5-9-2013 19:23 PDT | 69.8 | 30 | 4.9 | 10.1 | 339 | 44.4
5/9/2013 20:00:06 to 5/9/2013 20:59:56 | 39.4047 | 48.7409 | 2.4 | 6.9362 | 226.3661 | 224.1075 | 195.2228 | 134.7347 | 71.2531 |  | 5-9-2013 20:34 PDT | 66 | 32 | 8 | 11 | 93 | 42.4
5/9/2013 23:00:06 to 5/9/2013 23:58:56 | 40.7911 | 50.9273 | 3.2 | 6.9362 | 226.9373 | 224.7641 | 194.9777 | 134.5212 | 68.0427 |  | 5-9-2013 23:22 PDT | 61 | 40 | 3 | 5 | 339 | 42.3
5/10/2013 00:01:06 to 5/10/2013 01:00:56 | 41.2456 | 51.3817 | 3.2 | 6.9362 | 226.7572 | 224.7075 | 194.7703 | 134.5253 | 67.2822 |  | 5-10-2013 0:25 PDT | 57 | 50 | 3 | 5 | 52 | 43
5/10/2013 01:01:06 to 5/10/2013 02:00:56 | 42.7322 | 52.8683 | 3.2 | 6.9362 | 226.8606 | 224.7467 | 194.3028 | 134.5992 | 65.0564 |  | 5-10-2013 1:28 PDT | 54 | 56 | 4 | 7 | 353 | 42.5
5/10/2013 02:01:06 to 5/10/2013 03:00:56 | 42.3424 | 52.4786 | 3.2 | 6.9362 | 226.8411 | 224.7731 | 194.5525 | 134.5736 | 61.0389 |  | 5-10-2013 2:31 PDT | 54 | 56 | 5 | 7 | 193 | 42.5
5/10/2013 03:01:06 to 5/10/2013 04:00:56 | 41.6967 | 51.8329 | 3.2 | 6.9362 | 226.7739 | 224.7178 | 194.9592 | 134.6475 | 62.9181 |  | 5-10-2013 3:34 PDT | 53 | 56 | 3 | 4 | 48 | 41.5
5/10/2013 04:01:06 to 5/10/2013 05:00:56 | 43.5015 | 53.6376 | 3.2 | 6.9362 | 227.0467 | 225.0114 | 194.5039 | 134.5458 | 60.4733 |  | 5-10-2013 4:37 PDT | 49 | 66 | 2 | 3 | 42 | 40.9
5/10/2013 05:01:06 to 5/10/2013 06:00:56 | 43.1274 | 53.2635 | 3.2 | 6.9362 | 226.7508 | 224.8608 | 194.5231 | 134.6033 | 57.4111 |  | 5-10-2013 5:23 PDT | 46.4 | 73 | 2.5 | 5.6 | 11 | 40.3
5/10/2013 06:01:06 to 5/10/2013 07:00:56 | 41.0614 | 51.1976 | 3.2 | 6.9362 | 226.4372 | 224.5439 | 195.6297 | 134.5817 | 63.7911 |  | 5-10-2013 6:22 PDT | 55 | 53 | 7 | 9 | 32 | 42.3
5/10/2013 07:01:06 to 5/10/2013 08:00:56 | 40.3705 | 50.5067 | 3.2 | 6.9362 | 226.5508 | 224.5331 | 196.5075 | 134.3953 | 74.575 |  | 5-10-2013 7:25 PDT | 60 | 43 | 5 | 8 | 11 | 42.8
5/10/2013 08:01:06 to 5/10/2013 09:00:56 | 38.9861 | 49.1223 | 3.2 | 6.9362 | 226.525 | 224.3828 | 196.0228 | 131.3442 | 81.8739 |  | 5-10-2013 8:28 PDT | 66 | 33 | 8 | 12 | 357 | 43
5/10/2013 09:01:06 to 5/10/2013 10:00:56 | 38.443 | 48.5791 | 3.2 | 6.9362 | 226.5347 | 224.2017 | 193.4433 | 127.0892 | 84.7108 |  | 5-10-2013 9:31 PDT | 70 | 29 | 11 | 14 | 326 | 43.9
5/10/2013 10:01:06 to 5/10/2013 11:00:56 | 36.0643 | 46.2005 | 3.2 | 6.9362 | 226.7642 | 224.2825 | 194.4283 | 127.0436 | 87.1578 |  | 5-10-2013 10:34 PDT | 74 | 25 | 6 | 14 | 354 | 44.3
5/10/2013 11:01:06 to 5/10/2013 12:00:56 | 36.4465 | 46.5827 | 3.2 | 6.9362 | 227.1861 | 224.7789 | 194.4894 | 126.9114 | 89.1775 |  | 5-10-2013 11:37 PDT | 78 | 20 | 4 | 13 | 356 | 43.2
5/13/2013 12:00:06 to 5/13/2013 12:59:56 | 30.3119 | 42.1752 | 2.3 | 9.5632 | 225.4981 | 223.4008 | 195.4467 | 131.5183 | 88.0122 |  | 5-13-2013 12:24 PDT | 86 | 12 | 12 | 26 | 205 | 39.6
5/13/2013 13:00:06 to 5/13/2013 13:59:56 | 29.4806 | 41.3439 | 2.3 | 9.5632 | 225.9542 | 223.9356 | 196.5917 | 131.5186 | 91.4786 |  | 5-13-2013 13:27 PDT | 88 | 11 | 14 | 26 | 215 | 39.5
5/13/2013 16:00:02 to 5/13/2013 16:59:52 | 30.7123 | 42.3748 | 2.0992 | 9.5632 | 226.28 | 223.5353 | 195.4783 | 130.8511 | 89.1947 |  | 5-13-2013 16:28 PDT | 87 | 11 | 16 | 32 | 237 | 38.7
5/13/2013 17:00:02 to 5/13/2013 17:59:52 | 31.1199 | 42.7831 | 2.1 | 9.5632 | 226.1575 | 223.2822 | 195.3117 | 130.9417 | 87.1869 |  | 5-13-2013 17:32 PDT | 86 | 11 | 18 | 28 | 230 | 38
5/13/2013 18:00:02 to 5/13/2013 18:59:52 | 31.4127 | 43.076 | 2.1 | 9.5632 | 226.2522 | 223.4108 | 195.6086 | 130.8253 | 85.5847 |  | 5-13-2013 18:26 PDT | 85 | 11 | 16 | 24 | 226 | 37.3
5/13/2013 19:00:02 to 5/13/2013 19:59:52 | 33.8028 | 45.6419 | 2.2758 | 9.5632 | 226.5503 | 223.81 | 194.8822 | 130.1458 | 82.1425 |  | 5-13-2013 19:29 PDT | 80 | 12 | 13 | 19 | 240 | 35.2
5/13/2013 20:00:02 to 5/13/2013 20:59:52 | 34.6643 | 46.7584 | 2.5308 | 9.5632 | 226.9119 | 224.4372 | 194.9222 | 129.8556 | 78.0225 |  | 5-13-2013 20:43 PDT | 75.4 | 12 | 6 | 10.3 | 213 | 31.8
5/13/2013 21:00:02 to 5/13/2013 21:59:52 | 34.6692 | 47.0324 | 2.8 | 9.5632 | 226.8392 | 224.4014 | 195.0142 | 130.5894 | 75.6267 |  | 5-13-2013 21:26 PDT | 72 | 14 | 7 | 10 | 203 | 32
5/13/2013 22:00:02 to 5/13/2013 22:59:52 | 35.0668 | 48.0136 | 3.3836 | 9.5632 | 226.8942 | 224.5558 | 194.3783 | 130.5167 | 74.3736 |  | 5-13-2013 22:38 PDT | 69 | 15 | 5 | 8 | 191 | 30.9
5/13/2013 23:00:02 to 5/13/2013 23:58:52 | 36.232 | 49.3953 | 3.6 | 9.5632 | 226.7336 | 224.5277 | 194.1331 | 130.4393 | 72.5088 |  | 5-13-2013 23:32 PDT | 67 | 26 | 3 | 6 | 41 | 39.3
5/14/2013 00:00:22 to 5/14/2013 00:59:52 | 37.0913 | 50.2545 | 3.6 | 9.5632 | 226.8958 | 224.6631 | 194.0366 | 130.433 | 71.5737 |  | 5-14-2013 0:26 PDT | 66 | 32 | 3 | 7 | 90 | 42.4
5/14/2013 01:00:02 to 5/14/2013 01:59:52 | 37.9534 | 51.1167 | 3.6 | 9.5632 | 227.1308 | 224.8897 | 193.8131 | 130.3364 | 70.8633 |  | 5-14-2013 1:39 PDT | 61 | 42 | 3 | 5 | 128 | 43.3
5/14/2013 02:00:02 to 5/14/2013 02:59:52 | 37.4347 | 50.5979 | 3.6 | 9.5632 | 227.2911 | 225.0211 | 194.1981 | 130.2511 | 69.6781 |  | 5-14-2013 2:24 PDT | 58 | 49 | 1 | 3 | 154 | 43.5
5/14/2013 03:00:02 to 5/14/2013 03:59:52 | 38.103 | 51.2662 | 3.6 | 9.5632 | 227.255 | 225.0389 | 194.0503 | 130.2047 | 68.4344 |  | 5-14-2013 3:23 PDT | 55.9 | 53 | 0.9 | 2.9 | 151 | 43.1
5/14/2013 04:00:02 to 5/14/2013 04:59:52 | 39.2648 | 52.4281 | 3.6 | 9.5632 | 227.0756 | 224.8836 | 193.2567 | 130.1575 | 65.5969 |  | 5-14-2013 4:23 PDT | 54.9 | 53 | 0.4 | 3.6 | 128 | 42.2
5/14/2013 05:00:02 to 5/14/2013 05:59:52 | 39.6921 | 52.8554 | 3.6 | 9.5632 | 227.0989 | 224.9253 | 193.1117 | 130.0425 | 63.2961 |  | 5-14-2013 6:03 PDT | 53.1 | 59 | 0 | 0.7 | 56 | 42.6
5/14/2013 06:00:02 to 5/14/2013 06:59:52 | 38.5496 | 51.7128 | 3.6 | 9.5632 | 226.9472 | 224.7803 | 193.9922 | 130.0342 | 66.5861 |  | 5-14-2013 6:46 PDT | 58 | 50 | 3 | 5 | 32 | 43.9
5/14/2013 07:00:02 to 5/14/2013 07:59:52 | 39.6838 | 52.847 | 3.6 | 9.5632 | 227.2419 | 225.0022 | 193.3047 | 130.1311 | 79.9597 |  | 5-14-2013 7:31 PDT | 62 | 39 | 1 | 3 | 4 | 42.7
5/14/2013 08:00:02 to 5/14/2013 08:59:52 | 38.0223 | 51.1856 | 3.6 | 9.5632 | 227.2528 | 224.9633 | 194.1942 | 130.0233 | 84.7428 |  | 5-14-2013 8:25 PDT | 66 | 36 | 1 | 5 | 347 | 44.7
5/14/2013 09:00:02 to 5/14/2013 09:59:52 | 34.7556 | 47.8822 | 3.5633 | 9.5632 | 227.4522 | 225.0492 | 197.0831 | 130.0208 | 92.5358 |  | 5-14-2013 9:37 PDT | 75 | 25 | 1 | 6 | 23 | 45.1
5/14/2013 10:00:02 to 5/14/2013 10:59:52 | 34.6412 | 47.7045 | 3.5 | 9.5632 | 227.52 | 225.0744 | 195.0403 | 129.8869 | 93.3175 |  | 5-14-2013 10:32 PDT | 79 | 14 | 7 | 12 | 206 | 37.3
5/28/2013 14:00:03 to 5/28/2013 14:59:53 | 40.1569 | 46.3913 | 2.9 | 3.3344 | 226.805 | 224.87 | 196.9928 | 129.5136 | 70.3528 |  | 5-28-2013 14:43 PDT | 63.3 | 32 | 10.1 | 18.1 | 275 | 40.1
5/28/2013 15:00:03 to 5/28/2013 15:59:53 | 41.454 | 47.8584 | 3.0083 | 3.3961 | 226.9356 | 225.0231 | 195.5631 | 129.1928 | 70.6147 |  | 5-28-2013 15:26 PDT | 62 | 32 | 6 | 12 | 246 | 39
5/28/2013 16:00:03 to 5/28/2013 16:59:53 | 39.3811 | 45.9309 | 3.1 | 3.4498 | 226.985 | 225.0175 | 197.38 | 128.2161 | 72.0725 |  | 5-28-2013 16:29 PDT | 66 | 27 | 7 | 13 | 316 | 39.2
5/28/2013 17:00:03 to 5/28/2013 17:59:53 | 40.3719 | 46.8364 | 3.1 | 3.3645 | 226.9344 | 224.8572 | 194.0469 | 124.3219 | 72.2772 |  | 5-28-2013 17:32 PDT | 67 | 24 | 6 | 11 | 265 | 37.8
5/28/2013 18:00:03 to 5/28/2013 18:59:53 | 40.1781 | 46.5636 | 3.1 | 3.2855 | 227.0067 | 224.8353 | 194.0761 | 124.9172 | 70.9489 |  | 5-28-2013 18:35 PDT | 67 | 24 | 6 | 13 | 263 | 37.8
5/28/2013 19:00:03 to 5/28/2013 19:59:53 | 40.6813 | 46.9612 | 3.1 | 3.18 | 226.9367 | 224.8931 | 193.9369 | 124.7575 | 68.9161 |  | 5-28-2013 19:23 PDT | 64.2 | 26 | 3.6 | 7.4 | 272 | 37
5/28/2013 20:00:03 to 5/28/2013 20:59:53 | 41.1495 | 47.3854 | 3.1 | 3.1359 | 227.0164 | 225.0664 | 194.2492 | 124.8286 | 66.0958 |  | 5-28-2013 20:23 PDT | 56.1 | 44 | 1.1 | 3.4 | 78 | 39.8
5/28/2013 21:00:03 to 5/28/2013 21:59:53 | 42.411 | 48.3384 | 3.1 | 2.8274 | 226.9036 | 224.8489 | 193.3575 | 124.9761 | 61.3931 |  | 5-28-2013 21:23 PDT | 54 | 48 | 7 | 9 | 102 | 39.5
5/28/2013 22:00:03 to 5/28/2013 22:59:53 | 42.4008 | 48.4579 | 3.1 | 2.9571 | 227.0953 | 225.1328 | 193.9622 | 124.8375 | 61.0408 |  | 5-28-2013 22:27 PDT | 52 | 52 | 2 | 3 | 186 | 39.2
5/28/2013 23:00:03 to 5/28/2013 23:58:53 | 43.0419 | 49.0665 | 3.1 | 2.9245 | 226.8994 | 225.0356 | 193.8398 | 124.8932 | 58.6201 |  | 5-28-2013 23:30 PDT | 47 | 63 | 2 | 4 | 309 | 38.2
5/29/2013 00:00:33 to 5/29/2013 00:59:53 | 44.3852 | 50.4759 | 3.1 | 2.9907 | 227.0555 | 225.2003 | 193.0465 | 124.8431 | 57.3936 |  | 5-29-2013 0:33 PDT | 46 | 64 | 2 | 5 | 357 | 37.5
5/29/2013 01:00:03 to 5/29/2013 01:59:53 | 42.4649 | 48.3514 | 3.3969 | 2.4895 | 226.3114 | 224.4364 | 193.0058 | 125.1611 | 54.8514 |  | 5-29-2013 1:36 PDT | 46 | 67 | 7 | 13 | 174 | 38.4
5/29/2013 02:00:03 to 5/29/2013 02:59:53 | 40.8376 | 46.8603 | 3.6 | 2.4227 | 226.3156 | 224.3256 | 193.4072 | 125.0756 | 55.7258 |  | 5-29-2013 2:23 PDT | 53.2 | 45 | 7.6 | 12.3 | 182 | 37.6
5/29/2013 03:00:03 to 5/29/2013 03:59:53 | 40.7542 | 46.9748 | 3.6 | 2.6206 | 226.5489 | 224.6311 | 195.0306 | 125.085 | 56.5903 |  | 5-29-2013 3:21 PDT | 46 | 66 | 3 | 7 | 241 | 38.1
5/29/2013 04:00:03 to 5/29/2013 04:59:53 | 41.2222 | 47.5371 | 3.6 | 2.7149 | 226.4492 | 224.5903 | 194.8558 | 124.9814 | 55.8547 |  | 5-29-2013 4:24 PDT | 49 | 61 | 5 | 10 | 206 | 39.4
5/29/2013 05:00:03 to 5/29/2013 05:59:53 | 41.4045 | 47.5493 | 3.6 | 2.5448 | 226.1306 | 224.1433 | 193.1933 | 125.06 | 54.5039 |  | 5-29-2013 5:27 PDT | 53 | 54 | 8 | 15 | 188 | 40.8
5/29/2013 06:00:03 to 5/29/2013 06:59:53 | 40.1161 | 46.3855 | 3.6 | 2.6694 | 225.8622 | 223.8725 | 193.5347 | 125.2517 | 58.7608 |  | 5-29-2013 6:30 PDT | 56 | 50 | 14 | 22 | 171 | 42.1
5/29/2013 07:00:03 to 5/29/2013 07:59:53 | 39.3872 | 45.872 | 3.5667 | 2.9182 | 225.9753 | 223.9156 | 195.0133 | 125.0117 | 60.7819 |  | 5-29-2013 7:33 PDT | 55 | 54 | 14 | 19 | 188 | 42.7
5/29/2013 08:00:03 to 5/29/2013 08:59:53 | 38.5718 | 45.2617 | 3.5 | 3.1899 | 225.9825 | 223.9658 | 196.8225 | 124.9442 | 65.2278 |  | 5-29-2013 8:36 PDT | 59 | 50 | 15 | 22 | 195 | 44.8
5/29/2013 09:00:03 to 5/29/2013 09:59:53 | 40.5949 | 47.0436 | 3.5 | 2.9487 | 225.8731 | 223.83 | 193.1756 | 125.0231 | 62.7958 |  | 5-29-2013 9:23 PDT | 58.8 | 42 | 16.1 | 22.6 | 206 | 41.3
5/29/2013 10:00:03 to 5/29/2013 10:59:53 | 38.9892 | 45.9229 | 3.5 | 3.4337 | 226.5475 | 224.305 | 194.7039 | 125.0006 | 71.2164 |  | 5-29-2013 10:27 PDT | 62 | 31 | 15 | 24 | 250 | 38.4
5/29/2013 11:00:03 to 5/29/2013 11:59:53 | 39.4718 | 46.3004 | 3.5 | 3.3286 | 226.5228 | 224.2722 | 193.5742 | 124.9556 | 71.9881 |  | 5-29-2013 11:30 PDT | 66 | 26 | 15 | 26 | 243 | 38.5
5/29/2013 12:00:03 to 5/29/2013 12:59:53 | 36.967 | 43.9158 | 3.435 | 3.5138 | 226.6214 | 224.2622 | 195.7272 | 125.0336 | 75.9622 |  | 5-29-2013 12:33 PDT | 69 | 22 | 15 | 24 | 265 | 37.8
5/29/2013 13:00:03 to 5/29/2013 13:59:53 | 36.5029 | 43.3618 | 3.2 | 3.6589 | 227.0439 | 224.7197 | 197.6283 | 124.8158 | 77.2478 |  | 5-29-2013 13:36 PDT | 70 | 18 | 9 | 19 | 241 | 35
5/29/2013 14:00:03 to 5/29/2013 14:59:53 | 35.5609 | 42.2507 | 3.2 | 3.4898 | 226.9619 | 224.6619 | 197.7344 | 124.6506 | 76.9622 |  | 5-29-2013 14:23 PDT | 70.7 | 18 | 12.8 | 22.8 | 241 | 35.5
5/29/2013 15:00:03 to 5/29/2013 15:59:53 | 35.7089 | 42.2519 | 3.2 | 3.343 | 226.8703 | 224.5772 | 196.4414 | 124.6883 | 76.3761 |  | 5-29-2013 15:25 PDT | 71 | 13 | 13 | 25 | 275 | 29.9
5/29/2013 16:00:03 to 5/29/2013 16:59:53 | 36.7383 | 43.1125 | 3.2 | 3.1741 | 226.8139 | 224.4625 | 194.5506 | 124.8111 | 75.6264 |  | 5-29-2013 16:28 PDT | 72 | 13 | 12 | 23 | 268 | 30.7
5/29/2013 17:00:03 to 5/29/2013 17:59:53 | 37.1729 | 43.4997 | 3.2 | 3.1268 | 226.8658 | 224.5117 | 194.5475 | 124.7939 | 74.4503 |  | 5-29-2013 17:23 PDT | 70.5 | 13 | 10.3 | 18.3 | 291 | 29.6
5/29/2013 18:00:03 to 5/29/2013 18:59:53 | 37.3086 | 43.6352 | 3.2 | 3.1266 | 226.6694 | 224.5239 | 195.2806 | 127.8128 | 73.16 |  | 5-29-2013 18:34 PDT | 69 | 16 | 10 | 18 | 312 | 32.1
5/29/2013 19:00:03 to 5/29/2013 19:59:53 | 36.9893 | 43.3041 | 3.2 | 3.1148 | 226.3672 | 224.4542 | 198.1611 | 130.7381 | 70.7819 |  | 5-29-2013 19:23 PDT | 66.4 | 17 | 10.7 | 18.1 | 326 | 31.1
5/29/2013 20:00:03 to 5/29/2013 20:59:53 | 40.453 | 46.7307 | 3.2 | 3.0776 | 226.6122 | 224.7772 | 196.2869 | 130.635 | 67.7742 |  | 5-29-2013 20:43 PDT | 57.6 | 26 | 1.6 | 5.1 | 13 | 31.5
5/29/2013 21:00:03 to 5/29/2013 21:59:53 | 40.3783 | 46.4594 | 3.2 | 2.8811 | 226.585 | 224.7389 | 195.8022 | 130.5378 | 65.3361 |  | 5-29-2013 21:26 PDT | 58 | 25 | 5 | 7 | 65 | 31.2
5/29/2013 22:00:03 to 5/29/2013 22:59:53 | 39.806 | 46.1356 | 3.2 | 3.1296 | 227.1581 | 225.2389 | 200.4936 | 130.3442 | 64.3856 |  | 5-29-2013 22:29 PDT | 51 | 37 | 1 | 3 | 86 | 32.1
5/29/2013 23:00:03 to 5/29/2013 23:59:53 | 43.6415 | 49.8713 | 3.2 | 3.0298 | 227.0675 | 225.2036 | 194.3828 | 130.4756 | 62.5897 |  | 5-29-2013 23:23 PDT | 49.3 | 39 | 0.4 | 2.2 | 56 | 31.6
5/30/2013 00:00:33 to 5/30/2013 00:59:53 | 44.3137 | 50.4072 | 3.2 | 2.8935 | 227.0213 | 225.1342 | 194.1375 | 130.5566 | 60.5468 |  | 5-30-2013 0:35 PDT | 50 | 40 | 4 | 6 | 92 | 32.6
5/30/2013 01:00:03 to 5/30/2013 01:59:53 | 43.8812 | 49.9142 | 3.2 | 2.833 | 227.0222 | 225.1258 | 194.2489 | 130.4036 | 59.7844 |  | 5-30-2013 1:38 PDT | 51 | 37 | 0 | 2 | 169 | 32.1
5/30/2013 02:00:03 to 5/30/2013 02:59:53 | 44.7572 | 50.8778 | 3.2 | 2.9205 | 227.0117 | 225.1725 | 193.8042 | 130.3558 | 59.5208 |  | 5-30-2013 2:23 PDT | 45.9 | 49 | 3.1 | 4.2 | 83 | 32.6
5/30/2013 03:00:03 to 5/30/2013 03:59:53 | 44.2522 | 50.2795 | 3.2 | 2.8273 | 226.7944 | 224.9978 | 193.9553 | 130.4286 | 58.8892 |  | 5-30-2013 3:25 PDT | 49 | 44 | 3 | 5 | 40 | 33.5
5/30/2013 04:00:03 to 5/30/2013 04:59:53 | 44.0218 | 50.0664 | 3.2 | 2.8446 | 226.6311 | 224.9008 | 193.8475 | 130.3036 | 58.325 |  | 5-30-2013 4:28 PDT | 47 | 49 | 3 | 5 | 49 | 33.6
5/30/2013 05:00:03 to 5/30/2013 05:59:53 | 44.5478 | 50.7463 | 3.2972 | 2.9013 | 226.8608 | 225.0994 | 194.5556 | 130.1561 | 57.3431 |  | 5-30-2013 5:32 PDT | 44 | 55 | 1 | 3 | 360 | 32.9
5/30/2013 06:00:03 to 5/30/2013 06:59:53 | 44.8615 | 51.9884 | 3.3 | 3.8269 | 227.0608 | 225.2667 | 195.2392 | 130.2769 | 65.9733 |  | 5-30-2013 6:35 PDT | 47 | 53 | 1 | 4 | 49 | 35
5/30/2013 07:00:03 to 5/30/2013 07:59:53 | 45.7876 | 53.7066 | 3.3 | 4.6191 | 227.0419 | 225.1953 | 193.3808 | 130.6325 | 75.0772 |  | 5-30-2013 7:38 PDT | 53 | 37 | 1 | 4 | 28 | 33.9
5/30/2013 08:00:03 to 5/30/2013 08:59:53 | 44.1817 | 52.1843 | 3.3 | 4.7026 | 227.2686 | 225.2975 | 193.8344 | 131.2733 | 79.1631 |  | 5-30-2013 8:23 PDT | 57.7 | 34 | 2.5 | 6 | 257 | 36.4
5/30/2013 09:00:03 to 5/30/2013 09:59:53 | 41.298 | 49.7158 | 3.3 | 5.1178 | 227.2636 | 225.2528 | 196.0997 | 131.7208 | 85.5311 |  | 5-30-2013 9:43 PDT | 63.5 | 29 | 3.1 | 8.3 | 243 | 38.4
5/30/2013 10:00:03 to 5/30/2013 10:59:53 | 41.4971 | 49.7993 | 3.3683 | 4.9339 | 227.1347 | 225.0586 | 194.9128 | 131.4028 | 82.4786 |  | 5-30-2013 10:26 PDT | 65 | 27 | 4 | 13 | 200 | 38.3
5/30/2013 11:00:03 to 5/30/2013 11:59:53 | 40.2414 | 47.3294 | 3.4 | 3.6879 | 227.05 | 224.9289 | 194.8683 | 130.2825 | 76.2769 |  | 5-30-2013 11:30 PDT | 68 | 22 | 9 | 15 | 213 | 37
5/30/2013 12:00:03 to 5/30/2013 12:59:53 | 37.752 | 44.3738 | 3.4 | 3.2218 | 226.8992 | 224.7628 | 196.7133 | 129.6194 | 73.7439 |  | 5-30-2013 12:33 PDT | 69 | 19 | 8 | 17 | 176 | 35.1
5/30/2013 13:00:03 to 5/30/2013 13:59:53 | 38.0518 | 44.7488 | 3.4 | 3.297 | 227.2164 | 225.0086 | 195.9147 | 129.8792 | 76.3114 |  | 5-30-2013 13:36 PDT | 72 | 14 | 7 | 15 | 234 | 32
5/30/2013 14:00:03 to 5/30/2013 14:59:53 | 35.888 | 42.4857 | 3.4 | 3.1977 | 226.9925 | 224.6081 | 197.2181 | 129.9961 | 76.5556 |  | 5-30-2013 14:23 PDT | 73.9 | 12 | 8.1 | 17 | 247 | 30.7
5/30/2013 15:00:03 to 5/30/2013 15:59:53 | 35.2929 | 41.8097 | 3.4 | 3.1168 | 227.0742 | 224.8428 | 197.695 | 129.9389 | 76.7872 |  | 5-30-2013 15:21 PDT | 77 | 12 | 9 | 18 | 192 | 33
5/30/2013 16:00:03 to 5/30/2013 16:59:53 | 34.8755 | 41.5492 | 3.3303 | 3.3434 | 227.0847 | 224.8661 | 198.9153 | 129.8522 | 79.0558 |  | 5-30-2013 16:24 PDT | 75 | 12 | 7 | 17 | 270 | 31.5
5/30/2013 17:00:03 to 5/30/2013 17:59:53 | 36.0619 | 42.6362 | 3.3 | 3.2744 | 226.9283 | 224.6561 | 196.1842 | 129.955 | 79.0917 |  | 5-30-2013 17:27 PDT | 76 | 12 | 9 | 22 | 284 | 32.3
5/30/2013 18:00:03 to 5/30/2013 18:59:53 | 36.5379 | 43.0411 | 3.3 | 3.2032 | 226.98 | 224.6692 | 196.0431 | 129.7847 | 77.4253 |  | 5-30-2013 18:30 PDT | 73 | 14 | 7 | 13 | 298 | 32.8
5/30/2013 19:00:03 to 5/30/2013 19:59:53 | 36.7282 | 43.0954 | 3.3 | 3.0672 | 226.6575 | 224.4292 | 196.0453 | 129.9783 | 75.0206 |  | 5-30-2013 19:33 PDT | 71 | 15 | 7 | 18 | 294 | 32.5

## Runtime Tally
Month of Runtime | Total Runtime (Incld's Factory) [hr] | Site Runtime [hr] | Total Gross Energy (Site Only) [kWh] | Gross Energy for Month [kWh] | Notes
2013-03-12 | 169 | - | 0 | - | Factory Hours
Start-Up to 3/31/2013 | 206 | 37 | 1741 | 1741
4/1/13 to 4/30/2013 | 225 | 56 | 2763 | 1022
5/1/13 to 5/31/2013 | 327 | 158 | 7541 | 4778