## Sheet1
| GETEM Input | Hydro-A Current | Hydro-A 2020 | Hydro-B Current | Hydro-B 2020 | Hydro-C Current | Hydro-C 2020 | Hydro-D Current | Hydro-D 2020 | Hydro-E Current | Hydro-E 2020 | EGS-A Current | EGS-A 2030 | EGS-B Current | EGS-B 2030 | EGS-C Current | EGS-C 2030 | EGS-D Current | EGS-D 2030 | EGS-E Current | EGS-E 2030
| Case | A | A | B | B | C | C | D | D | E | E | A | A | B | B | C | C | D | D | E | E
| Temp. (C) | 140 | 140 | 175 | 175 | 175 | 175 | 225 | 225 | 140 | 140 | 100 | 100 | 150 | 150 | 175 | 175 | 250 | 250 | 325 | 325
| Depth (m) | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 2500 | 2500 | 2500 | 2500 | 2000 | 2000 | 2500 | 2500 | 3000 | 3000 | 3500 | 3500 | 4000 | 4000
| Plant Type | Binary | Binary | Flash | Flash | Binary | Binary | Flash | Flash | Binary | Binary | Binary | Binary | Binary | Binary | Binary | Binary | Flash | Flash | Flash | Flash
| Power | 25/15/5 | 25 | 50/30/20 | 50 | 50/30/10 | 50 | 50/40/20 | 50 | 25/15/5 | 25 | 15/10/5 | 25 | 25/15/7 | 35 | 30/20/10 | 40 | 40/25/15 | 50 | 40/30/20 | 50
| Well Flow Rate | 160/100/70 | 100 | 110/80/50 | 80 | 160/100/70 | 100 | 110/80/50 | 80 | 160/100/70 | 100 | 60/40/30 | 100 | 60/40/30 | 100 | 60/40/30 | 100 | 60/40/30 | 80 | 60/40/30 | 80
| LCOE (cents/kWh) | 24.24 | 10.67 | 13.86 | 6.66 | 13.71 | 6.55 | 11.52 | 5.45 | 32.48 | 13.84 | 77.53 | 20.22 | 28.64 | 7.02 | 24.77 | 5.85 | 17.94 | 5.15 | 13.91 | 3.91
Row
35 | TECHNOLOGY YEAR | 2012 | 2020 | 2012 | 2020 | 2012 | 2020 | 2012 | 2020 | 2012 | 2020 | 2012 | 2030 | 2012 | 2030 | 2012 | 2030 | 2012 | 2030 | 2012 | 2030
| REFERENCE YEAR | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011
40 | Utilization Factor | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95% | 96%/95%/88% | 95%
41 | Contingency | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10% | 5%/15%/25% | 10%
42 | Royalty (thru Yr 10) | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75% | 1.75%
43 | Royalty (after Yr 10) | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5%
44 | Discount Rate | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7% | 6%/7%/9% | 7%
46 | Project Life (Period of Operation) (yrs) | 30/30/30 | 30 | 30/30/30 | 30 | 30/30/30 | 30 | 30/30/30 | 30 | 30/30/30 | 30 | 30/20/10 | 30 | 30/20/10 | 30 | 30/20/10 | 30 | 30/20/10 | 30 | 30/20/10 | 30
47 | Calculations based on Fixed Charge Rate (FCR) | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8% | 9%/10.8%/13% | 10.8%
52 | Duration of Exploration Phase (yrs) | 1.5/2/4 | 1 | 1.5/2/4 | 1 | 1.5/2/4 | 1 | 1.5/2/4 | 1 | 1.5/2/4 | 1 | 0.5/1/3 | 1 | 0.5/1/3 | 1 | 0.5/1/3 | 1 | 0.5/1/3 | 1 | 0.5/1/3 | 1
53 | Duration of Confirmation Phase (yrs) | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1 | 1/1.5/2 | 1
55 | Duration of Well Field Development Phase (yrs) | 1/1.5/2 | 1.25 | 1/1.5/2 | 1.25 | 1/1.5/2 | 1.25 | 1/1.5/2 | 1.25 | 1/1.5/2 | 1.25 | 2/2/3 | 1.5 | 2/2/3 | 1.5 | 2/2/3 | 1.5 | 2/2/3 | 1.5 | 2/2/3 | 1.5
56 | Duration of Plant Design and Construction (yrs) | 1.25/2/2.5 | 1.5 | 1.25/1.5/2.5 | 1.5 | 1.25/2/2.5 | 1.5 | 1.25/1.5/2.5 | 1.5 | 1.25/2/2.5 | 1.5 | 1.25/2/2.5 | 1.5 | 1.25/2/2.5 | 1.5 | 1.25/2/2.5 | 1.5 | 1.25/1.5/2.5 | 1.5 | 1.25/1.5/2.5 | 1.5
62 | Exploration Pre-Op Discount Rate | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7%
63 | Confirmation Pre-Op Discount Rate | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7% | 30% | 7%
64 | Well Field Development (including Stimulation) Pre-Op Discount Rate | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7% | 15% | 7%
65 | Plant Construction & Startup Pre-Op Discount Rate | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7%
77 | Resource Temperature (C) | 140 | 140 | 175 | 175 | 175 | 175 | 225 | 225 | 140 | 140 | 100 | 100 | 150 | 150 | 175 | 175 | 250 | 250 | 325 | 325
78 | Resource Depth (m) | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 2500 | 2500 | 2500 | 2500 | 2000 | 2000 | 2500 | 2500 | 3000 | 3000 | 3500 | 3500 | 4000 | 4000
85 | Number of Locations Evaluated Before Exploration Drilling Begins | 1/6/10 | 5 | 1/6/10 | 5 | 1/6/10 | 5 | 1/6/10 | 5 | 1/6/10 | 5 | 1/3/5 | 2 | 1/3/5 | 2 | 1/3/5 | 2 | 1/3/5 | 2 | 1/3/5 | 2
86 | Permitting Process Costs for Pre-Drilling Activities | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k | $60k
89 | Lump Sum Cost for Pre-Drilling Exploration Activities at each site | $100k/$500k/$1M | $350k (.7 factor) | $100k/$500k/$1M | $350k (.7 factor) | $100k/$500k/$1M | $350k (.7 factor) | $100k/$500k/$1M | $350k (.7 factor) | $100k/$500k/$1M | $350k (.7 factor) | $150k/$250k/$500k | $150k (.6 factor) | $150k/$250k/$500k | $150k (.6 factor) | $150k/$250k/$500k | $150k (.6 factor) | $150k/$250k/$500k | $150k (.6 factor) | $150k/$250k/$500k | $150k (.6 factor)
152 | Will the Project have Exploration Drilling? | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
153 | Number of Sites where Exploration Drilling Occurs | 1/5/10 | 3 | 1/5/10 | 3 | 1/5/10 | 3 | 1/5/10 | 3 | 1/5/10 | 3 | 1/2/3 | 1.5 | 1/2/3 | 1.5 | 1/2/3 | 1.5 | 1/2/3 | 1.5 | 1/2/3 | 1.5
154 | Site Exploration Drilling Cost | $1M/$3M/$7M | $1.8M (.6 factor) | $1M/$3M/$7M | $1.8M (.6 factor) | $1M/$3M/$7M | $1.8M (.6 factor) | $1M/$3M/$7M | $1.8M (.6 factor) | $1M/$3M/$7M | $1.8M (.6 factor) | $1M/$1.5M/$2M | $1.0M | $1M/$1.5M/$2M | $1.0M | $1M/$1.5M/$2M | $1.0M | $1M/$1.5M/$2M | $1.0M | $1M/$1.5M/$2M | $1.0M
155 | Permitting Process Costs for Drilling - Exploration/Confirmation Phases | $125k | $125k | $125k | $125k | $125k | $125k | $125k | $125k | $125k | $125k | $250k | $250k | $250k | $250k | $250k | $250k | $250k | $250k | $250k | $250k
156 | Leasing Cost (per acre) | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30 | $2/$30/$1,000 | 30
| Total Exploration Costs (M$) | $19.07M | $7.90M | $19.14M | $7.95M | $19.09M | $7.92M | $19.09M | $7.89M | $19.07M | $7.89M | $4.52M | $2.36M | $4.46M | $2.32M | $4.46M | $2.32M | $4.46M | $2.31M | $4.45M | $2.30M
| Total Exploration Costs (M$/MW) | $1.27M | $0.32M | $0.64M | $0.16M | $0.64M | $0.16M | $0.48M | $0.16M | $1.27M | $0.32M | $0.45M | $0.09M | $0.30M | $0.07M | $0.22M | $0.06M | $0.18M | $0.05M | $0.15M | $0.05M
159 | Number of Confirmation Drilling Sites Needed per Successful Project | 1/2/4 | 1.5 | 1/2/4 | 1.5 | 1/2/4 | 1.5 | 1/2/4 | 1.5 | 1/2/4 | 1.5 | 1/1.5/3 | 1 | 1/1.5/3 | 1 | 1/1.5/3 | 1 | 1/1.5/3 | 1 | 1/1.5/3 | 1
161 | Number of wells at Each Unsuccessful Site | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0 | 1.5 | 0
162 | Confirmation Well Success Ratio at Successful Site | 80%/60%/40% | 75% | 80%/60%/40% | 75% | 80%/60%/40% | 75% | 80%/60%/40% | 75% | 80%/60%/40% | 75% | 100%/100%/80% | 100% | 100%/100%/80% | 100% | 100%/100%/80% | 100% | 100%/100%/80% | 100% | 100%/100%/80% | 100%
164 | Number of Successful Confirmation Wells Required | 1/3/6 | 2 | 1/3/6 | 2 | 1/3/6 | 2 | 1/3/6 | 2 | 1/3/6 | 2 | 2/3/6 | 2 | 2/3/6 | 2 | 2/3/6 | 2 | 2/3/6 | 2 | 2/3/6 | 2
170 | Multiplier for Confirmation Well Costs (>= 1) | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2 | 1/1.2/1.5 | 1.2
172 | Confirmation Well Cost Used | $3.80M | $2.28M | $3.80M | $2.28M | $3.80M | $2.28M | $7.27M | $4.36M | $7.27M | $4.36M | $5.41M | $2.71M | $7.27M | $3.63M | $9.36M | $4.68M | $8.60M | $4.30M | $10.73M | $5.36M
182 | % of total confirmation costs attributed to non-drilling activities | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
183 | enter Stimulation Cost | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k
185 | Well Testing Cost at each site | $150k | $150k | $150k | $150k | $150k | $150k | $150k | $150k | $150k | $150k | $500k | $500k | $500k | $500k | $500k | $500k | $500k | $500k | $500k | $500k
| Total Confirmation costs (M$) | $28.21M | $9.00M | $28.21M | $9.00M | $28.21M | $9.00M | $53.72M | $17.01M | $53.72M | $17.01M | $25.81M | $6.52M | $33.12M | $8.46M | $41.37M | $10.66M | $38.34M | $9.86M | $46.74M | $12.10M
| Total Confirmation costs (M$/MW) | $1.88M | $0.36M | $0.94M | $0.18M | $0.94M | $0.18M | $1.34M | $0.34M | $3.58M | $0.68M | $2.58M | $0.26M | $2.21M | $0.24M | $2.07M | $0.27M | $1.53M | $0.20M | $1.56M | $0.24M
189 | Drilling Success Rate during the final phase of well field development | 90%/80%/60% | 85% | 90%/80%/60% | 85% | 90%/80%/60% | 85% | 90%/80%/60% | 85% | 90%/80%/60% | 85% | 100%/100%/80% | 100% | 100%/100%/80% | 100% | 100%/100%/80% | 100% | 100%/100%/80% | 100% | 100%/100%/80% | 100%
194 | Ratio of Injection Wells to Production Wells | 0.75/0.75/2 | 0.75 | 0.4/0.75/2 | 0.75 | 0.6/0.75/2 | 0.75 | 0.3/0.75/2 | 0.75 | 0.75/0.75/2 | 0.75 | 0.5/0.5/1 | 0.5 | 0.5/0.5/1 | 0.5 | 0.5/0.5/1 | 0.5 | 0.5/0.5/1 | 0.5 | 0.5/0.5/1 | 0.5
225 | Production Well Cost Used | $1.5M/$3.16M/$7.0M | $1.9M (.6 factor) | $1.5M/$3.16M/$7.0M | $1.9M (.6 factor) | $1.5M/$3.16M/$7.0M | $1.9M (.6 factor) | $3.0M/$6.06M/$9.0M | $3.63M (.6 factor) | $3.0M/$6.06M/$9.0M | $3.63M (.6 factor) | $3.25M/$4.51M/$7.25M | $2.26M (.5 factor) | $3.5M/$6.06M$9.0M | $3.03M (.5 factor) | $6.0M/$7.80M/$10.0M | $3.90M (.5 factor) | $6.0M/$7.16M/$15.0M | $3.58M (.5 factor) | $7.5M/$8.94M/$17.5M | $4.47M (.5 factor)
228 | Injection Well Cost Used | $1.5M/$3.16M/$7.0M | $1.9M (.6 factor) | $1.5M/$3.16M/$7.0M | $1.9M (.6 factor) | $1.5M/$3.16M/$7.0M | $1.9M (.6 factor) | $3.0M/$6.06M/$9.0M | $3.63M (.6 factor) | $3.0M/$6.06M/$9.0M | $3.63M (.6 factor) | $3.25M/$4.51M/$7.25M | $2.26M (.5 factor) | $3.5M/$6.06M$9.0M | $3.03M (.5 factor) | $6.0M/$7.80M/$10.0M | $3.90M (.5 factor) | $6.0M/$9.75M/$15.0M | $4.87M (.5 factor) | $7.5M/$11.89M/$17.5M | $5.95M (.5 factor)
232 | Surface Equipment Cost per Well | $100k/$200k/$400k | $200k | $150k/$250k/$450k | $250k | $100k/$200k/$400k | $200k | $150k/$250k/$450k | $250k | $100k/$200k/$400k | $200k | $100k/$200k/$400k | $200k | $100k/$200k/$400k | $200k | $100k/$200k/$400k | $200k | $150k/$225k/$400k | $225k | $150k/$225k/$400k | $225k
237 | Other Well Field Development Costs, ( % of total cost ) | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
238 | Permitting (Utilization Plant) Cost for Well Field & Power Plant | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M | $500k/$1M/$2M | $1M
241 | Production Well Flow Rate (kg/sec) | 160/100/70 | 100 | 110/80/50 | 80 | 160/100/70 | 100 | 110/80/50 | 80 | 160/100/70 | 100 | 60/40/30 | 100 | 60/40/30 | 100 | 60/40/30 | 100 | 60/40/30 | 80 | 60/40/30 | 80
246 | enter Inputted Stimulation Cost | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k | $1M/$2.5M/$5M | $500k
255 | Input Production Well Drawdown (psi-h/1000lb) | 0.2/0.4/1.2 | 0.4 | 0.2/0.4/1.2 | 0.4 | 0.2/0.4/1.2 | 0.4 | 0.2/0.5/1.2 | 0.5 | 0.2/0.5/1.2 | 0.5 | 0.2/0.4/1.0 | 0.2 | 0.2/0.4/1.2 | 0.2 | 0.2/0.4/1.2 | 0.2 | 0.2/0.5/1.2 | 0.25 | 0.2/0.5/1.2 | 0.25
256 | Ratio of Injection Well Buildup to Production Well Drawdown | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
268 | Annual Rate of Decline (%/yr) | 0.2%/0.4%/1% | 0.4% | 0.3%/0.5%/0.75% | 0.5% | 0.2%/0.4%/1% | 0.4% | 0.3%/0.5%/0.75% | 0.5% | 0.2%/0.4%/1% | 0.4% | 0.2%/0.5%/1% | 0.25% | 0.2%/0.5%/1% | 0.25% | 0.2%/0.5%/1% | 0.25% | 0.2%/0.5%/1% | 0.25% | 0.2%/0.5%/1% | 0.25%
282 | Subsurface Water loss as % of injected flow (> 0) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2%/5%/10% | 1% | 2%/5%/10% | 1% | 2%/5%/10% | 1% | 2%/5%/10% | 1% | 2%/5%/10% | 1%
284 | Makeup Water cost ($/acre-ft) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | $800/$2,000/$3,000 | 2000 | $800/$2,000/$3,000 | 2000 | $800/$2,000/$3,000 | 2000 | $800/$2,000/$3,000 | 2000 | $800/$2,000/$3,000 | 2000
| Total Well Field Development (M$) | $26.81M | $38.93M | $58.71M | $63.52M | $38.05M | $49.65M | $63.31M | $53.02M | $39.22M | $58.60M | $150.78M | $92.13M | $58.07M | $45.66M | $76.97M | $45.68M | $61.94M | $32.85M | $41.13M | $18.46M
| Total Well Field Development (M$/MW) | $1.79M | $1.56M | $1.96M | $1.27M | $1.27M | $0.99M | $1.58M | $1.06M | $2.61M | $2.34M | $15.08M | $3.69M | $3.87M | $1.30M | $3.85M | $1.14M | $2.48M | $0.66M | $1.37M | $0.37M
286 | Pump & Driver Efficiency for Production and Injection Pump | 80%/67.5%/60% | 75% | 80%/67.5%/60% | 75% | 80%/67.5%/60% | 75% | 80%/67.5%/60% | 75% | 80%/67.5%/60% | 75% | 80%/67.5%/60% | 85% | 80%/67.5%/60% | 85% | 80%/67.5%/60% | 85% | 80%/67.5%/60% | 85% | 80%/67.5%/60% | 85%
294 | Excess Pressure at pump Suction and/or well head (psi) | 50 | 50 | NA | NA | 50 | 50 | NA | NA | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | NA | NA | NA | NA
296 | Production pump casing diameter (in) | 9.625 | 9.625 | NA | NA | 9.625 | 9.625 | NA | NA | 9.625 | 9.625 | 9.625 | 9.625 | 9.625 | 9.625 | 9.625 | 9.625 | NA | NA | NA | NA
299 | Is production interval open hole or cased (slotted/perforated)? | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | NA | NA | NA | NA
300 | Hole or Casing Diameter in Production Interval (in) | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 11.75/9.625/8.625 | 9.625 | 11.75/9.625/8.625 | 9.625 | 11.75/9.625/6.625 | 9.625 | 8.625/7.0/6.625 | 7 | 8.625/7.0/6.625 | 7
303 | Type of production pump used | Lineshaft | Lineshaft | NA | NA | Lineshaft | Lineshaft | NA | NA | Lineshaft | Lineshaft | Lineshaft | Lineshaft | Lineshaft | Lineshaft | Lineshaft | Lineshaft | NA | NA | NA | NA
311 | Calculated Installed Pump Cost | $0.40M | $0.38M | NA | NA | $0.43M | $0.41M | NA | NA | $0.41M | $0.39M | $0.15M | $0.24M | $0.11M | $0.21M | $0.07M | $0.19M | NA | NA | NA | NA
312 | Adjustment to calculated pump cost | 0.7/1/2 | 1 | NA | NA | 0.7/1/2 | 1 | NA | NA | 0.7/1/2 | 1 | 0.7/1/2 | 1 | 0.7/1/2 | 1 | 0.7/1/2 | 1 | NA | NA | NA | NA
316 | Is injection interval open hole or cased (slotted/perforated)? | Open | Open | Open | Open | Open | Open | Open | Open | Open | Open | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted | Perforated/slotted
317 | Hole or Casing Diameter in Injection Interval (in) | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 14.5/12.25/8.25 | 12.25 | 11.75/9.625/8.625 | 9.625 | 11.75/9.625/8.625 | 9.625 | 11.75/9.625/6.625 | 9.625 | 8.625/7.0/6.625 | 7 | 8.625/7.0/6.625 | 7
325 | Calculated injection pump cost | $1.08M | $1.40M | $1.14M | $1.37M | $1.07M | $1.35M | $0.90M | $0.94M | $1.15M | $1.48M | $1.29M | $2.24M | $0.60M | $1.30M | $0.45M | $1.14M | $0.81M | $1.08M | $0.67M | $0.84M
326 | Adjustment to calculated injection pump cost | 1 | 0.93 | 1 | 0.93 | 1 | 0.93 | 1 | 0.93 | 1 | 0.93 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9
353 | Labor Multiplier (burdened labor cost) | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8 | 1.2/1.8/2.2 | 1.8
355356 | User adjustment to Reference Scenario O&M Staff | 0.75/1/1.5 | 0.8 (.8 factor) | 0.75/1/1.5 | 0.8 (.8 factor) | 0.75/1/1.5 | 0.8 (.8 factor) | 0.75/1/1.5 | 0.8 (.8 factor) | 0.75/1/1.5 | 0.8 (.8 factor) | 0.75/1/1.5 | 0.8 (.8 factor) | 0.75/1/1.5 | 0.7 (.7 factor) | 0.75/1/1.5 | 0.7 (.7 factor) | 0.75/1/1.5 | 0.7 (.7 factor) | 0.75/1/1.5 | 0.7 (.7 factor)
358 | Annual Maintenance non-labor (fraction of field cost) (%) | 0.5%/1.5%/4% | 1.2% (.8 factor) | 0.5%/1.5%/4% | 1.2% (.8 factor) | 0.5%/1.5%/4% | 1.2% (.8 factor) | 0.5%/1.5%/4% | 1.2% (.8 factor) | 0.5%/1.5%/4% | 1.2% (.8 factor) | 0.5%/1.5%/4% | 1% (.67 factor) | 0.5%/1.5%/4% | 1% (.67 factor) | 0.5%/1.5%/4% | 1% (.67 factor) | 0.5%/1.5%/4% | 1% (.67 factor) | 0.5%/1.5%/4% | 1% (.67 factor)
360 | Field Maintenance Chemical Cost ($/gal) | NA | NA | 10 | 10 | NA | NA | 10 | 10 | NA | NA | NA | NA | NA | NA | NA | NA | 10 | 10 | 10 | 10
362 | Annual O&M non-labor (fraction of plant cost) (%) | 1.2%/1.8%/2.2% | 1.7% (.92 factor) | 1.2%/1.8%/2.2% | 1.7% (.92 factor) | 1.2%/1.8%/2.2% | 1.7% (.92 factor) | 1.2%/1.8%/2.2% | 1.7% (.92 factor) | 1.2%/1.8%/2.2% | 1.7% (.92 factor) | 1.2%/1.8%/2.2% | 1.5% (.83 factor) | 1.2%/1.8%/2.2% | 1.5% (.83 factor) | 1.2%/1.8%/2.2% | 1.5% (.83 factor) | 1.2%/1.8%/2.2% | 1.5% (.83 factor) | 1.2%/1.8%/2.2% | 1.5% (.83 factor)
364 | Power Plant MaintenanceChemical cost ($/gal) | NA | NA | 1 | 1 | NA | NA | 1 | 1 | NA | NA | NA | NA | NA | NA | NA | NA | 1 | 1 | 1 | 1
374 | Lineshaft pump operating life [p] (yr) | 5/3/1 | 6 | 5/3/1 | 3 | 5/3/1 | 6 | 5/3/1 | 3 | 5/3/1 | 3 | 5/3/1 | 6 | 5/3/1 | 6 | 5/3/1 | 6 | 5/3/1 | 3 | 5/3/1 | 3
380 | Taxes and Insurance (Plant & Well Field Capital Costs) | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75% | 0.75%
387 | Transmission Lines Number of Miles | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0 | 0/0/50 | 0
393 | Power Sales (MW) | 25/15/5 | 25 | 50/30/20 | 50 | 50/30/10 | 50 | 50/40/20 | 50 | 25/15/5 | 25 | 15/10/5 | 25 | 25/15/7 | 35 | 30/20/10 | 40 | 40/25/15 | 50 | 40/30/20 | 50
398 | Is the Conversion System Flash or Binary? | Binary | Binary | Flash | Flash | Binary | Binary | Flash | Flash | Binary | Binary | Binary | Binary | Binary | Binary | Binary | Binary | Flash | Flash | Flash | Flash
416 | Adjustment to T-G cost | 0.5/1/2 | 0.93 |  |  | 0.5/1/2 | 0.93 |  |  | 0.5/1/2 | 0.93 | 0.5/1/2 | 0.9 | 0.5/1/2 | 0.9 | 0.5/1/2 | 0.9
418 | Adjustment to ACC cost | 0.5/1/2 | 0.93 |  |  | 0.5/1/2 | 0.93 |  |  | 0.5/1/2 | 0.93 | 0.5/1/2 | 0.9 | 0.5/1/2 | 0.9 | 0.5/1/2 | 0.9
420 | Adjustment to GF HX cost | 0.5/1/2 | 0.93 |  |  | 0.5/1/2 | 0.93 |  |  | 0.5/1/2 | 0.93 | 0.5/1/2 | 0.9 | 0.5/1/2 | 0.9 | 0.5/1/2 | 0.9
422 | Adjustment to WF Pump cost | 1 | 0.93 |  |  | 1 | 0.93 |  |  | 1 | 0.93 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9
429 | Installation multiplier used for direct costs | 2.25/2.66/3 | 2.47 (.93 factor) |  |  | 2.25/2.66/3 | 2.46 (.93 factor) |  |  | 2.25/2.66/3 | 2.46 (.93 factor) | 2.25/2.65/3 | 2.09 (.8 factor) | 2.25/2.66/3 | 2.12 (.8 factor) | 2.25/2.66/3 | 2.12 (.8 factor)
433 | Indirect Cost Percentage Multiplier | 6%/12%/15% | 12% |  |  | 6%/12%/15% | 12% |  |  | 6%/12%/15% | 12% | 6%/12%/15% | 12% | 6%/12%/15% | 12% | 6%/12%/15% | 12%
439 | Reference Plant Cost Used Adjustment | 0.8/1/1.5 | NA |  |  | 0.8/1/1.5 | NA |  |  | 0.8/1/1.5 | NA | 0.8/1/1.5 | NA | 0.8/1/1.5 | NA | 0.8/1/1.5 | NA
448 | Installed Plant Costs Used (/kW) | 3496 | 2698 |  |  | 2304 | 1865 |  |  | 4126 | 3126 | 7063 | 4703 | 4057 | 2019 | 3116 | 1648
| Calculated Plant Cost (M$) | $64.49M | $82.82M | $79.35M | $95.50M | $78.87M | $105.80M | $72.18M | $69.62M | $79.71M | $96.58M | $95.31M | $167.52M | $63.84M | $77.73M | $63.50M | $70.26M | $47.20M | $58.57M | $41.81M | $45.82M
| Calculated Plant Cost (M$/MW) | $4.30M | $3.31M | $2.64M | $1.91M | $2.63M | $2.12M | $1.80M | $1.39M | $5.11M | $3.86M | $9.53M | $6.70M | $4.26M | $2.22M | $3.18M | $1.76M | $1.89M | $1.17M | $1.39M | $0.92M
456 | Case: T,wet bulb (F); B: 40/60/80; B: 60; D: 40/60/80; D: 60; D: 40/60/80; D: 60; E: 40/60/80; E: 60
459 | Case: Turbine efficiency; B: 85%/80%/75%; B: 82.5%; D: 85%/80%/75%; D: 82.5%; D: 85%/80%/75%; D: 85%; E: 85%/80%/75%; E: 85%
461 | Case: Cooling water and condensate pump efficiency; B: 80%/75%/70%; B: 78%; D: 80%/75%/70%; D: 78%; D: 80%/75%/70%; D: 80%; E: 80%/75%/70%; E: 80%
464 | Case: Number of flashes; B: 2; B: 2; D: 2; D: 2; D: 2; D: 2; E: 2; E: 2
475 | Case: CW pump head (ft); B: 65; B: 65; D: 65; D: 65; D: 65; D: 65; E: 65; E: 65
476 | Case: Cooling Water temperature rise -DT,cooling water (F); B: 15/20/30; B: 20; D: 15/22.5/30; D: 22.5; D: 15/20/30; D: 20; E: 15/24/30; E: 24
479 | Case: Condenser NCG partial pressure (inch-Hg); B: 0.315; B: 0.315; D: 0.32; D: 0.32; D: 0.32; D: 0.32; E: 0.32; E: 0.32
481 | Case: NCG level (ppm); B: 200/2,000/20k; B: 2000; D: 200/2,000/20k; D: 2000; D: 200/2,000/20k; D: 2000; E: 200/2,000/20k; E: 2000
483 | Case: H2S level (ppm); B: 0/20/200; B: 20; D: 0/20/200; D: 20; D: 0/20/200; D: 20; E: 0/20/200; E: 20
484 | Case: Method of NCG removal; B: Hybrid; B: Hybrid; D: Hybrid; D: Hybrid; D: Hybrid; D: Hybrid; E: Hybrid; E: Hybrid
497 | Case: Calculated Turbine-Generator Cost ($/kW); B: 391; B: 324; D: 334; D: 298; D: 405; D: 298; E: 380; E: 296
498 | Case: Adjustment to T-G cost; B: 0.5/1/2; B: 0.93; D: 0.5/1/2; D: 0.93; D: 0.5/1/2; D: 0.9; E: 0.5/1/2; E: 0.9
502 | Case: Adjustment to Cooling Tower cost; B: 0.5/1/2; B: 0.93; D: 0.5/1/2; D: 0.93; D: 0.5/1/2; D: 0.9; E: 0.5/1/2; E: 0.9
504 | Case: Adjustment to Condenser Cost; B: 0.5/1/2; B: 0.93; D: 0.5/1/2; D: 0.93; D: 0.5/1/2; D: 0.9; E: 0.5/1/2; E: 0.9
506 | Case: Adjustment to Pump Cost; B: 0.5/1/2; B: 0.93; D: 0.5/1/2; D: 0.93; D: 0.5/1/2; D: 0.9; E: 0.5/1/2; E: 0.9
508 | Case: Adjustment to NCG Removal Cost; B: 0.5/1/3; B: 0.93; D: 0.5/1/3; D: 0.93; D: 0.5/1/3; D: 0.9; E: 0.5/1/3; E: 0.9
510 | Case: Adjustment to H2S Abatement Sys Cost; B: 0.5/1/4; B: 0.93; D: 0.5/1/4; D: 0.93; D: 0.5/1/4; D: 0.9; E: 0.5/1/4; E: 0.9
517 | Case: Installation multiplier used for direct costs; B: 2/2.81/3; B: 2.62 (.93 factor); D: 2/2.51/3; D: 2.33 (.93 factor); D: 2/2.44/3; D: 2.18 (.9 factor); E: 2/2.18/3; E: 1.95 (.9 factor)
521 | Case: Inputted % Multiplier for Indirect Cost; B: 6%/12%/15%; B: 8%; D: 6%/12%/15%; D: 8%; D: 6%/12%/15%; D: 8%; E: 6%/12%/15%; E: 8%
527 | Case: Flash Plant Cost Used ($/kW); B: 2483; B: 1808; D: 1751; D: 1356; D: 1816; D: 1131; E: 1363; E: 898
527 | Case: Flash Plant Cost Used ($/kW) embedded multiplier; B: 0.85/1/1.33; B: NA; D: 0.85/1/1.33; D: NA; D: 0.85/1/1.33; D: NA; E: 0.85/1/1.33; E: NA
| Calculated Total Capital Cost (M$) | $138.59M | $138.65M | $185.40M | $175.97M | $164.22M | $172.37M | $208.30M | $147.55M | $188.72M | $180.08M | $276.41M | $268.53M | $159.49M | $134.18M | $186.30M | $128.93M | $151.94M | $103.59M | $134.13M | $78.69M
| Calculated Total Capital Cost (M$/MW) | $9.24M | $5.55M | $6.18M | $3.52M | $5.47M | $3.45M | $5.21M | $2.95M | $12.58M | $7.20M | $27.64M | $10.74M | $10.63M | $3.83M | $9.32M | $3.22M | $6.08M | $2.07M | $4.47M | $1.57M