## Averaged Data
Date/Time | Total Net Power Output (Calcuated) | Gross Power Output (Veris) | Pump Parasitic Load | Cooling Fan Parasitic Load (Calculated) | Geothermal Header Hot Water Temperature | Hot Water Supply Temperature | Hot Water Return Temperature | Hot Water Supply Flow Rate | Ambient Temperature (GM Sensor) | Notes | MESO West Weather Data Station ID: HMHNV | Date/Time | Ambient Temperature | Relative Humidity | Wind Speed | Wind Gust | Wind Direction | Dew Point
| kW | kW | kW | kW | F | F | F | gpm | F |  |  |  | F | % | mph | mph | Degrees | F
6/12/2013 12:00:07 to 6/12/2013 12:59:57 | 14.2631 | 29.6182 | 2.6 | 12.7551 | 225.1853 | 222.7311 | 199.2811 | 143.4147 | 86.4653 |  |  | 6-12-2013 12:28 PDT | 86 | 12 | 22 | 38 | 181 | 39.6
6/18/2013 16:00:02 to 6/18/2013 16:59:52 | 17.4342 | 32.6893 | 2.5 | 12.7551 | 223.7192 | 220.9192 | 197.8544 | 138.9356 | 85.0772 |  |  | 6-18-2013 16:35 PDT | 80 | 11 | 14 | 22 | 251 | 33.6
6/18/2013 17:00:02 to 6/18/2013 17:59:52 | 22.7754 | 38.0305 | 2.5 | 12.7551 | 224.3864 | 221.5494 | 196.6769 | 139.1769 | 78.0567 |  |  | 6-18-2013 17:38 PDT | 73 | 12 | 19 | 30 | 247 | 30
6/18/2013 18:00:02 to 6/18/2013 18:59:52 | 22.9476 | 38.2027 | 2.5 | 12.7551 | 224.9469 | 222.2267 | 197.1311 | 139.1008 | 73.9367 |  |  | 6-18-2013 18:20 PDT | 72 | 12 | 13 | 22 | 233 | 29.3
6/18/2013 19:00:02 to 6/18/2013 19:59:52 | 22.9179 | 38.173 | 2.5 | 12.7551 | 225.29 | 222.5517 | 197.3153 | 139.215 | 74.1781 |  |  | 6-18-2013 19:23 PDT | 73 | 12 | 12 | 18 | 239 | 30
6/18/2013 20:00:02 to 6/18/2013 20:59:52 | 25.3451 | 40.6002 | 2.5 | 12.7551 | 225.4175 | 222.9431 | 197.0636 | 139.525 | 71.1747 |  |  | 6-18-2013 20:26 PDT | 68 | 17 | 17 | 27 | 248 | 32.4
6/18/2013 21:00:02 to 6/18/2013 21:59:52 | 26.6755 | 42.0092 | 2.5786 | 12.7551 | 226.0644 | 223.9214 | 196.9742 | 139.945 | 67.3928 |  |  | 6-18-2013 21:28 PDT | 64 | 20 | 11 | 17 | 254 | 32.1
6/18/2013 22:00:02 to 6/18/2013 22:59:52 | 27.3983 | 43.0426 | 2.8892 | 12.7551 | 225.8428 | 223.7378 | 196.6622 | 140.7603 | 64.0856 |  |  | 6-18-2013 22:31 PDT | 61 | 23 | 16 | 25 | 244 | 32.1
6/18/2013 23:00:02 to 6/18/2013 23:58:52 | 27.8644 | 43.5195 | 2.9 | 12.7551 | 225.9802 | 223.9407 | 196.6263 | 140.6274 | 61.2675 |  |  | 6-18-2013 23:34 PDT | 57 | 27 | 6 | 11 | 213 | 31.7
6/19/2013 00:01:02 to 6/19/2013 00:59:52 | 28.6037 | 44.2918 | 2.9331 | 12.7551 | 225.9342 | 223.9347 | 196.4455 | 139.9698 | 58.7698 |  |  | 6-19-2013 0:37 PDT | 55 | 29 | 10 | 14 | 215 | 31.3
6/19/2013 01:00:02 to 6/19/2013 01:59:52 | 28.5595 | 44.5146 | 3.2 | 12.7551 | 225.9475 | 223.9442 | 196.6778 | 139.2472 | 57.2272 |  |  | 6-19-2013 1:40 PDT | 53 | 37 | 11 | 16 | 198 | 33.9
6/19/2013 02:00:02 to 6/19/2013 02:59:52 | 29.5207 | 45.4758 | 3.2 | 12.7551 | 225.8653 | 223.8567 | 196.0294 | 139.4925 | 55.2803 |  |  | 6-19-2013 2:22 PDT | 52 | 45 | 6 | 10 | 174 | 36.5
6/19/2013 03:00:02 to 6/19/2013 03:59:52 | 30.0638 | 46.0189 | 3.2 | 12.7551 | 225.8625 | 223.8425 | 195.9492 | 139.6497 | 54.0156 |  |  | 6-19-2013 3:25 PDT | 51 | 51 | 9 | 15 | 184 | 37.9
6/19/2013 04:00:02 to 6/19/2013 04:59:52 | 29.7005 | 45.6556 | 3.2 | 12.7551 | 225.6764 | 223.5814 | 196.3389 | 139.8819 | 52.0683 |  |  | 6-19-2013 4:28 PDT | 49 | 53 | 11 | 18 | 175 | 36.8
6/19/2013 05:00:02 to 6/19/2013 05:59:52 | 30.3872 | 46.3423 | 3.2 | 12.7551 | 225.9381 | 223.95 | 196.1558 | 139.7372 | 51.685 |  |  | 6-19-2013 5:31 PDT | 47 | 55 | 7 | 12 | 257 | 35.7
6/19/2013 06:00:02 to 6/19/2013 06:59:52 | 31.8632 | 47.8183 | 3.2 | 12.7551 | 225.9044 | 223.7475 | 195.9489 | 139.6542 | 51.8472 |  |  | 6-19-2013 6:34 PDT | 46 | 60 | 11 | 20 | 237 | 36.3
6/19/2013 07:00:02 to 6/19/2013 07:59:52 | 32.5875 | 48.5426 | 3.2 | 12.7551 | 226.0958 | 224.1089 | 195.5375 | 139.5197 | 51.9764 |  |  | 6-19-2013 7:37 PDT | 46 | 69 | 11 | 23 | 196 | 38.9
6/19/2013 08:00:02 to 6/19/2013 08:59:52 | 30.4405 | 46.3956 | 3.2 | 12.7551 | 226.1514 | 224.1617 | 199.6611 | 139.7075 | 55.9714 |  |  | 6-19-2013 8:40 PDT | 46 | 69 | 5 | 14 | 306 | 38.9
6/19/2013 09:00:02 to 6/19/2013 09:59:52 | 29.2638 | 45.2189 | 3.2 | 12.7551 | 226.2594 | 224.2875 | 197.9067 | 139.7231 | 63.7322 |  |  | 6-19-2013 9:44 PDT | 53 | 46 | 11 | 18 | 232 | 37.8
6/19/2013 10:00:02 to 6/19/2013 10:59:52 | 28.5553 | 44.5104 | 3.2 | 12.7551 | 225.9267 | 223.8981 | 198.4697 | 139.7106 | 61.0606 |  |  | 6-19-2013 10:26 PDT | 55 | 44 | 13 | 28 | 253 | 38.8
6/19/2013 11:00:02 to 6/19/2013 11:59:52 | 28.5716 | 44.5267 | 3.2 | 12.7551 | 226.3406 | 224.2836 | 196.8236 | 139.2519 | 62.0075 |  |  | 6-19-2013 11:29 PDT | 56 | 40 | 9 | 15 | 178 | 37.9
6/19/2013 12:00:02 to 6/19/2013 12:59:52 | 26.5007 | 42.4558 | 3.2 | 12.7551 | 226.745 | 224.4917 | 198.8308 | 139.0458 | 69.9097 |  |  | 6-19-2013 12:32 PDT | 63 | 27 | 9 | 18 | 257 | 36.7
6/19/2013 13:00:02 to 6/19/2013 13:59:52 | 25.3829 | 41.338 | 3.2 | 12.7551 | 226.5308 | 224.255 | 199.2525 | 139.2261 | 69.5828 |  |  | 6-19-2013 13:48 PDT | 66 | 18 | 10 | 17 | 208 | 31.8
6/19/2013 14:00:02 to 6/19/2013 14:59:52 | 26.146 | 42.1011 | 3.2 | 12.7551 | 226.3628 | 223.8894 | 197.2189 | 139.1461 | 68.4517 |  |  | 6-19-2013 14:09 PDT | 67 | 17 | 12 | 22 | 212 | 31.6
6/19/2013 15:00:02 to 6/19/2013 15:59:52 | 25.2051 | 41.1602 | 3.2 | 12.7551 | 226.4314 | 223.8811 | 197.8972 | 139.0736 | 69.5214 |  |  | 6-19-2013 15:36 PDT | 67 | 17 | 13 | 30 | 224 | 31.6
6/19/2013 16:00:02 to 6/19/2013 16:59:52 | 26.2668 | 42.2219 | 3.2 | 12.7551 | 226.4603 | 224.0769 | 197.4044 | 139.1781 | 69.18 |  |  | 6-19-2013 16:39 PDT | 65 | 19 | 12 | 22 | 253 | 32
6/19/2013 17:00:02 to 6/19/2013 17:59:52 | 27.7269 | 39.6574 | 3.2 | 8.7306 | 226.6222 | 224.2881 | 198.8644 | 139.3336 | 69.6856 |  |  | 6-19-2013 17:43 PDT | 67 | 17 | 16 | 25 | 271 | 31.6
6/19/2013 18:00:02 to 6/19/2013 18:59:52 | 28.7497 | 39.112 | 3.2 | 7.1623 | 226.7458 | 224.4411 | 198.1019 | 138.8319 | 70.3 |  |  | 6-19-2013 18:25 PDT | 66 | 17 | 10 | 20 | 256 | 30.8
6/19/2013 19:00:02 to 6/19/2013 19:59:52 | 30.0761 | 40.4956 | 3.2 | 7.2194 | 226.7406 | 224.5097 | 197.5708 | 137.9867 | 69.1517 |  |  | 6-19-2013 19:28 PDT | 64 | 20 | 5 | 11 | 304 | 32.1
6/19/2013 20:00:02 to 6/19/2013 20:59:52 | 31.4825 | 41.7193 | 3.2 | 7.0368 | 226.5339 | 224.4961 | 197.4828 | 140.3203 | 66.0617 |  |  | 6-19-2013 20:32 PDT | 59 | 22 | 6 | 10 | 320 | 29.7
6/19/2013 21:00:02 to 6/19/2013 21:59:52 | 32.3193 | 42.3737 | 3.2 | 6.8545 | 226.4203 | 224.4781 | 197.8042 | 142.5428 | 63.3592 |  |  | 6-19-2013 21:35 PDT | 56 | 24 | 3 | 5 | 41 | 28.8
6/19/2013 22:00:02 to 6/19/2013 22:59:53 | 33.592 | 43.5901 | 3.2 | 6.798 | 225.2886 | 223.3606 | 196.7728 | 143.0292 | 57.8947 |  |  | 6-19-2013 22:38 PDT | 54 | 39 | 16 | 24 | 59 | 35.7
6/19/2013 23:00:03 to 6/19/2013 23:59:03 | 33.3486 | 43.1508 | 3.2 | 6.6023 | 225.6777 | 223.6839 | 197.2535 | 142.8501 | 56.3197 |  |  | 6-19-2013 23:20 PDT | 53 | 37 | 13 | 19 | 72 | 33.9
6/20/2013 00:00:43 to 6/20/2013 00:59:53 | 34.0768 | 43.86 | 3.2 | 6.5832 | 225.5837 | 223.6986 | 196.7702 | 142.8174 | 55.8542 |  |  | 6-20-2013 0:23 PDT | 52 | 36 | 10 | 15 | 62 | 32.5
6/20/2013 01:00:03 to 6/20/2013 01:59:53 | 35.6373 | 45.5588 | 3.2 | 6.7215 | 225.9147 | 224.1372 | 196.6531 | 142.9061 | 55.4644 |  |  | 6-20-2013 1:26 PDT | 48 | 41 | 6 | 11 | 14 | 31.3
6/20/2013 02:00:03 to 6/20/2013 02:59:53 | 37.2407 | 47.2129 | 3.2 | 6.7722 | 226.3031 | 224.5683 | 196.5319 | 142.8228 | 53.1433 |  |  | 6-20-2013 2:29 PDT | 44 | 49 | 5 | 10 | 0 | 30.9
6/20/2013 03:00:03 to 6/20/2013 03:59:53 | 38.0241 | 48.0728 | 3.2 | 6.8487 | 226.1936 | 224.4303 | 196.2961 | 142.9781 | 51.5961 |  |  | 6-20-2013 3:32 PDT | 41 | 55 | 5 | 9 | 356 | 30.1
6/20/2013 04:00:03 to 6/20/2013 04:59:53 | 38.7167 | 48.6409 | 3.2 | 6.7242 | 226.2356 | 224.5381 | 196.0772 | 142.8925 | 49.2794 |  |  | 6-20-2013 4:35 PDT | 40 | 57 | 6 | 9 | 360 | 29.8
6/20/2013 05:00:03 to 6/20/2013 05:59:53 | 38.7611 | 48.7412 | 3.2 | 6.78 | 226.3528 | 224.5747 | 196.5769 | 143.0408 | 48.2425 |  |  | 6-20-2013 5:38 PDT | 37 | 60 | 5 | 7 | 357 | 27.9
6/20/2013 06:00:03 to 6/20/2013 06:59:53 | 38.2545 | 49.0258 | 3.2 | 7.5712 | 226.3836 | 224.6681 | 196.5572 | 142.8942 | 57.3308 |  |  | 6-20-2013 6:20 PDT | 41 | 55 | 5 | 7 | 353 | 30.1
6/20/2013 07:00:03 to 6/20/2013 07:59:53 | 35.1081 | 46.7683 | 3.2 | 8.4602 | 226.4844 | 224.6272 | 198.1547 | 142.3831 | 70.1836 |  |  | 6-20-2013 7:23 PDT | 50 | 44 | 9 | 11 | 320 | 34.3
6/20/2013 08:00:03 to 6/20/2013 08:59:53 | 16.1967 | 29.0462 | 2.2681 | 10.5814 | 226.2717 | 224.4614 | 205.5036 | 155.8344 | 74.5689 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds) beginning at 8am; hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 8:26 PDT | 55 | 35 | 8 | 12 | 6 | 34.6
6/20/2013 09:00:03 to 6/20/2013 09:59:53 | 12.2852 | 25.1069 | 2.1 | 10.7217 | 226.8736 | 224.8161 | 203.1308 | 124.8219 | 76.4569 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 9:29 PDT | 59 | 30 | 3 | 7 | 47 | 35.2
6/20/2013 10:00:03 to 6/20/2013 10:59:53 | 8.6195 | 21.1293 | 2.03 | 10.4798 | 227.2203 | 225.0183 | 205.2533 | 123.5283 | 79.1169 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 10:32 PDT | 64 | 25 | 5 | 10 | 234 | 36.1
6/20/2013 11:00:03 to 6/20/2013 11:59:53 | 8.8475 | 20.4768 | 2 | 9.6293 | 226.9806 | 224.6531 | 204.0308 | 123.5103 | 75.7372 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 11:43 PDT | 67 | 19 | 9 | 17 | 219 | 33.6
6/20/2013 12:00:03 to 6/20/2013 12:59:53 | 8.1215 | 19.3062 | 2 | 9.1847 | 226.9619 | 224.5264 | 203.6947 | 122.952 | 74.8192 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 12:25 PDT | 68 | 20 | 8 | 19 | 241 | 35.3
6/20/2013 13:00:03 to 6/20/2013 13:59:53 | 6.8294 | 17.7827 | 2 | 8.9533 | 227.0831 | 224.6133 | 204.3197 | 122.3197 | 75.2153 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 13:28 PDT | 70 | 18 | 8 | 20 | 203 | 35
6/20/2013 14:00:03 to 6/20/2013 14:59:53 | 5.9132 | 16.8714 | 2 | 8.9582 | 227.0606 | 224.5447 | 204.8097 | 121.5911 | 75.2136 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 14:27 PDT | 72 | 16 | 7 | 16 | 179 | 34.4
6/20/2013 15:00:03 to 6/20/2013 15:59:53 | 5.8356 | 16.5532 | 2 | 8.7176 | 227.0853 | 224.5608 | 204.4714 | 122.1986 | 74.7919 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 15:30 PDT | 70 | 17 | 6 | 14 | 189 | 33.9
6/20/2013 16:00:03 to 6/20/2013 16:59:53 | 5.1033 | 16.1718 | 2 | 9.0685 | 226.8936 | 224.2903 | 205.0958 | 121.8008 | 76.5556 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 16:33 PDT | 76 | 13 | 6 | 14 | 230 | 33.7
6/20/2013 17:00:03 to 6/20/2013 17:59:53 | 6.8155 | 17.5988 | 2 | 8.7833 | 226.8047 | 224.385 | 204.0147 | 122.5169 | 73.2839 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 17:36 PDT | 71 | 15 | 8 | 14 | 244 | 32.5
6/20/2013 18:00:03 to 6/20/2013 18:59:53 | 5.9837 | 16.9786 | 2 | 8.9949 | 227.1544 | 224.7783 | 205.0544 | 121.0381 | 74.8208 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 18:39 PDT | 75 | 14 | 3 | 10 | 200 | 34.3
6/20/2013 19:00:03 to 6/20/2013 19:59:53 | 7.2485 | 18.2043 | 2 | 8.9559 | 227.0747 | 224.8311 | 204.2672 | 121.7239 | 74.1011 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 19:21 PDT | 70 | 17 | 5 | 9 | 272 | 33.9
6/20/2013 20:00:03 to 6/20/2013 20:59:53 | 11.0936 | 22.0362 | 2 | 8.9427 | 226.5464 | 224.3419 | 201.9467 | 122.6097 | 70.6622 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 20:24 PDT | 67 | 19 | 7 | 12 | 264 | 33.6
6/20/2013 21:00:03 to 6/20/2013 21:59:53 | 25.6431 | 35.4508 | 2.0617 | 7.7461 | 226.1697 | 224.0058 | 192.7481 | 104.4381 | 65.4425 | Flow rates fluctuating dramatically (between approximately 90-160gpm, on average, every 30 seconds); hot water supply trim valve eventually diagnosed as the cause |  | 6-20-2013 21:27 PDT | 61 | 31 | 9 | 16 | 55 | 37.5
6/20/2013 22:00:03 to 6/20/2013 22:59:53 | 30.3249 | 40.1792 | 2.2 | 7.6543 | 225.5314 | 223.3086 | 187.9158 | 101.7872 | 62.775 |  |  | 6-20-2013 22:30 PDT | 58 | 43 | 11 | 23 | 1 | 41.1
6/20/2013 23:00:03 to 6/20/2013 23:59:03 | 33.0972 | 42.9644 | 2.2 | 7.6672 | 225.0321 | 222.6617 | 186.9065 | 102.0594 | 57.3454 |  |  | 6-20-2013 23:33 PDT | 53 | 54 | 14 | 22 | 11 | 40.8
6/21/2013 00:00:43 to 6/21/2013 00:59:53 | 31.77 | 41.1235 | 2.2 | 7.1534 | 225.7455 | 223.4236 | 187.9809 | 102.0461 | 55.8978 |  |  | 6-21-2013 0:36 PDT | 53 | 49 | 9 | 14 | 25 | 39
6/21/2013 01:00:03 to 6/21/2013 01:59:53 | 30.2757 | 39.3789 | 2.2 | 6.9032 | 226.4442 | 224.0983 | 188.6475 | 101.9172 | 56.7228 |  |  | 6-21-2013 1:39 PDT | 53 | 41 | 6 | 10 | 54 | 35.7
6/21/2013 02:00:03 to 6/21/2013 02:59:53 | 31.9643 | 41.4435 | 2.2258 | 7.2534 | 226.8867 | 224.6639 | 188.7606 | 101.9333 | 57.7917 |  |  | 6-21-2013 2:21 PDT | 48 | 55 | 5 | 7 | 38 | 36.6
6/21/2013 03:00:03 to 6/21/2013 03:59:53 | 32.4499 | 42.0933 | 2.4 | 7.2435 | 226.6631 | 224.4919 | 188.2322 | 102.0861 | 56.2789 |  |  | 6-21-2013 3:24 PDT | 48 | 54 | 7 | 8 | 45 | 36.3
6/21/2013 04:00:03 to 6/21/2013 04:59:53 | 32.231 | 41.7145 | 2.4 | 7.0834 | 226.9569 | 224.7178 | 188.4347 | 101.9281 | 55.7853 |  |  | 6-21-2013 4:27 PDT | 44 | 61 | 3 | 5 | 58 | 34.8
6/21/2013 05:00:03 to 6/21/2013 05:59:53 | 32.6696 | 42.1455 | 2.4 | 7.076 | 227.125 | 224.9858 | 188.985 | 102.1075 | 55.2711 |  |  | 6-21-2013 5:30 PDT | 41 | 67 | 0 | 2 | 157 | 33.6
6/21/2013 06:00:03 to 6/21/2013 06:59:53 | 32.2948 | 43.028 | 2.4 | 8.3332 | 227.0931 | 224.9492 | 188.2783 | 101.9239 | 66.2336 |  |  | 6-21-2013 6:33 PDT | 48 | 62 | 1 | 3 | 49 | 38.8
6/21/2013 07:00:03 to 6/21/2013 07:59:53 | 28.9353 | 40.4734 | 2.4 | 9.1381 | 227.2522 | 225.0119 | 191.0178 | 102.02 | 76.7986 |  |  | 6-21-2013 7:36 PDT | 53 | 50 | 1 | 4 | 191 | 39.4
6/21/2013 08:00:03 to 6/21/2013 08:59:53 | 26.1228 | 38.3495 | 2.4 | 9.8267 | 227.3781 | 225.1469 | 198.2819 | 112.8433 | 81.6911 |  |  | 6-21-2013 8:39 PDT | 57 | 42 | 2 | 5 | 219 | 39.7
6/21/2013 09:00:03 to 6/21/2013 09:59:53 | 29.3355 | 40.7085 | 2.4 | 8.973 | 227.425 | 225.1606 | 196.2886 | 123.2561 | 82.8586 |  |  | 6-21-2013 9:21 PDT | 60 | 35 | 3 | 8 | 208 | 38.9
6/21/2013 10:00:03 to 6/21/2013 10:59:53 | 27.4643 | 38.8306 | 2.4 | 8.9663 | 227.4683 | 225.12 | 197.8378 | 124.1467 | 84.1256 |  |  | 6-21-2013 10:25 PDT | 64 | 28 | 4 | 11 | 240 | 38.2
6/21/2013 11:00:03 to 6/21/2013 11:59:53 | 28.1509 | 38.8299 | 2.4 | 8.279 | 227.465 | 225.0075 | 194.9039 | 124.4675 | 81.0028 |  |  | 6-21-2013 11:28 PDT | 66 | 24 | 6 | 13 | 264 | 37
6/21/2013 12:00:03 to 6/21/2013 12:59:53 | 26.4532 | 36.9594 | 2.4 | 8.1062 | 227.4864 | 224.98 | 196.6339 | 124.4706 | 80.3072 |  |  | 6-21-2013 12:31 PDT | 70 | 15 | 4 | 9 | 291 | 31.7
6/21/2013 13:00:03 to 6/21/2013 13:59:53 | 22.7453 | 32.772 | 2.4 | 7.6267 | 227.4969 | 224.9522 | 198.4622 | 123.5933 | 79.1964 |  |  | 6-21-2013 13:34 PDT | 71 | 14 | 4 | 12 | 210 | 31.2
6/21/2013 14:00:03 to 6/21/2013 14:59:53 | 24.1067 | 34.4924 | 2.4 | 7.9857 | 227.4356 | 224.9156 | 198.74 | 122.7378 | 80.3667 |  |  | 6-21-2013 14:37 PDT | 73 | 14 | 5 | 14 | 219 | 32.8
6/21/2013 15:00:03 to 6/21/2013 15:59:53 | 21.4453 | 31.3673 | 2.4 | 7.522 | 227.4222 | 224.9078 | 199.5425 | 123.1883 | 78.5375 |  |  | 6-21-2013 15:40 PDT | 76 | 13 | 6 | 20 | 302 | 33.7
6/21/2013 16:00:03 to 6/21/2013 16:59:53 | 15.9988 | 20.9071 | 2.0433 | 2.865 | 227.3169 | 223.1108 | 201.63 | 91.0886 | 77.5456 |  |  | 6-21-2013 16:22 PDT | 73 | 13 | 6 | 13 | 109 | 31.4
6/21/2013 17:00:03 to 6/21/2013 17:59:52 | 9.3135 | 19.8787 | 1.9365 | 8.6287 | 227.2123 | 224.1181 | 202.7643 | 138.1972 | 76.893 |  |  | 6-21-2013 17:25 PDT | 75 | 13 | 2 | 7 | 179 | 32.9
6/21/2013 18:00:02 to 6/21/2013 18:59:52 | 6.6576 | 17.6338 | 1.8 | 9.1761 | 227.065 | 224.7208 | 206.5681 | 138.855 | 77.4 |  |  | 6-21-2013 18:28 PDT | 74 | 13 | 7 | 17 | 305 | 32.2
6/21/2013 19:00:02 to 6/21/2013 19:59:52 | 6.1987 | 17.2289 | 1.8 | 9.2302 | 226.8511 | 224.5611 | 206.3075 | 138.4658 | 76.0442 |  |  | 6-21-2013 19:31 PDT | 72 | 13 | 7 | 12 | 332 | 30.7
6/21/2013 20:00:02 to 6/21/2013 20:59:52 | 11.9444 | 22.3599 | 1.8 | 8.6156 | 226.76 | 224.5264 | 202.9981 | 140.5825 | 72.3144 |  |  | 6-21-2013 20:34 PDT | 66 | 17 | 4 | 8 | 4 | 30.8
6/21/2013 21:00:02 to 6/21/2013 21:59:52 | 14.3328 | 24.6203 | 1.8 | 8.4875 | 226.555 | 224.4606 | 203.0006 | 139.9367 | 69.2622 |  |  | 6-21-2013 21:37 PDT | 63 | 18 | 5 | 9 | 10 | 29.4
6/21/2013 22:00:02 to 6/21/2013 22:59:52 | 26.7677 | 36.4092 | 2.3261 | 7.3153 | 225.9686 | 223.9667 | 194.9581 | 118.7761 | 66.6692 |  |  | 6-21-2013 22:40 PDT | 62 | 24 | 13 | 19 | 62 | 33.7
6/21/2013 23:00:02 to 6/21/2013 23:59:02 | 29.3704 | 39.068 | 2.6 | 7.0976 | 225.7513 | 223.6059 | 191.9749 | 116.8572 | 64.2972 |  |  | 6-21-2013 23:43 PDT | 60 | 28 | 14 | 19 | 58 | 34.8
6/22/2013 00:00:42 to 6/22/2013 00:59:52 | 30.0379 | 39.7401 | 2.6 | 7.1022 | 225.6211 | 223.4093 | 192.2733 | 117.0312 | 62.0065 |  |  | 6-22-2013 0:25 PDT | 59 | 31 | 17 | 25 | 64 | 35.8
6/22/2013 01:00:02 to 6/22/2013 01:59:52 | 32.3279 | 42.2492 | 2.6 | 7.3212 | 226.0436 | 224.0022 | 191.605 | 116.8828 | 61.5678 |  |  | 6-22-2013 1:28 PDT | 56 | 34 | 10 | 16 | 27 | 35
6/22/2013 02:00:02 to 6/22/2013 02:59:52 | 33.6432 | 43.4347 | 2.6 | 7.1916 | 226.3389 | 224.2886 | 191.3519 | 116.9761 | 58.9928 |  |  | 6-22-2013 2:31 PDT | 50 | 42 | 7 | 11 | 353 | 33.5
6/22/2013 03:00:02 to 6/22/2013 03:59:52 | 33.276 | 42.9931 | 2.6 | 7.1171 | 225.6281 | 223.5744 | 191.0192 | 117.0281 | 56.7897 |  |  | 6-22-2013 3:34 PDT | 54 | 40 | 16 | 22 | 54 | 36.2
6/22/2013 04:00:02 to 6/22/2013 04:59:52 | 32.4625 | 42.0871 | 2.6044 | 7.0201 | 225.7481 | 223.6103 | 191.1447 | 116.99 | 57.3244 |  |  | 6-22-2013 4:38 PDT | 54 | 40 | 10 | 15 | 47 | 36.2
6/22/2013 05:00:02 to 6/22/2013 05:59:52 | 33.1584 | 43.3428 | 2.9981 | 7.1864 | 225.5547 | 223.48 | 190.8919 | 117.3685 | 57.2372 |  |  | 6-22-2013 5:20 PDT | 53 | 45 | 13 | 21 | 47 | 37.4
6/22/2013 06:00:02 to 6/22/2013 06:59:52 | 33.3906 | 44.1996 | 3 | 7.8091 | 225.5539 | 223.5256 | 190.5806 | 117.1133 | 63.1358 |  |  | 6-22-2013 6:23 PDT | 54 | 47 | 14 | 21 | 44 | 39.1
6/22/2013 07:00:02 to 6/22/2013 07:59:52 | 31.3075 | 42.8961 | 3 | 8.5886 | 225.8494 | 223.8039 | 192.6111 | 116.6039 | 70.7894 |  |  | 6-22-2013 7:26 PDT | 56 | 43 | 13 | 18 | 38 | 39.3
6/22/2013 08:00:02 to 6/22/2013 08:59:52 | 31.1281 | 42.9369 | 3 | 8.8089 | 225.9042 | 223.8725 | 191.1986 | 116.2883 | 74.6158 |  |  | 6-22-2013 8:29 PDT | 59 | 37 | 13 | 18 | 35 | 39.1
6/22/2013 09:00:02 to 6/22/2013 09:59:52 | 28.9762 | 40.4651 | 3 | 8.4889 | 226.3858 | 224.1403 | 192.9575 | 116.7975 | 76.4483 |  |  | 6-22-2013 9:32 PDT | 64 | 31 | 10 | 16 | 21 | 40.1
6/22/2013 10:00:02 to 6/22/2013 10:59:52 | 27.4873 | 39.1147 | 3 | 8.6274 | 227.0481 | 224.5553 | 193.1667 | 116.6644 | 81.4294 |  |  | 6-22-2013 10:35 PDT | 67 | 28 | 7 | 13 | 335 | 40.7
6/27/2013 19:00:03 to 6/27/2013 19:59:53 | 6.0842 | 21.0393 | 2.2 | 12.7551 | 226.8233 | 224.0531 | 187.7303 | 83.2774 | 95.9322 | Flow averages ~85gpm but occasionally fluctuates between 80-95gpm |  | 6-27-2013 19:32 PDT | 93 | 11 | 11 | 17 | 332 | 43.1
6/27/2013 20:00:03 to 6/27/2013 20:59:53 | 5.8314 | 20.7865 | 2.2 | 12.7551 | 226.9414 | 224.1886 | 190.2983 | 83.907 | 90.7986 | Flow averages ~85gpm but occasionally fluctuates between 80-95gpm |  | 6-27-2013 20:35 PDT | 85 | 12 | 4 | 6 | 51 | 38.9
6/27/2013 21:00:03 to 6/27/2013 21:59:53 | 7.2733 | 22.2284 | 2.2 | 12.7551 | 227.0183 | 224.2975 | 189.1233 | 83.3653 | 87.9022 | Flow averages ~85gpm but occasionally fluctuates between 80-95gpm |  | 6-27-2013 21:38 PDT | 83 | 12 | 5 | 9 | 62 | 37.4
6/27/2013 22:00:03 to 6/27/2013 22:59:53 | 9.7627 | 24.7178 | 2.2 | 12.7551 | 227.1556 | 224.4794 | 187.4281 | 83.5472 | 86.5136 | Flow averages ~85gpm but occasionally fluctuates between 80-95gpm |  | 6-27-2013 22:20 PDT | 79 | 14 | 4 | 7 | 86 | 37.3
6/27/2013 23:00:03 to 6/27/2013 23:59:03 | 11.4565 | 26.4116 | 2.2 | 12.7551 | 227.1558 | 224.4175 | 187.4285 | 83.6276 | 84.8132 | Flow averages ~85gpm but occasionally fluctuates between 80-95gpm |  | 6-27-2013 23:23 PDT | 79 | 14 | 6 | 8 | 41 | 37.3
6/28/2013 00:00:43 to 6/28/2013 00:59:53 | 13.0497 | 28.27 | 2.4652 | 12.7551 | 227.2767 | 224.5275 | 186.1781 | 83.7006 | 82.1747 | Flow rate stable |  | 6-28-2013 0:26 PDT | 73 | 16 | 2 | 5 | 45 | 35.2
6/28/2013 01:00:03 to 6/28/2013 01:59:53 | 13.5055 | 28.9606 | 2.7 | 12.7551 | 227.3792 | 224.6461 | 186.0739 | 83.6632 | 81.4947 | Flow rate stable |  | 6-28-2013 1:29 PDT | 71 | 20 | 2 | 4 | 28 | 37.7
6/28/2013 02:00:03 to 6/28/2013 02:59:53 | 16.0061 | 31.4613 | 2.7 | 12.7551 | 227.1764 | 224.4219 | 185.4014 | 83.6886 | 75.4361 | Flow rate stable |  | 6-28-2013 2:32 PDT | 67 | 22 | 3 | 6 | 176 | 36.2
6/28/2013 03:00:03 to 6/28/2013 03:59:53 | 15.887 | 31.3421 | 2.7 | 12.7551 | 227.0861 | 224.2947 | 185.3017 | 83.7039 | 77.1753 | Flow rate stable |  | 6-28-2013 3:35 PDT | 69 | 21 | 4 | 6 | 64 | 37
6/28/2013 04:00:03 to 6/28/2013 04:59:53 | 18.0448 | 33.4999 | 2.7 | 12.7551 | 227.2331 | 224.5997 | 185.0744 | 83.7554 | 75.4097 | Flow rate stable |  | 6-28-2013 4:38 PDT | 63 | 25 | 2 | 3 | 27 | 35.3
6/28/2013 05:00:03 to 6/28/2013 05:59:53 | 19.174 | 34.7046 | 2.7756 | 12.7551 | 226.7508 | 224.1494 | 184.1739 | 83.9092 | 72.0747 | Flow rate stable |  | 6-28-2013 5:20 PDT | 65 | 23 | 6 | 10 | 54 | 35.4
6/28/2013 06:00:03 to 6/28/2013 06:59:53 | 18.9913 | 34.9708 | 3.2244 | 12.7551 | 226.9961 | 224.3378 | 183.9861 | 83.9271 | 79.2803 | Flow rate stable |  | 6-28-2013 6:23 PDT | 63 | 25 | 6 | 10 | 353 | 35.3
6/28/2013 07:00:03 to 6/28/2013 07:59:53 | 16.7156 | 32.5468 | 3.0761 | 12.7551 | 226.8453 | 223.9747 | 184.8453 | 83.5142 | 88.6958 | Flow rate stable |  | 6-28-2013 7:26 PDT | 76 | 17 | 9 | 13 | 343 | 38.6
6/28/2013 08:00:03 to 6/28/2013 08:59:53 | 14.4864 | 30.2382 | 2.9967 | 12.7551 | 226.7556 | 223.8567 | 184.9408 | 83.4058 | 94.3439 | Flow rate stable |  | 6-28-2013 8:29 PDT | 82 | 15 | 12 | 17 | 335 | 40.8
6/28/2013 09:00:03 to 6/28/2013 09:59:53 | 11.4355 | 26.9976 | 2.8069 | 12.7551 | 226.9914 | 224.1983 | 186.4567 | 83.2714 | 98.1469 | Flow rate stable |  | 6-28-2013 9:32 PDT | 87 | 14 | 11 | 17 | 350 | 43.3
6/28/2013 10:00:03 to 6/28/2013 10:59:53 | 8.2835 | 23.8386 | 2.8 | 12.7551 | 227.3131 | 224.6086 | 186.8044 | 83.2019 | 102.7108 | Flow rate stable |  | 6-28-2013 10:36 PDT | 93 | 12 | 8 | 14 | 359 | 44.8
6/28/2013 11:00:03 to 6/28/2013 11:59:53 | 5.0313 | 20.5864 | 2.8 | 12.7551 | 227.4747 | 224.8178 | 187.2669 | 83.1437 | 105.2525 | Flow rate stable |  | 6-28-2013 11:39 PDT | 97 | 11 | 8 | 17 | 340 | 46
6/28/2013 12:00:03 to 6/28/2013 12:59:53 | 1.495 | 16.9412 | 2.6911 | 12.7551 | 227.4867 | 224.8092 | 189.2219 | 83.3606 | 105.9492 | Flow rate stable |  | 6-28-2013 12:21 PDT | 98 | 10 | 10 | 19 | 346 | 44.8

## Runtime Tally
Month of Runtime | Total Runtime (Incld's Factory) [hr] | Site Runtime [hr] | Total Gross Energy (Site Only) [kWh] | Gross Energy for Month [kWh] | Notes
2013-03-12 | 169 | - | 0 | - | Factory Hours
Start-Up to 3/31/2013 | 206 | 37 | 1741 | 1741
4/1/13 to 4/30/2013 | 225 | 56 | 2763 | 1022
5/1/13 to 5/31/2013 | 327 | 158 | 7541 | 4778
6/1/13 to 6/30/13 | 454 | 285 | 11723 | 4182