## Averages
Date/Time | Total Net Power Output (Calcuated) | Gross Power Output (Veris) | Pump Parasitic Load | Cooling Fan Parasitic Load (Calculated) | Geothermal Header Hot Water Temperature | Hot Water Supply Temperature | Hot Water Return Temperature | Hot Water Supply Flow Rate | Ambient Temperature (GM Sensor) | Notes | MESO West Weather Data Station ID: HMHNV | Date/Time | Ambient Temperature | Relative Humidity | Wind Speed | Wind Gust | Wind Direction | Dew Point
| kW | kW | kW | kW | F | F | F | gpm | F |  |  |  | F | % | mph | mph | Degrees | F
7/31/2013 15:07:45 to 7/31/2013 16:06:55 | 17.7358 | 31.4959 | 1.497 | 12.2631 | 211.0463 | 218.6687 | 198.2617 | 145.3181 | 92.2407 | Flow rate very unstable from 15:17-15:43-fluctuations from 225gpm to 50gpm; stabilized at ~150gpm after 15:43; Fan speed manually set to 100% from 15:17-15:50 |  | 7-31-2013 15:30 PDT | 93 | 11 | 9 | 16 | 168 | 43.1

## Runtime Tally
Month of Runtime | Total Runtime (Incld's Factory) [hr] | Site Runtime [hr] | Total Gross Energy (Site Only) [kWh] | Gross Energy for Month [kWh] | Notes
2013-03-12 | 169 | - | 0 | - | Factory Hours
Start-Up to 3/31/2013 | 206 | 37 | 1741 | 1741
4/1/13 to 4/30/2013 | 225 | 56 | 2763 | 1022
5/1/13 to 5/31/2013 | 327 | 158 | 7541 | 4778
6/1/13 to 6/30/13 | 454 | 285 | 11723 | 4182
7/1/13 to 7/31/13 | 465 | 296 | 12122 | 399