## Averaged Data
Date/Time | Total Net Power Output (Calcuated) | Gross Power Output (Veris) | Pump Parasitic Load | Cooling Fan Parasitic Load (Veris) | Geothermal Header Hot Water Temperature | Hot Water Supply Temperature | Hot Water Return Temperature | Hot Water Supply Flow Rate | Ambient Temperature (GM Sensor) | Notes | MESO West Weather Data Station ID: HMHNV | Date/Time | Ambient Temperature | Relative Humidity | Wind Speed | Wind Gust | Wind Direction | Dew Point
| kW | kW | kW | kW | F | F | F | gpm | F |  |  |  | F | % | mph | mph | Degrees | F
8/6/2013 11:00:00 to 8/6/2013 11:59:50 | 28.5896 | 42.1258 | 2.5 | 11.0362 | 214.5271 | 224.6785 | 202.4557 | 151.8928 | 98.3718 |  |  | 8-6-2013 11:35 PDT | 91 | 11 | 9 | 18 | 17 | 41.6
8/6/2013 12:00:00 to 8/6/2013 12:59:50 | 29.2742 | 42.4927 | 2.5528 | 10.6656 | 215.4678 | 224.963 | 200.2986 | 151.3547 | 99.3798 |  |  | 8-6-2013 12:38 PDT | 93 | 11 | 8 | 18 | 350 | 43.1
8/6/2013 13:00:00 to 8/6/2013 13:59:50 | 26.4235 | 39.8111 | 2.6 | 10.7876 | 216.8833 | 225.2372 | 202.8617 | 151.0522 | 102.6319 |  |  | 8-6-2013 13:41 PDT | 94 | 9 | 5 | 12 | 27 | 40
8/6/2013 14:00:00 to 8/6/2013 14:59:50 | 23.2826 | 36.7768 | 2.6 | 10.8943 | 217.7369 | 225.2719 | 206.0161 | 150.7047 | 103.0692 |  |  | 8-6-2013 14:44 PDT | 95 | 9 | 9 | 19 | 329 | 40.7
8/6/2013 15:00:00 to 8/6/2013 15:59:50 | 22.1288 | 35.3163 | 2.6 | 10.5874 | 218.4547 | 225.3531 | 206.6342 | 150.6306 | 102.505 |  |  | 8-6-2013 15:26 PDT | 97 | 9 | 8 | 20 | 264 | 42.1
8/6/2013 16:00:00 to 8/6/2013 16:59:50 | 26.6573 | 39.5 | 2.6 | 10.2426 | 217.8411 | 225.3439 | 201.6019 | 150.5761 | 102.03 |  |  | 8-6-2013 16:29 PDT | 97 | 8 | 8 | 17 | 20 | 39.8
8/6/2013 17:00:00 to 8/6/2013 17:59:50 | 27.7817 | 40.4313 | 2.6 | 10.0496 | 218.1578 | 225.2797 | 200.4758 | 150.6044 | 100.3919 |  |  | 8-6-2013 17:32 PDT | 97 | 7 | 4 | 11 | 21 | 37.4
8/6/2013 18:00:00 to 8/6/2013 18:59:50 | 28.792 | 40.9429 | 2.6 | 9.5508 | 216.6097 | 225.0186 | 200.1583 | 150.6981 | 95.9294 |  |  | 8-6-2013 18:35 PDT | 93 | 8 | 1 | 5 | 55 | 37.1
8/8/2013 12:00:05 to 8/8/2013 12:59:55 | 33.7069 | 47.4173 | 2.5 | 11.2105 | 218.412 | 225.3063 | 199.3411 | 151.8146 | 95.6336 |  |  | 8-8-2013 12:32 PDT | 83 | 21 | 4 | 11 | 240 | 48.1
8/8/2013 13:00:05 to 8/8/2013 13:59:55 | 32.1311 | 46.0006 | 2.9475 | 10.922 | 217.3353 | 225.3569 | 200.2919 | 151.7941 | 96.2761 |  |  | 8-8-2013 13:35 PDT | 87 | 18 | 5 | 12 | 282 | 48.2
8/8/2013 14:00:05 to 8/8/2013 14:59:55 | 31.6312 | 45.3992 | 3.2 | 10.568 | 217.7145 | 225.3819 | 200.713 | 151.7539 | 94.1766 |  |  | 8-8-2013 14:38 PDT | 89 | 16 | 4 | 10 | 263 | 47.4
8/8/2013 19:00:04 to 8/8/2013 19:59:54 | 35.8078 | 48.6839 | 3.3 | 9.576 | 214.9817 | 224.4306 | 198.5386 | 153.4159 | 79.2803 |  |  | 8-8-2013 19:32 PDT | 73 | 29 | 3 | 10 | 291 | 46.4
8/8/2013 20:00:04 to 8/8/2013 20:59:54 | 37.2414 | 49.6429 | 3.3 | 9.1014 | 215.2528 | 224.5761 | 198.6658 | 153.1764 | 74.8528 |  |  | 8-8-2013 20:35 PDT | 71 | 33 | 4 | 8 | 154 | 47.2
8/11/2013 13:00:06 to 8/11/2013 13:59:56 | 32.2301 | 45.9211 | 2.5536 | 11.1373 | 217.3053 | 224.5561 | 199.7759 | 154.1773 | 96.6059 |  |  | 8-11-2013 13:44 PDT | 87 | 12 | 6 | 13 | 248 | 40.4
8/11/2013 14:00:06 to 8/11/2013 14:59:56 | 30.7055 | 43.3916 | 2.6 | 10.0861 | 215.5358 | 224.2675 | 201.0319 | 153.7006 | 92.0811 |  |  | 8-11-2013 14:26 PDT | 87 | 11 | 11 | 19 | 220 | 38.7
8/11/2013 20:00:04 to 8/11/2013 20:59:54 | 35.5401 | 47.5356 | 2.5156 | 9.4799 | 216.3808 | 224.7481 | 199.7756 | 156.0078 | 82.9883 |  |  | 8-11-2013 20:23 PDT | 78 | 15 | 3 | 6 | 339 | 37.8
8/11/2013 21:00:04 to 8/11/2013 21:59:54 | 36.3237 | 48.4906 | 2.6361 | 9.5308 | 214.7953 | 224.5547 | 199.1894 | 156.185 | 80.8069 |  |  | 8-11-2013 21:26 PDT | 75 | 15 | 8 | 11 | 55 | 35.5
8/11/2013 22:00:04 to 8/11/2013 22:59:54 | 36.735 | 48.7332 | 2.7 | 9.2981 | 216.9379 | 224.8547 | 199.2994 | 156.34 | 79.9114 |  |  | 8-11-2013 22:29 PDT | 73 | 16 | 4 | 7 | 83 | 35.2
8/11/2013 23:00:04 to 8/11/2013 23:59:54 | 36.7125 | 48.6336 | 2.7 | 9.2211 | 217.735 | 224.8467 | 200.1375 | 156.3244 | 77.9439 |  |  | 8-11-2013 23:32 PDT | 70 | 15 | 4 | 6 | 97 | 31.7
8/12/2013 00:00:34 to 8/12/2013 00:59:54 | 37.2835 | 49.0216 | 2.7236 | 9.0145 | 215.0871 | 224.4768 | 198.9048 | 156.0919 | 74.7563 |  |  | 8-12-2013 0:35 PDT | 73 | 15 | 7 | 10 | 165 | 34
8/12/2013 01:00:04 to 8/12/2013 01:59:54 | 35.6849 | 47.5076 | 2.8 | 9.0226 | 214.5872 | 224.4267 | 200.3306 | 156.1644 | 74.8833 |  |  | 8-12-2013 1:38 PDT | 73 | 18 | 9 | 15 | 167 | 37.3
8/12/2013 02:00:04 to 8/12/2013 02:59:54 | 35.7061 | 47.5529 | 2.8 | 9.0467 | 214.2789 | 224.4672 | 202.1361 | 156.1625 | 74.2278 |  |  | 8-12-2013 2:41 PDT | 71 | 22 | 6 | 9 | 178 | 39.4
8/12/2013 03:00:04 to 8/12/2013 03:59:54 | 38.1175 | 49.9414 | 2.8 | 9.024 | 215.4703 | 224.5922 | 198.7553 | 155.9161 | 73.4936 |  |  | 8-12-2013 3:23 PDT | 71 | 22 | 5 | 14 | 185 | 39.4
8/12/2013 04:00:04 to 8/12/2013 04:59:54 | 38.2387 | 50.3234 | 2.8 | 9.2846 | 216.4367 | 224.7 | 201.5708 | 156.2439 | 71.5036 |  |  | 8-12-2013 4:26 PDT | 62 | 27 | 2 | 6 | 353 | 35.8
8/12/2013 05:00:04 to 8/12/2013 05:59:54 | 40.0414 | 52.1564 | 3.1186 | 8.9964 | 217.5853 | 224.7917 | 198.3897 | 156.0864 | 69.6 |  |  | 8-12-2013 5:29 PDT | 61 | 30 | 3 | 6 | 80 | 36.9
8/12/2013 06:00:04 to 8/12/2013 06:59:54 | 39.9777 | 52.2844 | 3.2 | 9.1068 | 217.9283 | 224.7867 | 198.3785 | 155.8006 | 70.4096 |  |  | 8-12-2013 6:32 PDT | 61 | 31 | 2 | 5 | 49 | 37.5
8/12/2013 07:00:04 to 8/12/2013 07:59:54 | 29.5303 | 44.6856 | 3.1631 | 11.9922 | 218.6136 | 224.9769 | 206.625 | 155.8003 | 84.2714 |  |  | 8-12-2013 7:35 PDT | 68 | 25 | 3 | 6 | 325 | 39.4
8/12/2013 08:00:04 to 8/12/2013 08:59:54 | 25.988 | 42.0094 | 3 | 13.0214 | 218.2869 | 225.1388 | 207.1439 | 156.5225 | 93.0891 |  |  | 8-12-2013 8:38 PDT | 74 | 21 | 1 | 4 | 296 | 41
8/12/2013 09:00:04 to 8/12/2013 09:59:54 | 30.6047 | 46.1978 | 3 | 12.5931 | 218.0447 | 225.3011 | 205.2225 | 156.5853 | 99.5894 |  |  | 8-12-2013 9:20 PDT | 79 | 17 | 1 | 4 | 335 | 40.9
8/12/2013 12:00:09 to 8/12/2013 12:59:59 | 32.1189 | 45.6513 | 2.5 | 11.0324 | 217.7025 | 225.4228 | 201.4492 | 157.5519 | 98.1547 |  |  | 8-12-2013 12:30 PDT | 88 | 11 | 6 | 15 | 280 | 39.5
8/12/2013 13:00:09 to 8/12/2013 13:59:59 | 30.0985 | 43.1143 | 2.5 | 10.5157 | 216.8425 | 225.0911 | 203.2836 | 157.5128 | 96.8231 |  |  | 8-12-2013 13:33 PDT | 90 | 11 | 8 | 17 | 216 | 40.9
8/12/2013 14:00:09 to 8/12/2013 14:59:59 | 30.7162 | 43.072 | 2.5 | 9.8558 | 215.625 | 224.5833 | 201.3378 | 157.45 | 93.44 |  |  | 8-12-2013 14:36 PDT | 91 | 10 | 15 | 23 | 200 | 39.8
8/12/2013 15:00:09 to 8/12/2013 15:59:59 | 28.915 | 40.9512 | 2.5 | 9.5361 | 215.5594 | 224.5711 | 204.2808 | 157.3947 | 91.7111 |  |  | 8-12-2013 15:39 PDT | 91 | 10 | 13 | 21 | 203 | 39.8
8/12/2013 16:00:09 to 8/12/2013 16:59:59 | 29.6141 | 41.5259 | 2.5 | 9.4118 | 215.7064 | 224.7475 | 203.1189 | 157.1694 | 91.3989 |  |  | 8-12-2013 16:42 PDT | 91 | 9 | 10 | 17 | 202 | 37.9
8/12/2013 17:00:09 to 8/12/2013 17:59:59 | 31.3487 | 43.1148 | 2.5 | 9.2661 | 215.8606 | 224.7461 | 200.6475 | 157.0769 | 89.6911 |  |  | 8-12-2013 17:24 PDT | 89 | 9 | 11 | 18 | 182 | 36.5
8/12/2013 18:00:09 to 8/12/2013 18:59:59 | 31.7689 | 43.3591 | 2.5 | 9.0902 | 218.5167 | 225.2219 | 201.9197 | 157.2928 | 89.1 |  |  | 8-12-2013 18:27 PDT | 88 | 9 | 3 | 6 | 223 | 35.8
8/12/2013 19:00:09 to 8/12/2013 19:59:59 | 31.9464 | 43.6582 | 2.5314 | 9.1804 | 217.8717 | 225.0658 | 202.7639 | 157.4711 | 87.7097 |  |  | 8-12-2013 19:30 PDT | 84 | 10 | 4 | 7 | 182 | 34.8
8/12/2013 20:00:09 to 8/12/2013 20:59:59 | 34.12 | 46.2341 | 2.6672 | 9.4469 | 216.9006 | 225.0206 | 201.9672 | 157.6101 | 84.5844 |  |  | 8-12-2013 20:33 PDT | 75 | 12 | 2 | 7 | 73 | 31.5
8/12/2013 21:00:09 to 8/12/2013 21:59:59 | 35.5933 | 47.8053 | 2.7 | 9.512 | 215.6689 | 224.8467 | 199.5683 | 157.5839 | 82.4328 |  |  | 8-12-2013 21:36 PDT | 77 | 12 | 7 | 10 | 83 | 33
8/12/2013 22:00:09 to 8/12/2013 22:59:59 | 36.4073 | 48.4147 | 2.7 | 9.3073 | 217.7436 | 225.0072 | 199.6897 | 157.6499 | 81.0706 |  |  | 8-12-2013 22:39 PDT | 73 | 15 | 5 | 6 | 109 | 34
8/12/2013 23:00:09 to 8/12/2013 23:59:09 | 36.2322 | 48.0374 | 2.7 | 9.1052 | 216.2749 | 224.7225 | 200.6701 | 157.8685 | 76.72 |  |  | 8-12-2013 23:21 PDT | 72 | 17 | 5 | 7 | 168 | 35.5
8/13/2013 00:00:09 to 8/13/2013 00:59:59 | 35.4919 | 47.3107 | 2.8233 | 8.9955 | 215.7542 | 224.7183 | 201.5453 | 157.8286 | 76.9142 |  |  | 8-13-2013 0:24 PDT | 72 | 18 | 5 | 9 | 168 | 36.5
8/13/2013 01:00:09 to 8/13/2013 01:59:59 | 35.6286 | 47.9719 | 3.3 | 9.0434 | 214.4367 | 224.5239 | 199.9381 | 157.6914 | 75.9797 |  |  | 8-13-2013 1:27 PDT | 74 | 17 | 8 | 11 | 165 | 37
8/13/2013 02:00:09 to 8/13/2013 02:59:59 | 36.8291 | 49.1848 | 3.3 | 9.0557 | 215.5289 | 224.5397 | 199.4214 | 157.5339 | 74.7825 |  |  | 8-13-2013 2:30 PDT | 72 | 20 | 6 | 9 | 155 | 38.5
8/13/2013 03:00:09 to 8/13/2013 03:59:59 | 36.6368 | 48.9519 | 3.3 | 9.0152 | 217.2103 | 224.75 | 200.1453 | 157.7736 | 74.46 |  |  | 8-13-2013 3:33 PDT | 67 | 23 | 2 | 6 | 71 | 37
8/13/2013 04:00:09 to 8/13/2013 04:59:59 | 38.5207 | 50.9502 | 3.3 | 9.1295 | 217.1325 | 224.8775 | 199.9464 | 157.8606 | 72.6908 |  |  | 8-13-2013 4:36 PDT | 61 | 26 | 5 | 7 | 6 | 34.3
8/13/2013 05:00:09 to 8/13/2013 05:59:59 | 38.8055 | 51.1333 | 3.3 | 9.0278 | 217.0519 | 224.8158 | 199.0586 | 157.8525 | 70.3194 |  |  | 8-13-2013 5:39 PDT | 63 | 27 | 2 | 4 | 158 | 36.7
8/13/2013 06:00:09 to 8/13/2013 06:59:59 | 38.0046 | 50.3934 | 3.3 | 9.0888 | 217.5267 | 224.8192 | 201.0519 | 157.9369 | 69.9472 |  |  | 8-13-2013 6:21 PDT | 61 | 30 | 2 | 5 | 119 | 36.9
8/13/2013 07:00:09 to 8/13/2013 07:59:59 | 32.0137 | 46.5463 | 3.2433 | 11.2893 | 219.0275 | 225.0997 | 205.2647 | 158.4819 | 84.1603 |  |  | 8-13-2013 7:25 PDT | 70 | 25 | 0 | 4 | 196 | 41
8/13/2013 08:00:09 to 8/13/2013 08:59:59 | 36.1294 | 51.3391 | 3.2 | 12.0097 | 218.4311 | 225.1278 | 199.117 | 157.9446 | 93.1351 |  |  | 8-13-2013 8:28 PDT | 74 | 20 | 2 | 5 | 229 | 40.1
8/13/2013 09:00:09 to 8/13/2013 09:59:59 | 34.2405 | 49.7983 | 3.2 | 12.3578 | 218.8159 | 225.3716 | 200.2675 | 157.9217 | 100.2672 |  |  | 8-13-2013 9:31 PDT | 80 | 16 | 2 | 5 | 226 | 40.5
8/13/2013 10:00:09 to 8/13/2013 10:59:59 | 33.2906 | 48.5615 | 3.2 | 12.071 | 218.8539 | 225.4567 | 199.6797 | 156.7486 | 101.06 |  |  | 8-13-2013 10:34 PDT | 84 | 13 | 3 | 8 | 254 | 39.7
8/13/2013 11:00:09 to 8/13/2013 11:59:59 | 31.3439 | 45.8829 | 3.2 | 11.3391 | 217.9753 | 225.4767 | 201.3683 | 155.3258 | 98.88 |  |  | 8-13-2013 11:37 PDT | 86 | 12 | 4 | 9 | 241 | 39.6
8/13/2013 12:00:09 to 8/13/2013 12:59:59 | 30.2532 | 44.1202 | 3.2 | 10.667 | 216.5492 | 225.1158 | 200.9175 | 155.1256 | 97.3236 |  |  | 8-13-2013 12:40 PDT | 90 | 9 | 10 | 17 | 215 | 37.2
8/13/2013 13:00:09 to 8/13/2013 13:59:59 | 28.8994 | 42.4974 | 3.2 | 10.3979 | 216.4089 | 224.9758 | 201.7532 | 155.0809 | 96.6738 |  |  | 8-13-2013 13:44 PDT | 91 | 8 | 12 | 20 | 217 | 35.7
8/13/2013 14:00:09 to 8/13/2013 14:59:59 | 28.5157 | 41.4994 | 3.2 | 9.7837 | 215.3622 | 224.6065 | 201.4456 | 155.2366 | 94.6992 |  |  | 8-13-2013 14:26 PDT | 94 | 8 | 14 | 28 | 192 | 37.8
8/13/2013 15:00:09 to 8/13/2013 15:59:59 | 27.5151 | 40.1138 | 3.2 | 9.3988 | 215.1544 | 224.4884 | 203.1263 | 155.2603 | 92.6691 |  |  | 8-13-2013 15:29 PDT | 93 | 7 | 18 | 28 | 202 | 34.7
8/13/2013 16:00:09 to 8/13/2013 16:59:59 | 27.7561 | 40.3715 | 3.2 | 9.4153 | 215.8911 | 224.7461 | 203.1175 | 155.1128 | 92.415 |  |  | 8-13-2013 16:32 PDT | 93 | 7 | 11 | 20 | 206 | 34.7
8/13/2013 17:00:09 to 8/13/2013 17:59:59 | 29.8217 | 42.4208 | 3.2 | 9.3991 | 216.8494 | 225.065 | 200.3478 | 155.1186 | 91.9133 |  |  | 8-13-2013 17:35 PDT | 91 | 7 | 8 | 20 | 154 | 33.3
8/13/2013 18:00:09 to 8/13/2013 18:59:59 | 29.8787 | 42.4756 | 3.2 | 9.3969 | 217.6797 | 225.1067 | 201.0903 | 155.0989 | 91.5472 |  |  | 8-13-2013 18:38 PDT | 90 | 7 | 7 | 13 | 195 | 32.6
8/13/2013 19:00:09 to 8/13/2013 19:59:59 | 31.7949 | 44.2218 | 3.2 | 9.2269 | 217.7844 | 225.1094 | 200.1108 | 155.0721 | 88.9028 |  |  | 8-13-2013 19:20 PDT | 88 | 7 | 4 | 9 | 191 | 31.3
8/13/2013 20:00:09 to 8/13/2013 20:59:59 | 31.8022 | 44.2956 | 3.2 | 9.2933 | 217.4836 | 225.0867 | 201.7247 | 155.4089 | 85.1814 |  |  | 8-13-2013 20:23 PDT | 77 | 10 | 3 | 6 | 185 | 29.8
8/13/2013 21:00:09 to 8/13/2013 21:59:59 | 32.7389 | 45.4614 | 3.2 | 9.5225 | 216.8617 | 225.0967 | 203.4592 | 156.2017 | 82.4964 |  |  | 8-13-2013 21:26 PDT | 74 | 11 | 3 | 6 | 54 | 29.3
8/13/2013 22:00:09 to 8/13/2013 22:59:59 | 34.6431 | 47.3469 | 3.3508 | 9.353 | 216.5283 | 224.9867 | 200.0561 | 156.8696 | 81.2989 |  |  | 8-13-2013 22:29 PDT | 73 | 12 | 3 | 6 | 93 | 30
8/13/2013 23:00:09 to 8/13/2013 23:58:59 | 35.6762 | 48.4067 | 3.4 | 9.3305 | 216.2619 | 224.9393 | 199.0455 | 157.3303 | 79.941 |  |  | 8-13-2013 23:32 PDT | 73 | 12 | 7 | 8 | 93 | 30
8/14/2013 00:00:49 to 8/14/2013 00:59:59 | 35.9693 | 48.2925 | 3.4 | 8.9232 | 217.4859 | 224.9427 | 199.0803 | 156.6085 | 76.9458 |  |  | 8-14-2013 0:35 PDT | 72 | 13 | 1 | 4 | 158 | 30.7
8/14/2013 01:00:09 to 8/14/2013 01:59:59 | 36.3833 | 48.8128 | 3.4 | 9.0295 | 217.4081 | 224.7728 | 198.7878 | 155.4758 | 76.9436 |  |  | 8-14-2013 1:38 PDT | 70 | 14 | 6 | 9 | 113 | 30.5
8/14/2013 02:00:09 to 8/14/2013 02:59:59 | 36.0371 | 48.4416 | 3.4 | 9.0045 | 215.8289 | 224.7247 | 198.8181 | 154.8997 | 76.6903 |  |  | 8-14-2013 2:41 PDT | 70 | 16 | 4 | 9 | 195 | 32.8
8/14/2013 03:00:09 to 8/14/2013 03:59:52 | 36.4629 | 49.2123 | 3.3671 | 9.3823 | 217.375 | 224.8966 | 201.0789 | 155.4067 | 74.618 |  |  | 8-14-2013 3:23 PDT | 62 | 19 | 2 | 5 | 356 | 29.6
8/14/2013 04:00:02 to 8/14/2013 04:59:52 | 40.0472 | 52.6411 | 3.3 | 9.2939 | 217.5694 | 224.9103 | 198.0967 | 155.4297 | 70.7003 |  |  | 8-14-2013 4:26 PDT | 60 | 24 | 2 | 5 | 137 | 32.1
8/14/2013 05:00:02 to 8/14/2013 05:59:52 | 38.9001 | 51.0768 | 3.3 | 8.8768 | 216.5036 | 224.7558 | 198.3953 | 155.5312 | 69.1053 |  |  | 8-14-2013 5:29 PDT | 62 | 23 | 4 | 7 | 188 | 33
8/14/2013 06:00:02 to 8/14/2013 06:59:52 | 37.1509 | 49.5734 | 3.3 | 9.1225 | 217.0294 | 224.8108 | 201.7981 | 155.4194 | 70.7942 |  |  | 8-14-2013 6:32 PDT | 58 | 27 | 0 | 3 | 198 | 32.5
8/14/2013 07:00:02 to 8/14/2013 07:59:52 | 30.0577 | 44.5058 | 3.0997 | 11.3484 | 218.4592 | 225.0235 | 205.5073 | 155.6518 | 83.257 |  |  | 8-14-2013 7:35 PDT | 66 | 22 | 1 | 3 | 184 | 35.4
8/14/2013 08:00:02 to 8/14/2013 08:59:52 | 34.0651 | 48.8142 | 3 | 11.7491 | 218.4558 | 225.1467 | 201.6816 | 155.1204 | 93.1102 |  |  | 8-14-2013 8:38 PDT | 76 | 17 | 2 | 3 | 186 | 38.6
8/14/2013 13:00:06 to 8/14/2013 13:59:56 | 26.5221 | 40.1576 | 3.0219 | 10.6136 | 217.3464 | 225.2883 | 203.1658 | 154.5256 | 102.3492 |  |  | 8-14-2013 13:26 PDT | 95 | 8 | 3 | 11 | 285 | 38.5
8/14/2013 14:00:06 to 8/14/2013 14:59:56 | 27.8902 | 41.1115 | 3.2 | 10.0212 | 216.8253 | 225.0844 | 201.0769 | 154.4125 | 99.2122 |  |  | 8-14-2013 14:29 PDT | 96 | 7 | 9 | 18 | 223 | 36.7
8/14/2013 15:00:06 to 8/14/2013 15:59:56 | 27.5797 | 40.215 | 3.2 | 9.4353 | 216.5347 | 224.8575 | 200.8278 | 154.1992 | 96.595 |  |  | 8-14-2013 15:33 PDT | 97 | 6 | 14 | 23 | 198 | 34.5
8/14/2013 22:00:08 to 8/14/2013 22:59:58 | 33.4982 | 45.1827 | 2.4 | 9.2845 | 218.6301 | 225.191 | 201.5814 | 154.2555 | 84.5811 |  |  | 8-14-2013 22:33 PDT | 77 | 11 | 5 | 7 | 96 | 31.5
8/16/2013 21:00:01 to 8/16/2013 21:59:51 | 31.4033 | 44.4426 | 3.8 | 9.2393 | 215.8792 | 224.3694 | 198.3547 | 149.8678 | 85.1425 |  |  | 8-16-2013 21:29 PDT | 76 | 8 | 7 | 10 | 93 | 25.2
8/16/2013 22:00:01 to 8/16/2013 22:59:51 | 32.3532 | 45.5505 | 3.8 | 9.3974 | 217.0408 | 224.7844 | 199.0856 | 149.85 | 84.0231 |  |  | 8-16-2013 22:32 PDT | 73 | 9 | 3 | 6 | 213 | 25.1
8/16/2013 23:00:01 to 8/16/2013 23:59:21 | 32.3547 | 45.5438 | 3.8 | 9.3891 | 216.587 | 224.9108 | 199.4977 | 149.6878 | 81.9456 |  |  | 8-16-2013 23:35 PDT | 71 | 10 | 5 | 8 | 174 | 25.4
8/17/2013 00:00:01 to 8/17/2013 00:59:51 | 33.3419 | 46.3109 | 3.988 | 8.9809 | 215.4194 | 224.7175 | 197.778 | 149.4871 | 81.2 |  |  | 8-17-2013 0:38 PDT | 77 | 11 | 8 | 12 | 176 | 31.5
8/17/2013 01:00:01 to 8/17/2013 01:59:51 | 33.3057 | 46.278 | 4 | 8.9723 | 215.6122 | 224.7769 | 197.6647 | 149.5633 | 81.2 |  |  | 8-17-2013 1:20 PDT | 76 | 13 | 7 | 11 | 160 | 33.7
8/17/2013 02:00:01 to 8/17/2013 02:59:51 | 33.3411 | 46.3139 | 4 | 8.9728 | 215.6506 | 224.7961 | 197.6561 | 149.5044 | 80.8525 |  |  | 8-17-2013 2:23 PDT | 74 | 13 | 6 | 9 | 169 | 32.2
8/17/2013 03:00:01 to 8/17/2013 03:59:52 | 33.4272 | 46.3924 | 4 | 8.9652 | 215.7916 | 224.8531 | 197.8158 | 149.2237 | 80.251 |  |  | 8-17-2013 3:26 PDT | 72 | 17 | 5 | 8 | 184 | 35.5
8/17/2013 04:00:02 to 8/17/2013 04:59:52 | 33.8033 | 46.7471 | 4 | 8.9439 | 216.7221 | 225.0291 | 198.2404 | 149.3 | 79.8234 |  |  | 8-17-2013 4:29 PDT | 66 | 22 | 4 | 6 | 199 | 35.4
8/17/2013 05:00:02 to 8/17/2013 05:59:52 | 33.2816 | 46.7139 | 4 | 9.4323 | 217.1261 | 225.2169 | 200.6261 | 149.5781 | 78.7053 |  |  | 8-17-2013 5:32 PDT | 62 | 26 | 2 | 5 | 27 | 35.2
8/17/2013 06:00:02 to 8/17/2013 06:59:52 | 32.4684 | 46.2977 | 4 | 9.8293 | 217.4564 | 225.4342 | 202.9386 | 149.4719 | 76.8333 |  |  | 8-17-2013 6:35 PDT | 62 | 28 | 0 | 3 | 100 | 36.5
8/17/2013 07:00:02 to 8/17/2013 07:59:52 | 35.2971 | 49.1486 | 4 | 9.8515 | 218.0425 | 225.495 | 198.8597 | 148.1719 | 79.2586 |  |  | 8-17-2013 7:38 PDT | 66 | 24 | 0 | 2 | 168 | 37
8/17/2013 08:00:02 to 8/17/2013 08:59:52 | 32.5877 | 47.4177 | 4 | 10.83 | 219.0356 | 225.4597 | 200.3703 | 147.6147 | 88.6864 |  |  | 8-17-2013 8:20 PDT | 75 | 19 | 0 | 2 | 206 | 39.9
8/17/2013 09:00:02 to 8/17/2013 09:59:52 | 29.2389 | 44.3668 | 4 | 11.1279 | 218.9194 | 225.3183 | 201.1831 | 148.9061 | 96.6236 |  |  | 8-17-2013 9:23 PDT | 84 | 14 | 2 | 4 | 234 | 41
8/17/2013 10:00:02 to 8/17/2013 10:59:52 | 28.6279 | 43.6418 | 4 | 11.0139 | 218.2108 | 225.2964 | 200.1975 | 148.9596 | 99.2486 |  |  | 8-17-2013 10:26 PDT | 88 | 13 | 3 | 7 | 179 | 42.6
8/17/2013 11:00:02 to 8/17/2013 11:59:52 | 26.6433 | 41.7459 | 4 | 11.1026 | 218.4072 | 225.3939 | 202.0317 | 148.9376 | 101.7397 |  |  | 8-17-2013 11:29 PDT | 89 | 13 | 5 | 9 | 261 | 43.4
8/17/2013 12:00:02 to 8/17/2013 12:59:52 | 26.7933 | 41.856 | 4 | 11.0627 | 218.7866 | 225.5253 | 200.7894 | 148.8517 | 103.2593 |  |  | 8-17-2013 12:32 PDT | 92 | 12 | 3 | 7 | 258 | 44
8/17/2013 13:00:02 to 8/17/2013 13:59:52 | 26.8321 | 41.7075 | 4 | 10.8754 | 218.1393 | 225.4101 | 199.707 | 148.9224 | 103.2908 |  |  | 8-17-2013 13:35 PDT | 93 | 12 | 7 | 14 | 250 | 44.8
8/17/2013 14:00:02 to 8/17/2013 14:59:52 | 26.703 | 40.8878 | 4 | 10.1848 | 217.5261 | 225.0762 | 200.0255 | 148.8992 | 99.9174 |  |  | 8-17-2013 14:38 PDT | 94 | 11 | 9 | 13 | 230 | 43.8
8/17/2013 15:00:02 to 8/17/2013 15:59:52 | 25.5658 | 39.2411 | 4 | 9.6753 | 217.7994 | 225.191 | 201.0229 | 148.8682 | 98.3805 |  |  | 8-17-2013 15:20 PDT | 94 | 12 | 6 | 13 | 260 | 45.5
8/17/2013 16:00:02 to 8/17/2013 16:59:52 | 26.3642 | 40.0909 | 4 | 9.7267 | 219.2236 | 225.3975 | 199.8641 | 148.9697 | 98.1771 |  |  | 8-17-2013 16:23 PDT | 94 | 12 | 4 | 12 | 299 | 45.5
8/17/2013 17:00:02 to 8/17/2013 17:59:52 | 24.5876 | 38.3095 | 4 | 9.722 | 217.8225 | 225.1706 | 202.1503 | 148.9116 | 98.7893 |  |  | 8-17-2013 17:26 PDT | 93 | 12 | 4 | 12 | 294 | 44.8
8/17/2013 18:00:02 to 8/17/2013 18:59:52 | 25.8261 | 39.4671 | 4 | 9.641 | 215.4806 | 224.8003 | 199.7889 | 149.0028 | 97.1344 |  |  | 8-17-2013 18:30 PDT | 92 | 11 | 11 | 17 | 336 | 42.4
8/17/2013 19:00:02 to 8/17/2013 19:59:52 | 28.2708 | 41.727 | 4 | 9.4562 | 214.62 | 224.6439 | 199.0575 | 149.1028 | 93.8486 |  |  | 8-17-2013 19:33 PDT | 87 | 11 | 6 | 10 | 0 | 38.7
8/17/2013 20:00:02 to 8/17/2013 20:59:52 | 28.1748 | 41.5283 | 4 | 9.3534 | 213.9981 | 224.5908 | 200.0986 | 149.1444 | 89.9883 |  |  | 8-17-2013 20:36 PDT | 84 | 11 | 7 | 12 | 51 | 36.6
8/17/2013 21:00:02 to 8/17/2013 21:59:52 | 28.8021 | 41.9934 | 4 | 9.1914 | 216.1083 | 224.8919 | 200.6239 | 149.3872 | 88.7589 |  |  | 8-17-2013 21:39 PDT | 82 | 10 | 7 | 10 | 86 | 33.4
8/17/2013 22:00:02 to 8/17/2013 22:59:52 | 30.7624 | 44.1326 | 4 | 9.3702 | 217.4703 | 225.1042 | 199.5764 | 149.4289 | 88.0872 |  |  | 8-17-2013 22:21 PDT | 79 | 9 | 7 | 9 | 92 | 29.4
8/17/2013 23:00:02 to 8/17/2013 23:59:22 | 34.2407 | 47.7102 | 4 | 9.4695 | 218.1067 | 225.4297 | 197.7501 | 149.2796 | 84.7527 |  |  | 8-17-2013 23:24 PDT | 73 | 11 | 2 | 4 | 23 | 28.5
8/18/2013 00:00:02 to 8/18/2013 00:59:52 | 34.1301 | 47.7635 | 4 | 9.6333 | 218.5835 | 225.4623 | 198.4877 | 149.3363 | 83.4404 |  |  | 8-18-2013 0:27 PDT | 68 | 13 | 3 | 5 | 299 | 27.7
8/18/2013 01:00:02 to 8/18/2013 01:59:52 | 34.7883 | 48.3198 | 4 | 9.5315 | 217.5237 | 225.4597 | 198.3131 | 149.537 | 81.4619 |  |  | 8-18-2013 1:30 PDT | 71 | 12 | 4 | 7 | 58 | 28.5
8/18/2013 02:00:02 to 8/18/2013 02:59:52 | 34.6591 | 48.2477 | 4 | 9.5886 | 215.5347 | 225.3429 | 198.1404 | 149.5847 | 81.0907 |  |  | 8-18-2013 2:33 PDT | 67 | 12 | 5 | 7 | 337 | 25.6
8/18/2013 03:00:02 to 8/18/2013 03:59:52 | 35.3355 | 49.0799 | 4 | 9.7444 | 216.244 | 225.3411 | 198.4173 | 149.6813 | 79.6187 |  |  | 8-18-2013 3:36 PDT | 62 | 15 | 2 | 9 | 349 | 25.5
8/18/2013 04:00:02 to 8/18/2013 04:59:52 | 35.6806 | 49.3434 | 4 | 9.6627 | 212.6828 | 224.9589 | 197.2769 | 149.6278 | 77.0819 |  |  | 8-18-2013 4:39 PDT | 68 | 14 | 7 | 11 | 17 | 29
8/18/2013 05:00:02 to 8/18/2013 05:59:52 | 36.7191 | 50.1301 | 4 | 9.411 | 212.6139 | 224.8544 | 196.6269 | 149.7394 | 75.6603 |  |  | 8-18-2013 5:21 PDT | 66 | 17 | 8 | 12 | 10 | 30.8
8/18/2013 06:00:02 to 8/18/2013 06:59:52 | 38.0853 | 51.5584 | 4 | 9.4731 | 212.7764 | 224.755 | 196.0008 | 149.8667 | 72.8733 |  |  | 8-18-2013 6:24 PDT | 64 | 21 | 9 | 14 | 342 | 33

## Runtime Tally
Month of Runtime | Total Runtime (Incld's Factory) [hr] | Site Runtime [hr] | Total Gross Energy (Site Only) [kWh] | Gross Energy for Month [kWh] | Notes
2013-03-12 | 169 | - | 0 | - | Factory Hours
Start-Up to 3/31/2013 | 206 | 37 | 1741 | 1741
4/1/13 to 4/30/2013 | 225 | 56 | 2763 | 1022
5/1/13 to 5/31/2013 | 327 | 158 | 7541 | 4778
6/1/13 to 6/30/13 | 454 | 285 | 11723 | 4182
7/1/13 to 7/31/13 | 465 | 296 | 12122 | 399
8/1/13 to 8/31/13 | 599 | 430 | 18320 | 6198