## Average
Date/Time | Total Net Power Output (Calculated) | Gross Power Output (Veris) | Pump Parasitic Load | Cooling Fan Parasitic Load (Veris) | Geothermal Header Hot Water Temperature | Hot Water Supply Temperature | Hot Water Return Temperature | Hot Water Supply Flow Rate | Ambient Temperature (GM Sensor) | Notes | MESO West WeatherData | Date/Time | Ambient Temperature | Relative Humidity | Wind Speed | Wind Gust | Wind Direction
| kW | kW | kW | kW | F | F | F | gpm | F |  | Station ID: HMHNV |  | F | % | mph | mph | Degrees
9/1/2013 0:00 to 9/1/2013 0:59 | 30.1306 | 43.4852 | 4 | 9.3546 | 217.6564 | 225.2628 | 201.9361 | 150.6903 | 83.3553 |  |  | NOTE: Data not available from MesoWest until 9/4/13
9/1/2013 1:00 to 9/1/2013 1:59 | 32.8009 | 46.2594 | 4 | 9.4584 | 217.9535 | 225.2315 | 198.6797 | 150.5295 | 83.5997
9/1/2013 2:00 to 9/1/2013 2:59 | 33.1706 | 46.5727 | 4 | 9.4021 | 215.8917 | 225.0336 | 199.0669 | 150.6031 | 81.9917
9/1/2013 3:00 to 9/1/2013 3:59 | 34.2823 | 47.6486 | 4 | 9.3664 | 216.8448 | 225.1003 | 198.3022 | 150.5749 | 80.4
9/1/2013 4:00 to 9/1/2013 4:59 | 35.1998 | 48.8541 | 4 | 9.6543 | 216.7725 | 225.2838 | 198.393 | 150.4132 | 79.7608
9/1/2013 5:00 to 9/1/2013 5:59 | 35.6874 | 49.168 | 4 | 9.4806 | 217.8878 | 225.3693 | 197.6798 | 150.3125 | 79.2634
9/1/2013 7:01 to 9/1/2013 7:59 | 32.8701 | 46.4585 | 4 | 9.5884 | 217.6895 | 225.2523 | 200.0904 | 150.3655 | 80.7414
9/1/2013 8:00 to 9/1/2013 8:59 | 29.1752 | 43.7161 | 4 | 10.5409 | 218.6426 | 225.4885 | 203.8734 | 150.7988 | 85.9536
9/1/2013 9:00 to 9/1/2013 9:59 | 31.5149 | 45.9635 | 4 | 10.4486 | 217.7812 | 225.2475 | 200.0968 | 150.36 | 88.9307
9/1/2013 10:00 to 9/1/2013 10:59 | 27.9616 | 43.0247 | 4 | 11.0631 | 218.0344 | 225.2431 | 202.4492 | 150.6158 | 96.6411
9/1/2013 11:00 to 9/1/2013 11:59 | 27.1276 | 42.2192 | 4 | 11.0915 | 217.0514 | 225.2264 | 202.4947 | 150.6386 | 99.3878
9/1/2013 12:00 to 9/1/2013 12:59 | 27.2434 | 42.1822 | 4 | 10.9388 | 218.6279 | 225.3006 | 201.7112 | 150.624 | 99.7704
9/1/2013 13:00 to 9/1/2013 13:59 | 27.7619 | 42.2475 | 4 | 10.4856 | 218.5693 | 225.2643 | 200.8243 | 150.6827 | 98.5719
9/1/2013 14:00 to 9/1/2013 14:59 | 27.4701 | 41.7534 | 4 | 10.2833 | 218.4439 | 225.3618 | 200.3694 | 150.4636 | 98.4873
9/1/2013 15:00 to 9/1/2013 15:59 | 27.2499 | 41.0376 | 4 | 9.7877 | 218.1088 | 225.2745 | 200.3442 | 150.4326 | 98.002
9/1/2013 16:00 to 9/1/2013 16:59 | 26.2443 | 39.9348 | 4 | 9.6905 | 218.4183 | 225.0861 | 200.6589 | 150.5542 | 97.3181
9/1/2013 17:00 to 9/1/2013 17:59 | 27.0151 | 40.7631 | 4 | 9.748 | 218.6586 | 225.0042 | 200.0569 | 150.6853 | 96.6339
9/1/2013 18:00 to 9/1/2013 18:59 | 28.2036 | 41.7547 | 4 | 9.5511 | 217.4289 | 224.8433 | 199.2183 | 150.2392 | 94.5569
9/1/2013 19:00 to 9/1/2013 19:59 | 29.8782 | 43.3289 | 4 | 9.4508 | 217.4325 | 224.9406 | 199.0997 | 150.0828 | 91.4264
9/1/2013 20:00 to 9/1/2013 20:59 | 31.1682 | 44.4122 | 4 | 9.2439 | 216.3014 | 224.6625 | 198.64 | 150.0167 | 86.6619
9/1/2013 21:00 to 9/1/2013 21:59 | 31.2594 | 44.3751 | 4 | 9.1158 | 215.9847 | 224.6925 | 198.2861 | 150.0433 | 85.2478
9/1/2013 22:00 to 9/1/2013 22:59 | 31.4629 | 44.3702 | 4 | 8.9073 | 215.5567 | 224.82 | 198.5906 | 150.3336 | 83.4094
9/1/2013 23:00 to 9/1/2013 23:59 | 31.5865 | 44.5453 | 4 | 8.9588 | 215.7517 | 224.9489 | 199.4278 | 150.1669 | 82.6834
9/2/2013 0:01 to 9/2/2013 0:59 | 32.1269 | 45.0604 | 4 | 8.9336 | 215.7306 | 224.977 | 200.3507 | 150.3112 | 80.5918
9/2/2013 1:00 to 9/2/2013 1:59 | 34.1261 | 47.1011 | 4 | 8.975 | 214.8404 | 224.7867 | 198.1545 | 150.3904 | 78.5069
9/2/2013 2:00 to 9/2/2013 2:59 | 34.1495 | 47.1173 | 4 | 8.9678 | 214.8728 | 224.8047 | 197.9342 | 150.4247 | 77.3419
9/2/2013 3:00 to 9/2/2013 3:59 | 34.1105 | 47.1902 | 4 | 9.0796 | 217.1097 | 225.2519 | 199.2664 | 150.4106 | 79.2819
9/2/2013 4:00 to 9/2/2013 4:59 | 35.4122 | 48.6932 | 4 | 9.281 | 216.7558 | 225.2986 | 197.8875 | 150.46 | 80.2083
9/2/2013 5:00 to 9/2/2013 5:59 | 35.6986 | 49.0205 | 4 | 9.3219 | 216.9619 | 225.2683 | 197.6081 | 151.1889 | 79.4725
9/2/2013 6:00 to 9/2/2013 6:59 | 34.7974 | 48.2478 | 4 | 9.4504 | 217.7814 | 225.4061 | 199.8511 | 152.2908 | 79.2917
9/2/2013 7:00 to 9/2/2013 7:59 | 35.472 | 49.0483 | 4 | 9.5762 | 216.3103 | 225.2947 | 198.1244 | 152.8492 | 78.5167
9/2/2013 8:00 to 9/2/2013 8:59 | 31.9799 | 46.175 | 4 | 10.195 | 217.0036 | 225.0976 | 200.7039 | 152.7356 | 84.4363
9/2/2013 9:00 to 9/2/2013 9:58 | 33.2613 | 47.0658 | 4 | 9.8046 | 214.7325 | 224.6248 | 197.9122 | 150.8755 | 85.5245
9/2/2013 10:00 to 9/2/2013 10:59 | 31.0247 | 44.8148 | 4 | 9.7901 | 214.956 | 224.6205 | 198.7918 | 150.1702 | 87.9429
9/2/2013 11:00 to 9/2/2013 11:59 | 28.186 | 42.0536 | 4 | 9.8676 | 215.3521 | 224.6756 | 201.9334 | 150.7201 | 91.0521
9/2/2013 12:00 to 9/2/2013 12:59 | 26.7488 | 40.7109 | 4 | 9.9621 | 215.4025 | 224.6193 | 202.5133 | 151.0949 | 92.5286
9/2/2013 13:00 to 9/2/2013 13:59 | 29.4416 | 42.9822 | 4 | 9.5406 | 215.6133 | 224.3281 | 199.8181 | 151.1317 | 89.9647
9/2/2013 14:00 to 9/2/2013 14:59 | 27.3536 | 41.0422 | 4 | 9.6886 | 215.4233 | 224.4708 | 201.0608 | 151.0539 | 92.6472
9/2/2013 15:00 to 9/2/2013 15:59 | 28.5192 | 41.8789 | 4 | 9.3598 | 215.1839 | 224.2747 | 199.4206 | 150.5231 | 91.4836
9/2/2013 16:00 to 9/2/2013 16:59 | 28.9894 | 42.4448 | 4 | 9.4554 | 215.7983 | 224.3475 | 199.1817 | 150.2133 | 91.8397
9/2/2013 17:00 to 9/2/2013 17:59 | 30.9324 | 44.5677 | 4 | 9.6353 | 215.8956 | 224.315 | 198.2861 | 150.5669 | 88.5
9/2/2013 18:00 to 9/2/2013 18:59 | 32.347 | 45.9707 | 4 | 9.6237 | 214.6978 | 224.5661 | 197.9814 | 150.8136 | 85.3197
9/2/2013 19:00 to 9/2/2013 19:59 | 21.7599 | 31.2279 | 3.0382 | 6.4299 | 213.4764 | 217.7896 | 191.2031 | 105.4278 | 83.5466
9/2/2013 20:00 to 9/2/2013 20:59 | 33.9283 | 47.3801 | 3.7753 | 9.6766 | 212.4199 | 224.575 | 199.4073 | 153.8694 | 80.5812
9/2/2013 21:00 to 9/2/2013 21:59 | 35.9177 | 49.4595 | 4 | 9.5418 | 214.4303 | 225.0478 | 197.9292 | 154.0894 | 80.0522
9/2/2013 22:00 to 9/2/2013 22:59 | 36.0073 | 49.0986 | 4 | 9.0913 | 212.3467 | 224.6169 | 197.7725 | 154.1619 | 76.0264
9/2/2013 23:00 to 9/2/2013 23:59 | 36.5949 | 49.9735 | 4 | 9.3786 | 212.5944 | 224.6317 | 197.9966 | 154.0048 | 75.5992
9/3/2013 0:01 to 9/3/2013 0:59 | 37.2917 | 50.7345 | 4 | 9.4428 | 212.2703 | 224.5569 | 197.3234 | 153.8769 | 74.114
9/3/2013 1:00 to 9/3/2013 1:59 | 36.4463 | 49.822 | 4 | 9.3757 | 212.7931 | 224.75 | 198.6522 | 153.8853 | 73.405
9/3/2013 2:00 to 9/3/2013 2:59 | 35.7474 | 49.054 | 4 | 9.3066 | 214.7167 | 225.2444 | 201.4194 | 153.5822 | 74.2761
9/4/2013 9:00 to 9/4/2013 9:59 | 33.3582 | 48.3116 | 4 | 10.9535 | 216.3208 | 225.3981 | 200.4194 | 151.5592 | 85.5419 |  |  | 2013-09-04 09:30 | 72 | 61 | 2 | 4 | 325
9/4/2013 10:00 to 9/4/2013 10:59 | 32.9921 | 48.1745 | 4 | 11.1824 | 215.8806 | 225.1036 | 199.1181 | 150.7058 | 91.2678 |  |  | 2013-09-04 10:33 | 76 | 50 | 4 | 8 | 356
9/4/2013 11:00 to 9/4/2013 11:59 | 31.1131 | 46.2659 | 4 | 11.1528 | 217.4028 | 225.2081 | 200.8611 | 150.3803 | 94.3758 |  |  | 2013-09-04 11:36 | 82 | 40 | 4 | 7 | 222
9/4/2013 12:00 to 9/4/2013 12:59 | 31.389 | 46.0211 | 4 | 10.6322 | 217.0786 | 225.2592 | 199.1269 | 149.9353 | 95.1867 |  |  | 2013-09-04 12:39 | 86 | 31 | 3 | 7 | 150
9/4/2013 13:00 to 9/4/2013 13:59 | 29.3259 | 43.7561 | 4 | 10.4302 | 217.0989 | 225.1156 | 199.3908 | 149.86 | 96.6158 |  |  | 2013-09-04 13:21 | 86 | 30 | 6 | 13 | 232
9/4/2013 14:00 to 9/4/2013 14:59 | 28.4239 | 42.3173 | 4 | 9.8933 | 216.135 | 224.5681 | 199.4764 | 149.7444 | 95.0014 |  |  | 2013-09-04 14:25 | 88 | 21 | 12 | 21 | 212
9/4/2013 15:00 to 9/4/2013 15:59 | 26.8247 | 40.1942 | 4 | 9.3696 | 216.2572 | 224.615 | 200.8686 | 149.5864 | 93.4008 |  |  | 2013-09-04 15:28 | 91 | 20 | 9 | 15 | 157
9/4/2013 16:00 to 9/4/2013 16:59 | 26.5447 | 39.945 | 4 | 9.4003 | 216.04 | 224.5094 | 201.2367 | 149.4781 | 93.2619 |  |  | 2013-09-04 16:31 | 93 | 16 | 9 | 17 | 198
9/4/2013 17:00 to 9/4/2013 17:59 | 27.1076 | 40.3562 | 4 | 9.2486 | 215.0689 | 224.3928 | 201.3869 | 149.7311 | 90.9236 |  |  | 2013-09-04 17:34 | 88 | 20 | 11 | 17 | 198
9/4/2013 18:00 to 9/4/2013 18:59 | 28.7379 | 41.6871 | 4 | 8.9492 | 214.7181 | 224.3208 | 201.2744 | 149.8953 | 86.4867 |  |  | 2013-09-04 18:37 | 85 | 21 | 9 | 15 | 167
9/4/2013 19:00 to 9/4/2013 19:59 | 32.2683 | 45.6773 | 4 | 9.4091 | 215.5542 | 225.1017 | 200.533 | 150.0705 | 83.0888 |  |  | 2013-09-04 19:30 | 76 | 40 | 5 | 8 | 61
9/4/2013 20:00 to 9/4/2013 20:59 | 32.8278 | 46.3538 | 4 | 9.5261 | 216.3766 | 225.2051 | 200.8465 | 150.2606 | 82.3737 |  |  | 2013-09-04 20:33 | 72 | 42 | 4 | 9 | 359
9/4/2013 21:00 to 9/4/2013 21:59 | 35.5828 | 49.0349 | 4 | 9.4521 | 214.8128 | 225.1978 | 197.6218 | 150.3847 | 79.5794 |  |  | 2013-09-04 21:36 | 70 | 44 | 7 | 10 | 90
9/4/2013 22:00 to 9/4/2013 22:59 | 34.3268 | 47.6764 | 4 | 9.3495 | 217.2345 | 225.2802 | 198.8986 | 150.3644 | 80.656 |  |  | 2013-09-04 22:39 | 71 | 41 | 3 | 6 | 73
9/4/2013 23:00 to 9/4/2013 23:59 | 36.3147 | 49.9283 | 4 | 9.6136 | 217.1376 | 225.4587 | 197.5826 | 150.2121 | 80.598 |  |  | 2013-09-04 23:21 | 67 | 53 | 1 | 5 | 353
9/5/2013 0:01 to 9/5/2013 0:59 | 36.9315 | 50.4709 | 4 | 9.5393 | 216.6323 | 225.2929 | 197.3114 | 150.35 | 77.8694 |  |  | 2013-09-05 00:24 | 67 | 51 | 3 | 5 | 23
9/5/2013 1:00 to 9/5/2013 1:59 | 37.7941 | 51.1082 | 4 | 9.3141 | 216.6556 | 225.3219 | 196.9836 | 150.3381 | 75.1217 |  |  | 2013-09-05 01:27 | 64 | 63 | 2 | 5 | 175
9/5/2013 2:00 to 9/5/2013 2:59 | 35.5144 | 48.6853 | 4 | 9.1709 | 216.6172 | 225.2708 | 200.04 | 150.47 | 74.3911 |  |  | 2013-09-05 02:30 | 65 | 64 | 1 | 5 | 169
9/5/2013 3:00 to 9/5/2013 3:59 | 32.4739 | 46.1179 | 4 | 9.6441 | 217.6783 | 225.6419 | 203.4619 | 150.9 | 77.3333 |  |  | 2013-09-05 03:33 | 64 | 65 | 0 | 2 | 150
9/5/2013 4:00 to 9/5/2013 4:59 | 34.7206 | 48.5387 | 4 | 9.8181 | 217.7852 | 225.6243 | 201.8716 | 150.8939 | 77.3328 |  |  | 2013-09-05 04:36 | 63 | 59 | 4 | 5 | 20
9/5/2013 5:00 to 9/5/2013 5:59 | 37.3322 | 50.8843 | 4 | 9.5522 | 216.0275 | 225.208 | 199.1639 | 150.7512 | 72.7682 |  |  | 2013-09-05 05:39 | 58 | 79 | 1 | 4 | 169
9/5/2013 6:00 to 9/5/2013 6:59 | 38.4065 | 51.7414 | 4 | 9.3349 | 216.1284 | 225.3736 | 198.3355 | 150.9935 | 71.2429 |  |  | 2013-09-05 06:21 | 60 | 73 | 3 | 6 | 65
9/5/2013 7:00 to 9/5/2013 7:59 | 36.1861 | 49.7907 | 4 | 9.6046 | 214.3986 | 225.2256 | 200.9614 | 151.0522 | 72.9586 |  |  | 2013-09-05 07:24 | 62 | 73 | 3 | 6 | 28
9/5/2013 8:00 to 9/5/2013 8:59 | 31.8828 | 46.5602 | 4 | 10.6773 | 216.4039 | 225.4319 | 202.4464 | 150.9953 | 82.2847 |  |  | 2013-09-05 08:27 | 69 | 61 | 4 | 6 | 342
9/5/2013 9:00 to 9/5/2013 9:59 | 32.6205 | 47.7107 | 4 | 11.0902 | 216.2803 | 225.2283 | 200.7103 | 150.7728 | 88.6275 |  |  | 2013-09-05 09:30 | 74 | 48 | 6 | 11 | 6
9/5/2013 10:00 to 9/5/2013 10:59 | 31.8176 | 46.9706 | 4 | 11.1529 | 217.7183 | 225.1756 | 199.9547 | 151.5775 | 93.1208 |  |  | 2013-09-05 10:33 | 80 | 35 | 4 | 7 | 312
9/5/2013 11:00 to 9/5/2013 11:59 | 31.699 | 46.7787 | 4 | 11.0797 | 218.2864 | 225.2392 | 198.9433 | 152.9089 | 96.2819 |  |  | 2013-09-05 11:36 | 84 | 27 | 5 | 10 | 260
9/5/2013 12:00 to 9/5/2013 12:59 | 29.2742 | 43.1057 | 4 | 9.8315 | 214.1736 | 224.3414 | 199.1817 | 153.9756 | 93.0347 |  |  | 2013-09-05 12:39 | 88 | 20 | 16 | 26 | 198
9/5/2013 13:00 to 9/5/2013 13:59 | 28.9461 | 42.319 | 4 | 9.3728 | 212.8872 | 223.8267 | 198.8892 | 153.0189 | 91.5969 |  |  | 2013-09-05 13:21 | 90 | 19 | 19 | 34 | 209
9/5/2013 14:00 to 9/5/2013 14:59 | 28.4459 | 41.6478 | 4 | 9.2018 | 212.3175 | 223.7078 | 198.7769 | 150.5631 | 90.9394 |  |  | 2013-09-05 14:24 | 89 | 18 | 22 | 34 | 192
9/5/2013 15:00 to 9/5/2013 15:59 | 25.9201 | 38.9157 | 4 | 8.9957 | 212.4256 | 223.5358 | 201.0094 | 149.5381 | 89.9883 |  |  | 2013-09-05 15:27 | 88 | 15 | 25 | 41 | 193
9/5/2013 16:00 to 9/5/2013 16:59 | 23.6492 | 36.6821 | 4 | 9.0329 | 213.1611 | 223.4578 | 203.0492 | 150.1933 | 91.4358 |  |  | 2013-09-05 16:30 | 91 | 11 | 21 | 30 | 217
9/5/2013 17:00 to 9/5/2013 17:59 | 27.5749 | 40.6392 | 4 | 9.0643 | 212.7225 | 223.1606 | 199.9656 | 150.4586 | 90.1353 |  |  | 2013-09-05 17:33 | 87 | 13 | 22 | 33 | 229
9/5/2013 18:00 to 9/5/2013 18:59 | 29.9602 | 43.0528 | 4 | 9.0926 | 213.4281 | 223.085 | 198.8017 | 150.5511 | 86.5011 |  |  | 2013-09-05 18:36 | 84 | 13 | 18 | 28 | 227
9/5/2013 19:00 to 9/5/2013 19:59 | 33.1811 | 46.127 | 4 | 8.9459 | 215.1394 | 224.4044 | 198.4364 | 150.3914 | 82.6339 |  |  | 2013-09-05 19:39 | 77 | 19 | 8 | 12 | 205
9/5/2013 20:00 to 9/5/2013 20:59 | 34.9494 | 48.0998 | 4 | 9.1504 | 215.9411 | 225.1017 | 197.9089 | 150.0878 | 79.9222 |  |  | 2013-09-05 20:21 | 73 | 16 | 8 | 12 | 203
9/5/2013 21:00 to 9/5/2013 21:59 | 34.9567 | 48.1046 | 4 | 9.1479 | 216.6125 | 225.2144 | 198.3728 | 149.9872 | 78.5136 |  |  | 2013-09-05 21:24 | 70 | 17 | 5 | 9 | 202
9/5/2013 22:00 to 9/5/2013 22:59 | 34.6436 | 47.9296 | 4 | 9.286 | 216.5669 | 225.1622 | 199.7922 | 150.1969 | 77.6036 |  |  | 2013-09-05 22:27 | 67 | 20 | 4 | 6 | 189
9/5/2013 23:00 to 9/5/2013 23:59 | 35.9094 | 49.1443 | 4 | 9.2348 | 216.3897 | 225.2659 | 199.6296 | 150.6036 | 75.5584 |  |  | 2013-09-05 23:31 | 63 | 24 | 5 | 7 | 56
9/6/2013 0:00 to 9/6/2013 0:59 | 35.7788 | 49.1599 | 4 | 9.3811 | 213.5541 | 225.0613 | 198.8916 | 150.4808 | 74.7 |  |  | 2013-09-06 00:34 | 65 | 22 | 4 | 7 | 44
9/6/2013 1:00 to 9/6/2013 1:59 | 37.3606 | 50.6695 | 4 | 9.3088 | 214.1233 | 225.1066 | 197.0689 | 150.2317 | 74.1921 |  |  | 2013-09-06 01:37 | 63 | 23 | 5 | 8 | 48
9/6/2013 2:00 to 9/6/2013 2:59 | 37.2483 | 50.3745 | 4 | 9.1262 | 214.1528 | 225 | 197.6746 | 150.3881 | 71.8633 |  |  | 2013-09-06 02:40 | 62 | 23 | 6 | 9 | 52
9/6/2013 3:00 to 9/6/2013 3:59 | 36.3136 | 49.728 | 4 | 9.4144 | 213.7225 | 225.0681 | 199.9512 | 150.4412 | 72.0415 |  |  | 2013-09-06 03:22 | 60 | 25 | 4 | 7 | 37
9/6/2013 4:00 to 9/6/2013 4:59 | 36.2742 | 49.5517 | 4 | 9.2775 | 213.5748 | 225.0264 | 200.7188 | 150.2948 | 70.9921 |  |  | 2013-09-06 04:25 | 62 | 23 | 5 | 9 | 55
9/6/2013 5:00 to 9/6/2013 5:59 | 37.1515 | 50.511 | 4 | 9.3594 | 213.6769 | 225.1 | 199.9316 | 150.3368 | 70.9491 |  |  | 2013-09-06 05:28 | 58 | 29 | 4 | 7 | 48
9/6/2013 6:00 to 9/6/2013 6:59 | 38.6151 | 52.0043 | 4 | 9.3892 | 212.3407 | 224.8624 | 197.4248 | 150.6342 | 69.8379 |  |  | 2013-09-06 06:31 | 56 | 32 | 7 | 8 | 25
9/6/2013 7:00 to 9/6/2013 7:59 | 38.7101 | 52.1201 | 4 | 9.4099 | 212.1215 | 224.731 | 196.5389 | 150.2932 | 70.2687 |  |  | 2013-09-06 07:34 | 63 | 28 | 4 | 7 | 28
9/6/2013 9:00 to 9/6/2013 9:59 | 28.5595 | 43.8492 | 4 | 11.2897 | 214.5269 | 225.2568 | 204.1698 | 149.0855 | 84.7782 |  |  | 2013-09-06 09:40 | 70 | 21 | 5 | 9 | 344
9/6/2013 10:00 to 9/6/2013 10:59 | 33.2588 | 48.7305 | 4 | 11.4717 | 215.1898 | 225.2251 | 199.5329 | 150.4052 | 89.0105 |  |  | 2013-09-06 10:33 | 73 | 20 | 5 | 10 | 344
9/6/2013 11:00 to 9/6/2013 11:59 | 32.7745 | 48.0208 | 4 | 11.2463 | 216.7453 | 225.066 | 199.855 | 150.3138 | 90.3094 |  |  | 2013-09-06 11:36 | 77 | 15 | 6 | 15 | 335
9/6/2013 12:00 to 9/6/2013 12:59 | 33.6011 | 48.6083 | 4 | 11.0072 | 217.533 | 225.1378 | 198.5028 | 150.1108 | 91.4369 |  |  | 2013-09-06 12:39 | 79 | 14 | 7 | 13 | 295
9/6/2013 13:00 to 9/6/2013 13:59 | 31.7512 | 46.4698 | 4 | 10.7185 | 217.3708 | 225.1389 | 199.7047 | 150.0989 | 91.9908 |  |  | 2013-09-06 13:21 | 80 | 15 | 5 | 15 | 354
9/6/2013 14:00 to 9/6/2013 14:59 | 31.8297 | 46.413 | 4 | 10.5833 | 217.6853 | 225.1036 | 198.9978 | 150.0817 | 92.5317 |  |  | 2013-09-06 14:24 | 82 | 14 | 6 | 16 | 304
9/6/2013 15:00 to 9/6/2013 15:59 | 32.6185 | 46.6077 | 4 | 9.9892 | 216.4383 | 224.9683 | 199.0672 | 150.1381 | 90.0492 |  |  | 2013-09-06 15:27 | 84 | 13 | 9 | 19 | 333
9/6/2013 16:00 to 9/6/2013 16:59 | 31.7084 | 45.6001 | 4 | 9.8917 | 217.7989 | 225.0411 | 198.9031 | 150.2053 | 88.7175 |  |  | 2013-09-06 16:30 | 84 | 13 | 7 | 13 | 305
9/6/2013 17:00 to 9/6/2013 17:59 | 32.0352 | 45.6813 | 4 | 9.6461 | 214.78 | 224.5367 | 198.6208 | 150.4292 | 87.4636 |  |  | 2013-09-06 17:33 | 82 | 13 | 9 | 15 | 323
9/6/2013 18:00 to 9/6/2013 18:59 | 32.2931 | 45.7469 | 4 | 9.4538 | 213.5633 | 224.5475 | 198.3611 | 150.5792 | 85.2736 |  |  | 2013-09-06 18:36 | 80 | 13 | 8 | 12 | 346
9/6/2013 19:00 to 9/6/2013 19:59 | 32.7773 | 46.2169 | 4 | 9.4396 | 212.98 | 224.9358 | 199.3389 | 150.4514 | 82.9783 |  |  | 2013-09-06 19:39 | 74 | 14 | 7 | 10 | 44
9/6/2013 20:00 to 9/6/2013 20:59 | 34.2248 | 47.5321 | 4 | 9.3073 | 213.9367 | 225.0567 | 198.1081 | 150.5031 | 80.9428 |  |  | 2013-09-06 20:21 | 72 | 14 | 7 | 9 | 66
9/6/2013 21:00 to 9/6/2013 21:59 | 35.2114 | 48.5018 | 4 | 9.2904 | 215.7475 | 225.3117 | 198.2297 | 150.6211 | 79.9125 |  |  | 2013-09-06 21:24 | 69 | 16 | 6 | 8 | 83
9/6/2013 22:00 to 9/6/2013 22:59 | 34.8334 | 48.4442 | 4 | 9.6108 | 216.7775 | 225.4811 | 200.7356 | 150.6611 | 79.4547 |  |  | 2013-09-06 22:27 | 62 | 21 | 3 | 5 | 64
9/6/2013 23:00 to 9/6/2013 23:59 | 36.1609 | 50.0764 | 4 | 9.9155 | 215.7296 | 225.4493 | 200.0304 | 150.7682 | 76.7715 |  |  | 2013-09-06 23:30 | 59 | 23 | 5 | 7 | 322
9/7/2013 0:01 to 9/7/2013 0:59 | 36.0105 | 49.1982 | 4 | 9.1877 | 209.6243 | 224.3111 | 197.0231 | 150.7666 | 72.6589 |  |  | 2013-09-07 00:33 | 69 | 21 | 12 | 19 | 58
9/7/2013 1:00 to 9/7/2013 1:59 | 36.4873 | 49.5901 | 4 | 9.1027 | 209.2133 | 224.0236 | 197.0836 | 150.7075 | 72.0861 |  |  | 2013-09-07 01:36 | 67 | 21 | 14 | 20 | 45
9/7/2013 2:00 to 9/7/2013 2:59 | 36.8132 | 49.8952 | 4 | 9.082 | 209.1667 | 224.215 | 196.9292 | 150.6953 | 70.5458 |  |  | 2013-09-07 02:39 | 65 | 23 | 11 | 15 | 45
9/7/2013 3:00 to 9/7/2013 3:59 | 37.9182 | 51.1967 | 4 | 9.2785 | 211.3036 | 224.5042 | 197.3786 | 150.7019 | 69.2453 |  |  | 2013-09-07 03:21 | 59 | 29 | 6 | 10 | 357
9/7/2013 4:00 to 9/7/2013 4:59 | 39.4051 | 52.6419 | 4 | 9.2368 | 211.4422 | 224.6814 | 196.5819 | 150.8794 | 66.6819 |  |  | 2013-09-07 04:24 | 55 | 33 | 6 | 11 | 17
9/7/2013 5:00 to 9/7/2013 5:59 | 38.9366 | 52.1727 | 4 | 9.2361 | 211.1139 | 224.5933 | 197.27 | 151.0764 | 65.1161 |  |  | 2013-09-07 05:27 | 54 | 37 | 5 | 8 | 6
9/7/2013 6:00 to 9/7/2013 6:59 | 39.2678 | 52.5435 | 4 | 9.2756 | 210.5627 | 224.5204 | 197.2863 | 151.2291 | 63.0468 |  |  | 2013-09-07 06:30 | 51 | 42 | 7 | 11 | 13
9/7/2013 7:00 to 9/7/2013 7:59 | 38.7593 | 52.0945 | 4 | 9.3352 | 210.8288 | 224.5974 | 198.6302 | 151.1823 | 63.7116 |  |  | 2013-09-07 07:33 | 55 | 39 | 7 | 13 | 357
9/7/2013 8:00 to 9/7/2013 8:59 | 36.8486 | 50.8174 | 4 | 9.9689 | 212.6747 | 224.648 | 198.3075 | 151.2101 | 72.1707 |  |  | 2013-09-07 08:36 | 64 | 32 | 11 | 14 | 333
9/7/2013 9:00 to 9/7/2013 9:59 | 35.43 | 49.8847 | 4 | 10.4547 | 212.3361 | 224.7517 | 197.6297 | 151.1172 | 80.3486 |  |  | 2013-09-07 09:39 | 71 | 27 | 10 | 17 | 28
9/7/2013 10:00 to 9/7/2013 10:59 | 30.7765 | 45.7676 | 4 | 10.9911 | 214.3581 | 225.0836 | 202.1153 | 151.3586 | 86.3275 |  |  | 2013-09-07 10:21 | 73 | 24 | 10 | 15 | 335
9/7/2013 11:00 to 9/7/2013 11:59 | 27.5957 | 42.998 | 4 | 11.4023 | 216.4122 | 225.1392 | 204.3933 | 151.5356 | 91.2844 |  |  | 2013-09-07 11:24 | 77 | 22 | 5 | 11 | 325
9/7/2013 12:00 to 9/7/2013 12:59 | 26.9014 | 41.9285 | 4 | 11.0271 | 217.9711 | 225.2817 | 204.5239 | 151.4747 | 93.1981 |  |  | 2013-09-07 12:27 | 84 | 16 | 4 | 8 | 305
9/7/2013 13:00 to 9/7/2013 13:59 | 26.4474 | 41.4274 | 4 | 10.9801 | 218.7189 | 225.4308 | 204.4397 | 151.3803 | 95.3814 |  |  | 2013-09-07 13:31 | 87 | 13 | 6 | 12 | 253
9/7/2013 14:00 to 9/7/2013 14:59 | 28.8784 | 43.5706 | 4 | 10.6921 | 218.4572 | 225.4056 | 201.5433 | 151.0428 | 95.9006 |  |  | 2013-09-07 14:34 | 87 | 13 | 7 | 20 | 215
9/7/2013 15:00 to 9/7/2013 15:59 | 29.3462 | 43.0201 | 4 | 9.6739 | 216.7214 | 224.8256 | 199.4633 | 150.8244 | 92.8589 |  |  | 2013-09-07 15:37 | 89 | 11 | 9 | 17 | 195
9/7/2013 16:00 to 9/7/2013 16:59 | 28.224 | 41.6799 | 4 | 9.4559 | 217.5011 | 225.0673 | 201.627 | 150.7403 | 91.1148 |  |  | 2013-09-07 16:40 | 88 | 11 | 5 | 13 | 158
9/7/2013 17:00 to 9/7/2013 17:59 | 30.2665 | 43.6345 | 4 | 9.368 | 217.5784 | 225.0461 | 199.4708 | 150.9434 | 90.758 |  |  | 2013-09-07 17:22 | 89 | 11 | 5 | 9 | 196
9/7/2013 18:00 to 9/7/2013 18:59 | 30.0763 | 43.5922 | 4 | 9.5159 | 217.3668 | 224.8531 | 199.4213 | 151.2116 | 90.25 |  |  | 2013-09-07 18:25 | 86 | 8 | 8 | 13 | 243
9/7/2013 19:00 to 9/7/2013 19:59 | 32.2847 | 45.7236 | 4 | 9.4389 | 217.3394 | 225.1344 | 199.185 | 151.0072 | 86.9728 |  |  | 2013-09-07 19:28 | 75 | 12 | 1 | 4 | 182
9/7/2013 20:00 to 9/7/2013 20:59 | 33.2887 | 46.8042 | 4 | 9.5156 | 214.4419 | 225.0758 | 198.6694 | 150.9847 | 84.4503 |  |  | 2013-09-07 20:31 | 75 | 15 | 5 | 8 | 62
9/7/2013 21:00 to 9/7/2013 21:59 | 33.4952 | 46.8518 | 4 | 9.3566 | 215.9253 | 225.1622 | 199.0861 | 151.2839 | 82.5739 |  |  | 2013-09-07 21:34 | 71 | 17 | 5 | 8 | 80
9/7/2013 22:00 to 9/7/2013 22:59 | 33.0945 | 46.2703 | 4 | 9.1758 | 218.11 | 225.3889 | 200.6825 | 151.1406 | 82.1639 |  |  | 2013-09-07 22:37 | 70 | 17 | 5 | 7 | 104
9/7/2013 23:00 to 9/7/2013 23:59 | 34.2822 | 47.9559 | 4 | 9.6737 | 216.9935 | 225.461 | 200.3815 | 151.0185 | 80.5893 |  |  | 2013-09-07 23:40 | 62 | 23 | 2 | 4 | 123
9/8/2013 0:02 to 9/8/2013 0:59 | 35.3188 | 48.4549 | 4 | 9.1361 | 215.5677 | 225.0055 | 197.6767 | 151.2343 | 77.5942 |  |  | 2013-09-08 00:22 | 65 | 22 | 4 | 6 | 199
9/8/2013 1:00 to 9/8/2013 1:59 | 35.0255 | 48.0271 | 4 | 9.0016 | 214.8561 | 224.8028 | 197.8694 | 152.2408 | 77.3792 |  |  | 2013-09-08 01:25 | 73 | 19 | 9 | 14 | 164
9/8/2013 2:00 to 9/8/2013 2:59 | 35.124 | 48.711 | 4 | 9.587 | 216.7189 | 225.295 | 199.9864 | 153.35 | 75.7217 |  |  | 2013-09-08 02:28 | 61 | 26 | 5 | 7 | 35
9/8/2013 3:00 to 9/8/2013 3:59 | 38.0392 | 51.5107 | 4 | 9.4715 | 217.0717 | 225.3389 | 197.3058 | 153.6589 | 73.5264 |  |  | 2013-09-08 03:31 | 58 | 31 | 3 | 6 | 162
9/8/2013 4:00 to 9/8/2013 4:59 | 35.9279 | 49.1986 | 4 | 9.2708 | 216.4136 | 225.2159 | 200.5062 | 152.6504 | 72.4963 |  |  | 2013-09-08 04:34 | 55 | 34 | 0 | 1 | 123
9/8/2013 5:00 to 9/8/2013 5:59 | 37.8714 | 51.3184 | 4 | 9.4471 | 216.7567 | 225.2578 | 199.1769 | 151.1245 | 70.6433 |  |  | 2013-09-08 05:37 | 54 | 38 | 3 | 5 | 202
9/8/2013 6:00 to 9/8/2013 6:59 | 39.7598 | 53.1577 | 4 | 9.3979 | 217.2 | 225.3626 | 196.6411 | 150.8742 | 68.8317 |  |  | 2013-09-08 06:40 | 53 | 38 | 2 | 4 | 150
9/8/2013 7:00 to 9/8/2013 7:59 | 38.3931 | 51.8468 | 4 | 9.4537 | 216.8353 | 225.3329 | 197.535 | 151.0703 | 70.5741 |  |  | 2013-09-08 07:44 | 61 | 28 | 0 | 2 | 203
9/8/2013 8:00 to 9/8/2013 8:59 | 33.2167 | 47.9413 | 4 | 10.7246 | 217.9506 | 225.5257 | 202.8799 | 151.4144 | 80.3335 |  |  | 2013-09-08 08:26 | 63 | 28 | 1 | 3 | 243
9/8/2013 9:00 to 9/8/2013 9:59 | 26.4131 | 42.077 | 4 | 11.664 | 218.174 | 225.5236 | 205.0069 | 151.652 | 90.4054 |  |  | 2013-09-08 09:29 | 73 | 20 | 2 | 5 | 222
9/8/2013 10:00 to 9/8/2013 10:59 | 27.9799 | 43.4001 | 4 | 11.4202 | 217.809 | 225.2299 | 203.3063 | 151.1397 | 94.8331 |  |  | 2013-09-08 10:32 | 81 | 16 | 3 | 8 | 208
9/8/2013 11:00 to 9/8/2013 11:59 | 30.6019 | 45.4373 | 4 | 10.8354 | 217.4377 | 225.2158 | 200.3731 | 150.4494 | 95.8956 |  |  | 2013-09-08 11:35 | 84 | 13 | 5 | 13 | 210
9/8/2013 12:00 to 9/8/2013 12:59 | 30.0396 | 44.4401 | 4 | 10.4005 | 217.6302 | 225.2272 | 200.2963 | 150.2185 | 95.1207 |  |  | 2013-09-08 12:38 | 86 | 11 | 5 | 13 | 253
9/8/2013 13:00 to 9/8/2013 13:59 | 26.4841 | 41.1654 | 4 | 10.6813 | 218.2215 | 225.3883 | 203.5779 | 150.5132 | 97.7574 |  |  | 2013-09-08 13:20 | 86 | 11 | 5 | 9 | 44
9/8/2013 14:00 to 9/8/2013 14:59 | 28.3962 | 43.0312 | 4 | 10.635 | 216.8161 | 225.1283 | 200.7681 | 150.6983 | 97.6008 |  |  | 2013-09-08 14:24 | 88 | 10 | 7 | 17 | 336
9/8/2013 15:00 to 9/8/2013 15:59 | 28.7944 | 42.8192 | 4 | 10.0247 | 217.6589 | 225.2706 | 200.9878 | 150.3586 | 95.0636 |  |  | 2013-09-08 15:27 | 90 | 9 | 3 | 9 | 268
9/8/2013 16:00 to 9/8/2013 16:59 | 29.7573 | 43.5977 | 4 | 9.8404 | 218.0133 | 225.0458 | 199.17 | 150.2553 | 93.5531 |  |  | 2013-09-08 16:30 | 88 | 8 | 7 | 16 | 299
9/8/2013 17:00 to 9/8/2013 17:59 | 29.5394 | 43.2263 | 4 | 9.6868 | 217.3575 | 224.9156 | 199.5064 | 150.4892 | 92.1697 |  |  | 2013-09-08 17:33 | 87 | 9 | 8 | 14 | 329
9/8/2013 18:00 to 9/8/2013 18:59 | 29.537 | 43.1301 | 4 | 9.5931 | 217.5969 | 224.85 | 200.7028 | 150.5786 | 90.5433 |  |  | 2013-09-08 18:36 | 84 | 11 | 7 | 12 | 319
9/8/2013 19:00 to 9/8/2013 19:59 | 31.302 | 44.8492 | 4 | 9.5472 | 216.1947 | 225.0006 | 200.9869 | 150.3939 | 87.6858 |  |  | 2013-09-08 19:39 | 73 | 17 | 2 | 4 | 41
9/8/2013 20:00 to 9/8/2013 20:59 | 33.2404 | 46.6174 | 4 | 9.377 | 215.5256 | 225.2314 | 198.5603 | 150.6206 | 84.5953 |  |  | 2013-09-08 20:21 | 75 | 17 | 7 | 8 | 83
9/8/2013 21:00 to 9/8/2013 21:59 | 33.3673 | 46.6223 | 4 | 9.255 | 213.6322 | 224.9481 | 198.3767 | 150.7825 | 82.8361 |  |  | 2013-09-08 21:24 | 76 | 18 | 8 | 11 | 51
9/8/2013 22:00 to 9/8/2013 22:59 | 33.1119 | 46.2445 | 4 | 9.1325 | 212.5814 | 224.7914 | 198.3119 | 150.3017 | 80.6739 |  |  | 2013-09-08 22:27 | 74 | 21 | 9 | 13 | 72
9/8/2013 23:00 to 9/8/2013 23:59 | 32.7533 | 46.0266 | 4 | 9.2732 | 212.2706 | 224.8036 | 199.9241 | 149.0779 | 79.6992 |  |  | 2013-09-08 23:30 | 72 | 23 | 10 | 14 | 55
9/9/2013 0:02 to 9/9/2013 0:59 | 32.3446 | 45.4159 | 4 | 9.0713 | 210.6647 | 224.4468 | 201.0546 | 149.6842 | 77.8991 |  |  | 2013-09-09 00:33 | 72 | 25 | 11 | 20 | 51
9/9/2013 1:00 to 9/9/2013 1:59 | 32.7483 | 45.7492 | 4 | 9.0009 | 210.3131 | 224.3314 | 200.355 | 150.5228 | 76.4497 |  |  | 2013-09-09 01:36 | 71 | 27 | 9 | 15 | 65
9/9/2013 2:00 to 9/9/2013 2:59 | 34.1583 | 47.1207 | 4 | 8.9624 | 209.8008 | 224.1136 | 198.4453 | 150.6086 | 74.9578 |  |  | 2013-09-09 02:39 | 69 | 32 | 12 | 18 | 45
9/9/2013 3:00 to 9/9/2013 3:59 | 35.4373 | 48.4569 | 4 | 9.0196 | 210.2522 | 224.2314 | 197.3575 | 150.4267 | 73.9258 |  |  | 2013-09-09 03:21 | 69 | 33 | 13 | 20 | 62
9/9/2013 4:00 to 9/9/2013 4:59 | 33.2856 | 46.6081 | 4 | 9.3224 | 210.4714 | 224.4561 | 201.3747 | 150.6108 | 73.675 |  |  | 2013-09-09 04:24 | 65 | 41 | 10 | 16 | 28
9/9/2013 5:00 to 9/9/2013 5:59 | 36.7251 | 49.6474 | 4 | 8.9224 | 207.9028 | 223.8597 | 196.7997 | 150.6278 | 70.4519 |  |  | 2013-09-09 05:27 | 65 | 42 | 15 | 20 | 51
9/9/2013 6:00 to 9/9/2013 6:59 | 37.167 | 50.1735 | 4 | 9.0065 | 209.2756 | 224.0883 | 196.8347 | 150.5839 | 69.4 |  |  | 2013-09-09 06:30 | 62 | 46 | 11 | 18 | 32
9/9/2013 7:00 to 9/9/2013 7:59 | 36.6351 | 49.7291 | 4 | 9.094 | 209.9481 | 224.1319 | 197.4567 | 150.8325 | 70.4706 |  |  | 2013-09-09 07:33 | 67 | 37 | 14 | 23 | 64
9/9/2013 8:00 to 9/9/2013 8:59 | 34.2717 | 47.7654 | 4 | 9.4937 | 209.5464 | 224.1319 | 199.8294 | 150.8786 | 74.9753 |  |  | 2013-09-09 08:37 | 67 | 37 | 15 | 21 | 21
9/9/2013 9:00 to 9/9/2013 9:59 | 33.2313 | 47.6803 | 4 | 10.449 | 212.5597 | 224.7075 | 200.5561 | 150.7389 | 81.4875 |  |  | 2013-09-09 09:40 | 70 | 34 | 7 | 13 | 337
9/9/2013 10:00 to 9/9/2013 10:59 | 31.7247 | 46.7319 | 4 | 11.0071 | 214.6 | 225.0761 | 201.5119 | 150.6508 | 87.1378 |  |  | 2013-09-09 10:22 | 72 | 32 | 10 | 20 | 326
9/9/2013 11:00 to 9/9/2013 11:59 | 32.4146 | 47.4777 | 4 | 11.0631 | 215.7269 | 224.9686 | 199.0903 | 150.5083 | 90.1181 |  |  | 2013-09-09 11:25 | 77 | 27 | 6 | 16 | 316
9/9/2013 12:00 to 9/9/2013 12:59 | 33.2706 | 47.602 | 4 | 10.3315 | 214.6153 | 224.8525 | 198.4439 | 150.3878 | 89.3319 |  |  | 2013-09-09 12:28 | 79 | 24 | 8 | 15 | 30
9/9/2013 13:00 to 9/9/2013 13:59 | 29.4174 | 43.7532 | 4 | 10.3358 | 215.3944 | 224.8581 | 202.0631 | 150.545 | 90.1467 |  |  | 2013-09-09 13:35 | 83 | 18 | 11 | 19 | 349
9/9/2013 14:00 to 9/9/2013 14:59 | 31.5739 | 45.9503 | 4 | 10.3764 | 216.8772 | 224.9147 | 198.6714 | 150.4992 | 91.5103 |  |  | 2013-09-09 14:28 | 83 | 16 | 10 | 17 | 311
9/9/2013 15:00 to 9/9/2013 15:59 | 31.3627 | 45.2617 | 4 | 9.899 | 215.0284 | 224.7319 | 198.5467 | 150.3664 | 89.7904 |  |  | 2013-09-09 15:31 | 83 | 15 | 10 | 18 | 319
9/9/2013 16:00 to 9/9/2013 16:59 | 31.5796 | 45.1842 | 4 | 9.6046 | 214.6219 | 224.6139 | 198.5844 | 150.4461 | 88.4525 |  |  | 2013-09-09 16:34 | 84 | 13 | 10 | 18 | 316
9/9/2013 17:00 to 9/9/2013 17:59 | 31.1654 | 44.7982 | 4 | 9.6328 | 214.1578 | 224.3989 | 198.8128 | 150.5572 | 87.5825 |  |  | 2013-09-09 17:37 | 82 | 14 | 13 | 19 | 320
9/9/2013 18:00 to 9/9/2013 18:59 | 31.5409 | 45.0958 | 4 | 9.5549 | 213.5106 | 224.1939 | 198.6339 | 150.5908 | 86.0111 |  |  | 2013-09-09 18:40 | 80 | 15 | 11 | 16 | 16
9/9/2013 19:00 to 9/9/2013 19:59 | 33.2492 | 46.6891 | 4 | 9.4399 | 213.3128 | 224.9267 | 198.3342 | 150.6739 | 83.4825 |  |  | 2013-09-09 19:44 | 74 | 21 | 9 | 11 | 48
9/9/2013 20:00 to 9/9/2013 20:59 | 33.4898 | 46.5573 | 4 | 9.0675 | 211.31 | 224.5411 | 197.7603 | 150.6253 | 80.7158 |  |  | 2013-09-09 20:26 | 75 | 20 | 11 | 17 | 65
9/9/2013 21:00 to 9/9/2013 21:59 | 33.1796 | 46.1216 | 4 | 8.942 | 210.1206 | 224.1364 | 197.6464 | 150.7522 | 77.9633 |  |  | 2013-09-09 21:29 | 74 | 23 | 13 | 22 | 66
9/9/2013 22:00 to 9/9/2013 22:59 | 34.0083 | 47.0458 | 4 | 9.0375 | 210.1594 | 224.2586 | 197.7375 | 150.7067 | 77.0517 |  |  | 2013-09-09 22:32 | 72 | 25 | 13 | 19 | 45
9/9/2013 23:00 to 9/9/2013 23:59 | 35.4663 | 48.7864 | 4 | 9.3201 | 211.6792 | 224.6604 | 198.2817 | 150.7309 | 76.8904 |  |  | 2013-09-09 23:35 | 69 | 28 | 8 | 12 | 28
9/10/2013 0:01 to 9/10/2013 0:59 | 35.3462 | 48.4878 | 4 | 9.1416 | 209.8658 | 224.2763 | 197.6577 | 150.7279 | 75.9081 |  |  | 2013-09-10 00:38 | 69 | 30 | 11 | 16 | 34
9/10/2013 1:00 to 9/10/2013 1:59 | 36.4986 | 49.8806 | 4 | 9.382 | 211.532 | 224.5865 | 197.7501 | 150.7352 | 74.3205 |  |  | 2013-09-10 01:20 | 66 | 32 | 9 | 13 | 23
9/10/2013 2:00 to 9/10/2013 2:59 | 37.5824 | 51.0074 | 4 | 9.425 | 212.0541 | 224.7294 | 196.8203 | 150.7613 | 72.8544 |  |  | 2013-09-10 02:23 | 61 | 38 | 5 | 8 | 0
9/10/2013 3:00 to 9/10/2013 3:59 | 37.2073 | 50.6451 | 4 | 9.4378 | 212.1178 | 224.5944 | 198.2223 | 150.8305 | 70.5415 |  |  | 2013-09-10 03:26 | 66 | 36 | 11 | 14 | 38
9/10/2013 4:00 to 9/10/2013 4:59 | 37.007 | 50.1717 | 4 | 9.1647 | 209.9586 | 224.375 | 197.1492 | 150.8433 | 69.6408 |  |  | 2013-09-10 04:29 | 65 | 38 | 11 | 15 | 48
9/10/2013 5:00 to 9/10/2013 5:59 | 37.0098 | 50.1197 | 4 | 9.1099 | 209.8097 | 224.2511 | 196.8622 | 150.6794 | 70 |  |  | 2013-09-10 05:32 | 64 | 39 | 11 | 16 | 31
9/10/2013 6:00 to 9/10/2013 6:59 | 36.7548 | 49.9589 | 4 | 9.2041 | 209.6728 | 224.2458 | 197.8656 | 150.7236 | 69.4925 |  |  | 2013-09-10 06:35 | 63 | 40 | 10 | 15 | 44
9/10/2013 7:00 to 9/10/2013 7:59 | 36.1676 | 49.5874 | 4 | 9.4198 | 211.0661 | 224.4108 | 199.2686 | 150.6822 | 68.9886 |  |  | 2013-09-10 07:38 | 61 | 41 | 5 | 9 | 353
9/10/2013 8:00 to 9/10/2013 8:59 | 31.8944 | 45.8578 | 4 | 9.9634 | 210.7383 | 224.3597 | 202.0769 | 150.9222 | 76.0083 |  |  | 2013-09-10 08:20 | 67 | 35 | 14 | 19 | 27
9/10/2013 9:00 to 9/10/2013 9:59 | 34.5774 | 48.5326 | 4 | 9.9552 | 209.8767 | 224.3906 | 197.7867 | 150.8208 | 80.5319 |  |  | 2013-09-10 09:23 | 71 | 31 | 13 | 19 | 38
9/10/2013 10:00 to 9/10/2013 10:59 | 33.2702 | 47.2312 | 4 | 9.9611 | 211.2739 | 224.7736 | 198.6167 | 150.6175 | 84.0058 |  |  | 2013-09-10 10:27 | 75 | 26 | 12 | 19 | 42
9/10/2013 11:00 to 9/10/2013 11:59 | 30.0199 | 44.5598 | 4 | 10.5398 | 213.5603 | 224.9511 | 201.9422 | 150.4833 | 89.1128 |  |  | 2013-09-10 11:38 | 79 | 22 | 7 | 15 | 31
9/10/2013 12:00 to 9/10/2013 12:59 | 28.6283 | 43.2104 | 4 | 10.5821 | 215.2953 | 224.9689 | 202.8436 | 150.8819 | 91.4933 |  |  | 2013-09-10 12:20 | 81 | 20 | 7 | 15 | 32
9/10/2013 13:00 to 9/10/2013 13:59 | 27.064 | 41.7299 | 4 | 10.666 | 217.42 | 225.1147 | 203.4711 | 150.9275 | 93.5286 |  |  | 2013-09-10 13:23 | 85 | 14 | 7 | 13 | 294
9/10/2013 14:00 to 9/10/2013 14:59 | 27.1372 | 41.7548 | 4 | 10.6176 | 216.0417 | 225.0483 | 202.5275 | 150.4928 | 94.73 |  |  | 2013-09-10 14:26 | 86 | 11 | 8 | 14 | 356
9/10/2013 15:00 to 9/10/2013 15:59 | 29.7301 | 43.8041 | 4 | 10.074 | 215.9269 | 224.8492 | 199.1147 | 150.5186 | 92.6536 |  |  | 2013-09-10 15:29 | 87 | 12 | 10 | 19 | 330
9/10/2013 16:00 to 9/10/2013 16:59 | 29.8788 | 43.6477 | 4 | 9.7689 | 215.0108 | 224.8189 | 199.1231 | 151.6067 | 91.4797 |  |  | 2013-09-10 16:32 | 86 | 11 | 7 | 15 | 34
9/10/2013 17:00 to 9/10/2013 17:59 | 30.7643 | 44.251 | 4 | 9.4867 | 214.185 | 224.5075 | 199.0264 | 153.1753 | 88.5056 |  |  | 2013-09-10 17:35 | 84 | 12 | 9 | 17 | 7
9/10/2013 18:00 to 9/10/2013 18:59 | 31.6576 | 45.1096 | 4 | 9.452 | 214.0992 | 224.5303 | 198.7214 | 154.0689 | 86.445 |  |  | 2013-09-10 18:38 | 80 | 12 | 6 | 9 | 32
9/10/2013 19:00 to 9/10/2013 19:59 | 32.4454 | 45.6908 | 4 | 9.2454 | 214.6069 | 224.9619 | 198.5558 | 152.8092 | 83.8822 |  |  | 2013-09-10 19:20 | 77 | 14 | 7 | 10 | 72
9/10/2013 20:00 to 9/10/2013 20:59 | 32.8363 | 46.0847 | 4 | 9.2484 | 215.1147 | 225.0456 | 198.6119 | 150.4644 | 81.7325 |  |  | 2013-09-10 20:23 | 75 | 17 | 7 | 9 | 82
9/10/2013 21:00 to 9/10/2013 21:59 | 34.1914 | 47.4221 | 4 | 9.2307 | 216.6003 | 225.2173 | 199.2771 | 149.8164 | 80.9459 |  |  | 2013-09-10 21:26 | 73 | 18 | 9 | 11 | 89
9/10/2013 22:01 to 9/10/2013 22:59 | 34.1062 | 47.535 | 4 | 9.4289 | 214.7289 | 225.1666 | 199.7014 | 150.362 | 80.2212 |  |  | 2013-09-10 22:29 | 70 | 20 | 8 | 11 | 31
9/10/2013 23:00 to 9/10/2013 23:59 | 34.944 | 48.1439 | 4 | 9.1999 | 211.384 | 224.6181 | 197.5613 | 150.5828 | 79.1828 |  |  | 2013-09-10 23:32 | 71 | 21 | 11 | 15 | 42
9/11/2013 0:01 to 9/11/2013 0:59 | 35.2059 | 48.2744 | 4 | 9.0685 | 209.8952 | 224.2491 | 197.2778 | 150.654 | 77.1483 |  |  | 2013-09-11 00:35 | 71 | 24 | 14 | 19 | 52
9/11/2013 1:00 to 9/11/2013 1:59 | 35.5922 | 48.655 | 4 | 9.0628 | 210.3375 | 224.4303 | 197.1711 | 150.4017 | 76.4 |  |  | 2013-09-11 01:38 | 71 | 25 | 10 | 14 | 38
9/11/2013 2:00 to 9/11/2013 2:59 | 35.7258 | 48.7386 | 4 | 9.0127 | 210.3873 | 224.4305 | 197.2382 | 150.0657 | 76.4 |  |  | 2013-09-11 02:24 | 72 | 24 | 11 | 17 | 47
9/11/2013 3:00 to 9/11/2013 3:59 | 34.527 | 47.5134 | 4 | 8.9864 | 209.4401 | 224.1655 | 197.2059 | 149.9894 | 76.4 |  |  | 2013-09-11 03:27 | 72 | 23 | 12 | 21 | 45
9/11/2013 4:00 to 9/11/2013 4:59 | 32.6482 | 45.6492 | 4 | 9.001 | 209.2322 | 224.0953 | 200.5503 | 150.2319 | 76.1206 |  |  | 2013-09-11 04:30 | 70 | 25 | 12 | 18 | 41
9/11/2013 5:00 to 9/11/2013 5:59 | 35.3707 | 48.3848 | 4 | 9.0141 | 208.7978 | 224.0967 | 197.0986 | 150.3028 | 74.6817 |  |  | 2013-09-11 05:33 | 68 | 27 | 11 | 16 | 45
9/11/2013 6:00 to 9/11/2013 6:59 | 36.061 | 49.2089 | 4 | 9.1479 | 210.1278 | 224.2064 | 197.6661 | 150.2969 | 73.1692 |  |  | 2013-09-11 06:36 | 68 | 27 | 8 | 14 | 40
9/11/2013 7:00 to 9/11/2013 7:59 | 37.386 | 50.9472 | 4 | 9.5613 | 212.6747 | 224.6467 | 196.4517 | 150.1156 | 73.1042 |  |  | 2013-09-11 07:39 | 70 | 27 | 10 | 16 | 11
9/11/2013 8:00 to 9/11/2013 8:59 | 34.4114 | 48.3221 | 4 | 9.9107 | 211.3539 | 224.2928 | 197.5872 | 150.2447 | 79.8039 |  |  | 2013-09-11 08:21 | 71 | 27 | 12 | 17 | 4
9/11/2013 9:00 to 9/11/2013 9:59 | 31.311 | 45.7757 | 4 | 10.4647 | 211.7472 | 224.4819 | 200.3831 | 150.1917 | 85.3094 |  |  | 2013-09-11 09:24 | 76 | 23 | 11 | 17 | 352
9/11/2013 10:00 to 9/11/2013 10:59 | 33.2194 | 47.0687 | 4 | 9.8493 | 210.9106 | 224.5231 | 198.1153 | 149.7478 | 83.3075 |  |  | 2013-09-11 10:27 | 75 | 23 | 12 | 17 | 24
9/11/2013 11:00 to 9/11/2013 11:59 | 31.2653 | 44.9808 | 4 | 9.7155 | 210.4561 | 224.5372 | 199.5372 | 149.7819 | 85.5739 |  |  | 2013-09-11 11:30 | 78 | 21 | 14 | 22 | 37
9/11/2013 12:00 to 9/11/2013 12:59 | 33.1166 | 46.633 | 4 | 9.5164 | 210.17 | 224.3717 | 198.1075 | 149.9792 | 81.7569 |  |  | 2013-09-11 12:31 | 75 | 23 | 14 | 20 | 32
9/11/2013 13:00 to 9/11/2013 13:59 | 34.0851 | 47.4254 | 4 | 9.3403 | 211.5508 | 224.6608 | 197.6611 | 149.6492 | 80.9708 |  |  | 2013-09-11 13:34 | 76 | 23 | 11 | 16 | 38
9/11/2013 14:00 to 9/11/2013 14:59 | 32.806 | 46.3748 | 4 | 9.5688 | 213.9153 | 224.7536 | 198.4514 | 148.4547 | 83.3797 |  |  | 2013-09-11 14:37 | 79 | 23 | 5 | 9 | 16
9/11/2013 15:00 to 9/11/2013 15:59 | 32.3229 | 45.9008 | 4 | 9.5779 | 215.3597 | 224.8242 | 198.795 | 148.3097 | 85.3369 |  |  | 2013-09-11 15:40 | 80 | 23 | 3 | 5 | 318
9/11/2013 16:00 to 9/11/2013 16:59 | 30.9726 | 44.7337 | 4 | 9.7611 | 218.2647 | 225.1578 | 201.54 | 149.8208 | 87.1997 |  |  | 2013-09-11 16:24 | 81 | 22 | 1 | 3 | 312
9/11/2013 17:00 to 9/11/2013 17:59 | 29.9102 | 43.5758 | 4 | 9.6656 | 217.2144 | 225.1056 | 202.5628 | 149.8536 | 86.7803 |  |  | 2013-09-11 17:27 | 80 | 22 | 1 | 5 | 328
9/11/2013 18:00 to 9/11/2013 18:59 | 32.2468 | 45.6967 | 4 | 9.4499 | 218.3903 | 225.3392 | 199.4067 | 149.7122 | 84.9708 |  |  | 2013-09-11 18:30 | 77 | 25 | 5 | 6 | 119
9/11/2013 19:00 to 9/11/2013 19:59 | 32.4725 | 45.8779 | 4 | 9.4054 | 217.6692 | 225.3564 | 199.2261 | 149.4906 | 84.3 |  |  | 2013-09-11 19:33 | 74 | 29 | 2 | 3 | 150
9/11/2013 20:00 to 9/11/2013 20:59 | 32.5993 | 46.0178 | 4 | 9.4185 | 214.9547 | 224.8653 | 198.8247 | 149.6972 | 83.3697 |  |  | 2013-09-11 20:36 | 76 | 29 | 11 | 19 | 3
9/11/2013 21:00 to 9/11/2013 21:59 | 33.1877 | 46.1475 | 4 | 8.9599 | 210.8303 | 224.3011 | 197.6397 | 149.8981 | 79.9136 |  |  | 2013-09-11 21:39 | 76 | 32 | 16 | 23 | 59
9/11/2013 22:00 to 9/11/2013 22:59 | 34.2362 | 47.5346 | 4 | 9.2984 | 212.8544 | 224.54 | 197.7467 | 149.9656 | 79.0778 |  |  | 2013-09-11 22:21 | 75 | 32 | 13 | 19 | 38
9/11/2013 23:00 to 9/11/2013 23:59 | 35.274 | 48.6069 | 4 | 9.3328 | 212.0458 | 224.6851 | 197.3899 | 150.0969 | 77.0228 |  |  | 2013-09-11 23:24 | 70 | 46 | 8 | 11 | 28
9/12/2013 0:01 to 9/12/2013 0:59 | 35.6742 | 49.032 | 4 | 9.3578 | 212.306 | 224.7613 | 197.3667 | 150.0715 | 76.7949 |  |  | 2013-09-12 00:27 | 68 | 50 | 6 | 9 | 6
9/12/2013 1:00 to 9/12/2013 1:59 | 36.2283 | 49.5252 | 4 | 9.2969 | 210.2486 | 224.3181 | 196.7597 | 149.9594 | 74.4667 |  |  | 2013-09-12 01:30 | 67 | 55 | 12 | 17 | 27
9/12/2013 2:00 to 9/12/2013 2:59 | 37.0182 | 50.0506 | 4 | 9.0324 | 209.3572 | 224.1128 | 196.3453 | 150.0131 | 72.9586 |  |  | 2013-09-12 02:23 | 65 | 56 | 11 | 17 | 11
9/12/2013 3:00 to 9/12/2013 3:59 | 37.174 | 50.2177 | 4 | 9.0438 | 210.5003 | 224.3442 | 196.6242 | 150.0622 | 72.1058 |  |  | 2013-09-12 03:26 | 66 | 55 | 11 | 14 | 25
9/12/2013 4:00 to 9/12/2013 4:59 | 37.1413 | 50.1863 | 4 | 9.0451 | 210.8614 | 224.42 | 196.8953 | 150.0764 | 72.145 |  |  | 2013-09-12 04:29 | 66 | 56 | 9 | 14 | 64
9/12/2013 5:00 to 9/12/2013 5:59 | 34.8324 | 48.1909 | 4 | 9.3585 | 212.8389 | 224.7517 | 200.4744 | 150.2092 | 72.6211 |  |  | 2013-09-12 05:32 | 66 | 57 | 9 | 13 | 38
9/12/2013 6:00 to 9/12/2013 6:59 | 36.7059 | 49.9738 | 4 | 9.2679 | 210.4953 | 224.4389 | 196.9067 | 150.1122 | 72.1614 |  |  | 2013-09-12 06:35 | 65 | 61 | 9 | 13 | 45
9/12/2013 7:00 to 9/12/2013 7:59 | 36.8799 | 49.9844 | 4 | 9.1045 | 210.3051 | 224.225 | 196.5905 | 150.0435 | 71.5533 |  |  | 2013-09-12 07:38 | 68 | 56 | 9 | 13 | 40
9/12/2013 8:00 to 9/12/2013 8:59 | 33.0518 | 46.7326 | 4 | 9.6808 | 210.2657 | 224.3609 | 200.7179 | 150.1269 | 76.8615 |  |  | 2013-09-12 08:20 | 68 | 54 | 12 | 18 | 44
9/12/2013 9:00 to 9/12/2013 9:59 | 31.396 | 45.7332 | 4 | 10.3372 | 212.1315 | 224.7614 | 201.0364 | 150.1691 | 84.0694 |  |  | 2013-09-12 09:23 | 73 | 47 | 11 | 16 | 21
9/12/2013 10:00 to 9/12/2013 10:59 | 31.4984 | 45.6955 | 4 | 10.1971 | 211.8278 | 224.8018 | 199.8124 | 150.103 | 86.4142 |  |  | 2013-09-12 10:26 | 77 | 34 | 14 | 21 | 20
9/18/2013 0:01 to 9/18/2013 0:59 | 40.6138 | 53.4326 | 3.9 | 8.9188 | 214.0885 | 223.4556 | 195.2891 | 152.5943 | 60.8903 |  |  | 2013-09-18 00:23 | 52 | 59 | 2 | 5 | 113
9/18/2013 1:00 to 9/18/2013 1:59 | 40.6846 | 53.7541 | 3.9 | 9.1695 | 214.1339 | 223.9403 | 195.4006 | 152.3528 | 61.7719 |  |  | 2013-09-18 01:26 | 50 | 63 | 2 | 5 | 160
9/18/2013 2:00 to 9/18/2013 2:59 | 41.3514 | 54.4639 | 3.9 | 9.2125 | 214.4989 | 224.2034 | 194.994 | 152.122 | 61.7211 |  |  | 2013-09-18 02:29 | 48 | 67 | 1 | 4 | 342
9/18/2013 3:00 to 9/18/2013 3:59 | 41.6052 | 54.7275 | 3.9 | 9.2223 | 215.4064 | 224.4015 | 195.5429 | 152.1 | 60.1666 |  |  | 2013-09-18 03:32 | 45 | 70 | 1 | 4 | 7
9/18/2013 4:00 to 9/18/2013 4:59 | 40.9919 | 54.187 | 3.9 | 9.295 | 213.8435 | 224.4149 | 196.8568 | 151.938 | 58.9538 |  |  | 2013-09-18 04:35 | 45 | 71 | 4 | 5 | 42
9/18/2013 5:00 to 9/18/2013 5:59 | 41.1419 | 54.3524 | 3.9 | 9.3105 | 212.4344 | 224.3476 | 197.6054 | 151.8536 | 57.9299 |  |  | 2013-09-18 05:38 | 43 | 74 | 1 | 3 | 21
9/18/2013 7:00 to 9/18/2013 7:59 | 42.7475 | 55.987 | 3.9 | 9.3394 | 214.0482 | 224.5728 | 194.8948 | 151.7626 | 57.2925 |  |  | 2013-09-18 07:23 | 42 | 76 | 1 | 4 | 302
9/18/2013 8:01 to 9/18/2013 8:59 | 39.2579 | 53.3867 | 3.9 | 10.2288 | 214.0788 | 224.6779 | 198.8769 | 152.1371 | 65.4913 |  |  | 2013-09-18 08:26 | 49 | 61 | 3 | 6 | 323
9/18/2013 9:00 to 9/18/2013 9:59 | 38.3242 | 53.1325 | 3.9 | 10.9083 | 213.6656 | 224.7408 | 198.1765 | 152.0553 | 72.9634 |  |  | 2013-09-18 09:29 | 55 | 50 | 3 | 7 | 354
9/18/2013 10:00 to 9/18/2013 10:59 | 38.5476 | 53.5023 | 3.9 | 11.0547 | 213.2257 | 224.7732 | 196.9867 | 151.6437 | 76.244 |  |  | 2013-09-18 10:32 | 58 | 43 | 5 | 15 | 352
9/18/2013 11:00 to 9/18/2013 11:59 | 36.5635 | 51.643 | 3.9 | 11.1795 | 215.2332 | 225.0051 | 198.9611 | 151.1731 | 78.3551 |  |  | 2013-09-18 11:35 | 60 | 35 | 5 | 13 | 354
9/18/2013 12:00 to 9/18/2013 12:59 | 37.871 | 53.0023 | 3.9 | 11.2314 | 216.3048 | 225.2278 | 196.7585 | 151.4332 | 81.2463 |  |  | 2013-09-18 12:38 | 62 | 32 | 6 | 13 | 356
9/18/2013 13:00 to 9/18/2013 13:59 | 36.1104 | 51.1793 | 3.9 | 11.169 | 216.0208 | 225.2603 | 199.24 | 152.0228 | 82.2856 |  |  | 2013-09-18 13:20 | 65 | 28 | 5 | 11 | 227
9/18/2013 14:00 to 9/18/2013 14:59 | 36.6092 | 51.619 | 4 | 11.0098 | 216.9161 | 225.255 | 197.9297 | 153.08 | 83.4208 |  |  | 2013-09-18 14:23 | 68 | 22 | 7 | 15 | 305
9/18/2013 15:00 to 9/18/2013 15:59 | 36.6405 | 50.9669 | 4 | 10.3264 | 216.7536 | 225.2736 | 197.6925 | 154.3453 | 80.4906 |  |  | 2013-09-18 15:26 | 70 | 16 | 3 | 10 | 260
9/18/2013 16:00 to 9/18/2013 16:59 | 36.343 | 50.3572 | 4 | 10.0142 | 217.2186 | 225.2692 | 197.9597 | 153.6986 | 78.7531 |  |  | 2013-09-18 16:29 | 71 | 13 | 2 | 7 | 326
9/18/2013 17:00 to 9/18/2013 17:59 | 35.4921 | 49.4413 | 4 | 9.9491 | 214.7286 | 224.9806 | 198.6011 | 151.6903 | 78.525 |  |  | 2013-09-18 17:33 | 69 | 20 | 5 | 10 | 359
9/18/2013 18:00 to 9/18/2013 18:59 | 35.9458 | 49.7606 | 4 | 9.8147 | 213.995 | 224.6886 | 198.3692 | 150.6522 | 76.0075 |  |  | 2013-09-18 18:36 | 65 | 23 | 8 | 11 | 325
9/18/2013 19:00 to 9/18/2013 19:59 | 38.0195 | 51.3862 | 4 | 9.3667 | 212.2547 | 224.6108 | 196.8078 | 150.9356 | 71.8869 |  |  | 2013-09-18 19:39 | 60 | 25 | 7 | 10 | 61
9/18/2013 20:00 to 9/18/2013 20:59 | 37.6187 | 50.5857 | 4 | 8.967 | 212.6089 | 224.3225 | 197.3578 | 151.1056 | 67.1517 |  |  | 2013-09-18 20:21 | 60 | 23 | 8 | 11 | 82
9/18/2013 21:00 to 9/18/2013 21:59 | 38.5356 | 51.447 | 4 | 8.9113 | 210.6206 | 224.2514 | 196.1906 | 151.0769 | 66.9872 |  |  | 2013-09-18 21:24 | 59 | 25 | 9 | 13 | 68
9/18/2013 22:00 to 9/18/2013 22:59 | 38.0793 | 50.989 | 4 | 8.9097 | 209.6803 | 224.02 | 195.9983 | 151.0614 | 66.4292 |  |  | 2013-09-18 22:27 | 59 | 29 | 9 | 14 | 66
9/18/2013 23:00 to 9/18/2013 23:59 | 38.2228 | 51.3628 | 4 | 9.14 | 210.2981 | 224.1808 | 197.2622 | 150.7833 | 65.1503 |  |  | 2013-09-18 23:30 | 55 | 32 | 5 | 9 | 45
9/19/2013 0:02 to 9/19/2013 0:59 | 40.6372 | 53.831 | 4 | 9.1939 | 209.6348 | 224.0562 | 195.451 | 150.6791 | 60.4942 |  |  | 2013-09-19 00:33 | 49 | 35 | 10 | 14 | 13
9/19/2013 1:00 to 9/19/2013 1:59 | 40.2284 | 53.1597 | 4 | 8.9313 | 207.3289 | 223.5569 | 195.4508 | 150.9506 | 60.3 |  |  | 2013-09-19 01:36 | 55 | 31 | 14 | 21 | 41
9/19/2013 2:00 to 9/19/2013 2:59 | 39.6992 | 52.6261 | 4 | 8.9268 | 206.5494 | 223.4268 | 195.2737 | 151.3142 | 60.2779 |  |  | 2013-09-19 02:39 | 54 | 32 | 15 | 20 | 51
9/19/2013 3:00 to 9/19/2013 3:59 | 40.7427 | 53.7798 | 4 | 9.0371 | 208.0422 | 223.6309 | 195.0844 | 150.9745 | 59.1187 |  |  | 2013-09-19 03:21 | 53 | 33 | 12 | 17 | 44
9/19/2013 4:00 to 9/19/2013 4:59 | 40.9017 | 53.6746 | 4 | 8.7729 | 206.8383 | 223.513 | 194.973 | 150.6487 | 56.8652 |  |  | 2013-09-19 04:24 | 52 | 34 | 12 | 17 | 47
9/19/2013 5:00 to 9/19/2013 5:59 | 40.8467 | 53.5583 | 4 | 8.7116 | 205.9637 | 223.2317 | 194.8559 | 150.7294 | 55.998 |  |  | 2013-09-19 05:27 | 51 | 36 | 13 | 20 | 48
9/19/2013 6:00 to 9/19/2013 6:59 | 41.6222 | 54.6531 | 4 | 9.0309 | 209.9436 | 224.0792 | 195.9661 | 151.0036 | 52.715 |  |  | 2013-09-19 06:30 | 41 | 49 | 6 | 10 | 360
9/19/2013 7:00 to 9/19/2013 7:59 | 43.4306 | 56.3279 | 4 | 8.8973 | 210.5514 | 224.2678 | 194.3925 | 150.5847 | 52.7964 |  |  | 2013-09-19 07:33 | 43 | 45 | 6 | 9 | 353
9/19/2013 8:00 to 9/19/2013 8:59 | 39.4068 | 53.2797 | 4 | 9.873 | 211.0844 | 224.2517 | 196.8914 | 150.8817 | 64.0917 |  |  | 2013-09-19 08:36 | 53 | 34 | 8 | 12 | 344
9/19/2013 9:00 to 9/19/2013 9:59 | 38.3673 | 52.2409 | 4 | 9.8737 | 208.1436 | 223.8336 | 196.4039 | 150.9431 | 68.1383 |  |  | 2013-09-19 09:39 | 59 | 29 | 13 | 20 | 38
9/19/2013 10:00 to 9/19/2013 10:59 | 37.269 | 51.3424 | 4 | 10.0734 | 210.9814 | 224.4136 | 197.3839 | 150.555 | 73.8189 |  |  | 2013-09-19 10:44 | 63 | 25 | 7 | 12 | 333
9/19/2013 11:00 to 9/19/2013 11:59 | 34.1128 | 49.3358 | 4 | 11.223 | 214.8167 | 225.2547 | 200.4222 | 149.5694 | 83.5625 |  |  | 2013-09-19 11:26 | 67 | 21 | 5 | 10 | 8
9/19/2013 12:00 to 9/19/2013 12:59 | 35.0398 | 50.3711 | 4 | 11.3313 | 217.0983 | 225.2636 | 198.9619 | 148.8489 | 86.4228 |  |  | 2013-09-19 12:29 | 71 | 16 | 4 | 11 | 281

## Runtime Tally
Month of Runtime | Total Runtime (Incld's Factory) [hr] | Site Runtime [hr] | Total Gross Energy (Site Only) [kWh] | Gross Energy for Month [kWh] | Notes
2013-03-12 | 169 | - | 0 | - | Factory Hours
Start-Up to 3/31/2013 | 206 | 37 | 1741 | 1741
4/1/13 to 4/30/2013 | 225 | 56 | 2763 | 1022
5/1/13 to 5/31/2013 | 327 | 158 | 7541 | 4778
6/1/13 to 6/30/13 | 454 | 285 | 11723 | 4182
7/1/13 to 7/31/13 | 465 | 296 | 12122 | 399
8/1/13 to 8/31/13 | 599 | 430 | 18320 | 6198
9/1/13 to 9/30/13 | 923 | 754 | 33517 | 15197