## Average
Date/Time | Total Net Power Output (Calculated) | Gross Power Output (Veris) | Pump Parasitic Load | Cooling Fan Parasitic Load (Veris) | Geothermal Header Hot Water Temperature | Hot Water Supply Temperature | Hot Water Return Temperature | Hot Water Supply Flow Rate | Ambient Temperature (GM Sensor) | Notes | MESO West WeatherData | Date/Time | Ambient Temperature | Relative Humidity | Wind Speed | Wind Gust | Wind Direction
| kW | kW | kW | kW | F | F | F | gpm | F |  | Station ID: HMHNV |  | F | % | mph | mph | Degrees
1/3/2014 18:00 to 1/3/2014 18:59 | 42.5284 | 54.8871 | 4.0228 | 8.3359 | 209.5103 | 222.5339 | 201.4764 | 174.6372 | 47.7825 |  |  | 2014-01-03 18:23 | 46 | 53 | 7 | 9 | 0
1/3/2014 19:00 to 1/3/2014 19:59 | 42.9204 | 55.3648 | 4.1 | 8.3444 | 212.786 | 223.457 | 197.9575 | 154.0199 | 46.898 |  |  | 2014-01-03 19:30 | 35 | 67 | 2 | 3 | 178
1/3/2014 20:00 to 1/3/2014 20:59 | 42.5808 | 54.9227 | 4.1 | 8.242 | 211.7531 | 223.3094 | 195.6542 | 148.5164 | 47.4667 |  |  | 2014-01-03 20:39 | 37 | 63 | 1 | 4 | 121
1/3/2014 21:00 to 1/3/2014 21:59 | 42.6412 | 55.3649 | 4.1 | 8.6236 | 212.9777 | 223.7972 | 197.6117 | 146.1613 | 44.932 |  |  | 2014-01-03 21:23 | 28 | 73 | 2 | 3 | 119
1/3/2014 22:00 to 1/3/2014 22:59 | 42.9253 | 55.6075 | 4.1735 | 8.5086 | 213.8599 | 223.9811 | 195.582 | 145.116 | 48.0474 |  |  | 2014-01-03 22:39 | 37 | 60 | 3 | 5 | 130
1/3/2014 23:00 to 1/3/2014 23:59 | 42.2011 | 55.3717 | 4.2 | 8.9706 | 213.8152 | 224.3056 | 196.3393 | 144.0188 | 51.2716 |  |  | 2014-01-03 23:27 | 34 | 59 | 3 | 4 | 37
1/5/2014 0:00 to 1/5/2014 0:59 | 39.5271 | 51.9074 | 4.2 | 8.1803 | 210.9145 | 223.9564 | 202.4684 | 147.9631 | 28.4254
1/5/2014 1:00 to 1/5/2014 1:59 | 41.4932 | 53.3926 | 4.2 | 7.6994 | 211.4697 | 224.0364 | 201.4483 | 147.7608 | 25.8172
1/5/2014 2:00 to 1/5/2014 2:59 | 39.878 | 52.0054 | 4.2 | 7.9274 | 211.7108 | 224.0103 | 201.9275 | 147.3303 | 26.9147
1/5/2014 3:00 to 1/5/2014 3:59 | 38.8769 | 51.0904 | 4.2 | 8.0135 | 211.7958 | 223.9847 | 202.1142 | 147.3086 | 28.2522
1/5/2014 4:00 to 1/5/2014 4:59 | 38.7609 | 51.0564 | 4.1047 | 8.1908 | 212.4158 | 224.1831 | 202.2633 | 149.7308 | 29.1525
1/5/2014 5:00 to 1/5/2014 5:59 | 41.0734 | 52.9609 | 4.1 | 7.7875 | 211.7513 | 224.0381 | 201.3541 | 150.6459 | 26.8361
1/5/2014 6:00 to 1/5/2014 6:59 | 39.6021 | 51.9688 | 4.1 | 8.2666 | 213.6164 | 224.365 | 201.928 | 151.6452 | 30.3935
1/5/2014 7:00 to 1/5/2014 7:59 | 38.9147 | 51.3914 | 4.1 | 8.3767 | 213.4305 | 224.4499 | 202.3398 | 150.6784 | 30.1798
1/5/2014 8:00 to 1/5/2014 8:59 | 40.391 | 52.8907 | 4.1 | 8.3997 | 213.7466 | 224.4449 | 202.0815 | 148.2798 | 32.0434
1/5/2014 9:00 to 1/5/2014 9:59 | 40.2071 | 53.7936 | 4.1 | 9.4866 | 215.1113 | 224.7828 | 201.6876 | 147.5513 | 42.9823
1/5/2014 10:00 to 1/5/2014 10:59 | 39.4453 | 53.6326 | 4.1 | 10.0873 | 213.1863 | 224.873 | 204.1137 | 159.9215 | 49.4657
1/5/2014 11:00 to 1/5/2014 11:59 | 40.8835 | 55.0321 | 4.1 | 10.0486 | 212.5363 | 224.8061 | 201.9757 | 155.1857 | 53.1702
1/5/2014 12:00 to 1/5/2014 12:59 | 41.0339 | 55.1747 | 4.1 | 10.0408 | 211.7273 | 224.6304 | 201.1091 | 152.694 | 53.8722
1/5/2014 13:00 to 1/5/2014 13:58 | 41.2586 | 55.2788 | 4.1 | 9.9202 | 213.134 | 224.9818 | 200.9131 | 151.248 | 55.0799
1/5/2014 14:00 to 1/5/2014 14:59 | 41.9182 | 55.8187 | 4.1 | 9.8005 | 213.3194 | 224.9713 | 200.1742 | 150.0651 | 55.5067
1/5/2014 15:00 to 1/5/2014 15:59 | 41.5665 | 55.0542 | 4.1 | 9.3877 | 211.524 | 224.6646 | 200.2444 | 149.3129 | 51.7067
1/5/2014 16:00 to 1/5/2014 16:59 | 41.622 | 54.73 | 4.1 | 9.0081 | 210.9784 | 224.6148 | 200.475 | 148.969 | 48.9142
1/22/2014 9:00 to 1/22/2014 9:59 | 41.3509 | 54.73 | 3.7535 | 9.6257 | 214.0419 | 223.7666 | 203.0708 | 165.9292 | 50.5723 |  |  | 2014-01-22 09:28 | 33 | 51 | 3 | 4 | 72
1/22/2014 10:00 to 1/22/2014 10:59 | 39.5895 | 53.8018 | 3.8 | 10.4123 | 214.8994 | 224.2245 | 202.7798 | 159.5384 | 61.3193 |  |  | 2014-01-22 10:35 | 47 | 34 | 2 | 4 | 281
1/22/2014 11:00 to 1/22/2014 11:59 | 39.8379 | 53.7924 | 3.8 | 10.1545 | 212.2272 | 223.8582 | 201.2122 | 154.6427 | 63.5913 |  |  | 2014-01-22 11:21 | 53 | 31 | 3 | 6 | 274
1/22/2014 12:00 to 1/22/2014 12:59 | 40.3655 | 53.4528 | 3.8 | 9.2873 | 211.0776 | 223.6129 | 199.7445 | 153.3463 | 58.8325 |  |  | 2014-01-22 12:28 | 63 | 22 | 12 | 15 | 195
1/22/2014 13:00 to 1/22/2014 13:59 | 39.0072 | 52.3951 | 3.8912 | 9.4968 | 214.9494 | 224.5894 | 201.2868 | 151.6712 | 62.8479 |  |  | 2014-01-22 13:37 | 64 | 20 | 3 | 5 | 261
1/22/2014 14:00 to 1/22/2014 14:59 | 38.0477 | 51.8844 | 3.9 | 9.9366 | 212.7696 | 224.4642 | 200.9072 | 148.7321 | 65.3834 |  |  | 2014-01-22 14:21 | 62 | 22 | 5 | 9 | 332
1/22/2014 15:00 to 1/22/2014 15:59 | 39.2022 | 52.5137 | 3.9 | 9.4114 | 210.191 | 223.9921 | 199.9388 | 147.2669 | 59.8567 |  |  | 2014-01-22 15:28 | 62 | 19 | 8 | 10 | 347
1/22/2014 16:00 to 1/22/2014 16:59 | 39.8951 | 52.928 | 3.9 | 9.1329 | 209.6595 | 223.8557 | 198.5405 | 146.4466 | 57.0337 |  |  | 2014-01-22 16:35 | 55 | 20 | 10 | 13 | 48
1/22/2014 17:00 to 1/22/2014 17:59 | 40.0803 | 52.5541 | 3.9 | 8.5737 | 207.1867 | 223.2696 | 198.0829 | 145.7017 | 50.7325 |  |  | 2014-01-22 17:20 | 50 | 23 | 11 | 14 | 62
1/22/2014 18:00 to 1/22/2014 18:59 | 40.5161 | 52.9979 | 3.9 | 8.5818 | 207.1315 | 223.2829 | 196.333 | 145.2225 | 49.782 |  |  | 2014-01-22 18:26 | 50 | 26 | 11 | 13 | 56
1/22/2014 19:00 to 1/22/2014 19:59 | 39.3451 | 52.0578 | 3.9 | 8.8127 | 207.1776 | 223.5032 | 199.4888 | 145.9985 | 49.4646 |  |  | 2014-01-22 19:34 | 41 | 32 | 8 | 10 | 45
1/22/2014 20:00 to 1/22/2014 20:59 | 41.0785 | 53.8803 | 3.9 | 8.9018 | 209.0314 | 223.9067 | 199.6267 | 146.3532 | 46.2985 |  |  | 2014-01-22 20:20 | 34 | 37 | 11 | 14 | 326
1/22/2014 21:00 to 1/22/2014 21:59 | 42.5058 | 54.8929 | 3.9 | 8.4871 | 207.4506 | 223.6359 | 198.0867 | 146.2675 | 42.6893 |  |  | 2014-01-22 21:27 | 29 | 41 | 7 | 9 | 352
1/22/2014 22:00 to 1/22/2014 22:59 | 42.4892 | 54.5623 | 3.9 | 8.1731 | 206.5664 | 223.3396 | 197.9499 | 146.0803 | 40.359 |  |  | 2014-01-22 22:35 | 28 | 44 | 9 | 13 | 359